## NOTE
NOTE:
1. Refer to the file "NFRL_CompositeBeamTest_TestSetup_and_InstrumentationLayout.xlsx" in this folder for test setup drawings and instrumentation layouts.
2. In this Excel file,
i. Tab "Channel List" provides a list of the sensors used for CB-DA-SC and their labels, locations, and the measurement units.
ii. Tab "User Events" provides recorded time stamps of major events during the test.
iii. Tab "CB-DA-SC-AmbientLoadingData" provides the data recorded during mechanical loading prior to ignition of a fire
iv. Tab "CB-DA-SC-FireLoadingData" provides the data recorded during fire loading.
Table 1. Test Matrix
Test No. | Specimen name | Test date | Beam-to-column connection | Slab end continuity | Applied Mechanical Load Level M/Mu | Fire Load
1 | CB-DA-AMB | 2017-09-21 | Welded/bolted double angles | - | 1 | -
2 | CB-DA | 2017-12-19 | Welded/bolted double angles | - | 0.45 | 4 MW
3 | CB-DA-SC | 2018-01-12 | Welded/bolted double angles | Included | 0.45 | 4 MW
4 | CB-SP | 2018-02-13 | Single plate | - | 0.45 | 4 MW
5 | CB-SP-SC | 2018-03-06 | Single plate | Included | 0.45 | 4 MW

## Channel List
Channel Name/Description | Legend/ID | Group Name | Range/Type | Range Low | Range High | Scaled Units
Strain @ South Top Flange (Bot Surf) | SG1 | SGMid | Strain gauge | -30000 | 30000 | microstrain
Strain @ South Middle Web | SG2 | SGMid | Strain gauge | -30000 | 30000 | microstrain
Strain @ South Bot Flange (Bot Surf) | SG3 | SGMid | Strain gauge | -30000 | 30000 | microstrain
Strain @ North Bot Flange (Bot Surf) | SG4 | SGMid | Strain gauge | -30000 | 30000 | microstrain
Strain @ North Top Flange (Bot Surf) | SG5 | SGMid | Strain gauge | -30000 | 30000 | microstrain
Strain @ West End (1'-9" from Slab End, Bot Bolt) | SGW2 | SGEnd | Strain gauge | -30000 | 30000 | microstrain
Strain @ West_Col_TopBrace_Top_North | ColW1 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ West_Col_TopBrace_Top_South | ColW2 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ West_Col_TopBrace_Bot_North | ColW3 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ West_Col_TopBrace_Bot_South | ColW4 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ West_Col_BotBrace_Top_North | ColW5 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ West_Col_BotBrace_Top_South | ColW6 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ West_Col_BotBrace_Bot_North | ColW7 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ West_Col_BotBrace_Bot_South | ColW8 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Rebar LoadCell @ West End (North) | LCW1 | RebarLoad | Load Cell | -230 | 230 | kN
Rebar LoadCell @ West End | LCW2 | RebarLoad | Load Cell | -230 | 230 | kN
Rebar LoadCell @ West End | LCW3 | RebarLoad | Load Cell | -230 | 230 | kN
Rebar LoadCell @ West End (South) | LCW4 | RebarLoad | Load Cell | -230 | 230 | kN
Strain @ East End (1'-9" from Slab End, Top Bolt) | SGE1 | SGEnd | Strain gauge | -30000 | 30000 | microstrain
Strain @ East End (1'-9" from Slab End, Bot Bolt) | SGE2 | SGEnd | Strain gauge | -30000 | 30000 | microstrain
Strain @ East_Col_TopBrace_Top_South | ColE1 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ East_Col_TopBrace_Top_North | ColE2 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ East_Col_TopBrace_Bot_South | ColE3 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ East_Col_TopBrace_Bot_North | ColE4 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ East_Col_BotBrace_Top_South | ColE5 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ East_Col_BotBrace_Top_North | ColE6 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @East_Col_BotBrace_Bot_South | ColE7 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Strain @ East_Col_BotBrace_Bot_North | ColE8 | SGColBrace | Strain gauge | -30000 | 30000 | microstrain
Rebar LoadCell @ East end (North) | LCE1 | RebarLoad | Load Cell | -230 | 230 | kN
Rebar LoadCell @ East end | LCE2 | RebarLoad | Load Cell | -230 | 230 | kN
Rebar LoadCell @ East end | LCE3 | RebarLoad | Load Cell | -230 | 230 | kN
Rebar LoadCell @ East end (South) | LCE4 | RebarLoad | Load Cell | -230 | 230 | kN
East End; Vertical Gardon Gage | HeatFlux_Gardon | HeatFlux | ±0.2V default | -50 | 500 | kW/m2
Beam East End (3.5" from bolt line along Top Bolt) | TCE_1 | TempEastConn | Thermocouple | 0 | 2000 | °C
Beam East End (3.5" from bolt line along Mid Bolt) | TCE_2 | TempEastConn | Thermocouple | 0 | 2000 | °C
East End; South Angle; Leg on Column; Top Bolt | TCE_4 | TempEastConn | Thermocouple | 0 | 2000 | °C
East End; South Angle; Leg on Beam; Mid Bolt (sleeve) | TCE_5 | TempEastConn | Thermocouple | 0 | 2000 | °C
East End; South Angle; Leg on Column; Mid Bolt (sleeve) | TCE_6 | TempEastConn | Thermocouple | 0 | 2000 | °C
East End; Sacrifical Pl; Top Corner | TCE_8 | TempEastConn | Thermocouple | 0 | 2000 | °C
East End; Sacrifical Pl; Bot Corner | TCE_9 | TempEastConn | Thermocouple | 0 | 2000 | °C
Section 6; Shear Stud; | TC6_21 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 8; North Slab | TC8_2 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; North Slab | TC8_3 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; North Slab | TC8_4 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; North Slab; Bot | TC8_5 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 6; Steel Deck Mid; Diagonal Rib (Middle height) | TC6_22 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 8; Mid Slab | TC8_7 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; Mid Slab | TC8_8 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; Mid Slab | TC8_9 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; Mid Slab; Bot | TC8_10 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; Beam; Top Flange | TC8_11 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; Beam; Top Web (stainless steel tube) | TC8_12 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; Beam; Mid Web (sleeve) | TC8_13 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; Beam; Bot Web | TC8_14 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; Beam; Bot Flange(sleeve) | TC8_15 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 6; Steel Deck Mid; Top Rib | TC6_23 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 8; South Slab | TC8_17 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; South Slab | TC8_18 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; South Slab | TC8_19 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 8; South Slab; Bot | TC8_20 | TempSect8 | Thermocouple | 0 | 2000 | °C
Section 5; Shear Stud; | TC5_21 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 7; North Slab | TC7_2 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; North Slab | TC7_3 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; North Slab | TC7_4 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; North Slab; Bot | TC7_5 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 5; Steel Deck Mid; Diagonal Rib (Middle height) | TC5_22 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 7; Mid Slab | TC7_7 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; Mid Slab | TC7_8 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; Mid Slab | TC7_9 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; Mid Slab; Bot | TC7_10 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; Beam; Top Flange (sleeve) | TC7_11 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; Beam; Top Web (sleeve) | TC7_12 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; Beam; Mid Web (sleeve) | TC7_13 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; Beam; Bot Flange (sleeve) | TC7_15 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 5; Steel Deck Mid; Top Rib | TC5_23 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 7; South Slab | TC7_17 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; South Slab | TC7_18 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; South Slab | TC7_19 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 7; South Slab; Bot | TC7_20 | TempSect7 | Thermocouple | 0 | 2000 | °C
Section 6; North Slab; Top | TC6_1 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; North Slab | TC6_2 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; North Slab | TC6_3 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; North Slab | TC6_4 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; North Slab; Bot | TC6_5 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; Mid Slab; Top | TC6_6 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; Mid Slab | TC6_7 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; Mid Slab | TC6_8 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; Mid Slab | TC6_9 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; Mid Slab; Bot | TC6_10 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; Beam; Top Flange | TC6_11 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; Beam; Top Web | TC6_12 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; Beam; Mid Web (sleeve) | TC6_13 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; Beam; Bot Web | TC6_14 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; Beam; Bot Flange (sleeve) | TC6_15 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; South Slab; Top | TC6_16 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; South Slab | TC6_17 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; South Slab | TC6_18 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; South Slab | TC6_19 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; South Slab; Bot | TC6_20 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 5; North Slab; Top | TC5_1 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; North Slab | TC5_2 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; North Slab | TC5_3 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; North Slab | TC5_4 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; North Slab; Bot | TC5_5 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; Mid Slab; Top | TC5_6 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; Mid Slab | TC5_7 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; Mid Slab | TC5_8 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; Mid Slab | TC5_9 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; Mid Slab; Bot | TC5_10 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; Beam; Top Flange (sleeve) | TC5_11 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; Beam; Top Web (sleeve) | TC5_12 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; Beam; Mid Web (sleeve) | TC5_13 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; Beam; Bot Web (sleeve) | TC5_14 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; South Slab; Top | TC5_16 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; South Slab | TC5_17 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; South Slab | TC5_18 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; South Slab | TC5_19 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; South Slab; Bot | TC5_20 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 6; Steel Deck South; Bot (Deck surf temp) | TC6_26 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 6; Steel Deck North; Bot (Deck surf temp) | TC6_25 | TempSect6 | Thermocouple | 0 | 2000 | °C
Section 5; Steel Deck South; Bot (Deck surf temp) | TC5_26 | TempSect5 | Thermocouple | 0 | 2000 | °C
Section 5; Steel Deck North (Deck surf temp) | TC5_25 | TempSect5 | Thermocouple | 0 | 2000 | °C
East Wall; South; Inserted Sheathed TC; 32" below the slab | TCC5 | CompTemp | Thermocouple | 0 | 2000 | °C
South Wall; East; Inserted Sheathed TC; 32" below the slab | TCC6 | CompTemp | Thermocouple | 0 | 2000 | °C
NE Slab; Upper Temp; Inserted Sheathed TC; 1" below the slab | TCC11 | CompTemp | Thermocouple | 0 | 2000 | °C
NE Slab; Lower Temp; Inserted Sheathed TC; 9" below the slab | TCC12 | CompTemp | Thermocouple | 0 | 2000 | °C
SE Slab; Upper Temp; Inserted Sheathed TC; 1" below the slab | TCC13 | CompTemp | Thermocouple | 0 | 2000 | °C
SE Slab; Lower Temp; Inserted Sheathed TC; 9" below the slab | TCC14 | CompTemp | Thermocouple | 0 | 2000 | °C
North Wall; West End Vent | TCC17 | VentTemp | Thermocouple | 0 | 2000 | °C
NorthWall; West Mid Vent | TCC18 | VentTemp | Thermocouple | 0 | 2000 | °C
North Wall; East Mid Vent | TCC19 | VentTemp | Thermocouple | 0 | 2000 | °C
North Wall; East End Vent | TCC20 | VentTemp | Thermocouple | 0 | 2000 | °C
South Wall; East End Vent | TCC21 | VentTemp | Thermocouple | 0 | 2000 | °C
South Wall; East Mid Vent | TCC22 | VentTemp | Thermocouple | 0 | 2000 | °C
South Wall; West Mid Vent | TCC23 | VentTemp | Thermocouple | 0 | 2000 | °C
South Wall; West End Vent | TCC24 | VentTemp | Thermocouple | 0 | 2000 | °C
East End; Horizontal DFT (front) | TCC25 | DFT | Thermocouple | 0 | 2000 | °C
East End; Horizontal DFT (back) | TCC26 | DFT | Thermocouple | 0 | 2000 | °C
East End; Vertical DFT (front) | TCC27 | DFT | Thermocouple | 0 | 2000 | °C
East End; Vertical DFT (back) | TCC28 | DFT | Thermocouple | 0 | 2000 | °C
Beam West End (3.5" from bolt line along Top Bolt) | TCW_1 | TempWestConn | Thermocouple | 0 | 2000 | °C
BeamWest End (3.5" from bolt line along Mid Bolt) | TCW_2 | TempWestConn | Thermocouple | 0 | 2000 | °C
Beam West End (3.5" from bolt line along Bot Bolt) | TCW_3 | TempWestConn | Thermocouple | 0 | 2000 | °C
West End; South Angle; Leg on Column; Top Bolt | TCW_4 | TempWestConn | Thermocouple | 0 | 2000 | °C
West End; South Angle; Leg on Beam; Mid Bolt (sleeve) | TCW_5 | TempWestConn | Thermocouple | 0 | 2000 | °C
West End; South Angle; Leg on Column; Mid Bolt (sleeve) | TCW_6 | TempWestConn | Thermocouple | 0 | 2000 | °C
West End; North Angle; Leg on Beam; Mid Bolt | TCW_7 | TempWestConn | Thermocouple | 0 | 2000 | °C
West End; Sacrifical Pl; Top Corner | TCW_8 | TempWestConn | Thermocouple | 0 | 2000 | °C
West End; Sacrifical Pl; Bot Corner | TCW_9 | TempWestConn | Thermocouple | 0 | 2000 | °C
Section 3; Shear Stud; | TC3_21 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 1; North Slab | TC1_2 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; North Slab | TC1_4 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; North Slab; Bot | TC1_5 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 3; Steel Deck Mid; Diagonal Rib (Middle height) | TC3_22 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 1; Mid Slab | TC1_7 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; Mid Slab | TC1_8 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; Mid Slab | TC1_9 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; Mid Slab; Bot | TC1_10 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; Beam; Top Flange | TC1_11 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; Beam; Top Web (stainless steel tube) | TC1_12 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; Beam; Mid Web (sleeve) | TC1_13 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; Beam; Bot Web | TC1_14 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; Beam; Bot Flange (sleeve) | TC1_15 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 3; Steel Deck Mid; Top Rib | TC3_23 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 1; South Slab | TC1_17 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; South Slab | TC1_18 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; South Slab | TC1_19 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 1; South Slab; Bot | TC1_20 | TempSect1 | Thermocouple | 0 | 2000 | °C
Section 4; Shear Stud; | TC4_21 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 2; North Slab | TC2_2 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 2; North Slab | TC2_4 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 2; North Slab; Bot | TC2_5 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 4; Steel Deck Mid; Diagonal Rib (Middle height) | TC4_22 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 2; Mid Slab | TC2_7 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 2; Mid Slab | TC2_8 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 2; Mid Slab | TC2_9 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 2; Mid Slab; Bot | TC2_10 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 2; Beam; Top Web (sleeve) | TC2_12 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 2; Beam; Mid Web (sleeve) | TC2_13 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 2; Beam; Bot Web (sleeve) | TC2_14 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 2; Beam; Bot Flange (sleeve) | TC2_15 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 4; Steel Deck Mid; Top Rib | TC4_23 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 2; South Slab | TC2_17 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 2; South Slab | TC2_18 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 2; South Slab | TC2_19 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 2; South Slab; Bot | TC2_20 | TempSect2 | Thermocouple | 0 | 2000 | °C
Section 3; North Slab; Top | TC3_1 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; North Slab | TC3_2 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; North Slab | TC3_3 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; North Slab | TC3_4 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; North Slab; Bot | TC3_5 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; Mid Slab; Top | TC3_6 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; Mid Slab | TC3_7 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; Mid Slab | TC3_8 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; Mid Slab | TC3_9 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; Mid Slab; Bot | TC3_10 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; Beam; Top Flange | TC3_11 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; Beam; Top Web | TC3_12 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; Beam; Mid Web (sleeve) | TC3_13 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; Beam; Bot Web | TC3_14 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; Beam; Bot Flange (sleeve) | TC3_15 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; South Slab; Top | TC3_16 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; South Slab | TC3_17 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; South Slab | TC3_18 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; South Slab | TC3_19 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; South Slab; Bot | TC3_20 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 4; North Slab; Top | TC4_1 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; North Slab | TC4_2 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; North Slab | TC4_3 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; North Slab | TC4_4 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; North Slab; Bot | TC4_5 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; Mid Slab; Top | TC4_6 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; Mid Slab | TC4_7 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; Mid Slab | TC4_8 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; Mid Slab | TC4_9 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; Mid Slab; Bot | TC4_10 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; Beam; Top Flange (sleeve) | TC4_11 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; Beam; Top Web (sleeve) | TC4_12 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; Beam; Bot Web (sleeve) | TC4_14 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; Beam; Bot Flange (sleeve) | TC4_15 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; South Slab; Top | TC4_16 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; South Slab | TC4_17 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; South Slab | TC4_18 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; South Slab | TC4_19 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; South Slab; Bot | TC4_20 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 3; Steel Deck South; Bot (Deck surf temp) | TC3_26 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 3; Steel Deck North; Bot (Deck surf temp) | TC3_25 | TempSect3 | Thermocouple | 0 | 2000 | °C
Section 4; Steel Deck South; Bot (Deck surf temp) | TC4_26 | TempSect4 | Thermocouple | 0 | 2000 | °C
Section 4; Steel Deck North; Bot (Deck surf temp) | TC4_25 | TempSect4 | Thermocouple | 0 | 2000 | °C
West Wall; North; Inserted Sheathed TC; 32" below the slab | TCC1 | CompTemp | Thermocouple | 0 | 2000 | °C
South Wall; Center; Inserted Sheathed TC; 32" below the slab | TCC7 | CompTemp | Thermocouple | 0 | 2000 | °C
South Wall; West; Inserted Sheathed TC; 32" below the slab | TCC8 | CompTemp | Thermocouple | 0 | 2000 | °C
NW Slab; Upper Temp; Inserted Sheathed TC; 1" below the slab | TCC9 | CompTemp | Thermocouple | 0 | 2000 | °C
NW Slab; Lower Temp; Inserted Sheathed TC; 9" below the slab | TCC10 | CompTemp | Thermocouple | 0 | 2000 | °C
SW Slab; Upper Temp; Inserted Sheathed TC; 1" below the slab | TCC15 | CompTemp | Thermocouple | 0 | 2000 | °C
SW Slab; Lower Temp; Inserted Sheathed TC; 9" below the slab | TCC16 | CompTemp | Thermocouple | 0 | 2000 | °C
North Wall; Center; Inserted Sheathed TC; 32" below the slab | TCC3 | CompTemp | Thermocouple | 0 | 2000 | °C
North Wall; East; Inserted Sheathed TC; 32" below the slab | TCC4 | CompTemp | Thermocouple | 0 | 2000 | °C
North Wall; West; Inserted Sheathed TC; 32" below the slab | TCC2 | CompTemp | Thermocouple | 0 | 2000 | °C
FBGTopTemp | FBGTopTemp | FO | Thermocouple | 0 | 2000 | °C
FBGBotTemp | FBGBotTemp | FO | Thermocouple | 0 | 2000 | °C
Sheathed TC1(Bottom Flange, 7.25 in. East of Section 2) | STC1 | TempBottomFlange | Thermocouple | 0 | 2000 | °C
Sheathed TC2(Bottom Flange, 19.25 in. West of Section 4) | STC2 | TempBottomFlange | Thermocouple | 0 | 2000 | °C
Sheathed TC3(Bottom Flange, 19.25 in. East of Section 5) | STC3 | TempBottomFlange | Thermocouple | 0 | 2000 | °C
Sheathed TC4(Bottom Flange, 7.25 in. West of Section 7) | STC4 | TempBottomFlange | Thermocouple | 0 | 2000 | °C
Vertical Displacement_Mid Span_Top Slab | VD2 | Disp | String potentiometer | -127 | 127 | mm
Vertical Displacement_West_Top Slab | VD3 | Disp | String potentiometer | -762 | 762 | mm
Vertical Displacement_Mid West_Top Slab | VD4 | Disp | String potentiometer | -762 | 762 | mm
Vertical Displacement_Mid East_Top Slab | VD5 | Disp | String potentiometer | -762 | 762 | mm
Rotation_Slab_West End_NS | RotSlabWx | Beam_Rot | Inclinometer | -5 | 5 | rad
Rotation_Slab_West End_EW | RotSlabWy | Beam_Rot | Inclinometer | -5 | 5 | rad
Rotation_Slab_East End_NS | RotSlabEx | Beam_Rot | Inclinometer | -5 | 5 | rad
Rotation_Slab_East End_EW | RotSlabEy | Beam_Rot | Inclinometer | -5 | 5 | rad
Rotation_Slab_Midpan_NS | RotSlabMx | Beam_Rot | Inclinometer | -5 | 5 | rad
Rotation_Slab_Midspan_EW | RotSlabMy | Beam_Rot | Inclinometer | -5 | 5 | rad
Rotation_Loading Truss_East | RotLT1 | Truss_Rot | Inclinometer | -5 | 5 | rad
Rotation_Loading Truss_Mid | RotLT2 | Truss_Rot | Inclinometer | -5 | 5 | rad
Rotation_Loading Truss_West | RotLT3 | Truss_Rot | Inclinometer | -5 | 5 | rad
Actuator NE Displacement | DispNE | MTS Disp | MTS built-in string potentiometer | -770 | 770 | mm
Actuator NE Force | LoadNE | MTS Load | MTS built-in string load cell | -230 | 230 | kN
Actuator SE Displacement | DispSE | MTS Disp | MTS built-in string potentiometer | -770 | 770 | mm
Actuator SE Force | LoadSE | MTS Load | MTS built-in string load cell | -230 | 230 | kN
Actuator NW Displacement | DispNW | MTS Disp | MTS built-in string potentiometer | -770 | 770 | mm
Actuator NW Force | LoadNW | MTS Load | MTS built-in string load cell | -230 | 230 | kN
Actuator SW Displacement | DispSW | MTS Disp | MTS built-in string potentiometer | -770 | 770 | mm
Actuator SW Force | LoadSW | MTS Load | MTS built-in string load cell | -230 | 230 | kN
Actuator NM Displacement | DispNM | MTS Disp | MTS built-in string potentiometer | -770 | 770 | mm
Actuator NM Force | LoadNM | MTS Load | MTS built-in string load cell | -230 | 230 | kN
Actuator SM Displacement | DispSM | MTS Disp | MTS built-in string potentiometer | -770 | 770 | mm
Actuator SM Force | LoadSM | MTS Load | MTS built-in string load cell | -230 | 230 | kN
HRR | HRR | HRR | NFRL inhouse calculation | 0 | 10000 | kW
HRR Burner | HRRburner | HRR | NFRL inhouse calculation | 0 | 10000 | kW
AvgULT |  | VideoDataOverlay | AvgULT=average(TCC1, TCC2, TCC3, TCC4, TCC5, TCC6, TCC7, TCC8) |  |  | °C
AvgVDMidspan |  | VideoDataOverlay | AvgVDMidspan=average(VD3, VD4) |  |  | mm
AvgAxialLoad |  | VideoDataOverlay | AvgAxialLoad=average(ColE2:ColE4, ColE5, ColE7, ColE8, ColW2:ColW4, ColW5, ColW8)*3.9 |  |  | kW
AvgBeamTemp |  | VideoDataOverlay | AvgBeamTemp=average(STC2, STC3) |  |  | °C
Note on A276: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Negative sign = compression load to the specimen
Note on A277: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Average bottom flange temperature

## User Events
Event Count | Time (s) | Time Stamp | Event Description
1 |  | 2018-01-12 11:20 | Mechanical loading initiated
2 |  | 2018-01-12 11:26 | Mechanical loading Reached Target Load
3 | 0 | 2018-01-12 13:26 | Natural gas flow initiated (HRRburner)
4 | 12 | 2018-01-12 13:26 | Fire ignition
7 | 3757 | 2018-01-12 14:28 | Unloading of actuator force started
5 | 3807 | 2018-01-12 14:29 | 30 min controlled cooling started
7 | 4284 | 2018-01-12 14:37 | Unloading of actuator force ended
6 | 5668 | 2018-01-12 15:00 | 30 min controlled cooling Ended (fire out)

## CB-DA-SC-AmbientLoadingData
Time (Date:1/12/2018 ) | Test Time (s) | SG1 (microstrain) | SG2 (microstrain) | SG3 (microstrain) | SG4 (microstrain) | SG5 (microstrain) | SGW2 (microstrain) | ColW1 (microstrain) | ColW2 (microstrain) | ColW3 (microstrain) | ColW4 (microstrain) | ColW5 (microstrain) | ColW6 (microstrain) | ColW7 (microstrain) | ColW8 (microstrain) | LCW1 (kN) | LCW2 (kN) | LCW3 (kN) | LCW4 (kN) | SGE1 (microstrain) | SGE2 (microstrain) | ColE1 (microstrain) | ColE2 (microstrain) | ColE3 (microstrain) | ColE4 (microstrain) | ColE5 (microstrain) | ColE6 (microstrain) | ColE7 (microstrain) | ColE8 (microstrain) | LCE1 (kN) | LCE2 (kN) | LCE3 (kN) | LCE4 (kN) | VD2 (mm) | VD3 (mm) | VD4 (mm) | VD5 (mm) | RotSlabWx (rad) | RotSlabWy (rad) | RotSlabEx (rad) | RotSlabEy (rad) | RotSlabMx (rad) | RotSlabMy (rad) | RotLT1 (rad) | RotLT2 (rad) | RotLT3 (rad) | DispNE (mm) | LoadNE (kN) | DispSE (mm) | LoadSE (kN) | DispNW (mm) | LoadNW (kN) | DispSW (mm) | LoadSW (kN) | DispNM (mm) | LoadNM (kN) | DispSM (mm) | LoadSM (kN)
11:20 | 0 | 28.887 | 15.5159 | 36.2869 | 43.638 | -1.2236 | -5.1289 | -0.4587 | -1.0057 | 0.6517 | 0.2955 | 0.3436 | -0.6906 | 7.1768 | 0.3291 | 0.3794 | 0.3749 | 0.371 | 0.2449 | -13.8518 |  | -0.2286 | -0.6918 | -1.5728 | -0.791 | 0.3616 |  | -0.0129 | 0.2761 | 1.914 | 1.6699 | 2.2554 | 0.8574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -370.9166 | 1.5867 | -370.8212 | 1.4614 | -370.8705 | 2.8597 | -370.9135 | 1.985 | -370.6735 | 2.7139 | -370.6612 | 1.794
11:20 | 1 | 28.9734 | 15.6571 | 36.3902 | 43.7563 | -1.215 | -5.1816 | -0.3702 | -0.9864 | 0.563 | 0.2191 | 0.3132 | -0.5779 | 7.1266 | 0.2751 | 0.379 | 0.3756 | 0.3716 | 0.2462 | -13.8062 |  | -0.2052 | -0.605 | -1.584 | -0.7675 | 0.3649 |  | 0.1255 | 0.2471 | 1.9134 | 1.6659 | 2.2533 | 0.8569 | -0.0039 | -0.0039 | 0.0359 | 0.0021 | -0.0003 | 0 | 0.0002 | 0.0001 | -0.0002 | -0.0004 | 0.0092 | -0.0054 | -0.0046 | -370.8828 | 1.5764 | -370.8028 | 1.4902 | -370.8674 | 2.8679 | -370.9535 | 1.985 | -370.6612 | 2.6852 | -370.6581 | 1.7982
11:20 | 2 | 28.9814 | 15.6108 | 36.4187 | 43.7081 | -1.3304 | -5.2796 | -0.437 | -0.989 | 0.6132 | 0.3412 | 0.3083 | -0.5803 | 7.1913 | 0.2405 | 0.3788 | 0.3759 | 0.3724 | 0.2449 | -13.8333 |  | -0.229 | -0.6864 | -1.6155 | -0.9015 | 0.2321 |  | 0.0736 | 0.2112 | 1.9151 | 1.6691 | 2.251 | 0.8562 | -0.0154 | -0.0269 | -0.0266 | -0.0212 | -0.0004 | 0.0008 | 0.0003 | 0.0002 | 0 | 0.0004 | 0.0028 | -0.0064 | -0.0109 | -370.9135 | 1.6195 | -370.7997 | 1.5004 | -370.9043 | 2.8515 | -370.9105 | 1.9727 | -370.6366 | 2.7098 | -370.6704 | 1.794
11:20 | 3 | 28.8819 | 15.6108 | 36.4033 | 43.6934 | -1.3776 | -5.3675 | -0.4946 | -0.9691 | 0.5678 | 0.3136 | 0.3537 | -0.6008 | 7.1893 | 0.3099 | 0.3782 | 0.3727 | 0.3714 | 0.2458 | -13.7735 |  | -0.2495 | -0.614 | -1.5087 | -0.8213 | 0.2661 |  | 0.0233 | 0.2034 | 1.9167 | 1.6733 | 2.2532 | 0.8562 | -0.0126 | -0.0472 | 0.0105 | -0.0182 | -0.0002 | 0.0006 | 0.0005 | 0.0002 | 0.0001 | -0.0005 | -0.0012 | -0.0091 | -0.0184 | -370.9351 | 1.6339 | -370.8058 | 1.4881 | -370.812 | 2.8412 | -370.9105 | 2.0035 | -370.6951 | 2.7283 | -370.6704 | 1.7776
11:20 | 4 | 29.0381 | 15.5971 | 36.4056 | 43.8142 | -1.271 | -5.3238 | -0.3747 | -0.9571 | 0.5844 | 0.3623 | 0.3769 | -0.7405 | 7.1231 | 0.262 | 0.3785 | 0.3738 | 0.3717 | 0.2468 | -13.8662 |  | -0.2567 | -0.6991 | -1.6263 | -0.873 | 0.2235 |  | -0.0246 | 0.2537 | 1.9167 | 1.6661 | 2.2505 | 0.8543 | -0.0145 | -0.0376 | 0.0024 | -0.0374 | -0.0001 | 0.0003 | 0.0005 | 0 | -0.0003 | -0.0003 | -0.0103 | 0.0031 | -0.0274 | -370.9597 | 1.6524 | -370.7843 | 1.4881 | -370.8212 | 2.8412 | -370.932 | 2.0158 | -370.7197 | 2.7303 | -370.6581 | 1.7653
11:20 | 5 | 28.9805 | 15.6912 | 36.4724 | 43.8581 | -1.2665 | -5.2979 | -0.4051 | -0.9085 | 0.5731 | 0.3755 | 0.4397 | -0.7351 | 7.1371 | 0.2801 | 0.3791 | 0.3743 | 0.3687 | 0.2461 | -13.833 |  | -0.2703 | -0.6601 | -1.662 | -0.9294 | 0.2109 |  | 0.0356 | 0.3535 | 1.9162 | 1.6706 | 2.2539 | 0.8546 | 0.0263 | -0.0374 | 0.0625 | -0.0379 | 0.0002 | 0.0001 | 0.0002 | 0.0003 | 0.0007 | -0.0003 | -0.0002 | -0.0158 | 0.0108 | -370.9105 | 1.6606 | -370.8089 | 1.521 | -370.8458 | 2.8391 | -370.9074 | 1.9829 | -370.655 | 2.7221 | -370.6766 | 1.7838
11:20 | 6 | 28.9281 | 15.7579 | 36.4723 | 43.8914 | -1.329 | -5.4075 | -0.2883 | -0.9255 | 0.5921 | 0.3986 | 0.4003 | -0.6546 | 7.2381 | 0.2881 | 0.3799 | 0.3742 | 0.3722 | 0.2455 | -13.7223 |  | -0.2117 | -0.729 | -1.6791 | -0.922 | 0.2547 |  | 0.0018 | 0.3581 | 1.9172 | 1.665 | 2.2479 | 0.8533 | -0.0155 | -0.0617 | -0.0104 | -0.0498 | -0.0003 | 0.0006 | 0.0002 | 0.0004 | -0.0004 | -0.0003 | -0.0011 | -0.0053 | -0.0263 | -370.9105 | 1.7017 | -370.8489 | 1.5497 | -370.9135 | 2.8412 | -370.852 | 1.9645 | -370.6612 | 2.7385 | -370.7166 | 1.8105
11:20 | 7 | 28.956 | 15.7703 | 36.455 | 43.8684 | -1.31 | -5.4703 | -0.5309 | -0.9633 | 0.6301 | 0.4693 | 0.3996 | -0.5594 | 7.2384 | 0.2973 | 0.3789 | 0.3741 | 0.3701 | 0.2456 | -13.7977 |  | -0.1722 | -0.7428 | -1.6456 | -0.9108 | 0.2401 |  | 0.0648 | 0.3585 | 1.9184 | 1.6667 | 2.248 | 0.8514 | -0.0121 | -0.018 | 0.0544 | 0.0041 | -0.0001 | 0.0009 | 0.0001 | 0.0001 | 0.0004 | -0.0006 | -0.0017 | -0.0153 | -0.0009 | -370.9105 | 1.6975 | -370.8151 | 1.5374 | -370.8489 | 2.8186 | -370.8951 | 1.9788 | -370.6612 | 2.7303 | -370.7166 | 1.7899
11:20 | 8 | 28.9815 | 15.7369 | 36.5849 | 43.9734 | -1.3516 | -5.4638 | -0.4508 | -0.9433 | 0.5875 | 0.4691 | 0.3914 | -0.6281 | 7.2696 | 0.3982 | 0.38 | 0.3759 | 0.3717 | 0.2448 | -13.8351 |  | -0.2148 | -0.6739 | -1.6716 | -0.8416 | 0.2493 |  | 0.0638 | 0.3551 | 1.9198 | 1.6705 | 2.2513 | 0.8521 | 0.0051 | 0.0108 | 0.0359 | 0.0217 | 0.0002 | 0.0008 | 0 | -0.0001 | -0.0002 | -0.0005 | 0.0218 | -0.0009 | 0.0065 | -370.9566 | 1.7099 | -370.7227 | 1.5394 | -370.8612 | 2.8617 | -370.9597 | 1.9953 | -370.6612 | 2.716 | -370.6366 | 1.7756
11:20 | 9 | 28.9213 | 15.8116 | 36.6802 | 44.0183 | -1.3855 | -5.5193 | -0.4921 | -0.9485 | 0.584 | 0.4322 | 0.419 | -0.6175 | 7.2785 | 0.3182 | 0.3803 | 0.3735 | 0.3748 | 0.2449 | -13.8901 |  | -0.0874 | -0.7902 | -1.7339 | -0.912 | 0.1791 |  | 0.071 | 0.3427 | 1.92 | 1.6713 | 2.251 | 0.8489 | 0.0097 | -0.0018 | 0.022 | 0.021 | 0.0001 | 0.0004 | 0.0002 | 0.0001 | -0.0002 | -0.0003 | 0.0043 | -0.0106 | -0.0093 | -370.8828 | 1.6934 | -370.7289 | 1.5661 | -370.8674 | 2.8658 | -370.9505 | 1.9932 | -370.6274 | 2.6872 | -370.6489 | 1.7797
11:20 | 10 | 28.8866 | 15.8172 | 36.7322 | 44.1074 | -1.3316 | -5.57 | -0.3894 | -0.8966 | 0.5992 | 0.5085 | 0.3682 | -0.5337 | 7.2963 | 0.4397 | 0.3787 | 0.3737 | 0.3748 | 0.2449 | -14.0117 |  | -0.1342 | -0.8182 | -1.6588 | -0.984 | 0.2703 |  | 0.0575 | 0.3529 | 1.9209 | 1.6744 | 2.2562 | 0.8499 | -0.0257 | -0.02 | 0.0173 | -0.0266 | -0.0002 | 0.0003 | 0.0006 | 0.0006 | 0.0004 | -0.0002 | -0.0024 | -0.0088 | -0.0077 | -370.9135 | 1.7386 | -370.772 | 1.5764 | -370.8489 | 2.8535 | -370.892 | 1.9891 | -370.655 | 2.716 | -370.6581 | 1.7879
11:20 | 11 | 28.868 | 15.7938 | 36.7342 | 44.0489 | -1.4473 | -5.7171 | -0.5569 | -0.9362 | 0.6707 | 0.3963 | 0.4222 | -0.6535 | 7.2285 | 0.3589 | 0.3777 | 0.376 | 0.3762 | 0.2456 | -13.948 |  | -0.2677 | -0.8124 | -1.6279 | -0.8591 | 0.3627 |  | -0.0616 | 0.3361 | 1.9218 | 1.6718 | 2.2544 | 0.8491 | -0.0244 | -0.0358 | 0.014 | -0.035 | -0.0005 | 0.0007 | -0.0001 | -0.0002 | -0.0004 | -0.0003 | 0.0171 | -0.0072 | 0.0046 | -370.9535 | 1.7817 | -370.7751 | 1.5723 | -370.8274 | 2.8412 | -370.9166 | 2.0035 | -370.6581 | 2.755 | -370.7135 | 1.7715
11:20 | 12 | 28.7759 | 15.8054 | 36.7365 | 44.0389 | -1.4983 | -5.6907 | -0.6425 | -0.9213 | 0.5673 | 0.4158 | 0.2327 | -0.6479 | 7.2095 | 0.3518 | 0.3788 | 0.3757 | 0.3719 | 0.2463 | -13.8979 |  | -0.1872 | -0.7003 | -1.6714 | -0.8573 | 0.2916 |  | -0.0273 | 0.361 | 1.9225 | 1.6669 | 2.2523 | 0.8488 | -0.0416 | -0.0473 | -0.0312 | -0.0699 | -0.0001 | 0.0006 | 0.0006 | 0.0003 | 0.0002 | -0.0004 | -0.0081 | -0.0066 | -0.01 | -370.9351 | 1.7591 | -370.7104 | 1.5764 | -370.8274 | 2.8617 | -370.9074 | 1.9953 | -370.6858 | 2.7324 | -370.652 | 1.7612
11:20 | 13 | 28.9275 | 15.8888 | 36.8617 | 44.1557 | -1.4701 | -5.7522 | -0.5291 | -0.9441 | 0.5707 | 0.3916 | 0.2115 | -0.6923 | 7.2149 | 0.3531 | 0.3791 | 0.3748 | 0.3736 | 0.2464 | -13.9373 |  | -0.2556 | -0.7428 | -1.7637 | -0.9359 | 0.3026 |  | -0.0416 | 0.3073 | 1.9228 | 1.6692 | 2.2555 | 0.848 | -0.0106 | -0.0105 | 0.0128 | -0.0048 | 0.0001 | 0.0004 | -0.0001 | 0.0001 | -0.0002 | -0.0002 | 0.0146 | -0.0067 | -0.009 | -370.9043 | 1.7674 | -370.7658 | 1.6277 | -370.8705 | 2.8761 | -370.8797 | 1.9829 | -370.6243 | 2.7139 | -370.7104 | 1.8064
11:20 | 14 | 28.8368 | 15.8973 | 36.878 | 44.3104 | -1.3273 | -5.6994 | -0.4882 | -0.9437 | 0.6222 | 0.3662 | 0.2667 | -0.7207 | 7.1525 | 0.3375 | 0.3779 | 0.3767 | 0.3711 | 0.2456 | -13.9468 |  | -0.2006 | -0.6879 | -1.7467 | -0.9344 | 0.272 |  | -0.0351 | 0.3836 | 1.9233 | 1.6667 | 2.253 | 0.8443 | -0.0147 | -0.0203 | 0.007 | -0.0313 | 0.0001 | 0.0004 | -0.0003 | 0 | 0.0001 | -0.0009 | 0.0057 | -0.0064 | -0.0013 | -370.9197 | 1.7715 | -370.7289 | 1.6462 | -370.8735 | 2.8843 | -370.8612 | 1.9686 | -370.6489 | 2.7118 | -370.6797 | 1.8105
11:20 | 15 | 28.873 | 15.9543 | 37.0032 | 44.2555 | -1.2432 | -5.6951 | -0.3299 | -0.8745 | 0.6324 | 0.2851 | 0.2425 | -0.818 | 7.1218 | 0.2623 | 0.3799 | 0.3759 | 0.3747 | 0.2467 | -14.0004 |  | -0.2833 | -0.6778 | -1.7718 | -1.0433 | 0.267 |  | 0.0564 | 0.3502 | 1.9232 | 1.6681 | 2.2548 | 0.8452 | -0.0045 | 0.0012 | 0.0266 | -0.0112 | -0.0002 | 0.0005 | 0.0005 | 0.0004 | 0.0005 | 0 | -0.0057 | -0.0058 | -0.0138 | -370.9105 | 1.8002 | -370.7166 | 1.638 | -370.8089 | 2.8679 | -370.9043 | 1.9891 | -370.6181 | 2.716 | -370.6735 | 1.7817
11:20 | 16 | 28.8838 | 15.9453 | 37.0018 | 44.3319 | -1.2466 | -5.7004 | -0.382 | -0.9024 | 0.5845 | 0.4724 | 0.2684 | -0.7425 | 7.1594 | 0.2783 | 0.3794 | 0.3769 | 0.3716 | 0.2446 | -14.083 |  | -0.2112 | -0.6978 | -1.7437 | -0.9721 | 0.1751 |  | 0.0292 | 0.312 | 1.9255 | 1.6712 | 2.2597 | 0.8447 | 0.0117 | 0.0233 | 0.0012 | -0.0176 | -0.0004 | 0.0011 | -0.0003 | -0.0002 | -0.0001 | -0.0004 | 0.0054 | -0.0041 | -0.0134 | -370.9597 | 1.831 | -370.7135 | 1.6565 | -370.8397 | 2.8823 | -370.9197 | 1.9932 | -370.6612 | 2.7324 | -370.6212 | 1.7632
11:20 | 17 | 28.9429 | 15.9896 | 37.0341 | 44.3978 | -1.2611 | -5.7218 | -0.4146 | -1.0071 | 0.5543 | 0.3295 | 0.2611 | -0.6397 | 7.1714 | 0.381 | 0.3778 | 0.3723 | 0.3733 | 0.2457 | -14.3062 |  | -0.2895 | -0.7347 | -1.6922 | -0.9369 | 0.2119 |  | -0.0362 | 0.3978 | 1.926 | 1.6711 | 2.255 | 0.8427 | 0.0088 | 0.003 | 0.044 | 0.0374 | 0.0002 | 0.0003 | 0.0001 | 0.0001 | 0.0001 | -0.0001 | 0.0075 | 0.006 | -0.012 | -370.9289 | 1.8228 | -370.6981 | 1.6811 | -370.8335 | 2.8699 | -370.9135 | 1.9665 | -370.6089 | 2.7118 | -370.6243 | 1.7797
11:20 | 18 | 28.9855 | 16.0869 | 37.0753 | 44.4547 | -1.1924 | -5.8071 | -0.4337 | -0.9561 | 0.6209 | 0.4271 | 0.3625 | -0.7273 | 7.151 | 0.3038 | 0.3785 | 0.3769 | 0.3753 | 0.2462 | -14.2034 |  | -0.2423 | -0.7163 | -1.6762 | -0.9312 | 0.2265 |  | -0.0143 | 0.3694 | 1.9286 | 1.6722 | 2.2564 | 0.8412 | -0.0154 | -0.0269 | 0.0197 | -0.0328 | 0.0001 | 0.0001 | 0.0009 | 0.0002 | -0.0003 | -0.0003 | -0.0018 | 0.0112 | -0.0007 | -370.9351 | 1.8536 | -370.6858 | 1.6914 | -370.8335 | 2.8741 | -370.8951 | 1.9645 | -370.6089 | 2.7077 | -370.6735 | 1.794
11:20 | 19 | 28.9416 | 15.9768 | 37.1145 | 44.3628 | -1.2592 | -5.7332 | -0.3754 | -0.9455 | 0.5645 | 0.3676 | 0.2335 | -0.7753 | 7.1308 | 0.2786 | 0.3778 | 0.3739 | 0.3746 | 0.2482 | -14.2568 |  | -0.197 | -0.8436 | -1.7025 | -1.0173 | 0.2352 |  | 0.041 | 0.5249 | 1.9283 | 1.6721 | 2.2547 | 0.8427 | -0.0205 | -0.0376 | -0.0045 | -0.0255 | -0.0002 | 0.0005 | 0.0004 | 0 | 0.0003 | -0.0004 | 0.0149 | -0.011 | 0.0019 | -370.9412 | 1.8762 | -370.6981 | 1.6996 | -370.8151 | 2.872 | -370.8951 | 1.9542 | -370.6027 | 2.7283 | -370.6366 | 1.7735
11:20 | 20 | 28.9503 | 16.0079 | 37.0567 | 44.3997 | -1.1892 | -5.7494 | -0.3162 | -0.9572 | 0.5239 | 0.2476 | 0.2537 | -0.8401 | 7.1443 | 0.3432 | 0.3777 | 0.3755 | 0.3712 | 0.2466 | -14.2798 |  | -0.2268 | -0.5929 | -1.7575 | -0.9786 | 0.2619 |  | -0.0166 | 0.3663 | 1.9298 | 1.6687 | 2.256 | 0.8413 | -0.0164 | -0.0452 | -0.0104 | -0.051 | -0.0004 | 0.0007 | 0.0007 | 0.0008 | 0 | 0.0001 | 0.0072 | -0.0129 | -0.0104 | -370.9535 | 1.8741 | -370.6581 | 1.7242 | -370.8551 | 2.8597 | -370.8889 | 1.9727 | -370.6304 | 2.7139 | -370.6397 | 1.7858
11:20 | 21 | 28.9155 | 16.0692 | 37.0672 | 44.4328 | -1.2158 | -5.9328 | -0.351 | -0.9848 | 0.5201 | 0.3943 | 0.31 | -0.8823 | 7.0838 | 0.273 | 0.3777 | 0.374 | 0.372 | 0.2452 | -14.3383 |  | -0.2107 | -0.6334 | -1.7436 | -1.0412 | 0.2658 |  | -0.0643 | 0.3708 | 1.9305 | 1.6719 | 2.2573 | 0.8387 | -0.0162 | -0.0162 | 0.0023 | -0.0224 | -0.0002 | 0.0004 | 0.0001 | 0 | -0.0003 | -0.0012 | 0.0058 | -0.0034 | -0.0124 | -370.9135 | 1.9029 | -370.7012 | 1.7509 | -370.8489 | 2.8823 | -370.9474 | 1.9624 | -370.615 | 2.7221 | -370.652 | 1.7797
11:20 | 22 | 28.9227 | 16.3114 | 37.5713 | 44.8896 | -1.242 | -6.4133 | -0.4189 | -0.9417 | 0.4516 | 0.3184 | 0.2477 | -0.7726 | 7.0869 | 0.2582 | 0.379 | 0.3742 | 0.374 | 0.2453 | -14.5485 |  | -0.2103 | -0.6445 | -1.7489 | -0.9021 | 0.2751 |  | -0.0174 | 0.3909 | 1.9419 | 1.6747 | 2.2646 | 0.826 | -0.0429 | -0.0368 | 0.0001 | -0.0183 | -0.0002 | -0.0002 | -0.0003 | 0 | -0.0001 | -0.0001 | 0.0117 | -0.002 | -0.0092 | -370.8181 | 2.1246 | -370.6581 | 1.9316 | -370.852 | 2.8658 | -370.8828 | 1.9316 | -370.5874 | 2.6913 | -370.6089 | 1.7489
11:20 | 23 | 29.05 | 16.6045 | 38.3597 | 45.7453 | -1.2844 | -6.9938 | -0.466 | -0.9958 | 0.4435 | 0.2371 | 0.1697 | -0.8468 | 7.0337 | 0.27 | 0.3791 | 0.3762 | 0.3772 | 0.2471 | -14.9868 |  | -0.1542 | -0.6637 | -1.9185 | -1.0535 | 0.24 |  | -0.0955 | 0.373 | 1.957 | 1.67 | 2.2743 | 0.8088 | -0.0126 | -0.0356 | 0.1031 | -0.0413 | 0.0002 | 0.0005 | 0.0002 | 0.0005 | 0.0002 | -0.0006 | 0.0153 | -0.0125 | 0.0109 | -370.6889 | 2.41 | -370.6704 | 2.1431 | -370.8458 | 2.8597 | -370.9135 | 1.9521 | -370.6181 | 2.6954 | -370.6058 | 1.7304
11:20 | 24 | 29.0544 | 16.9658 | 39.1522 | 46.4502 | -1.285 | -7.6632 | -0.5162 | -1.067 | 0.3015 | 0.2642 | 0.0675 | -0.8521 | 6.94 | 0.122 | 0.3782 | 0.3738 | 0.3735 | 0.2467 | -15.2348 |  | -0.276 | -0.6471 | -2.0466 | -1.2732 | 0.1979 |  | -0.124 | 0.2864 | 1.9709 | 1.6722 | 2.2826 | 0.7889 | 0.0127 | -0.0162 | 0.1933 | 0.0065 | -0.0003 | 0.001 | -0.0002 | -0.0005 | 0 | -0.0004 | -0.0003 | -0.0102 | -0.0134 | -370.575 | 2.6461 | -370.6335 | 2.3546 | -370.8028 | 2.8433 | -370.9074 | 1.9583 | -370.6027 | 2.6995 | -370.572 | 1.6975
11:20 | 25 | 29.01 | 17.2801 | 39.7205 | 47.0849 | -1.2887 | -8.1596 | -0.5668 | -1.0435 | 0.2205 | 0.1416 | -0.0129 | -0.9044 | 6.8628 | 0.0749 | 0.378 | 0.3704 | 0.3737 | 0.2467 | -15.5784 |  | -0.2421 | -0.7821 | -2.1145 | -1.2323 | 0.1676 |  | -0.1203 | 0.3508 | 1.9875 | 1.6727 | 2.2978 | 0.7706 | 0.0645 | 0.0356 | 0.2258 | 0.0359 | -0.0006 | 0.0004 | 0.0002 | 0.0001 | 0.0002 | -0.0001 | 0.0086 | -0.0074 | -0.0041 | -370.3966 | 2.8864 | -370.6458 | 2.5845 | -370.7935 | 2.8638 | -370.9012 | 1.9357 | -370.535 | 2.7016 | -370.535 | 1.6934
11:20 | 26 | 28.9929 | 17.583 | 40.4639 | 47.8412 | -1.2351 | -8.9032 | -0.4601 | -1.0698 | 0.1277 | -0.0102 | -0.0341 | -0.8824 | 6.8049 | -0.0055 | 0.3781 | 0.3713 | 0.3759 | 0.2474 | -15.8968 |  | -0.3169 | -0.7201 | -2.1858 | -1.2967 | 0.1075 |  | -0.2675 | 0.2116 | 1.9995 | 1.6751 | 2.3057 | 0.7542 | 0.0929 | 0.0754 | 0.2338 | 0.063 | 0.0003 | 0.0004 | 0.0008 | 0.0003 | 0 | -0.0004 | 0.0019 | -0.0005 | 0.0058 | -370.2858 | 3.0937 | -370.7043 | 2.8391 | -370.8674 | 2.8474 | -370.8304 | 1.9296 | -370.5473 | 2.718 | -370.5504 | 1.7509
11:20 | 27 | 28.9789 | 17.9515 | 41.1221 | 48.435 | -1.287 | -9.3458 | -0.6281 | -1.1169 | 0.0758 | -0.0656 | -0.1066 | -0.9848 | 6.7906 | -0.0329 | 0.3776 | 0.3682 | 0.3762 | 0.2462 | -16.1315 |  | -0.2884 | -0.7992 | -2.2208 | -1.4182 | 0.159 |  | -0.2274 | 0.1497 | 2.0112 | 1.6754 | 2.3171 | 0.7377 | 0.1438 | 0.1437 | 0.2431 | 0.1202 | -0.0003 | -0.0001 | 0.0003 | -0.0001 | -0.0004 | -0.0003 | -0.0078 | -0.0095 | -0.0016 | -370.1719 | 3.2765 | -370.6889 | 3.0157 | -370.8181 | 2.835 | -370.8058 | 1.9131 | -370.455 | 2.718 | -370.5381 | 1.7386
11:20 | 28 | 29.0909 | 18.1982 | 41.6229 | 49.1119 | -1.3087 | -9.8288 | -0.6241 | -1.0923 | 0.1111 | -0.1393 | -0.0921 | -1.0056 | 6.7377 | -0.0713 | 0.378 | 0.3713 | 0.3721 | 0.2464 | -16.2837 |  | -0.2528 | -0.7344 | -2.2665 | -1.5425 | 0.1423 |  | -0.2475 | 0.0647 | 2.0218 | 1.6736 | 2.3277 | 0.7242 | 0.1332 | 0.1389 | 0.1748 | 0.0922 | -0.0001 | 0.0007 | 0.0005 | 0.0003 | 0.0004 | -0.0006 | 0.0068 | -0.0034 | 0.0067 | -370.0735 | 3.4387 | -370.655 | 3.18 | -370.8028 | 2.8576 | -370.8705 | 1.9501 | -370.4673 | 2.7098 | -370.4735 | 1.7345
11:20 | 29 | 29.1265 | 18.4162 | 42.1777 | 49.6645 | -1.3197 | -10.2762 | -0.6986 | -1.1733 | 0.0552 | -0.1161 | -0.1301 | -0.9961 | 6.6885 | -0.0587 | 0.378 | 0.3737 | 0.3716 | 0.2481 | -16.4512 |  | -0.2777 | -0.6401 | -2.2942 | -1.4928 | 0.1755 |  | -0.2545 | 0.1827 | 2.0295 | 1.6778 | 2.3352 | 0.7135 | 0.1691 | 0.1226 | 0.2581 | 0.1217 | -0.0003 | 0.0007 | 0 | 0.0004 | -0.0001 | -0.0003 | 0.0118 | -0.006 | 0.008 | -369.9473 | 3.5639 | -370.5997 | 3.2929 | -370.7628 | 2.8884 | -370.8766 | 1.946 | -370.4243 | 2.6995 | -370.4212 | 1.7201
11:20 | 30 | 29.1446 | 18.6417 | 42.6372 | 50.0762 | -1.3597 | -10.6583 | -0.7565 | -1.0848 | 0.0909 | -0.2946 | -0.1137 | -0.9937 | 6.6542 | -0.0721 | 0.3783 | 0.3719 | 0.3741 | 0.2476 | -16.5191 |  | -0.1124 | -0.4949 | -2.2569 | -1.5355 | 0.1655 |  | -0.3392 | 0.0378 | 2.037 | 1.6793 | 2.338 | 0.7051 | 0.1921 | 0.1456 | 0.3149 | 0.122 | -0.0003 | 0.0006 | -0.0003 | -0.0001 | 0.0001 | -0.0006 | 0.0132 | -0.0044 | 0.0027 | -369.8888 | 3.6789 | -370.6304 | 3.4428 | -370.8028 | 2.872 | -370.8304 | 1.9542 | -370.4643 | 2.7077 | -370.4058 | 1.7509
11:20 | 31 | 29.143 | 18.8141 | 43.091 | 50.4476 | -1.2967 | -10.9215 | -0.7792 | -1.1767 | 0.0669 | -0.1674 | -0.1066 | -1.1193 | 6.5802 | -0.1442 | 0.3795 | 0.3672 | 0.3721 | 0.2475 | -16.6078 |  | -0.1638 | -0.4138 | -2.3196 | -1.4686 | 0.178 |  | -0.3648 | -0.0131 | 2.0421 | 1.6823 | 2.348 | 0.6945 | 0.1469 | 0.1583 | 0.3288 | 0.1053 | 0.0004 | 0.0005 | 0.0001 | 0.0005 | -0.0002 | -0.0004 | 0.0114 | -0.0072 | 0.0107 | -369.8796 | 3.8062 | -370.6674 | 3.5311 | -370.7351 | 2.8474 | -370.8243 | 1.946 | -370.3689 | 2.7468 | -370.4304 | 1.7509
11:20 | 32 | 29.172 | 19.0393 | 43.4116 | 50.6936 | -1.3859 | -11.2161 | -0.8348 | -1.1897 | 0.0242 | -0.2037 | -0.203 | -1.1215 | 6.667 | -0.222 | 0.3803 | 0.3688 | 0.3736 | 0.2474 | -16.6393 |  | -0.1219 | -0.5371 | -2.3355 | -1.5116 | 0.1347 |  | -0.3966 | 0.0436 | 2.0464 | 1.6824 | 2.3517 | 0.6882 | 0.1757 | 0.1466 | 0.3855 | 0.1402 | -0.0001 | 0.0005 | 0.0006 | 0.0003 | 0.0005 | -0.0004 | -0.0034 | -0.0084 | -0.0138 | -369.8519 | 3.8884 | -370.615 | 3.6153 | -370.7289 | 2.833 | -370.7689 | 1.9665 | -370.412 | 2.7611 | -370.4027 | 1.7509
11:20 | 33 | 29.1633 | 19.1524 | 43.6047 | 50.9331 | -1.3738 | -11.3812 | -0.8294 | -1.2609 | -0.0539 | -0.3547 | -0.1502 | -1.1049 | 6.6635 | -0.1402 | 0.3787 | 0.3706 | 0.3766 | 0.2469 | -16.6624 |  | -0.1362 | -0.5116 | -2.3466 | -1.5509 | 0.1815 |  | -0.3635 | 0.0392 | 2.05 | 1.6841 | 2.355 | 0.6838 | 0.1633 | 0.1457 | 0.3739 | 0.1448 | -0.0001 | 0.0009 | 0.0002 | 0.0002 | 0.0004 | 0 | -0.0071 | -0.0092 | 0.0009 | -369.8119 | 3.9274 | -370.6212 | 3.7056 | -370.7781 | 2.8679 | -370.8151 | 1.9583 | -370.3658 | 2.7447 | -370.3719 | 1.7735
11:20 | 34 | 29.1205 | 19.2396 | 43.8021 | 51.1718 | -1.3972 | -11.4635 | -0.8322 | -1.2048 | 0.0468 | -0.1859 | -0.1215 | -1.0795 | 6.6136 | -0.2353 | 0.3789 | 0.3697 | 0.3723 | 0.2476 | -16.8247 |  | -0.2396 | -0.5056 | -2.3301 | -1.6188 | 0.1265 |  | -0.4043 | 0.0754 | 2.0542 | 1.6852 | 2.3586 | 0.6811 | 0.166 | 0.1485 | 0.3924 | 0.1481 | -0.0002 | 0.0005 | 0.0008 | 0.0005 | -0.0002 | -0.0005 | 0.0086 | -0.0065 | 0.0063 | -369.7104 | 3.9479 | -370.6089 | 3.7816 | -370.8028 | 2.8638 | -370.7812 | 1.9439 | -370.3073 | 2.718 | -370.3843 | 1.7838
11:20 | 35 | 29.1735 | 19.3505 | 44.0135 | 51.3446 | -1.4059 | -11.5631 | -0.8695 | -1.266 | -0.0122 | -0.3603 | -0.1364 | -1.1523 | 6.5745 | -0.3047 | 0.3798 | 0.368 | 0.3705 | 0.2472 | -16.8042 |  | -0.1385 | -0.5524 | -2.3345 | -1.5683 | 0.1258 |  | -0.3929 | 0.1469 | 2.0571 | 1.69 | 2.3634 | 0.6784 | 0.2022 | 0.1497 | 0.4144 | 0.1714 | 0.0002 | 0.0005 | 0.0009 | 0.0001 | 0.0006 | -0.0003 | 0.0054 | -0.0179 | -0.0067 | -369.735 | 4.0198 | -370.6366 | 3.8247 | -370.7781 | 2.8741 | -370.772 | 1.9378 | -370.3289 | 2.7611 | -370.3935 | 1.7961
11:20 | 36 | 29.1362 | 19.3359 | 44.0344 | 51.4128 | -1.3563 | -11.6574 | -0.774 | -1.1921 | 0.0179 | -0.2831 | -0.196 | -1.1603 | 6.6235 | -0.2873 | 0.3765 | 0.3688 | 0.3702 | 0.2467 | -16.8078 |  | -0.0394 | -0.5361 | -2.4095 | -1.712 | 0.1433 |  | -0.4205 | 0.0147 | 2.0586 | 1.687 | 2.3632 | 0.6753 | 0.1841 | 0.1552 | 0.404 | 0.184 | 0.0001 | 0.0003 | 0.0004 | 0.0003 | -0.0001 | -0.0003 | 0.0046 | -0.0135 | 0.015 | -369.7319 | 4.0177 | -370.5566 | 3.8514 | -370.7289 | 2.8679 | -370.772 | 1.9665 | -370.3843 | 2.7509 | -370.3012 | 1.7674
11:20 | 37 | 29.1714 | 19.3299 | 44.2028 | 51.5338 | -1.3995 | -11.7259 | -0.7407 | -1.2597 | 0.0086 | -0.2448 | -0.1503 | -1.1974 | 6.6934 | -0.3059 | 0.3778 | 0.3726 | 0.3734 | 0.2462 | -16.8558 |  | -0.1792 | -0.7881 | -2.434 | -1.7669 | 0.1177 |  | -0.3257 | 0.0659 | 2.0587 | 1.6903 | 2.3634 | 0.6738 | 0.176 | 0.1646 | 0.3762 | 0.1711 | -0.0004 | 0.0004 | 0 | 0.0002 | 0.0004 | -0.0005 | -0.0031 | -0.0129 | -0.0141 | -369.7288 | 4.0403 | -370.5289 | 3.8781 | -370.7381 | 2.8741 | -370.8274 | 1.9727 | -370.3658 | 2.7365 | -370.2981 | 1.7591
11:20 | 38 | 29.1096 | 19.298 | 44.2604 | 51.6032 | -1.3296 | -11.784 | -0.7551 | -1.2304 | -0.0226 | -0.3759 | -0.2075 | -1.195 | 6.6194 | -0.2226 | 0.378 | 0.37 | 0.3774 | 0.2468 | -16.9991 |  | -0.1432 | -0.7014 | -2.3903 | -1.7071 | 0.1387 |  | -0.2947 | 0.0091 | 2.0589 | 1.6882 | 2.3663 | 0.673 | 0.1765 | 0.1475 | 0.3913 | 0.153 | 0 | 0.001 | -0.0003 | 0 | 0 | -0.0001 | 0.0111 | -0.0169 | -0.0119 | -369.698 | 4.0896 | -370.5935 | 3.9541 | -370.7443 | 2.8617 | -370.7935 | 1.9686 | -370.3166 | 2.7591 | -370.3412 | 1.7838
11:20 | 39 | 29.2232 | 19.4585 | 44.4456 | 51.8211 | -1.3266 | -11.8388 | -0.796 | -1.2339 | -0.0122 | -0.3398 | -0.2025 | -1.168 | 6.6471 | -0.2907 | 0.3787 | 0.3683 | 0.3724 | 0.2469 | -17.0788 |  | -0.2283 | -0.6203 | -2.4079 | -1.6543 | 0.1177 |  | -0.348 | 0.1309 | 2.062 | 1.6902 | 2.367 | 0.6697 | 0.1493 | 0.1724 | 0.4086 | 0.19 | -0.0002 | 0.0003 | 0.0005 | 0.0006 | -0.0001 | -0.0009 | 0.0065 | -0.0146 | -0.0196 | -369.6642 | 4.1101 | -370.6181 | 3.9705 | -370.7258 | 2.8658 | -370.7843 | 1.9398 | -370.3043 | 2.7652 | -370.3781 | 1.7776
11:20 | 40 | 29.191 | 19.4681 | 44.6251 | 51.9591 | -1.2743 | -11.995 | -0.7896 | -1.2151 | -0.0187 | -0.4153 | -0.2294 | -1.1595 | 6.6455 | -0.2275 | 0.3759 | 0.3674 | 0.3704 | 0.2452 | -17.142 |  | -0.1738 | -0.4837 | -2.3896 | -1.5164 | 0.2107 |  | -0.3646 | 0.0441 | 2.0633 | 1.6907 | 2.3708 | 0.6686 | 0.1737 | 0.1562 | 0.4005 | 0.1962 | 0.0006 | 0.0008 | 0.0004 | 0.0007 | 0 | -0.0001 | 0.0091 | -0.0115 | -0.0236 | -369.7073 | 4.1245 | -370.5689 | 4.0198 | -370.7443 | 2.8699 | -370.7904 | 1.9665 | -370.3289 | 2.7673 | -370.3135 | 1.7756
11:20 | 41 | 29.1128 | 19.55 | 44.6568 | 52.0843 | -1.3061 | -12.0998 | -0.8896 | -1.2837 | -0.0087 | -0.3325 | -0.3069 | -1.2036 | 6.6146 | -0.2804 | 0.3779 | 0.3687 | 0.3719 | 0.2465 | -17.2365 |  | -0.1679 | -0.4994 | -2.4215 | -1.7407 | 0.1117 |  | -0.3949 | -0.0282 | 2.0664 | 1.692 | 2.374 | 0.6675 | 0.2008 | 0.2006 | 0.4225 | 0.2114 | 0.0001 | 0.0008 | 0.0005 | 0.0004 | 0 | -0.0004 | -0.0058 | -0.0016 | -0.0233 | -369.6857 | 4.1594 | -370.5412 | 4.0403 | -370.7443 | 2.8638 | -370.7904 | 1.9645 | -370.3166 | 2.7591 | -370.3227 | 1.7776
11:20 | 42 | 29.1641 | 19.5616 | 44.6842 | 52.083 | -1.2825 | -12.0886 | -0.8535 | -1.3078 | -0.068 | -0.3547 | -0.2004 | -1.1798 | 6.5891 | -0.2161 | 0.3785 | 0.3726 | 0.3749 | 0.2483 | -17.4022 |  | -0.1549 | -0.4951 | -2.32 | -1.6885 | 0.1339 |  | -0.3668 | -0.0859 | 2.0665 | 1.6929 | 2.3733 | 0.6651 | 0.2043 | 0.1985 | 0.4237 | 0.2101 | -0.0008 | 0.0004 | 0.0002 | -0.0001 | -0.0001 | -0.0003 | -0.0007 | -0.0182 | -0.0155 | -369.655 | 4.184 | -370.5473 | 4.0608 | -370.7443 | 2.8741 | -370.7935 | 1.9583 | -370.255 | 2.7591 | -370.3258 | 1.7776
11:20 | 43 | 29.1804 | 19.5545 | 44.8858 | 52.1671 | -1.3837 | -12.1425 | -0.911 | -1.2692 | -0.0588 | -0.3473 | -0.3127 | -1.1184 | 6.6465 | -0.1899 | 0.3772 | 0.3679 | 0.3728 | 0.2468 | -17.4547 |  | -0.1403 | -0.4203 | -2.3337 | -1.6801 | 0.1115 |  | -0.4112 | 0.0047 | 2.0688 | 1.697 | 2.3719 | 0.6643 | 0.1904 | 0.1959 | 0.4075 | 0.2294 | -0.0002 | 0.0006 | 0.0004 | 0.0003 | 0.0002 | 0.0002 | 0.0136 | -0.0021 | 0.0108 | -369.6642 | 4.2046 | -370.5535 | 4.0978 | -370.772 | 2.8823 | -370.7812 | 1.9645 | -370.3104 | 2.7632 | -370.3227 | 1.7838
11:20 | 44 | 29.1155 | 19.6185 | 44.8575 | 52.2441 | -1.3411 | -12.217 | -0.8401 | -1.3535 | -0.0756 | -0.3347 | -0.2241 | -1.1185 | 6.5724 | -0.2451 | 0.3772 | 0.3667 | 0.3743 | 0.2454 | -17.4379 |  | -0.0486 | -0.5093 | -2.3726 | -1.6495 | 0.0754 |  | -0.4573 | -0.0301 | 2.0698 | 1.6958 | 2.3723 | 0.6631 | 0.2188 | 0.2303 | 0.4387 | 0.2359 | -0.0003 | 0.0001 | 0.0004 | -0.0001 | -0.0001 | -0.001 | 0.0006 | -0.0145 | -0.0027 | -369.6673 | 4.2251 | -370.5227 | 4.106 | -370.6889 | 2.8658 | -370.7812 | 1.9706 | -370.3012 | 2.7509 | -370.2981 | 1.7797
11:20 | 45 | 29.2306 | 19.7798 | 45.0562 | 52.3996 | -1.325 | -12.3036 | -0.8798 | -1.3107 | -0.0936 | -0.2856 | -0.1458 | -1.1641 | 6.6146 | -0.2577 | 0.378 | 0.3697 | 0.3739 | 0.247 | -17.5243 |  | -0.0444 | -0.4361 | -2.3221 | -1.6108 | 0.1292 |  | -0.4324 | 0.0349 | 2.0707 | 1.6974 | 2.3772 | 0.6624 | 0.1947 | 0.2236 | 0.4318 | 0.2408 | 0.0001 | 0.0004 | 0.0006 | 0.0001 | -0.0001 | 0.0001 | 0.0145 | 0.0046 | -0.0026 | -369.6734 | 4.2826 | -370.5197 | 4.1245 | -370.6981 | 2.872 | -370.8089 | 1.9768 | -370.335 | 2.7755 | -370.3073 | 1.755
11:20 | 46 | 29.1411 | 19.7063 | 45.1098 | 52.623 | -1.3687 | -12.3354 | -0.9129 | -1.2897 | -0.0725 | -0.3039 | -0.1786 | -1.1433 | 6.6366 | -0.2225 | 0.3799 | 0.3726 | 0.3773 | 0.248 | -17.6874 |  | -0.1435 | -0.6093 | -2.3342 | -1.7114 | 0.1479 |  | -0.3797 | 0.0184 | 2.0731 | 1.6953 | 2.3778 | 0.6594 | 0.1683 | 0.2146 | 0.3971 | 0.2443 | -0.0006 | 0.0002 | -0.0003 | 0 | 0.0002 | -0.001 | 0.0102 | -0.0063 | 0.0011 | -369.6027 | 4.3031 | -370.495 | 4.1696 | -370.7104 | 2.8679 | -370.8028 | 1.9521 | -370.3104 | 2.7693 | -370.295 | 1.7715
11:20 | 47 | 29.1273 | 19.7262 | 45.2611 | 52.6443 | -1.3352 | -12.4052 | -0.8668 | -1.2546 | -0.0338 | -0.24 | -0.1398 | -1.2252 | 6.5925 | -0.265 | 0.38 | 0.3692 | 0.3754 | 0.2471 | -17.6814 |  | -0.1712 | -0.5982 | -2.4569 | -1.7963 | 0.153 |  | -0.4157 | -0.0795 | 2.074 | 1.7015 | 2.3783 | 0.6566 | 0.1792 | 0.2312 | 0.4445 | 0.2487 | -0.0005 | 0.0006 | 0.0001 | 0.0006 | -0.0004 | -0.0002 | -0.0006 | -0.0092 | -0.009 | -369.5688 | 4.3216 | -370.5412 | 4.2456 | -370.7812 | 2.8576 | -370.7443 | 1.9501 | -370.2673 | 2.755 | -370.3043 | 1.8166
11:21 | 48 | 29.198 | 19.773 | 45.3576 | 52.8361 | -1.2983 | -12.5514 | -0.94 | -1.2287 | -0.0049 | -0.2397 | -0.1644 | -1.085 | 6.5768 | -0.2056 | 0.3801 | 0.3657 | 0.3735 | 0.2475 | -17.7623 |  | -0.1729 | -0.5141 | -2.4707 | -1.7095 | 0.2047 |  | -0.4858 | -0.0243 | 2.0767 | 1.6972 | 2.382 | 0.6559 | 0.1737 | 0.243 | 0.3832 | 0.2539 | 0.0001 | 0.0002 | 0.0006 | 0.0006 | 0.0006 | -0.0004 | -0.0002 | -0.0107 | -0.0096 | -369.6365 | 4.377 | -370.5443 | 4.2477 | -370.7474 | 2.8617 | -370.7658 | 1.946 | -370.2704 | 2.7734 | -370.3535 | 1.794
11:21 | 49 | 29.1775 | 19.8493 | 45.4823 | 52.9269 | -1.3497 | -12.5654 | -0.8037 | -1.3573 | -0.1198 | -0.34 | -0.2021 | -1.1391 | 6.6085 | -0.1995 | 0.3801 | 0.3688 | 0.3744 | 0.2489 | -17.8805 |  | -0.1243 | -0.5256 | -2.4606 | -1.8828 | 0.1737 |  | -0.3983 | 0.1067 | 2.0787 | 1.7033 | 2.3845 | 0.6547 | 0.1764 | 0.2399 | 0.4133 | 0.263 | 0 | 0.0002 | 0.0002 | 0.0001 | -0.0002 | -0.0004 | 0.0045 | 0.0017 | -0.0099 | -369.6211 | 4.375 | -370.4612 | 4.26 | -370.6951 | 2.8617 | -370.8058 | 1.9624 | -370.2642 | 2.7529 | -370.2858 | 1.7694
11:21 | 50 | 29.1516 | 19.7975 | 45.5048 | 52.9916 | -1.3869 | -12.5859 | -0.8591 | -1.2705 | -0.126 | -0.3115 | -0.136 | -1.0479 | 6.5272 | -0.234 | 0.38 | 0.3681 | 0.3745 | 0.2482 | -17.934 |  | -0.1636 | -0.4651 | -2.4207 | -1.7966 | 0.2274 |  | -0.4665 | 0.0466 | 2.0787 | 1.7054 | 2.3829 | 0.6522 | 0.2058 | 0.2865 | 0.411 | 0.2853 | -0.0003 | 0.0007 | 0.0003 | 0.0003 | 0.0001 | 0.0002 | 0.0018 | -0.0073 | -0.0113 | -369.578 | 4.3934 | -370.4335 | 4.2805 | -370.7443 | 2.8966 | -370.8366 | 1.9788 | -370.2735 | 2.757 | -370.2612 | 1.7571
11:21 | 51 | 29.1443 | 19.919 | 45.6011 | 53.0016 | -1.2808 | -12.5886 | -0.8078 | -1.2541 | -0.1317 | -0.4278 | -0.1125 | -1.083 | 6.523 | -0.2455 | 0.3794 | 0.3696 | 0.373 | 0.2489 | -17.955 |  | -0.1761 | -0.5359 | -2.4422 | -1.8728 | 0.1602 |  | -0.4826 | 0.026 | 2.0806 | 1.7041 | 2.3831 | 0.6526 | 0.222 | 0.2854 | 0.4723 | 0.3078 | -0.0008 | 0.0003 | 0.0002 | -0.0002 | 0.0001 | -0.0005 | 0.0122 | -0.0117 | -0.0113 | -369.5503 | 4.4119 | -370.452 | 4.3154 | -370.7289 | 2.8802 | -370.7689 | 1.9521 | -370.2673 | 2.7488 | -370.2458 | 1.7817
11:21 | 52 | 29.1734 | 20.0305 | 45.7348 | 53.1617 | -1.2704 | -12.7772 | -0.9281 | -1.2873 | -0.1062 | -0.4444 | -0.1159 | -1.133 | 6.5805 | -0.2304 | 0.379 | 0.3669 | 0.3738 | 0.248 | -18.0035 |  | -0.1434 | -0.5539 | -2.4481 | -1.853 | 0.1411 |  | -0.4149 | -0.0216 | 2.0807 | 1.7065 | 2.3848 | 0.6519 | 0.1893 | 0.2873 | 0.4225 | 0.2807 | 0.0001 | 0.001 | 0.0006 | 0.0002 | -0.0002 | 0 | 0.0055 | -0.0075 | -0.0062 | -369.6334 | 4.4797 | -370.5166 | 4.3236 | -370.7289 | 2.8638 | -370.7874 | 1.9645 | -370.3012 | 2.794 | -370.3043 | 1.7817
11:21 | 53 | 29.2959 | 20.1257 | 45.9351 | 53.2245 | -1.3866 | -12.8572 | -1.0809 | -1.3523 | -0.1574 | -0.4344 | -0.163 | -1.1395 | 6.5854 | -0.2013 | 0.3782 | 0.3679 | 0.3736 | 0.2479 | -18.1518 |  | -0.2423 | -0.5769 | -2.4621 | -1.8105 | 0.1018 |  | -0.4067 | 0.1064 | 2.081 | 1.7058 | 2.385 | 0.6509 | 0.2232 | 0.298 | 0.4341 | 0.2853 | 0 | 0.0004 | 0.0005 | 0.0005 | 0.0007 | -0.0001 | 0.0017 | -0.0081 | 0.0017 | -369.5965 | 4.4817 | -370.4797 | 4.3339 | -370.6951 | 2.8474 | -370.7351 | 1.9665 | -370.3073 | 2.7837 | -370.2827 | 1.7715
11:21 | 54 | 29.2426 | 20.0773 | 45.8788 | 53.2946 | -1.424 | -12.9555 | -1.0078 | -1.3317 | -0.1427 | -0.4012 | -0.1676 | -1.1428 | 6.5092 | -0.2348 | 0.3793 | 0.3707 | 0.3717 | 0.2477 | -18.1273 |  | -0.0621 | -0.7898 | -2.5039 | -1.8642 | 0.1177 |  | -0.4517 | 0.0334 | 2.0826 | 1.709 | 2.3833 | 0.6523 | 0.2184 | 0.3106 | 0.4237 | 0.292 | 0.0002 | 0.0007 | 0.0004 | 0.0003 | -0.0002 | -0.0001 | 0.0116 | -0.0084 | 0.0041 | -369.538 | 4.4756 | -370.4704 | 4.3627 | -370.7258 | 2.8761 | -370.8058 | 1.9665 | -370.2827 | 2.7817 | -370.2673 | 1.7694
11:21 | 55 | 29.368 | 20.2501 | 46.0013 | 53.3654 | -1.4306 | -12.8993 | -0.9654 | -1.2869 | -0.0567 | -0.4232 | -0.2246 | -1.0724 | 6.537 | -0.222 | 0.3783 | 0.366 | 0.3752 | 0.249 | -18.2005 |  | -0.0826 | -0.8329 | -2.5364 | -1.8503 | 0.1206 |  | -0.3692 | -0.0352 | 2.0821 | 1.7081 | 2.3857 | 0.6523 | 0.2112 | 0.2978 | 0.4086 | 0.2858 | -0.0002 | 0.0007 | 0.0005 | 0.0006 | 0.0003 | -0.0006 | 0.011 | -0.0072 | -0.0112 | -369.4826 | 4.4612 | -370.4827 | 4.3811 | -370.732 | 2.8679 | -370.7535 | 1.9419 | -370.2181 | 2.7447 | -370.2458 | 1.8105
11:21 | 56 | 29.3313 | 20.1268 | 45.9619 | 53.4198 | -1.4272 | -13.0121 | -1.0025 | -1.4039 | -0.1807 | -0.5661 | -0.2989 | -1.1142 | 6.5697 | -0.2743 | 0.3789 | 0.3674 | 0.3739 | 0.2473 | -18.2205 |  | -0.0587 | -0.6613 | -2.4171 | -1.8357 | 0.12 |  | -0.3932 | 0.0434 | 2.0825 | 1.7079 | 2.3848 | 0.6514 | 0.2025 | 0.2775 | 0.4052 | 0.2773 | -0.0002 | 0.0007 | 0.0002 | 0.0007 | 0 | -0.0003 | -0.0039 | -0.0115 | -0.0008 | -369.5473 | 4.5269 | -370.5197 | 4.375 | -370.7166 | 2.8782 | -370.7566 | 1.948 | -370.2366 | 2.7919 | -370.3073 | 1.7982
11:21 | 57 | 29.2333 | 20.093 | 46.0102 | 53.4532 | -1.3464 | -12.9572 | -0.9894 | -1.2535 | -0.1102 | -0.4958 | -0.2817 | -1.0444 | 6.5759 | -0.1603 | 0.3817 | 0.3687 | 0.3758 | 0.2491 | -18.1737 |  | -0.0573 | -0.6028 | -2.431 | -1.8525 | 0.1043 |  | -0.4687 | 0.1127 | 2.0832 | 1.7102 | 2.3841 | 0.6534 | 0.1889 | 0.2987 | 0.4434 | 0.2639 | 0.0002 | 0.0002 | 0.0004 | 0.0001 | 0.0001 | -0.0007 | 0.0044 | -0.0169 | -0.0111 | -369.5442 | 4.4797 | -370.4335 | 4.3483 | -370.7104 | 2.8658 | -370.7566 | 1.9665 | -370.2642 | 2.7591 | -370.2489 | 1.7756
11:21 | 58 | 29.2021 | 20.0365 | 45.7244 | 53.2036 | -1.3746 | -12.5051 | -1.0048 | -1.1984 | -0.0915 | -0.4074 | -0.1938 | -1.0695 | 6.6553 | -0.2486 | 0.38 | 0.3644 | 0.374 | 0.2485 | -17.931 |  | -0.1082 | -0.7775 | -2.4327 | -1.8249 | 0.0221 |  | -0.3695 | 0.0265 | 2.0734 | 1.709 | 2.3833 | 0.6634 | 0.2207 | 0.2842 | 0.4399 | 0.2727 | 0.0001 | 0.0004 | 0.0003 | 0.0007 | 0 | -0.0002 | -0.0018 | 0.001 | 0.0098 | -369.6334 | 4.2908 | -370.452 | 4.1738 | -370.7012 | 2.9007 | -370.812 | 1.9809 | -370.2796 | 2.8001 | -370.2673 | 1.8105
11:21 | 59 | 29.2604 | 19.8591 | 45.2681 | 52.7233 | -1.4468 | -12.0262 | -1.0267 | -1.2444 | -0.0833 | -0.1235 | -0.0784 | -1.0363 | 6.6235 | -0.2161 | 0.3794 | 0.3659 | 0.3738 | 0.2483 | -17.7057 |  | -0.2294 | -0.7209 | -2.3854 | -1.6744 | 0.1221 |  | -0.4254 | 0.0169 | 2.0617 | 1.7091 | 2.3727 | 0.6789 | 0.1813 | 0.2795 | 0.4306 | 0.2791 | -0.0003 | 0.0008 | 0.0011 | 0.0009 | 0.0002 | -0.0001 | 0.0092 | -0.0032 | 0.0069 | -369.7811 | 4.0485 | -370.4243 | 3.9397 | -370.7258 | 2.872 | -370.7535 | 1.9747 | -370.2519 | 2.796 | -370.3073 | 1.8536
11:21 | 60 | 29.2404 | 19.4655 | 44.7011 | 52.1286 | -1.4662 | -11.4401 | -0.9504 | -1.2371 | 0.0042 | -0.1114 | -0.1008 | -0.9491 | 6.7803 | -0.1138 | 0.3798 | 0.3648 | 0.3729 | 0.2469 | -17.4416 |  | -0.1957 | -0.7626 | -2.282 | -1.7095 | 0.1336 |  | -0.3761 | -0.0506 | 2.0473 | 1.7061 | 2.361 | 0.6928 | 0.215 | 0.2901 | 0.4179 | 0.284 | -0.0005 | 0.0007 | 0.0001 | 0.0002 | 0.0002 | -0.0002 | 0.004 | -0.0033 | -0.0071 | -369.9535 | 3.8493 | -370.4335 | 3.7364 | -370.7412 | 2.8884 | -370.7597 | 1.9871 | -370.3043 | 2.8001 | -370.3319 | 1.8762
11:21 | 61 | 29.2871 | 19.1441 | 44.271 | 51.5738 | -1.3522 | -10.9765 | -0.8605 | -1.2519 | 0.1191 | -0.144 | 0.0463 | -0.9809 | 6.7553 | -0.1056 | 0.378 | 0.3674 | 0.3729 | 0.2482 | -17.0683 |  | -0.1438 | -0.7088 | -2.2186 | -1.5624 | 0.0586 |  | -0.4065 | 0.1 | 2.0359 | 1.7086 | 2.3548 | 0.7062 | 0.2055 | 0.292 | 0.4318 | 0.2743 | 0.0001 | 0.0009 | 0.0006 | 0.0007 | -0.0004 | -0.0001 | 0.006 | -0.0174 | -0.0221 | -370.0581 | 3.6502 | -370.4212 | 3.5331 | -370.6981 | 2.8966 | -370.7812 | 1.9953 | -370.2919 | 2.7899 | -370.3627 | 1.8782
11:21 | 62 | 29.2642 | 18.9998 | 43.6264 | 51.0789 | -1.3678 | -10.5266 | -0.7692 | -1.2391 | 0.0436 | -0.0629 | -0.019 | -1.0385 | 6.7875 | -0.1111 | 0.3789 | 0.369 | 0.3753 | 0.2467 | -16.8507 |  | -0.1522 | -0.7635 | -2.2592 | -1.5893 | 0.0493 |  | -0.3913 | 0.0589 | 2.0285 | 1.7112 | 2.3492 | 0.7191 | 0.2005 | 0.2698 | 0.3855 | 0.2524 | 0.0003 | 0.0003 | 0.0002 | 0 | -0.0002 | -0.0007 | 0.0089 | 0 | 0.0112 | -370.1781 | 3.49 | -370.4089 | 3.3525 | -370.7443 | 2.9439 | -370.7874 | 2.0096 | -370.3719 | 2.796 | -370.3596 | 1.8556
11:21 | 63 | 29.2746 | 18.853 | 43.2807 | 50.7247 | -1.404 | -10.2271 | -0.7851 | -1.1876 | 0.1304 | -0.0791 | -0.0918 | -1.1158 | 6.7908 | -0.072 | 0.3768 | 0.366 | 0.3714 | 0.2472 | -16.7346 |  | -0.1233 | -0.8432 | -2.2406 | -1.4615 | 0.1291 |  | -0.2992 | 0.0825 | 2.0203 | 1.7091 | 2.3437 | 0.7297 | 0.1987 | 0.2679 | 0.4017 | 0.2503 | 0 | 0.0003 | 0.0001 | 0.0001 | -0.0005 | -0.0002 | 0.0126 | -0.0098 | -0.0022 | -370.2027 | 3.3299 | -370.4027 | 3.221 | -370.7351 | 2.9767 | -370.7689 | 2.0692 | -370.3381 | 2.7714 | -370.3658 | 1.8721
11:21 | 64 | 29.2276 | 18.701 | 42.9954 | 50.3189 | -1.366 | -9.92 | -0.752 | -1.17 | 0.2216 | -0.1092 | 0.0185 | -0.972 | 6.8536 | 0.0301 | 0.3792 | 0.3695 | 0.3703 | 0.2464 | -16.4918 |  | -0.1996 | -0.8227 | -2.1908 | -1.3979 | 0.1157 |  | -0.2804 | 0.0022 | 2.0149 | 1.7073 | 2.3415 | 0.7376 | 0.1708 | 0.24 | 0.345 | 0.2165 | -0.0004 | 0.0009 | 0.0003 | 0.0002 | 0.0002 | -0.0008 | 0.0046 | -0.0132 | 0.002 | -370.3043 | 3.2252 | -370.4335 | 3.0999 | -370.732 | 3.0301 | -370.7535 | 2.0774 | -370.3104 | 2.7796 | -370.4181 | 1.8618
11:21 | 65 | 29.2816 | 18.6063 | 42.7207 | 50.166 | -1.3338 | -9.7519 | -0.7225 | -1.1647 | 0.2019 | -0.0595 | -0.0145 | -0.96 | 6.8448 | 0.1046 | 0.3792 | 0.372 | 0.3765 | 0.2451 | -16.3636 |  | -0.1151 | -0.9295 | -2.1478 | -1.3974 | 0.0254 |  | -0.1964 | 0.0503 | 2.0086 | 1.7071 | 2.3348 | 0.7427 | 0.1792 | 0.2428 | 0.3693 | 0.2371 | -0.0004 | 0.0005 | 0 | -0.0002 | -0.0001 | -0.0005 | 0.0007 | -0.0093 | -0.0213 | -370.3781 | 3.1245 | -370.4304 | 2.9952 | -370.692 | 3.0835 | -370.7812 | 2.1349 | -370.3843 | 2.7775 | -370.4366 | 1.8392
11:21 | 66 | 29.2635 | 18.5655 | 42.594 | 50.0432 | -1.2642 | -9.5778 | -0.6987 | -1.1111 | 0.1863 | -0.01 | 0.0061 | -0.9344 | 6.858 | -0.001 | 0.3796 | 0.3693 | 0.3745 | 0.2468 | -16.4085 |  | -0.143 | -0.8185 | -2.1866 | -1.462 | 0.0923 |  | -0.1856 | 0.077 | 2.0053 | 1.7104 | 2.3318 | 0.7471 | 0.1803 | 0.2207 | 0.3253 | 0.1974 | 0 | 0 | 0.0001 | 0.0001 | -0.0001 | -0.0006 | -0.0097 | -0.0204 | 0.0037 | -370.3996 | 3.0424 | -370.3073 | 2.8905 | -370.7227 | 3.143 | -370.7935 | 2.1801 | -370.3812 | 2.7468 | -370.3689 | 1.8228
11:21 | 67 | 29.2579 | 18.4942 | 42.4879 | 49.9568 | -1.3039 | -9.4737 | -0.6904 | -1.11 | 0.2422 | 0.0061 | 0.0602 | -0.915 | 6.8208 | -0.0016 | 0.3791 | 0.3696 | 0.3721 | 0.2456 | -16.2553 |  | -0.0504 | -0.8252 | -2.0911 | -1.3861 | 0.1179 |  | -0.143 | 0.1672 | 2.0036 | 1.7088 | 2.3271 | 0.7506 | 0.1755 | 0.2564 | 0.367 | 0.2214 | -0.0002 | 0.0003 | 0.0009 | 0.0006 | -0.0002 | -0.0005 | 0.0059 | 0.0016 | -0.0205 | -370.455 | 2.9747 | -370.3689 | 2.8597 | -370.7166 | 3.1985 | -370.7658 | 2.2581 | -370.375 | 2.716 | -370.4027 | 1.8433
11:21 | 68 | 29.2519 | 18.588 | 42.4941 | 49.9859 | -1.3632 | -9.4965 | -0.7631 | -1.1507 | 0.2364 | 0.0228 | 0.0773 | -0.9185 | 6.8555 | -0.0468 | 0.381 | 0.3713 | 0.3731 | 0.2456 | -16.1618 |  | -0.0351 | -0.8087 | -2.1525 | -1.4481 | 0.1007 |  | -0.2431 | 0.0628 | 2.0041 | 1.7067 | 2.3253 | 0.7506 | 0.1992 | 0.274 | 0.4052 | 0.2553 | -0.0006 | 0.0003 | 0.0007 | 0.0003 | 0.0001 | 0 | -0.0085 | -0.0099 | -0.0098 | -370.5012 | 2.9398 | -370.3812 | 2.7878 | -370.6766 | 3.2621 | -370.7258 | 2.3197 | -370.3966 | 2.7529 | -370.3966 | 1.8146
11:21 | 69 | 29.2229 | 18.5865 | 42.6408 | 50.1298 | -1.3186 | -9.5146 | -0.663 | -1.1267 | 0.168 | 0.0165 | 0.0171 | -0.9599 | 6.8341 | -0.0346 | 0.3792 | 0.3706 | 0.3734 | 0.2459 | -16.2166 |  | -0.0462 | -0.7522 | -2.1441 | -1.479 | 0.1043 |  | -0.2067 | 0.084 | 2.0009 | 1.7061 | 2.3221 | 0.7518 | 0.199 | 0.2277 | 0.3982 | 0.2267 | -0.0004 | 0.0005 | 0.0007 | 0.0004 | 0.0004 | -0.0004 | 0.0065 | -0.0185 | -0.0066 | -370.535 | 2.9151 | -370.4243 | 2.757 | -370.6427 | 3.3319 | -370.7043 | 2.408 | -370.4273 | 2.7632 | -370.4489 | 1.8105
11:21 | 70 | 29.1833 | 18.6195 | 42.7061 | 50.2206 | -1.305 | -9.6112 | -0.6946 | -1.1245 | 0.113 | -0.0009 | 0.0385 | -0.9491 | 6.8311 | -0.0235 | 0.3794 | 0.367 | 0.3756 | 0.2457 | -16.1978 |  | -0.1316 | -0.7374 | -2.1986 | -1.5132 | 0.1677 |  | -0.251 | 0.0865 | 2.0024 | 1.7062 | 2.3253 | 0.7504 | 0.1678 | 0.2429 | 0.3589 | 0.2195 | -0.0002 | 0.0002 | 0.0003 | 0.0001 | -0.0002 | -0.0002 | -0.0104 | 0.0031 | -0.0169 | -370.5535 | 2.8597 | -370.3504 | 2.6995 | -370.5997 | 3.4284 | -370.6981 | 2.5024 | -370.4304 | 2.7447 | -370.3843 | 1.7776
11:21 | 71 | 29.1859 | 18.7779 | 42.8595 | 50.3408 | -1.3461 | -9.7275 | -0.7168 | -1.1824 | 0.0608 | 0.0428 | -0.002 | -1.1035 | 6.7849 | -0.0744 | 0.3796 | 0.3655 | 0.3737 | 0.2471 | -16.251 |  | -0.1585 | -0.8189 | -2.1823 | -1.465 | 0.0955 |  | -0.1237 | 0.1585 | 2.003 | 1.7024 | 2.3226 | 0.7467 | 0.1899 | 0.2245 | 0.3693 | 0.2071 | 0.0003 | 0.0002 | -0.0001 | -0.0003 | 0.0003 | -0.0007 | -0.0073 | 0.001 | 0.0033 | -370.5473 | 2.8391 | -370.3627 | 2.7242 | -370.6766 | 3.5331 | -370.6889 | 2.5907 | -370.3627 | 2.7365 | -370.4212 | 1.8084
11:21 | 72 | 29.1303 | 18.7139 | 43.1342 | 50.5581 | -1.2807 | -9.7473 | -0.6329 | -1.1695 | 0.0565 | -0.0449 | 0.007 | -0.9801 | 6.7655 | -0.0404 | 0.3787 | 0.3667 | 0.3745 | 0.2471 | -16.2247 |  | -0.1432 | -0.7991 | -2.1753 | -1.4001 | 0.1199 |  | -0.2197 | 0.1254 | 2.0053 | 1.7056 | 2.3266 | 0.7464 | 0.1589 | 0.2283 | 0.36 | 0.1882 | -0.0005 | 0.0002 | 0.0002 | 0.0004 | 0.0001 | 0 | 0.0045 | 0.0012 | -0.0036 | -370.5073 | 2.8125 | -370.3566 | 2.7118 | -370.6335 | 3.6112 | -370.6243 | 2.6646 | -370.3658 | 2.7468 | -370.4089 | 1.8043
11:21 | 73 | 29.1579 | 18.9401 | 43.3643 | 50.8039 | -1.407 | -9.9091 | -0.6774 | -1.1458 | -0.0052 | -0.1349 | -0.1026 | -0.9441 | 6.7702 | -0.0706 | 0.3786 | 0.3639 | 0.3735 | 0.2482 | -16.2244 |  | -0.2456 | -0.7815 | -2.1225 | -1.325 | 0.1491 |  | -0.2608 | 0.1628 | 2.0087 | 1.7051 | 2.3307 | 0.7442 | 0.1737 | 0.2256 | 0.3311 | 0.202 | -0.0003 | 0.0008 | 0.0004 | 0.0004 | 0.0007 | 0 | 0.0017 | -0.0122 | 0.0107 | -370.5381 | 2.8371 | -370.3935 | 2.6913 | -370.5904 | 3.7118 | -370.6181 | 2.7837 | -370.3689 | 2.7796 | -370.4273 | 1.7899
11:21 | 74 | 29.1267 | 18.9955 | 43.5996 | 51.0395 | -1.3851 | -10.0679 | -0.7197 | -1.0961 | 0.0534 | -0.0929 | 0.0103 | -0.9603 | 6.7662 | -0.0472 | 0.3791 | 0.3617 | 0.3741 | 0.2462 | -16.2157 |  | -0.1651 | -0.8115 | -2.183 | -1.4412 | 0.2036 |  | -0.3162 | 0.037 | 2.0134 | 1.7049 | 2.3347 | 0.7413 | 0.181 | 0.2273 | 0.3878 | 0.2219 | -0.0002 | 0.0003 | 0 | 0.0001 | 0 | -0.0005 | 0.0029 | -0.0142 | 0.0128 | -370.5812 | 2.7919 | -370.3012 | 2.6461 | -370.535 | 3.8165 | -370.5966 | 2.911 | -370.3719 | 2.7509 | -370.3289 | 1.7674
11:21 | 75 | 29.0812 | 19.1665 | 43.9764 | 51.3531 | -1.3872 | -10.2193 | -0.4782 | -1.1185 | -0.0246 | -0.1647 | -0.0849 | -0.9891 | 6.7408 | -0.1107 | 0.3784 | 0.3622 | 0.374 | 0.2467 | -16.3273 |  | -0.2653 | -0.7824 | -2.2146 | -1.4263 | 0.1894 |  | -0.3185 | -0.0111 | 2.0169 | 1.7071 | 2.3337 | 0.7363 | 0.216 | 0.2333 | 0.4017 | 0.2214 | 0.0001 | 0.0002 | 0.0005 | 0.0002 | 0.0001 | -0.0001 | 0.008 | -0.0132 | 0.0134 | -370.5566 | 2.7858 | -370.2919 | 2.6646 | -370.5073 | 3.9417 | -370.5997 | 3.0465 | -370.3658 | 2.7591 | -370.3381 | 1.7509
11:21 | 76 | 29.2599 | 19.3444 | 44.3536 | 51.7092 | -1.3017 | -10.2779 | -0.5575 | -1.1492 | -0.1279 | -0.2973 | -0.0744 | -0.9467 | 6.7592 | -0.1083 | 0.3793 | 0.3609 | 0.3737 | 0.2467 | -16.3198 |  | -0.2944 | -0.7695 | -2.2603 | -1.4785 | 0.1504 |  | -0.3673 | 0.0487 | 2.0196 | 1.7084 | 2.333 | 0.7319 | 0.238 | 0.2549 | 0.4457 | 0.2529 | 0.0001 | 0.0005 | 0.0008 | 0.0004 | 0.0002 | -0.0003 | -0.0043 | 0.0005 | -0.0145 | -370.5535 | 2.7775 | -370.3258 | 2.6544 | -370.4766 | 4.0239 | -370.5227 | 3.1225 | -370.3319 | 2.7611 | -370.3381 | 1.7694
11:21 | 77 | 29.2102 | 19.8207 | 45.2279 | 52.5552 | -1.1872 | -10.7505 | -0.5779 | -1.1794 | -0.1074 | -0.229 | -0.0859 | -1.01 | 6.7819 | -0.0919 | 0.3796 | 0.36 | 0.3763 | 0.2487 | -16.3832 |  | -0.4097 | -0.8835 | -2.2509 | -1.5134 | 0.1179 |  | -0.378 | -0.0113 | 2.0299 | 1.7098 | 2.3403 | 0.723 | 0.2585 | 0.2815 | 0.4272 | 0.2406 | -0.0003 | 0.0007 | 0 | 0 | -0.0004 | -0.0001 | -0.0037 | -0.0003 | 0.0157 | -370.6181 | 2.794 | -370.3535 | 2.6195 | -370.4181 | 4.1142 | -370.5012 | 3.2354 | -370.3012 | 2.8556 | -370.335 | 1.792
11:21 | 78 | 29.1404 | 20.4539 | 46.4368 | 53.7787 | -1.1814 | -11.3617 | -0.5667 | -1.0425 | -0.17 | -0.251 | -0.0374 | -1.0386 | 6.6479 | -0.1198 | 0.3799 | 0.3558 | 0.3705 | 0.2475 | -16.4564 |  | -0.4146 | -1.0091 | -2.3223 | -1.5389 | 0.0417 |  | -0.4168 | -0.0497 | 2.0412 | 1.7066 | 2.3487 | 0.7093 | 0.3574 | 0.3396 | 0.4654 | 0.2282 | 0.0002 | 0.0008 | 0.001 | 0.0004 | 0.0003 | -0.0006 | 0.006 | 0.0012 | -0.0011 | -370.5904 | 2.7344 | -370.2981 | 2.5887 | -370.3596 | 4.2087 | -370.4396 | 3.3442 | -370.3135 | 2.9274 | -370.2458 | 1.8741
11:21 | 79 | 29.0501 | 20.9431 | 47.7075 | 55.0257 | -1.2062 | -11.7978 | -0.5385 | -1.0149 | -0.1789 | -0.3953 | -0.0921 | -1.0694 | 6.6096 | -0.2071 | 0.3793 | 0.3574 | 0.3715 | 0.2455 | -16.5652 |  | -0.3572 | -0.8828 | -2.3325 | -1.5715 | -0.0213 |  | -0.4438 | -0.1976 | 2.0561 | 1.7073 | 2.3562 | 0.6942 | 0.3628 | 0.351 | 0.4631 | 0.2692 | 0 | 0.0002 | 0 | 0 | -0.0002 | -0.0005 | 0.008 | -0.0186 | -0.0049 | -370.575 | 2.6913 | -370.3073 | 2.5804 | -370.3473 | 4.3257 | -370.4181 | 3.4366 | -370.2181 | 3.0055 | -370.2273 | 1.9973
11:21 | 80 | 29.1153 | 21.6454 | 49.253 | 56.5239 | -1.3435 | -12.4787 | -0.6034 | -0.9836 | -0.1972 | -0.3628 | -0.0795 | -1.0714 | 6.5791 | -0.2726 | 0.379 | 0.3523 | 0.3728 | 0.2466 | -16.6689 |  | -0.3432 | -0.9006 | -2.457 | -1.7816 | -0.0566 |  | -0.5783 | -0.351 | 2.0776 | 1.7107 | 2.3685 | 0.6708 | 0.3603 | 0.3718 | 0.5093 | 0.2681 | -0.0001 | -0.0002 | 0 | 0.0001 | 0.0001 | -0.0008 | 0.0126 | -0.0201 | -0.031 | -370.4581 | 2.7755 | -370.2612 | 2.6646 | -370.3412 | 4.4181 | -370.3781 | 3.5352 | -370.0981 | 3.0691 | -370.1442 | 2.0733
11:21 | 81 | 29.1264 | 22.5461 | 50.9892 | 58.2537 | -1.2997 | -13.2704 | -0.735 | -1.0625 | -0.2584 | -0.3973 | -0.1701 | -1.2886 | 6.4607 | -0.322 | 0.3796 | 0.3529 | 0.3709 | 0.2443 | -16.9404 |  | -0.3854 | -0.8277 | -2.5247 | -1.7846 | 0.0369 |  | -0.6502 | -0.2404 | 2.0996 | 1.7152 | 2.3883 | 0.6416 | 0.3656 | 0.4347 | 0.558 | 0.2433 | -0.0006 | 0.0008 | 0.0006 | 0.0003 | 0.0003 | -0.0004 | -0.0038 | 0.0063 | -0.0089 | -370.4181 | 2.9398 | -370.2673 | 2.7591 | -370.2642 | 4.4941 | -370.3227 | 3.6194 | -370.0273 | 3.1697 | -370.0765 | 2.1164
11:21 | 82 | 29.24 | 23.2998 | 52.5514 | 59.9844 | -1.2975 | -13.8195 | -0.7101 | -1.093 | -0.2663 | -0.619 | -0.2355 | -1.2238 | 6.4493 | -0.4081 | 0.3813 | 0.3547 | 0.3738 | 0.2469 | -17.8113 |  | -0.4443 | -0.9058 | -2.5893 | -1.9399 | 0.0244 |  | -0.6426 | -0.3694 | 2.1179 | 1.7163 | 2.3991 | 0.6227 | 0.416 | 0.4969 | 0.6274 | 0.3012 | -0.0005 | 0.0003 | 0 | 0.0001 | 0.0002 | -0.0005 | 0.0166 | -0.0136 | 0.0108 | -370.3258 | 3.0896 | -370.2827 | 2.8987 | -370.1966 | 4.5741 | -370.3135 | 3.7036 | -370.0058 | 3.2477 | -370.0212 | 2.2006
11:21 | 83 | 29.1623 | 24.1352 | 54.3885 | 61.7681 | -1.1002 | -14.2115 | -0.662 | -1.189 | -0.3812 | -0.6729 | -0.3184 | -1.1907 | 6.4254 | -0.3344 | 0.3797 | 0.3498 | 0.3726 | 0.2456 | -18.5743 |  | -0.4157 | -0.8722 | -2.6698 | -2.0223 | -0.0571 |  | -0.6198 | -0.364 | 2.1298 | 1.722 | 2.4095 | 0.6113 | 0.5169 | 0.5339 | 0.7027 | 0.4178 | 0.0002 | 0.0007 | 0.0006 | 0.0009 | 0.0001 | -0.0003 | -0.0012 | -0.0096 | -0.0051 | -370.215 | 3.1903 | -370.2489 | 3.0198 | -370.1873 | 4.6173 | -370.2396 | 3.7836 | -369.895 | 3.3052 | -369.9011 | 2.2622
11:21 | 84 | 29.3322 | 25.0241 | 56.2032 | 63.624 | -1.1842 | -14.6777 | -0.7809 | -1.2047 | -0.456 | -0.7945 | -0.4045 | -1.2593 | 6.4139 | -0.4582 | 0.3806 | 0.3521 | 0.3706 | 0.2466 | -19.3548 |  | -0.3381 | -0.8493 | -2.6803 | -2.055 | 0.0059 |  | -0.6861 | -0.4332 | 2.1431 | 1.7323 | 2.4184 | 0.5987 | 0.5508 | 0.6776 | 0.7548 | 0.5033 | 0.0001 | 0 | 0.0004 | 0.0005 | 0 | -0.0003 | 0.0053 | -0.0001 | -0.0186 | -370.1165 | 3.2806 | -370.2427 | 3.143 | -370.1289 | 4.6994 | -370.2027 | 3.8514 | -369.8027 | 3.3915 | -369.8611 | 2.3382
11:21 | 85 | 29.3796 | 25.9185 | 58.0566 | 65.5162 | -1.0041 | -15.1547 | -0.6712 | -1.1303 | -0.516 | -0.7948 | -0.43 | -1.3544 | 6.2934 | -0.6065 | 0.3803 | 0.3505 | 0.3705 | 0.2465 | -20.2985 |  | -0.3426 | -0.8475 | -2.7382 | -2.0119 | -0.0687 |  | -0.7391 | -0.3979 | 2.162 | 1.7409 | 2.4328 | 0.5886 | 0.5951 | 0.745 | 0.7988 | 0.5303 | -0.0005 | 0.0003 | 0.0001 | 0.0004 | 0.0006 | 0.0001 | -0.0078 | -0.0013 | -0.0197 | -370.0058 | 3.3791 | -370.2119 | 3.2416 | -370.055 | 4.7815 | -370.1504 | 3.9315 | -369.7442 | 3.4777 | -369.7411 | 2.408
11:21 | 86 | 29.3963 | 26.8229 | 59.991 | 67.4083 | -0.8924 | -15.5727 | -0.6587 | -1.0363 | -0.5035 | -0.8038 | -0.3141 | -1.3952 | 6.2614 | -0.5304 | 0.3809 | 0.3524 | 0.3694 | 0.2463 | -21.7106 |  | -0.3397 | -0.7425 | -2.7738 | -2.0071 | 0.0367 |  | -0.7552 | -0.4821 | 2.1755 | 1.7535 | 2.4284 | 0.5785 | 0.6232 | 0.7788 | 0.8798 | 0.5465 | -0.0002 | 0.0005 | 0.0002 | 0.0003 | -0.0001 | 0 | 0.0027 | -0.0064 | -0.0118 | -369.9165 | 3.4654 | -370.2181 | 3.336 | -370.015 | 4.8534 | -370.0673 | 4.0198 | -369.6427 | 3.566 | -369.6765 | 2.4921
11:21 | 87 | 29.4451 | 27.7237 | 61.7333 | 69.0899 | -0.8715 | -15.9293 | -0.6254 | -1.0456 | -0.4597 | -0.8734 | -0.2905 | -1.4345 | 6.2649 | -0.536 | 0.3827 | 0.353 | 0.3715 | 0.2464 | -23.2034 |  | -0.3823 | -0.8693 | -2.8921 | -2.1899 | -0.1546 |  | -0.715 | -0.4361 | 2.1863 | 1.766 | 2.4312 | 0.5737 | 0.7533 | 0.8741 | 0.9574 | 0.6246 | -0.0004 | 0.0002 | -0.0004 | -0.0006 | 0.0003 | -0.0008 | 0.0072 | -0.0111 | 0.0004 | -369.8704 | 3.5434 | -370.2242 | 3.4223 | -369.9688 | 4.9437 | -370.055 | 4.1142 | -369.5811 | 3.6522 | -369.6211 | 2.5804
11:21 | 88 | 29.4623 | 28.5063 | 63.4482 | 70.7517 | -0.9284 | -16.2029 | -0.6763 | -0.9471 | -0.4176 | -0.8247 | -0.3238 | -1.4154 | 6.2401 | -0.6321 | 0.381 | 0.3514 | 0.3715 | 0.2456 | -24.0227 |  | -0.3564 | -0.7868 | -2.9138 | -2.2351 | -0.1264 |  | -0.7496 | -0.4322 | 2.1996 | 1.7738 | 2.4389 | 0.5684 | 0.7491 | 0.8758 | 0.9342 | 0.6558 | 0.0001 | 0.0003 | 0.0001 | 0.0003 | -0.0001 | -0.0001 | -0.0003 | 0.0067 | -0.003 | -369.8088 | 3.605 | -370.1289 | 3.4757 | -369.9381 | 5.0258 | -369.9935 | 4.1635 | -369.4857 | 3.72 | -369.4919 | 2.6482
11:21 | 89 | 29.4585 | 29.2308 | 64.8695 | 72.3354 | -0.8761 | -16.2997 | -0.6162 | -0.9751 | -0.4769 | -0.9173 | -0.3069 | -1.4384 | 6.2268 | -0.6545 | 0.3807 | 0.3491 | 0.3705 | 0.2465 | -24.7888 |  | -0.2975 | -0.7352 | -2.9738 | -2.2869 | -0.1244 |  | -0.8458 | -0.4737 | 2.2112 | 1.7763 | 2.4418 | 0.5611 | 0.7654 | 0.9211 | 1.0603 | 0.6953 | -0.0002 | -0.0001 | 0.001 | 0.001 | 0.0001 | -0.0008 | 0.0035 | -0.0144 | -0.0073 | -369.7411 | 3.6625 | -370.1104 | 3.5475 | -369.935 | 5.0916 | -369.9719 | 4.2764 | -369.3996 | 3.7877 | -369.4396 | 2.716
11:21 | 90 | 29.4488 | 29.8758 | 66.4636 | 73.7986 | -0.8108 | -16.7062 | -0.6261 | -1.1348 | -0.6028 | -1.0359 | -0.4182 | -1.4421 | 6.2176 | -0.709 | 0.3806 | 0.3494 | 0.3739 | 0.2464 | -25.5035 |  | -0.3724 | -0.9104 | -2.9932 | -2.3237 | -0.1717 |  | -0.8842 | -0.5703 | 2.2241 | 1.7843 | 2.4431 | 0.5909 | 0.8318 | 1.0164 | 1.1205 | 0.6809 | -0.0007 | 0.0003 | 0.0003 | 0.0005 | 0 | -0.0004 | 0.002 | -0.0235 | -0.0058 | -369.7042 | 3.7097 | -370.1412 | 3.6009 | -369.8458 | 5.1388 | -369.9073 | 4.3421 | -369.3473 | 3.8596 | -369.3473 | 2.7858
11:21 | 91 | 29.3856 | 30.4697 | 67.9775 | 75.198 | -0.7706 | -16.9365 | -0.6221 | -1.1745 | -0.6675 | -1.043 | -0.4426 | -1.3717 | 6.2946 | -0.6303 | 0.3806 | 0.3498 | 0.374 | 0.2461 | -26.1132 |  | -0.3965 | -0.9986 | -3.1281 | -2.4999 | -0.2777 |  | -0.9152 | -0.5755 | 2.2342 | 1.79 | 2.4479 | 0.6119 | 0.8806 | 1.0881 | 1.1426 | 0.7633 | -0.0003 | 0.0002 | 0 | 0.0004 | -0.0001 | -0.0002 | -0.009 | -0.0016 | -0.022 | -369.6734 | 3.7939 | -370.1104 | 3.6296 | -369.7873 | 5.2127 | -369.8919 | 4.414 | -369.298 | 3.9705 | -369.3196 | 2.8453
11:21 | 92 | 29.3612 | 31.1761 | 69.4899 | 76.6388 | -0.8623 | -17.2818 | -0.6286 | -1.1768 | -0.6955 | -1.3051 | -0.4757 | -1.4991 | 6.1215 | -0.7545 | 0.3809 | 0.3457 | 0.3729 | 0.2462 | -26.7881 |  | -0.3568 | -0.9467 | -3.0802 | -2.4818 | -0.1657 |  | -0.9677 | -0.6072 | 2.2423 | 1.7915 | 2.4489 | 0.6039 | 0.9269 | 1.0881 | 1.241 | 0.7979 | 0.0002 | 0.0003 | 0.0003 | 0.0004 | 0.0001 | -0.0007 | -0.0059 | -0.0006 | 0.0074 | -369.6273 | 3.8042 | -370.0612 | 3.6522 | -369.7657 | 5.2702 | -369.7934 | 4.4982 | -369.2149 | 4.0321 | -369.1995 | 2.909
11:21 | 93 | 29.3827 | 31.9888 | 71.058 | 78.3563 | -0.9044 | -17.4736 | -0.6569 | -1.1228 | -0.7051 | -1.1742 | -0.4974 | -1.4665 | 6.1812 | -0.6821 | 0.3796 | 0.3457 | 0.3731 | 0.2455 | -27.1121 |  | -0.4188 | -0.9154 | -3.151 | -2.48 | -0.1803 |  | -0.9935 | -0.644 | 2.2528 | 1.8014 | 2.4479 | 0.6031 | 0.9543 | 1.1732 | 1.3453 | 0.8939 | 0.0001 | 0.0001 | -0.0003 | -0.0003 | 0.0001 | -0.0001 | 0.003 | 0.0003 | -0.0083 | -369.5596 | 3.8103 | -370.0888 | 3.6933 | -369.7504 | 5.3605 | -369.7719 | 4.568 | -369.1442 | 4.0937 | -369.1534 | 3.0137
11:21 | 94 | 29.3052 | 32.6688 | 72.6742 | 79.8859 | -0.8903 | -17.6155 | -0.657 | -1.1156 | -0.7824 | -1.1406 | -0.4298 | -1.4469 | 6.0807 | -0.7058 | 0.3815 | 0.3469 | 0.3724 | 0.248 | -27.3793 |  | -0.4412 | -0.93 | -3.1706 | -2.4885 | -0.2376 |  | -1.0424 | -0.6923 | 2.2614 | 1.8064 | 2.449 | 0.6688 | 0.9644 | 1.2585 | 1.3417 | 0.8702 | -0.0005 | -0.0001 | 0.0005 | 0.0009 | 0.0003 | -0.0005 | 0.0075 | -0.0204 | 0.0208 | -369.5134 | 3.798 | -370.0335 | 3.7159 | -369.7257 | 5.4406 | -369.7227 | 4.6296 | -368.9965 | 4.1614 | -369.098 | 3.0937
11:21 | 95 | 29.3044 | 33.372 | 74.1532 | 81.3028 | -0.9168 | -17.7155 | -0.613 | -1.1429 | -0.8064 | -1.1392 | -0.4495 | -1.5179 | 6.1088 | -0.7617 | 0.3824 | 0.3469 | 0.3707 | 0.2467 | -28.1041 |  | -0.5213 | -0.9003 | -3.207 | -2.4747 | -0.2221 |  | -1.1053 | -0.6938 | 2.2715 | 1.8148 | 2.4543 | 0.6605 | 1.0491 | 1.2739 | 1.3278 | 0.8857 | -0.0002 | 0.0008 | 0.0002 | 0.0003 | -0.0006 | -0.0004 | -0.0045 | -0.0118 | -0.0155 | -369.4734 | 3.8452 | -370.0396 | 3.7097 | -369.6611 | 5.5309 | -369.6734 | 4.6953 | -368.978 | 4.2826 | -369.0334 | 3.1779
11:21 | 96 | 29.1841 | 34.0659 | 75.4942 | 82.772 | -0.9162 | -17.7648 | -0.7423 | -1.1923 | -0.8732 | -1.354 | -0.5691 | -1.6185 | 6.0682 | -0.8084 | 0.3818 | 0.3463 | 0.3736 | 0.2466 | -28.4946 |  | -0.486 | -0.9126 | -3.2108 | -2.4597 | -0.1499 |  | -1.0453 | -0.7563 | 2.2822 | 1.8197 | 2.4547 | 0.6474 | 1.1289 | 1.3074 | 1.4353 | 0.9369 | -0.0003 | 0.0001 | 0.0005 | 0.0007 | 0.0003 | -0.0006 | 0.0023 | -0.0022 | 0.0168 | -369.5042 | 3.837 | -369.9658 | 3.7056 | -369.5934 | 5.6028 | -369.6734 | 4.8164 | -368.9257 | 4.3421 | -368.9411 | 3.2293
11:21 | 97 | 29.2607 | 34.7712 | 77.2004 | 84.4277 | -0.9798 | -17.2216 | -0.5681 | -1.21 | -0.9193 | -1.2968 | -0.5405 | -1.5427 | 6.0089 | -0.7805 | 0.3842 | 0.3485 | 0.3718 | 0.2483 | -28.967 |  | -0.54 | -0.8754 | -3.2225 | -2.5239 | -0.1905 |  | -1.091 | -0.7957 | 2.2931 | 1.8334 | 2.4539 | 0.6363 | 1.1261 | 1.374 | 1.5083 | 0.9917 | 0 | -0.0003 | 0.0007 | 0.0009 | -0.0004 | -0.0002 | -0.0121 | 0.0063 | 0 | -369.5073 | 3.835 | -369.9258 | 3.6933 | -369.535 | 5.6993 | -369.6304 | 4.9129 | -368.9134 | 4.4284 | -368.8334 | 3.3073
11:21 | 98 | 29.2904 | 35.5103 | 78.7824 | 85.9731 | -0.9047 | -16.9854 | -0.7083 | -1.1534 | -0.875 | -1.2997 | -0.5837 | -1.5539 | 6.0012 | -0.8025 | 0.383 | 0.3448 | 0.3709 | 0.2475 | -29.5433 |  | -0.5914 | -1.0562 | -3.2991 | -2.598 | -0.2776 |  | -1.1917 | -0.8597 | 2.3028 | 1.8416 | 2.4568 | 0.6284 | 1.1206 | 1.4551 | 1.5327 | 1.0435 | 0.0001 | -0.0002 | 0.0004 | 0.0007 | 0.0002 | -0.0005 | -0.0033 | 0.0051 | -0.0038 | -369.4119 | 3.8309 | -369.9319 | 3.7138 | -369.498 | 5.7773 | -369.5934 | 4.9909 | -368.7534 | 4.5105 | -368.7749 | 3.3956
11:21 | 99 | 29.2465 | 36.2939 | 80.3585 | 87.4787 | -1.0098 | -16.9836 | -0.6645 | -1.077 | -0.8414 | -1.3057 | -0.5392 | -1.6453 | 6.01 | -0.7805 | 0.3825 | 0.3481 | 0.3738 | 0.2464 | -30.0356 |  | -0.5212 | -1.1249 | -3.3943 | -2.691 | -0.2655 |  | -1.1706 | -0.8659 | 2.3124 | 1.8448 | 2.4615 | 0.6201 | 1.2119 | 1.4769 | 1.5978 | 1.0816 | -0.0001 | 0.0004 | 0.0004 | 0.0009 | 0.0003 | 0 | 0.0024 | -0.0144 | 0.0086 | -369.3657 | 3.8617 | -369.9473 | 3.7282 | -369.4611 | 5.843 | -369.4826 | 5.0443 | -368.7041 | 4.6296 | -368.7195 | 3.4839
11:21 | 100 | 29.2048 | 36.9474 | 81.8187 | 88.9209 | -1.1145 | -17.1393 | -0.7041 | -1.1209 | -0.9876 | -1.3142 | -0.5644 | -1.5608 | 6.0497 | -0.84 | 0.3804 | 0.348 | 0.373 | 0.2451 | -30.4343 |  | -0.4943 | -1.1443 | -3.4259 | -2.7651 | -0.2062 |  | -1.1789 | -0.8372 | 2.3215 | 1.8506 | 2.4657 | 0.6196 | 1.273 | 1.5496 | 1.6855 | 1.0743 | 0.0001 | 0.0002 | 0.0004 | 0.0009 | -0.0005 | -0.0004 | -0.0097 | -0.011 | -0.0075 | -369.3657 | 3.8719 | -369.9565 | 3.7241 | -369.4242 | 5.9067 | -369.4303 | 5.1326 | -368.6641 | 4.722 | -368.7134 | 3.568
11:21 | 101 | 29.1686 | 37.5332 | 83.1929 | 90.264 | -1.1417 | -17.2342 | -0.7569 | -1.116 | -1.049 | -1.4461 | -0.5523 | -1.6214 | 5.9691 | -0.8928 | 0.3818 | 0.3466 | 0.3746 | 0.2476 | -30.8319 |  | -0.5414 | -1.2443 | -3.537 | -2.84 | -0.2774 |  | -1.2209 | -0.9963 | 2.3293 | 1.8579 | 2.4771 | 0.6233 | 1.2926 | 1.6501 | 1.7065 | 1.1049 | 0.0002 | 0 | 0.0002 | 0.0005 | 0.0006 | -0.0003 | 0.0077 | -0.0073 | 0.0003 | -369.3411 | 3.8473 | -369.8827 | 3.7077 | -369.3842 | 6.0114 | -369.4057 | 5.2168 | -368.5872 | 4.7712 | -368.578 | 3.6235
11:21 | 102 | 29.0993 | 38.0786 | 84.5894 | 91.5368 | -1.1202 | -17.3784 | -0.6943 | -1.1403 | -1.1062 | -1.478 | -0.6649 | -1.7793 | 5.8704 | -0.9312 | 0.3816 | 0.3457 | 0.37 | 0.2459 | -31.2355 |  | -0.5618 | -1.094 | -3.4991 | -2.8208 | -0.2983 |  | -1.1743 | -0.9169 | 2.3368 | 1.8669 | 2.4796 | 0.6212 | 1.3142 | 1.6834 | 1.7375 | 1.1909 | -0.0002 | -0.0001 | 0.0002 | 0.0007 | -0.0003 | -0.0005 | 0.0092 | -0.0122 | -0.0039 | -369.2796 | 3.8165 | -369.8334 | 3.7446 | -369.3473 | 6.1038 | -369.4303 | 5.2763 | -368.4426 | 4.8308 | -368.5103 | 3.722
11:21 | 103 | 29.0071 | 38.5935 | 85.6399 | 92.7107 | -1.0951 | -17.4649 | -0.6698 | -1.2225 | -1.1705 | -1.5271 | -0.7743 | -1.7578 | 5.7964 | -0.8877 | 0.3795 | 0.3439 | 0.371 | 0.2465 | -31.6641 |  | -0.558 | -1.0617 | -3.5525 | -2.7859 | -0.3396 |  | -1.2515 | -0.9617 | 2.3425 | 1.8704 | 2.4858 | 0.6145 | 1.3417 | 1.6818 | 1.7493 | 1.2292 | -0.0002 | 0.0002 | 0.0007 | 0.0007 | 0.0004 | -0.0004 | 0.0018 | -0.0066 | 0.0025 | -369.2888 | 3.837 | -369.8211 | 3.7344 | -369.3349 | 6.149 | -369.3442 | 5.3236 | -368.3872 | 4.8944 | -368.4333 | 3.7836
11:21 | 104 | 28.9547 | 38.9769 | 86.6316 | 93.6046 | -1.2617 | -17.6773 | -0.6967 | -1.1559 | -1.1222 | -1.5059 | -0.7305 | -1.7525 | 5.8533 | -0.9695 | 0.3818 | 0.3436 | 0.3748 | 0.2477 | -32.1132 |  | -0.4959 | -1.0955 | -3.501 | -2.7823 | -0.2992 |  | -1.2162 | -0.8882 | 2.349 | 1.8756 | 2.4933 | 0.6105 | 1.3635 | 1.6922 | 1.8105 | 1.2168 | -0.0004 | 0.0002 | 0.0007 | 0.0008 | 0.0001 | -0.0002 | 0.0127 | -0.008 | -0.0006 | -369.3226 | 3.8617 | -369.8242 | 3.7282 | -369.2765 | 6.19 | -369.3534 | 5.4098 | -368.4241 | 4.9786 | -368.3903 | 3.8165
11:21 | 105 | 28.8766 | 39.4239 | 87.5997 | 94.5918 | -1.2652 | -17.6874 | -0.6203 | -1.1509 | -1.1454 | -1.5851 | -0.8018 | -1.621 | 5.8465 | -0.9813 | 0.3827 | 0.3462 | 0.3741 | 0.2485 | -32.3455 |  | -0.4449 | -1.0728 | -3.5026 | -2.8817 | -0.2553 |  | -1.2753 | -1.048 | 2.3542 | 1.8829 | 2.4987 | 0.6052 | 1.4051 | 1.7625 | 1.8696 | 1.2235 | 0 | 0.0001 | 0.0005 | 0.0008 | 0.0004 | -0.0004 | 0.0075 | -0.0165 | -0.0167 | -369.3072 | 3.8719 | -369.7719 | 3.7097 | -369.2119 | 6.2373 | -369.3011 | 5.4714 | -368.3626 | 5.0135 | -368.3379 | 3.8411
11:21 | 106 | 28.8087 | 39.8267 | 88.4823 | 95.596 | -1.3292 | -17.979 | -0.5871 | -1.045 | -1.0953 | -1.5902 | -0.6987 | -1.683 | 5.7557 | -1.011 | 0.3816 | 0.3455 | 0.374 | 0.2474 | -32.6311 |  | -0.4094 | -1.1249 | -3.5436 | -2.884 | -0.3297 |  | -1.2822 | -1.0073 | 2.36 | 1.8874 | 2.5022 | 0.6001 | 1.4324 | 1.79 | 1.8832 | 1.2287 | -0.0001 | -0.0002 | 0 | 0.0004 | 0.0004 | 0 | 0.0034 | -0.0156 | 0.0003 | -369.2796 | 3.8617 | -369.7719 | 3.7446 | -369.218 | 6.3009 | -369.3226 | 5.5084 | -368.3256 | 5.0833 | -368.3102 | 3.913
11:21 | 107 | 28.7618 | 40.2301 | 89.3633 | 96.5745 | -1.4542 | -18.0845 | -0.683 | -1.0841 | -1.1957 | -1.5734 | -0.7073 | -1.6872 | 5.8885 | -1.1133 | 0.3824 | 0.3447 | 0.3753 | 0.2496 | -32.9967 |  | -0.4976 | -1.0977 | -3.5997 | -2.9188 | -0.3316 |  | -1.3685 | -0.9644 | 2.3647 | 1.8956 | 2.505 | 0.5969 | 1.4888 | 1.8347 | 1.9181 | 1.2612 | -0.0003 | 0 | 0 | 0.0008 | 0.0001 | -0.0002 | -0.0075 | -0.0103 | -0.0097 | -369.2642 | 3.876 | -369.7688 | 3.7611 | -369.218 | 6.3235 | -369.2211 | 5.5392 | -368.2395 | 5.1367 | -368.2795 | 3.9849
11:22 | 108 | 28.7809 | 40.685 | 90.651 | 97.5567 | -1.5536 | -18.2328 | -0.7364 | -1.1218 | -1.253 | -1.6674 | -0.7309 | -1.6676 | 5.7891 | -1.0925 | 0.3816 | 0.3438 | 0.3699 | 0.2485 | -33.2708 |  | -0.4039 | -1.1139 | -3.6537 | -2.9152 | -0.268 |  | -1.2987 | -1.1319 | 2.3713 | 1.9033 | 2.5114 | 0.5958 | 1.4858 | 1.8664 | 1.9435 | 1.3161 | -0.0005 | 0 | 0.0003 | 0.0007 | 0.0003 | -0.0002 | -0.002 | -0.0064 | -0.0168 | -369.2549 | 3.8699 | -369.8027 | 3.7713 | -369.178 | 6.3769 | -369.1842 | 5.6069 | -368.2302 | 5.2147 | -368.2826 | 4.0403
11:22 | 109 | 28.6115 | 41.0987 | 91.6233 | 98.6552 | -1.6902 | -18.4048 | -0.6035 | -1.0749 | -1.2203 | -1.608 | -0.7468 | -1.7306 | 5.7835 | -1.1268 | 0.3828 | 0.3441 | 0.373 | 0.2487 | -33.4536 |  | -0.4536 | -1.1652 | -3.606 | -2.9621 | -0.3188 |  | -1.2605 | -1.0007 | 2.3769 | 1.9084 | 2.5155 | 0.6545 | 1.515 | 1.8955 | 2.0085 | 1.42 | -0.0003 | -0.0002 | 0.0002 | 0.0005 | -0.0001 | -0.0003 | 0.0096 | -0.0119 | 0.0023 | -369.218 | 3.8329 | -369.7288 | 3.7385 | -369.0918 | 6.459 | -369.2026 | 5.6747 | -368.1441 | 5.2435 | -368.1779 | 4.0998
11:22 | 110 | 28.6036 | 41.6362 | 92.7234 | 99.8991 | -1.7628 | -18.6486 | -0.7022 | -1.0927 | -1.2417 | -1.6786 | -0.7417 | -1.6725 | 5.7946 | -1.0467 | 0.3824 | 0.3438 | 0.3739 | 0.2475 | -33.7396 |  | -0.413 | -1.1322 | -3.6354 | -3.0454 | -0.3041 |  | -1.3875 | -1.124 | 2.3858 | 1.9143 | 2.5128 | 0.6728 | 1.5467 | 1.9619 | 2.1265 | 1.4287 | 0.0001 | -0.0002 | 0.0006 | 0.0001 | 0 | -0.0007 | 0.0101 | -0.0066 | -0.0023 | -369.178 | 3.8124 | -369.6765 | 3.7118 | -369.1103 | 6.5596 | -369.1842 | 5.7424 | -368.0641 | 5.3112 | -368.0918 | 4.143
11:22 | 111 | 28.5819 | 42.0522 | 93.648 | 100.8079 | -1.7778 | -18.8459 | -0.7887 | -1.1233 | -1.333 | -1.8256 | -0.8058 | -1.6147 | 5.8039 | -1.0436 | 0.383 | 0.3466 | 0.37 | 0.2465 | -34.0307 |  | -0.3836 | -1.185 | -3.7184 | -3.099 | -0.3455 |  | -1.4917 | -1.0933 | 2.3915 | 1.92 | 2.5136 | 0.6659 | 1.6038 | 2.0074 | 2.1035 | 1.4276 | -0.0004 | -0.0003 | 0.0003 | 0.0004 | -0.0004 | -0.0004 | 0.0127 | 0.0016 | -0.0031 | -369.1811 | 3.8062 | -369.6519 | 3.7344 | -369.1165 | 6.5986 | -369.0949 | 5.7979 | -368.0333 | 5.3728 | -368.0179 | 4.2312
11:22 | 112 | 28.5271 | 42.4045 | 94.6211 | 101.7088 | -1.7324 | -18.9173 | -0.7318 | -1.048 | -1.2944 | -1.6211 | -0.8009 | -1.7017 | 5.6696 | -1.2245 | 0.382 | 0.3462 | 0.3718 | 0.2478 | -34.2558 |  | -0.5531 | -1.2394 | -3.6209 | -3.0388 | -0.344 |  | -1.378 | -1.1384 | 2.3967 | 1.9225 | 2.5232 | 0.6608 | 1.6333 | 2.0368 | 2.1119 | 1.4678 | -0.0001 | 0.0003 | 0.0004 | 0.0005 | 0.0004 | -0.0006 | 0.0076 | -0.0228 | -0.0061 | -369.2211 | 3.8226 | -369.6796 | 3.6974 | -368.9872 | 6.6438 | -369.0826 | 5.8554 | -368.0241 | 5.4427 | -368.0271 | 4.2559
11:22 | 113 | 28.3711 | 42.8368 | 95.5574 | 102.6643 | -1.8955 | -19.1639 | -0.7534 | -1.0451 | -1.42 | -1.7567 | -0.7809 | -1.7813 | 5.6653 | -1.2447 | 0.3822 | 0.3486 | 0.3718 | 0.2472 | -34.6022 |  | -0.6073 | -1.1828 | -3.6249 | -3.0538 | -0.357 |  | -1.418 | -1.1089 | 2.4034 | 1.9468 | 2.5263 | 0.6555 | 1.6556 | 2.0534 | 2.1427 | 1.4624 | -0.0007 | -0.0003 | 0.0003 | 0.001 | 0.0001 | -0.0001 | -0.0046 | -0.0069 | 0.0011 | -369.2303 | 3.8432 | -369.6242 | 3.7015 | -368.9872 | 6.6931 | -369.0795 | 5.9375 | -367.9779 | 5.5063 | -367.981 | 4.2846
11:22 | 114 | 28.3056 | 43.3764 | 96.6325 | 103.7351 | -1.9494 | -19.3465 | -0.6554 | -1.0406 | -1.4864 | -1.728 | -0.6811 | -1.6695 | 5.7267 | -1.1737 | 0.3832 | 0.3456 | 0.3712 | 0.2459 | -34.873 |  | -0.6064 | -1.1564 | -3.7403 | -3.0925 | -0.2934 |  | -1.4142 | -1.0696 | 2.4113 | 1.9555 | 2.5347 | 0.6497 | 1.6689 | 2.0667 | 2.1843 | 1.4702 | -0.0002 | -0.0005 | 0 | 0.0003 | 0 | -0.001 | -0.0062 | -0.0081 | -0.0322 | -369.178 | 3.837 | -369.5688 | 3.7118 | -368.9411 | 6.767 | -369.0241 | 5.9478 | -367.9133 | 5.5453 | -367.9164 | 4.3421
11:22 | 115 | 28.2611 | 43.8088 | 97.6853 | 104.744 | -2.0066 | -19.627 | -0.7513 | -1.0177 | -1.4659 | -1.7752 | -0.7856 | -1.7147 | 5.6943 | -1.2438 | 0.3824 | 0.3468 | 0.3695 | 0.246 | -35.1665 |  | -0.5201 | -1.1115 | -3.673 | -3.1585 | -0.3814 |  | -1.4658 | -1.1264 | 2.4171 | 1.9538 | 2.5363 | 0.6418 | 1.6845 | 2.0938 | 2.2411 | 1.5029 | -0.0001 | -0.0005 | 0 | 0.0008 | 0 | -0.0001 | 0.0046 | 0.0035 | 0.0005 | -369.1903 | 3.8452 | -369.6119 | 3.7713 | -369.0088 | 6.804 | -368.9565 | 6.0052 | -367.8364 | 5.5925 | -367.9102 | 4.4407
11:22 | 116 | 28.2165 | 44.3348 | 98.8783 | 105.9259 | -2.0188 | -19.7551 | -0.8479 | -0.9799 | -1.4791 | -1.8168 | -0.8159 | -1.7086 | 5.6364 | -1.2865 | 0.3842 | 0.3449 | 0.3722 | 0.2463 | -35.5706 |  | -0.4484 | -1.1159 | -3.6409 | -3.1761 | -0.3205 |  | -1.4747 | -1.1619 | 2.4234 | 1.9474 | 2.5394 | 0.6352 | 1.6953 | 2.1683 | 2.2991 | 1.5769 | -0.0001 | 0.0001 | 0.0004 | 0.0011 | 0.0002 | -0.0002 | -0.0018 | -0.0153 | -0.0062 | -369.1411 | 3.8596 | -369.578 | 3.7734 | -368.9164 | 6.8553 | -368.9226 | 6.0443 | -367.8179 | 5.6603 | -367.8394 | 4.4817
11:22 | 117 | 28.0409 | 44.8321 | 100.0275 | 107.1096 | -2.1604 | -19.9458 | -0.8632 | -0.9639 | -1.5342 | -1.8863 | -0.8507 | -1.7802 | 5.6784 | -1.3009 | 0.382 | 0.3421 | 0.3707 | 0.2467 | -35.9963 |  | -0.527 | -1.0877 | -3.6733 | -3.1366 | -0.295 |  | -1.4823 | -1.1484 | 2.4304 | 1.9441 | 2.5439 | 0.6292 | 1.7243 | 2.2203 | 2.2933 | 1.5884 | 0 | 0.0004 | 0.0001 | 0.001 | 0.0004 | -0.0004 | 0.0101 | -0.0182 | 0.0052 | -369.1811 | 3.8822 | -369.5165 | 3.7795 | -368.8457 | 6.9374 | -368.938 | 6.1305 | -367.7594 | 5.7239 | -367.7748 | 4.5269
11:22 | 118 | 27.9602 | 45.4082 | 101.4205 | 108.3616 | -2.2614 | -20.1353 | -0.7952 | -0.9523 | -1.6313 | -1.9197 | -0.8543 | -1.6986 | 5.5603 | -1.3442 | 0.384 | 0.3465 | 0.3767 | 0.247 | -36.488 |  | -0.6005 | -1.1355 | -3.7852 | -3.1148 | -0.3341 |  | -1.5492 | -1.1868 | 2.4389 | 1.952 | 2.5532 | 0.6274 | 1.8349 | 2.2442 | 2.299 | 1.6299 | -0.0002 | -0.0002 | 0.0005 | 0.0011 | 0.0003 | 0.0002 | 0.0149 | -0.0132 | -0.0009 | -369.1688 | 3.9068 | -369.3965 | 3.7877 | -368.858 | 7.0113 | -368.9257 | 6.2065 | -367.7164 | 5.7671 | -367.6517 | 4.5721
11:22 | 119 | 27.897 | 45.9621 | 102.898 | 109.839 | -2.2961 | -20.5051 | -0.798 | -0.9626 | -1.6843 | -1.9698 | -0.9824 | -1.6632 | 5.5376 | -1.3225 | 0.3835 | 0.3446 | 0.3723 | 0.2452 | -36.9523 |  | -0.5902 | -1.1309 | -3.8008 | -3.1504 | -0.3226 |  | -1.5602 | -1.169 | 2.4483 | 1.9625 | 2.5565 | 0.623 | 1.8509 | 2.3063 | 2.415 | 1.6798 | 0.0001 | -0.0003 | 0.0003 | 0.0003 | 0.0005 | -0.0003 | -0.0033 | -0.0018 | -0.0223 | -369.1257 | 3.915 | -369.4088 | 3.8596 | -368.8241 | 7.0791 | -368.8764 | 6.266 | -367.6394 | 5.8307 | -367.6517 | 4.6583
11:22 | 120 | 27.9089 | 46.6787 | 104.4412 | 111.2887 | -2.4447 | -20.8933 | -0.8544 | -0.9563 | -1.7125 | -2.0898 | -0.9151 | -1.6719 | 5.5365 | -1.336 | 0.3839 | 0.3451 | 0.3719 | 0.2475 | -37.3596 |  | -0.6008 | -1.2253 | -3.8673 | -3.349 | -0.3281 |  | -1.5138 | -1.1647 | 2.4581 | 1.9737 | 2.5526 | 0.612 | 1.8462 | 2.3942 | 2.4828 | 1.6878 | -0.0001 | -0.0003 | -0.0001 | -0.0001 | -0.0004 | -0.0006 | -0.0002 | -0.0038 | -0.0243 | -369.1411 | 3.9992 | -369.3996 | 3.8925 | -368.7441 | 7.1448 | -368.8241 | 6.3255 | -367.5656 | 5.9334 | -367.5779 | 4.7158
11:22 | 121 | 27.9435 | 47.3699 | 105.8806 | 112.9513 | -2.5575 | -21.2518 | -0.856 | -1.0187 | -1.7697 | -2.0657 | -1.0221 | -1.8104 | 5.5006 | -1.3552 | 0.3831 | 0.3462 | 0.3705 | 0.2469 | -37.8379 |  | -0.6051 | -1.2357 | -3.9892 | -3.399 | -0.4013 |  | -1.5012 | -1.18 | 2.4684 | 1.9782 | 2.5453 | 0.6083 | 1.8737 | 2.4332 | 2.5294 | 1.7377 | -0.0005 | -0.0002 | 0.0007 | 0.0008 | 0.0005 | -0.0004 | -0.0017 | -0.0062 | -0.0127 | -369.0949 | 4.0608 | -369.3596 | 3.915 | -368.6918 | 7.2043 | -368.7318 | 6.4077 | -367.4886 | 6.0114 | -367.5133 | 4.7795
11:22 | 122 | 27.8266 | 48.0637 | 107.5302 | 114.505 | -2.7233 | -21.5617 | -0.8225 | -1.0476 | -1.7464 | -2.1497 | -0.9545 | -1.7729 | 5.4422 | -1.3632 | 0.3838 | 0.3444 | 0.3689 | 0.2449 | -38.4482 |  | -0.7195 | -1.2556 | -3.9907 | -3.3921 | -0.4294 |  | -1.6112 | -1.2637 | 2.4772 | 1.9842 | 2.5533 | 0.6211 | 1.9438 | 2.4628 | 2.5929 | 1.7156 | -0.0004 | -0.0001 | 0.0005 | 0.0009 | -0.0003 | -0.0002 | 0.0119 | -0.0064 | 0.0103 | -369.1072 | 4.0875 | -369.2642 | 3.989 | -368.6764 | 7.2824 | -368.7226 | 6.5021 | -367.4271 | 6.0874 | -367.424 | 4.8595
11:22 | 123 | 27.7226 | 48.8107 | 109.1294 | 116.1721 | -2.7643 | -21.8201 | -0.8067 | -1.0709 | -1.8257 | -2.1521 | -1.011 | -1.8648 | 5.389 | -1.4951 | 0.3842 | 0.3476 | 0.3721 | 0.2459 | -38.9953 |  | -0.6396 | -1.1796 | -4.0868 | -3.4709 | -0.3813 |  | -1.6065 | -1.3287 | 2.4883 | 1.9875 | 2.5599 | 0.6401 | 2.0524 | 2.5945 | 2.6367 | 1.7957 | -0.0001 | -0.0006 | 0.0004 | 0.0009 | 0.0003 | -0.0003 | 0.0049 | -0.0035 | -0.014 | -368.9626 | 4.1306 | -369.2365 | 4.0485 | -368.6149 | 7.3748 | -368.6795 | 6.5514 | -367.2794 | 6.1408 | -367.3594 | 4.9355
11:22 | 124 | 27.7455 | 49.6067 | 110.9064 | 117.9548 | -2.9187 | -22.2223 | -0.8653 | -1.05 | -1.9119 | -2.0658 | -0.9609 | -1.8889 | 5.421 | -1.4222 | 0.3835 | 0.3454 | 0.3731 | 0.2476 | -39.6844 |  | -0.6528 | -1.1705 | -4.1171 | -3.6134 | -0.4352 |  | -1.6778 | -1.2774 | 2.4992 | 1.9948 | 2.572 | 0.6242 | 2.0728 | 2.5859 | 2.6895 | 1.8608 | 0.0002 | -0.0001 | 0.0002 | 0.0011 | 0 | -0.0003 | 0.0049 | -0.0048 | -0.0032 | -368.9103 | 4.1902 | -369.1903 | 4.1245 | -368.618 | 7.461 | -368.6364 | 6.6192 | -367.2332 | 6.2208 | -367.2517 | 5.0279
11:22 | 125 | 27.6305 | 50.4372 | 112.7561 | 119.7124 | -2.9855 | -22.5334 | -0.8556 | -0.9314 | -1.8958 | -2.1421 | -1.0195 | -1.8542 | 5.4273 | -1.4684 | 0.3842 | 0.3448 | 0.3723 | 0.2472 | -40.3764 |  | -0.7845 | -1.1674 | -4.1121 | -3.52 | -0.463 |  | -1.6802 | -1.3666 | 2.5076 | 2.0083 | 2.5863 | 0.6082 | 2.0837 | 2.6662 | 2.7562 | 1.9419 | -0.0005 | -0.0002 | -0.0001 | 0.0006 | 0 | -0.0004 | -0.0063 | -0.015 | -0.0112 | -368.9472 | 4.2744 | -369.1134 | 4.1758 | -368.5533 | 7.5226 | -368.5687 | 6.7239 | -367.1532 | 6.3194 | -367.1655 | 5.0874
11:22 | 126 | 27.479 | 51.2349 | 114.6137 | 121.4728 | -3.0819 | -22.7186 | -0.8025 | -1.0092 | -1.9182 | -2.2258 | -1.0817 | -1.8447 | 5.395 | -1.4801 | 0.3846 | 0.3445 | 0.375 | 0.2479 | -41.2046 |  | -0.78 | -1.1355 | -4.1646 | -3.5278 | -0.471 |  | -1.7664 | -1.3095 | 2.52 | 2.0205 | 2.5874 | 0.5953 | 2.1749 | 2.8035 | 2.8434 | 2.0091 | 0.0001 | 0.0005 | -0.0002 | 0.0007 | 0 | -0.0007 | -0.0053 | -0.0105 | -0.0278 | -368.898 | 4.3236 | -369.0642 | 4.223 | -368.4549 | 7.5945 | -368.5595 | 6.8327 | -367.1102 | 6.3954 | -367.0978 | 5.1531
11:22 | 127 | 27.3675 | 51.949 | 116.2907 | 123.3067 | -3.1644 | -23.0373 | -0.8469 | -1.016 | -2.0165 | -2.2956 | -0.974 | -1.9429 | 5.3768 | -1.5658 | 0.3848 | 0.3438 | 0.3721 | 0.2475 | -41.8329 |  | -0.7386 | -1.1174 | -4.1699 | -3.5776 | -0.4784 |  | -1.8022 | -1.3927 | 2.5291 | 2.0332 | 2.582 | 0.5795 | 2.2235 | 2.777 | 2.8616 | 2.0064 | 0 | -0.0003 | 0.0005 | 0.0008 | -0.0001 | 0.0002 | -0.0081 | -0.0034 | -0.0082 | -368.9349 | 4.4058 | -369.018 | 4.2846 | -368.4241 | 7.691 | -368.5287 | 6.9066 | -367.0332 | 6.498 | -366.9932 | 5.2209
11:22 | 128 | 27.2546 | 52.6968 | 118.1165 | 125.1615 | -3.2301 | -23.2229 | -0.7572 | -0.9419 | -2.0213 | -2.1926 | -1.0793 | -2.0007 | 5.3828 | -1.561 | 0.3838 | 0.3453 | 0.3692 | 0.2468 | -42.5419 |  | -0.7413 | -1.2879 | -4.2343 | -3.666 | -0.4566 |  | -1.8112 | -1.4336 | 2.5413 | 2.034 | 2.5848 | 0.5753 | 2.2297 | 2.8641 | 2.9584 | 2.0537 | -0.0003 | -0.0005 | 0.0001 | 0.0006 | 0.0003 | -0.0006 | 0.011 | -0.0061 | -0.0009 | -368.8426 | 4.4715 | -368.9841 | 4.3791 | -368.3995 | 7.7587 | -368.4364 | 6.9662 | -366.9071 | 6.5719 | -366.944 | 5.3092
11:22 | 129 | 27.1175 | 53.4011 | 119.9257 | 126.8633 | -3.3907 | -23.2903 | -0.6738 | -0.9964 | -2.0911 | -2.3203 | -1.1067 | -2.0193 | 5.3737 | -1.5513 | 0.3847 | 0.3505 | 0.3696 | 0.2453 | -43.2797 |  | -0.7574 | -1.2751 | -4.2604 | -3.6774 | -0.4732 |  | -1.8238 | -1.4289 | 2.5491 | 2.0358 | 2.587 | 0.5696 | 2.277 | 2.9345 | 3.0522 | 2.1528 | -0.0004 | -0.0006 | 0.0001 | 0.0005 | -0.0001 | -0.0006 | 0.0146 | -0.0149 | -0.0037 | -368.7903 | 4.529 | -368.9626 | 4.4797 | -368.381 | 7.8285 | -368.3656 | 7.0421 | -366.7624 | 6.6541 | -366.8701 | 5.4036
11:22 | 130 | 27.0099 | 54.2978 | 121.789 | 128.711 | -3.5577 | -23.6568 | -0.7458 | -1.0509 | -2.117 | -2.5452 | -1.1631 | -1.9932 | 5.3685 | -1.6164 | 0.3845 | 0.3457 | 0.3724 | 0.2463 | -44.0125 |  | -0.735 | -1.3697 | -4.2533 | -3.6399 | -0.4851 |  | -1.8083 | -1.38 | 2.5591 | 2.0449 | 2.5921 | 0.5664 | 2.3569 | 2.9971 | 3.0973 | 2.227 | -0.0009 | -0.0003 | 0.0005 | 0.001 | 0.0006 | -0.0003 | 0.0125 | -0.0119 | -0.0008 | -368.7287 | 4.6316 | -368.9195 | 4.529 | -368.2918 | 7.9127 | -368.3256 | 7.1181 | -366.7317 | 6.7547 | -366.8024 | 5.455
11:22 | 131 | 26.9429 | 55.0437 | 123.5776 | 130.4859 | -3.6888 | -23.9032 | -0.6942 | -1.0596 | -2.2465 | -2.4721 | -1.1394 | -2.0215 | 5.3568 | -1.5728 | 0.3855 | 0.3486 | 0.3707 | 0.2473 | -44.7173 |  | -0.727 | -1.3236 | -4.2879 | -3.6732 | -0.4953 |  | -1.8865 | -1.4507 | 2.5671 | 2.0547 | 2.5947 | 0.5607 | 2.4369 | 3.0943 | 3.2033 | 2.2364 | -0.0004 | -0.0003 | 0.0001 | 0.0009 | 0.0002 | -0.0001 | 0.011 | -0.0149 | 0.0058 | -368.6887 | 4.6604 | -368.7995 | 4.5762 | -368.2179 | 7.9928 | -368.2949 | 7.2146 | -366.6609 | 6.804 | -366.6117 | 5.5166
11:22 | 132 | 26.7994 | 55.807 | 125.4293 | 132.2321 | -3.8519 | -24.1479 | -0.7073 | -1.0741 | -2.2188 | -2.5293 | -1.1302 | -1.9726 | 5.2404 | -1.6589 | 0.3857 | 0.3524 | 0.3706 | 0.2459 | -45.4987 |  | -0.755 | -1.2421 | -4.2573 | -3.7385 | -0.407 |  | -1.911 | -1.4497 | 2.5759 | 2.068 | 2.605 | 0.5849 | 2.4866 | 3.196 | 3.2516 | 2.2866 | 0.0001 | -0.0007 | 0.0003 | 0.0011 | -0.0005 | -0.0008 | -0.0055 | 0.0002 | -0.0004 | -368.6426 | 4.7199 | -368.738 | 4.6398 | -368.1902 | 8.0934 | -368.2887 | 7.3111 | -366.6086 | 6.884 | -366.5532 | 5.5761
11:22 | 133 | 26.8007 | 56.7292 | 127.3822 | 134.1 | -4.0208 | -24.4299 | -0.6237 | -1.0663 | -2.22 | -2.5062 | -1.1223 | -2.0179 | 5.2349 | -1.6962 | 0.3837 | 0.3516 | 0.3739 | 0.2474 | -46.1504 |  | -0.7549 | -1.3771 | -4.3315 | -3.7843 | -0.468 |  | -1.9313 | -1.4339 | 2.5837 | 2.0774 | 2.6167 | 0.5955 | 2.5503 | 3.2192 | 3.3472 | 2.3316 | -0.0001 | -0.0006 | 0.0006 | 0.0015 | 0 | -0.0003 | -0.0002 | -0.0189 | -0.0119 | -368.5564 | 4.7877 | -368.7103 | 4.7261 | -368.1133 | 8.1509 | -368.2272 | 7.3789 | -366.4855 | 6.9559 | -366.467 | 5.6624
11:22 | 134 | 26.679 | 57.49 | 129.1043 | 135.8628 | -4.0147 | -24.607 | -0.5889 | -1.0165 | -2.1327 | -2.5751 | -1.1171 | -1.9406 | 5.2089 | -1.7188 | 0.3847 | 0.3529 | 0.3697 | 0.2449 | -46.8601 |  | -0.7874 | -1.3695 | -4.4946 | -3.8201 | -0.5971 |  | -1.9826 | -1.4685 | 2.5972 | 2.075 | 2.6206 | 0.5861 | 2.6361 | 3.328 | 3.4386 | 2.3653 | -0.0003 | 0 | 0 | 0.001 | 0 | 0 | 0.0062 | -0.0081 | -0.0191 | -368.6149 | 4.8965 | -368.701 | 4.802 | -368.1072 | 8.2125 | -368.1472 | 7.4446 | -366.4086 | 7.0709 | -366.4455 | 5.7506
11:22 | 135 | 26.457 | 58.2166 | 130.8103 | 137.5933 | -4.2137 | -24.7197 | -0.6236 | -1.088 | -2.279 | -2.67 | -1.1945 | -2.0945 | 5.2188 | -1.7187 | 0.3865 | 0.3502 | 0.3717 | 0.2462 | -47.5613 |  | -0.7645 | -1.4116 | -4.5511 | -3.9363 | -0.6102 |  | -1.9747 | -1.4943 | 2.6076 | 2.079 | 2.6249 | 0.5798 | 2.6564 | 3.3831 | 3.4681 | 2.3982 | -0.0004 | -0.0003 | 0.0005 | 0.0008 | 0 | -0.0005 | 0.0096 | -0.0019 | -0.008 | -368.4949 | 4.9663 | -368.6672 | 4.8801 | -368.0241 | 8.2741 | -368.0487 | 7.5082 | -366.2978 | 7.1489 | -366.3562 | 5.8287
11:22 | 136 | 26.3681 | 58.9626 | 132.567 | 139.3299 | -4.4789 | -25.0426 | -0.6009 | -1.0091 | -2.2954 | -2.6925 | -1.13 | -2.1439 | 5.1842 | -1.7512 | 0.3852 | 0.3493 | 0.374 | 0.2455 | -48.2641 |  | -0.82 | -1.3932 | -4.5284 | -3.9882 | -0.625 |  | -2.0374 | -1.4876 | 2.6146 | 2.0841 | 2.6371 | 0.5712 | 2.7082 | 3.4464 | 3.574 | 2.5069 | -0.0002 | -0.0005 | 0.0004 | 0.0007 | -0.0002 | -0.0001 | 0.0115 | -0.0117 | 0.0006 | -368.5041 | 5.0197 | -368.5749 | 4.9478 | -368.0056 | 8.3603 | -368.0271 | 7.6088 | -366.2455 | 7.2146 | -366.2455 | 5.9005
11:22 | 137 | 26.1812 | 59.718 | 134.4457 | 141.235 | -4.6073 | -25.3714 | -0.6507 | -1.035 | -2.3954 | -2.7769 | -1.1931 | -2.1447 | 5.1278 | -1.7579 | 0.386 | 0.3514 | 0.3708 | 0.2473 | -48.9637 |  | -0.7516 | -1.4555 | -4.6514 | -4.249 | -0.6018 |  | -2.007 | -1.5926 | 2.6253 | 2.0921 | 2.6449 | 0.5648 | 2.7554 | 3.4935 | 3.6068 | 2.5783 | -0.0001 | -0.0008 | 0.0003 | 0.0008 | 0.0006 | -0.0006 | 0.0085 | -0.0044 | -0.0168 | -368.3872 | 5.069 | -368.5072 | 5.0217 | -367.9441 | 8.4753 | -367.9933 | 7.6786 | -366.1101 | 7.2762 | -366.1501 | 5.9724
11:22 | 138 | 26.12 | 60.5895 | 136.3572 | 143.208 | -4.7123 | -25.6358 | -0.6972 | -1.0325 | -2.3579 | -2.657 | -1.1476 | -2.1237 | 5.0997 | -1.7387 | 0.3872 | 0.3527 | 0.3694 | 0.2443 | -49.7678 |  | -0.8283 | -1.4094 | -4.6366 | -4.1859 | -0.72 |  | -1.9755 | -1.6041 | 2.6368 | 2.1045 | 2.6556 | 0.5686 | 2.8434 | 3.593 | 3.6748 | 2.6013 | 0 | -0.0003 | 0.0013 | 0.0015 | 0.0002 | -0.0001 | 0.0133 | -0.0041 | -0.0125 | -368.3318 | 5.1306 | -368.4426 | 5.0916 | -367.9287 | 8.5595 | -367.9841 | 7.7772 | -366.0178 | 7.3378 | -366.0054 | 6.0545
11:22 | 139 | 25.9403 | 61.336 | 138.2622 | 145.1009 | -4.8621 | -25.9399 | -0.6582 | -1.0143 | -2.4052 | -2.7851 | -1.2187 | -2.1122 | 5.0825 | -1.8489 | 0.3874 | 0.3524 | 0.3715 | 0.2454 | -50.4133 |  | -0.7957 | -1.3549 | -4.7256 | -4.0829 | -0.6044 |  | -2.0922 | -1.5278 | 2.6435 | 2.108 | 2.6621 | 0.5911 | 2.8316 | 3.6564 | 3.7642 | 2.6197 | -0.0004 | -0.0002 | 0.0002 | 0.001 | 0.0003 | -0.0007 | 0.0147 | -0.0042 | 0.0038 | -368.3472 | 5.2127 | -368.4333 | 5.1819 | -367.8948 | 8.6498 | -367.9102 | 7.8491 | -365.9531 | 7.4487 | -365.9839 | 6.1428
11:22 | 140 | 25.8654 | 62.3782 | 140.3767 | 146.9953 | -5.083 | -26.3208 | -0.6978 | -0.9567 | -2.4468 | -2.7474 | -1.1945 | -2.2338 | 4.9379 | -1.8698 | 0.388 | 0.3549 | 0.371 | 0.243 | -51.1189 |  | -0.8217 | -1.3686 | -4.7923 | -4.2877 | -0.578 |  | -2.0738 | -1.6747 | 2.652 | 2.1147 | 2.6636 | 0.5847 | 2.9027 | 3.6754 | 3.7941 | 2.7198 | -0.0001 | -0.0006 | 0.0005 | 0.0014 | -0.0002 | -0.0007 | -0.0023 | -0.0179 | -0.0023 | -368.2856 | 5.301 | -368.381 | 5.225 | -367.7656 | 8.7032 | -367.8394 | 7.9394 | -365.8485 | 7.5575 | -365.8731 | 6.1982
11:22 | 141 | 25.7434 | 63.1808 | 142.2448 | 148.984 | -5.1567 | -26.4786 | -0.6136 | -1.0363 | -2.4542 | -2.9501 | -1.2172 | -2.2365 | 4.9866 | -2.0115 | 0.3866 | 0.3572 | 0.3711 | 0.2441 | -51.823 |  | -0.7808 | -1.421 | -4.8182 | -4.129 | -0.5941 |  | -2.1032 | -1.715 | 2.6604 | 2.1254 | 2.6691 | 0.5796 | 2.9744 | 3.7586 | 3.8866 | 2.7554 | 0.0004 | -0.0006 | 0.0005 | 0.0014 | 0 | 0 | -0.0118 | -0.0215 | -0.0128 | -368.2918 | 5.3872 | -368.3287 | 5.2969 | -367.704 | 8.7792 | -367.7748 | 8.0421 | -365.8208 | 7.6581 | -365.7962 | 6.2845
11:22 | 142 | 25.6733 | 63.9784 | 144.2839 | 151.0298 | -5.3628 | -26.8682 | -0.4882 | -0.9914 | -2.5737 | -2.7519 | -1.3119 | -2.1494 | 4.9959 | -1.9053 | 0.3868 | 0.3554 | 0.3689 | 0.2446 | -52.593 |  | -0.8035 | -1.2567 | -4.8629 | -4.2264 | -0.6438 |  | -2.1138 | -1.6988 | 2.6702 | 2.1301 | 2.6772 | 0.5747 | 3.0351 | 3.8598 | 4.0201 | 2.817 | -0.0003 | -0.0008 | -0.0002 | 0.0008 | 0.0002 | -0.0006 | 0.0068 | -0.0148 | -0.0064 | -368.181 | 5.4385 | -368.2518 | 5.3728 | -367.6548 | 8.8839 | -367.7348 | 8.1098 | -365.6854 | 7.7197 | -365.6823 | 6.3584
11:22 | 143 | 25.5543 | 64.9009 | 146.2349 | 152.9334 | -5.574 | -27.0995 | -0.5707 | -0.9945 | -2.644 | -2.935 | -1.3134 | -2.1714 | 4.9427 | -1.9919 | 0.3881 | 0.3568 | 0.3704 | 0.2455 | -53.3797 |  | -0.8097 | -1.1462 | -4.9458 | -4.2652 | -0.6613 |  | -2.2453 | -1.7704 | 2.6805 | 2.1463 | 2.6816 | 0.5702 | 3.0694 | 3.9056 | 4.036 | 2.8633 | -0.0005 | -0.0005 | 0.0003 | 0.0012 | 0 | 0.0003 | 0.0038 | -0.0035 | -0.012 | -368.0918 | 5.5001 | -368.2025 | 5.494 | -367.6671 | 8.9599 | -367.6794 | 8.1735 | -365.5623 | 7.7957 | -365.6177 | 6.4775
11:22 | 144 | 25.4437 | 65.8339 | 148.1781 | 154.9016 | -5.7066 | -27.4281 | -0.6221 | -0.9016 | -2.7291 | -2.9314 | -1.2374 | -2.2695 | 4.8837 | -2.0062 | 0.3888 | 0.3585 | 0.3691 | 0.2455 | -54.0525 |  | -0.8233 | -1.101 | -4.9435 | -4.2715 | -0.64 |  | -2.3457 | -1.8079 | 2.6922 | 2.1608 | 2.6958 | 0.5698 | 3.1665 | 4.0085 | 4.1465 | 2.9249 | -0.0004 | -0.0003 | 0.0003 | 0.001 | 0.0003 | -0.0005 | 0.0035 | -0.0044 | -0.0167 | -368.0518 | 5.6049 | -368.1687 | 5.5843 | -367.6087 | 9.0625 | -367.6117 | 8.2556 | -365.4885 | 7.8922 | -365.5377 | 6.5576
11:22 | 145 | 25.3898 | 66.6484 | 150.2758 | 156.9661 | -5.9037 | -27.8385 | -0.5859 | -0.9338 | -2.7349 | -2.9608 | -1.214 | -2.2485 | 4.8893 | -2.0357 | 0.3873 | 0.3551 | 0.3688 | 0.2454 | -54.8347 |  | -1.0013 | -1.2086 | -4.9845 | -4.2921 | -0.6916 |  | -2.3015 | -1.8546 | 2.7031 | 2.1719 | 2.6967 | 0.5668 | 3.1733 | 4.0672 | 4.1485 | 2.922 | 0 | -0.0005 | 0.0002 | 0.0007 | -0.0004 | -0.0003 | 0.0138 | -0.0046 | 0.0081 | -368.0056 | 5.6726 | -368.1102 | 5.6377 | -367.504 | 9.1385 | -367.5686 | 8.3542 | -365.3962 | 7.9764 | -365.4239 | 6.613
11:22 | 146 | 25.2831 | 67.7058 | 152.4151 | 159.0688 | -5.9484 | -28.1073 | -0.6407 | -0.9937 | -2.7312 | -2.9866 | -1.2513 | -2.2231 | 4.8434 | -2.0753 | 0.3881 | 0.3583 | 0.3701 | 0.2456 | -55.6327 |  | -1.0128 | -1.2724 | -5.0757 | -4.4202 | -0.6596 |  | -2.2533 | -1.8997 | 2.714 | 2.1867 | 2.6979 | 0.5879 | 3.2554 | 4.0973 | 4.2589 | 3.0539 | 0 | -0.0009 | 0.0007 | 0.0014 | 0.0006 | -0.0004 | 0.0029 | -0.0156 | -0.0003 | -368.0271 | 5.7547 | -368.0302 | 5.6973 | -367.4609 | 9.235 | -367.5594 | 8.4835 | -365.35 | 8.0688 | -365.3039 | 6.6951
11:22 | 147 | 25.059 | 68.5369 | 154.4651 | 161.1104 | -6.0847 | -28.2761 | -0.5993 | -1.0513 | -2.7895 | -3.1205 | -1.2305 | -2.322 | 4.9181 | -2.0704 | 0.3881 | 0.3586 | 0.3667 | 0.2431 | -56.4116 |  | -0.9378 | -1.2982 | -5.1423 | -4.438 | -0.715 |  | -2.3317 | -1.9709 | 2.7239 | 2.1967 | 2.7056 | 0.5888 | 3.3662 | 4.2022 | 4.3893 | 3.129 | 0.0001 | -0.0002 | 0.0009 | 0.0013 | 0 | -0.0004 | 0.0062 | -0.0052 | 0.0038 | -367.9256 | 5.8102 | -367.9564 | 5.7712 | -367.384 | 9.3233 | -367.4948 | 8.5636 | -365.2054 | 8.1468 | -365.1962 | 6.7711
11:22 | 148 | 24.9582 | 69.4967 | 156.5689 | 163.1156 | -6.3087 | -28.498 | -0.6576 | -0.9817 | -2.7907 | -3.1613 | -1.3099 | -2.3141 | 4.9131 | -2.209 | 0.3898 | 0.3581 | 0.3669 | 0.2454 | -57.1392 |  | -1.0006 | -1.3109 | -5.2138 | -4.5836 | -0.662 |  | -2.3185 | -1.9596 | 2.7344 | 2.2032 | 2.7108 | 0.574 | 3.3905 | 4.3075 | 4.406 | 3.1251 | -0.0004 | -0.0005 | 0 | 0.0009 | 0.0003 | -0.0004 | -0.0028 | -0.0062 | -0.0094 | -367.8918 | 5.8985 | -367.9287 | 5.8779 | -367.3286 | 9.4034 | -367.3994 | 8.6334 | -365.0946 | 8.2392 | -365.1315 | 6.8799
11:22 | 149 | 24.9316 | 70.333 | 158.6895 | 165.1505 | -6.51 | -28.7433 | -0.6303 | -0.9332 | -2.7884 | -3.1601 | -1.3724 | -2.3944 | 4.753 | -2.1766 | 0.39 | 0.354 | 0.3684 | 0.2454 | -57.8649 |  | -0.9284 | -1.2328 | -5.2004 | -4.4949 | -0.6786 |  | -2.4335 | -2.0391 | 2.7458 | 2.2138 | 2.7162 | 0.5655 | 3.4414 | 4.3641 | 4.5571 | 3.2503 | 0.0002 | -0.0004 | 0.0003 | 0.0014 | 0.0002 | -0.0004 | 0.006 | -0.01 | 0.0038 | -367.8517 | 6.0155 | -367.9041 | 5.9621 | -367.3194 | 9.4773 | -367.3379 | 8.7278 | -365.0208 | 8.3706 | -365.0454 | 6.96
11:22 | 150 | 24.9494 | 71.4535 | 161.0312 | 167.5511 | -6.5805 | -29.0362 | -0.6399 | -0.9719 | -2.8852 | -3.297 | -1.3069 | -2.3545 | 4.7268 | -2.1842 | 0.39 | 0.3552 | 0.3733 | 0.247 | -58.7502 |  | -0.9675 | -1.351 | -5.3059 | -4.5978 | -0.7023 |  | -2.3211 | -2.0802 | 2.7566 | 2.2256 | 2.7229 | 0.5572 | 3.5399 | 4.4394 | 4.6306 | 3.3032 | 0.0003 | -0.0004 | 0.0001 | 0.0015 | -0.0002 | -0.0005 | 0.0067 | -0.0092 | -0.0093 | -367.8148 | 6.0894 | -367.8271 | 6.0319 | -367.2148 | 9.5553 | -367.2609 | 8.8285 | -364.9654 | 8.4691 | -364.9561 | 7.0462
11:22 | 151 | 24.7614 | 72.4015 | 163.1983 | 169.7363 | -6.7293 | -29.2467 | -0.6255 | -0.9047 | -2.8612 | -3.2636 | -1.335 | -2.3596 | 4.7698 | -2.2659 | 0.3904 | 0.3535 | 0.369 | 0.2453 | -59.5201 |  | -1.0387 | -1.3979 | -5.3583 | -4.6681 | -0.6646 |  | -2.4974 | -2.0181 | 2.7695 | 2.2373 | 2.7225 | 0.5512 | 3.5643 | 4.5158 | 4.7207 | 3.3292 | -0.0005 | -0.001 | 0.0005 | 0.0013 | 0.0004 | -0.0006 | -0.0019 | -0.0037 | -0.0296 | -367.7994 | 6.1633 | -367.7564 | 6.1202 | -367.1902 | 9.6888 | -367.2302 | 8.9393 | -364.8638 | 8.5615 | -364.8177 | 7.1468
11:22 | 152 | 24.6772 | 73.3567 | 165.3753 | 171.9916 | -6.9623 | -29.5745 | -0.6914 | -0.9916 | -3.0088 | -3.3434 | -1.4154 | -2.4272 | 4.6659 | -2.2959 | 0.391 | 0.356 | 0.3718 | 0.245 | -60.3376 |  | -1.003 | -1.351 | -5.3986 | -4.7442 | -0.6774 |  | -2.4384 | -2.0371 | 2.7805 | 2.252 | 2.7349 | 0.5417 | 3.6346 | 4.6034 | 4.7603 | 3.4207 | -0.0005 | -0.0004 | 0.001 | 0.0014 | 0.0002 | 0 | -0.0009 | -0.0081 | -0.0051 | -367.6394 | 6.2229 | -367.6733 | 6.2126 | -367.1378 | 9.775 | -367.2148 | 9.0112 | -364.6638 | 8.6272 | -364.7192 | 7.2351
11:22 | 153 | 24.532 | 74.3257 | 167.71 | 174.1473 | -6.9902 | -29.8239 | -0.512 | -0.983 | -3.1391 | -3.4182 | -1.4076 | -2.4868 | 4.6526 | -2.4384 | 0.3916 | 0.3547 | 0.3714 | 0.2459 | -61.0348 |  | -1.0712 | -1.3502 | -5.5084 | -4.763 | -0.6839 |  | -2.6005 | -2.1518 | 2.7908 | 2.2578 | 2.7447 | 0.592 | 3.6863 | 4.707 | 4.7859 | 3.4851 | -0.0002 | -0.0007 | 0.0001 | 0.001 | 0.0005 | -0.0007 | 0.003 | -0.0169 | -0.0131 | -367.5963 | 6.3173 | -367.6394 | 6.3112 | -367.1071 | 9.9023 | -367.1071 | 9.1077 | -364.5623 | 8.7361 | -364.6023 | 7.3583
11:22 | 154 | 24.3903 | 75.3425 | 169.9859 | 176.4322 | -7.2286 | -30.1277 | -0.6338 | -0.938 | -3.1945 | -3.4449 | -1.4612 | -2.4917 | 4.6236 | -2.3268 | 0.3915 | 0.3559 | 0.3711 | 0.245 | -61.7891 |  | -1.1 | -1.4276 | -5.4577 | -4.7433 | -0.6454 |  | -2.6247 | -2.1523 | 2.7992 | 2.2722 | 2.7634 | 0.6638 | 3.7824 | 4.7858 | 4.9705 | 3.5343 | -0.0004 | -0.0011 | 0.0008 | 0.0019 | 0.0004 | -0.0001 | -0.0021 | -0.0229 | -0.006 | -367.5594 | 6.4077 | -367.5625 | 6.3748 | -367.0025 | 9.9618 | -367.0517 | 9.2083 | -364.4607 | 8.8346 | -364.513 | 7.4158
11:22 | 155 | 24.2862 | 76.3462 | 172.156 | 178.613 | -7.4235 | -30.3979 | -0.689 | -0.9448 | -3.2974 | -3.5476 | -1.608 | -2.5013 | 4.6091 | -2.3357 | 0.3926 | 0.3554 | 0.3716 | 0.2441 | -62.5842 |  | -1.0224 | -1.4856 | -5.5446 | -4.8552 | -0.6674 |  | -2.6512 | -2.2658 | 2.8117 | 2.2937 | 2.7743 | 0.6462 | 3.8181 | 4.914 | 5.0373 | 3.6383 | -0.0001 | -0.0008 | 0.0003 | 0.0015 | 0.0008 | -0.0002 | 0.0192 | -0.0031 | 0.0093 | -367.5748 | 6.4898 | -367.4671 | 6.457 | -366.9255 | 10.0748 | -367.0117 | 9.3356 | -364.4115 | 8.9475 | -364.3746 | 7.5103
11:22 | 156 | 24.1572 | 77.3064 | 174.3904 | 180.8908 | -7.5983 | -30.6293 | -0.5839 | -0.9492 | -3.2842 | -3.631 | -1.5815 | -2.4929 | 4.5574 | -2.4593 | 0.3922 | 0.3542 | 0.3701 | 0.2441 | -63.3577 |  | -1.0499 | -1.5225 | -5.554 | -4.8939 | -0.6525 |  | -2.7298 | -2.2811 | 2.8254 | 2.3078 | 2.7667 | 0.6312 | 3.9186 | 4.9566 | 5.1652 | 3.7336 | -0.0004 | -0.0007 | -0.0004 | 0.0012 | -0.0001 | -0.0004 | -0.0018 | -0.0063 | -0.0253 | -367.4825 | 6.574 | -367.3963 | 6.5165 | -366.8424 | 10.1651 | -366.9286 | 9.4177 | -364.3069 | 9.0276 | -364.2484 | 7.578
11:22 | 157 | 24.1427 | 78.1841 | 176.4437 | 182.9334 | -7.8116 | -30.8266 | -0.5518 | -0.9986 | -3.399 | -3.6276 | -1.5926 | -2.4865 | 4.5744 | -2.4559 | 0.3922 | 0.3542 | 0.3716 | 0.244 | -64.1929 |  | -1.1682 | -1.5391 | -5.6281 | -4.9283 | -0.6707 |  | -2.7446 | -2.2795 | 2.835 | 2.3149 | 2.7706 | 0.6186 | 3.988 | 5.0433 | 5.2038 | 3.7261 | 0 | -0.0004 | 0.0005 | 0.0018 | 0.0003 | -0.0002 | -0.0112 | 0.0039 | -0.0012 | -367.4025 | 6.6561 | -367.3748 | 6.6602 | -366.8271 | 10.2534 | -366.9224 | 9.4978 | -364.1807 | 9.1344 | -364.1868 | 7.6868
11:22 | 158 | 23.9819 | 79.141 | 178.3666 | 184.8922 | -7.8677 | -31.1171 | -0.5165 | -0.9577 | -3.4213 | -3.6278 | -1.6061 | -2.5688 | 4.4588 | -2.5072 | 0.3932 | 0.3586 | 0.3719 | 0.2452 | -64.8884 |  | -1.1746 | -1.6108 | -5.7039 | -4.9731 | -0.7465 |  | -2.7513 | -2.2715 | 2.8474 | 2.3302 | 2.7783 | 0.6098 | 4.0065 | 5.1427 | 5.2474 | 3.7981 | 0.0001 | -0.0013 | -0.0002 | 0.0011 | 0.0003 | -0.0005 | 0.0038 | -0.0124 | -0.0111 | -367.3656 | 6.767 | -367.3379 | 6.7465 | -366.787 | 10.3047 | -366.8271 | 9.5512 | -364.073 | 9.2145 | -364.1161 | 7.7649
11:22 | 159 | 23.8616 | 79.9524 | 180.2687 | 186.8364 | -8.0139 | -31.2598 | -0.5221 | -1.04 | -3.5049 | -3.6352 | -1.5874 | -2.5623 | 4.417 | -2.4701 | 0.3934 | 0.3543 | 0.3726 | 0.2453 | -65.5685 |  | -1.1387 | -1.601 | -5.7454 | -5.0986 | -0.7309 |  | -2.7667 | -2.1901 | 2.8556 | 2.3369 | 2.7856 | 0.6014 | 4.0569 | 5.1758 | 5.3392 | 3.8771 | -0.0001 | -0.0011 | 0.0002 | 0.0015 | 0.0001 | 0 | 0.0078 | 0.0057 | -0.0174 | -367.3009 | 6.8553 | -367.3286 | 6.8491 | -366.7347 | 10.3725 | -366.7409 | 9.6354 | -364.0299 | 9.3151 | -364.0545 | 7.8573
11:22 | 160 | 23.771 | 80.7654 | 182.1174 | 188.551 | -8.1084 | -31.3746 | -0.4678 | -1.0707 | -3.4744 | -3.7286 | -1.6222 | -2.6578 | 4.4274 | -2.4632 | 0.3944 | 0.3521 | 0.3716 | 0.2441 | -66.2462 |  | -1.1072 | -1.6354 | -5.821 | -5.106 | -0.7439 |  | -2.8154 | -2.273 | 2.8657 | 2.3435 | 2.7949 | 0.5969 | 4.1201 | 5.2562 | 5.3723 | 3.929 | 0.0001 | -0.0008 | 0.0008 | 0.0017 | 0 | -0.0008 | -0.0033 | -0.014 | -0.0076 | -367.2179 | 6.9107 | -367.2148 | 6.9189 | -366.6393 | 10.4505 | -366.7101 | 9.7134 | -363.9007 | 9.3582 | -363.9345 | 7.9148
11:22 | 161 | 23.7424 | 81.5742 | 183.9772 | 190.42 | -8.4129 | -31.6082 | -0.4202 | -1.1239 | -3.559 | -3.8259 | -1.7186 | -2.5785 | 4.3838 | -2.4564 | 0.3943 | 0.3505 | 0.3688 | 0.2441 | -66.954 |  | -1.0479 | -1.5725 | -5.8802 | -5.2405 | -0.8091 |  | -2.8232 | -2.3488 | 2.8728 | 2.3538 | 2.8009 | 0.5907 | 4.1495 | 5.3203 | 5.5012 | 3.9522 | -0.0004 | -0.0006 | 0.0003 | 0.0013 | -0.0003 | -0.0003 | -0.0022 | -0.0156 | -0.015 | -367.1317 | 6.9949 | -367.1563 | 7.0154 | -366.6363 | 10.5532 | -366.6947 | 9.7955 | -363.8237 | 9.4383 | -363.8391 | 7.9825
11:22 | 162 | 23.5327 | 82.3528 | 185.7271 | 192.1791 | -8.5029 | -31.8172 | -0.4095 | -1.0988 | -3.5167 | -3.777 | -1.6995 | -2.6147 | 4.3655 | -2.5797 | 0.395 | 0.3509 | 0.3746 | 0.2449 | -67.7215 |  | -1.148 | -1.7426 | -5.9513 | -5.427 | -0.8954 |  | -2.8636 | -2.3818 | 2.8832 | 2.3672 | 2.8072 | 0.6031 | 4.1832 | 5.3714 | 5.5078 | 3.9851 | 0.0001 | -0.0007 | 0.0015 | 0.0021 | 0.001 | -0.0004 | 0.0064 | -0.005 | -0.0131 | -367.0763 | 7.0647 | -367.0855 | 7.1017 | -366.5993 | 10.625 | -366.6301 | 9.8592 | -363.7007 | 9.4855 | -363.7222 | 8.0667
11:22 | 163 | 23.3342 | 83.141 | 187.559 | 193.9522 | -8.612 | -32.1054 | -0.4845 | -0.937 | -3.5722 | -3.879 | -1.6607 | -2.5494 | 4.2719 | -2.6064 | 0.3933 | 0.3523 | 0.3715 | 0.2475 | -68.352 |  | -1.0755 | -1.735 | -5.9734 | -5.2869 | -0.8841 |  | -2.8992 | -2.4526 | 2.8978 | 2.3333 | 2.8065 | 0.6579 | 4.2784 | 5.4722 | 5.6352 | 4.0465 | 0.0001 | -0.001 | 0.0006 | 0.0016 | 0 | 0.0001 | 0.0042 | -0.0031 | -0.0145 | -367.064 | 7.1633 | -367.0917 | 7.2043 | -366.5532 | 10.6825 | -366.5686 | 9.9413 | -363.6606 | 9.5943 | -363.676 | 8.1427
11:22 | 164 | 23.2078 | 83.9485 | 189.4091 | 195.8215 | -8.7986 | -32.2617 | -0.5034 | -0.9569 | -3.6291 | -3.9209 | -1.7817 | -2.6657 | 4.3161 | -2.6918 | 0.395 | 0.3509 | 0.3699 | 0.2462 | -69.0006 |  | -1.1296 | -1.7755 | -6.0984 | -5.3472 | -0.9465 |  | -2.899 | -2.3478 | 2.9072 | 2.3407 | 2.8016 | 0.6878 | 4.3225 | 5.5279 | 5.7254 | 4.085 | 0.0001 | -0.0009 | 0.0001 | 0.0015 | 0.0003 | -0.0005 | 0.0235 | -0.0163 | -0.0014 | -367.0363 | 7.2577 | -367.0209 | 7.2618 | -366.4424 | 10.738 | -366.5563 | 10.0255 | -363.5468 | 9.6703 | -363.5653 | 8.1817
11:22 | 165 | 23.0719 | 84.7942 | 191.1613 | 197.6561 | -9.068 | -32.5407 | -0.5387 | -0.9703 | -3.753 | -4.0153 | -1.795 | -2.6897 | 4.3125 | -2.7208 | 0.3949 | 0.3497 | 0.3684 | 0.2457 | -69.6956 |  | -1.2027 | -1.6225 | -5.9843 | -5.3211 | -0.8864 |  | -2.9175 | -2.4292 | 2.9138 | 2.34 | 2.7744 | 0.6723 | 4.3709 | 5.5994 | 5.7336 | 4.1389 | -0.0004 | -0.0005 | 0.0002 | 0.0017 | 0.0006 | -0.0001 | -0.0013 | -0.0093 | -0.0171 | -366.9994 | 7.346 | -366.9871 | 7.3357 | -366.3993 | 10.8221 | -366.4978 | 10.1117 | -363.5222 | 9.7647 | -363.4791 | 8.2556
11:22 | 166 | 23.0491 | 85.6753 | 193.256 | 199.5755 | -9.0968 | -32.7404 | -0.4533 | -1.0057 | -3.7931 | -4.0259 | -1.82 | -2.6613 | 4.2036 | -2.7792 | 0.395 | 0.3541 | 0.3705 | 0.2475 | -70.3134 |  | -1.1001 | -1.5778 | -6.0476 | -5.4163 | -0.8901 |  | -2.9402 | -2.4532 | 2.9214 | 2.3427 | 2.7773 | 0.6562 | 4.3762 | 5.6624 | 5.8072 | 4.2255 | -0.0002 | -0.001 | 0.0004 | 0.0018 | 0.0001 | -0.0001 | 0.0031 | -0.0062 | -0.0034 | -366.9224 | 7.3994 | -366.904 | 7.4343 | -366.3593 | 10.8879 | -366.4147 | 10.1631 | -363.3929 | 9.8325 | -363.3652 | 8.3254
11:22 | 167 | 23.0302 | 86.5272 | 195.2287 | 201.5026 | -9.1718 | -32.9527 | -0.4816 | -1.0439 | -3.8881 | -4.0736 | -1.8112 | -2.6661 | 4.2121 | -2.7293 | 0.3968 | 0.3558 | 0.3724 | 0.2491 | -71.2395 |  | -1.1659 | -1.6869 | -6.0737 | -5.3416 | -0.8269 |  | -2.9422 | -2.4599 | 2.9216 | 2.3487 | 2.784 | 0.6466 | 4.4566 | 5.7254 | 5.8866 | 4.26 | 0.0002 | -0.001 | 0.0001 | 0.0015 | 0.0004 | -0.0008 | 0.0014 | 0.002 | -0.0254 | -366.8178 | 7.4856 | -366.9009 | 7.5534 | -366.3778 | 10.972 | -366.3624 | 10.2411 | -363.2822 | 9.9023 | -363.3468 | 8.4507
11:23 | 168 | 22.9006 | 87.4504 | 197.1988 | 203.5176 | -9.3566 | -33.1813 | -0.4411 | -0.9794 | -3.8764 | -4.0763 | -1.76 | -2.7444 | 4.1901 | -2.8404 | 0.3959 | 0.3584 | 0.3716 | 0.2495 | -71.9123 |  | -1.2416 | -1.6195 | -6.104 | -5.3687 | -0.8267 |  | -3.066 | -2.5367 | 2.8972 | 2.3606 | 2.7927 | 0.6418 | 4.5176 | 5.8269 | 5.9656 | 4.2976 | 0 | -0.0011 | 0.0003 | 0.0016 | 0 | -0.0002 | -0.0027 | -0.0113 | -0.0157 | -366.747 | 7.5801 | -366.864 | 7.6335 | -366.3009 | 11.0685 | -366.2947 | 10.3232 | -363.1929 | 9.9947 | -363.2668 | 8.5266
11:23 | 169 | 22.8432 | 88.324 | 199.2207 | 205.5279 | -9.4434 | -33.3509 | -0.5072 | -0.9642 | -3.9409 | -4.1261 | -1.79 | -2.7665 | 4.0793 | -2.839 | 0.398 | 0.3541 | 0.3759 | 0.2502 | -72.7573 |  | -1.2506 | -1.7695 | -6.1194 | -5.4206 | -0.8862 |  | -3.0873 | -2.5028 | 2.9046 | 2.3716 | 2.7929 | 0.6354 | 4.6034 | 5.8606 | 6.0995 | 4.4172 | -0.0001 | -0.0009 | 0.0004 | 0.0011 | 0.0005 | -0.0005 | 0.005 | -0.0072 | 0.0056 | -366.7286 | 7.6622 | -366.747 | 7.6992 | -366.2332 | 11.1363 | -366.2639 | 10.4197 | -363.0791 | 10.085 | -363.1191 | 8.5759
11:23 | 170 | 22.7248 | 89.2578 | 201.241 | 207.4958 | -9.6065 | -33.6157 | -0.5286 | -1.0632 | -3.882 | -4.1676 | -1.8595 | -2.8139 | 4.0667 | -2.8885 | 0.3965 | 0.3526 | 0.3727 | 0.2486 | -73.5871 |  | -1.2995 | -1.76 | -6.2795 | -5.5502 | -0.9699 |  | -3.0474 | -2.5556 | 2.9222 | 2.378 | 2.7995 | 0.6301 | 4.6539 | 5.9863 | 6.1334 | 4.4789 | -0.0005 | -0.0009 | 0.0003 | 0.0014 | 0.0001 | -0.0002 | 0.0063 | 0.0017 | -0.0017 | -366.6793 | 7.73 | -366.6793 | 7.7628 | -366.1501 | 11.2307 | -366.2147 | 10.5409 | -363.0452 | 10.1487 | -363.0175 | 8.656
11:23 | 171 | 22.697 | 90.17 | 203.2212 | 209.5684 | -9.7631 | -33.9424 | -0.4766 | -1.0402 | -3.9843 | -4.2741 | -1.899 | -2.8374 | 4.1357 | -2.9216 | 0.3963 | 0.3542 | 0.3741 | 0.2505 | -74.1195 |  | -1.2464 | -1.9345 | -6.3942 | -5.6391 | -1.0844 |  | -3.0604 | -2.5658 | 2.992 | 2.3966 | 2.8118 | 0.6282 | 4.7308 | 6.0863 | 6.2347 | 4.5031 | 0.0001 | -0.0009 | 0.0005 | 0.0017 | 0.0004 | -0.0006 | -0.0048 | -0.0124 | -0.0052 | -366.5963 | 7.7957 | -366.6117 | 7.8285 | -366.1039 | 11.3067 | -366.1901 | 10.6066 | -362.9006 | 10.2411 | -362.9191 | 8.7176
11:23 | 172 | 22.6408 | 91.012 | 205.335 | 211.5272 | -9.8693 | -34.0786 | -0.3956 | -1.0316 | -3.9615 | -4.2433 | -1.8797 | -2.8387 | 4.12 | -2.9712 | 0.3962 | 0.3541 | 0.3765 | 0.2512 | -74.8463 |  | -1.2543 | -1.9331 | -6.3724 | -5.7077 | -1.1031 |  | -3.0861 | -2.5388 | 2.9959 | 2.4012 | 2.8203 | 0.6281 | 4.759 | 6.1317 | 6.3004 | 4.5846 | 0.0001 | -0.0012 | -0.0003 | 0.0008 | 0.0001 | -0.0005 | -0.011 | -0.0065 | -0.0017 | -366.5563 | 7.8963 | -366.6055 | 7.9456 | -366.0578 | 11.3929 | -366.1408 | 10.6907 | -362.8114 | 10.3376 | -362.8483 | 8.8264
11:23 | 173 | 22.5671 | 91.9049 | 207.2166 | 213.4957 | -9.911 | -34.1727 | -0.4047 | -1.0222 | -4.043 | -4.3488 | -2.0108 | -2.811 | 4.0554 | -2.9972 | 0.3976 | 0.3559 | 0.3762 | 0.2531 | -75.6035 |  | -1.2258 | -1.96 | -6.4704 | -5.7597 | -1.0769 |  | -3.1386 | -2.6021 | 3.0026 | 2.4133 | 2.8272 | 0.6476 | 4.8549 | 6.2334 | 6.3931 | 4.633 | -0.0004 | -0.0008 | 0.0005 | 0.0022 | 0.0003 | -0.0004 | -0.0025 | -0.0151 | -0.0077 | -366.5316 | 8.003 | -366.5655 | 8.0441 | -366.0301 | 11.4463 | -366.0085 | 10.7482 | -362.7467 | 10.4423 | -362.7929 | 8.9229
11:23 | 174 | 22.436 | 92.6991 | 209.1413 | 215.3591 | -10.0674 | -34.2971 | -0.3108 | -0.9913 | -4.1248 | -4.5125 | -2.0098 | -2.8487 | 3.9981 | -2.978 | 0.3982 | 0.3537 | 0.3783 | 0.2536 | -76.3321 |  | -1.2051 | -2.0385 | -6.5435 | -5.7746 | -1.0844 |  | -3.1528 | -2.6878 | 3.0092 | 2.4221 | 2.8467 | 0.6492 | 4.8769 | 6.2437 | 6.4534 | 4.6732 | -0.0003 | -0.0007 | 0.0002 | 0.0016 | 0.0005 | -0.0004 | 0.0014 | -0.0088 | -0.0098 | -366.467 | 8.0729 | -366.544 | 8.1242 | -365.9654 | 11.5326 | -365.9654 | 10.8406 | -362.636 | 10.5121 | -362.7006 | 8.9865
11:23 | 175 | 22.3253 | 93.4999 | 210.8824 | 217.2437 | -10.1389 | -34.6392 | -0.3944 | -0.9817 | -4.1825 | -4.5082 | -1.988 | -2.9006 | 4.0547 | -2.9844 | 0.3982 | 0.3556 | 0.375 | 0.254 | -77.0729 |  | -1.3007 | -1.9431 | -6.473 | -5.7051 | -1.002 |  | -3.1945 | -2.8251 | 3.0176 | 2.4309 | 2.8626 | 0.6442 | 4.9504 | 6.3229 | 6.5025 | 4.701 | -0.0004 | -0.0013 | 0 | 0.0016 | 0.0001 | -0.0002 | -0.0046 | -0.0145 | -0.0093 | -366.4239 | 8.1365 | -366.427 | 8.1899 | -365.8947 | 11.6332 | -365.987 | 10.9207 | -362.5406 | 10.5675 | -362.5559 | 9.0646
11:23 | 176 | 22.2488 | 94.3221 | 212.7445 | 219.169 | -10.3746 | -34.7437 | -0.3419 | -0.9644 | -4.188 | -4.6592 | -1.9403 | -2.8648 | 3.9476 | -2.9642 | 0.397 | 0.3531 | 0.3764 | 0.254 | -77.7727 |  | -1.2368 | -1.9374 | -6.5666 | -5.7842 | -1.0398 |  | -3.1882 | -2.8206 | 3.0259 | 2.441 | 2.8654 | 0.64 | 4.9795 | 6.4099 | 6.5857 | 4.8273 | 0.0002 | -0.0016 | 0.0008 | 0.0021 | 0.0004 | -0.0006 | 0.0005 | -0.0072 | 0.0042 | -366.3409 | 8.1899 | -366.3316 | 8.2453 | -365.8454 | 11.7235 | -365.9316 | 11.0049 | -362.4267 | 10.625 | -362.4452 | 9.118
11:23 | 177 | 22.1993 | 95.0423 | 214.5692 | 220.8688 | -10.4706 | -34.858 | -0.3092 | -0.9762 | -4.2146 | -4.5659 | -2.0087 | -2.9018 | 3.914 | -2.9945 | 0.3985 | 0.3506 | 0.3767 | 0.2565 | -78.4202 |  | -1.3037 | -1.9543 | -6.6296 | -5.8522 | -1.0266 |  | -3.1677 | -2.8468 | 3.0357 | 2.4546 | 2.8665 | 0.6348 | 5.0472 | 6.4602 | 6.6522 | 4.832 | 0 | -0.0014 | 0.0004 | 0.0014 | 0.0003 | -0.0001 | 0.0079 | -0.0013 | 0.0052 | -366.267 | 8.2802 | -366.307 | 8.3542 | -365.8393 | 11.7892 | -365.8885 | 11.0747 | -362.3836 | 10.7113 | -362.359 | 9.2145
11:23 | 178 | 22.1413 | 95.9067 | 216.3875 | 222.7003 | -10.6364 | -35.0384 | -0.3641 | -1.0038 | -4.2663 | -4.7377 | -1.9871 | -2.9244 | 3.9816 | -2.9659 | 0.3984 | 0.3538 | 0.3802 | 0.257 | -79.0968 |  | -1.2256 | -2.0287 | -6.6994 | -5.8361 | -1.0003 |  | -3.2134 | -2.8002 | 3.0429 | 2.4606 | 2.8676 | 0.6362 | 5.0961 | 6.5437 | 6.6832 | 4.8637 | -0.0007 | -0.0013 | 0.0004 | 0.0017 | 0.0005 | -0.0006 | 0.0148 | 0.0015 | 0.0077 | -366.2301 | 8.3747 | -366.2824 | 8.4199 | -365.7562 | 11.8262 | -365.827 | 11.1322 | -362.2821 | 10.8119 | -362.3098 | 9.2699
11:23 | 179 | 21.9753 | 96.7014 | 218.1208 | 224.3994 | -10.7657 | -35.1849 | -0.3122 | -0.9903 | -4.3455 | -4.7776 | -2.1021 | -3.0306 | 3.8992 | -3.0542 | 0.3977 | 0.3584 | 0.3779 | 0.2591 | -79.824 |  | -1.3484 | -1.9911 | -6.7772 | -5.8991 | -1.0893 |  | -3.2331 | -2.875 | 3.0528 | 2.4679 | 2.8776 | 0.6441 | 5.1615 | 6.6497 | 6.8041 | 4.9797 | -0.0002 | -0.0006 | 0.0004 | 0.0016 | 0 | -0.0004 | 0.0115 | -0.015 | -0.0006 | -366.2301 | 8.4732 | -366.2639 | 8.4958 | -365.6731 | 11.8878 | -365.7685 | 11.2328 | -362.2575 | 10.9002 | -362.2482 | 9.3377
11:23 | 180 | 21.889 | 97.5027 | 219.9473 | 226.2305 | -10.8518 | -35.2909 | -0.2895 | -1.0831 | -4.4006 | -4.6891 | -2.1688 | -3.048 | 3.7837 | -3.1979 | 0.3976 | 0.3514 | 0.3792 | 0.2587 | -80.5345 |  | -1.288 | -2.04 | -6.7814 | -5.951 | -1.036 |  | -3.3181 | -2.7898 | 3.0611 | 2.478 | 2.8838 | 0.6399 | 5.2225 | 6.6932 | 6.8867 | 5.0064 | -0.0003 | -0.0017 | 0.0005 | 0.0021 | 0.0004 | -0.0009 | 0.0077 | -0.0129 | -0.0095 | -366.1593 | 8.5369 | -366.1778 | 8.5718 | -365.6547 | 11.9699 | -365.7131 | 11.2964 | -362.1498 | 10.9679 | -362.1559 | 9.4013
11:23 | 181 | 21.8948 | 98.4055 | 221.8157 | 228.1453 | -10.9336 | -35.4631 | -0.3616 | -1.05 | -4.4167 | -4.7421 | -2.2232 | -2.9882 | 3.7465 | -3.161 | 0.3998 | 0.355 | 0.3821 | 0.2616 | -81.215 |  | -1.4192 | -1.8991 | -6.7341 | -5.9649 | -1.1148 |  | -3.3029 | -2.8165 | 3.0684 | 2.4851 | 2.8896 | 0.635 | 5.2788 | 6.7726 | 6.9322 | 5.0682 | 0.0001 | -0.0011 | 0.0006 | 0.0022 | 0.0004 | -0.0002 | 0.0128 | -0.0123 | -0.0127 | -366.0485 | 8.5903 | -366.1562 | 8.6683 | -365.6423 | 12.0746 | -365.67 | 11.3622 | -362.0544 | 11.0254 | -362.0759 | 9.4916
11:23 | 182 | 21.7748 | 99.2408 | 223.805 | 230.0123 | -11.0795 | -35.6531 | -0.3144 | -1.0059 | -4.4307 | -4.792 | -2.1676 | -2.9906 | 3.8118 | -3.1775 | 0.4 | 0.3557 | 0.3825 | 0.2625 | -81.9621 |  | -1.3544 | -1.9236 | -6.8451 | -6.0555 | -1.0905 |  | -3.2844 | -2.742 | 3.0755 | 2.4953 | 2.8905 | 0.6357 | 5.3261 | 6.8431 | 7.0724 | 5.1269 | -0.0002 | -0.001 | 0.0002 | 0.0017 | 0 | -0.0007 | 0.0122 | -0.0198 | 0.0052 | -365.9993 | 8.6642 | -366.1193 | 8.771 | -365.63 | 12.1629 | -365.6116 | 11.4361 | -361.919 | 11.1075 | -361.9713 | 9.582
11:23 | 183 | 21.7298 | 100.0762 | 225.7505 | 231.9507 | -11.1923 | -35.8592 | -0.2508 | -0.9411 | -4.5618 | -4.8114 | -2.2267 | -2.9685 | 3.8211 | -3.1227 | 0.3991 | 0.3523 | 0.3853 | 0.263 | -82.6816 |  | -1.3412 | -1.986 | -6.8841 | -6.1083 | -1.1522 |  | -3.3181 | -2.8682 | 3.0853 | 2.5049 | 2.8913 | 0.631 | 5.4018 | 6.936 | 7.1182 | 5.1682 | -0.0005 | -0.0011 | 0 | 0.0019 | 0 | -0.0008 | 0.0196 | 0.0003 | 0.0188 | -365.9531 | 8.7504 | -366.0239 | 8.8079 | -365.5285 | 12.2245 | -365.5439 | 11.51 | -361.8328 | 11.1938 | -361.8697 | 9.6333
11:23 | 184 | 21.6768 | 100.8955 | 227.6396 | 233.8608 | -11.3406 | -36.1143 | -0.2582 | -0.8812 | -4.5851 | -4.7606 | -2.1877 | -3.0071 | 3.7072 | -3.1585 | 0.4003 | 0.3546 | 0.3864 | 0.2633 | -83.4044 |  | -1.3735 | -2.0137 | -6.9201 | -6.1006 | -1.1341 |  | -3.3118 | -2.883 | 3.0962 | 2.5199 | 2.8994 | 0.6282 | 5.4534 | 7.0165 | 7.1766 | 5.202 | 0.0001 | -0.0013 | 0.0003 | 0.0021 | 0 | -0.0001 | 0.0172 | -0.0144 | 0.0094 | -365.9808 | 8.8346 | -365.9685 | 8.8716 | -365.4577 | 12.3046 | -365.55 | 11.6373 | -361.7836 | 11.2821 | -361.7528 | 9.6888
11:23 | 185 | 21.5768 | 101.7778 | 229.4882 | 235.7252 | -11.3405 | -36.2468 | -0.2553 | -0.9658 | -4.6113 | -4.7722 | -2.2678 | -3.0452 | 3.7 | -3.2412 | 0.3985 | 0.357 | 0.3929 | 0.2652 | -84.1171 |  | -1.413 | -1.9954 | -7.0106 | -6.1661 | -1.1274 |  | -3.462 | -3.0328 | 3.1045 | 2.5325 | 2.896 | 0.6269 | 5.4907 | 7.048 | 7.2481 | 5.2568 | 0 | -0.0016 | 0.0001 | 0.0016 | 0.0003 | -0.0006 | -0.0084 | -0.0045 | -0.0022 | -365.907 | 8.9106 | -365.8762 | 8.9352 | -365.3839 | 12.3621 | -365.4762 | 11.7133 | -361.682 | 11.3539 | -361.6697 | 9.7565
11:23 | 186 | 21.5 | 102.5436 | 231.2593 | 237.4062 | -11.4849 | -36.303 | -0.2682 | -0.9744 | -4.711 | -4.9418 | -2.2855 | -3.011 | 3.6986 | -3.1777 | 0.3999 | 0.351 | 0.3909 | 0.2654 | -84.9173 |  | -1.4387 | -2.0659 | -7.0375 | -6.2095 | -1.1628 |  | -3.4482 | -2.9673 | 3.0967 | 2.5342 | 2.9045 | 0.6272 | 5.5115 | 7.0918 | 7.2722 | 5.319 | 0.0002 | -0.0011 | 0.0006 | 0.0018 | 0.0002 | -0.0004 | 0.0003 | -0.014 | -0.0066 | -365.8116 | 8.9886 | -365.8701 | 9.0502 | -365.3469 | 12.4442 | -365.4331 | 11.7564 | -361.5866 | 11.4402 | -361.6266 | 9.8489
11:23 | 187 | 21.4514 | 103.2952 | 232.9358 | 239.0477 | -11.5219 | -36.4564 | -0.1861 | -1.0183 | -4.6851 | -4.8988 | -2.26 | -3.0019 | 3.7305 | -3.233 | 0.3995 | 0.3502 | 0.3912 | 0.266 | -85.4707 |  | -1.4479 | -2.1933 | -7.0437 | -6.2862 | -1.1575 |  | -3.5203 | -2.9899 | 3.1021 | 2.5508 | 2.8967 | 0.6266 | 5.558 | 7.1673 | 7.3671 | 5.3646 | -0.0006 | -0.0013 | 0.0006 | 0.002 | 0.0008 | -0.0003 | -0.0043 | 0.0062 | -0.0256 | -365.787 | 9.0728 | -365.8824 | 9.1488 | -365.3808 | 12.512 | -365.3469 | 11.8057 | -361.5036 | 11.5182 | -361.5743 | 9.9516
11:23 | 188 | 21.3438 | 104.0966 | 234.508 | 240.6082 | -11.668 | -36.5077 | -0.1806 | -1.0258 | -4.7518 | -4.9066 | -2.2754 | -3.0751 | 3.6965 | -3.2111 | 0.3994 | 0.3471 | 0.3956 | 0.2688 | -86.1006 |  | -1.3692 | -2.2738 | -7.0778 | -6.2787 | -1.2573 |  | -3.4549 | -2.9582 | 3.1097 | 2.5788 | 2.9007 | 0.6287 | 5.6405 | 7.2496 | 7.4199 | 5.4068 | -0.0004 | -0.0011 | 0.0006 | 0.002 | 0.0003 | -0.0003 | 0.0085 | 0.0052 | 0.0023 | -365.6885 | 9.1303 | -365.8208 | 9.2124 | -365.31 | 12.5654 | -365.2885 | 11.8652 | -361.4328 | 11.5839 | -361.4666 | 9.9967
11:23 | 189 | 21.2483 | 104.7042 | 236.0559 | 242.2093 | -11.8721 | -36.6211 | -0.2012 | -1.0625 | -4.7818 | -5.0042 | -2.3412 | -3.0707 | 3.6877 | -3.3071 | 0.3993 | 0.3484 | 0.3989 | 0.2701 | -86.6962 |  | -1.4193 | -2.1214 | -7.1194 | -6.2185 | -1.2059 |  | -3.5038 | -3.0192 | 3.1195 | 2.5897 | 2.8981 | 0.6352 | 5.6885 | 7.315 | 7.4461 | 5.4427 | 0.0002 | -0.0013 | 0.0005 | 0.0028 | 0.0004 | 0 | 0.0038 | -0.0028 | 0.0022 | -365.6947 | 9.1898 | -365.6947 | 9.2699 | -365.2362 | 12.6331 | -365.3315 | 11.9535 | -361.3774 | 11.625 | -361.3435 | 10.0296
11:23 | 190 | 21.1815 | 105.5322 | 237.6872 | 243.8486 | -12.1103 | -36.8439 | -0.2677 | -1.0483 | -4.8315 | -5.0592 | -2.3277 | -3.1162 | 3.6109 | -3.3081 | 0.3985 | 0.3535 | 0.4011 | 0.2711 | -87.1926 |  | -1.3803 | -2.1292 | -7.2175 | -6.3554 | -1.2264 |  | -3.484 | -3.1148 | 3.1287 | 2.5912 | 2.8905 | 0.6448 | 5.7146 | 7.3468 | 7.5402 | 5.5676 | -0.0001 | -0.0013 | 0.0001 | 0.0021 | 0.0003 | -0.0008 | 0.0149 | -0.0028 | 0.0086 | -365.6023 | 9.2555 | -365.6608 | 9.3315 | -365.1808 | 12.7255 | -365.2885 | 12.0356 | -361.3066 | 11.6968 | -361.242 | 10.083
11:23 | 191 | 21.1499 | 106.2476 | 239.4247 | 245.5918 | -12.1725 | -37.1197 | -0.3169 | -1.0246 | -4.8664 | -5.063 | -2.3872 | -3.203 | 3.5381 | -3.38 | 0.4006 | 0.3562 | 0.4031 | 0.2733 | -87.881 |  | -1.4899 | -2.1195 | -7.2012 | -6.3398 | -1.2223 |  | -3.5959 | -3.0796 | 3.1406 | 2.5863 | 2.898 | 0.6671 | 5.7808 | 7.4072 | 7.6117 | 5.5934 | -0.0003 | -0.0014 | 0.0004 | 0.0021 | -0.0002 | -0.0002 | -0.0042 | -0.0116 | -0.0088 | -365.5562 | 9.3294 | -365.627 | 9.4198 | -365.1531 | 12.785 | -365.2146 | 12.0972 | -361.1651 | 11.7666 | -361.2051 | 10.1713
11:23 | 192 | 21.0997 | 107.0204 | 241.1575 | 247.4144 | -12.2624 | -37.2775 | -0.4502 | -1.024 | -4.9977 | -5.0466 | -2.4376 | -3.0597 | 3.5966 | -3.3706 | 0.3992 | 0.3499 | 0.4057 | 0.2752 | -88.4026 |  | -1.536 | -2.0813 | -7.2838 | -6.4252 | -1.1872 |  | -3.5529 | -3.1422 | 3.1507 | 2.5963 | 2.9113 | 0.6742 | 5.8503 | 7.5112 | 7.6348 | 5.6454 | -0.0007 | -0.0021 | 0.0004 | 0.0024 | 0.0002 | -0.0009 | 0.0127 | -0.0021 | -0.0218 | -365.5193 | 9.4485 | -365.6331 | 9.4978 | -365.1069 | 12.8364 | -365.1315 | 12.1485 | -361.1128 | 11.8837 | -361.1897 | 10.2493
11:23 | 193 | 21.0359 | 107.7106 | 242.8501 | 249.1505 | -12.38 | -37.4719 | -0.3437 | -0.9994 | -4.9833 | -5.1877 | -2.3723 | -3.1656 | 3.5856 | -3.3407 | 0.3995 | 0.3592 | 0.4082 | 0.2774 | -89.1784 |  | -1.6338 | -2.0779 | -7.2615 | -6.3921 | -1.2451 |  | -3.5957 | -3.2239 | 3.1588 | 2.6015 | 2.9137 | 0.6659 | 5.8798 | 7.5756 | 7.7466 | 5.6745 | -0.0002 | -0.0013 | 0.0003 | 0.0017 | 0.0002 | -0.0002 | -0.0078 | 0.0003 | -0.0184 | -365.5008 | 9.5224 | -365.6116 | 9.5902 | -365.0731 | 12.9062 | -365.0577 | 12.2348 | -361.0297 | 11.9617 | -361.1066 | 10.3335
11:23 | 194 | 20.9985 | 108.5808 | 244.7533 | 250.9694 | -12.4756 | -37.5868 | -0.3537 | -0.8863 | -5.0125 | -5.3234 | -2.3666 | -3.079 | 3.5677 | -3.3832 | 0.4004 | 0.3598 | 0.4096 | 0.2794 | -89.6752 |  | -1.4768 | -2.1865 | -7.3339 | -6.4617 | -1.2252 |  | -3.6073 | -3.1091 | 3.1635 | 2.6127 | 2.9252 | 0.6599 | 5.9117 | 7.5784 | 7.8117 | 5.707 | 0 | -0.0018 | 0.0006 | 0.0016 | 0.0004 | -0.0008 | 0.0061 | 0.0031 | -0.0163 | -365.4085 | 9.5656 | -365.5039 | 9.6456 | -365.0023 | 12.9965 | -365.0423 | 12.3087 | -360.9712 | 12.0007 | -360.962 | 10.3786
11:23 | 195 | 20.974 | 109.3723 | 246.7123 | 252.723 | -12.436 | -37.5391 | -0.2236 | -0.9495 | -5.0207 | -5.1496 | -2.4388 | -3.2417 | 3.4933 | -3.523 | 0.4003 | 0.3558 | 0.4111 | 0.2818 | -90.2627 |  | -1.5616 | -2.1502 | -7.4506 | -6.5331 | -1.235 |  | -3.6225 | -3.0813 | 3.1677 | 2.6149 | 2.9263 | 0.6567 | 5.9557 | 7.6862 | 7.8815 | 5.7325 | -0.0002 | -0.0013 | 0.0007 | 0.0024 | -0.0001 | -0.0007 | 0.0147 | -0.0112 | 0.0022 | -365.3192 | 9.6313 | -365.4516 | 9.7216 | -364.9961 | 13.1074 | -365.0484 | 12.399 | -360.845 | 12.0705 | -360.8635 | 10.4608
11:23 | 196 | 20.938 | 110.2691 | 248.5422 | 254.6773 | -12.691 | -37.7515 | -0.2524 | -0.9746 | -4.9504 | -5.2099 | -2.3484 | -3.1713 | 3.501 | -3.4177 | 0.4001 | 0.3693 | 0.4175 | 0.2847 | -90.8674 |  | -1.5212 | -2.295 | -7.5445 | -6.5328 | -1.3407 |  | -3.6516 | -3.1552 | 3.1796 | 2.6152 | 2.9372 | 0.6645 | 6.0256 | 7.7674 | 8.0141 | 5.8026 | -0.0004 | -0.001 | 0.0003 | 0.0021 | 0.0002 | -0.0006 | -0.0023 | -0.0053 | -0.0112 | -365.3131 | 9.6929 | -365.3777 | 9.8037 | -364.9531 | 13.1731 | -364.9254 | 12.4688 | -360.7527 | 12.1444 | -360.7589 | 10.547
11:23 | 197 | 20.8319 | 111.0168 | 250.2434 | 256.4906 | -12.7255 | -37.9831 | -0.2001 | -0.9949 | -5.0832 | -5.3102 | -2.405 | -3.1501 | 3.4854 | -3.4548 | 0.4019 | 0.3883 | 0.4257 | 0.2859 | -91.3169 |  | -1.567 | -2.257 | -7.5451 | -6.5783 | -1.3449 |  | -3.7086 | -3.2441 | 3.1885 | 2.6178 | 2.9472 | 0.7076 | 6.0624 | 7.8621 | 8.0282 | 5.9028 | -0.0004 | -0.0015 | -0.0001 | 0.0018 | 0.0005 | -0.0005 | 0.016 | 0.0055 | -0.0015 | -365.2454 | 9.7935 | -365.3254 | 9.8612 | -364.8546 | 13.2121 | -364.9223 | 12.5571 | -360.6666 | 12.2574 | -360.7127 | 10.6045
11:23 | 198 | 20.7861 | 111.8633 | 252.1766 | 258.4387 | -12.8626 | -38.0704 | -0.1223 | -1.0173 | -5.0947 | -5.3921 | -2.5161 | -3.16 | 3.4135 | -3.412 | 0.4005 | 0.3791 | 0.4268 | 0.289 | -91.7005 |  | -1.6033 | -2.319 | -7.5533 | -6.5961 | -1.351 |  | -3.7574 | -3.2988 | 3.1969 | 2.6381 | 2.9445 | 0.7078 | 6.1112 | 7.9226 | 8.12 | 5.939 | 0.0002 | -0.0014 | 0.0008 | 0.0025 | 0.0008 | 0 | -0.0048 | -0.0003 | -0.0277 | -365.2515 | 9.8859 | -365.3162 | 9.9413 | -364.7777 | 13.2901 | -364.8577 | 12.6536 | -360.6358 | 12.3436 | -360.6327 | 10.6723
11:23 | 199 | 20.6798 | 112.775 | 254.0869 | 260.2923 | -12.9801 | -38.2453 | -0.161 | -0.941 | -5.1073 | -5.4392 | -2.4935 | -3.0922 | 3.4681 | -3.4807 | 0.4007 | 0.3714 | 0.4317 | 0.291 | -92.0436 |  | -1.6401 | -2.3196 | -7.682 | -6.6453 | -1.3136 |  | -3.7861 | -3.2966 | 3.206 | 2.6481 | 2.9496 | 0.7052 | 6.1518 | 7.9745 | 8.2212 | 5.9807 | -0.0002 | -0.0021 | 0.0007 | 0.0022 | 0.0005 | -0.0003 | -0.0001 | -0.0049 | -0.015 | -365.1685 | 9.9393 | -365.2115 | 10.0009 | -364.713 | 13.3784 | -364.8023 | 12.7132 | -360.5158 | 12.4114 | -360.5004 | 10.738
11:23 | 200 | 20.6524 | 113.5909 | 256.0066 | 262.2002 | -13.0664 | -38.2595 | -0.1487 | -0.9904 | -5.1818 | -5.5299 | -2.5416 | -3.0639 | 3.5178 | -3.3801 | 0.4015 | 0.3682 | 0.4367 | 0.2954 | -92.2534 |  | -1.574 | -2.2984 | -7.7044 | -6.6775 | -1.3212 |  | -3.7489 | -3.2807 | 3.2095 | 2.655 | 2.9551 | 0.7023 | 6.1793 | 8.0249 | 8.2233 | 6.0495 | -0.0007 | -0.0016 | 0.0002 | 0.002 | -0.0002 | -0.0004 | 0.0007 | -0.0023 | -0.0224 | -365.0823 | 9.9926 | -365.2208 | 10.1097 | -364.75 | 13.4688 | -364.753 | 12.7727 | -360.3927 | 12.4791 | -360.445 | 10.8509
11:23 | 201 | 20.5454 | 114.3779 | 257.856 | 264.0829 | -13.2136 | -38.3386 | -0.244 | -0.914 | -5.1453 | -5.4605 | -2.5135 | -3.145 | 3.3711 | -3.4819 | 0.4016 | 0.3641 | 0.4445 | 0.2978 | -92.5672 |  | -1.5694 | -2.3503 | -7.6563 | -6.595 | -1.27 |  | -3.7164 | -3.2912 | 3.212 | 2.6619 | 2.9566 | 0.7008 | 6.2327 | 8.1479 | 8.3138 | 6.0962 | -0.0006 | -0.0018 | 0.0008 | 0.0025 | 0.0004 | -0.0005 | 0.0071 | -0.0161 | -0.0269 | -365.07 | 10.0645 | -365.1531 | 10.1754 | -364.7315 | 13.5632 | -364.6977 | 12.8302 | -360.3096 | 12.5551 | -360.3927 | 10.9453
11:23 | 202 | 20.5505 | 115.2054 | 259.7585 | 265.9565 | -13.2341 | -38.4556 | -0.2002 | -0.9085 | -5.2314 | -5.4262 | -2.4532 | -3.1512 | 3.4872 | -3.497 | 0.4024 | 0.3647 | 0.4506 | 0.3017 | -92.993 |  | -1.5473 | -2.3116 | -7.6521 | -6.6909 | -1.2747 |  | -3.7271 | -3.3112 | 3.2155 | 2.6664 | 2.9598 | 0.6936 | 6.3 | 8.1573 | 8.3576 | 6.1347 | -0.0001 | -0.0017 | 0.0005 | 0.002 | 0 | -0.0004 | 0.0032 | -0.0034 | -0.0062 | -364.9931 | 10.1282 | -365.07 | 10.2123 | -364.6053 | 13.6289 | -364.6761 | 12.937 | -360.2419 | 12.6331 | -360.2573 | 10.9782
11:23 | 203 | 20.4678 | 116.1036 | 261.8347 | 267.8702 | -13.2929 | -38.7037 | -0.166 | -0.9409 | -5.2981 | -5.4986 | -2.5719 | -3.1334 | 3.4455 | -3.5199 | 0.4023 | 0.3678 | 0.4539 | 0.3042 | -93.3824 |  | -1.6072 | -2.3566 | -7.7051 | -6.7306 | -1.306 |  | -3.7795 | -3.3429 | 3.2212 | 2.6711 | 2.967 | 0.6855 | 6.3589 | 8.2278 | 8.4341 | 6.2339 | 0.0004 | -0.0017 | 0.0007 | 0.0025 | 0.0007 | -0.0008 | 0.0025 | -0.0118 | -0.0036 | -365.0238 | 10.1959 | -364.9777 | 10.2657 | -364.5315 | 13.6946 | -364.6392 | 13.0417 | -360.2173 | 12.7173 | -360.1527 | 11.046
11:23 | 204 | 20.4824 | 117.0358 | 263.6437 | 269.7952 | -13.4276 | -38.7727 | 0.0059 | -0.8467 | -5.3006 | -5.4741 | -2.6281 | -3.1922 | 3.2694 | -3.5723 | 0.4026 | 0.3631 | 0.4585 | 0.3098 | -93.6709 |  | -1.5364 | -2.3593 | -7.7048 | -6.7282 | -1.2921 |  | -3.7585 | -3.408 | 3.2288 | 2.6804 | 2.976 | 0.6759 | 6.4508 | 8.3486 | 8.6321 | 6.3537 | -0.0001 | -0.0015 | 0.0007 | 0.0021 | 0.0005 | 0 | 0.002 | -0.004 | -0.024 | -364.9438 | 10.2657 | -364.9407 | 10.3417 | -364.4669 | 13.785 | -364.5746 | 13.1115 | -360.0665 | 12.7933 | -360.0542 | 11.1199
11:23 | 205 | 20.3963 | 118.0145 | 265.6129 | 271.8644 | -13.5662 | -38.9191 | -0.1024 | -0.8967 | -5.3918 | -5.5163 | -2.6287 | -3.2149 | 3.2776 | -3.5757 | 0.4027 | 0.3609 | 0.4689 | 0.3124 | -94.1011 |  | -1.6095 | -2.2911 | -7.7607 | -6.7649 | -1.1858 |  | -3.7542 | -3.4271 | 3.2376 | 2.6897 | 2.9783 | 0.6623 | 6.4783 | 8.3993 | 8.6198 | 6.3462 | -0.0002 | -0.0012 | 0.0001 | 0.0017 | 0.0006 | -0.0008 | -0.0052 | -0.0117 | -0.017 | -364.833 | 10.3417 | -364.9254 | 10.4382 | -364.4884 | 13.8527 | -364.4669 | 13.1567 | -359.9773 | 12.8815 | -359.9957 | 11.2246
11:23 | 206 | 20.3388 | 118.8968 | 267.5811 | 273.7248 | -13.7364 | -39.1834 | -0.1621 | -0.9321 | -5.4314 | -5.7152 | -2.6812 | -3.2021 | 3.3505 | -3.489 | 0.4035 | 0.3646 | 0.4748 | 0.3164 | -94.3529 |  | -1.5059 | -2.3258 | -7.8003 | -6.8289 | -1.2854 |  | -3.7187 | -3.3892 | 3.2503 | 2.6825 | 2.9855 | 0.6544 | 6.569 | 8.5072 | 8.6803 | 6.4027 | 0.0001 | -0.0015 | 0.0003 | 0.0022 | 0.0003 | -0.0004 | -0.0033 | -0.0079 | -0.0161 | -364.79 | 10.4197 | -364.8884 | 10.5429 | -364.4453 | 13.9287 | -364.3992 | 13.2306 | -359.848 | 12.9822 | -359.9219 | 11.3211
11:23 | 207 | 20.3075 | 119.9014 | 269.6148 | 275.6666 | -13.7619 | -39.3297 | -0.1364 | -0.8694 | -5.4537 | -5.7922 | -2.6653 | -3.1314 | 3.2753 | -3.6673 | 0.4033 | 0.368 | 0.4782 | 0.3197 | -94.7162 |  | -1.6481 | -2.3108 | -7.8436 | -6.7969 | -1.2403 |  | -3.855 | -3.574 | 3.2682 | 2.6357 | 2.9859 | 0.6484 | 6.6587 | 8.5565 | 8.7658 | 6.4686 | 0.0004 | -0.0012 | 0.0004 | 0.0024 | 0.0005 | 0.0001 | 0.0204 | -0.001 | 0.0029 | -364.75 | 10.4895 | -364.8023 | 10.6045 | -364.3284 | 14.0355 | -364.4084 | 13.3374 | -359.765 | 13.0663 | -359.8296 | 11.3909
11:23 | 208 | 20.2213 | 120.6884 | 271.5392 | 277.7656 | -13.9173 | -39.5288 | -0.1169 | -0.8979 | -5.4576 | -5.9355 | -2.5779 | -3.2188 | 3.2055 | -3.6557 | 0.4038 | 0.3614 | 0.4847 | 0.3247 | -94.9749 |  | -1.7306 | -2.3561 | -7.8722 | -6.863 | -1.2702 |  | -3.8896 | -3.4948 | 3.2813 | 2.665 | 2.9744 | 0.6769 | 6.6439 | 8.5933 | 8.7994 | 6.4955 | -0.0002 | -0.0017 | 0.0001 | 0.0022 | 0.0005 | -0.0004 | 0.0054 | -0.0027 | 0.0075 | -364.7438 | 10.547 | -364.6946 | 10.6517 | -364.2761 | 14.1422 | -364.3684 | 13.4503 | -359.7219 | 13.132 | -359.6603 | 11.4504
11:23 | 209 | 20.1865 | 121.6586 | 273.6022 | 279.7826 | -13.9653 | -39.6374 | -0.0927 | -0.8275 | -5.4506 | -5.8206 | -2.6197 | -3.2238 | 3.1858 | -3.6387 | 0.4042 | 0.3621 | 0.4908 | 0.3287 | -95.3986 |  | -1.7456 | -2.4585 | -7.8703 | -6.8923 | -1.1253 |  | -3.9528 | -3.4906 | 3.2909 | 2.6592 | 2.9825 | 0.6869 | 6.6894 | 8.685 | 8.9248 | 6.5357 | -0.0006 | -0.0015 | 0.0007 | 0.0027 | 0.0001 | -0.0002 | 0.0079 | -0.0157 | -0.0116 | -364.6823 | 10.6168 | -364.6269 | 10.7318 | -364.2299 | 14.2264 | -364.3284 | 13.5242 | -359.608 | 13.2183 | -359.5742 | 11.5367
11:23 | 210 | 20.1241 | 122.6286 | 275.6653 | 281.7946 | -14.0337 | -39.7419 | -0.0601 | -0.8246 | -5.4354 | -5.806 | -2.5897 | -3.2815 | 3.1053 | -3.7382 | 0.405 | 0.3646 | 0.4953 | 0.3307 | -95.7998 |  | -1.6846 | -2.4184 | -7.9235 | -6.9017 | -1.252 |  | -3.9556 | -3.5307 | 3.3042 | 2.6576 | 2.9856 | 0.6786 | 6.7802 | 8.7878 | 8.9684 | 6.6766 | 0.0002 | -0.0014 | 0.0005 | 0.0021 | 0.0003 | -0.0007 | 0.0057 | 0.0031 | -0.0061 | -364.6484 | 10.7133 | -364.6269 | 10.8242 | -364.1838 | 14.2921 | -364.2022 | 13.6022 | -359.5188 | 13.3435 | -359.5342 | 11.6373
11:23 | 211 | 19.9693 | 123.5512 | 277.7152 | 283.8666 | -14.1661 | -39.9023 | -0.0923 | -0.7964 | -5.5822 | -5.8267 | -2.5762 | -3.2718 | 3.0975 | -3.775 | 0.4066 | 0.3649 | 0.5035 | 0.3357 | -96.2646 |  | -1.7742 | -2.4896 | -7.9504 | -7.0379 | -1.3495 |  | -3.9872 | -3.4935 | 3.3145 | 2.6515 | 2.9986 | 0.6738 | 6.8032 | 8.8275 | 9.101 | 6.7018 | 0.0001 | -0.0017 | 0.0006 | 0.0029 | 0.0001 | -0.0005 | 0.025 | -0.0111 | 0.0215 | -364.5469 | 10.7975 | -364.6084 | 10.9145 | -364.1376 | 14.364 | -364.153 | 13.6782 | -359.4234 | 13.4421 | -359.448 | 11.7317
11:23 | 212 | 19.9706 | 124.3785 | 279.7555 | 285.7783 | -14.4035 | -40.0658 | -0.0472 | -0.7384 | -5.6202 | -5.9184 | -2.6118 | -3.3035 | 3.0509 | -3.759 | 0.4072 | 0.37 | 0.5081 | 0.3405 | -96.624 |  | -1.78 | -2.5259 | -8.0193 | -7.0097 | -1.3367 |  | -4.0417 | -3.5704 | 3.3207 | 2.6512 | 3.004 | 0.6681 | 6.8605 | 8.9141 | 9.1691 | 6.7398 | 0.0004 | -0.0014 | 0.0006 | 0.002 | 0.0009 | -0.0003 | -0.0089 | -0.0138 | -0.0195 | -364.5161 | 10.8632 | -364.513 | 10.9741 | -364.0884 | 14.4482 | -364.1099 | 13.7747 | -359.2665 | 13.5037 | -359.3465 | 11.8139
11:23 | 213 | 19.8719 | 125.309 | 281.6963 | 287.7663 | -14.4901 | -40.2941 | -0.0696 | -0.8126 | -5.6882 | -5.9243 | -2.6002 | -3.3429 | 3.0428 | -3.8407 | 0.408 | 0.3717 | 0.5168 | 0.3451 | -97.0935 |  | -1.7127 | -2.5972 | -8.1522 | -7.0829 | -1.3504 |  | -4.1211 | -3.6236 | 3.3169 | 2.6565 | 3.0091 | 0.6657 | 6.9873 | 8.9944 | 9.2418 | 6.8499 | -0.0002 | -0.0016 | 0.0002 | 0.002 | 0.0001 | -0.0006 | 0.0055 | 0.0005 | -0.0245 | -364.4422 | 10.9063 | -364.4053 | 11.0357 | -364.0299 | 14.5632 | -364.113 | 13.8753 | -359.1926 | 13.5797 | -359.208 | 11.8816
11:23 | 214 | 19.9146 | 126.3592 | 283.872 | 289.8715 | -14.4749 | -40.4461 | -0.1533 | -0.8499 | -5.7159 | -5.8982 | -2.6402 | -3.3623 | 2.9833 | -3.8092 | 0.4106 | 0.3802 | 0.5221 | 0.3522 | -97.5797 |  | -1.7108 | -2.5443 | -8.1076 | -7.1541 | -1.3263 |  | -4.0684 | -3.6343 | 3.3259 | 2.6693 | 3.0034 | 0.67 | 7.0177 | 9.0941 | 9.3292 | 6.8921 | -0.0006 | -0.0013 | 0.0007 | 0.0022 | 0.0003 | -0.0006 | 0.0178 | -0.0018 | 0.0065 | -364.4176 | 10.9967 | -364.3684 | 11.1178 | -363.993 | 14.635 | -364.0761 | 13.9821 | -359.1003 | 13.67 | -359.1495 | 11.974
11:23 | 215 | 19.7546 | 127.1644 | 285.7173 | 291.8402 | -14.5845 | -40.3989 | 0.0248 | -0.7842 | -5.8486 | -6.0556 | -2.7754 | -3.4029 | 2.9101 | -3.8292 | 0.4097 | 0.385 | 0.5306 | 0.3565 | -97.9992 |  | -1.7025 | -2.5798 | -8.1932 | -7.119 | -1.3824 |  | -4.0392 | -3.5983 | 3.3387 | 2.6852 | 2.9888 | 0.6741 | 7.0464 | 9.1463 | 9.3737 | 6.9597 | -0.0001 | -0.0018 | 0.0011 | 0.0029 | 0.0008 | -0.0004 | 0.0076 | 0.0037 | -0.0277 | -364.353 | 11.1034 | -364.3099 | 11.1979 | -363.9222 | 14.6843 | -363.9499 | 14.0581 | -359.0264 | 13.7665 | -359.0449 | 12.052
11:23 | 216 | 19.6804 | 128.125 | 287.8471 | 293.8912 | -14.6421 | -40.4626 | 0.1986 | -0.7887 | -5.8034 | -5.9497 | -2.7163 | -3.4206 | 2.9261 | -3.8067 | 0.412 | 0.381 | 0.5367 | 0.3638 | -98.3706 |  | -1.6878 | -2.4782 | -8.2116 | -7.0948 | -1.3148 |  | -4.1263 | -3.7024 | 3.3539 | 2.692 | 3.0188 | 0.6729 | 7.1551 | 9.2546 | 9.508 | 6.977 | -0.0003 | -0.0021 | 0.0001 | 0.0023 | -0.0001 | -0.0002 | 0.0195 | -0.0157 | -0.0088 | -364.3069 | 11.2041 | -364.2884 | 11.2841 | -363.8668 | 14.7459 | -363.8822 | 14.1176 | -358.9126 | 13.8774 | -358.9834 | 12.1321
11:23 | 217 | 19.6088 | 128.9902 | 289.857 | 295.8927 | -14.7831 | -40.6556 | 0.2238 | -0.8824 | -5.8597 | -6.0979 | -2.6949 | -3.4383 | 2.9098 | -4.0009 | 0.4116 | 0.3783 | 0.5452 | 0.3672 | -98.7541 |  | -1.7677 | -2.4476 | -8.229 | -7.1344 | -1.3149 |  | -4.1322 | -3.7208 | 3.3683 | 2.6957 | 3.0261 | 0.6733 | 7.1806 | 9.3035 | 9.5313 | 7.03 | -0.0001 | -0.0019 | 0.0008 | 0.0029 | 0.0005 | -0.0005 | 0.0129 | -0.0122 | 0.0121 | -364.2699 | 11.2656 | -364.2207 | 11.3642 | -363.8422 | 14.8444 | -363.833 | 14.2264 | -358.8787 | 13.9595 | -358.8726 | 12.2225
11:23 | 218 | 19.5216 | 129.8657 | 291.8295 | 297.83 | -14.8332 | -40.8115 | 0.1737 | -0.9627 | -5.9575 | -6.0715 | -2.7027 | -3.4483 | 2.9408 | -3.9052 | 0.4129 | 0.3734 | 0.5568 | 0.372 | -99.2614 |  | -1.7707 | -2.4879 | -8.2134 | -7.2497 | -1.2564 |  | -4.1435 | -3.8218 | 3.372 | 2.7049 | 3.0332 | 0.6712 | 7.2333 | 9.356 | 9.692 | 7.1065 | -0.0004 | -0.0016 | 0.0005 | 0.003 | 0.0002 | -0.0006 | 0.0152 | -0.0064 | -0.0146 | -364.1838 | 11.3067 | -364.1499 | 11.4381 | -363.7683 | 14.9574 | -363.796 | 14.2942 | -358.7003 | 14.017 | -358.728 | 12.3005
11:23 | 219 | 19.5024 | 130.7337 | 293.7783 | 299.8153 | -14.8274 | -40.982 | 0.1188 | -0.9487 | -5.9673 | -6.1987 | -2.8001 | -3.5246 | 2.8752 | -3.9881 | 0.4135 | 0.3743 | 0.5583 | 0.3754 | -99.7286 |  | -1.711 | -2.4524 | -8.2306 | -7.1977 | -1.3043 |  | -4.1677 | -3.8166 | 3.3601 | 2.7198 | 3.0276 | 0.6669 | 7.3248 | 9.4994 | 9.7428 | 7.2152 | 0 | -0.0018 | 0.0002 | 0.0021 | 0.0004 | -0.0004 | -0.0086 | -0.0064 | 0.0046 | -364.0915 | 11.3683 | -364.0822 | 11.5305 | -363.7591 | 15.0477 | -363.7899 | 14.3845 | -358.5649 | 14.0909 | -358.6356 | 12.3949
11:23 | 220 | 19.3022 | 131.6547 | 295.6385 | 301.7736 | -14.9745 | -41.1075 | 0.1138 | -0.8595 | -5.9992 | -6.2371 | -2.775 | -3.632 | 2.9054 | -4.0663 | 0.4145 | 0.3806 | 0.5666 | 0.3826 | -100.2343 |  | -1.7277 | -2.4688 | -8.3404 | -7.2736 | -1.3061 |  | -4.1993 | -3.8959 | 3.3702 | 2.718 | 3.036 | 0.6647 | 7.3606 | 9.5063 | 9.7846 | 7.2451 | -0.0002 | -0.0023 | 0.0005 | 0.0025 | 0.0006 | -0.0002 | 0.0048 | -0.0071 | 0.0013 | -364.1161 | 11.4792 | -364.0422 | 11.6209 | -363.6914 | 15.1216 | -363.713 | 14.4892 | -358.5587 | 14.2121 | -358.5372 | 12.4812
11:23 | 221 | 19.2853 | 132.5726 | 297.7365 | 303.8383 | -15.1335 | -41.1972 | 0.1682 | -0.8866 | -6.0705 | -6.2808 | -2.7426 | -3.5951 | 2.9499 | -4.0298 | 0.4149 | 0.3776 | 0.5747 | 0.3866 | -100.8102 |  | -1.7293 | -2.3887 | -8.2746 | -7.2936 | -1.3298 |  | -4.2894 | -3.8384 | 3.381 | 2.7333 | 3.0417 | 0.6698 | 7.3763 | 9.6259 | 9.8964 | 7.2848 | 0 | -0.0022 | -0.0001 | 0.0022 | 0.0002 | -0.0008 | 0.0132 | -0.0115 | -0.0024 | -364.0915 | 11.5777 | -364.0022 | 11.6783 | -363.5591 | 15.1771 | -363.6606 | 14.6042 | -358.4941 | 14.3168 | -358.4787 | 12.5407
11:23 | 222 | 19.2645 | 133.5252 | 299.9746 | 305.897 | -15.2127 | -41.3798 | 0.1579 | -0.8306 | -6.1363 | -6.3717 | -2.7472 | -3.6616 | 2.8778 | -4.0876 | 0.4155 | 0.3776 | 0.5823 | 0.3914 | -101.4198 |  | -1.7781 | -2.4385 | -8.3905 | -7.3661 | -1.3167 |  | -4.2927 | -3.9062 | 3.3939 | 2.7463 | 3.0513 | 0.6784 | 7.4441 | 9.6822 | 9.9197 | 7.3576 | -0.0004 | -0.0016 | 0.0005 | 0.0025 | 0.0005 | -0.0006 | 0.0225 | -0.0067 | -0.0028 | -364.0145 | 11.6496 | -363.9222 | 11.7502 | -363.516 | 15.2756 | -363.5899 | 14.6864 | -358.3741 | 14.4009 | -358.3649 | 12.6249
11:23 | 223 | 19.2117 | 134.3881 | 301.9222 | 307.8318 | -15.4843 | -41.5564 | 0.2278 | -0.7835 | -6.1218 | -6.3365 | -2.7383 | -3.7002 | 2.8607 | -4.0114 | 0.4148 | 0.3799 | 0.5896 | 0.3938 | -101.9923 |  | -1.8262 | -2.4163 | -8.4591 | -7.3861 | -1.3737 |  | -4.299 | -3.8653 | 3.4067 | 2.7704 | 3.0606 | 0.6942 | 7.5482 | 9.74 | 10.0528 | 7.4327 | -0.0008 | -0.0021 | 0.0008 | 0.0026 | 0.0003 | -0.0004 | 0.0034 | -0.0033 | -0.0124 | -363.9037 | 11.7174 | -363.8791 | 11.857 | -363.5222 | 15.3721 | -363.5222 | 14.7582 | -358.2264 | 14.4749 | -358.3095 | 12.7337
11:23 | 224 | 19.0719 | 135.3257 | 303.8459 | 309.8032 | -15.6038 | -41.7238 | 0.1747 | -0.7694 | -6.2061 | -6.3649 | -2.7718 | -3.7035 | 2.8167 | -4.0858 | 0.4151 | 0.4001 | 0.5964 | 0.3973 | -102.6409 |  | -1.7582 | -2.5077 | -8.5833 | -7.5364 | -1.3773 |  | -4.3564 | -3.9923 | 3.4181 | 2.7874 | 3.0678 | 0.6982 | 7.5488 | 9.8444 | 10.0629 | 7.4571 | -0.0001 | -0.0022 | 0.0003 | 0.0025 | 0.0008 | -0.0001 | 0.0022 | -0.0043 | -0.0125 | -363.8576 | 11.779 | -363.7745 | 11.9596 | -363.4822 | 15.4666 | -363.5037 | 14.8301 | -358.0941 | 14.5447 | -358.1802 | 12.8282
11:23 | 225 | 19.0643 | 136.2052 | 305.8212 | 311.82 | -15.5186 | -41.7829 | 0.1584 | -0.7461 | -6.2714 | -6.4459 | -2.8423 | -3.7466 | 2.7523 | -4.056 | 0.4165 | 0.4251 | 0.6027 | 0.4015 | -103.1812 |  | -1.8844 | -2.52 | -8.5488 | -7.5156 | -1.3995 |  | -4.3111 | -3.8794 | 3.4295 | 2.8005 | 3.0755 | 0.7121 | 7.6141 | 9.8926 | 10.1769 | 7.5329 | 0.0001 | -0.0023 | 0.001 | 0.0031 | 0.0001 | -0.0003 | -0.0047 | -0.0135 | -0.0189 | -363.8453 | 11.8652 | -363.7222 | 12.011 | -363.4237 | 15.5364 | -363.4237 | 14.8999 | -358.0233 | 14.6309 | -358.0756 | 12.8959
11:23 | 226 | 18.9324 | 137.0917 | 307.6941 | 313.766 | -15.6884 | -41.8813 | 0.0978 | -0.7918 | -6.3342 | -6.5755 | -2.9447 | -3.7152 | 2.7661 | -4.0972 | 0.4182 | 0.4218 | 0.6141 | 0.406 | -103.8127 |  | -1.811 | -2.5521 | -8.5612 | -7.4908 | -1.4063 |  | -4.3446 | -4.0135 | 3.4442 | 2.8315 | 3.0803 | 0.7107 | 7.7593 | 10.0322 | 10.3244 | 7.6367 | -0.0002 | -0.0019 | 0.0003 | 0.0024 | 0.0005 | -0.0006 | 0.0042 | -0.012 | -0.0114 | -363.8022 | 11.9453 | -363.6883 | 12.0746 | -363.3006 | 15.6103 | -363.4052 | 15.0375 | -358.011 | 14.7171 | -357.9864 | 12.9575
11:23 | 227 | 18.905 | 138.0186 | 309.7537 | 315.6645 | -15.8629 | -42.1044 | 0.2532 | -0.8649 | -6.3648 | -6.6211 | -2.9488 | -3.7225 | 2.72 | -4.1516 | 0.4197 | 0.4151 | 0.6194 | 0.407 | -104.3176 |  | -1.8112 | -2.5854 | -8.672 | -7.611 | -1.4582 |  | -4.3965 | -4.0352 | 3.4579 | 2.8183 | 3.0858 | 0.7084 | 7.7636 | 10.0766 | 10.2849 | 7.6539 | 0.0001 | -0.0016 | 0 | 0.0023 | 0 | -0.0004 | 0 | 0.008 | 0.0045 | -363.796 | 12.0356 | -363.6422 | 12.1465 | -363.2514 | 15.6883 | -363.3775 | 15.1093 | -357.9371 | 14.8075 | -357.8787 | 13.0273
11:24 | 228 | 18.8881 | 138.9288 | 311.9203 | 317.9143 | -15.9243 | -42.3025 | 0.2073 | -0.8607 | -6.3596 | -6.7616 | -2.9474 | -3.8381 | 2.6448 | -4.2479 | 0.4194 | 0.41 | 0.6253 | 0.409 | -104.9201 |  | -1.7732 | -2.5495 | -8.6975 | -7.7342 | -1.4926 |  | -4.4072 | -4.0217 | 3.4725 | 2.8181 | 3.0923 | 0.7067 | 7.773 | 10.1091 | 10.4038 | 7.7153 | -0.0003 | -0.0021 | 0.0008 | 0.0026 | 0.0003 | -0.0012 | 0.0152 | -0.011 | -0.0022 | -363.7068 | 12.1177 | -363.5899 | 12.2368 | -363.2206 | 15.7725 | -363.3006 | 15.1709 | -357.7463 | 14.8855 | -357.8079 | 13.1156
11:24 | 229 | 18.7387 | 140.0267 | 314.1264 | 320.2826 | -15.9746 | -42.4021 | 0.2251 | -0.8282 | -6.4427 | -6.6711 | -3.0333 | -3.7929 | 2.6422 | -4.2504 | 0.4219 | 0.4105 | 0.6346 | 0.4121 | -105.4398 |  | -1.8111 | -2.6258 | -8.7375 | -7.7197 | -1.4815 |  | -4.4753 | -4.002 | 3.4773 | 2.826 | 3.0634 | 0.6995 | 7.8364 | 10.2303 | 10.5029 | 7.7725 | 0.0003 | -0.0019 | 0.0001 | 0.0018 | 0.0003 | -0.0004 | -0.0093 | -0.0142 | -0.0063 | -363.596 | 12.1896 | -363.5622 | 12.3641 | -363.2452 | 15.8423 | -363.2083 | 15.2325 | -357.651 | 14.9635 | -357.7617 | 13.2285
11:24 | 230 | 18.7167 | 141.0221 | 316.1226 | 322.5114 | -16.1118 | -42.6667 | 0.253 | -0.8097 | -6.5215 | -6.6582 | -3.09 | -3.7259 | 2.6518 | -4.1905 | 0.4226 | 0.4157 | 0.6453 | 0.4139 | -106.0105 |  | -1.9286 | -2.6667 | -8.873 | -7.7929 | -1.5089 |  | -4.3985 | -4.0426 | 3.4833 | 2.8298 | 3.0391 | 0.7255 | 7.9 | 10.2766 | 10.5724 | 7.8071 | -0.0001 | -0.0024 | 0.0006 | 0.0027 | 0.0005 | -0.0006 | 0.0083 | -0.0044 | 0.0075 | -363.516 | 12.2779 | -363.5314 | 12.4216 | -363.1314 | 15.9224 | -363.1498 | 15.3064 | -357.5709 | 15.0477 | -357.654 | 13.2901
11:24 | 231 | 18.6555 | 141.9281 | 318.0988 | 324.6901 | -16.2699 | -42.9254 | 0.1371 | -0.7467 | -6.3987 | -6.6909 | -2.9873 | -3.7975 | 2.6245 | -4.1898 | 0.4269 | 0.4146 | 0.6503 | 0.4199 | -106.4092 |  | -1.87 | -2.7069 | -8.9154 | -7.9265 | -1.5613 |  | -4.4959 | -4.082 | 3.4866 | 2.8387 | 3.0494 | 0.737 | 7.954 | 10.3365 | 10.7089 | 7.8664 | 0.0001 | -0.0017 | 0.0007 | 0.0028 | 0.0007 | -0.0006 | 0.007 | -0.0084 | -0.0017 | -363.4822 | 12.3354 | -363.4114 | 12.473 | -363.0606 | 16.0066 | -363.156 | 15.407 | -357.4971 | 15.1114 | -357.5402 | 13.3333
11:24 | 232 | 18.5145 | 142.8409 | 319.8897 | 326.7184 | -16.3707 | -43.0168 | 0.156 | -0.8171 | -6.5603 | -6.7589 | -3.0384 | -3.8348 | 2.5833 | -4.3283 | 0.4272 | 0.4103 | 0.6552 | 0.424 | -106.9107 |  | -1.8994 | -2.7602 | -8.8536 | -7.9131 | -1.5285 |  | -4.4196 | -4.178 | 3.4745 | 2.8474 | 3.0465 | 0.7686 | 7.9882 | 10.4571 | 10.7119 | 7.9474 | -0.0002 | -0.0019 | 0.0005 | 0.0028 | -0.0001 | -0.0004 | -0.0052 | -0.0061 | -0.0012 | -363.4822 | 12.4175 | -363.356 | 12.5592 | -363.0206 | 16.099 | -363.1498 | 15.4994 | -357.4786 | 15.1914 | -357.4263 | 13.4031
11:24 | 233 | 18.6277 | 143.7642 | 321.9398 | 328.6579 | -16.5457 | -43.122 | 0.264 | -0.8131 | -6.6472 | -6.8687 | -3.147 | -3.8521 | 2.5715 | -4.3619 | 0.4286 | 0.4063 | 0.6634 | 0.4277 | -107.391 |  | -1.826 | -2.6955 | -8.9104 | -7.9507 | -1.6619 |  | -4.4928 | -4.1241 | 3.4838 | 2.8621 | 3.0464 | 0.7723 | 8.0653 | 10.465 | 10.8252 | 8.0067 | 0.0001 | -0.002 | 0.0004 | 0.0029 | 0.0003 | -0.0009 | -0.0087 | -0.0083 | -0.0039 | -363.4022 | 12.4955 | -363.3099 | 12.6536 | -363.0021 | 16.1647 | -363.1006 | 15.5651 | -357.3555 | 15.2613 | -357.3463 | 13.4852
11:24 | 234 | 18.5933 | 144.7865 | 323.69 | 330.4187 | -16.5319 | -43.3337 | 0.2276 | -0.7775 | -6.6204 | -6.8 | -3.1208 | -3.906 | 2.5451 | -4.3712 | 0.4292 | 0.4111 | 0.6722 | 0.4337 | -108.0004 |  | -1.965 | -2.6518 | -8.9908 | -7.9281 | -1.5634 |  | -4.5618 | -4.1558 | 3.4966 | 2.872 | 3.0562 | 0.7533 | 8.1172 | 10.5805 | 10.8491 | 8.0292 | 0.0002 | -0.0022 | 0.0006 | 0.0029 | 0.0001 | 0 | 0.0068 | 0.0082 | -0.0052 | -363.3437 | 12.6085 | -363.3345 | 12.7501 | -362.9744 | 16.216 | -362.9867 | 15.6247 | -357.254 | 15.368 | -357.3155 | 13.5694
11:24 | 235 | 18.4635 | 145.7396 | 325.5121 | 332.3641 | -16.6775 | -43.6166 | 0.2533 | -0.7984 | -6.7065 | -6.9983 | -3.1278 | -3.8776 | 2.4997 | -4.4319 | 0.4315 | 0.4154 | 0.6794 | 0.4383 | -108.5581 |  | -1.944 | -2.7 | -9.0566 | -8.0855 | -1.5802 |  | -4.5938 | -4.2534 | 3.5098 | 2.8793 | 3.0623 | 0.7395 | 8.1383 | 10.6477 | 10.9326 | 8.149 | -0.0004 | -0.0023 | -0.0001 | 0.0024 | 0.0009 | -0.0008 | -0.0042 | -0.0087 | -0.0177 | -363.2822 | 12.6885 | -363.3099 | 12.861 | -362.9129 | 16.292 | -362.879 | 15.6842 | -357.1955 | 15.4563 | -357.2232 | 13.6638
11:24 | 236 | 18.4869 | 146.6857 | 327.5931 | 334.3364 | -16.763 | -43.7584 | 0.3266 | -0.7744 | -6.7281 | -6.9358 | -3.0636 | -3.9339 | 2.3857 | -4.4905 | 0.4342 | 0.4196 | 0.6872 | 0.4451 | -109.0833 |  | -1.9729 | -2.82 | -9.2011 | -8.0469 | -1.5921 |  | -4.5678 | -4.1959 | 3.5232 | 2.8967 | 3.0755 | 0.7258 | 8.1848 | 10.6825 | 11.0533 | 8.1843 | -0.0003 | -0.0018 | 0.0011 | 0.0028 | 0.0004 | -0.0005 | 0.0003 | -0.0013 | -0.0003 | -363.2483 | 12.7522 | -363.1837 | 12.9267 | -362.8514 | 16.368 | -362.8698 | 15.7807 | -357.0509 | 15.5097 | -357.1248 | 13.7234
11:24 | 237 | 18.3151 | 147.6178 | 329.498 | 336.3279 | -16.9537 | -43.9908 | 0.222 | -0.7882 | -6.7734 | -7.099 | -3.0766 | -3.9558 | 2.4089 | -4.4295 | 0.4366 | 0.4151 | 0.6953 | 0.4512 | -109.5217 |  | -1.9466 | -2.7965 | -9.1785 | -8.1778 | -1.5734 |  | -4.5894 | -4.2219 | 3.5398 | 2.9148 | 3.0816 | 0.7145 | 8.2986 | 10.744 | 11.0383 | 8.177 | -0.0005 | -0.0025 | 0.0008 | 0.0027 | 0.0004 | -0.0006 | 0.0072 | -0.0072 | -0.0139 | -363.1345 | 12.7953 | -363.0945 | 12.9945 | -362.7867 | 16.4809 | -362.8637 | 15.869 | -356.9894 | 15.5734 | -356.9647 | 13.7809
11:24 | 238 | 18.2621 | 148.5563 | 331.4 | 338.3172 | -17.0154 | -44.1123 | 0.2058 | -0.8597 | -6.8643 | -7.0437 | -3.1247 | -3.8575 | 2.3998 | -4.5699 | 0.437 | 0.4167 | 0.6991 | 0.4553 | -110.141 |  | -2.0727 | -2.715 | -9.1845 | -8.1817 | -1.6394 |  | -4.7001 | -4.2871 | 3.5562 | 2.9345 | 3.0812 | 0.713 | 8.3241 | 10.8157 | 11.1212 | 8.1797 | -0.0002 | -0.0026 | 0.0007 | 0.0027 | 0.0008 | -0.0004 | 0.0147 | -0.0149 | -0.0114 | -363.1283 | 12.8918 | -363.076 | 13.1054 | -362.7621 | 16.563 | -362.8483 | 15.9635 | -356.9186 | 15.6637 | -356.9094 | 13.8835
11:24 | 239 | 18.2921 | 149.4994 | 333.3193 | 340.253 | -17.0715 | -44.2578 | 0.1943 | -0.7595 | -6.9333 | -7.1951 | -3.1507 | -3.9061 | 2.3373 | -4.5521 | 0.4389 | 0.4194 | 0.71 | 0.4626 | -110.7005 |  | -2.0641 | -2.8113 | -9.2437 | -8.1912 | -1.6429 |  | -4.6855 | -4.2695 | 3.5722 | 2.9491 | 3.0921 | 0.7142 | 8.3697 | 10.8616 | 11.2567 | 8.2992 | -0.0005 | -0.0024 | 0.001 | 0.0032 | 0.0003 | -0.0006 | -0.0042 | -0.005 | -0.0115 | -363.0914 | 13.0006 | -363.0483 | 13.1772 | -362.7129 | 16.6164 | -362.7652 | 16.0477 | -356.8355 | 15.7664 | -356.8232 | 13.941
11:24 | 240 | 18.3203 | 150.6544 | 335.2033 | 342.2235 | -17.1582 | -44.4801 | 0.2006 | -0.8074 | -7.0073 | -7.1645 | -3.2217 | -4.0245 | 2.3295 | -4.5257 | 0.4427 | 0.4193 | 0.7201 | 0.4683 | -111.1084 |  | -2.0687 | -2.8098 | -9.215 | -8.3301 | -1.6367 |  | -4.6987 | -4.3033 | 3.5892 | 2.9627 | 3.0993 | 0.7035 | 8.4412 | 11.0084 | 11.3007 | 8.3931 | -0.0008 | -0.0022 | 0.0005 | 0.0028 | 0.0008 | -0.0006 | -0.0081 | -0.0041 | -0.0135 | -363.0114 | 13.0992 | -363.0144 | 13.2717 | -362.6113 | 16.68 | -362.6698 | 16.1031 | -356.7032 | 15.8649 | -356.7801 | 14.0252
11:24 | 241 | 18.298 | 151.6015 | 337.1845 | 344.2753 | -17.1399 | -44.6555 | 0.13 | -0.7703 | -6.9073 | -7.1634 | -3.1922 | -4.0491 | 2.282 | -4.6682 | 0.4441 | 0.4236 | 0.728 | 0.4761 | -111.5785 |  | -2.0159 | -2.8725 | -9.2641 | -8.245 | -1.6084 |  | -4.7389 | -4.2972 | 3.5934 | 2.9695 | 3.1109 | 0.7035 | 8.5211 | 11.065 | 11.4383 | 8.4614 | -0.0001 | -0.0022 | 0.0002 | 0.0032 | 0.0003 | -0.0002 | 0.0007 | -0.0084 | -0.0058 | -363.0021 | 13.1731 | -362.9437 | 13.3476 | -362.5929 | 16.7683 | -362.6267 | 16.2037 | -356.6416 | 15.9429 | -356.6509 | 14.1155
11:24 | 242 | 18.2189 | 152.643 | 339.0896 | 346.172 | -17.2179 | -44.8505 | 0.1744 | -0.8561 | -7.0385 | -7.3322 | -3.2322 | -4.0628 | 2.2079 | -4.6875 | 0.4478 | 0.4283 | 0.7369 | 0.4828 | -112.0509 |  | -2.0858 | -2.83 | -9.3453 | -8.2748 | -1.6541 |  | -4.8581 | -4.3691 | 3.6113 | 2.9693 | 3.1221 | 0.7003 | 8.5351 | 11.1194 | 11.4748 | 8.5103 | -0.0002 | -0.0029 | 0.0004 | 0.0028 | 0.0007 | -0.0007 | -0.0054 | -0.0171 | -0.0066 | -362.8729 | 13.2162 | -362.8452 | 13.4318 | -362.5436 | 16.8772 | -362.5836 | 16.2735 | -356.5432 | 16.0045 | -356.5616 | 14.1915
11:24 | 243 | 18.1614 | 153.7147 | 341.2072 | 348.2393 | -17.2384 | -44.9426 | 0.1491 | -0.8335 | -7.0728 | -7.2498 | -3.2285 | -4.024 | 2.2808 | -4.5906 | 0.4494 | 0.4537 | 0.7454 | 0.4871 | -112.5295 |  | -1.9982 | -2.8913 | -9.459 | -8.4658 | -1.7415 |  | -4.8467 | -4.4356 | 3.621 | 2.9702 | 3.1266 | 0.6969 | 8.5685 | 11.2396 | 11.5727 | 8.5722 | -0.0001 | -0.0024 | 0 | 0.0027 | 0.0004 | -0.0002 | 0.0055 | -0.005 | -0.0236 | -362.7929 | 13.2819 | -362.7775 | 13.5222 | -362.4882 | 16.9839 | -362.5867 | 16.37 | -356.4139 | 16.0743 | -356.4386 | 14.2736
11:24 | 244 | 18.0841 | 154.7646 | 343.2299 | 350.2855 | -17.3513 | -45.0703 | 0.19 | -0.8 | -7.0905 | -7.2313 | -3.2739 | -4.0874 | 2.149 | -4.6953 | 0.4527 | 0.4692 | 0.7522 | 0.4922 | -113.1586 |  | -2.0548 | -2.9554 | -9.4344 | -8.5241 | -1.7166 |  | -4.9049 | -4.438 | 3.6383 | 2.9732 | 3.1374 | 0.6953 | 8.6581 | 11.2364 | 11.6366 | 8.5818 | -0.0002 | -0.0025 | 0.0005 | 0.0031 | 0.0008 | -0.0009 | 0.0061 | -0.0023 | 0.0119 | -362.7744 | 13.3887 | -362.7652 | 13.6043 | -362.4606 | 17.0702 | -362.5036 | 16.4542 | -356.3585 | 16.177 | -356.337 | 14.364
11:24 | 245 | 18.1006 | 155.706 | 345.3044 | 352.283 | -17.2892 | -45.1775 | 0.2345 | -0.8281 | -7.1425 | -7.3027 | -3.2 | -4.0982 | 2.0841 | -4.6822 | 0.4551 | 0.4603 | 0.759 | 0.4996 | -113.7343 |  | -2.0776 | -2.8922 | -9.5654 | -8.556 | -1.7024 |  | -4.8576 | -4.5068 | 3.6534 | 2.969 | 3.145 | 0.6962 | 8.6788 | 11.3496 | 11.6579 | 8.6716 | -0.0002 | -0.0022 | 0.0006 | 0.003 | 0.0004 | -0.0005 | 0.0145 | -0.012 | 0.0056 | -362.7806 | 13.4873 | -362.7098 | 13.67 | -362.3436 | 17.1236 | -362.4267 | 16.5425 | -356.2878 | 16.294 | -356.2601 | 14.4317
11:24 | 246 | 18.125 | 156.7468 | 347.2044 | 354.3884 | -17.4752 | -45.2815 | 0.3202 | -0.8612 | -7.2114 | -7.4378 | -3.3294 | -4.1829 | 2.1093 | -4.7493 | 0.4574 | 0.4557 | 0.772 | 0.5054 | -114.2969 |  | -1.9575 | -2.8544 | -9.5477 | -8.5624 | -1.6955 |  | -4.8741 | -4.5003 | 3.668 | 2.9626 | 3.1396 | 0.696 | 8.7266 | 11.4318 | 11.7617 | 8.7199 | 0.0001 | -0.0026 | 0.0005 | 0.0028 | 0.0004 | -0.0005 | -0.0036 | 0.0064 | -0.008 | -362.7621 | 13.5755 | -362.639 | 13.7501 | -362.2913 | 17.1872 | -362.3252 | 16.6349 | -356.1862 | 16.3864 | -356.1647 | 14.5118
11:24 | 247 | 18.0642 | 157.7061 | 349.2756 | 356.4504 | -17.6662 | -45.4873 | 0.1522 | -0.7725 | -7.2712 | -7.4286 | -3.3363 | -4.2325 | 2.0136 | -4.7633 | 0.4619 | 0.4534 | 0.7759 | 0.5118 | -114.9317 |  | -2.0058 | -2.9471 | -9.5451 | -8.6065 | -1.6701 |  | -4.9386 | -4.4523 | 3.6836 | 2.9607 | 3.1509 | 0.7417 | 8.8475 | 11.4779 | 11.8279 | 8.7587 | 0 | -0.0026 | 0.0008 | 0.0032 | 0.0004 | -0.0004 | -0.0005 | -0.0158 | -0.0121 | -362.6575 | 13.6454 | -362.5929 | 13.8507 | -362.2759 | 17.3104 | -362.3221 | 16.7273 | -356.0539 | 16.4665 | -356.0754 | 14.6104
11:24 | 248 | 18.0591 | 158.9255 | 351.3815 | 358.4774 | -17.6412 | -45.7378 | 0.2027 | -0.7977 | -7.2747 | -7.4771 | -3.2723 | -4.206 | 1.9949 | -4.7641 | 0.4642 | 0.4568 | 0.7834 | 0.52 | -115.4825 |  | -2.0767 | -2.9059 | -9.6631 | -8.6189 | -1.7265 |  | -4.9241 | -4.6132 | 3.701 | 2.9727 | 3.1659 | 0.7393 | 8.9281 | 11.6455 | 12.0264 | 8.8558 | -0.0001 | -0.0021 | 0.0005 | 0.0029 | 0.0002 | -0.0005 | 0.0086 | -0.0102 | -0.025 | -362.5098 | 13.7008 | -362.519 | 13.9472 | -362.2359 | 17.4151 | -362.2728 | 16.7827 | -355.9216 | 16.5261 | -355.9831 | 14.7171
11:24 | 249 | 17.9279 | 159.7901 | 353.1719 | 360.4548 | -17.672 | -45.7822 | 0.2912 | -0.8023 | -7.2557 | -7.4942 | -3.3605 | -4.2321 | 1.9995 | -4.9202 | 0.4666 | 0.458 | 0.7915 | 0.526 | -116.1129 |  | -2.0574 | -2.8784 | -9.6725 | -8.663 | -1.7152 |  | -4.8924 | -4.491 | 3.7186 | 3.0056 | 3.1797 | 0.7288 | 8.9434 | 11.6722 | 12.0287 | 8.9352 | -0.0005 | -0.0023 | 0.0008 | 0.0035 | 0.0009 | -0.0004 | 0.0131 | 0.0127 | -0.0094 | -362.4759 | 13.7932 | -362.4606 | 14.0293 | -362.1898 | 17.4931 | -362.1959 | 16.8833 | -355.7862 | 16.6246 | -355.8877 | 14.7911
11:24 | 250 | 17.8469 | 160.728 | 355.1679 | 362.5129 | -17.7619 | -45.8824 | 0.3122 | -0.7875 | -7.3166 | -7.5328 | -3.3571 | -4.2643 | 1.9441 | -4.9586 | 0.4687 | 0.4567 | 0.8024 | 0.5311 | -116.708 |  | -2.0157 | -2.9071 | -9.7041 | -8.6116 | -1.6763 |  | -4.9759 | -4.5116 | 3.733 | 3.0321 | 3.1828 | 0.7288 | 8.9862 | 11.7785 | 12.1066 | 8.9662 | -0.0002 | -0.0021 | 0.0006 | 0.0031 | 0.0004 | -0.0002 | 0.0103 | 0.0032 | -0.0107 | -362.5344 | 13.8815 | -362.4082 | 14.0889 | -362.0913 | 17.5629 | -362.1959 | 16.988 | -355.7708 | 16.7334 | -355.7739 | 14.8547
11:24 | 251 | 17.9196 | 161.7624 | 357.1374 | 364.6065 | -17.8715 | -45.9473 | 0.2513 | -0.8166 | -7.3596 | -7.6728 | -3.4293 | -4.2724 | 1.9774 | -4.9975 | 0.4726 | 0.4561 | 0.8093 | 0.5387 | -117.2436 |  | -2.0857 | -2.8472 | -9.7724 | -8.7059 | -1.7047 |  | -5.0258 | -4.6649 | 3.747 | 3.0404 | 3.1892 | 0.7247 | 9.0558 | 11.819 | 12.2331 | 9.036 | 0 | -0.0027 | 0.0004 | 0.0031 | 0.0006 | -0.0007 | 0.0107 | -0.0097 | -0.0186 | -362.4513 | 13.9616 | -362.3344 | 14.1546 | -362.0021 | 17.6286 | -362.0974 | 17.0845 | -355.697 | 16.8279 | -355.6539 | 14.9307
11:24 | 252 | 17.8315 | 162.8584 | 359.127 | 366.5718 | -17.9448 | -46.0398 | 0.2943 | -0.7757 | -7.4528 | -7.6172 | -3.453 | -4.2897 | 1.8702 | -4.8947 | 0.4757 | 0.46 | 0.8175 | 0.5459 | -117.7682 |  | -1.9883 | -2.8709 | -9.8446 | -8.8607 | -1.7581 |  | -4.9944 | -4.5365 | 3.7607 | 3.0534 | 3.1999 | 0.7197 | 9.0528 | 11.833 | 12.2216 | 9.0859 | -0.0002 | -0.0027 | 0.0006 | 0.0035 | 0.0004 | -0.0004 | -0.0009 | 0.0027 | -0.0186 | -362.3621 | 14.0622 | -362.2698 | 14.2367 | -361.9528 | 17.7313 | -362.0482 | 17.1543 | -355.5677 | 16.908 | -355.5769 | 15.0025
11:24 | 253 | 17.7654 | 163.7035 | 361.0083 | 368.5153 | -18.0686 | -46.0936 | 0.3759 | -0.8461 | -7.6261 | -7.6528 | -3.4692 | -4.309 | 1.8399 | -4.9615 | 0.4787 | 0.4759 | 0.8228 | 0.5531 | -118.3371 |  | -2.0119 | -2.9603 | -10.0453 | -8.8547 | -1.7451 |  | -5.0535 | -4.523 | 3.7758 | 3.0691 | 3.2093 | 0.7205 | 9.1551 | 11.9358 | 12.3684 | 9.1636 | 0.0001 | -0.0021 | 0.0004 | 0.0028 | 0.0007 | -0.0011 | -0.0074 | -0.012 | -0.0183 | -362.2544 | 14.1361 | -362.2759 | 14.3763 | -362.0113 | 17.8052 | -362.0021 | 17.2221 | -355.4569 | 16.9757 | -355.5246 | 15.1175
11:24 | 254 | 17.7192 | 164.5261 | 362.7117 | 370.1903 | -18.1207 | -46.2305 | 0.2517 | -0.9238 | -7.6726 | -7.7876 | -3.5206 | -4.303 | 1.7886 | -4.9698 | 0.4825 | 0.4743 | 0.8324 | 0.5583 | -118.8287 |  | -1.9711 | -2.8147 | -10.0192 | -8.8525 | -1.7335 |  | -5.1241 | -4.6431 | 3.7911 | 3.0846 | 3.2144 | 0.7212 | 9.2058 | 11.9683 | 12.3614 | 9.1526 | -0.0002 | -0.0026 | 0.0007 | 0.0031 | 0.0003 | -0.0007 | -0.0095 | -0.0215 | -0.0255 | -362.2359 | 14.2121 | -362.2575 | 14.4543 | -361.9436 | 17.8689 | -361.9097 | 17.2673 | -355.3554 | 17.0558 | -355.4569 | 15.1935
11:24 | 255 | 17.756 | 165.4631 | 364.2915 | 371.9139 | -18.193 | -46.2332 | 0.132 | -0.8685 | -7.6812 | -7.8136 | -3.4835 | -4.3256 | 1.7523 | -4.9442 | 0.4852 | 0.4723 | 0.8394 | 0.5632 | -119.2405 |  | -2.049 | -2.7128 | -10.1257 | -8.9053 | -1.8215 |  | -5.1335 | -4.5894 | 3.807 | 3.1 | 3.2194 | 0.7234 | 9.2512 | 12.0896 | 12.3947 | 9.2482 | 0.0004 | -0.0022 | 0.0007 | 0.0029 | 0.0005 | -0.0002 | 0.0129 | 0.0007 | 0.003 | -362.1682 | 14.3003 | -362.1775 | 14.4995 | -361.8574 | 17.9469 | -361.8851 | 17.3474 | -355.2877 | 17.1318 | -355.3308 | 15.2284
11:24 | 256 | 17.6994 | 166.4564 | 366.1727 | 373.9093 | -18.195 | -46.3063 | 0.1506 | -0.8491 | -7.6099 | -7.8423 | -3.5006 | -4.3801 | 1.7982 | -5.0867 | 0.4873 | 0.4738 | 0.8385 | 0.5687 | -119.8744 |  | -2.0658 | -2.6229 | -10.1781 | -8.9433 | -1.8244 |  | -5.1848 | -4.6553 | 3.8188 | 3.1125 | 3.2149 | 0.7311 | 9.2978 | 12.1764 | 12.5377 | 9.3012 | 0.0001 | -0.0025 | 0.0006 | 0.0026 | 0.0007 | -0.0009 | -0.0058 | -0.0094 | -0.0182 | -362.1959 | 14.3496 | -362.0544 | 14.5673 | -361.8113 | 18.0003 | -361.8944 | 17.45 | -355.26 | 17.1851 | -355.2046 | 15.2921
11:24 | 257 | 17.7441 | 167.2924 | 367.966 | 375.8998 | -18.3367 | -46.2601 | 0.1409 | -0.7257 | -7.6321 | -7.7012 | -3.5369 | -4.3098 | 1.8325 | -5.0457 | 0.4887 | 0.4777 | 0.8453 | 0.5737 | -120.2591 |  | -2.0389 | -2.6013 | -10.0863 | -9.02 | -1.7471 |  | -5.1521 | -4.6744 | 3.8287 | 3.1212 | 3.2249 | 0.7418 | 9.3337 | 12.218 | 12.62 | 9.3254 | -0.0008 | -0.0023 | 0.0003 | 0.0031 | 0.0006 | -0.0001 | 0.0099 | -0.0009 | -0.0008 | -362.079 | 14.4338 | -362.0728 | 14.6371 | -361.759 | 18.0455 | -361.8513 | 17.4623 | -355.1677 | 17.2509 | -355.18 | 15.3434
11:24 | 258 | 17.607 | 167.8437 | 368.955 | 377.1698 | -18.5414 | -46.1825 | 0.094 | -0.8677 | -7.6439 | -7.7773 | -3.4629 | -4.4207 | 1.7042 | -5.0901 | 0.492 | 0.4758 | 0.8442 | 0.5765 | -120.5601 |  | -2.0181 | -2.537 | -10.1656 | -9.0118 | -1.8505 |  | -5.2604 | -4.7445 | 3.8339 | 3.1228 | 3.2343 | 0.8773 | 9.3697 | 12.2191 | 12.6147 | 9.3385 | -0.0006 | -0.0026 | 0.0003 | 0.0033 | 0.0007 | -0.001 | 0.0088 | -0.0034 | -0.0113 | -362.0082 | 14.5139 | -362.0636 | 14.7438 | -361.7743 | 18.0496 | -361.7867 | 17.4788 | -355.06 | 17.2734 | -355.1246 | 15.3886
11:24 | 259 | 17.5456 | 168.213 | 369.7477 | 378.0822 | -18.5492 | -46.1699 | 0.1597 | -0.8342 | -7.6001 | -7.6554 | -3.5013 | -4.5046 | 1.6246 | -5.0164 | 0.4947 | 0.4814 | 0.8506 | 0.5812 | -120.823 |  | -1.9369 | -2.7067 | -10.1671 | -9.063 | -1.82 |  | -5.1868 | -4.7464 | 3.838 | 3.1402 | 3.2418 | 0.9152 | 9.4489 | 12.3568 | 12.7096 | 9.4163 | -0.0002 | -0.0026 | 0.0007 | 0.0034 | 0.0005 | -0.0002 | 0.011 | -0.0048 | 0.0052 | -361.999 | 14.5878 | -362.0605 | 14.8034 | -361.7651 | 18.0886 | -361.7467 | 17.4993 | -355.0815 | 17.3104 | -355.0846 | 15.4029
11:24 | 260 | 17.5187 | 168.5915 | 370.4538 | 378.8947 | -18.7121 | -46.0934 | 0.0562 | -0.8102 | -7.6641 | -7.8169 | -3.552 | -4.4114 | 1.655 | -5.0833 | 0.4975 | 0.4846 | 0.8485 | 0.5811 | -121.1117 |  | -2.0333 | -2.7403 | -10.2352 | -8.9574 | -1.8042 |  | -5.2677 | -4.8228 | 3.8443 | 3.1499 | 3.2466 | 0.9116 | 9.4701 | 12.3371 | 12.7109 | 9.4325 | 0.0001 | -0.0028 | 0.0007 | 0.0035 | 0.0008 | -0.0008 | -0.001 | -0.0156 | -0.0045 | -361.959 | 14.6535 | -362.0451 | 14.8752 | -361.7067 | 18.0824 | -361.7959 | 17.5198 | -355.0261 | 17.3104 | -355.0415 | 15.4132
11:24 | 261 | 17.5241 | 168.9835 | 371.0227 | 379.6302 | -18.6792 | -46.1594 | 0.1265 | -0.8359 | -7.7171 | -7.7967 | -3.5856 | -4.4056 | 1.6762 | -5.0505 | 0.4953 | 0.4838 | 0.8517 | 0.5841 | -121.3156 |  | -2.0673 | -2.7854 | -10.1823 | -8.9216 | -1.7622 |  | -5.1478 | -4.6653 | 3.8477 | 3.15 | 3.2457 | 0.9038 | 9.4806 | 12.3822 | 12.7963 | 9.4892 | -0.0002 | -0.0029 | 0.0008 | 0.0032 | 0.0003 | -0.0005 | 0.0174 | -0.0047 | -0.004 | -361.8574 | 14.7151 | -362.0021 | 14.9389 | -361.719 | 18.0865 | -361.7374 | 17.5013 | -354.9923 | 17.3268 | -355.0108 | 15.4173
11:24 | 262 | 17.5538 | 169.4703 | 371.4031 | 380.0674 | -18.7541 | -46.1408 | 0.1517 | -0.9227 | -7.7847 | -7.9657 | -3.6972 | -4.468 | 1.6763 | -5.1434 | 0.4971 | 0.4845 | 0.8457 | 0.5842 | -121.4733 |  | -2.0755 | -2.8422 | -10.3482 | -9.1114 | -1.8876 |  | -5.1772 | -4.7189 | 3.8517 | 3.1559 | 3.2519 | 0.8972 | 9.4539 | 12.3729 | 12.7643 | 9.5145 | -0.0001 | -0.0021 | 0.0008 | 0.0029 | 0.0005 | -0.0009 | 0.0233 | -0.0105 | 0.0199 | -361.8328 | 14.7664 | -361.9836 | 14.9882 | -361.6605 | 18.0763 | -361.7405 | 17.5157 | -354.9431 | 17.3104 | -354.9584 | 15.4173
11:24 | 263 | 17.5521 | 169.7927 | 371.6619 | 380.567 | -18.8293 | -46.2041 | 0.0048 | -0.8238 | -7.6786 | -7.9605 | -3.5937 | -4.4946 | 1.6051 | -5.1108 | 0.499 | 0.4883 | 0.8513 | 0.5853 | -121.6973 |  | -1.9938 | -2.7393 | -10.3072 | -9.0974 | -1.8515 |  | -5.2446 | -4.7911 | 3.8556 | 3.1611 | 3.2552 | 0.8926 | 9.4818 | 12.3602 | 12.762 | 9.5254 | -0.0003 | -0.0026 | 0.0008 | 0.0036 | 0.0003 | -0.0006 | 0.008 | -0.0027 | -0.0065 | -361.8051 | 14.865 | -361.9928 | 15.0683 | -361.682 | 18.0865 | -361.7405 | 17.5116 | -354.9554 | 17.3309 | -354.9738 | 15.4255
11:24 | 264 | 17.5187 | 170.0285 | 372.0636 | 381.0391 | -18.7815 | -46.1503 | 0.053 | -0.8437 | -7.723 | -7.8568 | -3.5199 | -4.3808 | 1.7466 | -4.9974 | 0.5007 | 0.4891 | 0.8506 | 0.5879 | -121.861 |  | -1.9896 | -2.7611 | -10.2948 | -9.0969 | -1.8319 |  | -5.2271 | -4.8261 | 3.858 | 3.163 | 3.256 | 0.8891 | 9.4769 | 12.3961 | 12.7594 | 9.5024 | 0.0004 | -0.0025 | 0.001 | 0.0034 | 0.0005 | -0.0005 | 0.0201 | -0.007 | 0.0067 | -361.759 | 14.9348 | -362.0359 | 15.1422 | -361.6974 | 18.0742 | -361.6759 | 17.5096 | -354.9584 | 17.3474 | -354.9523 | 15.4461
11:24 | 265 | 17.5134 | 170.2063 | 372.3702 | 381.4801 | -18.913 | -46.2513 | 0.0522 | -0.7911 | -7.6583 | -7.9714 | -3.5676 | -4.4708 | 1.6997 | -5.0032 | 0.5011 | 0.4942 | 0.8542 | 0.5877 | -122.0342 |  | -2.1533 | -2.7989 | -10.4135 | -9.1499 | -1.8698 |  | -5.142 | -4.8308 | 3.8626 | 3.1741 | 3.2568 | 0.8839 | 9.5067 | 12.432 | 12.7915 | 9.5314 | 0.0004 | -0.0025 | 0.0006 | 0.0032 | 0.001 | -0.0003 | 0.0104 | -0.0016 | -0.001 | -361.6851 | 14.9923 | -362.0236 | 15.2038 | -361.6666 | 18.0516 | -361.7159 | 17.5178 | -354.8938 | 17.3474 | -354.9677 | 15.4502
11:24 | 266 | 17.5329 | 170.4993 | 372.7736 | 381.8411 | -18.9667 | -46.3912 | 0.0267 | -0.8656 | -7.7239 | -7.9409 | -3.4756 | -4.4873 | 1.6857 | -5.0565 | 0.5014 | 0.4944 | 0.8526 | 0.5893 | -122.2062 |  | -2.0576 | -2.7704 | -10.3764 | -9.0511 | -1.7882 |  | -5.2419 | -4.8023 | 3.8677 | 3.1773 | 3.257 | 0.8782 | 9.5002 | 12.3903 | 12.8048 | 9.5433 | -0.0007 | -0.0029 | 0.0006 | 0.0036 | 0.0006 | -0.0004 | 0.0336 | -0.0022 | 0.0177 | -361.639 | 15.0477 | -361.9651 | 15.2695 | -361.6882 | 18.0742 | -361.7128 | 17.5198 | -354.8907 | 17.3391 | -354.8784 | 15.4276
11:24 | 267 | 17.4309 | 170.8356 | 373.2301 | 382.2543 | -19.0074 | -46.4579 | 0.1032 | -0.8335 | -7.7657 | -7.8501 | -3.5418 | -4.4541 | 1.6436 | -5.0499 | 0.5027 | 0.4977 | 0.8552 | 0.591 | -122.2819 |  | -2.0199 | -2.7438 | -10.3357 | -9.1631 | -1.8827 |  | -5.1826 | -4.7202 | 3.8716 | 3.187 | 3.2669 | 0.8738 | 9.494 | 12.4713 | 12.877 | 9.5419 | -0.0002 | -0.0022 | 0.0007 | 0.0034 | 0.0012 | -0.0006 | 0.0073 | -0.0155 | 0.0046 | -361.6113 | 15.097 | -361.919 | 15.3372 | -361.6482 | 18.0988 | -361.7159 | 17.5342 | -354.8446 | 17.3227 | -354.8169 | 15.4235
11:24 | 268 | 17.4423 | 171.07 | 373.4721 | 382.5902 | -19.0245 | -46.4873 | 0.1771 | -0.9287 | -7.7719 | -7.7783 | -3.5392 | -4.477 | 1.7252 | -5.0428 | 0.5027 | 0.4953 | 0.8549 | 0.5913 | -122.4972 |  | -2.0658 | -2.792 | -10.299 | -9.1809 | -1.8586 |  | -5.1835 | -4.694 | 3.8775 | 3.1874 | 3.2672 | 0.8686 | 9.5211 | 12.5036 | 12.9468 | 9.5701 | -0.0001 | -0.0027 | 0.0005 | 0.0037 | 0.0002 | -0.0004 | 0.0002 | -0.0139 | -0.0125 | -361.562 | 15.1791 | -361.9436 | 15.4132 | -361.6174 | 18.068 | -361.7067 | 17.5383 | -354.8446 | 17.3309 | -354.8569 | 15.4276
11:24 | 269 | 17.4969 | 171.3379 | 373.7016 | 383.0885 | -19.0855 | -46.5993 | 0.1379 | -0.8928 | -7.7684 | -7.7875 | -3.5639 | -4.5082 | 1.6511 | -5.0565 | 0.5039 | 0.4987 | 0.8567 | 0.5926 | -122.6194 |  | -2.0338 | -2.75 | -10.2603 | -9.1355 | -1.8498 |  | -5.1278 | -4.701 | 3.8819 | 3.1909 | 3.2684 | 0.8647 | 9.5096 | 12.5383 | 12.9691 | 9.5648 | 0 | -0.0029 | 0.0004 | 0.003 | 0.0005 | -0.001 | -0.007 | -0.0074 | -0.0211 | -361.5189 | 15.288 | -362.0113 | 15.4851 | -361.639 | 18.0516 | -361.6051 | 17.5116 | -354.8261 | 17.3761 | -354.863 | 15.4481
11:24 | 270 | 17.3561 | 171.4863 | 374.1962 | 383.4904 | -19.1019 | -46.7141 | 0.1381 | -0.9232 | -7.808 | -7.7792 | -3.5898 | -4.5413 | 1.5543 | -5.1728 | 0.5046 | 0.4979 | 0.858 | 0.5928 | -122.7611 |  | -1.947 | -2.8352 | -10.3978 | -9.1826 | -1.8361 |  | -5.15 | -4.6777 | 3.8863 | 3.1971 | 3.2683 | 0.8613 | 9.5143 | 12.5371 | 12.9446 | 9.6042 | -0.0001 | -0.0027 | 0.0004 | 0.0026 | 0.0008 | -0.0003 | 0.009 | -0.0223 | -0.0043 | -361.4912 | 15.3475 | -361.9867 | 15.5836 | -361.642 | 18.0598 | -361.6359 | 17.528 | -354.8107 | 17.374 | -354.8415 | 15.4563
11:24 | 271 | 17.3563 | 171.6332 | 374.5423 | 383.9909 | -19.1357 | -46.7613 | 0.1824 | -0.8944 | -7.8159 | -7.8581 | -3.6578 | -4.4929 | 1.549 | -5.1383 | 0.5047 | 0.5002 | 0.8597 | 0.5943 | -122.9959 |  | -1.9688 | -2.829 | -10.5254 | -9.2684 | -1.838 |  | -5.1334 | -4.7187 | 3.89 | 3.1972 | 3.2691 | 0.8552 | 9.5528 | 12.5405 | 12.9748 | 9.6666 | -0.0002 | -0.0024 | 0.0007 | 0.003 | 0.0005 | -0.0008 | -0.0013 | -0.0062 | -0.0031 | -361.4789 | 15.3947 | -361.9097 | 15.6432 | -361.6266 | 18.0906 | -361.6974 | 17.5506 | -354.7307 | 17.3453 | -354.8015 | 15.4481
11:24 | 272 | 17.3267 | 171.776 | 374.9145 | 384.356 | -19.1631 | -46.8147 | 0.2082 | -0.896 | -7.7838 | -7.828 | -3.6832 | -4.4501 | 1.5519 | -5.0932 | 0.5048 | 0.5012 | 0.8616 | 0.5972 | -123.1259 |  | -2.0227 | -2.769 | -10.3569 | -9.1297 | -1.8308 |  | -5.1556 | -4.743 | 3.8999 | 3.2038 | 3.273 | 0.8523 | 9.5789 | 12.5498 | 12.9758 | 9.6337 | 0.0003 | -0.0022 | 0.0011 | 0.0036 | 0.0005 | -0.0004 | 0.0054 | -0.0026 | -0.0155 | -361.4143 | 15.4461 | -361.8574 | 15.6965 | -361.5959 | 18.0947 | -361.7067 | 17.5609 | -354.7553 | 17.3412 | -354.7215 | 15.4194
11:24 | 273 | 17.3523 | 171.9891 | 375.3234 | 384.6734 | -19.1451 | -46.8955 | 0.1961 | -0.8653 | -7.7313 | -7.9167 | -3.6409 | -4.5237 | 1.4576 | -5.1939 | 0.5051 | 0.5018 | 0.8621 | 0.597 | -123.2769 |  | -2.027 | -2.7119 | -10.3176 | -9.1469 | -1.7766 |  | -5.2165 | -4.8163 | 3.9072 | 3.2149 | 3.2755 | 0.8493 | 9.6124 | 12.5661 | 12.9754 | 9.6841 | 0.0001 | -0.0029 | 0.0004 | 0.0029 | 0.0005 | -0.0002 | 0.0104 | -0.0053 | 0.0064 | -361.3682 | 15.5343 | -361.8605 | 15.7828 | -361.5682 | 18.0824 | -361.6513 | 17.5445 | -354.7061 | 17.3391 | -354.7307 | 15.4378
11:24 | 274 | 17.4488 | 172.3218 | 375.7954 | 385.101 | -19.2418 | -47.0672 | 0.2458 | -0.8988 | -7.826 | -7.8807 | -3.6566 | -4.4784 | 1.5897 | -5.1739 | 0.5057 | 0.5032 | 0.8611 | 0.5975 | -123.407 |  | -1.9041 | -2.7439 | -10.3473 | -9.1384 | -1.8345 |  | -5.281 | -4.7807 | 3.9082 | 3.2192 | 3.2776 | 0.8465 | 9.6203 | 12.5973 | 12.9674 | 9.6857 | 0.0001 | -0.0023 | 0.0008 | 0.0037 | 0.0006 | -0.0007 | 0.019 | -0.0031 | -0.0147 | -361.3805 | 15.6411 | -361.919 | 15.8731 | -361.6082 | 18.0619 | -361.602 | 17.526 | -354.7461 | 17.3823 | -354.7861 | 15.4604
11:24 | 275 | 17.4844 | 172.5136 | 377.6946 | 386.7909 | -19.2558 | -47.2159 | 0.1091 | -0.8696 | -7.7965 | -7.9419 | -3.6018 | -4.5112 | 1.5416 | -5.2208 | 0.5069 | 0.506 | 0.8645 | 0.5985 | -123.6429 |  | -1.9209 | -2.7124 | -10.408 | -9.1017 | -1.7991 |  | -5.2304 | -4.8316 | 3.9112 | 3.2234 | 3.282 | 0.844 | 9.6285 | 12.5996 | 13.0212 | 9.6883 | -0.0001 | -0.0023 | 0.0009 | 0.004 | 0.0007 | 0 | 0.0008 | -0.0142 | 0.01 | -361.3466 | 15.7068 | -361.8944 | 15.9553 | -361.5866 | 18.068 | -361.6328 | 17.5424 | -354.7061 | 17.374 | -354.7738 | 15.4625
11:24 | 276 | 17.4177 | 172.6792 | 385.8632 | 392.2656 | -19.366 | -47.2813 | 0.0709 | -0.9121 | -7.7742 | -7.7327 | -3.6477 | -4.5577 | 1.5556 | -5.1217 | 0.5079 | 0.5051 | 0.8649 | 0.5999 | -123.7668 |  | -1.9431 | -2.668 | -10.5068 | -9.183 | -1.8465 |  | -5.1967 | -4.7355 | 3.9123 | 3.2286 | 3.2862 | 0.8407 | 9.6783 | 12.6378 | 13.0649 | 9.7324 | -0.0003 | -0.0023 | 0.0002 | 0.0033 | 0.0004 | -0.001 | 0.0052 | -0.0077 | -0.0037 | -361.2943 | 15.7479 | -361.8144 | 16.0086 | -361.5743 | 18.0947 | -361.6236 | 17.5486 | -354.6569 | 17.3494 | -354.7184 | 15.4399
11:24 | 277 | 17.3879 | 172.8964 | 389.1408 | 395.0304 | -19.3527 | -47.3455 | 0.162 | -0.9161 | -7.8745 | -7.8782 | -3.7826 | -4.5799 | 1.5669 | -5.2754 | 0.5075 | 0.5056 | 0.8669 | 0.604 | -124.0179 |  | -1.9471 | -2.7403 | -10.4507 | -9.2286 | -1.8053 |  | -5.24 | -4.7489 | 3.9152 | 3.2289 | 3.2884 | 0.8394 | 9.6005 | 12.5821 | 13.0205 | 9.6744 | -0.0004 | -0.0031 | 0.0002 | 0.0031 | -0.0001 | -0.0005 | 0.0046 | 0.0008 | -0.0142 | -361.2697 | 15.8013 | -361.7497 | 16.0538 | -361.5928 | 18.0968 | -361.6236 | 17.5547 | -354.6938 | 17.3248 | -354.623 | 15.4337
11:24 | 278 | 17.3988 | 173.1109 | 390.5767 | 396.2477 | -19.3907 | -47.4338 | 0.1125 | -0.8645 | -7.7548 | -7.9252 | -3.6673 | -4.5809 | 1.5245 | -5.1472 | 0.5087 | 0.5057 | 0.8677 | 0.6053 | -124.1225 |  | -1.9322 | -2.8313 | -10.5283 | -9.3881 | -1.9121 |  | -5.2583 | -4.7032 | 3.9174 | 3.2348 | 3.2888 | 0.8381 | 9.6139 | 12.6076 | 13.1244 | 9.7155 | 0.0001 | -0.0029 | 0.0006 | 0.0031 | 0.0006 | -0.0011 | -0.0007 | -0.0082 | -0.0131 | -361.2451 | 15.8711 | -361.7559 | 16.1339 | -361.5436 | 18.0742 | -361.639 | 17.5547 | -354.6723 | 17.3432 | -354.6415 | 15.4461
11:24 | 279 | 17.4577 | 173.3502 | 391.5946 | 397.8257 | -19.4042 | -47.4986 | 0.2137 | -0.9452 | -7.932 | -8.0273 | -3.6742 | -4.5384 | 1.5544 | -5.1417 | 0.5095 | 0.5086 | 0.8681 | 0.6052 | -124.3298 |  | -1.8681 | -2.7997 | -10.5742 | -9.2152 | -1.7972 |  | -5.2661 | -4.8662 | 3.9195 | 3.2437 | 3.2836 | 0.8361 | 9.6288 | 12.6458 | 13.1284 | 9.7302 | -0.0006 | -0.0027 | 0.0002 | 0.0031 | 0.0006 | -0.0007 | 0.0026 | -0.018 | -0.002 | -361.2297 | 15.9573 | -361.7959 | 16.2078 | -361.5651 | 18.0639 | -361.5866 | 17.5506 | -354.6415 | 17.372 | -354.6723 | 15.4604
11:24 | 280 | 17.4669 | 173.5669 | 392.4066 | 399.0014 | -19.4135 | -47.7447 | 0.1167 | -0.8903 | -7.9171 | -8.073 | -3.7132 | -4.5411 | 1.5601 | -5.1472 | 0.509 | 0.5116 | 0.8697 | 0.6075 | -124.4149 |  | -1.8933 | -2.8712 | -10.5075 | -9.2489 | -1.7949 |  | -5.2215 | -4.7257 | 3.9219 | 3.2495 | 3.2677 | 0.8348 | 9.6483 | 12.6539 | 13.132 | 9.7261 | -0.0004 | -0.0026 | 0.001 | 0.0035 | 0.0007 | -0.0003 | 0.0104 | -0.003 | -0.0274 | -361.1681 | 16.0045 | -361.759 | 16.2612 | -361.5589 | 18.0865 | -361.6236 | 17.5424 | -354.62 | 17.3699 | -354.6476 | 15.4604
11:24 | 281 | 17.4055 | 173.6439 | 393.1246 | 399.7904 | -19.465 | -47.7879 | 0.1471 | -0.8822 | -7.9455 | -8.0198 | -3.6605 | -4.6019 | 1.527 | -5.2211 | 0.5097 | 0.5095 | 0.8707 | 0.6074 | -124.496 |  | -1.8042 | -2.8857 | -10.4227 | -9.3019 | -1.7724 |  | -5.2518 | -4.7522 | 3.9228 | 3.2518 | 3.2687 | 0.8344 | 9.677 | 12.6887 | 13.1455 | 9.7656 | 0 | -0.0025 | 0.0009 | 0.0035 | 0.0009 | -0.0004 | 0.0163 | -0.01 | -0.004 | -361.1681 | 16.0251 | -361.682 | 16.292 | -361.5343 | 18.0701 | -361.5836 | 17.5465 | -354.5892 | 17.3371 | -354.6015 | 15.4563
11:24 | 282 | 17.3847 | 173.9487 | 393.9215 | 400.4073 | -19.4699 | -47.7884 | 0.1123 | -0.8437 | -7.9216 | -7.8945 | -3.6385 | -4.5153 | 1.4903 | -5.2827 | 0.5091 | 0.5129 | 0.8721 | 0.6085 | -124.6618 |  | -1.8734 | -2.8189 | -10.5248 | -9.3281 | -1.8239 |  | -5.2826 | -4.7858 | 3.9263 | 3.2545 | 3.2686 | 0.8353 | 9.6749 | 12.7326 | 13.2113 | 9.8275 | 0.0002 | -0.0031 | 0.0004 | 0.0033 | 0.0002 | -0.0002 | 0.0292 | -0.0018 | 0.0043 | -361.1343 | 16.0846 | -361.6851 | 16.3289 | -361.522 | 18.0804 | -361.602 | 17.5568 | -354.5584 | 17.3474 | -354.5984 | 15.4481
11:24 | 283 | 17.3918 | 174.0942 | 394.3844 | 400.9397 | -19.5417 | -47.8299 | 0.0989 | -0.8267 | -7.9712 | -7.9884 | -3.7315 | -4.4738 | 1.5329 | -5.2019 | 0.5101 | 0.5146 | 0.8741 | 0.6102 | -124.7803 |  | -1.7919 | -2.8742 | -10.523 | -9.3724 | -1.7598 |  | -5.2706 | -4.848 | 3.9265 | 3.2531 | 3.2658 | 0.8375 | 9.7023 | 12.7836 | 13.207 | 9.8539 | -0.0004 | -0.003 | 0.0008 | 0.0036 | 0.0011 | -0.0006 | -0.006 | 0.0026 | -0.0228 | -361.1374 | 16.1339 | -361.6974 | 16.3946 | -361.5374 | 18.0845 | -361.6051 | 17.5527 | -354.583 | 17.3638 | -354.58 | 15.4645
11:24 | 284 | 17.4017 | 174.227 | 394.9272 | 401.3871 | -19.5487 | -47.9523 | 0.1173 | -0.8532 | -7.9262 | -8.0162 | -3.6505 | -4.5113 | 1.3979 | -5.2857 | 0.5104 | 0.5161 | 0.8721 | 0.6099 | -125.0169 |  | -1.8276 | -2.9251 | -10.4947 | -9.2676 | -1.8276 |  | -5.235 | -4.6887 | 3.9291 | 3.2539 | 3.2682 | 0.8382 | 9.7267 | 12.7731 | 13.219 | 9.8843 | -0.0003 | -0.0024 | 0.0003 | 0.0033 | 0.0007 | 0 | 0.0059 | -0.0051 | -0.0086 | -361.1312 | 16.1955 | -361.6882 | 16.4398 | -361.5343 | 18.1029 | -361.562 | 17.5547 | -354.5584 | 17.3658 | -354.5984 | 15.4686
11:24 | 285 | 17.3728 | 174.3282 | 395.3938 | 401.8411 | -19.5315 | -48.1345 | 0.0645 | -0.7738 | -7.8614 | -7.8993 | -3.6537 | -4.5631 | 1.4517 | -5.3035 | 0.5118 | 0.5173 | 0.8746 | 0.6128 | -125.0515 |  | -1.7592 | -2.9503 | -10.515 | -9.2432 | -1.8313 |  | -5.1955 | -4.7568 | 3.9306 | 3.2586 | 3.2705 | 0.8379 | 9.6901 | 12.7475 | 13.1961 | 9.8374 | -0.0005 | -0.0027 | 0.0005 | 0.0034 | 0.0006 | -0.0008 | 0.0165 | 0.005 | -0.0122 | -361.122 | 16.2386 | -361.6697 | 16.4788 | -361.4974 | 18.0804 | -361.5651 | 17.5527 | -354.5461 | 17.3761 | -354.58 | 15.4584
11:24 | 286 | 17.3892 | 174.5163 | 395.9342 | 402.2353 | -19.5822 | -48.094 | 0.1808 | -0.8898 | -7.9606 | -7.9429 | -3.6799 | -4.5388 | 1.4908 | -5.2499 | 0.5119 | 0.518 | 0.8805 | 0.6137 | -125.2682 |  | -1.7486 | -3.0332 | -10.5153 | -9.3742 | -1.866 |  | -5.2381 | -4.7503 | 3.9326 | 3.2619 | 3.2708 | 0.837 | 9.691 | 12.7372 | 13.2051 | 9.8433 | 0.0001 | -0.0025 | 0.0007 | 0.0037 | 0.0003 | -0.0007 | 0.0267 | -0.0115 | 0.0004 | -361.0912 | 16.2715 | -361.6297 | 16.5466 | -361.5251 | 18.0701 | -361.5436 | 17.5588 | -354.5399 | 17.3617 | -354.5338 | 15.4666
11:24 | 287 | 17.4724 | 174.6715 | 396.4237 | 402.5941 | -19.5523 | -48.1233 | 0.0789 | -0.8447 | -7.8981 | -7.9905 | -3.5753 | -4.4431 | 1.549 | -5.2609 | 0.5122 | 0.5209 | 0.8781 | 0.6146 | -125.4289 |  | -1.8145 | -2.9458 | -10.4854 | -9.3077 | -1.7957 |  | -5.2531 | -4.7442 | 3.934 | 3.2645 | 3.2735 | 0.8369 | 9.6715 | 12.7233 | 13.1899 | 9.8474 | -0.0001 | -0.0032 | 0.0006 | 0.0032 | 0.0003 | -0.0006 | 0.0281 | -0.0083 | 0.0173 | -361.0266 | 16.3187 | -361.6482 | 16.5897 | -361.5036 | 18.0988 | -361.562 | 17.5506 | -354.4969 | 17.3638 | -354.5338 | 15.4727
11:25 | 288 | 17.3826 | 174.7517 | 396.7658 | 402.9936 | -19.5775 | -48.1584 | 0.039 | -0.8357 | -7.9481 | -8.0105 | -3.71 | -4.4424 | 1.4403 | -5.253 | 0.5125 | 0.5216 | 0.878 | 0.6152 | -125.5434 |  | -1.8496 | -3.0361 | -10.4927 | -9.2459 | -1.8632 |  | -5.2549 | -4.7318 | 3.935 | 3.2663 | 3.2728 | 0.8345 | 9.7074 | 12.7129 | 13.1788 | 9.8374 | -0.0005 | -0.0024 | 0.0011 | 0.0037 | 0.0007 | -0.001 | 0.0105 | 0.0046 | -0.0143 | -361.0389 | 16.3392 | -361.5805 | 16.641 | -361.5374 | 18.0927 | -361.562 | 17.5363 | -354.4784 | 17.3515 | -354.4815 | 15.4768
11:25 | 289 | 17.3497 | 174.7951 | 397.1843 | 403.2733 | -19.5117 | -48.2267 | 0.1302 | -0.7517 | -7.8854 | -8.0233 | -3.6973 | -4.6029 | 1.4821 | -5.3571 | 0.5133 | 0.5234 | 0.8781 | 0.6162 | -125.6398 |  | -1.8193 | -2.9056 | -10.4885 | -9.2815 | -1.874 |  | -5.2909 | -4.7177 | 3.9388 | 3.2701 | 3.284 | 0.834 | 9.7071 | 12.7534 | 13.2221 | 9.8822 | -0.0003 | -0.0025 | 0.0011 | 0.0034 | 0.0004 | -0.0004 | -0.0062 | -0.0116 | -0.0318 | -361.0758 | 16.4029 | -361.5743 | 16.6739 | -361.4912 | 18.0845 | -361.5374 | 17.5773 | -354.4661 | 17.3576 | -354.5184 | 15.4584
11:25 | 290 | 17.2706 | 174.9828 | 397.5197 | 403.6716 | -19.6572 | -48.3606 | 0.1599 | -0.774 | -7.8836 | -8.0013 | -3.6501 | -4.6536 | 1.4715 | -5.2428 | 0.5139 | 0.5226 | 0.8776 | 0.6157 | -125.7757 |  | -1.8176 | -2.8425 | -10.5551 | -9.3303 | -1.7962 |  | -5.3694 | -4.7856 | 3.9386 | 3.2691 | 3.2777 | 0.8346 | 9.7329 | 12.7614 | 13.2567 | 9.8684 | 0.0002 | -0.0028 | 0 | 0.0031 | 0.0006 | -0.0008 | 0.0189 | -0.0038 | -0.0141 | -361.0789 | 16.4747 | -361.5959 | 16.7047 | -361.4543 | 18.0783 | -361.562 | 17.5794 | -354.5123 | 17.3946 | -354.5184 | 15.4604
11:25 | 291 | 17.3069 | 175.0778 | 397.8125 | 403.9865 | -19.7805 | -48.4604 | 0.1163 | -0.8647 | -7.9722 | -8.1317 | -3.7134 | -4.5043 | 1.5109 | -5.2233 | 0.5146 | 0.5231 | 0.8822 | 0.6161 | -126.0281 |  | -1.8654 | -2.7699 | -10.4319 | -9.3775 | -1.8076 |  | -5.3524 | -4.7023 | 3.9381 | 3.2714 | 3.2826 | 0.8352 | 9.7659 | 12.7604 | 13.3112 | 9.8886 | 0.0005 | -0.0025 | 0.0005 | 0.0036 | 0.0002 | -0.0006 | 0.0156 | 0.0018 | 0.0044 | -361.0728 | 16.4973 | -361.5436 | 16.7375 | -361.4728 | 18.0742 | -361.5159 | 17.5732 | -354.4907 | 17.3802 | -354.4969 | 15.4625
11:25 | 292 | 17.4191 | 175.2762 | 398.2788 | 404.2756 | -19.7751 | -48.4958 | 0.0566 | -0.836 | -7.9344 | -8.0992 | -3.7377 | -4.6594 | 1.4525 | -5.276 | 0.5144 | 0.5213 | 0.8815 | 0.6191 | -126.0467 |  | -1.8683 | -2.782 | -10.5179 | -9.393 | -1.7233 |  | -5.2902 | -4.7048 | 3.9391 | 3.2711 | 3.284 | 0.8344 | 9.778 | 12.7776 | 13.3364 | 9.8789 | -0.0002 | -0.0025 | 0 | 0.0029 | 0.0014 | -0.0004 | -0.0017 | -0.0089 | 0.0022 | -360.9651 | 16.5055 | -361.5374 | 16.793 | -361.4943 | 18.0886 | -361.5374 | 17.5465 | -354.4415 | 17.3658 | -354.4846 | 15.4748
11:25 | 293 | 17.4108 | 175.4267 | 398.602 | 404.6652 | -19.7097 | -48.4288 | 0.0481 | -0.8036 | -7.926 | -8.0872 | -3.7385 | -4.5965 | 1.3865 | -5.3527 | 0.5144 | 0.5207 | 0.8821 | 0.6202 | -126.1324 |  | -1.8262 | -2.8724 | -10.638 | -9.4263 | -1.7781 |  | -5.2756 | -4.6978 | 3.9402 | 3.2749 | 3.2861 | 0.8357 | 9.7941 | 12.7649 | 13.3533 | 9.8889 | -0.0003 | -0.0022 | 0.0002 | 0.0034 | 0.0006 | -0.0001 | 0.0065 | -0.0022 | -0.0161 | -361.0051 | 16.5384 | -361.5282 | 16.8505 | -361.5466 | 18.1173 | -361.5128 | 17.5465 | -354.4169 | 17.3535 | -354.4753 | 15.4892
11:25 | 294 | 17.4367 | 175.5331 | 398.9456 | 404.8211 | -19.7395 | -48.4358 | 0.1885 | -0.8327 | -7.969 | -8.08 | -3.6663 | -4.5501 | 1.4549 | -5.2775 | 0.5159 | 0.5196 | 0.8826 | 0.6194 | -126.3318 |  | -1.7093 | -2.9718 | -10.6808 | -9.3556 | -1.8147 |  | -5.3142 | -4.7404 | 3.9416 | 3.2769 | 3.2853 | 0.8347 | 9.7725 | 12.7371 | 13.3113 | 9.8682 | -0.0002 | -0.0026 | 0.0008 | 0.0038 | 0.0007 | -0.0011 | 0.0057 | -0.0099 | -0.0233 | -360.9651 | 16.5753 | -361.5066 | 16.8648 | -361.482 | 18.0947 | -361.5313 | 17.5342 | -354.4261 | 17.372 | -354.463 | 15.483
11:25 | 295 | 17.391 | 175.6452 | 399.2282 | 405.0963 | -19.7882 | -48.5033 | 0.093 | -0.9094 | -8.0354 | -8.0991 | -3.6583 | -4.616 | 1.3932 | -5.391 | 0.5146 | 0.5221 | 0.884 | 0.6189 | -126.3645 |  | -1.7717 | -2.9465 | -10.5745 | -9.2885 | -1.7329 |  | -5.3186 | -4.7189 | 3.9431 | 3.2818 | 3.2878 | 0.8355 | 9.8151 | 12.8204 | 13.3323 | 9.9103 | -0.0001 | -0.0035 | 0.0003 | 0.0031 | 0.0002 | -0.0006 | -0.0036 | -0.0052 | -0.0047 | -361.0235 | 16.6246 | -361.4759 | 16.8792 | -361.4482 | 18.0783 | -361.5589 | 17.5794 | -354.4753 | 17.3802 | -354.4538 | 15.4584
11:25 | 296 | 17.3331 | 175.7141 | 399.4277 | 405.3559 | -19.7708 | -48.5909 | -0.0337 | -0.8971 | -8.0748 | -8.178 | -3.771 | -4.5565 | 1.4759 | -5.3886 | 0.5163 | 0.526 | 0.8827 | 0.6211 | -126.4146 |  | -1.7985 | -2.9282 | -10.6283 | -9.3284 | -1.7592 |  | -5.2943 | -4.8469 | 3.9438 | 3.2823 | 3.2872 | 0.8371 | 9.7884 | 12.8111 | 13.3466 | 9.8605 | 0.0001 | -0.0029 | 0.0012 | 0.004 | 0.0006 | -0.0009 | 0.0008 | -0.0196 | -0.0096 | -361.0328 | 16.6698 | -361.4605 | 16.908 | -361.4266 | 18.0865 | -361.5528 | 17.5876 | -354.4753 | 17.3946 | -354.4415 | 15.4543
11:25 | 297 | 17.3127 | 175.7884 | 399.7719 | 405.6194 | -19.8462 | -48.5126 | 0.1311 | -0.8379 | -8.0386 | -8.1639 | -3.7843 | -4.6013 | 1.302 | -5.3703 | 0.5171 | 0.5252 | 0.8831 | 0.6213 | -126.4757 |  | -1.706 | -2.8985 | -10.5819 | -9.2786 | -1.7057 |  | -5.3218 | -4.7002 | 3.947 | 3.2851 | 3.2867 | 0.8368 | 9.8103 | 12.8736 | 13.3694 | 9.9283 | -0.0005 | -0.0028 | 0.0007 | 0.0034 | 0.0005 | -0.0009 | -0.0003 | 0.0022 | -0.0364 | -360.962 | 16.6903 | -361.4636 | 16.9757 | -361.4636 | 18.0886 | -361.5066 | 17.565 | -354.4138 | 17.3823 | -354.4322 | 15.4707
11:25 | 298 | 17.3709 | 175.9087 | 400.1007 | 405.8807 | -19.7975 | -48.6038 | 0.0728 | -0.9048 | -8.0406 | -8.1474 | -3.6695 | -4.6048 | 1.4239 | -5.2677 | 0.5166 | 0.5253 | 0.8826 | 0.6216 | -126.6484 |  | -1.7314 | -2.8916 | -10.5728 | -9.4393 | -1.731 |  | -5.2561 | -4.67 | 3.947 | 3.2852 | 3.2889 | 0.8347 | 9.8092 | 12.8724 | 13.3217 | 9.9619 | -0.0001 | -0.0021 | 0.0004 | 0.0029 | 0.0007 | -0.0003 | 0.0152 | -0.0193 | -0.0219 | -360.9466 | 16.7047 | -361.4574 | 17.0127 | -361.5066 | 18.0988 | -361.4697 | 17.5342 | -354.3645 | 17.3556 | -354.4353 | 15.5035
11:25 | 299 | 17.3921 | 176.0587 | 400.491 | 406.2512 | -19.8059 | -48.6844 | 0.0441 | -0.9549 | -8.0075 | -8.1122 | -3.7428 | -4.5297 | 1.5059 | -5.2742 | 0.5186 | 0.5282 | 0.8821 | 0.622 | -126.7119 |  | -1.8658 | -2.9746 | -10.5048 | -9.3757 | -1.7044 |  | -5.3435 | -4.7852 | 3.9471 | 3.285 | 3.2922 | 0.8369 | 9.8393 | 12.9025 | 13.3694 | 9.9687 | 0.0001 | -0.0029 | 0.0008 | 0.0032 | 0.0005 | -0.0011 | 0.0036 | -0.0098 | -0.0038 | -360.9066 | 16.754 | -361.4359 | 17.0496 | -361.4882 | 18.0927 | -361.5036 | 17.5486 | -354.3522 | 17.3843 | -354.4199 | 15.4933
11:25 | 300 | 17.2991 | 176.1289 | 400.6537 | 406.409 | -19.7404 | -48.596 | 0.1162 | -0.8696 | -7.9933 | -8.1257 | -3.7598 | -4.5468 | 1.4556 | -5.3782 | 0.5189 | 0.5277 | 0.8853 | 0.6217 | -126.8872 |  | -1.8157 | -2.9812 | -10.4544 | -9.2857 | -1.6892 |  | -5.3902 | -4.7752 | 3.9486 | 3.2904 | 3.2962 | 0.8358 | 9.8543 | 12.9175 | 13.3725 | 9.9781 | -0.0003 | -0.0031 | 0.0005 | 0.0034 | 0.0005 | -0.0002 | 0.0033 | -0.0099 | 0.0066 | -360.9066 | 16.7704 | -361.3866 | 17.0537 | -361.4297 | 18.0988 | -361.5343 | 17.5712 | -354.4046 | 17.3802 | -354.3922 | 15.4645
11:25 | 301 | 17.3028 | 176.2047 | 400.9732 | 406.6924 | -19.8554 | -48.6268 | 0.102 | -0.8715 | -7.9836 | -8.102 | -3.7567 | -4.6204 | 1.5248 | -5.3192 | 0.5177 | 0.5299 | 0.8855 | 0.6214 | -126.928 |  | -1.8369 | -3.0228 | -10.5972 | -9.3389 | -1.7763 |  | -5.2874 | -4.9125 | 3.9508 | 3.2927 | 3.2955 | 0.836 | 9.8499 | 12.9244 | 13.3372 | 10.009 | -0.0005 | -0.0026 | 0.0002 | 0.0034 | 0.0006 | -0.001 | -0.0087 | -0.0099 | -0.0176 | -360.9466 | 16.8135 | -361.362 | 17.062 | -361.4174 | 18.1029 | -361.5436 | 17.5855 | -354.4138 | 17.3802 | -354.3522 | 15.4481
11:25 | 302 | 17.3008 | 176.2888 | 401.2399 | 406.9307 | -19.9334 | -48.7906 | 0.1885 | -0.8531 | -8.0263 | -8.153 | -3.7086 | -4.5414 | 1.5429 | -5.3142 | 0.5184 | 0.5265 | 0.8853 | 0.6231 | -127.0438 |  | -1.8005 | -2.9373 | -10.702 | -9.4712 | -1.8348 |  | -5.2749 | -4.7509 | 3.9529 | 3.292 | 3.2886 | 0.8366 | 9.8406 | 12.9151 | 13.3688 | 9.9996 | -0.0007 | -0.0027 | 0.001 | 0.0036 | 0.0002 | -0.0006 | 0.0023 | -0.0038 | -0.0004 | -360.9374 | 16.8525 | -361.3835 | 17.1359 | -361.4482 | 18.0947 | -361.5066 | 17.5629 | -354.3553 | 17.3802 | -354.3984 | 15.4768
11:25 | 303 | 17.2886 | 176.3622 | 401.5181 | 407.1153 | -19.915 | -48.9015 | 0.228 | -0.8834 | -7.9734 | -8.2159 | -3.6124 | -4.5998 | 1.5316 | -5.3131 | 0.5187 | 0.5295 | 0.8858 | 0.6238 | -127.1763 |  | -1.8434 | -2.7806 | -10.6635 | -9.3655 | -1.6615 |  | -5.3317 | -4.8146 | 3.953 | 3.293 | 3.2889 | 0.8363 | 9.8518 | 12.9153 | 13.3948 | 10.0329 | 0 | -0.0027 | 0.0006 | 0.0029 | 0.0007 | -0.0005 | 0.0096 | -0.004 | -0.0022 | -360.9404 | 16.8895 | -361.4112 | 17.2098 | -361.5097 | 18.0824 | -361.4574 | 17.5506 | -354.3645 | 17.3946 | -354.3953 | 15.5035
11:25 | 304 | 17.3152 | 176.4483 | 401.7173 | 407.3482 | -19.9765 | -48.9835 | 0.105 | -0.9369 | -8.0609 | -8.1719 | -3.5745 | -4.5655 | 1.4877 | -5.3457 | 0.5198 | 0.5296 | 0.8862 | 0.6248 | -127.2579 |  | -1.8575 | -2.8828 | -10.6789 | -9.3213 | -1.7734 |  | -5.3759 | -4.9032 | 3.9558 | 3.2973 | 3.2909 | 0.8353 | 9.8512 | 12.9024 | 13.3202 | 10.0278 | -0.0002 | -0.0032 | 0.0006 | 0.0032 | 0.0006 | -0.0004 | 0.0148 | -0.0104 | -0.0138 | -360.8881 | 16.9285 | -361.3897 | 17.2201 | -361.4451 | 18.0886 | -361.482 | 17.5465 | -354.3276 | 17.3864 | -354.3984 | 15.483
11:25 | 305 | 17.2832 | 176.5574 | 401.9798 | 407.7138 | -19.9556 | -49.0211 | 0.1874 | -0.9597 | -8.0964 | -8.196 | -3.5657 | -4.5999 | 1.4346 | -5.31 | 0.5197 | 0.5282 | 0.887 | 0.6255 | -127.2936 |  | -1.8227 | -2.9226 | -10.7325 | -9.394 | -1.8113 |  | -5.3928 | -4.8133 | 3.9556 | 3.2981 | 3.2929 | 0.8365 | 9.8669 | 12.9477 | 13.3979 | 10.077 | -0.0003 | -0.0029 | 0.0009 | 0.0033 | 0.0004 | -0.0006 | 0.0179 | 0.0035 | -0.0157 | -360.8635 | 16.949 | -361.2912 | 17.2303 | -361.442 | 18.0886 | -361.5005 | 17.5588 | -354.3553 | 17.374 | -354.3276 | 15.4625
11:25 | 306 | 17.2801 | 176.701 | 402.242 | 407.8795 | -19.9436 | -49.0504 | 0.1265 | -0.9285 | -8.1144 | -8.1793 | -3.6276 | -4.5738 | 1.4728 | -5.3197 | 0.5206 | 0.5319 | 0.8854 | 0.627 | -127.4145 |  | -1.7448 | -2.9661 | -10.669 | -9.4352 | -1.8048 |  | -5.4565 | -4.8632 | 3.9568 | 3.3003 | 3.2938 | 0.8372 | 9.9005 | 12.9581 | 13.4313 | 10.1048 | -0.0004 | -0.0027 | 0.0005 | 0.003 | 0.0008 | -0.0006 | 0.0105 | -0.0157 | -0.0213 | -360.8758 | 16.9696 | -361.2789 | 17.2591 | -361.4112 | 18.1091 | -361.5436 | 17.5794 | -354.3153 | 17.3617 | -354.2907 | 15.4543
11:25 | 307 | 17.2914 | 176.8057 | 402.467 | 408.0941 | -19.9531 | -49.071 | 0.1335 | -0.924 | -8 | -8.1232 | -3.6599 | -4.4411 | 1.4906 | -5.3016 | 0.5208 | 0.5316 | 0.8882 | 0.6281 | -127.5037 |  | -1.7469 | -3.0733 | -10.7809 | -9.4813 | -1.9121 |  | -5.4025 | -4.8083 | 3.9578 | 3.2999 | 3.2947 | 0.8368 | 9.8576 | 12.9673 | 13.4469 | 10.1022 | -0.0004 | -0.0025 | 0.0006 | 0.0035 | 0.0005 | -0.0003 | 0.0201 | -0.0085 | 0.0161 | -360.8204 | 17.0168 | -361.3035 | 17.3207 | -361.4205 | 18.0783 | -361.5005 | 17.5629 | -354.3215 | 17.3946 | -354.3461 | 15.4768
11:25 | 308 | 17.3007 | 176.9649 | 402.7637 | 408.3359 | -19.9976 | -49.1184 | 0.1333 | -0.9722 | -8.0584 | -8.0848 | -3.5759 | -4.5148 | 1.5351 | -5.2795 | 0.5209 | 0.5316 | 0.8851 | 0.6284 | -127.549 |  | -1.7159 | -3.0415 | -10.7897 | -9.3806 | -1.8754 |  | -5.3994 | -4.7901 | 3.9592 | 3.3027 | 3.2957 | 0.8366 | 9.8677 | 12.9548 | 13.4832 | 10.0824 | 0.0003 | -0.0028 | 0.0008 | 0.0037 | 0.0007 | -0.0008 | -0.0028 | 0.0028 | 0.0019 | -360.8327 | 17.0743 | -361.322 | 17.3494 | -361.4482 | 18.105 | -361.4482 | 17.5506 | -354.2938 | 17.3864 | -354.383 | 15.4953
11:25 | 309 | 17.3549 | 177.0468 | 402.8953 | 408.5364 | -19.996 | -49.1237 | 0.1632 | -0.9432 | -8.0394 | -8.0901 | -3.5447 | -4.6123 | 1.428 | -5.571 | 0.522 | 0.5341 | 0.8922 | 0.6301 | -127.6523 |  | -1.793 | -2.99 | -10.6661 | -9.4318 | -1.7743 |  | -5.4934 | -4.7966 | 3.9603 | 3.3051 | 3.297 | 0.8357 | 9.8857 | 12.9603 | 13.5247 | 10.0962 | -0.0004 | -0.0032 | 0.0007 | 0.0033 | 0.0002 | -0.0005 | 0.0009 | -0.0177 | 0.0097 | -360.845 | 17.0948 | -361.2789 | 17.3802 | -361.4174 | 18.1009 | -361.4851 | 17.5629 | -354.2938 | 17.3823 | -354.3184 | 15.4707
11:25 | 310 | 17.3809 | 177.1893 | 403.1806 | 408.722 | -19.9566 | -49.1891 | 0.1871 | -0.9429 | -8.0915 | -8.047 | -3.661 | -4.6194 | 1.43 | -5.5916 | 0.5218 | 0.5356 | 0.8904 | 0.6285 | -127.7751 |  | -1.8443 | -2.9387 | -10.6656 | -9.453 | -1.7537 |  | -5.4126 | -4.8914 | 3.9634 | 3.3051 | 3.2988 | 0.8376 | 9.8726 | 12.9304 | 13.4683 | 10.0707 | -0.0002 | -0.0024 | 0.0008 | 0.0038 | 0.0009 | -0.0004 | 0.0342 | -0.0145 | -0.0023 | -360.8266 | 17.1236 | -361.2728 | 17.3864 | -361.3989 | 18.0947 | -361.4912 | 17.5732 | -354.2599 | 17.3699 | -354.2876 | 15.4707
11:25 | 311 | 17.4691 | 177.3834 | 403.465 | 408.9744 | -19.9684 | -49.2576 | 0.1637 | -0.8508 | -8.0501 | -7.8613 | -3.6033 | -4.7484 | 1.3844 | -5.664 | 0.5202 | 0.5364 | 0.8876 | 0.6286 | -127.8836 |  | -1.8336 | -2.997 | -10.73 | -9.4566 | -1.8442 |  | -5.3162 | -4.8314 | 3.9661 | 3.3064 | 3.2992 | 0.8367 | 9.8507 | 12.9546 | 13.4919 | 10.0607 | -0.0003 | -0.0023 | 0.0008 | 0.0036 | 0.0007 | -0.0003 | 0.0119 | -0.009 | -0.011 | -360.7773 | 17.1605 | -361.2512 | 17.4295 | -361.3959 | 18.0968 | -361.4697 | 17.5609 | -354.2692 | 17.3823 | -354.2938 | 15.4625
11:25 | 312 | 17.4817 | 177.397 | 403.5901 | 409.186 | -20.0061 | -49.4441 | 0.0862 | -0.8381 | -8.0503 | -8.0379 | -3.5769 | -4.7806 | 1.326 | -5.722 | 0.5209 | 0.5389 | 0.8884 | 0.6305 | -127.9007 |  | -1.8313 | -2.9537 | -10.7379 | -9.5173 | -1.8123 |  | -5.365 | -4.8805 | 3.9669 | 3.315 | 3.3002 | 0.8383 | 9.8719 | 12.9521 | 13.521 | 10.0888 | -0.0001 | -0.0029 | 0.0004 | 0.0035 | 0.0003 | -0.0007 | 0.0004 | -0.0103 | -0.0153 | -360.7927 | 17.1872 | -361.2512 | 17.4849 | -361.4082 | 18.0927 | -361.4882 | 17.5732 | -354.2692 | 17.372 | -354.3061 | 15.4851
11:25 | 313 | 17.388 | 177.4508 | 403.8261 | 409.3969 | -19.9267 | -49.3572 | 0.1553 | -0.8498 | -8.0229 | -8.1257 | -3.623 | -4.6872 | 1.3738 | -5.69 | 0.5221 | 0.5365 | 0.8893 | 0.6313 | -128.0219 |  | -1.7507 | -2.8511 | -10.7058 | -9.4754 | -1.7813 |  | -5.3796 | -4.8467 | 3.9692 | 3.3132 | 3.3017 | 0.836 | 9.845 | 12.9314 | 13.5083 | 10.0842 | 0.0005 | -0.0027 | 0.0006 | 0.0032 | 0.0007 | -0.0009 | 0.0063 | 0.0075 | -0.0085 | -360.8235 | 17.2385 | -361.2297 | 17.5096 | -361.3989 | 18.0947 | -361.4789 | 17.5691 | -354.2753 | 17.3905 | -354.263 | 15.4666
11:25 | 314 | 17.3782 | 177.6416 | 404.0632 | 409.673 | -19.8609 | -49.3976 | 0.1277 | -0.8605 | -8.0252 | -8.1048 | -3.5977 | -4.7169 | 1.3055 | -5.6686 | 0.5209 | 0.5372 | 0.8902 | 0.6323 | -128.1294 |  | -1.7857 | -2.75 | -10.79 | -9.4775 | -1.768 |  | -5.4297 | -4.8596 | 3.9711 | 3.3129 | 3.305 | 0.838 | 9.8611 | 12.9997 | 13.5368 | 10.1174 | -0.0002 | -0.0026 | -0.0001 | 0.0029 | 0 | -0.0006 | 0.0034 | 0.0064 | -0.0079 | -360.802 | 17.2673 | -361.2389 | 17.5547 | -361.4082 | 18.0865 | -361.4574 | 17.5568 | -354.263 | 17.3843 | -354.2599 | 15.4727
11:25 | 315 | 17.401 | 177.7936 | 404.3597 | 409.9068 | -19.8251 | -49.4296 | 0.182 | -0.9185 | -8.1431 | -8.2034 | -3.7423 | -4.7568 | 1.3178 | -5.7741 | 0.5214 | 0.5372 | 0.8922 | 0.6321 | -128.1979 |  | -1.7656 | -2.8781 | -10.7635 | -9.5129 | -1.7991 |  | -5.3461 | -4.8659 | 3.9714 | 3.3107 | 3.3024 | 0.8379 | 9.8659 | 12.9811 | 13.5114 | 10.0879 | -0.0002 | -0.0025 | 0.0006 | 0.0033 | 0.001 | -0.0003 | -0.0026 | 0.0053 | -0.0303 | -360.7497 | 17.294 | -361.2082 | 17.5896 | -361.3835 | 18.0845 | -361.4574 | 17.5609 | -354.2168 | 17.3864 | -354.2722 | 15.4789
11:25 | 316 | 17.4299 | 177.8492 | 404.6736 | 410.1172 | -19.8634 | -49.5399 | 0.1584 | -0.8649 | -8.0706 | -8.102 | -3.7765 | -4.664 | 1.3096 | -5.6458 | 0.5218 | 0.5382 | 0.8948 | 0.6315 | -128.2935 |  | -1.8121 | -2.9267 | -10.7456 | -9.5484 | -1.7368 |  | -5.3731 | -4.7783 | 3.9745 | 3.3115 | 3.3072 | 0.8375 | 9.859 | 12.9568 | 13.5274 | 10.0868 | 0 | -0.0026 | 0.0005 | 0.0036 | 0.0008 | -0.0004 | 0.0096 | -0.0132 | -0.0164 | -360.7866 | 17.3432 | -361.1589 | 17.6245 | -361.3989 | 18.1112 | -361.4697 | 17.565 | -354.2599 | 17.3823 | -354.2076 | 15.4707
11:25 | 317 | 17.4486 | 177.9575 | 404.9385 | 410.5387 | -19.8953 | -49.6098 | 0.1315 | -0.8988 | -8.134 | -8.1461 | -3.7763 | -4.7292 | 1.3206 | -5.6081 | 0.5215 | 0.5379 | 0.895 | 0.6331 | -128.4079 |  | -1.8036 | -2.9632 | -10.7858 | -9.509 | -1.8835 |  | -5.3854 | -4.8215 | 3.9744 | 3.3098 | 3.3099 | 0.8376 | 9.8824 | 12.9683 | 13.5602 | 10.1166 | 0 | -0.0027 | 0.0003 | 0.0034 | 0.0003 | -0.001 | -0.0048 | -0.0026 | -0.0044 | -360.725 | 17.3638 | -361.1589 | 17.6636 | -361.4205 | 18.0947 | -361.4697 | 17.5814 | -354.2353 | 17.3617 | -354.223 | 15.4727
11:25 | 318 | 17.4367 | 178.1267 | 405.1702 | 410.8504 | -19.7395 | -49.6317 | 0.2012 | -0.9463 | -8.1631 | -8.0971 | -3.7065 | -4.6913 | 1.4028 | -5.5708 | 0.5228 | 0.5412 | 0.8933 | 0.6332 | -128.5051 |  | -1.7955 | -2.925 | -10.8586 | -9.5363 | -1.9112 |  | -5.4012 | -4.8639 | 3.9773 | 3.3117 | 3.3076 | 0.8369 | 9.9029 | 12.9719 | 13.5314 | 10.1131 | 0 | -0.0027 | 0.0004 | 0.0036 | 0.0003 | -0.0003 | 0.0045 | -0.0135 | -0.0073 | -360.7127 | 17.4274 | -361.1343 | 17.6923 | -361.3774 | 18.0865 | -361.4266 | 17.5629 | -354.223 | 17.3823 | -354.2076 | 15.4584
11:25 | 319 | 17.4596 | 178.1414 | 405.4764 | 411.0741 | -19.895 | -49.7631 | 0.1937 | -1.0307 | -8.1252 | -8.165 | -3.6355 | -4.6019 | 1.4439 | -5.6136 | 0.5223 | 0.5398 | 0.8934 | 0.634 | -128.5779 |  | -1.8403 | -2.8288 | -10.761 | -9.5455 | -1.8426 |  | -5.3866 | -4.8357 | 3.9775 | 3.3149 | 3.3117 | 0.836 | 9.88 | 12.9949 | 13.5121 | 10.1256 | -0.0003 | -0.0023 | 0.0005 | 0.0031 | 0.001 | -0.0011 | 0.0187 | -0.007 | -0.0123 | -360.7343 | 17.4541 | -361.1712 | 17.7518 | -361.3989 | 18.0804 | -361.3897 | 17.5486 | -354.2168 | 17.3987 | -354.2322 | 15.483
11:25 | 320 | 17.4036 | 178.141 | 405.6875 | 411.2517 | -20.001 | -49.9238 | 0.1237 | -1.0346 | -8.1293 | -8.1464 | -3.6428 | -4.6642 | 1.4584 | -5.7318 | 0.5237 | 0.5429 | 0.8979 | 0.6353 | -128.8221 |  | -1.7932 | -2.8994 | -10.8096 | -9.4744 | -1.8123 |  | -5.4076 | -4.8188 | 3.9771 | 3.3122 | 3.3114 | 0.8372 | 9.8889 | 13.0448 | 13.576 | 10.1221 | -0.0002 | -0.0024 | 0.0007 | 0.0035 | 0.0003 | -0.0005 | 0.0062 | -0.0041 | -0.0093 | -360.682 | 17.4931 | -361.1651 | 17.7929 | -361.3866 | 18.0865 | -361.4359 | 17.5671 | -354.183 | 17.4007 | -354.2722 | 15.4892
11:25 | 321 | 17.4789 | 178.2007 | 405.9418 | 411.5537 | -19.9986 | -49.9572 | 0.2185 | -0.9201 | -8.1947 | -7.949 | -3.6386 | -4.6661 | 1.5155 | -5.7632 | 0.5245 | 0.5449 | 0.8937 | 0.6361 | -128.795 |  | -1.7612 | -2.7986 | -10.8448 | -9.4862 | -1.7846 |  | -5.3942 | -4.8248 | 3.9793 | 3.3134 | 3.3138 | 0.8381 | 9.895 | 13.062 | 13.5451 | 10.1403 | -0.0003 | -0.0032 | 0.0008 | 0.0036 | 0.0001 | -0.0011 | 0.0046 | -0.0037 | -0.0116 | -360.7127 | 17.4993 | -361.0881 | 17.8011 | -361.3928 | 18.105 | -361.4266 | 17.5671 | -354.2076 | 17.3802 | -354.1615 | 15.4625
11:25 | 322 | 17.511 | 178.42 | 406.1816 | 411.7875 | -20.0196 | -49.9371 | 0.1309 | -0.9546 | -8.1684 | -7.9555 | -3.7071 | -4.5937 | 1.4534 | -5.767 | 0.5247 | 0.5458 | 0.8955 | 0.6348 | -128.9337 |  | -1.7161 | -2.727 | -10.7785 | -9.4054 | -1.7888 |  | -5.3906 | -4.8852 | 3.979 | 3.3123 | 3.312 | 0.84 | 9.8961 | 13.0458 | 13.5638 | 10.1298 | 0 | -0.003 | 0.0005 | 0.0032 | 0.0006 | -0.0005 | 0.0083 | 0.0073 | -0.007 | -360.6758 | 17.5239 | -361.0512 | 17.8073 | -361.3528 | 18.1009 | -361.4451 | 17.5773 | -354.183 | 17.3638 | -354.1368 | 15.444
11:25 | 323 | 17.4689 | 178.4658 | 406.367 | 411.9595 | -20.0127 | -49.9877 | 0.1437 | -0.9439 | -8.1296 | -8.1385 | -3.6914 | -4.6867 | 1.3841 | -5.8499 | 0.525 | 0.5479 | 0.8974 | 0.6359 | -129.082 |  | -1.9059 | -2.874 | -10.8144 | -9.4737 | -1.8477 |  | -5.3288 | -4.8217 | 3.9803 | 3.3163 | 3.3135 | 0.8412 | 9.9114 | 13.0607 | 13.5476 | 10.1228 | -0.0008 | -0.003 | 0.0008 | 0.0036 | 0.0001 | -0.0003 | 0.0064 | -0.0114 | -0.0179 | -360.6696 | 17.5671 | -361.0851 | 17.8586 | -361.3589 | 18.1009 | -361.4543 | 17.5753 | -354.1738 | 17.3864 | -354.1799 | 15.4727
11:25 | 324 | 17.5211 | 178.651 | 406.5236 | 412.1824 | -20.0422 | -50.0969 | 0.1557 | -0.9582 | -8.0702 | -8.0712 | -3.719 | -4.7019 | 1.3341 | -5.6734 | 0.5241 | 0.5473 | 0.9006 | 0.638 | -129.2012 |  | -1.8876 | -2.9368 | -10.8168 | -9.5154 | -1.8845 |  | -5.467 | -4.8635 | 3.9782 | 3.3131 | 3.3134 | 0.8426 | 9.9376 | 13.0991 | 13.5604 | 10.1593 | -0.0003 | -0.0026 | 0.0007 | 0.0035 | 0.0007 | -0.0008 | -0.008 | -0.006 | -0.0164 | -360.6573 | 17.6204 | -361.1158 | 17.8997 | -361.402 | 18.0824 | -361.3866 | 17.5609 | -354.1799 | 17.4007 | -354.223 | 15.483
11:25 | 325 | 17.5139 | 178.7342 | 406.8322 | 412.3812 | -20.0755 | -49.9857 | 0.1477 | -0.9035 | -8.093 | -8.0766 | -3.7807 | -4.6629 | 1.2606 | -5.6604 | 0.5248 | 0.5472 | 0.8969 | 0.6379 | -129.1625 |  | -1.8255 | -2.901 | -10.7776 | -9.5496 | -1.8261 |  | -5.3915 | -4.7952 | 3.9764 | 3.313 | 3.3145 | 0.844 | 9.9514 | 13.1188 | 13.5978 | 10.1904 | -0.0001 | -0.0027 | 0.0005 | 0.0033 | 0.0003 | -0.0002 | 0.02 | -0.0045 | -0.0229 | -360.6019 | 17.6122 | -361.1312 | 17.8976 | -361.3835 | 18.0906 | -361.3897 | 17.5424 | -354.1491 | 17.3966 | -354.2107 | 15.4851
11:25 | 326 | 17.5764 | 178.7185 | 406.8497 | 412.5174 | -20.0264 | -49.9126 | 0.148 | -0.8691 | -8.0541 | -7.9897 | -3.7284 | -4.5974 | 1.225 | -5.6196 | 0.5253 | 0.5477 | 0.898 | 0.6374 | -129.1861 |  | -1.7493 | -2.9586 | -10.8641 | -9.4848 | -1.8203 |  | -5.3422 | -4.7305 | 3.9757 | 3.3153 | 3.3127 | 0.8457 | 9.9782 | 13.1106 | 13.5941 | 10.1944 | 0 | -0.0031 | 0.0003 | 0.0036 | 0.0005 | -0.001 | 0.0105 | -0.0127 | -0.0162 | -360.6327 | 17.6184 | -361.0604 | 17.9038 | -361.3497 | 18.0927 | -361.4297 | 17.5753 | -354.1061 | 17.3782 | -354.1584 | 15.4748
11:25 | 327 | 17.5021 | 178.8689 | 407.1277 | 412.7712 | -19.8952 | -49.7222 | 0.2154 | -0.9169 | -8.059 | -8.0215 | -3.6989 | -4.6388 | 1.2189 | -5.574 | 0.5245 | 0.5502 | 0.8999 | 0.6385 | -129.2598 |  | -1.7734 | -2.9126 | -10.8923 | -9.5527 | -1.8052 |  | -5.365 | -4.7562 | 3.9753 | 3.3141 | 3.3142 | 0.8476 | 9.9688 | 13.1361 | 13.5631 | 10.1904 | 0 | -0.0027 | 0.0008 | 0.0035 | 0.0004 | -0.0005 | -0.0022 | -0.015 | -0.0282 | -360.6512 | 17.6225 | -361.0143 | 17.8935 | -361.3466 | 18.105 | -361.4636 | 17.5876 | -354.1768 | 17.3802 | -354.1122 | 15.444
11:25 | 328 | 17.5649 | 178.9025 | 407.1951 | 412.8419 | -19.9242 | -49.6288 | 0.3026 | -0.9304 | -8.0206 | -8.0715 | -3.7775 | -4.5895 | 1.2578 | -5.6172 | 0.5273 | 0.552 | 0.9044 | 0.6383 | -129.3282 |  | -1.7305 | -2.8756 | -10.8142 | -9.6024 | -1.8552 |  | -5.3219 | -4.7216 | 3.975 | 3.3155 | 3.3138 | 0.8514 | 9.9584 | 13.1142 | 13.5876 | 10.203 | -0.0008 | -0.0028 | 0.0005 | 0.0032 | 0.0006 | -0.0007 | -0.0068 | -0.0098 | 0.0054 | -360.6173 | 17.641 | -361.0574 | 17.9243 | -361.3497 | 18.105 | -361.4512 | 17.5937 | -354.1768 | 17.3802 | -354.1184 | 15.4584
11:25 | 329 | 17.4902 | 179.0062 | 407.4959 | 413.0562 | -19.8596 | -49.6949 | 0.2213 | -0.9828 | -8.0856 | -8.0223 | -3.7134 | -4.5222 | 1.2491 | -5.6406 | 0.5257 | 0.552 | 0.8975 | 0.6387 | -129.4714 |  | -1.7913 | -3.1452 | -10.7618 | -9.4961 | -1.8688 |  | -5.3285 | -4.816 | 3.9751 | 3.3147 | 3.3161 | 0.8542 | 9.9702 | 13.1082 | 13.5798 | 10.1865 | -0.0001 | -0.0025 | 0.0004 | 0.0031 | 0.0008 | -0.0009 | 0.013 | -0.0164 | -0.0048 | -360.6266 | 17.6759 | -361.0943 | 17.9387 | -361.3466 | 18.0783 | -361.4051 | 17.5588 | -354.1122 | 17.3987 | -354.1584 | 15.4727
11:25 | 330 | 17.586 | 179.0882 | 407.6568 | 413.2534 | -19.9898 | -49.7809 | 0.1572 | -0.9034 | -8.0719 | -7.972 | -3.6789 | -4.5714 | 1.1392 | -5.598 | 0.5271 | 0.5505 | 0.9014 | 0.639 | -129.5668 |  | -1.8826 | -3.0046 | -10.868 | -9.4968 | -1.925 |  | -5.2982 | -4.7157 | 3.9743 | 3.3116 | 3.31 | 0.853 | 10.0139 | 13.1408 | 13.6206 | 10.2755 | 0 | -0.0032 | 0.0007 | 0.0035 | 0.0005 | -0.0004 | 0.018 | -0.0079 | -0.0097 | -360.5835 | 17.6882 | -361.1097 | 17.9654 | -361.3774 | 18.0639 | -361.3559 | 17.5465 | -354.1215 | 17.4254 | -354.1799 | 15.5118
11:25 | 331 | 17.5627 | 179.2864 | 408.1694 | 413.7789 | -20.0137 | -49.9561 | 0.1718 | -0.9146 | -8.0124 | -7.92 | -3.6906 | -4.561 | 1.2604 | -5.4372 | 0.527 | 0.5504 | 0.9014 | 0.6395 | -129.6237 |  | -1.8261 | -2.9092 | -10.7612 | -9.4019 | -1.8258 |  | -5.2886 | -4.7389 | 3.9754 | 3.3141 | 3.3147 | 0.8536 | 9.9989 | 13.1546 | 13.6744 | 10.2608 | 0.0001 | -0.003 | 0.0006 | 0.0039 | 0.0006 | -0.0006 | 0.0058 | -0.0149 | -0.0125 | -360.5989 | 17.6882 | -361.0974 | 17.9715 | -361.3743 | 18.0865 | -361.3928 | 17.5629 | -354.0938 | 17.4356 | -354.1399 | 15.5426
11:25 | 332 | 17.533 | 179.5071 | 408.9428 | 414.2645 | -20.0317 | -50.1644 | 0.1412 | -0.8967 | -8.067 | -7.8971 | -3.7168 | -4.5753 | 1.1555 | -5.391 | 0.5278 | 0.5494 | 0.9093 | 0.6415 | -129.7704 |  | -1.7569 | -2.8882 | -10.7067 | -9.5365 | -1.8147 |  | -5.3403 | -4.8051 | 3.9794 | 3.3182 | 3.3164 | 0.851 | 10.0142 | 13.129 | 13.6755 | 10.2422 | 0 | -0.0026 | 0.0006 | 0.003 | 0.0001 | -0.0008 | 0.0214 | -0.0099 | -0.0077 | -360.5835 | 17.6471 | -361.0235 | 17.9531 | -361.3497 | 18.1071 | -361.4328 | 17.565 | -354.0815 | 17.4664 | -354.0599 | 15.559
11:25 | 333 | 17.5496 | 179.7839 | 409.7646 | 414.8911 | -20.0146 | -50.4869 | 0.0736 | -0.9396 | -8.1794 | -7.9403 | -3.6247 | -4.5037 | 1.1331 | -5.3599 | 0.5281 | 0.5519 | 0.9076 | 0.6434 | -129.7145 |  | -1.6355 | -2.9872 | -10.8297 | -9.5203 | -1.8701 |  | -5.4293 | -4.7923 | 3.9837 | 3.3177 | 3.3198 | 0.8474 | 10.0486 | 13.1408 | 13.7248 | 10.2697 | -0.0004 | -0.0024 | 0.0002 | 0.0033 | 0.0009 | -0.001 | 0.0131 | -0.0253 | -0.014 | -360.5312 | 17.643 | -361.0081 | 17.951 | -361.322 | 18.0947 | -361.4205 | 17.5629 | -354.0353 | 17.5075 | -354.0353 | 15.5939
11:25 | 334 | 17.5553 | 180.082 | 410.5566 | 415.639 | -20.0611 | -50.6752 | 0.1449 | -0.9596 | -8.1693 | -8.0096 | -3.6349 | -4.6225 | 1.235 | -5.3669 | 0.5289 | 0.5504 | 0.9106 | 0.6433 | -129.8379 |  | -1.6928 | -3.0303 | -10.8136 | -9.5876 | -1.8676 |  | -5.3749 | -4.7672 | 3.991 | 3.3218 | 3.32 | 0.8457 | 10.036 | 13.1742 | 13.7398 | 10.298 | -0.0001 | -0.0027 | 0.0003 | 0.0036 | 0.0001 | -0.0004 | 0.0099 | -0.0077 | 0.0077 | -360.5558 | 17.6594 | -361.0574 | 17.951 | -361.322 | 18.0804 | -361.3959 | 17.5568 | -354.0107 | 17.5835 | -354.0507 | 15.6719
11:25 | 335 | 17.6195 | 180.3805 | 411.2273 | 416.1659 | -20.0941 | -50.8353 | 0.1182 | -1.0111 | -8.0599 | -8.0187 | -3.6185 | -4.5792 | 1.2146 | -5.3567 | 0.5306 | 0.553 | 0.9141 | 0.6469 | -129.941 |  | -1.6975 | -2.9775 | -10.8558 | -9.7346 | -1.9203 |  | -5.3941 | -4.839 | 3.9961 | 3.3244 | 3.3282 | 0.842 | 10.0108 | 13.1255 | 13.7236 | 10.2678 | 0.0001 | -0.003 | 0.0008 | 0.0035 | 0.0007 | -0.0007 | 0.0078 | -0.0228 | 0.0009 | -360.6143 | 17.6882 | -361.0481 | 17.9798 | -361.3651 | 18.0763 | -361.3159 | 17.5547 | -354.023 | 17.6492 | -354.0414 | 15.7273
11:25 | 336 | 17.5873 | 180.6161 | 412.1033 | 416.8885 | -20.0023 | -50.9466 | 0.1627 | -0.991 | -8.1994 | -8.1815 | -3.621 | -4.4969 | 1.2165 | -5.4593 | 0.5306 | 0.5589 | 0.9136 | 0.647 | -129.9982 |  | -1.6702 | -2.967 | -10.9512 | -9.6426 | -1.9088 |  | -5.3837 | -4.8628 | 3.9996 | 3.3244 | 3.3301 | 0.839 | 10.0427 | 13.1756 | 13.7258 | 10.2866 | 0.0001 | -0.0025 | 0.0005 | 0.0036 | 0.0003 | -0.0003 | 0.011 | -0.0148 | -0.0222 | -360.5435 | 17.6697 | -361.0481 | 17.9674 | -361.2974 | 18.0721 | -361.3559 | 17.5486 | -353.9368 | 17.6923 | -354.0138 | 15.7705
11:25 | 337 | 17.5719 | 180.9183 | 412.8272 | 417.4883 | -19.9708 | -51.1041 | 0.2117 | -1.0114 | -8.1911 | -8.0788 | -3.6357 | -4.6164 | 1.1977 | -5.3663 | 0.5326 | 0.5622 | 0.9176 | 0.6506 | -130.1142 |  | -1.7237 | -3.0136 | -10.9387 | -9.6441 | -1.8616 |  | -5.4053 | -4.9196 | 4.0029 | 3.3275 | 3.3294 | 0.839 | 10.0443 | 13.2168 | 13.7222 | 10.2956 | -0.0006 | -0.0027 | 0.0004 | 0.0034 | 0.0003 | -0.001 | 0.0038 | 0.0018 | -0.0008 | -360.5312 | 17.6307 | -360.9712 | 17.9305 | -361.3005 | 18.0968 | -361.3682 | 17.5465 | -353.9184 | 17.7067 | -353.9061 | 15.8013
11:25 | 338 | 17.597 | 181.2666 | 413.5911 | 418.2295 | -20.0572 | -51.2087 | 0.1678 | -1.0386 | -8.2394 | -8.0735 | -3.7945 | -4.6094 | 1.112 | -5.4233 | 0.5337 | 0.5652 | 0.9244 | 0.6535 | -130.3009 |  | -1.7193 | -2.9583 | -10.9765 | -9.6583 | -1.9615 |  | -5.4586 | -4.8318 | 4.0061 | 3.3284 | 3.3074 | 0.8423 | 10.0417 | 13.261 | 13.7398 | 10.3153 | -0.0002 | -0.0029 | 0.0008 | 0.0035 | 0.0012 | 0 | 0.003 | 0.0021 | -0.0092 | -360.5373 | 17.6553 | -360.9897 | 17.9407 | -361.2666 | 18.0906 | -361.3897 | 17.5629 | -353.903 | 17.7785 | -353.9091 | 15.8464
11:25 | 339 | 17.6083 | 181.5615 | 414.0164 | 418.9537 | -20.0728 | -51.3465 | 0.1767 | -1.0591 | -8.2545 | -8.0044 | -3.7931 | -4.6005 | 1.1516 | -5.4024 | 0.5344 | 0.5605 | 0.9243 | 0.6544 | -130.406 |  | -1.7902 | -3.0474 | -11.0505 | -9.6828 | -2.0104 |  | -5.4399 | -4.8242 | 4.0105 | 3.3312 | 3.3289 | 0.8587 | 10.0453 | 13.3396 | 13.7776 | 10.3421 | 0.0003 | -0.0028 | 0.0003 | 0.0033 | 0.0002 | -0.0006 | 0.0167 | -0.0096 | -0.0123 | -360.5558 | 17.6533 | -360.9958 | 17.9572 | -361.2943 | 18.0701 | -361.3466 | 17.5629 | -353.863 | 17.8463 | -353.8845 | 15.9203
11:25 | 340 | 17.6288 | 181.9598 | 414.7835 | 419.8062 | -20.0938 | -51.4278 | 0.071 | -1.0329 | -8.2602 | -8.1069 | -3.7067 | -4.636 | 1.0847 | -5.4232 | 0.5359 | 0.5571 | 0.9305 | 0.6543 | -130.5715 |  | -1.7857 | -2.9544 | -11.0123 | -9.6584 | -1.9469 |  | -5.4675 | -4.7992 | 4.0128 | 3.3328 | 3.3277 | 0.859 | 10.0709 | 13.3244 | 13.8478 | 10.3508 | -0.0003 | -0.0032 | 0.0005 | 0.0031 | 0.0004 | -0.0008 | -0.0077 | -0.0101 | -0.0189 | -360.5343 | 17.6348 | -361.0051 | 17.9448 | -361.2666 | 18.0763 | -361.3005 | 17.5424 | -353.8322 | 17.875 | -353.8476 | 15.9676
11:25 | 341 | 17.6626 | 182.318 | 415.5673 | 420.4964 | -20.0502 | -51.5602 | 0.1507 | -0.9594 | -8.351 | -8.3003 | -3.6978 | -4.539 | 1.2728 | -5.3338 | 0.5379 | 0.5583 | 0.9324 | 0.6577 | -130.7082 |  | -1.7918 | -2.9347 | -10.9528 | -9.6029 | -1.8775 |  | -5.4747 | -4.8478 | 4.0157 | 3.335 | 3.3301 | 0.8566 | 10.0741 | 13.3223 | 13.877 | 10.3936 | 0.0001 | -0.0022 | 0.0004 | 0.0033 | 0.0003 | -0.0005 | 0.015 | -0.0126 | 0.0063 | -360.4758 | 17.643 | -360.9835 | 17.9243 | -361.2728 | 18.0824 | -361.2912 | 17.5342 | -353.7799 | 17.9305 | -353.786 | 15.9984
11:25 | 342 | 17.7742 | 182.7691 | 416.3148 | 421.2325 | -20.1304 | -51.7927 | 0.078 | -0.956 | -8.3965 | -8.1988 | -3.6559 | -4.5539 | 1.2137 | -5.416 | 0.5366 | 0.5564 | 0.9338 | 0.6596 | -130.9221 |  | -1.8899 | -2.9913 | -10.9378 | -9.6431 | -1.8853 |  | -5.416 | -4.8563 | 4.017 | 3.3424 | 3.3308 | 0.8561 | 10.094 | 13.336 | 13.9115 | 10.4086 | -0.0005 | -0.0027 | 0.0006 | 0.0035 | 0.0004 | -0.0009 | 0.009 | -0.009 | -0.0144 | -360.5004 | 17.6204 | -360.9651 | 17.9387 | -361.2451 | 18.0783 | -361.3159 | 17.5547 | -353.7676 | 17.9818 | -353.783 | 16.0661
11:25 | 343 | 17.7514 | 183.0826 | 417.1257 | 421.9819 | -20.1589 | -51.9401 | 0.0537 | -0.9196 | -8.3737 | -8.243 | -3.7022 | -4.4856 | 1.1755 | -5.2209 | 0.5395 | 0.5647 | 0.9402 | 0.6612 | -131.2413 |  | -1.8434 | -3.0592 | -10.9157 | -9.6332 | -1.8828 |  | -5.4361 | -4.7619 | 4.0214 | 3.3764 | 3.3312 | 0.8554 | 10.1401 | 13.3477 | 13.9134 | 10.4193 | -0.0001 | -0.0027 | 0.0005 | 0.0036 | 0.0003 | -0.0006 | 0.0195 | 0.0006 | 0.0056 | -360.5219 | 17.6348 | -360.9189 | 17.9202 | -361.2512 | 18.0763 | -361.3159 | 17.5506 | -353.7214 | 18.0393 | -353.7614 | 16.1031
11:25 | 344 | 17.6548 | 183.4083 | 417.7542 | 422.5661 | -20.1367 | -51.9724 | 0.1336 | -0.8652 | -8.3506 | -8.3188 | -3.6887 | -4.5984 | 1.0587 | -5.4595 | 0.5406 | 0.6035 | 0.9436 | 0.6634 | -131.3868 |  | -1.7933 | -2.9477 | -10.8797 | -9.5471 | -1.8082 |  | -5.4967 | -4.7885 | 4.0243 | 3.3864 | 3.3266 | 0.8546 | 10.1795 | 13.3812 | 13.9468 | 10.4356 | 0.0002 | -0.0028 | 0.0007 | 0.0037 | 0.0003 | -0.0011 | 0.0117 | -0.0029 | -0.0061 | -360.5035 | 17.6143 | -360.9281 | 17.9223 | -361.2266 | 18.066 | -361.2789 | 17.5527 | -353.6753 | 18.0742 | -353.6814 | 16.14
11:25 | 345 | 17.7019 | 183.8052 | 418.5084 | 423.3212 | -19.9486 | -51.9753 | 0.1881 | -0.8544 | -8.3631 | -8.3206 | -3.6154 | -4.589 | 1.1715 | -5.4231 | 0.5427 | 0.6009 | 0.9485 | 0.6643 | -131.5708 |  | -1.8218 | -2.8744 | -10.9377 | -9.6856 | -1.8627 |  | -5.5363 | -4.8283 | 4.025 | 3.3865 | 3.3253 | 0.8565 | 10.2016 | 13.3914 | 13.9203 | 10.4122 | -0.0007 | -0.0028 | 0.0003 | 0.0037 | 0.0006 | -0.0006 | 0.0015 | -0.0106 | -0.0037 | -360.4327 | 17.604 | -360.9097 | 17.9223 | -361.2082 | 18.0701 | -361.282 | 17.5527 | -353.6506 | 18.1153 | -353.663 | 16.1934
11:25 | 346 | 17.7341 | 184.0305 | 419.2434 | 423.9984 | -19.9914 | -52.0652 | 0.1267 | -0.795 | -8.3137 | -8.3085 | -3.5965 | -4.5999 | 1.2933 | -5.3819 | 0.5446 | 0.5863 | 0.9455 | 0.6642 | -131.7469 |  | -1.8391 | -2.9457 | -10.9324 | -9.5856 | -1.7996 |  | -5.5001 | -4.8986 | 4.0255 | 3.3784 | 3.3266 | 0.8555 | 10.1886 | 13.4426 | 13.9229 | 10.4499 | -0.0003 | -0.0025 | 0.0007 | 0.0034 | 0.0007 | -0.0006 | 0.0036 | -0.003 | -0.0133 | -360.4327 | 17.6143 | -360.9097 | 17.9079 | -361.1989 | 18.0721 | -361.2451 | 17.5383 | -353.623 | 18.1769 | -353.6537 | 16.2386
11:25 | 347 | 17.7472 | 184.4522 | 420.0183 | 424.6764 | -20.0126 | -52.2294 | 0.1236 | -0.7963 | -8.356 | -8.4592 | -3.6258 | -4.553 | 1.2765 | -5.4288 | 0.546 | 0.589 | 0.949 | 0.6683 | -131.8893 |  | -1.7339 | -2.92 | -10.9684 | -9.6225 | -1.7444 |  | -5.4921 | -5.02 | 4.027 | 3.3761 | 3.3256 | 0.8575 | 10.1935 | 13.4817 | 13.9765 | 10.4559 | -0.0002 | -0.0029 | 0.0004 | 0.0033 | 0.0009 | -0.0005 | 0.0152 | -0.0056 | -0.0098 | -360.4573 | 17.6081 | -360.922 | 17.9284 | -361.1774 | 18.0619 | -361.2635 | 17.5547 | -353.6014 | 18.2179 | -353.6291 | 16.2899
11:26 | 348 | 17.6707 | 184.7549 | 420.6655 | 425.3151 | -20.0397 | -52.2204 | 0.1788 | -0.8485 | -8.3913 | -8.5072 | -3.5988 | -4.5567 | 1.3855 | -5.4469 | 0.5486 | 0.5861 | 0.9546 | 0.6682 | -132.0245 |  | -1.8207 | -2.9486 | -10.9726 | -9.6248 | -1.8294 |  | -5.509 | -4.9953 | 4.0253 | 3.3704 | 3.3278 | 0.862 | 10.2015 | 13.5129 | 14.0313 | 10.4522 | 0.0001 | -0.0032 | 0.0008 | 0.0036 | 0.0004 | -0.0002 | 0.0019 | 0.0072 | -0.0023 | -360.4266 | 17.5999 | -360.8666 | 17.9017 | -361.1928 | 18.0804 | -361.242 | 17.5465 | -353.5306 | 18.2652 | -353.5645 | 16.3228
11:26 | 349 | 17.6685 | 184.9947 | 421.4377 | 426.1073 | -20.0318 | -52.2755 | 0.1781 | -0.8863 | -8.3948 | -8.3 | -3.548 | -4.5426 | 1.2973 | -5.5185 | 0.55 | 0.5844 | 0.9544 | 0.6687 | -132.2246 | -7.6321 | -1.7936 | -2.8812 | -10.884 | -9.6447 | -1.8097 |  | -5.5249 | -4.8981 | 4.0282 | 3.3715 | 3.3311 | 0.864 | 10.2187 | 13.5304 | 14.0854 | 10.5207 | -0.0003 | -0.0034 | 0.0005 | 0.0029 | 0.0007 | -0.0009 | -0.0014 | -0.008 | 0.0064 | -360.3804 | 17.5937 | -360.842 | 17.8791 | -361.1681 | 18.0845 | -361.242 | 17.5363 | -353.5183 | 18.296 | -353.5091 | 16.3618
11:26 | 350 | 17.6772 | 185.3206 | 422.2078 | 426.7864 | -20.0289 | -52.4578 | 0.1142 | -0.857 | -8.4035 | -8.305 | -3.6101 | -4.5367 | 1.2559 | -5.3991 | 0.5516 | 0.5815 | 0.9579 | 0.6714 | -132.2949 | -7.6814 | -1.8465 | -2.9789 | -10.8613 | -9.6547 | -1.9225 |  | -5.463 | -4.8997 | 4.0293 | 3.3697 | 3.3296 | 0.8626 | 10.2223 | 13.5338 | 14.0816 | 10.5363 | -0.0004 | -0.0024 | 0.0007 | 0.0038 | 0.0006 | 0 | 0.0024 | -0.0183 | -0.0116 | -360.4204 | 17.5814 | -360.8666 | 17.9079 | -361.1774 | 18.0721 | -361.2451 | 17.5588 | -353.4845 | 18.3411 | -353.5122 | 16.4275
11:26 | 351 | 17.724 | 185.7477 | 422.9161 | 427.3497 | -20.0867 | -52.442 | 0.1657 | -0.883 | -8.4928 | -8.3829 | -3.7697 | -4.4977 | 1.1712 | -5.3398 | 0.5544 | 0.5803 | 0.9607 | 0.6727 | -132.5179 | -7.7616 | -1.8931 | -2.9766 | -10.8533 | -9.6036 | -1.8739 |  | -5.4814 | -4.9257 | 4.0307 | 3.3675 | 3.3339 | 0.8653 | 10.2579 | 13.5179 | 14.1208 | 10.5593 | -0.0001 | -0.0023 | 0.0011 | 0.0039 | 0.0007 | -0.0008 | 0.0149 | -0.0158 | -0.0232 | -360.4112 | 17.6061 | -360.842 | 17.8956 | -361.1343 | 18.0639 | -361.2205 | 17.5568 | -353.4753 | 18.3986 | -353.5091 | 16.4521
11:26 | 352 | 17.7666 | 186.118 | 423.5083 | 428.056 | -20.076 | -52.3743 | 0.2086 | -0.9053 | -8.4742 | -8.3962 | -3.7451 | -4.5112 | 1.2078 | -5.2731 | 0.5554 | 0.5796 | 0.9638 | 0.675 | -132.5508 | -7.7498 | -1.7875 | -2.9914 | -10.9297 | -9.6532 | -1.8735 |  | -5.5194 | -4.9404 | 4.0326 | 3.3695 | 3.331 | 0.8668 | 10.2881 | 13.571 | 14.1211 | 10.5954 | -0.0002 | -0.0033 | 0.0006 | 0.0037 | 0.0004 | -0.0005 | 0.0228 | 0.0014 | -0.0024 | -360.3742 | 17.602 | -360.8112 | 17.8812 | -361.1251 | 18.0619 | -361.1589 | 17.5301 | -353.4291 | 18.452 | -353.4537 | 16.4953
11:26 | 353 | 17.7584 | 186.3671 | 424.0862 | 428.683 | -20.1076 | -52.4044 | 0.2332 | -0.7601 | -8.3131 | -8.2746 | -3.6314 | -4.5207 | 1.1988 | -5.4409 | 0.5564 | 0.5775 | 0.9623 | 0.675 | -132.7346 | -7.8587 | -1.8121 | -2.9747 | -10.9069 | -9.6635 | -1.8505 |  | -5.5115 | -4.9273 | 4.0351 | 3.3701 | 3.3335 | 0.8678 | 10.3413 | 13.578 | 14.1341 | 10.6254 | 0.0002 | -0.0027 | 0.0005 | 0.0037 | 0.0009 | -0.0008 | 0.0032 | -0.0059 | -0.0161 | -360.3742 | 17.5999 | -360.8327 | 17.9099 | -361.1374 | 18.0619 | -361.1835 | 17.5691 | -353.4229 | 18.4787 | -353.4414 | 16.5507
11:26 | 354 | 17.6572 | 186.6632 | 424.7538 | 429.2707 | -20.133 | -52.3058 | 0.2926 | -0.8392 | -8.2631 | -8.2609 | -3.6923 | -4.533 | 1.2097 | -5.3583 | 0.5574 | 0.5762 | 0.969 | 0.6765 | -132.9119 | -8.0263 | -1.8438 | -2.9632 | -10.9795 | -9.6903 | -1.8397 |  | -5.4787 | -4.9498 | 4.0376 | 3.3668 | 3.3381 | 0.8644 | 10.3529 | 13.6126 | 14.1504 | 10.5911 | -0.0004 | -0.0025 | 0.0005 | 0.0036 | 0.0004 | -0.0011 | 0.0295 | 0.0012 | -0.0012 | -360.3835 | 17.5999 | -360.8266 | 17.9182 | -361.1035 | 18.0824 | -361.1989 | 17.5465 | -353.3522 | 18.528 | -353.4414 | 16.5877
11:26 | 355 | 17.613 | 186.9405 | 425.3786 | 429.9693 | -19.9842 | -52.352 | 0.1624 | -0.8424 | -8.3169 | -8.2475 | -3.7594 | -4.5344 | 1.1868 | -5.3916 | 0.5602 | 0.5807 | 0.9683 | 0.6779 | -132.979 | -8.0767 | -1.9157 | -2.9798 | -11.0103 | -9.7416 | -1.8201 |  | -5.4795 | -5.0201 | 4.0422 | 3.3701 | 3.3409 | 0.8622 | 10.3727 | 13.6725 | 14.1511 | 10.6345 | -0.0006 | -0.0027 | 0.0001 | 0.0031 | 0.0002 | -0.0005 | 0.0106 | -0.0074 | -0.0221 | -360.3219 | 17.5753 | -360.7497 | 17.875 | -361.1097 | 18.0947 | -361.202 | 17.5404 | -353.3152 | 18.5506 | -353.3091 | 16.602
11:26 | 356 | 17.6206 | 187.2208 | 426.0248 | 430.5306 | -20.0394 | -50.8848 | 0.1319 | -0.8316 | -8.3347 | -8.2686 | -3.6332 | -4.5405 | 1.1562 | -5.3549 | 0.5607 | 0.5807 | 0.9681 | 0.6795 | -133.0396 | -8.1161 | -1.9363 | -2.9663 | -11.0138 | -9.7036 | -1.7967 |  | -5.4954 | -4.9485 | 4.0465 | 3.3683 | 3.3395 | 0.861 | 10.3461 | 13.6749 | 14.1943 | 10.6309 | 0.0002 | -0.0028 | 0.0006 | 0.0037 | 0.0007 | -0.0006 | 0.0086 | 0.0076 | -0.0132 | -360.3281 | 17.5732 | -360.7558 | 17.9058 | -361.1312 | 18.0865 | -361.1866 | 17.5732 | -353.3122 | 18.5752 | -353.3522 | 16.6677
11:26 | 357 | 17.7002 | 187.6062 | 426.8321 | 431.2502 | -20.0291 | -48.5643 | 0.1488 | -0.8926 | -8.2801 | -8.2332 | -3.6614 | -4.427 | 1.1984 | -5.2421 | 0.5613 | 0.5786 | 0.9666 | 0.6788 | -133.0269 | -7.9964 | -1.8757 | -2.9135 | -10.8941 | -9.5124 | -1.7524 |  | -5.3902 | -4.9306 | 4.0541 | 3.3664 | 3.3481 | 0.8564 | 10.3935 | 13.705 | 14.242 | 10.6146 | 0 | -0.0033 | 0.0008 | 0.0036 | 0.0006 | -0.0001 | -0.0049 | -0.0248 | -0.0311 | -360.3435 | 17.6143 | -360.7989 | 17.8976 | -361.1066 | 18.0721 | -361.202 | 17.5588 | -353.2845 | 18.643 | -353.3245 | 16.678
11:26 | 358 | 17.7962 | 187.9805 | 427.633 | 431.9855 | -20.0422 | -48.01 | 0.1852 | -0.8529 | -8.2311 | -8.2743 | -3.6018 | -4.4273 | 1.2019 | -5.2704 | 0.5612 | 0.5794 | 0.9696 | 0.6776 | -133.0086 | -8.1379 | -1.8624 | -2.9194 | -10.8757 | -9.5061 | -1.7391 |  | -5.386 | -4.8019 | 4.0606 | 3.3685 | 3.3495 | 0.8524 | 10.3612 | 13.6955 | 14.2369 | 10.6292 | -0.0001 | -0.0029 | 0.0007 | 0.0035 | 0.0008 | -0.0009 | 0.012 | -0.0063 | -0.001 | -360.3527 | 17.6102 | -360.7589 | 17.8812 | -361.0574 | 18.0455 | -361.0789 | 17.5342 | -353.2445 | 18.6758 | -353.3152 | 16.7088
11:26 | 359 | 17.8238 | 188.1983 | 428.1438 | 432.5782 | -20.0403 | -47.8805 | 0.213 | -0.7828 | -8.1446 | -8.0965 | -3.6588 | -4.3438 | 1.168 | -5.3588 | 0.5632 | 0.5754 | 0.9717 | 0.6789 | -133.0232 | -8.276 | -1.8701 | -2.8876 | -10.8988 | -9.6428 | -1.7533 |  | -5.4445 | -4.897 | 4.0653 | 3.3659 | 3.3485 | 0.8554 | 10.4084 | 13.7375 | 14.2818 | 10.6348 | -0.0003 | -0.0028 | 0.0009 | 0.004 | 0 | -0.0005 | 0.0016 | -0.0114 | 0.0007 | -360.3158 | 17.5958 | -360.7866 | 17.8894 | -361.0881 | 18.0516 | -361.1035 | 17.5445 | -353.2383 | 18.7045 | -353.2722 | 16.7642
11:26 | 360 | 17.8415 | 188.3224 | 428.5113 | 432.9622 | -20.1489 | -48.0534 | 0.0869 | -0.8304 | -8.2982 | -8.168 | -3.643 | -4.3763 | 1.0999 | -5.3541 | 0.563 | 0.5764 | 0.9755 | 0.6802 | -132.9943 | -8.3218 | -1.8389 | -2.982 | -10.9276 | -9.6053 | -1.7905 |  | -5.4621 | -4.8548 | 4.0678 | 3.367 | 3.348 | 0.8614 | 10.4005 | 13.7292 | 14.2944 | 10.6566 | -0.0003 | -0.0026 | 0.0003 | 0.0035 | 0.0003 | -0.0009 | -0.0023 | -0.0018 | -0.0252 | -360.325 | 17.6081 | -360.762 | 17.9038 | -361.0851 | 18.0947 | -361.122 | 17.5588 | -353.2229 | 18.721 | -353.2414 | 16.7786
11:26 | 361 | 17.8297 | 188.3994 | 428.751 | 433.1623 | -20.1505 | -48.0214 | 0.1074 | -0.7854 | -8.2435 | -8.128 | -3.6336 | -4.3042 | 1.1825 | -5.3166 | 0.564 | 0.5773 | 0.9704 | 0.6818 | -133.0357 | -8.3396 | -1.9054 | -2.9368 | -10.9001 | -9.5805 | -1.7333 |  | -5.3876 | -4.9214 | 4.0691 | 3.3663 | 3.3474 | 0.8624 | 10.397 | 13.72 | 14.2856 | 10.6876 | 0.0001 | -0.0029 | 0.0005 | 0.0039 | 0.0004 | -0.0005 | 0.0074 | -0.0057 | -0.0053 | -360.2819 | 17.5814 | -360.6881 | 17.8812 | -361.0666 | 18.0886 | -361.1528 | 17.5691 | -353.1645 | 18.6963 | -353.1429 | 16.7519
11:26 | 362 | 17.804 | 188.6388 | 429.1146 | 433.4132 | -20.103 | -47.9818 | 0.1362 | -0.7393 | -8.2229 | -8.1345 | -3.6115 | -4.3651 | 1.1188 | -5.3953 | 0.5657 | 0.5755 | 0.9686 | 0.6819 | -133.015 | -8.2916 | -1.8228 | -3.107 | -10.9275 | -9.6229 | -1.7342 |  | -5.443 | -4.8782 | 4.0694 | 3.3681 | 3.3475 | 0.8642 | 10.4063 | 13.7465 | 14.3002 | 10.6854 | -0.0001 | -0.0027 | 0.0003 | 0.0033 | 0.0004 | -0.0009 | 0.0129 | 0.0064 | 0.0082 | -360.2388 | 17.5978 | -360.6912 | 17.9058 | -361.0512 | 18.0988 | -361.1312 | 17.5732 | -353.1891 | 18.7066 | -353.1829 | 16.793
11:26 | 363 | 17.7842 | 188.7763 | 429.1878 | 433.5586 | -20.1919 | -47.9579 | 0.0894 | -0.8307 | -8.2103 | -8.1489 | -3.6468 | -4.3912 | 1.144 | -5.4316 | 0.5653 | 0.5788 | 0.972 | 0.6826 | -132.9454 | -8.2705 | -1.8291 | -2.9253 | -10.9915 | -9.6508 | -1.7511 |  | -5.4799 | -4.7669 | 4.0685 | 3.3656 | 3.3482 | 0.8659 | 10.4133 | 13.7591 | 14.2948 | 10.7331 | -0.0005 | -0.0029 | 0.0002 | 0.0029 | 0.0007 | -0.0007 | 0.0059 | -0.0074 | -0.0017 | -360.2758 | 17.6574 | -360.762 | 17.9264 | -361.1004 | 18.0865 | -361.1035 | 17.5814 | -353.2106 | 18.7436 | -353.2106 | 16.7848
11:26 | 364 | 17.8581 | 188.7787 | 429.4476 | 433.8443 | -20.1073 | -47.9031 | 0.2787 | -0.8058 | -8.2952 | -8.1428 | -3.6937 | -4.4414 | 1.0953 | -5.4069 | 0.566 | 0.5791 | 0.9737 | 0.683 | -132.972 | -8.2522 | -1.8629 | -3.0052 | -11.0055 | -9.653 | -1.8591 |  | -5.3896 | -4.8347 | 4.07 | 3.3671 | 3.3499 | 0.866 | 10.4203 | 13.7313 | 14.3009 | 10.7577 | -0.0004 | -0.003 | 0.0003 | 0.0032 | 0 | -0.001 | -0.0006 | -0.0102 | -0.0145 | -360.2819 | 17.6677 | -360.7466 | 17.9325 | -361.0328 | 18.0598 | -361.0728 | 17.5465 | -353.1552 | 18.7579 | -353.2106 | 16.7889
11:26 | 365 | 17.9214 | 188.9292 | 429.5574 | 434.0028 | -19.9948 | -47.8235 | 0.2197 | -0.8292 | -8.3065 | -8.2078 | -3.7547 | -4.3672 | 1.1983 | -5.2682 | 0.5666 | 0.5806 | 0.9719 | 0.6836 | -133.0002 | -8.1481 | -1.8934 | -2.9212 | -10.8629 | -9.5777 | -1.7548 |  | -5.4784 | -4.9292 | 4.0702 | 3.3646 | 3.3443 | 0.8676 | 10.4363 | 13.7594 | 14.2852 | 10.7092 | 0 | -0.0028 | 0.001 | 0.0037 | 0.0007 | -0.0009 | 0.0144 | -0.0154 | 0.0157 | -360.2819 | 17.6738 | -360.7497 | 17.9469 | -361.0635 | 18.0763 | -361.0789 | 17.5773 | -353.1952 | 18.7538 | -353.2383 | 16.793
11:26 | 366 | 17.8964 | 189.1137 | 429.7497 | 434.2051 | -19.9965 | -47.8584 | 0.1496 | -0.8495 | -8.2799 | -8.1421 | -3.7165 | -4.4244 | 1.151 | -5.3432 | 0.5681 | 0.5805 | 0.9703 | 0.6835 | -132.9499 | -8.2381 | -1.8261 | -2.9885 | -10.9732 | -9.6446 | -1.7857 |  | -5.428 | -4.865 | 4.0696 | 3.3674 | 3.3459 | 0.8699 | 10.4179 | 13.7464 | 14.3166 | 10.7321 | 0.0001 | -0.0034 | 0.0007 | 0.0034 | 0.0005 | -0.0002 | 0.0057 | -0.005 | -0.0027 | -360.2388 | 17.6718 | -360.7158 | 17.9551 | -361.0635 | 18.1091 | -361.1189 | 17.5712 | -353.146 | 18.7333 | -353.186 | 16.8012
11:26 | 367 | 17.8415 | 189.0395 | 429.8028 | 434.3218 | -20.0271 | -47.8463 | 0.223 | -0.8516 | -8.3207 | -8.2698 | -3.7808 | -4.4147 | 1.1333 | -5.3032 | 0.567 | 0.5822 | 0.9733 | 0.6835 | -133.0373 | -8.2708 | -1.9098 | -2.9261 | -10.9098 | -9.5331 | -1.7292 |  | -5.4908 | -4.9317 | 4.0698 | 3.3718 | 3.346 | 0.8695 | 10.4051 | 13.7339 | 14.3057 | 10.7533 | -0.0005 | -0.0031 | 0.0011 | 0.0043 | 0.0006 | -0.001 | 0.021 | -0.0094 | 0.0133 | -360.1835 | 17.6471 | -360.6758 | 17.9284 | -361.0358 | 18.1255 | -361.1158 | 17.5671 | -353.1152 | 18.7066 | -353.1398 | 16.7724
11:26 | 368 | 17.9545 | 189.0799 | 429.9958 | 434.4411 | -20.0406 | -47.9395 | 0.2645 | -0.8182 | -8.2911 | -8.3069 | -3.7086 | -4.4362 | 1.1516 | -5.2651 | 0.5677 | 0.5829 | 0.9734 | 0.683 | -133.0672 | -8.2453 | -1.8304 | -2.9594 | -10.9675 | -9.5767 | -1.7801 |  | -5.488 | -4.8721 | 4.0709 | 3.3727 | 3.3511 | 0.8752 | 10.4098 | 13.7326 | 14.3033 | 10.8161 | -0.0004 | -0.0027 | 0.0007 | 0.0038 | 0.0003 | -0.0005 | 0.0078 | -0.0161 | -0.0071 | -360.2419 | 17.6738 | -360.7127 | 17.9695 | -361.0574 | 18.1317 | -361.1435 | 17.5876 | -353.1583 | 18.7271 | -353.1398 | 16.8012
11:26 | 369 | 17.8515 | 189.0875 | 430.0575 | 434.5738 | -20.0191 | -47.9024 | 0.1916 | -0.835 | -8.3046 | -8.2705 | -3.6672 | -4.5205 | 1.1789 | -5.2102 | 0.567 | 0.582 | 0.9679 | 0.6831 | -133.0899 | -8.2886 | -1.8313 | -2.8346 | -10.876 | -9.5787 | -1.7794 |  | -5.4373 | -4.96 | 4.0713 | 3.372 | 3.3493 | 0.8825 | 10.4409 | 13.7293 | 14.3649 | 10.8295 | -0.0004 | -0.003 | 0.0004 | 0.0039 | 0.0012 | -0.0005 | 0.0113 | -0.0098 | -0.0313 | -360.1835 | 17.6964 | -360.7004 | 17.9736 | -361.0328 | 18.1029 | -361.1097 | 17.5671 | -353.1522 | 18.7333 | -353.1614 | 16.795
11:26 | 370 | 17.8073 | 189.1177 | 430.1459 | 434.6854 | -20.0697 | -47.8938 | 0.2313 | -0.864 | -8.3825 | -8.2627 | -3.6432 | -4.4266 | 1.0816 | -5.3661 | 0.569 | 0.5876 | 0.9712 | 0.6848 | -133.0089 | -8.3086 | -1.8425 | -2.8913 | -10.8258 | -9.6074 | -1.7007 |  | -5.4187 | -4.9125 | 4.072 | 3.3693 | 3.3462 | 0.8839 | 10.4329 | 13.8021 | 14.3159 | 10.8157 | -0.0002 | -0.0032 | 0.0007 | 0.0038 | 0.0007 | -0.0004 | 0.0142 | -0.0036 | -0.0219 | -360.2358 | 17.7272 | -360.7435 | 17.9777 | -361.0451 | 18.0865 | -361.042 | 17.5506 | -353.1306 | 18.7641 | -353.1891 | 16.7848
11:26 | 371 | 17.7957 | 189.1795 | 430.3074 | 434.8656 | -20.1609 | -47.9674 | 0.2039 | -0.8079 | -8.4258 | -8.3351 | -3.6254 | -4.4195 | 1.1318 | -5.3516 | 0.5691 | 0.5824 | 0.9709 | 0.6834 | -133.0545 | -8.3934 | -1.7821 | -2.8498 | -10.8212 | -9.6231 | -1.6969 |  | -5.4152 | -4.9207 | 4.0727 | 3.3715 | 3.3445 | 0.883 | 10.4294 | 13.7697 | 14.3244 | 10.8237 | -0.0004 | -0.0033 | 0.0003 | 0.0031 | 0.0008 | -0.0003 | 0.0153 | 0.0001 | -0.0037 | -360.2388 | 17.7395 | -360.7743 | 18.0208 | -361.0512 | 18.0886 | -361.0297 | 17.565 | -353.1583 | 18.7682 | -353.2045 | 16.8053
11:26 | 372 | 17.8479 | 189.288 | 430.3681 | 434.9952 | -20.1171 | -48.0023 | 0.2026 | -0.8203 | -8.4462 | -8.3925 | -3.6005 | -4.3932 | 1.1592 | -5.2775 | 0.5698 | 0.5848 | 0.9714 | 0.6841 | -133.1045 | -8.32 | -1.8793 | -2.8041 | -10.8606 | -9.6916 | -1.7776 |  | -5.4525 | -4.9619 | 4.0739 | 3.3726 | 3.3483 | 0.8837 | 10.4365 | 13.7648 | 14.34 | 10.7971 | -0.0007 | -0.0028 | 0.0004 | 0.0035 | 0.0006 | -0.001 | 0.0065 | -0.0007 | -0.0247 | -360.2019 | 17.7067 | -360.7189 | 18.0167 | -361.0235 | 18.1009 | -361.0912 | 17.5506 | -353.1337 | 18.7477 | -353.1245 | 16.7971
11:26 | 373 | 17.9752 | 189.334 | 430.6288 | 435.0774 | -20.1739 | -48.0917 | 0.2536 | -0.7505 | -8.4481 | -8.3712 | -3.566 | -4.4077 | 1.0768 | -5.3787 | 0.57 | 0.5872 | 0.9697 | 0.683 | -133.1732 | -8.3395 | -1.926 | -2.8872 | -10.887 | -9.7301 | -1.7576 |  | -5.4232 | -5.035 | 4.0739 | 3.3712 | 3.3516 | 0.8851 | 10.4629 | 13.8148 | 14.2941 | 10.7937 | -0.0005 | -0.003 | 0.0012 | 0.004 | 0.0002 | -0.0001 | 0.0145 | -0.0063 | -0.0144 | -360.1619 | 17.7026 | -360.6943 | 18.0003 | -361.0235 | 18.1296 | -361.0912 | 17.5588 | -353.1029 | 18.7169 | -353.106 | 16.7909
11:26 | 374 | 17.8782 | 189.3429 | 430.6958 | 435.1596 | -20.2203 | -48.0122 | 0.3376 | -0.7111 | -8.3997 | -8.4408 | -3.6333 | -4.4363 | 1.0569 | -5.3159 | 0.5701 | 0.5829 | 0.973 | 0.6842 | -133.168 | -8.4017 | -1.8137 | -2.9502 | -10.8683 | -9.6259 | -1.7319 |  | -5.4099 | -4.9907 | 4.076 | 3.3733 | 3.349 | 0.8858 | 10.4351 | 13.8161 | 14.337 | 10.8291 | 0.0003 | -0.0031 | 0.0008 | 0.0038 | 0.0009 | -0.0008 | 0.0076 | -0.002 | 0.003 | -360.205 | 17.719 | -360.7004 | 18.027 | -361.0481 | 18.144 | -361.1343 | 17.5732 | -353.1306 | 18.7395 | -353.1091 | 16.8032
11:26 | 375 | 17.8618 | 189.4156 | 430.9534 | 435.2196 | -20.3425 | -48.0962 | 0.1858 | -0.6899 | -8.3344 | -8.3302 | -3.6329 | -4.3895 | 1.1675 | -5.1774 | 0.5706 | 0.5891 | 0.9724 | 0.6838 | -133.1674 | -8.3682 | -1.8489 | -2.8603 | -10.9004 | -9.6529 | -1.7236 |  | -5.3673 | -4.9414 | 4.0742 | 3.3736 | 3.3496 | 0.8858 | 10.4433 | 13.8009 | 14.3492 | 10.8204 | 0.0002 | -0.003 | 0.0003 | 0.0036 | 0.0004 | -0.0001 | 0.0033 | 0.0111 | -0.0184 | -360.1958 | 17.7375 | -360.6943 | 18.0167 | -361.0143 | 18.1112 | -361.0758 | 17.5568 | -353.106 | 18.7456 | -353.1121 | 16.7909
11:26 | 376 | 17.8585 | 189.4084 | 430.8847 | 435.2965 | -20.3097 | -48.0971 | 0.1897 | -0.7328 | -8.2913 | -8.3869 | -3.6227 | -4.4122 | 1.2576 | -5.2746 | 0.5714 | 0.585 | 0.9724 | 0.6842 | -133.2129 | -8.3528 | -1.9881 | -2.859 | -10.8854 | -9.6467 | -1.7578 |  | -5.4085 | -5.0226 | 4.075 | 3.3704 | 3.3511 | 0.8864 | 10.4628 | 13.8324 | 14.354 | 10.8103 | -0.0004 | -0.0029 | 0.0004 | 0.0037 | 0.0007 | -0.0005 | 0.0019 | -0.0033 | -0.0112 | -360.2111 | 17.7683 | -360.7373 | 18.0311 | -360.9989 | 18.0824 | -360.9958 | 17.5383 | -353.1306 | 18.7785 | -353.1398 | 16.795
11:26 | 377 | 17.8145 | 189.524 | 430.9516 | 435.4444 | -20.2649 | -48.1109 | 0.2153 | -0.7373 | -8.2914 | -8.4975 | -3.6765 | -4.4408 | 1.1814 | -5.1626 | 0.5696 | 0.5858 | 0.9701 | 0.6842 | -133.1876 | -8.4097 | -1.9537 | -2.7612 | -10.8593 | -9.6809 | -1.7446 |  | -5.4798 | -4.9943 | 4.0751 | 3.3722 | 3.3563 | 0.8871 | 10.442 | 13.8751 | 14.3731 | 10.8648 | -0.0003 | -0.0025 | 0.0002 | 0.0032 | 0.0003 | -0.0011 | 0.0003 | 0.0035 | -0.027 | -360.1865 | 17.7724 | -360.7589 | 18.0557 | -361.0635 | 18.1009 | -361.0635 | 17.5609 | -353.1121 | 18.7785 | -353.1952 | 16.8197
11:26 | 378 | 17.8596 | 189.653 | 431.1347 | 435.5564 | -20.2809 | -48.225 | 0.2289 | -0.6006 | -8.3068 | -8.4044 | -3.6473 | -4.4499 | 1.1144 | -5.1751 | 0.5702 | 0.5846 | 0.9724 | 0.6833 | -133.2505 | -8.4831 | -1.9385 | -2.7054 | -10.8305 | -9.6497 | -1.6863 |  | -5.4975 | -4.9647 | 4.0752 | 3.3708 | 3.3541 | 0.8875 | 10.4375 | 13.8298 | 14.3492 | 10.8262 | -0.0003 | -0.0031 | 0.0007 | 0.0039 | 0.0005 | -0.0006 | 0.0035 | -0.0087 | -0.0064 | -360.1681 | 17.758 | -360.7066 | 18.0434 | -361.0697 | 18.1194 | -361.0574 | 17.5609 | -353.0845 | 18.7538 | -353.1091 | 16.8074
11:26 | 379 | 17.9737 | 189.7513 | 431.1642 | 435.6417 | -20.3355 | -48.2532 | 0.2517 | -0.7004 | -8.3581 | -8.3818 | -3.7297 | -4.4711 | 1.1317 | -5.2633 | 0.5711 | 0.5871 | 0.9767 | 0.6852 | -133.3173 | -8.4551 | -1.9857 | -2.8214 | -10.881 | -9.7039 | -1.724 |  | -5.4209 | -5.0277 | 4.0771 | 3.3697 | 3.353 | 0.8876 | 10.4478 | 13.8346 | 14.3789 | 10.8244 | 0.0002 | -0.0028 | 0.0007 | 0.0039 | 0.001 | -0.0006 | 0.0001 | 0 | -0.0224 | -360.1804 | 17.7354 | -360.645 | 18.0106 | -360.9774 | 18.1317 | -361.1035 | 17.5629 | -353.0968 | 18.7292 | -353.0691 | 16.7786
11:26 | 380 | 17.9547 | 189.8319 | 431.265 | 435.731 | -20.3439 | -48.243 | 0.2491 | -0.7027 | -8.3162 | -8.4711 | -3.714 | -4.4066 | 1.1822 | -5.3609 | 0.573 | 0.584 | 0.9714 | 0.6855 | -133.2371 | -8.4115 | -1.8883 | -2.8252 | -11.0103 | -9.7928 | -1.8094 |  | -5.3628 | -5.002 | 4.0771 | 3.372 | 3.3511 | 0.8882 | 10.4259 | 13.8471 | 14.3956 | 10.8262 | -0.0001 | -0.003 | 0.0006 | 0.0035 | 0.0005 | -0.0005 | 0.0048 | -0.0145 | -0.0079 | -360.1435 | 17.7539 | -360.6543 | 18.0516 | -361.002 | 18.1194 | -361.1035 | 17.5732 | -353.1214 | 18.7374 | -353.1121 | 16.7991
11:26 | 381 | 17.8821 | 189.8298 | 431.2782 | 435.736 | -20.2655 | -48.2447 | 0.2208 | -0.678 | -8.3041 | -8.3543 | -3.665 | -4.3351 | 1.2388 | -5.3249 | 0.5719 | 0.5854 | 0.9733 | 0.6859 | -133.2823 | -8.5224 | -1.9864 | -2.9161 | -11.1504 | -9.7577 | -1.9413 |  | -5.4343 | -4.9896 | 4.0775 | 3.3746 | 3.3547 | 0.8884 | 10.4329 | 13.8482 | 14.4132 | 10.8219 | -0.0004 | -0.0029 | 0.0009 | 0.0039 | 0.001 | -0.0006 | 0.0071 | -0.0132 | -0.0034 | -360.1896 | 17.7991 | -360.722 | 18.0619 | -361.0051 | 18.1091 | -361.082 | 17.5671 | -353.1121 | 18.7764 | -353.1152 | 16.8094
11:26 | 382 | 17.9127 | 189.9895 | 431.2976 | 435.7323 | -20.2838 | -48.3866 | 0.1709 | -0.7329 | -8.3382 | -8.4573 | -3.6587 | -4.382 | 1.1624 | -5.2882 | 0.5717 | 0.5866 | 0.9715 | 0.6861 | -133.1435 | -8.5101 | -1.842 | -2.8321 | -11.0701 | -9.6871 | -1.8533 |  | -5.4083 | -4.9898 | 4.0765 | 3.3729 | 3.3556 | 0.8884 | 10.4572 | 13.8726 | 14.433 | 10.8168 | -0.0001 | -0.0028 | 0.0006 | 0.0033 | 0.0003 | -0.0002 | 0.01 | -0.0159 | -0.0082 | -360.1465 | 17.8011 | -360.7343 | 18.066 | -361.0081 | 18.0906 | -361.0204 | 17.5301 | -353.066 | 18.7723 | -353.1645 | 16.8238
11:26 | 383 | 17.8436 | 190.0147 | 431.387 | 435.7239 | -20.2864 | -48.2825 | 0.1809 | -0.7141 | -8.3542 | -8.4965 | -3.6608 | -4.3677 | 1.2246 | -5.3143 | 0.5731 | 0.5916 | 0.9733 | 0.6866 | -133.1465 | -8.6118 | -1.8904 | -2.809 | -11.0159 | -9.6652 | -1.8611 |  | -5.4218 | -4.9398 | 4.0764 | 3.3737 | 3.3585 | 0.8909 | 10.4422 | 13.898 | 14.4058 | 10.802 | 0.0001 | -0.0033 | 0.0007 | 0.0036 | 0.0011 | -0.0004 | 0.0073 | -0.0042 | -0.0084 | -360.1588 | 17.7765 | -360.7035 | 18.066 | -361.0143 | 18.0988 | -361.042 | 17.5527 | -353.0875 | 18.7661 | -353.1245 | 16.8279
11:26 | 384 | 17.9063 | 190.1375 | 431.3956 | 435.7724 | -20.2883 | -48.2889 | 0.1567 | -0.6896 | -8.3727 | -8.4058 | -3.5456 | -4.3937 | 1.1931 | -5.2459 | 0.5731 | 0.5902 | 0.9699 | 0.6865 | -133.152 | -8.5246 | -1.8896 | -2.7463 | -10.9916 | -9.6572 | -1.8287 |  | -5.4274 | -4.9779 | 4.0776 | 3.3728 | 3.3519 | 0.8919 | 10.4572 | 13.8668 | 14.4793 | 10.811 | 0.0003 | -0.0028 | 0.0005 | 0.0035 | 0.0001 | -0.0007 | 0.0086 | -0.0066 | 0.0137 | -360.1835 | 17.7806 | -360.7035 | 18.0701 | -361.0328 | 18.142 | -361.082 | 17.5712 | -353.0691 | 18.7559 | -353.1121 | 16.8217
11:26 | 385 | 17.9592 | 190.2484 | 431.501 | 435.8937 | -20.3783 | -48.4152 | 0.0743 | -0.6072 | -8.3002 | -8.5079 | -3.6722 | -4.3056 | 1.1363 | -5.2643 | 0.5723 | 0.5938 | 0.9766 | 0.6859 | -133.2062 | -8.5041 | -1.8196 | -2.7967 | -10.9739 | -9.6268 | -1.764 |  | -5.3511 | -4.9558 | 4.0763 | 3.3731 | 3.3535 | 0.8921 | 10.4538 | 13.9037 | 14.4915 | 10.8255 | -0.0003 | -0.003 | 0 | 0.0036 | 0.0005 | -0.001 | 0.0099 | -0.0157 | -0.0044 | -360.1958 | 17.7621 | -360.6573 | 18.0619 | -361.0358 | 18.1337 | -361.1128 | 17.5773 | -353.0814 | 18.7395 | -353.0537 | 16.7991
11:26 | 386 | 17.9947 | 190.2062 | 431.6676 | 436.1817 | -20.335 | -48.3884 | 0.188 | -0.6622 | -8.3051 | -8.5523 | -3.7757 | -4.4002 | 1.1263 | -5.2625 | 0.5733 | 0.591 | 0.9738 | 0.6861 | -133.2887 | -8.5667 | -1.8246 | -2.7579 | -10.9474 | -9.6603 | -1.7877 |  | -5.3508 | -4.8405 | 4.0771 | 3.3702 | 3.3567 | 0.8924 | 10.4698 | 13.9202 | 14.4933 | 10.8348 | -0.0009 | -0.0028 | 0.0006 | 0.004 | 0.0009 | -0.0003 | 0.0096 | -0.0157 | -0.0144 | -360.1496 | 17.7744 | -360.6758 | 18.0639 | -360.9958 | 18.1132 | -361.0666 | 17.5671 | -353.0568 | 18.7477 | -353.0383 | 16.8176
11:26 | 387 | 17.9699 | 190.4033 | 431.7642 | 436.2591 | -20.3702 | -48.4087 | 0.188 | -0.6725 | -8.3589 | -8.4517 | -3.8139 | -4.3807 | 1.1434 | -5.2262 | 0.5731 | 0.587 | 0.9704 | 0.6867 | -133.2975 | -8.5601 | -1.8775 | -2.8286 | -10.9452 | -9.7169 | -1.7615 |  | -5.382 | -4.9579 | 4.0772 | 3.3747 | 3.3564 | 0.8937 | 10.4375 | 13.8818 | 14.4766 | 10.8089 | 0 | -0.0029 | 0.0005 | 0.004 | 0.0007 | -0.0008 | 0.0234 | -0.0147 | -0.0045 | -360.1404 | 17.8175 | -360.7373 | 18.0804 | -361.002 | 18.0988 | -361.0358 | 17.5609 | -353.0937 | 18.7846 | -353.1275 | 16.8115
11:26 | 388 | 17.7767 | 190.3957 | 431.7604 | 436.2805 | -20.3491 | -48.3565 | 0.2487 | -0.6704 | -8.3759 | -8.5164 | -3.7724 | -4.5073 | 1.0637 | -5.3622 | 0.5745 | 0.5896 | 0.9715 | 0.6864 | -133.2041 | -8.4785 | -1.7444 | -2.8022 | -11.0096 | -9.6749 | -1.7789 |  | -5.4226 | -4.9713 | 4.0772 | 3.3731 | 3.358 | 0.8939 | 10.4745 | 13.8958 | 14.4735 | 10.8226 | -0.0002 | -0.0031 | 0.0006 | 0.0035 | 0.0008 | -0.0008 | 0.0179 | 0.0038 | 0.0065 | -360.1527 | 17.8258 | -360.7466 | 18.1009 | -361.0235 | 18.1029 | -361.0666 | 17.5609 | -353.1029 | 18.7826 | -353.1522 | 16.8361
11:26 | 389 | 17.9268 | 190.4445 | 431.8147 | 436.4274 | -20.4097 | -48.3327 | 0.1974 | -0.7032 | -8.3784 | -8.4872 | -3.739 | -4.4556 | 1.1403 | -5.3023 | 0.5733 | 0.5902 | 0.9717 | 0.6874 | -133.0929 | -8.4795 | -1.7664 | -2.878 | -11.0305 | -9.7519 | -1.8727 |  | -5.4217 | -4.9675 | 4.0771 | 3.3721 | 3.3567 | 0.8929 | 10.4686 | 13.8844 | 14.464 | 10.8103 | -0.0001 | -0.0028 | 0.0009 | 0.0039 | 0.0001 | -0.0006 | 0.0047 | -0.0139 | -0.0206 | -360.1435 | 17.8011 | -360.6881 | 18.0886 | -360.9835 | 18.1091 | -361.0697 | 17.5547 | -353.0691 | 18.7518 | -353.0814 | 16.8197
11:26 | 390 | 17.9758 | 190.4812 | 431.8451 | 436.4698 | -20.3086 | -48.3151 | 0.2468 | -0.7607 | -8.4485 | -8.4359 | -3.8382 | -4.4232 | 1.1659 | -5.3524 | 0.5737 | 0.591 | 0.9726 | 0.687 | -133.1505 | -8.5397 | -1.7565 | -2.7709 | -10.9821 | -9.7042 | -1.7479 |  | -5.3592 | -4.928 | 4.077 | 3.3757 | 3.3581 | 0.8948 | 10.4596 | 13.9037 | 14.4915 | 10.8082 | -0.0006 | -0.0028 | 0.0007 | 0.0035 | 0.0007 | -0.0011 | 0.005 | -0.0177 | -0.0144 | -360.0973 | 17.7744 | -360.6327 | 18.0639 | -360.9897 | 18.1358 | -361.0728 | 17.565 | -353.0414 | 18.7374 | -353.0383 | 16.8053
11:26 | 391 | 17.9601 | 190.5627 | 431.9568 | 436.5175 | -20.3201 | -48.3743 | 0.2021 | -0.7358 | -8.3979 | -8.4195 | -3.8392 | -4.4539 | 1.1234 | -5.4063 | 0.5737 | 0.5911 | 0.973 | 0.6864 | -133.1592 | -8.4488 | -1.7451 | -2.9002 | -10.97 | -9.7055 | -1.8386 |  | -5.4554 | -4.9354 | 4.0778 | 3.3724 | 3.3581 | 0.8945 | 10.4629 | 13.8842 | 14.5025 | 10.8168 | 0 | -0.0028 | 0.0005 | 0.004 | 0.0003 | -0.0005 | 0.0111 | -0.0173 | 0.0077 | -360.1158 | 17.7826 | -360.6666 | 18.0947 | -360.9958 | 18.1337 | -361.0974 | 17.5691 | -353.0691 | 18.7436 | -353.0568 | 16.8238
11:26 | 392 | 17.9794 | 190.5448 | 431.9999 | 436.5684 | -20.3592 | -48.354 | 0.2109 | -0.7967 | -8.4572 | -8.594 | -3.8123 | -4.4144 | 1.193 | -5.4628 | 0.5742 | 0.5926 | 0.972 | 0.6863 | -133.1692 | -8.4612 | -1.7596 | -2.9813 | -11.0178 | -9.7528 | -1.9271 |  | -5.4309 | -4.9266 | 4.0799 | 3.3727 | 3.3558 | 0.8949 | 10.4653 | 13.8633 | 14.4463 | 10.8194 | 0.0001 | -0.0033 | 0.0005 | 0.0036 | 0.0007 | -0.0009 | 0.0071 | -0.0126 | -0.0175 | -360.1681 | 17.8196 | -360.7096 | 18.0927 | -360.9989 | 18.1112 | -361.0543 | 17.5712 | -353.0783 | 18.7703 | -353.1029 | 16.8197
11:26 | 393 | 17.9709 | 190.6168 | 432.0542 | 436.6724 | -20.3398 | -48.3403 | 0.2063 | -0.7957 | -8.3862 | -8.5444 | -3.7462 | -4.3146 | 1.2153 | -5.5263 | 0.5732 | 0.5931 | 0.971 | 0.6856 | -133.1127 | -8.5214 | -1.7993 | -2.93 | -10.9332 | -9.7518 | -1.8185 |  | -5.4652 | -4.9557 | 4.079 | 3.373 | 3.3572 | 0.8964 | 10.4377 | 13.8988 | 14.4445 | 10.787 | -0.0002 | -0.003 | 0.0005 | 0.0034 | 0.0006 | -0.0007 | -0.0024 | -0.0133 | -0.0016 | -360.1558 | 17.8237 | -360.7497 | 18.0906 | -360.9897 | 18.0968 | -361.0112 | 17.5424 | -353.0783 | 18.7846 | -353.1214 | 16.8279
11:26 | 394 | 17.9941 | 190.5692 | 432.0121 | 436.7059 | -20.4459 | -48.4717 | 0.1645 | -0.7287 | -8.3941 | -8.6204 | -3.8751 | -4.4233 | 1.2747 | -5.4575 | 0.5733 | 0.5936 | 0.9698 | 0.6856 | -133.1829 | -8.5463 | -1.7981 | -2.9752 | -10.9136 | -9.8171 | -1.8155 |  | -5.4956 | -4.9845 | 4.0793 | 3.376 | 3.3527 | 0.8976 | 10.4502 | 13.8947 | 14.4616 | 10.8038 | -0.0004 | -0.0028 | 0.0011 | 0.0044 | 0.0009 | -0.0003 | -0.0057 | -0.0036 | -0.0019 | -360.1281 | 17.8237 | -360.7066 | 18.0906 | -361.0081 | 18.0927 | -361.0235 | 17.5629 | -353.0906 | 18.7744 | -353.0937 | 16.8299
11:26 | 395 | 17.9529 | 190.5848 | 432.0623 | 436.8469 | -20.4404 | -48.4134 | 0.233 | -0.7308 | -8.4957 | -8.5925 | -3.7637 | -4.3535 | 1.3652 | -5.3754 | 0.5747 | 0.597 | 0.9695 | 0.686 | -133.2148 | -8.4889 | -1.8885 | -3.0066 | -10.9764 | -9.7817 | -1.8846 |  | -5.5031 | -5.0348 | 4.0788 | 3.3769 | 3.3569 | 0.8992 | 10.4562 | 13.9059 | 14.4643 | 10.8165 | -0.0009 | -0.0034 | 0.0008 | 0.004 | 0.0004 | -0.0006 | -0.0051 | -0.0059 | 0.005 | -360.1034 | 17.8032 | -360.7035 | 18.0906 | -360.9989 | 18.1399 | -361.0974 | 17.565 | -353.0537 | 18.762 | -353.0721 | 16.834
11:26 | 396 | 17.9489 | 190.6433 | 432.1974 | 436.8232 | -20.4449 | -48.2437 | 0.3086 | -0.6463 | -8.4619 | -8.5958 | -3.8538 | -4.3907 | 1.3566 | -5.4092 | 0.5738 | 0.5967 | 0.9698 | 0.6868 | -133.1754 | -8.5263 | -1.7935 | -2.9357 | -10.8952 | -9.8263 | -1.8016 |  | -5.4022 | -4.9492 | 4.0775 | 3.3755 | 3.3572 | 0.8998 | 10.4894 | 13.9285 | 14.5144 | 10.8193 | 0 | -0.003 | 0.0011 | 0.0037 | 0.0005 | -0.0003 | 0.0073 | -0.0009 | -0.0115 | -360.1065 | 17.7785 | -360.6604 | 18.0947 | -361.0204 | 18.1379 | -361.1189 | 17.5712 | -353.0229 | 18.7374 | -353.0537 | 16.8217
11:26 | 397 | 17.8887 | 190.7019 | 432.164 | 436.8224 | -20.3883 | -48.2698 | 0.278 | -0.6766 | -8.3105 | -8.6448 | -3.7268 | -4.297 | 1.38 | -5.362 | 0.5748 | 0.5965 | 0.9694 | 0.6871 | -133.3044 | -8.5609 | -1.8438 | -2.9626 | -10.9192 | -9.8071 | -1.959 |  | -5.3489 | -4.8608 | 4.0789 | 3.3726 | 3.3574 | 0.9006 | 10.4722 | 13.9282 | 14.4834 | 10.8374 | 0.0001 | -0.003 | 0.0009 | 0.0037 | 0.0007 | -0.001 | 0.0086 | -0.0119 | -0.0101 | -360.1219 | 17.797 | -360.6604 | 18.0845 | -361.002 | 18.1317 | -361.0512 | 17.565 | -353.0383 | 18.7415 | -353.026 | 16.8217
11:26 | 398 | 17.9357 | 190.7074 | 432.1228 | 436.8679 | -20.4357 | -48.284 | 0.2295 | -0.8217 | -8.4013 | -8.6678 | -3.7794 | -4.4303 | 1.3538 | -5.4395 | 0.5761 | 0.5947 | 0.9709 | 0.6865 | -133.2106 | -8.6889 | -1.7587 | -2.9252 | -10.8807 | -9.6748 | -1.8042 |  | -5.3787 | -4.9624 | 4.0792 | 3.3752 | 3.3576 | 0.9016 | 10.4872 | 13.9085 | 14.5096 | 10.8121 | -0.0005 | -0.0028 | 0.0008 | 0.0033 | 0 | -0.0005 | -0.0071 | 0.0064 | -0.0046 | -360.1404 | 17.8381 | -360.7066 | 18.0865 | -360.9712 | 18.0968 | -361.0143 | 17.5588 | -353.0629 | 18.7846 | -353.1029 | 16.8135
11:26 | 399 | 17.944 | 190.7586 | 432.2304 | 436.8879 | -20.3572 | -48.2229 | 0.3013 | -0.8085 | -8.3627 | -8.6745 | -3.786 | -4.3942 | 1.4224 | -5.4821 | 0.5746 | 0.5966 | 0.9701 | 0.6866 | -133.155 | -8.5199 | -1.7669 | -2.9319 | -10.9218 | -9.7209 | -1.7547 |  | -5.4206 | -4.9447 | 4.0774 | 3.3742 | 3.3571 | 0.9028 | 10.4755 | 13.8914 | 14.5175 | 10.8402 | 0 | -0.0026 | 0.0007 | 0.0036 | 0.0006 | -0.0006 | -0.0016 | -0.0113 | -0.0311 | -360.1373 | 17.8319 | -360.7373 | 18.0968 | -360.9989 | 18.0988 | -361.0451 | 17.5629 | -353.0752 | 18.7908 | -353.1245 | 16.8402
11:26 | 400 | 17.9583 | 190.7553 | 432.2225 | 436.9105 | -20.4419 | -48.2889 | 0.222 | -0.812 | -8.357 | -8.5882 | -3.7197 | -4.4215 | 1.3974 | -5.5193 | 0.5748 | 0.5976 | 0.9703 | 0.6868 | -133.1647 | -8.5883 | -1.7417 | -2.8899 | -10.9116 | -9.7017 | -1.7477 |  | -5.3734 | -4.8901 | 4.0769 | 3.3767 | 3.3562 | 0.9018 | 10.53 | 13.9224 | 14.4834 | 10.8316 | -0.0001 | -0.0031 | 0.0007 | 0.0038 | 0.0001 | -0.0007 | -0.0082 | -0.0086 | -0.0042 | -360.1465 | 17.8011 | -360.682 | 18.1009 | -361.0112 | 18.1173 | -361.0481 | 17.5609 | -353.0414 | 18.76 | -353.0568 | 16.832
11:26 | 401 | 17.9532 | 190.7179 | 432.2407 | 436.9333 | -20.4051 | -48.3303 | 0.2196 | -0.6752 | -8.3259 | -8.5947 | -3.7192 | -4.4126 | 1.4154 | -5.408 | 0.5746 | 0.5952 | 0.9684 | 0.6877 | -133.1885 | -8.5694 | -1.7949 | -2.9411 | -10.9469 | -9.7874 | -1.7346 |  | -5.4096 | -4.7591 | 4.0773 | 3.3743 | 3.356 | 0.904 | 10.4954 | 13.8703 | 14.4939 | 10.8031 | 0 | -0.0034 | 0.0008 | 0.0037 | 0.0009 | -0.0007 | 0.0047 | -0.0063 | -0.0226 | -360.0758 | 17.7765 | -360.6389 | 18.066 | -361.0143 | 18.144 | -361.0851 | 17.565 | -353.0198 | 18.7374 | -353.0168 | 16.8074
11:26 | 402 | 17.8421 | 190.7045 | 432.2921 | 436.9759 | -20.4127 | -48.3408 | 0.2994 | -0.6667 | -8.3124 | -8.5541 | -3.6267 | -4.3789 | 1.3953 | -5.4343 | 0.5745 | 0.5965 | 0.9707 | 0.6876 | -133.2103 | -8.5739 | -1.8779 | -2.9572 | -10.911 | -9.7368 | -1.8372 |  | -5.3697 | -4.8349 | 4.0762 | 3.3742 | 3.359 | 0.9044 | 10.456 | 13.8888 | 14.4722 | 10.8215 | -0.0002 | -0.0031 | 0.0008 | 0.0041 | 0.0008 | -0.0006 | -0.0078 | -0.0104 | -0.0069 | -360.0727 | 17.7806 | -360.6543 | 18.0865 | -361.0081 | 18.1276 | -361.0789 | 17.5691 | -353.0321 | 18.7374 | -353.0537 | 16.8217
11:26 | 403 | 17.9222 | 190.8174 | 432.3842 | 436.9867 | -20.379 | -48.2933 | 0.2105 | -0.6477 | -8.3014 | -8.6056 | -3.6376 | -4.4852 | 1.4219 | -5.4378 | 0.5745 | 0.5988 | 0.9692 | 0.6874 | -133.1607 | -8.5002 | -1.812 | -2.8221 | -10.8893 | -9.7687 | -1.8247 |  | -5.3856 | -4.7714 | 4.0774 | 3.3748 | 3.3596 | 0.9053 | 10.4643 | 13.9023 | 14.4776 | 10.8249 | -0.0005 | -0.0026 | 0.0003 | 0.0038 | 0.0002 | -0.0006 | 0.0148 | -0.0103 | -0.0028 | -360.1681 | 17.8175 | -360.7004 | 18.0968 | -361.0051 | 18.1071 | -361.0512 | 17.565 | -353.0814 | 18.7826 | -353.0568 | 16.8238
11:26 | 404 | 17.9023 | 190.8034 | 432.3911 | 437.0417 | -20.422 | -48.2871 | 0.2805 | -0.6201 | -8.2851 | -8.6941 | -3.6437 | -4.3855 | 1.3914 | -5.4106 | 0.5744 | 0.5974 | 0.97 | 0.6859 | -133.2552 | -8.5158 | -1.8587 | -2.8247 | -10.9406 | -9.8453 | -1.7857 |  | -5.3554 | -4.853 | 4.076 | 3.3751 | 3.3572 | 0.9067 | 10.4977 | 13.89 | 14.4909 | 10.8053 | -0.0001 | -0.0026 | 0.0002 | 0.0035 | 0.0012 | -0.0006 | 0.0182 | -0.0149 | 0.0006 | -360.1527 | 17.8299 | -360.7158 | 18.0947 | -360.9927 | 18.0886 | -360.9927 | 17.5527 | -353.0598 | 18.7928 | -353.1091 | 16.8299
11:26 | 405 | 17.9325 | 190.8259 | 432.3935 | 437.0626 | -20.5164 | -48.2376 | 0.197 | -0.563 | -8.3363 | -8.692 | -3.6726 | -4.4815 | 1.3782 | -5.4485 | 0.5768 | 0.5953 | 0.9715 | 0.6874 | -133.3604 | -8.576 | -1.8324 | -2.8181 | -10.8756 | -9.6424 | -1.7282 |  | -5.2922 | -4.7636 | 4.074 | 3.3712 | 3.3592 | 0.9067 | 10.493 | 13.9085 | 14.4923 | 10.841 | 0.0002 | -0.0029 | 0.001 | 0.0037 | 0.0006 | -0.0002 | 0.0088 | -0.0054 | -0.0149 | -360.1619 | 17.8093 | -360.6881 | 18.0968 | -360.9927 | 18.0988 | -361.0081 | 17.5609 | -353.0414 | 18.7764 | -353.0568 | 16.8238
11:26 | 406 | 17.8974 | 190.9086 | 432.389 | 437.0638 | -20.3779 | -48.1852 | 0.3652 | -0.5911 | -8.3622 | -8.5611 | -3.6272 | -4.4159 | 1.3896 | -5.4959 | 0.5741 | 0.5962 | 0.9677 | 0.6876 | -133.2624 | -8.64 | -1.8205 | -2.7712 | -10.9776 | -9.6977 | -1.7727 |  | -5.3567 | -4.8595 | 4.0751 | 3.3732 | 3.3534 | 0.9078 | 10.5069 | 13.8992 | 14.4997 | 10.8262 | -0.0002 | -0.0034 | 0.0006 | 0.0033 | 0.0008 | -0.0004 | 0.0204 | -0.0056 | -0.0005 | -360.0604 | 17.7806 | -360.6543 | 18.0865 | -361.0204 | 18.1235 | -361.0543 | 17.5506 | -353.0229 | 18.7518 | -353.0475 | 16.8299
11:26 | 407 | 17.978 | 190.9837 | 432.5239 | 437.2546 | -20.3946 | -48.1375 | 0.3843 | -0.5759 | -8.257 | -8.5083 | -3.6191 | -4.3783 | 1.3877 | -5.525 | 0.5755 | 0.5993 | 0.9713 | 0.6879 | -133.153 | -8.5608 | -1.9129 | -2.9259 | -11.0747 | -9.7547 | -1.8426 |  | -5.4234 | -4.9119 | 4.0756 | 3.3764 | 3.3564 | 0.907 | 10.4712 | 13.8862 | 14.4789 | 10.7971 | -0.0006 | -0.0028 | 0.0007 | 0.0037 | 0.0002 | -0.0005 | 0.0003 | -0.003 | -0.0178 | -360.0727 | 17.7683 | -360.6512 | 18.0865 | -361.0051 | 18.1522 | -361.1035 | 17.5691 | -353.0537 | 18.7436 | -353.0229 | 16.8279
11:27 | 408 | 17.9777 | 191.0033 | 432.6122 | 437.2523 | -20.3199 | -48.1307 | 0.4603 | -0.6573 | -8.2857 | -8.5405 | -3.6283 | -4.4171 | 1.4217 | -5.4326 | 0.5765 | 0.595 | 0.969 | 0.6881 | -133.1627 | -8.5206 | -1.8936 | -2.9383 | -10.9183 | -9.7794 | -1.802 |  | -5.3924 | -4.8728 | 4.0753 | 3.3766 | 3.3554 | 0.9079 | 10.5012 | 13.9281 | 14.4708 | 10.8089 | -0.0006 | -0.0027 | 0.0009 | 0.0036 | 0.001 | -0.0007 | 0.0024 | -0.0122 | -0.0102 | -360.1804 | 17.797 | -360.682 | 18.0804 | -361.0051 | 18.1071 | -361.0666 | 17.5629 | -353.0629 | 18.762 | -353.0352 | 16.8176
11:27 | 409 | 17.9648 | 190.9614 | 432.5333 | 437.257 | -20.348 | -48.2455 | 0.384 | -0.6875 | -8.3259 | -8.4875 | -3.7394 | -4.5412 | 1.3416 | -5.473 | 0.5761 | 0.5989 | 0.9615 | 0.6861 | -133.1963 | -8.6431 | -1.8742 | -2.9946 | -10.8743 | -9.7381 | -1.778 |  | -5.4433 | -4.8482 | 4.074 | 3.3752 | 3.3568 | 0.909 | 10.5162 | 13.9084 | 14.4854 | 10.801 | -0.0002 | -0.0029 | 0.0004 | 0.0038 | 0.0004 | -0.0004 | -0.0039 | 0.0045 | -0.0182 | -360.1404 | 17.8258 | -360.7127 | 18.0804 | -360.9866 | 18.0906 | -361.0204 | 17.5527 | -353.0445 | 18.7867 | -353.0629 | 16.8238
11:27 | 410 | 18.0055 | 191.003 | 432.631 | 437.2551 | -20.4291 | -48.2447 | 0.324 | -0.6752 | -8.3126 | -8.4687 | -3.682 | -4.4468 | 1.2818 | -5.4794 | 0.5773 | 0.5984 | 0.9701 | 0.686 | -133.242 | -8.6459 | -1.8812 | -3.0767 | -10.9996 | -9.8421 | -1.8521 |  | -5.4137 | -4.8909 | 4.0767 | 3.376 | 3.3568 | 0.9096 | 10.5415 | 13.9168 | 14.5365 | 10.8428 | 0.0002 | -0.0031 | 0.0002 | 0.0035 | 0.0008 | -0.001 | -0.0061 | -0.0009 | -0.0276 | -360.1558 | 17.8196 | -360.7127 | 18.0845 | -360.9897 | 18.0927 | -361.0266 | 17.5671 | -353.0629 | 18.7846 | -353.0691 | 16.8279
11:27 | 411 | 17.9259 | 191.089 | 432.5964 | 437.2334 | -20.4223 | -48.2927 | 0.3216 | -0.7292 | -8.3692 | -8.5333 | -3.817 | -4.4009 | 1.2681 | -5.5364 | 0.5762 | 0.6018 | 0.967 | 0.6868 | -133.126 | -8.5995 | -1.7154 | -3.0208 | -10.9903 | -9.7379 | -1.8107 |  | -5.4101 | -4.8635 | 4.0757 | 3.3768 | 3.3545 | 0.9102 | 10.5151 | 13.8899 | 14.5014 | 10.7883 | -0.0002 | -0.0027 | 0.0006 | 0.0035 | 0.0005 | -0.0007 | 0.0204 | 0.0018 | -0.0022 | -360.1096 | 17.7929 | -360.6943 | 18.0845 | -361.002 | 18.1276 | -361.0543 | 17.5527 | -353.0321 | 18.7641 | -353.0383 | 16.834
11:27 | 412 | 17.9183 | 191.0782 | 432.5941 | 437.3397 | -20.5293 | -48.214 | 0.2342 | -0.6531 | -8.306 | -8.4346 | -3.7392 | -4.442 | 1.2671 | -5.5659 | 0.5754 | 0.6035 | 0.9707 | 0.6886 | -133.0944 | -8.5769 | -1.6246 | -2.87 | -10.9646 | -9.6685 | -1.7977 |  | -5.3501 | -4.7449 | 4.0749 | 3.375 | 3.3589 | 0.9105 | 10.5196 | 13.9178 | 14.4963 | 10.8211 | -0.0005 | -0.0027 | 0.0005 | 0.0037 | 0.0005 | -0.0007 | 0.0201 | -0.0023 | -0.0114 | -360.1004 | 17.7703 | -360.642 | 18.0783 | -361.0051 | 18.1337 | -361.0851 | 17.5629 | -353.0198 | 18.7353 | -352.9952 | 16.8094
11:27 | 413 | 18.0231 | 191.0934 | 432.4975 | 437.4054 | -20.4502 | -48.2101 | 0.2876 | -0.5864 | -8.2999 | -8.4697 | -3.6981 | -4.4389 | 1.3375 | -5.4462 | 0.5762 | 0.6013 | 0.9651 | 0.6864 | -133.0608 | -8.5794 | -1.7327 | -3.0399 | -10.911 | -9.8259 | -1.9002 |  | -5.3888 | -4.8855 | 4.0739 | 3.3754 | 3.3569 | 0.9109 | 10.4885 | 13.9268 | 14.48 | 10.814 | -0.0005 | -0.0032 | 0.0005 | 0.0034 | 0.0006 | -0.0008 | 0.0078 | -0.0082 | -0.0202 | -360.1034 | 17.7703 | -360.642 | 18.0824 | -361.0051 | 18.1276 | -361.0728 | 17.5588 | -353.0229 | 18.762 | -353.0137 | 16.8238
11:27 | 414 | 17.92 | 190.9106 | 432.3373 | 437.1934 | -20.5886 | -48.2825 | 0.2484 | -0.6407 | -8.3633 | -8.3703 | -3.6867 | -4.2926 | 1.3969 | -5.5345 | 0.5755 | 0.5993 | 0.9661 | 0.6848 | -133.1319 | -8.5685 | -1.8319 | -2.9565 | -10.9131 | -9.7297 | -1.8995 |  | -5.3994 | -4.8427 | 4.0754 | 3.3793 | 3.3581 | 0.9129 | 10.5196 | 13.9005 | 14.479 | 10.8385 | -0.0002 | -0.0032 | 0.0009 | 0.0035 | 0.0006 | -0.0003 | 0.0198 | 0.0009 | 0.0085 | -360.1342 | 17.8032 | -360.6912 | 18.068 | -360.9651 | 18.1153 | -361.0266 | 17.5691 | -353.0537 | 18.7764 | -353.0445 | 16.8217
11:27 | 415 | 17.8904 | 190.9468 | 432.4716 | 437.2334 | -20.5166 | -48.3913 | 0.2876 | -0.6711 | -8.3372 | -8.3554 | -3.7055 | -4.2887 | 1.4359 | -5.537 | 0.5758 | 0.5985 | 0.9621 | 0.6853 | -133.1483 | -8.6588 | -1.811 | -2.9175 | -10.9288 | -9.7298 | -1.8659 |  | -5.3212 | -4.9445 | 4.076 | 3.3774 | 3.3577 | 0.9119 | 10.5369 | 13.9236 | 14.5079 | 10.8442 | -0.0002 | -0.003 | 0.0011 | 0.0039 | 0.0006 | -0.0008 | 0.0027 | -0.0037 | 0.0013 | -360.1681 | 17.8217 | -360.7189 | 18.0804 | -360.9804 | 18.1091 | -361.0235 | 17.5691 | -353.0352 | 18.7908 | -353.0845 | 16.8238
11:27 | 416 | 17.9605 | 190.9025 | 432.5103 | 437.3278 | -20.4954 | -48.3184 | 0.2351 | -0.774 | -8.3674 | -8.3162 | -3.7781 | -4.396 | 1.3948 | -5.5071 | 0.5775 | 0.6026 | 0.9667 | 0.6863 | -133.1458 | -8.6411 | -1.8532 | -2.9275 | -10.9104 | -9.6597 | -1.8575 |  | -5.3349 | -4.8942 | 4.076 | 3.3769 | 3.3572 | 0.9135 | 10.5416 | 13.934 | 14.5297 | 10.8605 | -0.0006 | -0.0032 | 0.001 | 0.004 | 0.0003 | -0.0004 | 0.0059 | -0.006 | 0.0052 | -360.1588 | 17.8032 | -360.685 | 18.0865 | -361.002 | 18.1379 | -361.0358 | 17.5712 | -353.0568 | 18.7764 | -353.0537 | 16.8258
11:27 | 417 | 17.9848 | 190.956 | 432.4508 | 437.4344 | -20.4865 | -48.3559 | 0.2622 | -0.703 | -8.3365 | -8.3095 | -3.6792 | -4.3817 | 1.2753 | -5.5955 | 0.5771 | 0.5981 | 0.9667 | 0.6859 | -133.1087 | -8.6625 | -1.7732 | -2.888 | -10.9149 | -9.6302 | -1.7979 |  | -5.3449 | -4.9378 | 4.0746 | 3.3757 | 3.3565 | 0.9139 | 10.5207 | 13.8959 | 14.5151 | 10.8164 | -0.0002 | -0.0026 | 0.0009 | 0.0039 | 0.0007 | -0.001 | 0.0004 | -0.0089 | -0.031 | -360.0696 | 17.7785 | -360.642 | 18.0763 | -361.0051 | 18.1522 | -361.0481 | 17.565 | -352.9952 | 18.7518 | -353.026 | 16.8299
11:27 | 418 | 17.9292 | 190.9684 | 432.3699 | 437.3629 | -20.4948 | -48.3744 | 0.2649 | -0.7048 | -8.3513 | -8.4098 | -3.7098 | -4.4293 | 1.3132 | -5.6119 | 0.5778 | 0.6035 | 0.9669 | 0.6861 | -133.1735 | -8.6297 | -1.8389 | -2.9412 | -10.8821 | -9.6292 | -1.7658 |  | -5.4004 | -4.8223 | 4.0744 | 3.3757 | 3.3587 | 0.9145 | 10.5221 | 13.8908 | 14.5065 | 10.8306 | 0.0003 | -0.003 | 0 | 0.0034 | 0.0004 | -0.0006 | 0.0289 | 0.0005 | 0.006 | -360.0788 | 17.7518 | -360.6296 | 18.0742 | -361.002 | 18.1728 | -361.0666 | 17.5588 | -352.9952 | 18.7333 | -353.0075 | 16.8135
11:27 | 419 | 17.9549 | 191.1005 | 432.5593 | 437.4608 | -20.5028 | -48.4341 | 0.1564 | -0.744 | -8.3763 | -8.5384 | -3.7393 | -4.4831 | 1.394 | -5.6373 | 0.5761 | 0.6012 | 0.9647 | 0.6866 | -133.0889 | -8.6022 | -1.838 | -3.0816 | -10.795 | -9.6961 | -1.7736 |  | -5.4403 | -4.9011 | 4.0762 | 3.3752 | 3.3599 | 0.9139 | 10.5495 | 13.9252 | 14.5587 | 10.8557 | 0.0002 | -0.0033 | 0.0011 | 0.004 | 0.0007 | -0.0006 | 0 | 0.0124 | -0.0064 | -360.125 | 17.797 | -360.6727 | 18.0804 | -361.002 | 18.1481 | -361.0451 | 17.5568 | -353.0445 | 18.7661 | -353.0291 | 16.8279
11:27 | 420 | 17.9382 | 191.0587 | 432.5885 | 437.4503 | -20.5941 | -48.4588 | 0.15 | -0.6475 | -8.3267 | -8.4077 | -3.6915 | -4.3366 | 1.4916 | -5.5888 | 0.5761 | 0.6025 | 0.9677 | 0.685 | -133.1346 | -8.6139 | -1.8514 | -3.1721 | -10.8447 | -9.7179 | -1.8862 |  | -5.3559 | -4.8577 | 4.0753 | 3.3744 | 3.3605 | 0.9145 | 10.5416 | 13.8877 | 14.5066 | 10.8374 | -0.0006 | -0.0028 | 0.0004 | 0.0033 | 0.0005 | -0.0009 | 0.0206 | 0.006 | 0.005 | -360.165 | 17.8196 | -360.7004 | 18.0721 | -360.9527 | 18.1296 | -361.0512 | 17.5773 | -353.0629 | 18.7908 | -353.0568 | 16.8176
11:27 | 421 | 17.9434 | 191.0473 | 432.5263 | 437.5128 | -20.6178 | -48.4845 | 0.2435 | -0.717 | -8.3483 | -8.4468 | -3.7063 | -4.3833 | 1.3351 | -5.7583 | 0.5781 | 0.6 | 0.9676 | 0.6854 | -133.1562 | -8.7023 | -1.8584 | -3.1376 | -10.9066 | -9.6917 | -1.8156 |  | -5.3539 | -4.818 | 4.0728 | 3.3762 | 3.3618 | 0.9159 | 10.536 | 13.8758 | 14.4745 | 10.7981 | -0.0002 | -0.0026 | 0.0005 | 0.0037 | 0.0001 | -0.0008 | 0.0103 | -0.0059 | 0.0016 | -360.1681 | 17.7991 | -360.6696 | 18.0598 | -360.9404 | 18.1173 | -361.0174 | 17.5506 | -353.0383 | 18.7826 | -353.0537 | 16.8115
11:27 | 422 | 17.8417 | 190.9969 | 432.5099 | 437.4834 | -20.5231 | -48.4554 | 0.3969 | -0.7251 | -8.3225 | -8.4706 | -3.6702 | -4.2936 | 1.3621 | -5.66 | 0.5787 | 0.6041 | 0.964 | 0.6873 | -133.1671 | -8.6898 | -1.7572 | -3.0836 | -10.9417 | -9.6284 | -1.7565 |  | -5.3885 | -4.8207 | 4.0746 | 3.3752 | 3.3562 | 0.9157 | 10.5668 | 13.9426 | 14.5482 | 10.8437 | 0.0004 | -0.0027 | 0.0013 | 0.0041 | 0.0009 | -0.0004 | 0.0138 | -0.0067 | -0.0087 | -360.1065 | 17.7806 | -360.682 | 18.0763 | -361.002 | 18.1399 | -361.042 | 17.5383 | -353.0229 | 18.76 | -353.0598 | 16.8197
11:27 | 423 | 17.9765 | 191.1204 | 432.5333 | 437.5836 | -20.6017 | -48.5063 | 0.3057 | -0.7288 | -8.3505 | -8.4227 | -3.657 | -4.2862 | 1.4094 | -5.5438 | 0.5774 | 0.602 | 0.9636 | 0.6859 | -133.0855 | -8.6633 | -1.7948 | -3.0054 | -10.9611 | -9.7291 | -1.752 |  | -5.3459 | -4.8197 | 4.073 | 3.3786 | 3.3577 | 0.9152 | 10.5657 | 13.9124 | 14.5226 | 10.8431 | 0.0001 | -0.0029 | 0.0008 | 0.0036 | 0.0006 | 0 | 0.0066 | -0.0171 | -0.0103 | -360.0788 | 17.7621 | -360.6635 | 18.0968 | -361.0297 | 18.1625 | -361.0789 | 17.5363 | -352.9952 | 18.7415 | -352.9952 | 16.8443
11:27 | 424 | 17.9056 | 191.0677 | 432.5273 | 437.489 | -20.6313 | -48.4613 | 0.3571 | -0.6639 | -8.2986 | -8.3597 | -3.6136 | -4.3151 | 1.4876 | -5.5539 | 0.5759 | 0.6065 | 0.9678 | 0.688 | -133.0675 | -8.7153 | -1.8279 | -3.0571 | -10.9761 | -9.6931 | -1.7744 |  | -5.3152 | -4.8192 | 4.0726 | 3.3816 | 3.36 | 0.9173 | 10.5382 | 13.8841 | 14.5014 | 10.8288 | -0.0002 | -0.0031 | 0.0012 | 0.0043 | 0.001 | -0.0009 | 0.0099 | -0.004 | 0.0032 | -360.1219 | 17.7826 | -360.6543 | 18.0804 | -361.0081 | 18.1687 | -361.0451 | 17.5363 | -353.0198 | 18.7559 | -353.0168 | 16.8258
11:27 | 425 | 17.9927 | 191.174 | 432.5933 | 437.5148 | -20.5951 | -48.4529 | 0.2713 | -0.6707 | -8.2519 | -8.3188 | -3.5545 | -4.4229 | 1.3685 | -5.6703 | 0.5771 | 0.6021 | 0.9621 | 0.6872 | -133.0572 | -8.6747 | -1.7722 | -2.8737 | -11.0225 | -9.7476 | -1.8359 |  | -5.3329 | -4.8019 | 4.0724 | 3.3785 | 3.3586 | 0.9177 | 10.56 | 13.9123 | 14.5332 | 10.8377 | 0.0001 | -0.0024 | 0.001 | 0.0036 | 0.0003 | -0.0003 | 0.0065 | -0.0204 | -0.0201 | -360.1281 | 17.795 | -360.6481 | 18.0557 | -360.9774 | 18.142 | -361.0481 | 17.5568 | -353.0168 | 18.7805 | -353.0321 | 16.8094
11:27 | 426 | 17.9483 | 191.1003 | 432.6041 | 437.4348 | -20.5837 | -48.4526 | 0.2914 | -0.7434 | -8.301 | -8.49 | -3.5741 | -4.3345 | 1.4035 | -5.5788 | 0.5767 | 0.6035 | 0.964 | 0.6875 | -133.0032 | -8.6898 | -1.6817 | -2.8449 | -10.9664 | -9.6253 | -1.7673 |  | -5.3771 | -4.8967 | 4.0715 | 3.3793 | 3.3594 | 0.9183 | 10.5314 | 13.9117 | 14.5164 | 10.8454 | -0.0004 | -0.0031 | 0.0001 | 0.0033 | 0.0007 | -0.0011 | 0.0042 | -0.0096 | -0.0098 | -360.1835 | 17.8114 | -360.6696 | 18.0578 | -360.9558 | 18.1194 | -361.0174 | 17.5588 | -353.0629 | 18.7969 | -353.0291 | 16.8032
11:27 | 427 | 17.9678 | 191.2024 | 432.634 | 437.5291 | -20.5532 | -48.4231 | 0.3532 | -0.7315 | -8.3723 | -8.5226 | -3.6026 | -4.3732 | 1.3959 | -5.5891 | 0.5774 | 0.6004 | 0.9636 | 0.6871 | -133.1362 | -8.7661 | -1.7441 | -2.8143 | -10.9935 | -9.7965 | -1.8774 |  | -5.3763 | -4.8765 | 4.071 | 3.3754 | 3.3593 | 0.9198 | 10.514 | 13.8539 | 14.4585 | 10.7934 | 0.0003 | -0.0028 | 0.0005 | 0.0038 | 0.001 | -0.0005 | -0.0067 | -0.0043 | -0.0196 | -360.1188 | 17.7888 | -360.6727 | 18.0598 | -360.9774 | 18.144 | -361.0358 | 17.5404 | -353.0506 | 18.7846 | -353.0537 | 16.8074
11:27 | 428 | 18.1301 | 191.2553 | 432.6476 | 437.612 | -20.575 | -48.3203 | 0.2897 | -0.7515 | -8.281 | -8.4311 | -3.6808 | -4.3483 | 1.4706 | -5.6342 | 0.5772 | 0.6036 | 0.965 | 0.6865 | -133.22 | -8.7528 | -1.8322 | -2.8446 | -10.965 | -9.6768 | -1.7215 |  | -5.4107 | -4.8415 | 4.0716 | 3.3786 | 3.3588 | 0.9197 | 10.5163 | 13.8851 | 14.4844 | 10.8014 | -0.0002 | -0.0032 | 0.0011 | 0.004 | 0.0003 | -0.0009 | -0.0056 | 0.0043 | 0.0027 | -360.0819 | 17.7601 | -360.685 | 18.0886 | -361.0266 | 18.1584 | -361.0635 | 17.5321 | -352.9737 | 18.7477 | -353.0291 | 16.8484
11:27 | 429 | 18.0376 | 191.2074 | 432.5688 | 437.5639 | -20.5696 | -48.3836 | 0.3077 | -0.8618 | -8.3521 | -8.5386 | -3.7016 | -4.3124 | 1.4711 | -5.5882 | 0.5749 | 0.6031 | 0.9642 | 0.6862 | -133.1524 | -8.7151 | -1.7497 | -2.8582 | -11.0426 | -9.7246 | -1.7745 |  | -5.4141 | -4.8193 | 4.0703 | 3.3786 | 3.3589 | 0.9189 | 10.551 | 13.8909 | 14.4844 | 10.836 | -0.0005 | -0.0028 | 0.0005 | 0.0037 | 0.0008 | -0.0007 | 0.0084 | -0.0191 | -0.0114 | -360.085 | 17.7683 | -360.6635 | 18.0742 | -361.0389 | 18.1584 | -361.0358 | 17.526 | -352.986 | 18.76 | -353.0291 | 16.8361
11:27 | 430 | 17.9823 | 191.2367 | 432.6591 | 437.5392 | -20.5906 | -48.4489 | 0.2888 | -0.7778 | -8.3062 | -8.5542 | -3.7379 | -4.2672 | 1.4383 | -5.5589 | 0.5777 | 0.6056 | 0.9702 | 0.6865 | -133.1495 | -8.6221 | -1.7139 | -2.9093 | -10.9931 | -9.8504 | -1.7695 |  | -5.4142 | -4.8037 | 4.0708 | 3.3758 | 3.3609 | 0.9204 | 10.5521 | 13.9038 | 14.5042 | 10.8136 | -0.0004 | -0.0028 | 0.0011 | 0.0038 | 0.0004 | -0.0007 | 0.0058 | 0.0039 | -0.0026 | -360.1465 | 17.7806 | -360.6666 | 18.0537 | -360.9835 | 18.142 | -361.042 | 17.5609 | -353.0291 | 18.7887 | -352.9983 | 16.8074
11:27 | 431 | 17.9373 | 191.2107 | 432.5529 | 437.5264 | -20.5854 | -48.3548 | 0.3123 | -0.7752 | -8.3189 | -8.4721 | -3.6807 | -4.3139 | 1.442 | -5.6476 | 0.5756 | 0.6025 | 0.9659 | 0.6863 | -133.0765 | -8.6756 | -1.7361 | -2.9613 | -11.0619 | -9.6773 | -1.7558 |  | -5.4655 | -4.8427 | 4.0709 | 3.3771 | 3.3562 | 0.9217 | 10.5727 | 13.9482 | 14.5345 | 10.8734 | -0.0004 | -0.0029 | 0.0006 | 0.0037 | 0.0011 | -0.0005 | -0.0016 | -0.0024 | -0.0019 | -360.1681 | 17.7991 | -360.6666 | 18.0434 | -360.9374 | 18.1296 | -361.0543 | 17.5691 | -353.026 | 18.7908 | -353.0229 | 16.8032
11:27 | 432 | 18.0134 | 191.3742 | 432.7478 | 437.6619 | -20.5407 | -48.4557 | 0.3077 | -0.8302 | -8.393 | -8.4196 | -3.6999 | -4.3518 | 1.425 | -5.557 | 0.5774 | 0.6011 | 0.9618 | 0.6875 | -133.0311 | -8.6346 | -1.7785 | -2.889 | -10.984 | -9.6457 | -1.7555 |  | -5.4095 | -4.8731 | 4.0703 | 3.3812 | 3.3584 | 0.9217 | 10.5508 | 13.9318 | 14.5164 | 10.8175 | 0.0002 | -0.0032 | 0.0005 | 0.0035 | 0.0004 | -0.0004 | 0.0018 | -0.003 | -0.0051 | -360.1404 | 17.7765 | -360.6543 | 18.0475 | -360.9712 | 18.1358 | -361.0051 | 17.5424 | -353.0229 | 18.7826 | -352.9952 | 16.8094
11:27 | 433 | 17.929 | 191.296 | 432.6098 | 437.5477 | -20.6679 | -48.4245 | 0.2531 | -0.8184 | -8.4892 | -8.5373 | -3.6193 | -4.3674 | 1.5375 | -5.4885 | 0.577 | 0.6018 | 0.9638 | 0.6876 | -133.0987 | -8.6606 | -1.7665 | -2.9274 | -10.8775 | -9.6512 | -1.7361 |  | -5.3072 | -4.8028 | 4.0724 | 3.3796 | 3.363 | 0.9233 | 10.5429 | 13.906 | 14.5232 | 10.8277 | -0.0003 | -0.0032 | 0.0005 | 0.0032 | 0.0007 | -0.0011 | 0.0129 | -0.01 | -0.0092 | -360.0542 | 17.758 | -360.6727 | 18.0927 | -361.0235 | 18.1604 | -361.0328 | 17.526 | -352.9737 | 18.7703 | -353.0414 | 16.8566
11:27 | 434 | 17.99 | 191.4002 | 432.7014 | 437.5698 | -20.609 | -48.4255 | 0.3434 | -0.8144 | -8.3803 | -8.4913 | -3.5087 | -4.3412 | 1.5383 | -5.5602 | 0.5756 | 0.6032 | 0.9651 | 0.6883 | -133.0306 | -8.672 | -1.8004 | -2.8546 | -10.9283 | -9.7339 | -1.7389 |  | -5.3886 | -4.8041 | 4.0704 | 3.3789 | 3.3593 | 0.9225 | 10.5197 | 13.9004 | 14.5011 | 10.8504 | -0.0006 | -0.0026 | -0.0001 | 0.0031 | 0.0007 | -0.0005 | 0.0046 | 0.0029 | -0.0197 | -360.0881 | 17.7662 | -360.6604 | 18.0906 | -361.042 | 18.1728 | -361.0604 | 17.5342 | -352.9614 | 18.7703 | -353.0229 | 16.8546
11:27 | 435 | 17.9849 | 191.5063 | 432.7032 | 437.5805 | -20.6388 | -48.4141 | 0.3543 | -0.7721 | -8.2885 | -8.4223 | -3.5466 | -4.3648 | 1.4731 | -5.5937 | 0.5754 | 0.602 | 0.9619 | 0.6879 | -132.992 | -8.6355 | -1.7588 | -2.7629 | -11.0537 | -9.7294 | -1.8147 |  | -5.3927 | -4.8139 | 4.0698 | 3.376 | 3.357 | 0.9227 | 10.5428 | 13.9061 | 14.5011 | 10.8215 | -0.0001 | -0.003 | 0.0006 | 0.0036 | 0.0003 | -0.0009 | 0.0036 | -0.0099 | 0.0058 | -360.1034 | 17.7662 | -360.6635 | 18.0537 | -360.9527 | 18.1481 | -361.042 | 17.5445 | -353.0106 | 18.7723 | -353.0137 | 16.832
11:27 | 436 | 17.9638 | 191.4198 | 432.6502 | 437.5922 | -20.6378 | -48.4637 | 0.2284 | -0.7125 | -8.2669 | -8.4257 | -3.5245 | -4.2851 | 1.4797 | -5.5458 | 0.5775 | 0.6051 | 0.9643 | 0.6871 | -132.9554 | -8.6644 | -1.7157 | -2.7961 | -10.9594 | -9.6313 | -1.7843 |  | -5.305 | -4.7731 | 4.0706 | 3.3731 | 3.3558 | 0.9225 | 10.4769 | 13.8747 | 14.4626 | 10.8082 | 0.0002 | -0.0034 | 0.0009 | 0.0037 | 0.0006 | -0.0009 | 0.0105 | -0.0127 | -0.0029 | -360.1527 | 17.7744 | -360.642 | 18.0352 | -360.922 | 18.1194 | -361.0451 | 17.5568 | -353.0537 | 18.7826 | -353.0106 | 16.8094
11:27 | 437 | 17.9574 | 191.4328 | 432.7108 | 437.6816 | -20.7033 | -48.3887 | 0.3249 | -0.6318 | -8.2415 | -8.3613 | -3.54 | -4.2566 | 1.5328 | -5.5442 | 0.5782 | 0.6047 | 0.9631 | 0.6866 | -132.9528 | -8.6955 | -1.8088 | -2.8112 | -10.9636 | -9.6747 | -1.7833 |  | -5.3379 | -4.7555 | 4.0705 | 3.3759 | 3.3586 | 0.924 | 10.5439 | 13.9015 | 14.4967 | 10.8053 | -0.0002 | -0.0032 | 0.0007 | 0.0038 | 0.0007 | -0.0003 | 0.0016 | -0.0081 | 0.0015 | -360.1127 | 17.7765 | -360.6543 | 18.0455 | -360.9312 | 18.1317 | -361.0635 | 17.5568 | -353.0383 | 18.7908 | -352.9921 | 16.8176
11:27 | 438 | 17.9928 | 191.4319 | 432.7503 | 437.6789 | -20.733 | -48.349 | 0.2945 | -0.7727 | -8.268 | -8.4341 | -3.53 | -4.2407 | 1.5439 | -5.504 | 0.5783 | 0.603 | 0.9593 | 0.6882 | -132.9671 | -8.6926 | -1.8001 | -2.9138 | -10.9957 | -9.6918 | -1.7524 |  | -5.3688 | -4.8105 | 4.0697 | 3.3776 | 3.3619 | 0.924 | 10.5474 | 13.8992 | 14.4882 | 10.8551 | -0.001 | -0.0031 | 0.0013 | 0.004 | 0.0009 | -0.0005 | -0.0076 | -0.0029 | -0.0259 | -360.1188 | 17.7724 | -360.685 | 18.0927 | -361.0235 | 18.144 | -361.0297 | 17.5424 | -352.9952 | 18.7826 | -353.0321 | 16.8525
11:27 | 439 | 17.9293 | 191.4442 | 432.7107 | 437.7056 | -20.7015 | -48.3645 | 0.2387 | -0.7671 | -8.2743 | -8.4428 | -3.5867 | -4.2516 | 1.4393 | -5.4779 | 0.5775 | 0.5986 | 0.9612 | 0.6885 | -132.9305 | -8.7413 | -1.785 | -2.8882 | -10.9365 | -9.5806 | -1.7492 |  | -5.5022 | -4.8114 | 4.0697 | 3.3768 | 3.3572 | 0.9233 | 10.5657 | 13.9124 | 14.5574 | 10.8719 | -0.0004 | -0.0027 | 0.0009 | 0.0035 | 0.0007 | 0.0001 | 0.0052 | -0.0142 | -0.0339 | -360.0758 | 17.7559 | -360.6912 | 18.0968 | -361.0297 | 18.1666 | -361.0543 | 17.5363 | -352.9583 | 18.76 | -353.0291 | 16.8546
11:27 | 440 | 18.0681 | 191.5216 | 432.7776 | 437.7132 | -20.6341 | -48.338 | 0.2795 | -0.6698 | -8.2998 | -8.4987 | -3.5598 | -4.2371 | 1.5236 | -5.4558 | 0.5761 | 0.601 | 0.9592 | 0.6864 | -132.8793 | -8.7665 | -1.7758 | -2.8493 | -10.946 | -9.7105 | -1.7184 |  | -5.4598 | -4.7902 | 4.0689 | 3.3783 | 3.3592 | 0.9241 | 10.5591 | 13.8991 | 14.5161 | 10.8208 | 0.0001 | -0.0034 | 0.0003 | 0.0031 | 0.0006 | -0.0011 | 0.0251 | 0.0016 | 0.001 | -360.0881 | 17.7642 | -360.6389 | 18.0516 | -360.9927 | 18.1379 | -361.0297 | 17.5301 | -353.0075 | 18.7703 | -352.9891 | 16.8299
11:27 | 441 | 17.9307 | 191.5138 | 432.7781 | 437.7409 | -20.6321 | -48.299 | 0.2981 | -0.7439 | -8.2567 | -8.4412 | -3.5416 | -4.2834 | 1.4698 | -5.4608 | 0.5776 | 0.6034 | 0.9623 | 0.6884 | -132.8919 | -8.6831 | -1.8313 | -2.8754 | -10.9702 | -9.7048 | -1.8142 |  | -5.496 | -4.7993 | 4.0668 | 3.3784 | 3.3556 | 0.9258 | 10.5475 | 13.9048 | 14.5392 | 10.8035 | -0.0001 | -0.0032 | 0.0007 | 0.0034 | 0.0003 | -0.0004 | 0.0119 | -0.0095 | -0.0222 | -360.1342 | 17.7744 | -360.642 | 18.0393 | -360.9404 | 18.1358 | -361.0543 | 17.565 | -353.0568 | 18.7867 | -353.0014 | 16.8115
11:27 | 442 | 18.0052 | 191.5682 | 432.7292 | 437.6988 | -20.7768 | -48.3071 | 0.2876 | -0.7645 | -8.2915 | -8.4114 | -3.5411 | -4.3246 | 1.4456 | -5.5141 | 0.5758 | 0.6043 | 0.962 | 0.6883 | -132.992 | -8.7813 | -1.7566 | -2.8288 | -11.0407 | -9.705 | -1.7844 |  | -5.4185 | -4.7659 | 4.0675 | 3.3761 | 3.353 | 0.9262 | 10.5404 | 13.9155 | 14.5226 | 10.8016 | -0.0001 | -0.0027 | 0 | 0.0032 | 0.0008 | -0.0007 | -0.0076 | -0.0093 | -0.0194 | -360.1773 | 17.795 | -360.6789 | 18.0434 | -360.9589 | 18.142 | -361.0358 | 17.5671 | -353.0475 | 18.7969 | -353.0445 | 16.8197
11:27 | 443 | 17.9835 | 191.609 | 432.7025 | 437.7494 | -20.7445 | -48.303 | 0.4016 | -0.7696 | -8.2723 | -8.3318 | -3.5531 | -4.3275 | 1.4787 | -5.5015 | 0.5781 | 0.6034 | 0.9615 | 0.6886 | -132.9853 | -8.7568 | -1.7882 | -2.8356 | -11.0254 | -9.6364 | -1.7774 |  | -5.4189 | -4.8307 | 4.0676 | 3.3758 | 3.3591 | 0.9268 | 10.5476 | 13.8816 | 14.4861 | 10.8155 | -0.0005 | -0.0027 | 0.0002 | 0.0034 | 0.0005 | -0.0005 | -0.0094 | 0.0004 | -0.0143 | -360.1219 | 17.7683 | -360.6604 | 18.0475 | -360.9989 | 18.142 | -361.0266 | 17.5424 | -352.9798 | 18.7744 | -353.0229 | 16.8299
11:27 | 444 | 17.9532 | 191.5693 | 432.6906 | 437.7582 | -20.7296 | -48.2562 | 0.3626 | -0.7071 | -8.2978 | -8.4299 | -3.5331 | -4.3098 | 1.5342 | -5.3781 | 0.5773 | 0.6042 | 0.9652 | 0.6887 | -132.9349 | -8.7007 | -1.7521 | -2.9149 | -11.0502 | -9.6351 | -1.8555 |  | -5.3995 | -4.8123 | 4.0689 | 3.3745 | 3.3565 | 0.9275 | 10.5357 | 13.9052 | 14.4844 | 10.837 | 0.0002 | -0.0027 | 0.0008 | 0.0038 | 0.001 | -0.0005 | 0.0123 | 0 | -0.0097 | -360.0788 | 17.7416 | -360.6604 | 18.0516 | -361.0174 | 18.1625 | -361.0297 | 17.5239 | -352.9583 | 18.7477 | -353.0168 | 16.8587
11:27 | 445 | 17.9835 | 191.5795 | 432.6915 | 437.7367 | -20.6696 | -48.1746 | 0.4299 | -0.7265 | -8.2618 | -8.3029 | -3.5855 | -4.292 | 1.5826 | -5.4262 | 0.578 | 0.6044 | 0.9622 | 0.6875 | -132.9655 | -8.6951 | -1.8353 | -2.9556 | -11.0126 | -9.7201 | -1.8415 |  | -5.3966 | -4.7735 | 4.068 | 3.3776 | 3.3596 | 0.9272 | 10.5543 | 13.9352 | 14.5079 | 10.8385 | 0 | -0.0033 | 0.0003 | 0.0039 | 0.0001 | -0.0012 | 0.0116 | -0.0127 | -0.0062 | -360.0942 | 17.7518 | -360.6635 | 18.0537 | -361.0235 | 18.1666 | -361.0174 | 17.5383 | -352.9644 | 18.7764 | -352.9921 | 16.8423
11:27 | 446 | 17.9105 | 191.4946 | 432.6315 | 437.7867 | -20.7769 | -48.364 | 0.3698 | -0.7567 | -8.3213 | -8.4287 | -3.5527 | -4.3183 | 1.4923 | -5.4639 | 0.5783 | 0.6022 | 0.964 | 0.6888 | -132.9702 | -8.7046 | -1.7068 | -2.9463 | -11.0256 | -9.6956 | -1.9173 |  | -5.3487 | -4.745 | 4.0679 | 3.3803 | 3.3543 | 0.9284 | 10.5624 | 13.9143 | 14.527 | 10.841 | -0.0001 | -0.0026 | 0.0005 | 0.0036 | 0.0005 | -0.0004 | -0.0024 | -0.0047 | -0.0216 | -360.1435 | 17.7601 | -360.6727 | 18.029 | -360.9558 | 18.144 | -361.0574 | 17.5629 | -353.0321 | 18.7846 | -353.0229 | 16.8238
11:27 | 447 | 17.9495 | 191.5807 | 432.8606 | 437.801 | -20.7174 | -48.3774 | 0.3408 | -0.8252 | -8.3329 | -8.3464 | -3.5577 | -4.3186 | 1.507 | -5.3723 | 0.577 | 0.6045 | 0.9605 | 0.6885 | -132.9103 | -8.676 | -1.7697 | -2.7891 | -10.9966 | -9.7413 | -1.805 |  | -5.3805 | -4.7121 | 4.0678 | 3.376 | 3.3564 | 0.9291 | 10.5783 | 13.9484 | 14.5308 | 10.8495 | -0.0003 | -0.0029 | 0.001 | 0.0038 | 0.001 | -0.0006 | 0.0144 | -0.0098 | 0.0025 | -360.1619 | 17.7765 | -360.6543 | 18.0085 | -360.9343 | 18.1296 | -361.0389 | 17.5691 | -353.0752 | 18.7826 | -353.0044 | 16.8094
11:27 | 448 | 17.8923 | 191.5795 | 432.8458 | 437.7903 | -20.7075 | -48.316 | 0.3137 | -0.7681 | -8.3017 | -8.3548 | -3.5271 | -4.2692 | 1.502 | -5.4307 | 0.5783 | 0.6023 | 0.9623 | 0.6879 | -132.8971 | -8.7431 | -1.7614 | -2.7358 | -11.0854 | -9.6613 | -1.8019 |  | -5.3892 | -4.7516 | 4.0683 | 3.3783 | 3.3568 | 0.9298 | 10.5717 | 13.9119 | 14.4837 | 10.8215 | 0.0001 | -0.0024 | 0 | 0.0031 | 0.0002 | -0.0005 | -0.002 | -0.0061 | 0.0078 | -360.1311 | 17.7621 | -360.6358 | 18.0126 | -360.9466 | 18.1399 | -361.0266 | 17.5383 | -352.9983 | 18.7764 | -353.0075 | 16.8156
11:27 | 449 | 17.9219 | 191.6585 | 432.8577 | 437.7933 | -20.6478 | -48.191 | 0.4538 | -0.7639 | -8.3161 | -8.3492 | -3.5211 | -4.276 | 1.4446 | -5.4879 | 0.578 | 0.6014 | 0.9613 | 0.6887 | -132.9032 | -8.6887 | -1.7597 | -2.777 | -11.0275 | -9.7531 | -1.8033 |  | -5.4261 | -4.7943 | 4.0678 | 3.3807 | 3.3629 | 0.9299 | 10.5335 | 13.8969 | 14.4865 | 10.8121 | 0.0001 | -0.0031 | 0.0008 | 0.0037 | 0.0009 | -0.0006 | 0.0054 | -0.0186 | -0.01 | -360.0758 | 17.7375 | -360.6727 | 18.0537 | -361.0204 | 18.1461 | -361.0451 | 17.5301 | -352.946 | 18.7703 | -353.0475 | 16.8587
11:27 | 450 | 17.9119 | 191.6608 | 432.8536 | 437.8412 | -20.7114 | -48.2282 | 0.4157 | -0.7564 | -8.3238 | -8.4462 | -3.4895 | -4.2626 | 1.4907 | -5.4278 | 0.5777 | 0.6055 | 0.9596 | 0.6854 | -133.0043 | -8.7191 | -1.8902 | -2.777 | -11.0335 | -9.6415 | -1.7367 |  | -5.3329 | -4.7746 | 4.0675 | 3.3789 | 3.3597 | 0.9319 | 10.5291 | 13.8862 | 14.4847 | 10.8144 | -0.0002 | -0.0031 | 0.0004 | 0.0035 | 0.0002 | -0.0008 | 0.0223 | -0.0115 | -0.0211 | -360.0973 | 17.7539 | -360.6758 | 18.0393 | -361.0174 | 18.1645 | -361.0451 | 17.528 | -352.9706 | 18.7723 | -353.0198 | 16.8525
11:27 | 451 | 17.9704 | 191.6514 | 432.8554 | 437.7995 | -20.7371 | -48.2193 | 0.4973 | -0.7991 | -8.2098 | -8.3422 | -3.5699 | -4.272 | 1.5202 | -5.4011 | 0.5786 | 0.6036 | 0.9613 | 0.6871 | -133.0493 | -8.7253 | -1.9275 | -2.7944 | -11.0143 | -9.5993 | -1.8537 |  | -5.3815 | -4.8246 | 4.0676 | 3.3709 | 3.3568 | 0.9326 | 10.5615 | 13.878 | 14.4878 | 10.8353 | -0.0004 | -0.0028 | 0.0007 | 0.0035 | 0.0005 | -0.001 | 0.0125 | -0.0019 | 0.0078 | -360.125 | 17.7559 | -360.6389 | 18.0064 | -360.9897 | 18.1522 | -361.042 | 17.5424 | -352.9983 | 18.7703 | -353.0168 | 16.8217
11:27 | 452 | 18.0687 | 191.6606 | 432.9151 | 437.8824 | -20.7178 | -48.056 | 0.459 | -0.789 | -8.2182 | -8.3133 | -3.5527 | -4.273 | 1.4895 | -5.4362 | 0.5788 | 0.604 | 0.9624 | 0.6884 | -132.9683 | -8.6534 | -1.8831 | -2.7509 | -10.9288 | -9.6679 | -1.8076 |  | -5.4619 | -4.8786 | 4.0673 | 3.37 | 3.3591 | 0.9311 | 10.5601 | 13.8714 | 14.4664 | 10.7984 | -0.0007 | -0.0028 | 0.0011 | 0.0043 | 0.0012 | -0.0003 | 0.0276 | -0.0141 | 0.01 | -360.1558 | 17.7457 | -360.6266 | 17.9798 | -360.9281 | 18.1194 | -361.0358 | 17.5629 | -353.0321 | 18.7744 | -352.9921 | 16.8094
11:27 | 453 | 17.9646 | 191.6218 | 432.918 | 437.8708 | -20.6819 | -48.2024 | 0.4453 | -0.7701 | -8.1942 | -8.3099 | -3.5589 | -4.2354 | 1.5047 | -5.3966 | 0.5785 | 0.606 | 0.9624 | 0.6884 | -132.9299 | -8.6441 | -1.8609 | -2.8454 | -11.0083 | -9.5411 | -1.9123 |  | -5.4208 | -4.8992 | 4.0675 | 3.3711 | 3.3576 | 0.9315 | 10.5532 | 13.8876 | 14.4882 | 10.8147 | 0.0001 | -0.003 | 0.0006 | 0.0038 | 0.0007 | -0.0005 | -0.0012 | -0.0006 | -0.014 | -360.1465 | 17.7744 | -360.6573 | 17.9962 | -360.9681 | 18.1461 | -361.0758 | 17.565 | -353.0321 | 18.7969 | -353.0137 | 16.8197
11:27 | 454 | 17.9911 | 191.6347 | 432.8891 | 437.9234 | -20.6684 | -48.2075 | 0.4133 | -0.6697 | -8.1377 | -8.3519 | -3.4961 | -4.2752 | 1.4557 | -5.2926 | 0.5774 | 0.6067 | 0.9659 | 0.6889 | -132.9721 | -8.65 | -1.9176 | -2.8293 | -11.0794 | -9.6792 | -1.8717 |  | -5.4287 | -4.8312 | 4.0675 | 3.3705 | 3.3589 | 0.9307 | 10.5763 | 13.8993 | 14.495 | 10.8316 | 0.0001 | -0.0032 | 0.0008 | 0.0037 | 0.001 | -0.0007 | 0 | -0.0034 | -0.0151 | -360.1219 | 17.758 | -360.6758 | 18.0064 | -360.9712 | 18.1481 | -361.0174 | 17.5404 | -352.9798 | 18.7785 | -353.0168 | 16.8464
11:27 | 455 | 18.0205 | 191.612 | 432.8897 | 437.9187 | -20.7021 | -48.2542 | 0.4388 | -0.6766 | -8.1402 | -8.3719 | -3.3435 | -4.2787 | 1.4955 | -5.3929 | 0.5783 | 0.6082 | 0.9601 | 0.6895 | -132.9604 | -8.6609 | -1.8924 | -2.7998 | -11.0195 | -9.5472 | -1.8272 |  | -5.494 | -4.8588 | 4.0662 | 3.368 | 3.3586 | 0.9329 | 10.5854 | 13.9089 | 14.5127 | 10.8629 | -0.0006 | -0.003 | 0.0008 | 0.0036 | 0.0006 | -0.0001 | 0.0116 | -0.0039 | -0.0155 | -360.085 | 17.7252 | -360.6727 | 18.029 | -360.9835 | 18.1379 | -360.9927 | 17.5178 | -352.9521 | 18.7559 | -353.0044 | 16.8566
11:27 | 456 | 18.0191 | 191.6753 | 432.9516 | 437.8647 | -20.7385 | -48.2758 | 0.3701 | -0.6927 | -8.1053 | -8.3528 | -3.4249 | -4.2884 | 1.5037 | -5.4027 | 0.5781 | 0.609 | 0.9625 | 0.6888 | -132.9593 | -8.735 | -1.8354 | -2.7641 | -11.0274 | -9.7001 | -1.8155 |  | -5.5055 | -4.9075 | 4.067 | 3.3695 | 3.3611 | 0.933 | 10.5658 | 13.9353 | 14.5205 | 10.8438 | -0.0004 | -0.0027 | 0.0005 | 0.0029 | 0.0006 | -0.0012 | 0.013 | -0.0137 | 0.0102 | -360.1096 | 17.7498 | -360.6881 | 18.029 | -361.002 | 18.1666 | -361.0389 | 17.526 | -352.986 | 18.7867 | -353.0445 | 16.8587
11:27 | 457 | 18.1249 | 191.7318 | 432.9993 | 438.0293 | -20.6368 | -48.1901 | 0.4019 | -0.7171 | -8.0845 | -8.3636 | -3.5276 | -4.2809 | 1.4281 | -5.4153 | 0.5769 | 0.6063 | 0.9617 | 0.6882 | -133.0151 | -8.7889 | -1.9064 | -2.9212 | -10.9814 | -9.7509 | -1.7838 |  | -5.4204 | -4.9253 | 4.0663 | 3.3701 | 3.3596 | 0.9331 | 10.582 | 13.9341 | 14.525 | 10.8543 | -0.0005 | -0.0033 | 0.0007 | 0.0038 | 0.0003 | -0.0004 | -0.0061 | 0.0018 | -0.0108 | -360.1988 | 17.7539 | -360.6604 | 18.0023 | -360.9774 | 18.1604 | -361.042 | 17.5486 | -352.9891 | 18.7764 | -353.0014 | 16.832
11:27 | 458 | 18.0454 | 191.6582 | 433.0067 | 437.9172 | -20.7006 | -48.2561 | 0.4146 | -0.7767 | -8.1269 | -8.3864 | -3.5639 | -4.341 | 1.41 | -5.5149 | 0.578 | 0.6048 | 0.9634 | 0.6891 | -133.0297 | -8.8437 | -1.9681 | -2.9612 | -10.9794 | -9.6779 | -1.8365 |  | -5.4001 | -4.8307 | 4.0665 | 3.3688 | 3.3581 | 0.9332 | 10.5706 | 13.8934 | 14.5287 | 10.832 | -0.0001 | -0.003 | 0.0006 | 0.0036 | 0.0007 | -0.001 | 0.0147 | -0.003 | -0.0213 | -360.1527 | 17.7457 | -360.6235 | 17.9736 | -360.9589 | 18.1317 | -361.0481 | 17.5671 | -353.0291 | 18.7682 | -352.9829 | 16.8053
11:27 | 459 | 18.088 | 191.7617 | 432.9651 | 437.8779 | -20.6976 | -48.2021 | 0.4165 | -0.7306 | -8.0782 | -8.2735 | -3.5525 | -4.3259 | 1.3948 | -5.5161 | 0.5776 | 0.6046 | 0.9644 | 0.6878 | -133.0452 | -8.7905 | -1.9731 | -2.9597 | -10.9816 | -9.7035 | -1.9032 |  | -5.4567 | -4.8568 | 4.0665 | 3.3717 | 3.3558 | 0.9331 | 10.5613 | 13.942 | 14.4909 | 10.8342 | -0.0007 | -0.0037 | 0.0004 | 0.0038 | 0.0006 | -0.0004 | 0.0101 | -0.0092 | -0.0152 | -360.1342 | 17.7477 | -360.6358 | 17.9941 | -360.9435 | 18.1563 | -361.0451 | 17.5588 | -353.0291 | 18.7867 | -352.986 | 16.8156
11:27 | 460 | 18.1054 | 191.8031 | 432.9902 | 437.9161 | -20.7801 | -48.1577 | 0.4308 | -0.7543 | -8.2143 | -8.3025 | -3.6141 | -4.2985 | 1.4769 | -5.5042 | 0.5773 | 0.6042 | 0.9635 | 0.6857 | -133.0041 | -8.8642 | -1.8712 | -3.0686 | -11.0313 | -9.779 | -1.9138 |  | -5.4159 | -4.7906 | 4.0663 | 3.3714 | 3.3582 | 0.9339 | 10.5544 | 13.883 | 14.4953 | 10.7984 | -0.0004 | -0.0029 | 0.0011 | 0.0043 | 0.0006 | -0.0008 | 0.0045 | -0.001 | -0.0146 | -360.1034 | 17.7559 | -360.685 | 18.0352 | -360.9958 | 18.144 | -361.0481 | 17.5465 | -352.9737 | 18.7846 | -353.0014 | 16.8402
11:27 | 461 | 17.9867 | 191.7547 | 432.9122 | 437.8449 | -20.8382 | -48.2933 | 0.2997 | -0.7996 | -8.1459 | -8.3045 | -3.6143 | -4.3509 | 1.456 | -5.4835 | 0.5774 | 0.608 | 0.9649 | 0.6879 | -133.0354 | -8.9049 | -1.9582 | -3.0044 | -10.9863 | -9.6711 | -1.8833 |  | -5.4429 | -4.7422 | 4.0661 | 3.3693 | 3.3571 | 0.9335 | 10.5625 | 13.891 | 14.4854 | 10.8356 | -0.0002 | -0.0028 | 0.0004 | 0.0034 | 0.0011 | -0.0006 | 0.0137 | 0.0063 | -0.0088 | -360.0911 | 17.7169 | -360.6573 | 18.0331 | -361.0143 | 18.1502 | -360.9897 | 17.5075 | -352.9583 | 18.7538 | -353.0106 | 16.8525
11:27 | 462 | 18.0781 | 191.7978 | 432.9779 | 437.8905 | -20.8909 | -48.309 | 0.3163 | -0.7425 | -8.1571 | -8.4036 | -3.6518 | -4.445 | 1.389 | -5.4765 | 0.5781 | 0.6064 | 0.9633 | 0.6864 | -132.9796 | -8.8265 | -1.9356 | -2.9355 | -10.9355 | -9.5906 | -1.8647 |  | -5.4813 | -4.8591 | 4.0663 | 3.3694 | 3.359 | 0.9347 | 10.5624 | 13.8854 | 14.5038 | 10.8295 | 0.0001 | -0.003 | 0.0007 | 0.0038 | 0.0009 | -0.0001 | 0.0018 | -0.0069 | -0.0093 | -360.045 | 17.7354 | -360.6881 | 18.0331 | -361.0112 | 18.1584 | -361.0174 | 17.526 | -352.946 | 18.7744 | -353.0291 | 16.8464
11:27 | 463 | 18.0719 | 191.7279 | 432.847 | 437.8705 | -20.9516 | -48.3137 | 0.3764 | -0.8258 | -8.1789 | -8.398 | -3.6856 | -4.3702 | 1.4328 | -5.5154 | 0.5789 | 0.6034 | 0.9629 | 0.6875 | -133.0321 | -8.8333 | -1.9769 | -2.9126 | -10.8869 | -9.6259 | -1.9119 |  | -5.437 | -4.9292 | 4.0653 | 3.3698 | 3.3565 | 0.9346 | 10.5786 | 13.9248 | 14.5209 | 10.8626 | -0.0002 | -0.0032 | 0.0008 | 0.0037 | 0.0007 | -0.0007 | 0.0056 | -0.0192 | 0.0151 | -360.1496 | 17.7334 | -360.6666 | 18.0106 | -360.9712 | 18.1584 | -361.0635 | 17.5609 | -353.0075 | 18.7846 | -353.0014 | 16.8258
11:27 | 464 | 18.0377 | 191.6402 | 432.9255 | 437.8822 | -20.8494 | -48.373 | 0.3921 | -0.8387 | -8.2788 | -8.3875 | -3.7712 | -4.3466 | 1.4113 | -5.4438 | 0.5781 | 0.6048 | 0.969 | 0.687 | -132.9311 | -8.7682 | -1.9528 | -2.8747 | -10.9038 | -9.587 | -1.7978 |  | -5.4995 | -4.9354 | 4.063 | 3.3702 | 3.356 | 0.9351 | 10.5729 | 13.9247 | 14.5314 | 10.8515 | -0.0004 | -0.0031 | 0.0006 | 0.0039 | 0.0003 | -0.0001 | -0.0068 | -0.0033 | 0.0088 | -360.1681 | 17.7498 | -360.645 | 17.99 | -360.9466 | 18.1379 | -361.0297 | 17.565 | -353.026 | 18.7785 | -352.9952 | 16.8012
11:27 | 465 | 18.026 | 191.6829 | 432.8601 | 437.862 | -20.8899 | -48.47 | 0.2241 | -0.7974 | -8.165 | -8.3148 | -3.7159 | -4.3196 | 1.41 | -5.472 | 0.5777 | 0.6055 | 0.967 | 0.6871 | -132.9304 | -8.6664 | -1.842 | -2.8879 | -10.786 | -9.6107 | -1.8071 |  | -5.4084 | -4.8655 | 4.0656 | 3.3723 | 3.3567 | 0.9365 | 10.5864 | 13.945 | 14.5335 | 10.8459 | 0 | -0.0022 | 0.0012 | 0.0042 | 0.0012 | -0.0006 | 0.0091 | -0.0082 | -0.0045 | -360.1342 | 17.7436 | -360.645 | 17.9982 | -360.9158 | 18.1543 | -361.0051 | 17.5527 | -353.0106 | 18.7826 | -352.9891 | 16.8094
11:27 | 466 | 18.009 | 191.6638 | 432.8784 | 437.9859 | -20.8647 | -48.4618 | 0.2907 | -0.8075 | -8.1226 | -8.2154 | -3.6186 | -4.2715 | 1.4124 | -5.4547 | 0.5788 | 0.6065 | 0.9631 | 0.6881 | -132.9914 | -8.6968 | -1.8777 | -2.8949 | -10.8298 | -9.6449 | -1.7549 |  | -5.4147 | -4.8162 | 4.0636 | 3.3732 | 3.3584 | 0.9363 | 10.5451 | 13.9199 | 14.5202 | 10.8414 | 0.0001 | -0.0029 | 0.0005 | 0.0032 | 0.0003 | -0.0009 | 0.0105 | -0.0069 | -0.0175 | -360.1188 | 17.7436 | -360.7066 | 18.0516 | -361.0235 | 18.181 | -361.0358 | 17.5363 | -352.9891 | 18.7887 | -353.0291 | 16.8464
11:27 | 467 | 17.988 | 191.7034 | 432.9123 | 437.9747 | -20.8997 | -48.3554 | 0.3425 | -0.812 | -8.187 | -8.3264 | -3.7498 | -4.313 | 1.3935 | -5.4351 | 0.5781 | 0.6038 | 0.9635 | 0.6877 | -133.0178 | -8.6697 | -1.8689 | -2.8944 | -11.0166 | -9.59 | -1.8004 |  | -5.4741 | -4.7744 | 4.0639 | 3.367 | 3.3555 | 0.9361 | 10.5567 | 13.9257 | 14.4796 | 10.8472 | 0 | -0.0031 | 0.0007 | 0.0038 | 0.0007 | -0.0008 | 0.0047 | 0.0026 | -0.0206 | -360.0634 | 17.7128 | -360.685 | 18.0557 | -361.0328 | 18.1769 | -361.0297 | 17.5178 | -352.9552 | 18.7661 | -352.9952 | 16.8566
11:28 | 468 | 17.914 | 191.7283 | 432.9123 | 438.0089 | -20.8326 | -48.4007 | 0.2917 | -0.6956 | -8.1954 | -8.4358 | -3.7509 | -4.2843 | 1.4303 | -5.549 | 0.5792 | 0.6057 | 0.9629 | 0.6889 | -132.9622 | -8.8029 | -1.935 | -2.8919 | -10.8579 | -9.5913 | -1.8274 |  | -5.4909 | -4.8046 | 4.0632 | 3.3738 | 3.3604 | 0.938 | 10.5705 | 13.9166 | 14.5066 | 10.8201 | 0 | -0.0026 | 0.0008 | 0.0039 | 0.0004 | -0.0009 | 0.0042 | 0.0051 | -0.0072 | -360.085 | 17.7272 | -360.642 | 18.0208 | -360.9897 | 18.1769 | -361.0235 | 17.526 | -352.9491 | 18.7682 | -352.9983 | 16.834
11:28 | 469 | 17.9551 | 191.6813 | 432.9578 | 437.9556 | -20.7928 | -48.254 | 0.3891 | -0.7893 | -8.1596 | -8.3272 | -3.7922 | -4.2826 | 1.3799 | -5.5187 | 0.579 | 0.6078 | 0.9632 | 0.6861 | -132.8954 | -8.685 | -1.9819 | -2.8971 | -10.8562 | -9.6474 | -1.7992 |  | -5.4552 | -4.8749 | 4.0641 | 3.3687 | 3.3548 | 0.9373 | 10.5603 | 13.8884 | 14.4922 | 10.8169 | -0.0005 | -0.0027 | 0.0004 | 0.0033 | 0.0003 | -0.0008 | 0.0074 | -0.0163 | -0.016 | -360.165 | 17.7354 | -360.6696 | 18.0208 | -360.9651 | 18.181 | -361.0789 | 17.565 | -353.0291 | 18.7846 | -353.0229 | 16.832
11:28 | 470 | 17.9162 | 191.7024 | 433.0487 | 437.991 | -20.8911 | -48.3073 | 0.324 | -0.72 | -8.1863 | -8.3455 | -3.6954 | -4.3209 | 1.3497 | -5.436 | 0.5791 | 0.6082 | 0.9624 | 0.6861 | -132.9184 | -8.7195 | -1.8824 | -2.9153 | -10.9033 | -9.5491 | -1.8432 |  | -5.4477 | -4.8365 | 4.0627 | 3.3712 | 3.3578 | 0.9393 | 10.5369 | 13.8947 | 14.5079 | 10.8211 | 0.0003 | -0.0023 | 0.0002 | 0.0036 | 0.0011 | -0.0007 | 0.0068 | -0.0077 | -0.0024 | -360.1681 | 17.7375 | -360.6327 | 18.0106 | -360.9281 | 18.1584 | -361.042 | 17.5568 | -353.0137 | 18.7764 | -352.9675 | 16.8032
11:28 | 471 | 17.9891 | 191.7837 | 433.0859 | 437.9531 | -20.8731 | -48.3733 | 0.2777 | -0.7347 | -8.2137 | -8.3769 | -3.6268 | -4.2579 | 1.4048 | -5.4307 | 0.578 | 0.6077 | 0.962 | 0.6861 | -132.8856 | -8.7556 | -1.9176 | -2.836 | -10.9428 | -9.6923 | -1.7719 |  | -5.3143 | -4.7799 | 4.064 | 3.3709 | 3.3577 | 0.938 | 10.5428 | 13.9235 | 14.5185 | 10.8446 | -0.0001 | -0.0032 | 0.0004 | 0.0036 | 0.0002 | -0.0007 | 0.0048 | -0.0072 | -0.014 | -360.1404 | 17.7313 | -360.645 | 17.9982 | -360.9312 | 18.1645 | -361.0143 | 17.526 | -352.9891 | 18.7805 | -352.986 | 16.8156
11:28 | 472 | 18.0203 | 191.7895 | 433.1126 | 438.1203 | -20.886 | -48.3475 | 0.3017 | -0.6931 | -8.2374 | -8.4032 | -3.6762 | -4.3076 | 1.404 | -5.4623 | 0.5786 | 0.6058 | 0.9638 | 0.6863 | -132.9536 | -8.8319 | -1.998 | -2.9114 | -10.9621 | -9.7834 | -1.806 |  | -5.4382 | -4.956 | 4.0624 | 3.3667 | 3.3576 | 0.938 | 10.5774 | 13.9352 | 14.5427 | 10.8327 | -0.0002 | -0.0032 | 0.0009 | 0.0036 | 0.0008 | -0.0008 | -0.0014 | -0.0095 | -0.018 | -360.1219 | 17.7395 | -360.7127 | 18.0516 | -361.0143 | 18.1789 | -361.0543 | 17.5239 | -352.9921 | 18.7785 | -353.026 | 16.8546
11:28 | 473 | 18.0164 | 191.85 | 433.1002 | 438.1045 | -20.843 | -48.3838 | 0.4546 | -0.7594 | -8.2317 | -8.3677 | -3.6308 | -4.276 | 1.4028 | -5.4093 | 0.5783 | 0.6042 | 0.9605 | 0.687 | -132.9289 | -8.7229 | -1.9953 | -3.0938 | -10.9433 | -9.6762 | -1.7992 |  | -5.3613 | -4.829 | 4.0633 | 3.3706 | 3.3578 | 0.9387 | 10.5601 | 13.9293 | 14.5127 | 10.8331 | -0.0003 | -0.0028 | 0.0006 | 0.0038 | 0.0006 | -0.0003 | 0.0013 | 0.0045 | -0.0153 | -360.085 | 17.719 | -360.682 | 18.0496 | -361.0204 | 18.183 | -361.0112 | 17.5034 | -352.9367 | 18.7764 | -352.986 | 16.8525
11:28 | 474 | 17.8673 | 191.794 | 433.1225 | 438.0214 | -20.8442 | -48.3021 | 0.4583 | -0.7421 | -8.2338 | -8.4024 | -3.6601 | -4.2678 | 1.4132 | -5.353 | 0.5782 | 0.6076 | 0.9618 | 0.6875 | -132.9642 | -8.7235 | -1.938 | -3.1274 | -11.0487 | -9.834 | -1.8809 |  | -5.4123 | -4.8945 | 4.0639 | 3.3693 | 3.3593 | 0.9378 | 10.5741 | 13.8968 | 14.5202 | 10.8356 | -0.0006 | -0.0026 | 0.0006 | 0.0036 | 0.0009 | -0.0004 | 0.0118 | -0.0076 | -0.0148 | -360.0911 | 17.7293 | -360.6543 | 18.027 | -360.9743 | 18.1769 | -360.9989 | 17.5055 | -352.9675 | 18.7764 | -352.986 | 16.8258
11:28 | 475 | 17.9544 | 191.8198 | 433.1265 | 438.0925 | -20.7913 | -48.3366 | 0.4799 | -0.7238 | -8.2275 | -8.3661 | -3.662 | -4.1797 | 1.3951 | -5.3079 | 0.5791 | 0.6098 | 0.9641 | 0.6868 | -132.9175 | -8.7818 | -1.8771 | -3.0763 | -10.9927 | -9.7664 | -1.8952 |  | -5.4607 | -4.867 | 4.0628 | 3.3711 | 3.3576 | 0.9395 | 10.5613 | 13.9247 | 14.5256 | 10.8342 | -0.0001 | -0.0031 | 0.0007 | 0.0032 | 0.0006 | -0.0002 | 0.0038 | 0.0038 | -0.0187 | -360.1465 | 17.7334 | -360.6512 | 18.029 | -360.9681 | 18.1769 | -361.042 | 17.5486 | -352.986 | 18.7805 | -352.986 | 16.8361
11:28 | 476 | 17.9294 | 191.8706 | 433.1614 | 438.0982 | -20.9102 | -48.374 | 0.3745 | -0.7122 | -8.2703 | -8.3709 | -3.6647 | -4.2909 | 1.3112 | -5.4226 | 0.5783 | 0.608 | 0.9633 | 0.6858 | -132.8718 | -8.7919 | -1.7532 | -3.048 | -10.9411 | -9.6649 | -1.8847 |  | -5.5097 | -4.8953 | 4.0627 | 3.3706 | 3.3567 | 0.9406 | 10.5246 | 13.8697 | 14.483 | 10.8109 | -0.0004 | -0.004 | 0.0001 | 0.0035 | 0.0001 | -0.001 | 0.0014 | -0.0014 | 0.0065 | -360.1835 | 17.7293 | -360.6573 | 18.0085 | -360.9251 | 18.1707 | -361.0789 | 17.5568 | -353.0014 | 18.7846 | -352.9768 | 16.8053
11:28 | 477 | 17.9441 | 191.8432 | 433.2008 | 438.1039 | -20.8608 | -48.4063 | 0.4228 | -0.7391 | -8.2775 | -8.3415 | -3.7888 | -4.2585 | 1.2382 | -5.3759 | 0.5795 | 0.6062 | 0.9637 | 0.6872 | -132.8369 | -8.7753 | -1.8443 | -3.0239 | -10.9219 | -9.7423 | -1.8781 |  | -5.5289 | -4.9096 | 4.0614 | 3.3693 | 3.357 | 0.9412 | 10.5532 | 13.9107 | 14.4939 | 10.8031 | -0.0004 | -0.003 | 0.0007 | 0.0036 | 0.0006 | -0.0005 | 0.0088 | -0.0019 | 0.0031 | -360.1281 | 17.7293 | -360.642 | 18.0064 | -360.9281 | 18.183 | -361.0174 | 17.5178 | -352.9798 | 18.7867 | -352.9706 | 16.8094
11:28 | 478 | 17.9429 | 191.7575 | 433.08 | 437.9917 | -20.9278 | -48.3311 | 0.4132 | -0.7986 | -8.2238 | -8.3037 | -3.712 | -4.2838 | 1.4071 | -5.3356 | 0.5784 | 0.6058 | 0.9613 | 0.6863 | -132.7673 | -8.7956 | -1.7676 | -2.9984 | -10.9551 | -9.6421 | -1.7841 |  | -5.47 | -4.8963 | 4.0623 | 3.37 | 3.3593 | 0.94 | 10.5694 | 13.9153 | 14.4926 | 10.8483 | -0.0004 | -0.0028 | 0.0008 | 0.0038 | 0.0003 | -0.0006 | 0.0013 | -0.0095 | -0.0013 | -360.125 | 17.7272 | -360.645 | 18.0372 | -360.9897 | 18.1604 | -361.0235 | 17.5239 | -352.9644 | 18.7764 | -352.9983 | 16.8484
11:28 | 479 | 17.9372 | 191.7669 | 433.2176 | 438.0546 | -20.9136 | -48.2895 | 0.3638 | -0.7647 | -8.2073 | -8.3343 | -3.7052 | -4.3899 | 1.2961 | -5.4159 | 0.5786 | 0.6096 | 0.961 | 0.6883 | -132.8502 | -8.694 | -1.7123 | -3.0127 | -10.9351 | -9.7266 | -1.8064 |  | -5.4175 | -4.9208 | 4.0631 | 3.3698 | 3.3593 | 0.9394 | 10.5717 | 13.9294 | 14.5079 | 10.85 | -0.0002 | -0.0026 | 0.0007 | 0.0037 | 0.0008 | -0.001 | 0.0109 | 0.0008 | -0.0138 | -360.1004 | 17.7293 | -360.7066 | 18.0475 | -361.0266 | 18.1645 | -360.9958 | 17.5239 | -352.9768 | 18.7928 | -353.0445 | 16.8484
11:28 | 480 | 17.9155 | 191.7901 | 433.1328 | 438.0846 | -20.8372 | -48.3115 | 0.4627 | -0.7584 | -8.2656 | -8.3484 | -3.6712 | -4.2776 | 1.3144 | -5.4054 | 0.5783 | 0.6091 | 0.9664 | 0.6868 | -132.7795 | -8.6844 | -1.7758 | -2.9566 | -11.0088 | -9.6912 | -1.768 |  | -5.4412 | -4.8722 | 4.0621 | 3.3715 | 3.3625 | 0.9407 | 10.5887 | 13.9531 | 14.5594 | 10.8885 | 0.0003 | -0.0027 | 0.001 | 0.0042 | 0.0004 | -0.0004 | 0.0049 | -0.0135 | -0.0103 | -360.1127 | 17.7416 | -360.6912 | 18.0188 | -360.9743 | 18.181 | -361.0574 | 17.5219 | -352.9491 | 18.7846 | -353.0229 | 16.8299
11:28 | 481 | 17.9062 | 191.8652 | 433.2441 | 438.1517 | -20.865 | -48.3938 | 0.3476 | -0.684 | -8.1778 | -8.2964 | -3.7516 | -4.3226 | 1.3398 | -5.3736 | 0.5773 | 0.6071 | 0.9615 | 0.6868 | -132.756 | -8.6906 | -1.7492 | -3.0288 | -11.0393 | -9.7654 | -1.8586 |  | -5.4025 | -4.7623 | 4.0613 | 3.3707 | 3.357 | 0.9411 | 10.6018 | 13.9304 | 14.5546 | 10.8515 | -0.0011 | -0.0036 | 0.0004 | 0.0034 | 0.0006 | -0.0011 | 0.0104 | -0.0041 | -0.0259 | -360.0911 | 17.7149 | -360.6235 | 18.0167 | -360.9958 | 18.1666 | -360.9989 | 17.5342 | -352.9891 | 18.7682 | -352.986 | 16.8197
11:28 | 482 | 17.9123 | 191.7694 | 433.3022 | 438.0851 | -20.9056 | -48.43 | 0.329 | -0.6972 | -8.1674 | -8.2362 | -3.6206 | -4.3712 | 1.2859 | -5.453 | 0.5779 | 0.6094 | 0.962 | 0.6862 | -132.7642 | -8.6187 | -1.7592 | -3.0224 | -10.988 | -9.7373 | -1.868 |  | -5.4177 | -4.8029 | 4.06 | 3.3693 | 3.3584 | 0.9401 | 10.5877 | 13.94 | 14.5549 | 10.8539 | -0.0001 | -0.0025 | 0.0009 | 0.0035 | 0.0003 | -0.0005 | 0.0022 | -0.0102 | -0.0122 | -360.125 | 17.7149 | -360.645 | 18.0208 | -360.9681 | 18.1728 | -361.0512 | 17.5465 | -352.9983 | 18.7661 | -352.9921 | 16.8197
11:28 | 483 | 17.9186 | 191.7601 | 433.1637 | 438.144 | -20.9182 | -48.3561 | 0.3003 | -0.7324 | -8.1805 | -8.2956 | -3.5725 | -4.3653 | 1.2526 | -5.3864 | 0.5774 | 0.6075 | 0.9612 | 0.6872 | -132.737 | -8.6817 | -1.8404 | -2.9628 | -11.0488 | -9.7312 | -1.8588 |  | -5.4205 | -4.7609 | 4.0602 | 3.3703 | 3.3562 | 0.9408 | 10.5786 | 13.9247 | 14.5198 | 10.811 | -0.0003 | -0.0024 | 0.0004 | 0.0033 | 0.0006 | -0.0009 | 0.0084 | -0.001 | 0.0008 | -360.1342 | 17.7354 | -360.6973 | 18.029 | -360.9651 | 18.183 | -361.0512 | 17.5404 | -352.9798 | 18.7908 | -353.0044 | 16.8299
11:28 | 484 | 17.8738 | 191.7382 | 433.2069 | 438.0863 | -20.9592 | -48.4752 | 0.401 | -0.8154 | -8.2738 | -8.4148 | -3.6517 | -4.2871 | 1.3068 | -5.4364 | 0.5782 | 0.61 | 0.9628 | 0.6888 | -132.8098 | -8.6711 | -1.82 | -2.8065 | -11.0312 | -9.6759 | -1.8432 |  | -5.3029 | -4.7527 | 4.0604 | 3.3716 | 3.3602 | 0.9423 | 10.5603 | 13.9058 | 14.5153 | 10.8054 | -0.0003 | -0.0031 | 0.0007 | 0.0034 | 0.0006 | -0.0007 | 0.023 | -0.0088 | -0.0037 | -360.1619 | 17.7128 | -360.645 | 18.0188 | -360.9435 | 18.1522 | -361.0112 | 17.5157 | -352.9398 | 18.7764 | -352.9952 | 16.8135
11:28 | 485 | 17.9374 | 191.8079 | 433.3804 | 438.1753 | -21.0305 | -48.4129 | 0.3423 | -0.7238 | -8.2458 | -8.4004 | -3.5759 | -4.3446 | 1.286 | -5.4011 | 0.5791 | 0.6101 | 0.9587 | 0.6872 | -132.7875 | -8.6774 | -1.8007 | -2.875 | -10.9855 | -9.7247 | -1.781 |  | -5.4406 | -4.735 | 4.0601 | 3.3703 | 3.3553 | 0.9419 | 10.5231 | 13.898 | 14.4463 | 10.7905 | 0.0002 | -0.0031 | 0.0007 | 0.0038 | 0.0006 | -0.0008 | 0.0011 | -0.0075 | -0.022 | -360.125 | 17.7334 | -360.6573 | 18.0352 | -360.9897 | 18.181 | -361.0112 | 17.5239 | -352.9983 | 18.7969 | -352.9983 | 16.832
11:28 | 486 | 17.989 | 191.8149 | 433.3357 | 438.1943 | -21.0043 | -48.379 | 0.3082 | -0.6804 | -8.2072 | -8.3681 | -3.5805 | -4.3121 | 1.3051 | -5.4032 | 0.5787 | 0.6105 | 0.962 | 0.6865 | -132.6967 | -8.6406 | -1.7566 | -2.8364 | -11.0617 | -9.7613 | -1.8593 |  | -5.4168 | -4.7856 | 4.0596 | 3.3694 | 3.3577 | 0.9432 | 10.5636 | 13.927 | 14.511 | 10.8363 | -0.0002 | -0.0027 | 0.0004 | 0.0038 | 0.0006 | -0.001 | 0.0144 | -0.0066 | -0.0027 | -360.0881 | 17.7293 | -360.682 | 18.0331 | -360.9681 | 18.1728 | -361.0358 | 17.5383 | -352.9675 | 18.7826 | -352.9921 | 16.8258
11:28 | 487 | 17.9443 | 191.7646 | 433.3521 | 438.1997 | -21.0174 | -48.5009 | 0.2458 | -0.6786 | -8.2801 | -8.3972 | -3.6608 | -4.2575 | 1.277 | -5.448 | 0.5787 | 0.6116 | 0.9609 | 0.6874 | -132.7703 | -8.5751 | -1.7213 | -2.8464 | -10.9286 | -9.6449 | -1.8105 |  | -5.4522 | -4.8975 | 4.0607 | 3.3779 | 3.3616 | 0.9444 | 10.5625 | 13.8968 | 14.5028 | 10.8298 | -0.0001 | -0.0025 | 0.0006 | 0.0037 | 0.0008 | -0.0002 | 0.0091 | -0.0085 | 0.0038 | -360.1034 | 17.7231 | -360.6543 | 18.0167 | -360.9651 | 18.1604 | -361.0204 | 17.5239 | -352.9306 | 18.7723 | -352.9952 | 16.8197
11:28 | 488 | 17.9447 | 191.7879 | 433.4665 | 438.2472 | -21.1012 | -48.4512 | 0.2808 | -0.7729 | -8.2966 | -8.5093 | -3.7087 | -4.2224 | 1.3063 | -5.4787 | 0.579 | 0.608 | 0.9609 | 0.6878 | -132.7923 | -8.6594 | -1.676 | -2.8867 | -10.984 | -9.6921 | -1.8529 |  | -5.3887 | -4.79 | 4.0606 | 3.3693 | 3.3597 | 0.9428 | 10.6213 | 13.9563 | 14.5546 | 10.8698 | 0.0001 | -0.0028 | 0.0011 | 0.0041 | 0.0009 | -0.0006 | 0.0212 | 0.0054 | -0.0049 | -360.1219 | 17.7293 | -360.6358 | 18.0188 | -360.9651 | 18.183 | -361.0297 | 17.5363 | -352.9675 | 18.7867 | -352.9768 | 16.8176
11:28 | 489 | 17.9908 | 191.8826 | 433.4442 | 438.2381 | -21.047 | -48.4418 | 0.3335 | -0.6856 | -8.2144 | -8.441 | -3.6425 | -4.2548 | 1.3377 | -5.4779 | 0.5779 | 0.6108 | 0.9623 | 0.6851 | -132.7226 | -8.6698 | -1.7356 | -2.8887 | -10.9901 | -9.7543 | -1.8388 |  | -5.4203 | -4.8569 | 4.0593 | 3.3719 | 3.3628 | 0.9428 | 10.5752 | 13.9269 | 14.5331 | 10.8945 | 0.0004 | -0.0028 | 0.0004 | 0.0035 | 0.0003 | -0.0003 | 0.0006 | -0.0117 | -0.0225 | -360.1311 | 17.7252 | -360.6758 | 18.0352 | -360.9651 | 18.1707 | -361.0451 | 17.5465 | -352.9921 | 18.7928 | -353.0137 | 16.8361
11:28 | 490 | 17.9395 | 191.8812 | 433.5554 | 438.1845 | -20.9874 | -48.4681 | 0.3135 | -0.7087 | -8.22 | -8.4245 | -3.6296 | -4.2302 | 1.2932 | -5.3789 | 0.5785 | 0.6124 | 0.9612 | 0.6871 | -132.7276 | -8.5904 | -1.7953 | -2.9578 | -11.0275 | -9.7492 | -1.8363 |  | -5.3626 | -4.655 | 4.0593 | 3.3691 | 3.3604 | 0.9427 | 10.5682 | 13.926 | 14.5512 | 10.8291 | -0.0002 | -0.003 | 0.0009 | 0.0037 | 0.0007 | -0.0011 | 0.0103 | -0.0029 | 0.0021 | -360.125 | 17.7108 | -360.6543 | 18.0352 | -360.9374 | 18.1563 | -361.0266 | 17.5116 | -352.9367 | 18.7826 | -353.0014 | 16.8299
11:28 | 491 | 18.0116 | 191.8475 | 433.3663 | 438.1869 | -21.0239 | -48.4171 | 0.3789 | -0.77 | -8.2432 | -8.367 | -3.6759 | -4.1335 | 1.3583 | -5.3493 | 0.5799 | 0.6106 | 0.9583 | 0.6885 | -132.8731 | -8.6878 | -1.8235 | -2.9084 | -11.0291 | -9.7596 | -1.8301 |  | -5.387 | -4.8069 | 4.0607 | 3.3712 | 3.3596 | 0.9452 | 10.589 | 13.9178 | 14.5311 | 10.85 | -0.0002 | -0.0021 | 0.0005 | 0.0032 | 0.0004 | -0.0003 | 0.0125 | 0.0049 | 0.0063 | -360.0973 | 17.7313 | -360.6604 | 18.0208 | -360.9866 | 18.1728 | -360.9989 | 17.5075 | -352.9491 | 18.8031 | -353.0075 | 16.8197
11:28 | 492 | 17.9859 | 191.905 | 433.5087 | 438.1113 | -21.0879 | -48.512 | 0.3487 | -0.7425 | -8.2554 | -8.3678 | -3.6789 | -4.1614 | 1.3764 | -5.3857 | 0.5781 | 0.6139 | 0.9648 | 0.6875 | -132.8347 | -8.7681 | -1.7794 | -2.9225 | -11.1191 | -9.7027 | -1.8388 |  | -5.3527 | -4.7757 | 4.0581 | 3.3721 | 3.3573 | 0.9433 | 10.5626 | 13.8967 | 14.5075 | 10.8245 | -0.0004 | -0.0025 | 0.0007 | 0.0037 | 0.0005 | -0.0007 | 0.0136 | -0.0136 | -0.0064 | -360.1435 | 17.7108 | -360.6666 | 18.0311 | -360.9804 | 18.1871 | -361.0297 | 17.5321 | -352.9952 | 18.799 | -352.9983 | 16.8299
11:28 | 493 | 17.9802 | 191.9162 | 433.4824 | 438.255 | -20.9598 | -48.375 | 0.3342 | -0.7092 | -8.2059 | -8.2784 | -3.6886 | -4.2271 | 1.3412 | -5.3925 | 0.5786 | 0.6132 | 0.9615 | 0.6871 | -132.797 | -8.6909 | -1.7939 | -2.8444 | -11.1183 | -9.7171 | -1.8706 |  | -5.4142 | -4.7726 | 4.0585 | 3.3683 | 3.3584 | 0.9452 | 10.566 | 13.8829 | 14.4711 | 10.793 | -0.0001 | -0.0033 | 0.0008 | 0.0039 | 0.0005 | -0.0008 | 0.0046 | -0.0103 | 0.0184 | -360.165 | 17.7169 | -360.5927 | 18.0208 | -360.9989 | 18.1871 | -361.0574 | 17.5506 | -353.0137 | 18.7723 | -352.9675 | 16.8299
11:28 | 494 | 18.0289 | 191.8697 | 433.522 | 438.2375 | -20.9027 | -48.3714 | 0.4211 | -0.7087 | -8.2489 | -8.3774 | -3.6938 | -4.2154 | 1.3394 | -5.3829 | 0.5786 | 0.6161 | 0.966 | 0.6879 | -132.8051 | -8.7677 | -1.8326 | -2.8305 | -11.0267 | -9.6717 | -1.7996 |  | -5.369 | -4.8012 | 4.0582 | 3.3715 | 3.3581 | 0.9448 | 10.5638 | 13.9267 | 14.5079 | 10.8259 | 0.0001 | -0.0031 | 0.0005 | 0.0034 | -0.0001 | -0.0008 | 0.0163 | -0.0046 | -0.0275 | -360.1219 | 17.6944 | -360.6173 | 17.9941 | -360.922 | 18.1687 | -361.0635 | 17.5301 | -352.9644 | 18.7682 | -352.9398 | 16.795
11:28 | 495 | 17.9792 | 191.9256 | 433.3974 | 438.2481 | -20.9304 | -48.2615 | 0.3936 | -0.8182 | -8.2619 | -8.2778 | -3.6774 | -4.1257 | 1.4357 | -5.3382 | 0.5805 | 0.6119 | 0.9647 | 0.6864 | -132.7033 | -8.6841 | -1.874 | -2.8279 | -11.0163 | -9.663 | -1.738 |  | -5.4193 | -4.8287 | 4.0573 | 3.3711 | 3.3606 | 0.9441 | 10.5521 | 13.8979 | 14.4742 | 10.8486 | -0.0006 | -0.0031 | 0.0007 | 0.004 | 0.001 | -0.0011 | 0.0181 | -0.0171 | 0.0048 | -360.1435 | 17.7334 | -360.6543 | 18.0229 | -360.9527 | 18.1707 | -361.0266 | 17.5363 | -352.9798 | 18.7949 | -353.0106 | 16.8197
11:28 | 496 | 17.9526 | 191.9445 | 433.4697 | 438.2172 | -20.8531 | -48.287 | 0.3987 | -0.8284 | -8.2369 | -8.2697 | -3.6837 | -4.2391 | 1.354 | -5.4568 | 0.5775 | 0.6134 | 0.9627 | 0.6861 | -132.7341 | -8.6927 | -1.8964 | -2.8109 | -11.0404 | -9.6509 | -1.7775 |  | -5.3995 | -4.8723 | 4.0593 | 3.3719 | 3.3598 | 0.9448 | 10.5866 | 13.9099 | 14.5362 | 10.8413 | -0.0003 | -0.0026 | 0.0008 | 0.004 | 0.0006 | -0.0004 | 0.0096 | -0.0121 | -0.0181 | -360.0973 | 17.7149 | -360.6881 | 18.0496 | -361.0328 | 18.1666 | -360.9743 | 17.5055 | -352.9244 | 18.7764 | -353.0229 | 16.8525
11:28 | 497 | 17.9214 | 191.8998 | 433.4424 | 438.2487 | -21.0976 | -48.4113 | 0.3872 | -0.853 | -8.1954 | -8.4141 | -3.7363 | -4.2479 | 1.3549 | -5.4717 | 0.5796 | 0.6086 | 0.9596 | 0.6871 | -132.6938 | -8.6714 | -1.9084 | -2.9883 | -11.093 | -9.7268 | -1.8905 |  | -5.3659 | -4.8492 | 4.0582 | 3.3691 | 3.3607 | 0.9463 | 10.5936 | 13.9225 | 14.5423 | 10.8717 | 0.0001 | -0.0027 | 0.0001 | 0.0032 | 0.001 | -0.0005 | 0.0105 | -0.0059 | -0.0073 | -360.0511 | 17.7067 | -360.685 | 18.0434 | -360.9897 | 18.1728 | -361.0143 | 17.5034 | -352.9583 | 18.7928 | -352.986 | 16.8361
11:28 | 498 | 17.9468 | 191.91 | 433.471 | 438.2843 | -21.0273 | -48.4196 | 0.3335 | -0.7837 | -8.1813 | -8.3348 | -3.7016 | -4.2449 | 1.3299 | -5.4065 | 0.5783 | 0.6151 | 0.959 | 0.686 | -132.7381 | -8.7555 | -1.8891 | -3.0941 | -11.1552 | -9.6858 | -1.8756 |  | -5.3422 | -4.8693 | 4.0578 | 3.3728 | 3.3633 | 0.9469 | 10.5672 | 13.884 | 14.512 | 10.8349 | -0.0003 | -0.0035 | 0.0009 | 0.0036 | 0.0004 | -0.0004 | 0.0028 | -0.0061 | 0.0026 | -360.1558 | 17.7108 | -360.6481 | 18.0311 | -360.9589 | 18.181 | -361.0666 | 17.5445 | -352.986 | 18.7785 | -352.9737 | 16.8156
11:28 | 499 | 17.9978 | 191.9444 | 433.4513 | 438.3136 | -21.0149 | -48.4725 | 0.3522 | -0.8077 | -8.1937 | -8.2907 | -3.673 | -4.2114 | 1.3532 | -5.4689 | 0.58 | 0.613 | 0.9597 | 0.6864 | -132.8181 | -8.8241 | -1.925 | -3.1589 | -11.0978 | -9.7322 | -1.8466 |  | -5.4242 | -4.8602 | 4.0588 | 3.3723 | 3.3619 | 0.9473 | 10.5924 | 13.9562 | 14.5941 | 10.8644 | -0.0001 | -0.0027 | 0.0007 | 0.0031 | 0.0009 | -0.0005 | -0.0058 | 0.0071 | -0.0051 | -360.1527 | 17.7046 | -360.6266 | 17.9921 | -360.9466 | 18.1502 | -361.0481 | 17.5486 | -353.026 | 18.7949 | -352.9583 | 16.7909
11:28 | 500 | 17.9203 | 191.8999 | 433.4457 | 438.307 | -21.0401 | -48.4642 | 0.4004 | -0.7946 | -8.2719 | -8.3527 | -3.7254 | -4.2166 | 1.4371 | -5.451 | 0.5792 | 0.6124 | 0.9581 | 0.6868 | -132.807 | -8.7501 | -1.8887 | -2.8315 | -11.0779 | -9.6934 | -1.8797 |  | -5.4462 | -4.8467 | 4.059 | 3.3732 | 3.3606 | 0.9469 | 10.5672 | 13.9302 | 14.5062 | 10.8176 | -0.0009 | -0.0029 | 0.0006 | 0.0035 | 0.0003 | -0.0005 | 0.0076 | -0.0094 | -0.0107 | -360.1435 | 17.721 | -360.6543 | 17.9962 | -360.9066 | 18.1645 | -361.0112 | 17.5404 | -353.0321 | 18.7887 | -352.9829 | 16.7991
11:28 | 501 | 17.9473 | 191.9079 | 433.4209 | 438.3504 | -21.0756 | -48.3543 | 0.4636 | -0.8583 | -8.2535 | -8.3077 | -3.6482 | -4.2436 | 1.4425 | -5.4355 | 0.5782 | 0.6099 | 0.9594 | 0.6863 | -132.7611 | -8.7845 | -1.8737 | -2.8866 | -11.1007 | -9.8132 | -1.9097 |  | -5.3646 | -4.7456 | 4.0568 | 3.3732 | 3.3601 | 0.9483 | 10.5867 | 13.8981 | 14.4994 | 10.8305 | -0.0001 | -0.0029 | 0.001 | 0.0036 | 0.0008 | -0.0008 | 0.0084 | -0.0021 | -0.006 | -360.1127 | 17.719 | -360.6881 | 18.0414 | -361.0081 | 18.1769 | -361.0328 | 17.5301 | -352.9675 | 18.7887 | -353.0383 | 16.8443
11:28 | 502 | 17.9435 | 192.0071 | 433.5966 | 438.303 | -21.0402 | -48.4251 | 0.4157 | -0.8543 | -8.1778 | -8.4551 | -3.6302 | -4.2087 | 1.4856 | -5.3671 | 0.5786 | 0.6115 | 0.9609 | 0.6865 | -132.7562 | -8.7439 | -1.931 | -2.877 | -11.1405 | -9.7787 | -1.9453 |  | -5.4164 | -4.8197 | 4.0567 | 3.3734 | 3.3608 | 0.9464 | 10.597 | 13.9145 | 14.5406 | 10.846 | 0.0001 | -0.0035 | 0.0008 | 0.0042 | 0.0011 | -0.0006 | 0.0285 | -0.0034 | 0.0072 | -360.0727 | 17.6923 | -360.645 | 18.0414 | -361.0235 | 18.1789 | -360.9958 | 17.5137 | -352.9152 | 18.762 | -352.986 | 16.834
11:28 | 503 | 18.0372 | 192.0625 | 433.5939 | 438.3584 | -20.9822 | -48.4441 | 0.3886 | -0.7712 | -8.1113 | -8.373 | -3.563 | -4.169 | 1.5525 | -5.3496 | 0.5797 | 0.6113 | 0.9598 | 0.6857 | -132.7056 | -8.7977 | -2.0069 | -2.9558 | -11.1231 | -9.7887 | -1.9522 |  | -5.3949 | -4.8808 | 4.0565 | 3.3724 | 3.3602 | 0.9464 | 10.6064 | 13.912 | 14.5658 | 10.8558 | -0.0002 | -0.0029 | 0.0003 | 0.0036 | 0.0001 | -0.001 | -0.0089 | -0.0129 | -0.0146 | -360.085 | 17.7026 | -360.6296 | 18.0208 | -360.9866 | 18.1871 | -361.042 | 17.5178 | -352.9614 | 18.7764 | -352.9583 | 16.8299
11:28 | 504 | 18.0076 | 192.0189 | 433.4855 | 438.3015 | -20.9954 | -48.4226 | 0.322 | -0.7939 | -8.2061 | -8.232 | -3.5957 | -4.2031 | 1.5171 | -5.339 | 0.5782 | 0.6112 | 0.9612 | 0.6872 | -132.7788 | -8.8498 | -1.9573 | -2.925 | -11.0658 | -9.7532 | -1.9298 |  | -5.3824 | -4.8294 | 4.0579 | 3.3707 | 3.3563 | 0.9479 | 10.5762 | 13.9169 | 14.5434 | 10.8655 | -0.0002 | -0.0026 | 0.0008 | 0.004 | 0.0011 | -0.0006 | 0.0059 | -0.0123 | -0.0156 | -360.1865 | 17.7293 | -360.6481 | 18.0126 | -360.9558 | 18.1707 | -361.0512 | 17.5547 | -352.9952 | 18.7887 | -352.9952 | 16.8074
11:28 | 505 | 17.8517 | 191.8934 | 433.3769 | 438.2674 | -21.13 | -48.4687 | 0.3012 | -0.8514 | -8.2644 | -8.383 | -3.6165 | -4.2428 | 1.4377 | -5.4535 | 0.578 | 0.6098 | 0.962 | 0.6884 | -132.751 | -8.704 | -1.8326 | -2.9074 | -11.0393 | -9.7933 | -1.9538 |  | -5.3448 | -4.8001 | 4.0573 | 3.3745 | 3.3626 | 0.9478 | 10.6064 | 13.9236 | 14.5427 | 10.8327 | -0.0002 | -0.0025 | -0.0001 | 0.0034 | 0.0004 | -0.0002 | 0.0342 | 0.0031 | 0.0094 | -360.1742 | 17.7293 | -360.642 | 17.9962 | -360.9343 | 18.144 | -360.9989 | 17.5445 | -353.0137 | 18.799 | -352.9706 | 16.8053
11:28 | 506 | 17.956 | 191.9435 | 433.4899 | 438.3445 | -21.1399 | -48.5701 | 0.2101 | -0.8365 | -8.1859 | -8.3596 | -3.6725 | -4.1926 | 1.4516 | -5.4131 | 0.5797 | 0.6134 | 0.9615 | 0.688 | -132.6943 | -8.8674 | -1.9663 | -2.9611 | -11.0188 | -9.7373 | -1.9453 |  | -5.3041 | -4.8498 | 4.0559 | 3.3738 | 3.3612 | 0.9472 | 10.5647 | 13.9051 | 14.5297 | 10.8143 | 0.0002 | -0.0026 | 0.0006 | 0.0036 | 0.0006 | -0.0008 | 0.0033 | -0.0092 | -0.0142 | -360.1558 | 17.721 | -360.645 | 18.0249 | -360.9774 | 18.1666 | -361.002 | 17.5342 | -352.986 | 18.7969 | -352.9829 | 16.8299
11:28 | 507 | 18.0115 | 191.9791 | 433.5127 | 438.4001 | -21.1548 | -48.4963 | 0.2946 | -0.8827 | -8.2591 | -8.458 | -3.6912 | -4.1911 | 1.4752 | -5.481 | 0.5801 | 0.6111 | 0.9616 | 0.6877 | -132.6342 | -8.7624 | -1.963 | -2.9144 | -11.0054 | -9.7635 | -1.9652 |  | -5.3769 | -4.8211 | 4.0546 | 3.3704 | 3.359 | 0.948 | 10.5994 | 13.9109 | 14.5529 | 10.8432 | 0.0003 | -0.0031 | 0.0013 | 0.0037 | 0.0007 | -0.0001 | 0.0012 | -0.0116 | 0.0001 | -360.0665 | 17.7149 | -360.6604 | 18.0311 | -360.9989 | 18.1974 | -361.0297 | 17.5178 | -352.9429 | 18.7764 | -352.9952 | 16.8402
11:28 | 508 | 17.9282 | 191.9839 | 433.5095 | 438.3278 | -21.1187 | -48.4873 | 0.256 | -0.7567 | -8.2206 | -8.4788 | -3.6278 | -4.1425 | 1.5583 | -5.4124 | 0.5783 | 0.6125 | 0.9627 | 0.6889 | -132.8032 | -8.8223 | -1.9358 | -2.9158 | -11.0527 | -9.7304 | -1.9985 |  | -5.2677 | -4.8165 | 4.0563 | 3.3738 | 3.3625 | 0.9482 | 10.574 | 13.9374 | 14.527 | 10.841 | -0.0004 | -0.0027 | 0.0008 | 0.0036 | 0.0009 | -0.0005 | 0.0135 | -0.0011 | -0.0277 | -360.0634 | 17.6841 | -360.6081 | 18.0188 | -361.0112 | 18.1769 | -361.002 | 17.5116 | -352.9183 | 18.7641 | -352.9337 | 16.8258
11:28 | 509 | 18.0699 | 192.113 | 433.698 | 438.4596 | -21.0439 | -48.3839 | 0.3223 | -0.7693 | -8.2584 | -8.3947 | -3.6762 | -4.1259 | 1.461 | -5.3425 | 0.5782 | 0.6086 | 0.9615 | 0.6866 | -132.752 | -8.7693 | -1.9671 | -2.9193 | -11.025 | -9.7044 | -1.9438 |  | -5.3224 | -4.8395 | 4.0557 | 3.3707 | 3.3574 | 0.9482 | 10.5475 | 13.9106 | 14.464 | 10.8093 | -0.0004 | -0.0026 | 0.0013 | 0.0041 | 0.0007 | -0.0006 | 0.0142 | -0.0066 | -0.0183 | -360.1219 | 17.7026 | -360.6573 | 18.027 | -360.9527 | 18.181 | -361.0604 | 17.5424 | -352.9891 | 18.7846 | -352.9552 | 16.8279
11:28 | 510 | 18.1172 | 192.165 | 433.7124 | 438.4658 | -21.144 | -48.332 | 0.3967 | -0.8103 | -8.1911 | -8.5735 | -3.667 | -4.113 | 1.5092 | -5.3111 | 0.5784 | 0.6098 | 0.9584 | 0.6849 | -132.67 | -8.7512 | -1.8541 | -2.7717 | -11.0686 | -9.7322 | -1.955 |  | -5.3493 | -4.8502 | 4.055 | 3.375 | 3.3585 | 0.9485 | 10.5636 | 13.927 | 14.482 | 10.8536 | 0.0001 | -0.0027 | 0.0006 | 0.0037 | 0.0006 | -0.0006 | 0.0029 | -0.0103 | -0.01 | -360.165 | 17.7395 | -360.682 | 18.0311 | -360.9435 | 18.1584 | -361.0297 | 17.5321 | -353.0075 | 18.8175 | -353.0168 | 16.8074
11:28 | 511 | 18.0092 | 192.0731 | 433.5677 | 438.3472 | -21.001 | -48.3422 | 0.4304 | -0.865 | -8.1695 | -8.4836 | -3.7003 | -4.1393 | 1.5549 | -5.3225 | 0.5781 | 0.6085 | 0.9594 | 0.6849 | -132.6901 | -8.7107 | -1.8784 | -2.7743 | -11.0416 | -9.7732 | -1.837 |  | -5.3114 | -4.6862 | 4.0546 | 3.3741 | 3.3592 | 0.9486 | 10.566 | 13.906 | 14.5232 | 10.845 | 0.0001 | -0.003 | 0.0004 | 0.0034 | 0.0008 | -0.001 | -0.0045 | 0.0011 | -0.0185 | -360.1896 | 17.7169 | -360.6389 | 18.0331 | -360.9897 | 18.1543 | -361.002 | 17.5445 | -352.986 | 18.7928 | -352.9921 | 16.8197
11:28 | 512 | 17.9362 | 191.9532 | 433.6241 | 438.3647 | -21.0139 | -48.3026 | 0.3901 | -0.8858 | -8.1873 | -8.47 | -3.6612 | -4.1385 | 1.4269 | -5.4275 | 0.5787 | 0.6133 | 0.9601 | 0.6863 | -132.6562 | -8.7099 | -1.8052 | -2.7337 | -11.065 | -9.7664 | -1.968 |  | -5.2911 | -4.8576 | 4.0562 | 3.3692 | 3.3575 | 0.9493 | 10.5867 | 13.9271 | 14.5294 | 10.8417 | 0 | -0.0031 | 0.0007 | 0.0039 | 0.0008 | -0.0001 | 0.0039 | -0.0064 | 0.0033 | -360.1034 | 17.7005 | -360.6727 | 18.0516 | -360.9712 | 18.1871 | -361.0543 | 17.5219 | -352.9644 | 18.7867 | -352.986 | 16.834
11:28 | 513 | 17.9921 | 191.9947 | 433.6866 | 438.3296 | -21.005 | -48.1661 | 0.4567 | -0.8804 | -8.2519 | -8.4957 | -3.6868 | -4.365 | 1.3202 | -5.5155 | 0.5796 | 0.6133 | 0.9624 | 0.6878 | -132.6559 | -8.8139 | -1.8017 | -2.7372 | -11.0022 | -9.8146 | -1.9958 |  | -5.3115 | -4.8897 | 4.0549 | 3.3748 | 3.3608 | 0.9502 | 10.6005 | 13.9179 | 14.5148 | 10.8554 | -0.0001 | -0.0021 | 0 | 0.0034 | 0.0009 | -0.0006 | 0.0036 | -0.0059 | -0.0012 | -360.1219 | 17.7005 | -360.6266 | 18.0331 | -361.0112 | 18.1892 | -361.0666 | 17.5239 | -352.9367 | 18.7744 | -352.9644 | 16.832
11:28 | 514 | 18.0257 | 192.0114 | 433.7646 | 438.3332 | -21.0372 | -48.2823 | 0.4077 | -0.8906 | -8.2739 | -8.4689 | -3.6537 | -4.2062 | 1.4281 | -5.4139 | 0.5792 | 0.6128 | 0.9619 | 0.6875 | -132.696 | -8.8161 | -1.8766 | -2.6896 | -10.9682 | -9.7726 | -1.9119 |  | -5.2983 | -4.8642 | 4.0555 | 3.3746 | 3.3613 | 0.9503 | 10.5799 | 13.9083 | 14.5018 | 10.8476 | -0.0001 | -0.0028 | 0.0007 | 0.0038 | -0.0002 | -0.0008 | -0.0006 | -0.0122 | -0.007 | -360.1096 | 17.7005 | -360.6327 | 18.029 | -360.9681 | 18.1748 | -361.0204 | 17.5383 | -352.9706 | 18.7723 | -352.9552 | 16.8258
11:28 | 515 | 17.9614 | 192.0144 | 433.7737 | 438.346 | -20.9691 | -48.2775 | 0.4325 | -0.8665 | -8.2713 | -8.3131 | -3.6554 | -4.2981 | 1.3706 | -5.4638 | 0.5769 | 0.6075 | 0.9614 | 0.6883 | -132.7851 | -8.7015 | -1.9498 | -2.5817 | -10.9083 | -9.6573 | -1.8865 |  | -5.3627 | -4.8727 | 4.0547 | 3.3743 | 3.3597 | 0.9508 | 10.5854 | 13.9378 | 14.5069 | 10.8398 | -0.0001 | -0.0032 | 0.0012 | 0.0039 | 0.0007 | -0.0006 | -0.0055 | -0.0071 | -0.0078 | -360.1527 | 17.7252 | -360.6543 | 18.0167 | -360.9681 | 18.1604 | -361.0143 | 17.528 | -352.9398 | 18.8031 | -352.9768 | 16.8115
11:28 | 516 | 17.9131 | 191.9701 | 433.7172 | 438.3362 | -21.0103 | -48.2034 | 0.4613 | -0.8102 | -8.2817 | -8.4088 | -3.6975 | -4.227 | 1.4017 | -5.4975 | 0.5795 | 0.6121 | 0.9599 | 0.687 | -132.8085 | -8.7236 | -2.0024 | -2.5968 | -10.8927 | -9.5772 | -1.8787 |  | -5.3575 | -4.8899 | 4.0553 | 3.3712 | 3.3598 | 0.9495 | 10.5891 | 13.935 | 14.5185 | 10.8562 | 0.0003 | -0.0029 | 0.0011 | 0.0035 | 0.0005 | -0.0004 | 0.0039 | -0.0075 | -0.0158 | -360.1496 | 17.7128 | -360.6573 | 18.0516 | -360.9558 | 18.1728 | -361.0204 | 17.5363 | -352.9644 | 18.8052 | -352.9798 | 16.8361
11:28 | 517 | 17.9005 | 191.8662 | 433.6924 | 438.3509 | -21.1572 | -48.4179 | 0.388 | -0.8089 | -8.2195 | -8.4759 | -3.656 | -4.2221 | 1.449 | -5.4179 | 0.5777 | 0.6125 | 0.9571 | 0.6887 | -132.7346 | -8.7484 | -1.985 | -2.6561 | -10.9909 | -9.71 | -1.8917 |  | -5.3893 | -4.8184 | 4.0572 | 3.3736 | 3.3588 | 0.9506 | 10.5903 | 13.9245 | 14.5072 | 10.823 | -0.0007 | -0.0029 | 0.0011 | 0.0042 | 0.0006 | -0.0006 | 0.0056 | -0.0072 | -0.0027 | -360.1435 | 17.721 | -360.6512 | 18.0393 | -360.9958 | 18.1871 | -361.0512 | 17.5404 | -352.9367 | 18.7826 | -352.9983 | 16.8299
11:28 | 518 | 17.9299 | 191.9666 | 433.7441 | 438.4142 | -21.149 | -48.4918 | 0.2999 | -0.9033 | -8.2071 | -8.4944 | -3.7856 | -4.1662 | 1.4397 | -5.3659 | 0.578 | 0.6142 | 0.9583 | 0.6865 | -132.7258 | -8.7501 | -1.8911 | -2.5896 | -10.9927 | -9.6947 | -1.8454 |  | -5.4113 | -4.9625 | 4.0559 | 3.3717 | 3.3596 | 0.9514 | 10.6017 | 13.9596 | 14.5451 | 10.8738 | -0.0003 | -0.0026 | 0.0008 | 0.0036 | 0.0008 | -0.0009 | 0.0008 | 0.0018 | -0.0093 | -360.0973 | 17.7087 | -360.6389 | 18.029 | -360.9558 | 18.181 | -361.0112 | 17.5239 | -352.9583 | 18.7846 | -352.9768 | 16.8217
11:28 | 519 | 17.8981 | 191.9221 | 433.6994 | 438.4562 | -21.2038 | -48.3823 | 0.3118 | -0.7671 | -8.197 | -8.4247 | -3.7501 | -4.1895 | 1.4062 | -5.4304 | 0.5788 | 0.6157 | 0.9592 | 0.6881 | -132.7059 | -8.7566 | -1.9214 | -2.5422 | -10.9778 | -9.6504 | -1.9513 |  | -5.3884 | -4.9588 | 4.0555 | 3.3719 | 3.36 | 0.9494 | 10.5742 | 13.9197 | 14.4949 | 10.8075 | -0.0004 | -0.0045 | -0.0001 | 0.0028 | -0.0002 | -0.0005 | 0.0121 | -0.012 | 0.0183 | -360.125 | 17.7005 | -360.642 | 18.0414 | -360.9774 | 18.1584 | -360.9989 | 17.5321 | -352.9337 | 18.7826 | -352.9583 | 16.832
11:28 | 520 | 17.9776 | 192.0277 | 433.7456 | 438.3958 | -21.1692 | -48.4786 | 0.2297 | -0.7921 | -8.1893 | -8.3974 | -3.6338 | -4.1771 | 1.4027 | -5.4577 | 0.5789 | 0.6177 | 0.9567 | 0.6869 | -132.7536 | -8.8098 | -1.927 | -2.6721 | -10.9992 | -9.6872 | -1.8672 |  | -5.4246 | -4.9056 | 4.054 | 3.372 | 3.3593 | 0.9513 | 10.589 | 13.889 | 14.5321 | 10.8438 | 0.0003 | -0.0032 | 0.0006 | 0.004 | 0.0014 | -0.0002 | 0.0183 | -0.0151 | -0.0036 | -360.1065 | 17.721 | -360.6666 | 18.0475 | -360.9681 | 18.1728 | -361.0328 | 17.528 | -352.9706 | 18.7969 | -352.9829 | 16.8258
11:28 | 521 | 18.0422 | 191.9307 | 433.7697 | 438.4642 | -21.157 | -48.4636 | 0.2354 | -0.7889 | -8.2133 | -8.382 | -3.7504 | -4.2008 | 1.4421 | -5.3207 | 0.5808 | 0.6141 | 0.9585 | 0.688 | -132.6787 | -8.7994 | -1.8951 | -2.7093 | -10.9582 | -9.6588 | -1.7918 |  | -5.3057 | -4.8947 | 4.0532 | 3.373 | 3.3601 | 0.9499 | 10.5983 | 13.9097 | 14.5341 | 10.8363 | -0.0004 | -0.0032 | 0.0009 | 0.0039 | 0.0007 | -0.0002 | -0.0063 | 0.0002 | -0.0067 | -360.1588 | 17.7087 | -360.6696 | 18.0393 | -360.9681 | 18.1789 | -361.002 | 17.5178 | -352.9583 | 18.7949 | -352.9768 | 16.8299
11:28 | 522 | 18.0288 | 191.948 | 433.7271 | 438.4798 | -21.2071 | -48.4931 | 0.2798 | -0.7472 | -8.2144 | -8.4147 | -3.7025 | -4.2222 | 1.4061 | -5.4205 | 0.5789 | 0.6112 | 0.9561 | 0.6866 | -132.6497 | -8.8009 | -1.8772 | -2.6655 | -10.9483 | -9.563 | -1.7889 |  | -5.388 | -4.896 | 4.0544 | 3.3726 | 3.3589 | 0.9516 | 10.5984 | 13.9326 | 14.5321 | 10.8486 | -0.0007 | -0.0028 | 0.0007 | 0.0037 | 0.0005 | -0.0008 | 0.0029 | -0.0131 | -0.0062 | -360.0973 | 17.6985 | -360.6543 | 18.0311 | -360.9404 | 18.1728 | -361.0235 | 17.528 | -352.9521 | 18.7703 | -352.9675 | 16.834
11:28 | 523 | 17.9942 | 191.9829 | 433.7907 | 438.4585 | -21.232 | -48.4749 | 0.2801 | -0.8007 | -8.2306 | -8.3934 | -3.7086 | -4.19 | 1.4522 | -5.48 | 0.5804 | 0.6168 | 0.9573 | 0.6849 | -132.7086 | -8.8195 | -1.9023 | -2.6916 | -11.01 | -9.6463 | -1.8218 |  | -5.3791 | -4.7828 | 4.0534 | 3.3728 | 3.3622 | 0.9535 | 10.5762 | 13.94 | 14.5144 | 10.8366 | -0.0001 | -0.0026 | 0.0013 | 0.0038 | 0.0008 | -0.0003 | 0.0201 | -0.0082 | -0.0143 | -360.1496 | 17.7067 | -360.6389 | 18.0188 | -360.9374 | 18.1953 | -361.0543 | 17.5198 | -352.9706 | 18.7805 | -352.946 | 16.8197
11:28 | 524 | 18.045 | 192.1006 | 433.792 | 438.4966 | -21.2184 | -48.4388 | 0.3121 | -0.7875 | -8.1974 | -8.3446 | -3.6736 | -4.1502 | 1.4287 | -5.4747 | 0.5803 | 0.6147 | 0.9569 | 0.6875 | -132.741 | -8.7744 | -2.0074 | -2.7677 | -10.9793 | -9.7418 | -1.8659 |  | -5.389 | -4.9048 | 4.0541 | 3.3711 | 3.3614 | 0.9523 | 10.5995 | 13.9281 | 14.5634 | 10.8551 | 0 | -0.0032 | 0.0003 | 0.0035 | 0.0002 | -0.0011 | 0.0224 | -0.0151 | 0.0026 | -360.1588 | 17.721 | -360.6266 | 18.0414 | -360.9804 | 18.1728 | -361.0081 | 17.5383 | -352.9491 | 18.7887 | -353.0014 | 16.8381
11:28 | 525 | 18.0564 | 192.0159 | 433.7697 | 438.4877 | -21.1694 | -48.4055 | 0.2798 | -0.6996 | -8.1376 | -8.3411 | -3.6252 | -4.1273 | 1.5145 | -5.3806 | 0.5806 | 0.6111 | 0.9614 | 0.6874 | -132.6229 | -8.7391 | -1.8846 | -2.7687 | -11.0071 | -9.5808 | -1.8033 |  | -5.3684 | -4.7891 | 4.0533 | 3.3722 | 3.3584 | 0.9511 | 10.5971 | 13.9375 | 14.5222 | 10.8348 | 0.0001 | -0.0029 | 0.0006 | 0.0035 | 0.0003 | -0.0005 | 0.0034 | 0.003 | -0.0052 | -360.1558 | 17.7108 | -360.6789 | 18.0393 | -360.9897 | 18.1707 | -360.9989 | 17.5239 | -352.9644 | 18.7805 | -352.9737 | 16.8299
11:28 | 526 | 18.1342 | 192.08 | 433.7139 | 438.4277 | -21.2279 | -48.4564 | 0.3028 | -0.7207 | -8.1675 | -8.3322 | -3.6873 | -4.225 | 1.4068 | -5.4631 | 0.58 | 0.6168 | 0.9575 | 0.6878 | -132.6418 | -8.6551 | -1.793 | -2.8083 | -11.0753 | -9.6372 | -1.8796 |  | -5.38 | -4.9689 | 4.0554 | 3.3761 | 3.3593 | 0.9512 | 10.5879 | 13.9051 | 14.5355 | 10.8663 | -0.0003 | -0.0024 | 0.0008 | 0.0037 | 0.0003 | -0.001 | 0.0118 | -0.0036 | 0.0125 | -360.1065 | 17.721 | -360.6481 | 18.0331 | -360.9774 | 18.1563 | -360.9835 | 17.5157 | -352.9367 | 18.7846 | -352.9891 | 16.834
11:28 | 527 | 18.0994 | 192.1084 | 433.7077 | 438.4867 | -21.2031 | -48.4941 | 0.3505 | -0.739 | -8.2977 | -8.4518 | -3.7253 | -4.1802 | 1.3637 | -5.4274 | 0.5785 | 0.6118 | 0.9563 | 0.6859 | -132.6861 | -8.7681 | -1.892 | -2.7815 | -11.0818 | -9.7059 | -1.8386 |  | -5.4123 | -4.9318 | 4.0536 | 3.3759 | 3.3593 | 0.9536 | 10.5625 | 13.9142 | 14.5086 | 10.8183 | -0.0006 | -0.0029 | 0.0002 | 0.0034 | 0.0012 | -0.0005 | 0.0108 | -0.0015 | -0.009 | -360.1219 | 17.721 | -360.6635 | 18.0516 | -360.9681 | 18.1789 | -361.0389 | 17.526 | -352.9491 | 18.7908 | -353.0229 | 16.8381
11:29 | 528 | 18.1398 | 192.1481 | 433.7505 | 438.4764 | -21.1635 | -48.4174 | 0.2858 | -0.719 | -8.2138 | -8.3459 | -3.7141 | -4.1672 | 1.4247 | -5.4423 | 0.5781 | 0.6141 | 0.9584 | 0.6869 | -132.7075 | -8.7692 | -1.9241 | -2.7754 | -11.0365 | -9.6946 | -1.8239 |  | -5.3774 | -4.8836 | 4.0543 | 3.3718 | 3.3576 | 0.9544 | 10.5821 | 13.9282 | 14.5123 | 10.8374 | 0.0003 | -0.003 | 0.0006 | 0.004 | 0.0002 | -0.0006 | 0.0117 | -0.0142 | -0.007 | -360.1342 | 17.7026 | -360.6081 | 18.0331 | -360.9897 | 18.1994 | -361.0328 | 17.5506 | -352.9644 | 18.7723 | -352.9306 | 16.8217
11:29 | 529 | 18.0767 | 192.0362 | 433.7744 | 438.4885 | -21.1393 | -48.3546 | 0.2095 | -0.7701 | -8.2405 | -8.3306 | -3.7927 | -4.0985 | 1.4351 | -5.4266 | 0.578 | 0.6131 | 0.96 | 0.6858 | -132.6343 | -8.784 | -1.923 | -2.8014 | -11.0102 | -9.6477 | -1.8532 |  | -5.3468 | -4.9073 | 4.053 | 3.3757 | 3.3577 | 0.9524 | 10.5694 | 13.9269 | 14.5099 | 10.8251 | 0 | -0.0031 | 0.0007 | 0.0043 | 0.0009 | -0.0007 | 0.0063 | -0.021 | -0.0102 | -360.0942 | 17.6861 | -360.6173 | 18.0188 | -360.9374 | 18.1707 | -361.0635 | 17.5404 | -352.946 | 18.762 | -352.9029 | 16.8012
11:29 | 530 | 18.2021 | 192.0936 | 433.7306 | 438.6051 | -21.2143 | -48.4487 | 0.2511 | -0.7915 | -8.2683 | -8.2777 | -3.7704 | -4.1581 | 1.3608 | -5.4337 | 0.5796 | 0.6136 | 0.9599 | 0.687 | -132.7397 | -8.7275 | -1.8516 | -2.8444 | -11.0882 | -9.7328 | -1.9315 |  | -5.3951 | -5.0152 | 4.054 | 3.3699 | 3.3586 | 0.9517 | 10.565 | 13.9161 | 14.4908 | 10.8505 | -0.0001 | -0.0027 | 0.0002 | 0.0036 | 0.0004 | -0.0002 | 0.0151 | -0.0017 | -0.0053 | -360.125 | 17.7169 | -360.6573 | 18.0311 | -360.9374 | 18.1666 | -360.9897 | 17.528 | -352.9367 | 18.7969 | -352.9644 | 16.832
11:29 | 531 | 18.1902 | 192.1753 | 433.7676 | 438.5933 | -21.2084 | -48.4078 | 0.2865 | -0.8082 | -8.2852 | -8.4315 | -3.7391 | -4.2077 | 1.3344 | -5.55 | 0.5783 | 0.6124 | 0.9583 | 0.6851 | -132.7332 | -8.7407 | -1.8796 | -2.8373 | -11.069 | -9.731 | -1.8949 |  | -5.3582 | -4.8523 | 4.0525 | 3.3748 | 3.3567 | 0.9532 | 10.5833 | 13.9235 | 14.5242 | 10.8562 | -0.0005 | -0.0028 | 0.001 | 0.0041 | 0.0008 | -0.0006 | 0.0166 | -0.0108 | -0.0032 | -360.1404 | 17.7149 | -360.7004 | 18.0701 | -361.0112 | 18.1769 | -360.9958 | 17.5137 | -352.9798 | 18.8011 | -353.0291 | 16.8525
11:29 | 532 | 18.1189 | 191.9925 | 433.7947 | 438.4969 | -21.1717 | -48.4356 | 0.1982 | -0.7687 | -8.2491 | -8.3229 | -3.7875 | -4.2369 | 1.39 | -5.5013 | 0.579 | 0.6125 | 0.9595 | 0.6851 | -132.6728 | -8.8255 | -1.9676 | -2.8 | -11.0753 | -9.709 | -1.9546 |  | -5.4006 | -4.9464 | 4.0527 | 3.3738 | 3.3577 | 0.9546 | 10.5855 | 13.9318 | 14.5512 | 10.8464 | 0.0001 | -0.0025 | 0.0007 | 0.0035 | 0.0007 | 0 | 0.0109 | -0.0005 | -0.0114 | -360.1158 | 17.7108 | -360.6604 | 18.0414 | -360.9958 | 18.1748 | -360.9835 | 17.5116 | -352.9183 | 18.7764 | -353.0168 | 16.8299
11:29 | 533 | 18.0715 | 192.0619 | 433.8184 | 438.4402 | -21.1971 | -48.4775 | 0.2619 | -0.7498 | -8.2738 | -8.2271 | -3.6873 | -4.2419 | 1.3192 | -5.4731 | 0.5785 | 0.6133 | 0.9591 | 0.687 | -132.6613 | -8.8249 | -1.8752 | -2.6696 | -11.005 | -9.6557 | -1.8779 |  | -5.3027 | -4.8586 | 4.0535 | 3.3719 | 3.3569 | 0.9542 | 10.5762 | 13.9341 | 14.5192 | 10.8312 | 0.0002 | -0.0034 | 0.0006 | 0.0034 | 0.0008 | -0.0007 | 0.0066 | -0.0068 | -0.0052 | -360.165 | 17.6902 | -360.6389 | 18.0249 | -360.9497 | 18.1748 | -361.0389 | 17.5363 | -352.9614 | 18.7826 | -352.9491 | 16.8032
11:29 | 534 | 18.0768 | 192.0444 | 433.893 | 438.5117 | -21.1176 | -48.4483 | 0.3148 | -0.8127 | -8.2396 | -8.2539 | -3.7376 | -4.2361 | 1.3474 | -5.4253 | 0.5803 | 0.613 | 0.9556 | 0.6852 | -132.6597 | -8.7977 | -1.9005 | -2.7205 | -10.9954 | -9.6326 | -1.8683 |  | -5.303 | -4.8539 | 4.053 | 3.3747 | 3.3593 | 0.9545 | 10.5509 | 13.9199 | 14.5375 | 10.8587 | -0.0001 | -0.0028 | 0.0006 | 0.0036 | 0.0005 | -0.0009 | 0.0029 | -0.0154 | -0.0071 | -360.1619 | 17.7128 | -360.6081 | 18.0023 | -360.9558 | 18.1707 | -361.0358 | 17.5547 | -352.9921 | 18.7887 | -352.9583 | 16.795
11:29 | 535 | 18.0555 | 192.0089 | 433.8718 | 438.5085 | -21.0783 | -48.3318 | 0.3074 | -0.7725 | -8.2753 | -8.2636 | -3.6898 | -4.1925 | 1.3988 | -5.4626 | 0.5805 | 0.6142 | 0.9579 | 0.6871 | -132.6638 | -8.8136 | -1.8501 | -2.7035 | -10.8707 | -9.6749 | -1.8586 |  | -5.3139 | -4.7821 | 4.0535 | 3.3736 | 3.3614 | 0.9539 | 10.6076 | 13.9247 | 14.5314 | 10.8573 | -0.0002 | -0.0028 | -0.0003 | 0.0027 | 0.0003 | -0.0006 | 0.002 | -0.0127 | -0.0175 | -360.1281 | 17.7067 | -360.6173 | 18.0064 | -360.9035 | 18.1625 | -361.0204 | 17.5301 | -352.9614 | 18.7887 | -352.946 | 16.7868
11:29 | 536 | 18.0577 | 191.9546 | 433.7899 | 438.5767 | -21.14 | -48.4056 | 0.3224 | -0.8477 | -8.279 | -8.2089 | -3.6702 | -4.1322 | 1.4056 | -5.5084 | 0.5798 | 0.6117 | 0.9595 | 0.6866 | -132.7518 | -8.842 | -1.8786 | -2.7471 | -10.9056 | -9.6214 | -1.861 |  | -5.3703 | -4.9462 | 4.0529 | 3.3719 | 3.3565 | 0.9536 | 10.5499 | 13.9129 | 14.5293 | 10.8349 | -0.0004 | -0.0032 | 0.0005 | 0.0039 | 0.0009 | -0.0012 | 0.0036 | -0.0102 | -0.0125 | -360.0942 | 17.7128 | -360.6696 | 18.0496 | -360.9897 | 18.1748 | -361.0143 | 17.5096 | -352.9306 | 18.7867 | -352.9798 | 16.8381
11:29 | 537 | 18.0838 | 191.983 | 433.8162 | 438.5351 | -21.0966 | -48.4034 | 0.2449 | -0.7793 | -8.3042 | -8.2739 | -3.6922 | -4.2759 | 1.3687 | -5.5667 | 0.5813 | 0.6129 | 0.9593 | 0.6875 | -132.7356 | -8.8196 | -1.8712 | -2.7518 | -10.9478 | -9.7112 | -1.8912 |  | -5.3774 | -4.9009 | 4.0535 | 3.3728 | 3.3588 | 0.9551 | 10.5971 | 13.9258 | 14.5096 | 10.841 | 0 | -0.003 | 0.0007 | 0.0039 | 0.0008 | -0.0002 | 0.0082 | -0.0123 | -0.0021 | -360.0911 | 17.6964 | -360.6912 | 18.0578 | -361.0358 | 18.1933 | -361.0358 | 17.5096 | -352.9521 | 18.7846 | -352.9983 | 16.8381
11:29 | 538 | 18.047 | 191.9457 | 433.7842 | 438.5944 | -21.132 | -48.4395 | 0.1984 | -0.6497 | -8.1728 | -8.2203 | -3.6569 | -4.3333 | 1.445 | -5.4423 | 0.5806 | 0.6135 | 0.9572 | 0.6867 | -132.6912 | -8.8439 | -1.7677 | -2.788 | -10.9016 | -9.7338 | -1.8532 |  | -5.4109 | -5.0161 | 4.0534 | 3.3719 | 3.3601 | 0.9539 | 10.5961 | 13.9188 | 14.5419 | 10.8519 | -0.0002 | -0.0032 | 0.0006 | 0.0039 | 0.0005 | -0.0012 | 0.0105 | -0.0158 | -0.0026 | -360.0973 | 17.6985 | -360.6358 | 18.027 | -360.9558 | 18.1748 | -361.0204 | 17.5178 | -352.9152 | 18.7805 | -352.9552 | 16.7991
11:29 | 539 | 18.0168 | 191.9383 | 433.7058 | 438.6229 | -21.2449 | -48.4965 | 0.1277 | -0.7131 | -8.1651 | -8.3063 | -3.7223 | -4.341 | 1.3158 | -5.5352 | 0.5808 | 0.6116 | 0.9612 | 0.6856 | -132.6782 | -8.8583 | -1.8943 | -2.8297 | -10.8871 | -9.6879 | -1.8066 |  | -5.3979 | -4.894 | 4.0528 | 3.3717 | 3.3599 | 0.9558 | 10.5845 | 13.9014 | 14.5304 | 10.8288 | -0.0002 | -0.0028 | 0.0007 | 0.0035 | 0.0001 | -0.0005 | 0.0051 | -0.0113 | 0.0075 | -360.1588 | 17.6902 | -360.6173 | 18.0126 | -360.9127 | 18.1604 | -361.0451 | 17.5547 | -352.9614 | 18.7805 | -352.9429 | 16.7909
11:29 | 540 | 18.095 | 191.9947 | 433.7633 | 438.6431 | -21.2517 | -48.5742 | 0.0852 | -0.7236 | -8.0847 | -8.1989 | -3.674 | -4.2529 | 1.4191 | -5.5531 | 0.5817 | 0.6133 | 0.9607 | 0.687 | -132.6665 | -8.9269 | -1.8867 | -2.7571 | -10.967 | -9.6994 | -1.8021 |  | -5.3839 | -4.9978 | 4.0546 | 3.3741 | 3.3585 | 0.9558 | 10.5809 | 13.9387 | 14.5236 | 10.8301 | -0.0001 | -0.0024 | 0.0006 | 0.0037 | 0.0009 | -0.0005 | 0.0084 | -0.0134 | -0.0123 | -360.1896 | 17.7272 | -360.6235 | 18.0208 | -360.9589 | 18.1789 | -361.0358 | 17.5506 | -352.9737 | 18.8052 | -352.9552 | 16.7909
11:29 | 541 | 18.0427 | 192.0665 | 433.8671 | 438.6352 | -21.1935 | -48.4951 | 0.1875 | -0.6845 | -8.0611 | -8.2193 | -3.6833 | -4.1347 | 1.3822 | -5.4686 | 0.5806 | 0.6101 | 0.9572 | 0.6849 | -132.7457 | -8.966 | -1.9457 | -2.7376 | -10.8884 | -9.6804 | -1.8385 |  | -5.3822 | -4.9584 | 4.0535 | 3.3743 | 3.358 | 0.9548 | 10.5867 | 13.9097 | 14.5515 | 10.8536 | -0.0002 | -0.0031 | 0.0006 | 0.004 | 0.0005 | -0.0006 | 0.021 | -0.0174 | 0.0013 | -360.1219 | 17.7026 | -360.6604 | 18.0414 | -360.9897 | 18.1687 | -361.0266 | 17.5301 | -352.9491 | 18.7846 | -352.9706 | 16.8156
11:29 | 542 | 18.016 | 191.9863 | 433.778 | 438.6013 | -21.2031 | -48.5971 | 0.1911 | -0.6714 | -8.0908 | -8.1992 | -3.7153 | -4.1396 | 1.4206 | -5.4794 | 0.5792 | 0.6133 | 0.9618 | 0.6844 | -132.6086 | -8.8094 | -2.0149 | -2.6508 | -10.936 | -9.6301 | -1.8451 |  | -5.399 | -4.8984 | 4.0524 | 3.3734 | 3.3606 | 0.9547 | 10.6029 | 13.926 | 14.5512 | 10.8522 | 0.0001 | -0.0028 | 0.001 | 0.0038 | 0.0004 | -0.001 | 0.0103 | -0.0159 | -0.0093 | -360.1004 | 17.6902 | -360.6358 | 18.0393 | -360.9774 | 18.1748 | -361.0174 | 17.5178 | -352.9029 | 18.7682 | -352.9737 | 16.8217
11:29 | 543 | 18.0298 | 191.9756 | 433.7897 | 438.6883 | -21.2664 | -48.5178 | 0.1773 | -0.8208 | -8.1477 | -8.3317 | -3.7224 | -4.1642 | 1.4014 | -5.4914 | 0.5792 | 0.6105 | 0.9575 | 0.6854 | -132.646 | -8.8041 | -1.9251 | -2.6743 | -10.9606 | -9.6185 | -1.8518 |  | -5.4051 | -4.8837 | 4.0525 | 3.3751 | 3.3563 | 0.9566 | 10.5532 | 13.9512 | 14.4997 | 10.8262 | -0.0005 | -0.0032 | 0.0008 | 0.0037 | 0.0007 | -0.0006 | 0.0009 | -0.0046 | 0.0011 | -360.1188 | 17.7128 | -360.645 | 18.0393 | -360.9712 | 18.1892 | -361.0174 | 17.5219 | -352.9644 | 18.7928 | -352.9583 | 16.8032
11:29 | 544 | 18.0632 | 192.0771 | 433.7911 | 438.6731 | -21.2277 | -48.5795 | 0.1602 | -0.7438 | -8.2245 | -8.2665 | -3.7289 | -4.194 | 1.4481 | -5.514 | 0.5797 | 0.6128 | 0.9553 | 0.6854 | -132.6321 | -8.8449 | -1.9594 | -2.7305 | -10.9463 | -9.6845 | -1.8584 |  | -5.4964 | -4.9511 | 4.0518 | 3.3713 | 3.3582 | 0.9572 | 10.5729 | 13.9188 | 14.5419 | 10.8577 | -0.0004 | -0.0026 | 0.0007 | 0.0042 | 0.0003 | -0.0008 | 0.0071 | -0.0188 | 0.01 | -360.1435 | 17.7026 | -360.6512 | 18.0249 | -360.9251 | 18.1707 | -361.0328 | 17.5424 | -352.9552 | 18.7887 | -352.9398 | 16.8012
11:29 | 545 | 18.0493 | 192.0996 | 433.9279 | 438.6768 | -21.2231 | -48.5568 | 0.1557 | -0.7587 | -8.1652 | -8.2453 | -3.7253 | -4.2359 | 1.439 | -5.4645 | 0.5794 | 0.6122 | 0.9531 | 0.6844 | -132.5803 | -8.8872 | -1.9163 | -2.7247 | -10.9662 | -9.6201 | -1.8689 |  | -5.4435 | -4.9366 | 4.0517 | 3.3743 | 3.3613 | 0.9572 | 10.5856 | 13.9142 | 14.5086 | 10.853 | -0.0003 | -0.003 | 0.0005 | 0.004 | 0.0011 | -0.0008 | 0.0021 | -0.0085 | -0.009 | -360.1127 | 17.7087 | -360.645 | 18.0249 | -360.9374 | 18.1604 | -361.0204 | 17.5342 | -352.9367 | 18.7805 | -352.9583 | 16.7991
11:29 | 546 | 18.1094 | 192.1055 | 433.8656 | 438.6278 | -21.1849 | -48.5808 | 0.2904 | -0.8385 | -8.1797 | -8.2587 | -3.7924 | -4.2442 | 1.474 | -5.4546 | 0.5803 | 0.6128 | 0.9564 | 0.6866 | -132.6268 | -8.863 | -1.9263 | -2.8433 | -11.0974 | -9.7114 | -1.9394 |  | -5.4222 | -4.9178 | 4.0521 | 3.3745 | 3.3591 | 0.9559 | 10.5983 | 13.9444 | 14.5399 | 10.8652 | 0.0002 | -0.003 | 0.0004 | 0.0035 | 0.0002 | -0.0006 | 0.0089 | -0.0124 | 0.0007 | -360.1496 | 17.7108 | -360.6604 | 18.027 | -360.9743 | 18.1851 | -360.9989 | 17.5301 | -352.9768 | 18.8011 | -352.9706 | 16.8053
11:29 | 547 | 18.0909 | 192.0849 | 433.8185 | 438.6074 | -21.2321 | -48.5579 | 0.2864 | -0.803 | -8.1672 | -8.1996 | -3.7312 | -4.1816 | 1.5293 | -5.3916 | 0.5796 | 0.613 | 0.9585 | 0.686 | -132.6355 | -8.8903 | -1.8704 | -2.859 | -11.0361 | -9.7371 | -1.9047 |  | -5.3711 | -4.9111 | 4.052 | 3.3761 | 3.3611 | 0.9571 | 10.5787 | 13.9188 | 14.513 | 10.8288 | 0.0003 | -0.0029 | 0.0007 | 0.004 | 0.0006 | -0.0011 | -0.006 | -0.0121 | 0.0043 | -360.1034 | 17.6985 | -360.6604 | 18.0352 | -360.9743 | 18.1789 | -361.0143 | 17.528 | -352.9337 | 18.7785 | -352.946 | 16.8032
11:29 | 548 | 18.0281 | 192.1295 | 433.854 | 438.6435 | -21.1939 | -48.6087 | 0.2435 | -0.7245 | -8.182 | -8.1882 | -3.6576 | -4.1833 | 1.5099 | -5.4409 | 0.5809 | 0.6142 | 0.9587 | 0.6857 | -132.6789 | -8.8207 | -1.9366 | -2.9132 | -11.0881 | -9.8553 | -1.9264 |  | -5.4203 | -4.8999 | 4.0515 | 3.3731 | 3.3611 | 0.9574 | 10.5867 | 13.9387 | 14.512 | 10.859 | -0.0004 | -0.0026 | 0.0005 | 0.0034 | 0.0005 | -0.0003 | 0.0034 | -0.0095 | -0.022 | -360.0788 | 17.6759 | -360.6296 | 18.0311 | -360.9497 | 18.1728 | -361.0512 | 17.5301 | -352.9244 | 18.7805 | -352.946 | 16.8135
11:29 | 549 | 18.0879 | 192.1375 | 433.8289 | 438.7025 | -21.2357 | -48.4728 | 0.2709 | -0.7837 | -8.2808 | -8.2373 | -3.7781 | -4.1412 | 1.5336 | -5.4028 | 0.5807 | 0.6106 | 0.9597 | 0.6866 | -132.708 | -8.8776 | -1.9259 | -2.911 | -11.097 | -9.8931 | -1.9439 |  | -5.4448 | -4.7978 | 4.0516 | 3.3728 | 3.3572 | 0.9568 | 10.6075 | 13.9423 | 14.574 | 10.8623 | -0.0002 | -0.0025 | 0.0009 | 0.0035 | 0.0003 | -0.0011 | 0.0083 | -0.0035 | -0.0159 | -360.1804 | 17.7087 | -360.6512 | 18.0188 | -360.9712 | 18.1851 | -361.0481 | 17.5301 | -352.9337 | 18.7928 | -352.986 | 16.8053
11:29 | 550 | 18.0838 | 192.1415 | 433.8616 | 438.6528 | -21.3047 | -48.2988 | 0.2136 | -0.7757 | -8.2486 | -7.9914 | -3.7605 | -4.0924 | 1.5503 | -5.3738 | 0.5807 | 0.6117 | 0.9566 | 0.6846 | -132.6597 | -8.8497 | -1.928 | -2.8962 | -11.0239 | -9.7651 | -1.8918 |  | -5.3701 | -4.8055 | 4.0517 | 3.3722 | 3.3571 | 0.9574 | 10.6029 | 13.9548 | 14.5617 | 10.8583 | 0 | -0.0028 | 0.0011 | 0.004 | 0.0006 | -0.0007 | 0.0097 | -0.0124 | -0.0087 | -360.1496 | 17.721 | -360.6758 | 18.0249 | -360.9497 | 18.1707 | -361.0266 | 17.5363 | -352.9521 | 18.799 | -352.9675 | 16.7991
11:29 | 551 | 18.0585 | 192.015 | 433.8354 | 438.6485 | -21.2028 | -48.4553 | 0.2899 | -0.7651 | -8.2413 | -8.1736 | -3.8004 | -4.1094 | 1.5161 | -5.3193 | 0.5797 | 0.6146 | 0.9584 | 0.6864 | -132.6643 | -8.9056 | -1.9541 | -2.8845 | -11.0453 | -9.8308 | -1.8946 |  | -5.432 | -4.7653 | 4.0529 | 3.3728 | 3.358 | 0.9569 | 10.582 | 13.9632 | 14.5549 | 10.8655 | 0.0002 | -0.0027 | 0.0008 | 0.0035 | 0.0007 | -0.0006 | 0.0203 | 0.0063 | -0.0215 | -360.1311 | 17.7046 | -360.6358 | 18.0126 | -360.9374 | 18.1543 | -360.9804 | 17.526 | -352.9675 | 18.8011 | -352.9552 | 16.795
11:29 | 552 | 18.0746 | 192.0549 | 433.8081 | 438.5874 | -21.2661 | -48.4806 | 0.2259 | -0.7653 | -8.2561 | -8.1504 | -3.7106 | -4.1621 | 1.4998 | -5.3443 | 0.5802 | 0.6135 | 0.9549 | 0.6855 | -132.6544 | -8.8761 | -1.8841 | -2.8231 | -11.04 | -9.8092 | -1.837 |  | -5.457 | -4.7817 | 4.0524 | 3.3758 | 3.3578 | 0.9578 | 10.5996 | 13.9222 | 14.5045 | 10.8382 | -0.0002 | -0.0026 | 0.0012 | 0.0042 | 0.001 | -0.0008 | 0.0133 | -0.0048 | -0.0102 | -360.1158 | 17.7026 | -360.6666 | 18.0537 | -360.9774 | 18.1748 | -361.0328 | 17.528 | -352.9737 | 18.7969 | -352.9583 | 16.8238
11:29 | 553 | 18.0566 | 192.1119 | 433.8523 | 438.6619 | -21.2827 | -48.4817 | 0.2519 | -0.7835 | -8.2139 | -8.1456 | -3.6961 | -4.2072 | 1.5033 | -5.4456 | 0.5805 | 0.6159 | 0.9566 | 0.6877 | -132.6507 | -8.9269 | -1.8284 | -2.8558 | -11.0072 | -9.7715 | -1.9354 |  | -5.3847 | -4.7533 | 4.0506 | 3.3724 | 3.3578 | 0.9583 | 10.559 | 13.9107 | 14.4939 | 10.8378 | -0.0003 | -0.0026 | 0.0006 | 0.0039 | 0.0008 | -0.0002 | -0.0007 | -0.0026 | -0.0187 | -360.1219 | 17.6738 | -360.6081 | 18.0229 | -360.9651 | 18.1953 | -361.0451 | 17.5178 | -352.9429 | 18.762 | -352.9398 | 16.8053
11:29 | 554 | 17.9922 | 192.0088 | 433.6894 | 438.6093 | -21.3269 | -48.4886 | 0.1215 | -0.8475 | -8.318 | -8.2807 | -3.7867 | -4.2245 | 1.4205 | -5.5003 | 0.5794 | 0.6139 | 0.9585 | 0.6861 | -132.5706 | -8.9434 | -1.7617 | -2.8155 | -10.9652 | -9.7424 | -1.928 |  | -5.4275 | -4.793 | 4.0503 | 3.3729 | 3.3572 | 0.9583 | 10.5798 | 13.9258 | 14.5096 | 10.8352 | 0.0002 | -0.0025 | 0.0008 | 0.0035 | 0.0007 | -0.001 | 0.0148 | 0.0052 | -0.0283 | -360.0911 | 17.6759 | -360.6143 | 18.0188 | -360.9681 | 18.1892 | -361.0481 | 17.5424 | -352.9367 | 18.7641 | -352.9183 | 16.8053
11:29 | 555 | 18.1668 | 192.0929 | 433.7828 | 438.6251 | -21.322 | -48.5299 | 0.1469 | -0.8696 | -8.286 | -8.3002 | -3.7859 | -4.234 | 1.5164 | -5.4259 | 0.5785 | 0.6131 | 0.9566 | 0.6851 | -132.5666 | -8.9654 | -1.8082 | -2.8141 | -10.9215 | -9.7444 | -1.886 |  | -5.4199 | -4.83 | 4.0495 | 3.3698 | 3.3569 | 0.9575 | 10.5477 | 13.8929 | 14.4898 | 10.8163 | 0 | -0.0032 | 0.0006 | 0.0037 | 0.0005 | 0.0001 | 0.0018 | -0.0122 | -0.0082 | -360.1527 | 17.719 | -360.6512 | 18.0249 | -360.9681 | 18.1687 | -361.0328 | 17.5465 | -352.9891 | 18.8011 | -352.9583 | 16.7991
11:29 | 556 | 18.1053 | 192.0382 | 433.7995 | 438.5573 | -21.2049 | -48.6362 | 0.1472 | -0.7595 | -8.3088 | -8.3132 | -3.7198 | -4.2391 | 1.4309 | -5.5323 | 0.5787 | 0.6162 | 0.9575 | 0.6858 | -132.6374 | -9.021 | -1.774 | -2.8728 | -10.9334 | -9.7986 | -1.8859 |  | -5.4937 | -4.8199 | 4.0506 | 3.3742 | 3.3579 | 0.9571 | 10.5924 | 13.9271 | 14.5178 | 10.8417 | 0.0002 | -0.0026 | 0.0009 | 0.0038 | 0.0007 | -0.0009 | -0.0043 | 0.0009 | -0.0112 | -360.1065 | 17.7128 | -360.6727 | 18.0229 | -360.922 | 18.1399 | -360.9589 | 17.4931 | -352.9521 | 18.8134 | -352.9829 | 16.8094
11:29 | 557 | 18.0425 | 192.0348 | 433.7849 | 438.5653 | -21.2962 | -48.6424 | 0.1312 | -0.8305 | -8.2939 | -8.2654 | -3.747 | -4.2157 | 1.4277 | -5.4972 | 0.5788 | 0.6159 | 0.957 | 0.6866 | -132.5806 | -8.918 | -1.737 | -2.8168 | -10.9089 | -9.7486 | -1.8139 |  | -5.4454 | -4.7775 | 4.05 | 3.3727 | 3.3555 | 0.9587 | 10.5914 | 13.9315 | 14.5259 | 10.8414 | -0.0005 | -0.0028 | 0.0007 | 0.0033 | 0.0003 | -0.0006 | 0.0068 | -0.0144 | 0.0078 | -360.1619 | 17.6964 | -360.685 | 18.0352 | -360.9804 | 18.1604 | -360.9712 | 17.5239 | -352.9583 | 18.7969 | -353.0014 | 16.8238
11:29 | 558 | 18.0936 | 192.0425 | 433.7924 | 438.5133 | -21.3186 | -48.499 | 0.1793 | -0.7458 | -8.2444 | -8.2078 | -3.7923 | -4.1952 | 1.3852 | -5.5462 | 0.579 | 0.6106 | 0.9546 | 0.6859 | -132.6326 | -8.9096 | -1.7766 | -2.8144 | -10.8511 | -9.7264 | -1.8411 |  | -5.4425 | -4.7578 | 4.0505 | 3.3693 | 3.3567 | 0.9596 | 10.5937 | 13.9223 | 14.5287 | 10.8436 | -0.0003 | -0.0028 | 0.0005 | 0.0034 | 0.0004 | -0.001 | 0.0168 | -0.0073 | -0.0009 | -360.1034 | 17.6944 | -360.6296 | 18.027 | -360.9835 | 18.1892 | -361.0358 | 17.5404 | -352.9306 | 18.7723 | -352.9521 | 16.8074
11:29 | 559 | 18.2601 | 192.1949 | 433.8964 | 438.6819 | -21.3032 | -48.5209 | 0.1933 | -0.7845 | -8.2808 | -8.211 | -3.7375 | -4.2975 | 1.3991 | -5.505 | 0.5812 | 0.6093 | 0.9557 | 0.6872 | -132.5481 | -8.8435 | -1.7867 | -2.8428 | -10.9758 | -9.7675 | -1.8496 |  | -5.4593 | -4.7853 | 4.0505 | 3.3722 | 3.3587 | 0.9584 | 10.5982 | 13.9329 | 14.5525 | 10.8706 | 0.0001 | -0.0034 | 0.0008 | 0.0035 | 0.0007 | -0.0011 | 0.0084 | -0.0145 | -0.0152 | -360.1127 | 17.68 | -360.5927 | 17.9982 | -360.9404 | 18.1892 | -361.0451 | 17.5404 | -352.9398 | 18.7641 | -352.9091 | 16.7827
11:29 | 560 | 18.1679 | 192.1835 | 433.6975 | 438.5963 | -21.2599 | -48.5925 | 0.18 | -0.7535 | -8.2896 | -8.2525 | -3.663 | -4.4138 | 1.3365 | -5.5904 | 0.58 | 0.6122 | 0.9598 | 0.6878 | -132.5557 | -8.9082 | -1.8006 | -2.8088 | -10.9399 | -9.6768 | -1.7924 |  | -5.445 | -4.8228 | 4.0516 | 3.372 | 3.3604 | 0.9589 | 10.6134 | 13.9536 | 14.5603 | 10.8515 | -0.0002 | -0.003 | 0.0004 | 0.0035 | 0.0003 | -0.0006 | 0.0104 | 0.0017 | -0.0067 | -360.1311 | 17.6902 | -360.6266 | 18.0331 | -360.9681 | 18.181 | -361.0512 | 17.5486 | -352.9768 | 18.7785 | -352.9521 | 16.7991
11:29 | 561 | 18.2622 | 192.215 | 433.8159 | 438.6583 | -21.2222 | -48.575 | 0.2019 | -0.8002 | -8.2298 | -8.2646 | -3.7357 | -4.3562 | 1.3713 | -5.4655 | 0.5794 | 0.6118 | 0.9584 | 0.6871 | -132.5559 | -8.9259 | -1.9177 | -2.9243 | -10.9469 | -9.7193 | -1.9291 |  | -5.419 | -4.743 | 4.0503 | 3.3751 | 3.3598 | 0.9574 | 10.5995 | 13.9107 | 14.5634 | 10.832 | -0.0006 | -0.003 | 0.0005 | 0.0035 | 0.0008 | -0.0011 | 0.0021 | 0.0004 | -0.0242 | -360.1804 | 17.7169 | -360.6573 | 18.0393 | -360.9743 | 18.1645 | -360.9681 | 17.5301 | -352.9337 | 18.799 | -352.9583 | 16.8115
11:29 | 562 | 18.1106 | 192.1614 | 433.7995 | 438.6036 | -21.2205 | -48.5449 | 0.2349 | -0.7643 | -8.2967 | -8.3168 | -3.7078 | -4.374 | 1.4085 | -5.4575 | 0.5791 | 0.6087 | 0.9573 | 0.6859 | -132.5529 | -8.8799 | -1.8504 | -2.9311 | -11.0178 | -9.6764 | -1.8672 |  | -5.4279 | -4.7472 | 4.0501 | 3.3713 | 3.3568 | 0.9589 | 10.5741 | 13.9199 | 14.5144 | 10.8298 | -0.0005 | -0.0029 | 0.0005 | 0.0035 | 0.0002 | -0.0005 | 0.01 | -0.0001 | -0.0215 | -360.1219 | 17.7149 | -360.6881 | 18.0619 | -360.962 | 18.1563 | -360.9651 | 17.5116 | -352.9183 | 18.8011 | -352.9983 | 16.8217
11:29 | 563 | 18.1419 | 192.2081 | 433.8943 | 438.5216 | -21.2442 | -48.478 | 0.2105 | -0.6869 | -8.2365 | -8.2367 | -3.6695 | -4.2498 | 1.4888 | -5.4302 | 0.5794 | 0.6127 | 0.9573 | 0.6855 | -132.4474 | -8.9789 | -1.8467 | -2.8715 | -10.9771 | -9.7126 | -1.8672 |  | -5.4261 | -4.8152 | 4.0495 | 3.3701 | 3.3589 | 0.961 | 10.558 | 13.9267 | 14.5137 | 10.8433 | -0.0001 | -0.0033 | 0.0004 | 0.0039 | 0.0009 | -0.0006 | -0.003 | -0.0065 | -0.0299 | -360.1404 | 17.7067 | -360.6912 | 18.0598 | -360.9927 | 18.1892 | -361.0266 | 17.5383 | -352.9429 | 18.799 | -353.0137 | 16.8217
11:29 | 564 | 18.1272 | 192.1097 | 433.8121 | 438.5538 | -21.2247 | -48.5246 | 0.2676 | -0.6825 | -8.1872 | -8.1588 | -3.6981 | -4.2165 | 1.455 | -5.4133 | 0.5794 | 0.612 | 0.9563 | 0.687 | -132.5607 | -8.9319 | -1.8632 | -2.8347 | -10.9014 | -9.7033 | -1.8021 |  | -5.4147 | -4.86 | 4.0481 | 3.3712 | 3.3592 | 0.9588 | 10.5718 | 13.9234 | 14.529 | 10.8681 | -0.0001 | -0.0038 | 0.0008 | 0.0036 | -0.0001 | -0.0004 | 0.0054 | -0.0013 | -0.0083 | -360.1773 | 17.6779 | -360.6019 | 18.0208 | -360.9466 | 18.1789 | -361.0358 | 17.5404 | -352.9737 | 18.7661 | -352.9214 | 16.795
11:29 | 565 | 18.1288 | 192.1013 | 433.7055 | 438.5252 | -21.3407 | -48.6109 | 0.1896 | -0.7374 | -8.2263 | -8.1817 | -3.69 | -4.2795 | 1.4346 | -5.4994 | 0.5796 | 0.6126 | 0.9552 | 0.6862 | -132.5197 | -9.0012 | -1.8629 | -2.7619 | -10.7671 | -9.5529 | -1.6924 |  | -5.3855 | -4.8575 | 4.0481 | 3.374 | 3.3592 | 0.9603 | 10.5914 | 13.9548 | 14.5386 | 10.8583 | -0.0001 | -0.003 | 0.0007 | 0.0033 | 0.0005 | -0.0005 | 0.008 | -0.0101 | -0.0139 | -360.1619 | 17.6841 | -360.6143 | 18.0044 | -360.9281 | 18.1625 | -361.0358 | 17.5486 | -352.9491 | 18.7805 | -352.9306 | 16.7827
11:29 | 566 | 18.0514 | 192.1828 | 433.8124 | 438.5584 | -21.2777 | -48.4989 | 0.2891 | -0.709 | -8.1957 | -8.1828 | -3.5572 | -4.2953 | 1.4083 | -5.5752 | 0.58 | 0.6131 | 0.9578 | 0.6876 | -132.5607 | -9.0634 | -1.8992 | -2.7633 | -10.8623 | -9.695 | -1.7734 |  | -5.4663 | -4.8497 | 4.0493 | 3.3727 | 3.3584 | 0.9601 | 10.6155 | 13.9737 | 14.5662 | 10.9102 | 0 | -0.0025 | 0.0011 | 0.0041 | 0.0005 | -0.0007 | 0.0124 | 0.0049 | -0.0035 | -360.1342 | 17.7046 | -360.6543 | 18.0414 | -360.9404 | 18.1645 | -361.0297 | 17.5301 | -352.9614 | 18.8031 | -352.9706 | 16.8053
11:29 | 567 | 18.106 | 192.1253 | 433.7995 | 438.5803 | -21.2104 | -48.4767 | 0.3079 | -0.7133 | -8.2724 | -8.1727 | -3.5755 | -4.2723 | 1.3309 | -5.5456 | 0.5798 | 0.6113 | 0.9548 | 0.6863 | -132.5506 | -8.9642 | -1.8658 | -2.7038 | -10.7824 | -9.6822 | -1.7372 |  | -5.3689 | -4.8601 | 4.0479 | 3.3745 | 3.3584 | 0.9604 | 10.5982 | 13.9734 | 14.5815 | 10.8821 | -0.0005 | -0.0033 | 0.0009 | 0.0038 | 0.0007 | -0.0008 | 0.0002 | -0.0073 | -0.0135 | -360.0727 | 17.6841 | -360.6543 | 18.0537 | -360.9835 | 18.1379 | -360.962 | 17.5034 | -352.8844 | 18.7703 | -352.9675 | 16.8299
11:29 | 568 | 17.9914 | 192.0589 | 433.7613 | 438.545 | -21.2068 | -48.4473 | 0.2222 | -0.7051 | -8.2574 | -8.1753 | -3.5814 | -4.3403 | 1.3021 | -5.6106 | 0.5793 | 0.6163 | 0.9537 | 0.6847 | -132.6028 | -8.9315 | -1.9337 | -2.7147 | -10.8843 | -9.6138 | -1.7758 |  | -5.3712 | -4.7117 | 4.0499 | 3.3752 | 3.3609 | 0.9615 | 10.6005 | 13.9526 | 14.5495 | 10.8496 | 0.0003 | -0.0031 | 0.0004 | 0.0036 | 0.0007 | -0.0005 | -0.0039 | 0.0061 | -0.0181 | -360.1034 | 17.7005 | -360.6727 | 18.068 | -361.0112 | 18.1748 | -361.0266 | 17.5137 | -352.9306 | 18.7826 | -352.9829 | 16.8361
11:29 | 569 | 18.0499 | 192.044 | 433.8265 | 438.5997 | -21.2557 | -48.5124 | 0.2323 | -0.7259 | -8.2546 | -8.2717 | -3.6349 | -4.2652 | 1.4187 | -5.5811 | 0.5792 | 0.6182 | 0.9548 | 0.6866 | -132.5775 | -8.9384 | -1.8409 | -2.7344 | -10.8807 | -9.6917 | -1.7947 |  | -5.4754 | -4.7633 | 4.0501 | 3.3729 | 3.36 | 0.9604 | 10.611 | 13.9571 | 14.5413 | 10.8605 | 0 | -0.0029 | 0.0008 | 0.0037 | 0.0002 | -0.0009 | 0.0094 | -0.0027 | -0.0002 | -360.1004 | 17.6841 | -360.6266 | 18.0331 | -360.962 | 18.1584 | -361.0297 | 17.528 | -352.9337 | 18.7785 | -352.9491 | 16.8074
11:29 | 570 | 18.1153 | 192.0851 | 433.8404 | 438.5665 | -21.2357 | -48.3325 | 0.3242 | -0.7952 | -8.1927 | -8.3541 | -3.6558 | -4.2509 | 1.4137 | -5.6204 | 0.5792 | 0.6164 | 0.955 | 0.6856 | -132.5413 | -8.9556 | -1.8802 | -2.7452 | -10.8784 | -9.6559 | -1.7666 |  | -5.3788 | -4.6773 | 4.0493 | 3.3747 | 3.3593 | 0.9603 | 10.5902 | 13.9594 | 14.5256 | 10.8573 | -0.0005 | -0.0026 | 0.0005 | 0.0034 | 0.0007 | -0.0009 | 0.0119 | -0.0107 | 0.0012 | -360.1619 | 17.6944 | -360.6112 | 17.9962 | -360.9189 | 18.1337 | -361.0389 | 17.5547 | -352.9737 | 18.7826 | -352.9306 | 16.795
11:29 | 571 | 18.1646 | 192.0196 | 433.7968 | 438.6033 | -21.1048 | -48.475 | 0.3198 | -0.7501 | -8.232 | -8.3638 | -3.6362 | -4.2321 | 1.4103 | -5.4839 | 0.5792 | 0.6165 | 0.9564 | 0.687 | -132.5492 | -8.9709 | -1.8684 | -2.7071 | -10.9223 | -9.7357 | -1.7023 |  | -5.3661 | -4.6737 | 4.0469 | 3.3741 | 3.3547 | 0.9611 | 10.6018 | 13.9189 | 14.514 | 10.8457 | -0.0003 | -0.0026 | 0.0002 | 0.0036 | 0.0002 | -0.0007 | 0.0123 | -0.0255 | -0.0228 | -360.2173 | 17.7169 | -360.6512 | 18.027 | -360.9312 | 18.1358 | -361.0389 | 17.565 | -352.9921 | 18.8154 | -352.9768 | 16.8012
11:29 | 572 | 18.1028 | 192.1474 | 433.8482 | 438.6151 | -21.2376 | -48.4336 | 0.3692 | -0.7269 | -8.2045 | -8.4156 | -3.6023 | -4.3055 | 1.3751 | -5.5709 | 0.5779 | 0.6114 | 0.9559 | 0.6869 | -132.5707 | -8.9649 | -1.8832 | -2.7286 | -10.8954 | -9.7166 | -1.8156 |  | -5.3604 | -4.6731 | 4.0475 | 3.3716 | 3.357 | 0.9616 | 10.6075 | 13.9479 | 14.5614 | 10.8742 | 0 | -0.0029 | 0.0014 | 0.004 | 0.0008 | -0.001 | 0.0052 | -0.0001 | -0.0177 | -360.1065 | 17.7026 | -360.6389 | 18.0208 | -360.9466 | 18.1461 | -360.9835 | 17.5342 | -352.9214 | 18.7805 | -352.9398 | 16.793
11:29 | 573 | 18.1569 | 192.1547 | 433.8826 | 438.6763 | -21.1341 | -48.3786 | 0.327 | -0.8003 | -8.2553 | -8.3648 | -3.6544 | -4.2312 | 1.4629 | -5.5978 | 0.5799 | 0.6183 | 0.9612 | 0.687 | -132.5141 | -8.9108 | -1.7915 | -2.8782 | -10.8541 | -9.7761 | -1.806 |  | -5.274 | -4.6515 | 4.0477 | 3.3714 | 3.3588 | 0.9604 | 10.5842 | 13.9656 | 14.5587 | 10.8788 | 0.0005 | -0.0029 | 0.0009 | 0.0039 | 0.0008 | -0.0001 | 0.0283 | 0.0003 | -0.0056 | -360.0604 | 17.6738 | -360.6266 | 18.0639 | -361.0081 | 18.1645 | -361.0174 | 17.528 | -352.9029 | 18.7723 | -352.9706 | 16.8279
11:29 | 574 | 18.121 | 192.1208 | 433.8227 | 438.6507 | -21.1503 | -48.4034 | 0.3193 | -0.7924 | -8.2111 | -8.3965 | -3.625 | -4.2799 | 1.411 | -5.5431 | 0.5793 | 0.6162 | 0.9583 | 0.6861 | -132.6131 | -8.9394 | -1.8476 | -3.0607 | -10.8699 | -9.7058 | -1.7978 |  | -5.3753 | -4.7658 | 4.0492 | 3.3738 | 3.3607 | 0.9607 | 10.6122 | 13.9466 | 14.5185 | 10.8735 | -0.0004 | -0.0029 | 0.0005 | 0.004 | 0.0009 | -0.0006 | 0.0003 | -0.0058 | -0.024 | -360.1188 | 17.68 | -360.6327 | 18.0475 | -361.0112 | 18.1707 | -361.0081 | 17.5404 | -352.9091 | 18.7641 | -352.9367 | 16.8197
11:29 | 575 | 18.1135 | 192.1879 | 433.8826 | 438.6816 | -21.1912 | -48.4145 | 0.3964 | -0.8039 | -8.1861 | -8.246 | -3.6169 | -4.2643 | 1.4558 | -5.573 | 0.5796 | 0.6156 | 0.9588 | 0.6871 | -132.5442 | -8.8236 | -1.7718 | -2.9093 | -10.9299 | -9.607 | -1.8083 |  | -5.3448 | -4.7955 | 4.0499 | 3.3718 | 3.3592 | 0.9601 | 10.5717 | 13.9352 | 14.5542 | 10.8789 | -0.0002 | -0.0026 | 0.0004 | 0.0035 | 0.0008 | -0.0008 | 0.0169 | -0.0145 | -0.012 | -360.125 | 17.6861 | -360.6143 | 18.029 | -360.9466 | 18.1522 | -361.0112 | 17.5404 | -352.9491 | 18.7785 | -352.946 | 16.8135
11:29 | 576 | 18.1236 | 192.1075 | 433.8542 | 438.671 | -21.2787 | -48.2719 | 0.3093 | -0.819 | -8.1936 | -8.3228 | -3.6948 | -4.2526 | 1.4979 | -5.5417 | 0.5791 | 0.6121 | 0.9538 | 0.686 | -132.5686 | -8.8787 | -1.7756 | -2.9935 | -11.0358 | -9.6798 | -1.8343 |  | -5.4273 | -4.8369 | 4.0485 | 3.3744 | 3.3602 | 0.9611 | 10.5913 | 13.9491 | 14.5338 | 10.8291 | 0.0001 | -0.0029 | 0.0003 | 0.0032 | 0.0005 | -0.0005 | -0.0007 | 0.0054 | -0.011 | -360.1742 | 17.7108 | -360.6789 | 18.0188 | -360.9343 | 18.1399 | -361.0481 | 17.5671 | -352.9706 | 18.8011 | -352.9583 | 16.7991
11:29 | 577 | 18.1065 | 192.1296 | 433.7923 | 438.6167 | -21.1586 | -48.2784 | 0.3486 | -0.7655 | -8.1773 | -8.2263 | -3.6697 | -4.2336 | 1.4583 | -5.5535 | 0.5797 | 0.6138 | 0.9591 | 0.6871 | -132.4934 | -8.8526 | -1.7478 | -2.8646 | -10.9587 | -9.7173 | -1.7909 |  | -5.3264 | -4.7022 | 4.0494 | 3.3713 | 3.36 | 0.9614 | 10.572 | 13.9172 | 14.4796 | 10.8116 | 0.0001 | -0.0028 | 0.0005 | 0.0037 | 0.0009 | -0.0006 | 0.0053 | -0.0074 | -0.0104 | -360.1558 | 17.7046 | -360.6266 | 18.0249 | -360.9251 | 18.1194 | -360.9866 | 17.5465 | -352.9367 | 18.7949 | -352.946 | 16.7909
11:29 | 578 | 18.0733 | 192.0551 | 433.7317 | 438.5669 | -21.1574 | -48.4195 | 0.3441 | -0.797 | -8.233 | -8.2507 | -3.6045 | -4.2605 | 1.4735 | -5.536 | 0.5804 | 0.6162 | 0.9524 | 0.6866 | -132.6538 | -8.7944 | -1.8271 | -2.8655 | -11.0876 | -9.849 | -1.9316 |  | -5.3748 | -4.8019 | 4.0473 | 3.3736 | 3.3574 | 0.9625 | 10.5833 | 13.9061 | 14.5185 | 10.81 | 0 | -0.003 | 0.0009 | 0.0038 | 0.001 | 0.0003 | 0.0193 | -0.0119 | 0.0102 | -360.1311 | 17.6923 | -360.6666 | 18.0434 | -360.9651 | 18.1543 | -360.9835 | 17.5568 | -353.0014 | 18.7928 | -352.9644 | 16.8135
11:29 | 579 | 18.1624 | 192.1147 | 433.8783 | 438.67 | -21.2606 | -48.4184 | 0.3854 | -0.8055 | -8.2096 | -8.3005 | -3.6327 | -4.2494 | 1.4508 | -5.5429 | 0.5795 | 0.6171 | 0.9536 | 0.6855 | -132.6612 | -8.804 | -1.7762 | -2.8749 | -10.9964 | -9.7905 | -1.8298 |  | -5.4535 | -4.7814 | 4.0467 | 3.3741 | 3.36 | 0.9625 | 10.6041 | 13.9674 | 14.5678 | 10.8714 | -0.0005 | -0.0028 | 0.0005 | 0.0038 | 0.0005 | -0.001 | 0.0007 | -0.0067 | 0.0026 | -360.1219 | 17.6841 | -360.645 | 18.0516 | -360.9743 | 18.1584 | -361.0112 | 17.5321 | -352.906 | 18.7703 | -352.9891 | 16.8156
11:29 | 580 | 18.1254 | 192.1093 | 433.9544 | 438.5792 | -21.3438 | -48.36 | 0.3863 | -0.7522 | -8.2611 | -8.2434 | -3.6674 | -4.2847 | 1.4831 | -5.6061 | 0.579 | 0.6139 | 0.9543 | 0.6852 | -132.6463 | -8.8442 | -1.7912 | -2.7713 | -10.9571 | -9.7954 | -1.8841 |  | -5.4134 | -4.7653 | 4.0486 | 3.3735 | 3.3586 | 0.9625 | 10.5924 | 13.9503 | 14.5236 | 10.8532 | -0.0001 | -0.0029 | 0.0012 | 0.004 | 0.0004 | -0.0003 | 0.011 | 0.0035 | 0.0108 | -360.1034 | 17.6594 | -360.5989 | 18.0434 | -360.9774 | 18.1604 | -361.0112 | 17.5342 | -352.8752 | 18.7518 | -352.9491 | 16.8115
11:29 | 581 | 18.189 | 192.0988 | 433.8367 | 438.6635 | -21.1958 | -48.3007 | 0.4225 | -0.7868 | -8.1585 | -8.3449 | -3.651 | -4.3453 | 1.4087 | -5.6557 | 0.5809 | 0.6188 | 0.9598 | 0.6849 | -132.5831 | -8.8974 | -1.7676 | -2.8097 | -10.9148 | -9.6608 | -1.8642 |  | -5.4247 | -4.7473 | 4.0463 | 3.3761 | 3.3558 | 0.963 | 10.6028 | 13.9666 | 14.5233 | 10.8691 | -0.0001 | -0.0031 | 0.0009 | 0.0041 | 0.0008 | -0.0009 | 0.0049 | -0.0064 | -0.0036 | -360.1373 | 17.6944 | -360.6573 | 18.0639 | -360.9958 | 18.1625 | -361.0204 | 17.5629 | -352.9706 | 18.7805 | -352.9737 | 16.8238
11:29 | 582 | 18.1459 | 191.9973 | 433.8631 | 438.5406 | -21.1795 | -48.395 | 0.3457 | -0.706 | -8.2235 | -8.3384 | -3.7099 | -4.2934 | 1.4161 | -5.5877 | 0.579 | 0.6195 | 0.9582 | 0.6867 | -132.6433 | -8.9246 | -1.8127 | -2.9178 | -10.9237 | -9.633 | -1.8501 |  | -5.4211 | -4.8324 | 4.0478 | 3.3749 | 3.3581 | 0.9624 | 10.6191 | 13.971 | 14.5845 | 10.88 | 0.0001 | -0.0029 | 0.0003 | 0.0037 | 0.0003 | -0.0007 | 0.0059 | 0.0021 | -0.0094 | -360.1527 | 17.6923 | -360.6173 | 18.0126 | -360.8912 | 18.1379 | -361.0112 | 17.5424 | -352.9183 | 18.7723 | -352.9583 | 16.7827
11:29 | 583 | 18.202 | 192.1075 | 433.9489 | 438.689 | -21.3431 | -48.4395 | 0.4063 | -0.6593 | -8.2496 | -8.2454 | -3.6256 | -4.3519 | 1.3669 | -5.6815 | 0.5796 | 0.6152 | 0.9555 | 0.6866 | -132.6887 | -8.8362 | -1.7244 | -2.8633 | -11.0519 | -9.587 | -1.8317 |  | -5.4137 | -4.7617 | 4.0476 | 3.3735 | 3.3587 | 0.9638 | 10.6005 | 13.947 | 14.5795 | 10.8319 | -0.0002 | -0.0027 | 0.0006 | 0.0033 | 0.0005 | -0.0006 | 0.0023 | 0.0012 | -0.0064 | -360.165 | 17.7026 | -360.6573 | 18.029 | -360.9281 | 18.1337 | -361.0051 | 17.5527 | -352.9798 | 18.799 | -352.9829 | 16.7991
11:29 | 584 | 18.2951 | 192.2326 | 433.9986 | 438.7631 | -21.2497 | -48.4239 | 0.4621 | -0.7125 | -8.1593 | -8.2935 | -3.683 | -4.282 | 1.4167 | -5.6217 | 0.5799 | 0.6195 | 0.9593 | 0.6855 | -132.6597 | -8.7965 | -1.7746 | -2.8115 | -11.0467 | -9.6317 | -1.8785 |  | -5.4031 | -4.7727 | 4.0491 | 3.3725 | 3.3596 | 0.9636 | 10.6157 | 13.9558 | 14.5794 | 10.8829 | -0.0007 | -0.0029 | 0.0003 | 0.0029 | 0.0008 | -0.0009 | -0.0027 | 0.0019 | -0.0337 | -360.1158 | 17.6882 | -360.645 | 18.0455 | -360.9804 | 18.1604 | -361.0081 | 17.5342 | -352.9152 | 18.7805 | -352.9521 | 16.8053
11:29 | 585 | 18.2706 | 192.2427 | 434.0165 | 438.7456 | -21.2759 | -48.4086 | 0.4358 | -0.6931 | -8.186 | -8.3049 | -3.7073 | -4.2405 | 1.4814 | -5.5441 | 0.58 | 0.6215 | 0.9612 | 0.687 | -132.6416 | -8.8817 | -1.8659 | -2.8872 | -11.0597 | -9.6168 | -1.8395 |  | -5.4331 | -4.7855 | 4.0478 | 3.3713 | 3.3595 | 0.9626 | 10.581 | 13.9558 | 14.5273 | 10.854 | -0.0001 | -0.0028 | 0.0007 | 0.0035 | 0.0008 | -0.0004 | 0.0179 | 0.0026 | 0.0006 | -360.1342 | 17.6738 | -360.6143 | 18.0352 | -360.962 | 18.1645 | -361.0235 | 17.5486 | -352.9367 | 18.7579 | -352.9244 | 16.8012
11:29 | 586 | 18.1612 | 192.2242 | 434.0115 | 438.7336 | -21.336 | -48.4112 | 0.3148 | -0.6774 | -8.1446 | -8.2489 | -3.6722 | -4.3609 | 1.4253 | -5.5783 | 0.5801 | 0.6184 | 0.9589 | 0.6854 | -132.53 | -8.883 | -1.8633 | -2.9381 | -11.0422 | -9.7544 | -1.8823 |  | -5.4138 | -4.7674 | 4.047 | 3.3769 | 3.3564 | 0.9633 | 10.5786 | 13.9362 | 14.5546 | 10.863 | -0.0001 | -0.0032 | 0.0012 | 0.0038 | 0.0008 | -0.0009 | 0.0133 | 0.0021 | -0.0121 | -360.1496 | 17.6923 | -360.6666 | 18.0516 | -360.9374 | 18.1645 | -361.042 | 17.5465 | -352.906 | 18.7908 | -352.9675 | 16.793
11:29 | 587 | 18.2579 | 192.2342 | 433.9335 | 438.7419 | -21.2705 | -48.4741 | 0.4549 | -0.7033 | -8.1842 | -8.1449 | -3.6664 | -4.2663 | 1.4965 | -5.6291 | 0.5793 | 0.618 | 0.9563 | 0.6842 | -132.6289 | -8.907 | -1.827 | -2.9252 | -11.0289 | -9.7326 | -1.7984 |  | -5.3692 | -4.7861 | 4.0474 | 3.3739 | 3.3613 | 0.9626 | 10.5696 | 13.944 | 14.5079 | 10.8433 | -0.0003 | -0.0029 | 0.0007 | 0.0038 | 0.0005 | -0.0006 | 0.0169 | -0.0146 | -0.0109 | -360.1435 | 17.68 | -360.5989 | 18.0414 | -360.9312 | 18.1379 | -360.9897 | 17.5486 | -352.8844 | 18.762 | -352.9183 | 16.7868
11:30 | 588 | 18.3028 | 192.1921 | 433.9445 | 438.7984 | -21.2338 | -48.3728 | 0.4088 | -0.6771 | -8.146 | -8.3034 | -3.6729 | -4.2684 | 1.5363 | -5.561 | 0.5797 | 0.6144 | 0.9597 | 0.685 | -132.5354 | -8.8999 | -1.7988 | -2.9408 | -10.934 | -9.7379 | -1.78 |  | -5.3243 | -4.7971 | 4.0476 | 3.3749 | 3.3611 | 0.9644 | 10.5741 | 13.9373 | 14.5375 | 10.8414 | -0.0004 | -0.0029 | 0.0011 | 0.0043 | 0.0009 | -0.0006 | 0.0052 | -0.0047 | -0.0205 | -360.1465 | 17.7046 | -360.6512 | 18.0578 | -360.962 | 18.1604 | -361.0481 | 17.5609 | -352.9583 | 18.7867 | -352.9706 | 16.7971
11:30 | 589 | 18.2925 | 192.1245 | 434.0087 | 438.8313 | -21.2839 | -48.3732 | 0.4015 | -0.6952 | -8.1974 | -8.3306 | -3.7086 | -4.289 | 1.4834 | -5.5047 | 0.5808 | 0.6173 | 0.9574 | 0.6868 | -132.5393 | -8.9091 | -1.8345 | -2.8062 | -10.9685 | -9.7175 | -1.7099 |  | -5.3626 | -4.8418 | 4.0461 | 3.374 | 3.3581 | 0.9644 | 10.611 | 13.9457 | 14.5365 | 10.889 | -0.0002 | -0.0029 | 0.0004 | 0.0039 | 0.0007 | -0.0002 | 0.0067 | 0.0002 | -0.0085 | -360.1188 | 17.6985 | -360.6173 | 18.0229 | -360.9343 | 18.1358 | -360.9897 | 17.5424 | -352.9183 | 18.7846 | -352.9337 | 16.7724
11:30 | 590 | 18.276 | 192.1215 | 433.9275 | 438.8595 | -21.2919 | -48.5315 | 0.2982 | -0.7 | -8.1254 | -8.2755 | -3.6638 | -4.2357 | 1.4368 | -5.5756 | 0.5814 | 0.6149 | 0.9597 | 0.6885 | -132.5987 | -8.9185 | -1.7914 | -2.8128 | -11.0218 | -9.6703 | -1.7319 |  | -5.3349 | -4.8096 | 4.0459 | 3.3763 | 3.3577 | 0.9643 | 10.6064 | 13.9641 | 14.5427 | 10.8558 | 0.0005 | -0.003 | 0.0003 | 0.0035 | 0.0006 | -0.0006 | 0.0004 | -0.0129 | -0.0084 | -360.1558 | 17.6861 | -360.6696 | 18.0537 | -360.9712 | 18.1379 | -360.9804 | 17.5629 | -352.9552 | 18.7764 | -352.9614 | 16.8053
11:30 | 591 | 18.3757 | 192.1585 | 434.1252 | 438.8612 | -21.3417 | -48.422 | 0.2617 | -0.7588 | -8.2322 | -8.3794 | -3.6533 | -4.2479 | 1.4104 | -5.6572 | 0.5809 | 0.6163 | 0.9557 | 0.686 | -132.6586 | -8.9178 | -1.8785 | -2.8553 | -10.9832 | -9.7332 | -1.7532 |  | -5.3963 | -4.8408 | 4.0479 | 3.3756 | 3.3598 | 0.9652 | 10.581 | 13.9558 | 14.5736 | 10.8656 | -0.0002 | -0.0032 | 0.0005 | 0.0033 | 0.0005 | -0.0008 | -0.0079 | 0.0032 | -0.0007 | -360.1065 | 17.7005 | -360.645 | 18.0414 | -360.9866 | 18.1522 | -361.0297 | 17.5506 | -352.906 | 18.7785 | -352.946 | 16.7889
11:30 | 592 | 18.3449 | 192.1659 | 434.1006 | 438.8748 | -21.3265 | -48.5686 | 0.2394 | -0.7471 | -8.1896 | -8.3618 | -3.6205 | -4.2497 | 1.4266 | -5.6647 | 0.5815 | 0.6166 | 0.9575 | 0.6865 | -132.6629 | -8.8722 | -1.7937 | -2.8886 | -11.0349 | -9.7451 | -1.8107 |  | -5.3506 | -4.8195 | 4.0473 | 3.3766 | 3.3556 | 0.9639 | 10.6122 | 13.993 | 14.5774 | 10.8847 | -0.0005 | -0.0028 | 0 | 0.0028 | 0.0003 | -0.0008 | 0.0092 | -0.0189 | -0.0221 | -360.1435 | 17.6636 | -360.5804 | 18.0126 | -360.962 | 18.1687 | -361.0328 | 17.5424 | -352.9337 | 18.762 | -352.9091 | 16.7827
11:30 | 593 | 18.2419 | 192.1826 | 433.9523 | 438.8558 | -21.3828 | -48.5143 | 0.2495 | -0.6729 | -8.1383 | -8.1913 | -3.6264 | -4.2633 | 1.403 | -5.5776 | 0.5815 | 0.6143 | 0.9571 | 0.6875 | -132.6604 | -8.8565 | -1.8636 | -2.8049 | -11.0337 | -9.7422 | -1.7196 |  | -5.3769 | -4.8828 | 4.0475 | 3.3737 | 3.3584 | 0.9634 | 10.5811 | 13.9441 | 14.5436 | 10.866 | -0.0004 | -0.0028 | 0.0003 | 0.004 | 0.0005 | -0.0009 | 0.0025 | -0.0088 | -0.0293 | -360.1281 | 17.6697 | -360.6081 | 18.0455 | -360.962 | 18.1543 | -361.0789 | 17.5691 | -352.946 | 18.7682 | -352.9121 | 16.7889
11:30 | 594 | 18.2103 | 192.1887 | 434.121 | 438.7903 | -21.3836 | -48.5343 | 0.2405 | -0.7948 | -8.122 | -8.3759 | -3.7066 | -4.3551 | 1.373 | -5.6227 | 0.5811 | 0.6152 | 0.9554 | 0.6878 | -132.6078 | -8.8245 | -1.827 | -2.8365 | -11.0118 | -9.7228 | -1.7177 |  | -5.4044 | -4.7736 | 4.0472 | 3.3749 | 3.3568 | 0.963 | 10.5982 | 13.9331 | 14.5594 | 10.8529 | 0.0003 | -0.0026 | 0.0013 | 0.0041 | 0 | -0.0009 | 0.0077 | -0.0022 | -0.0352 | -360.1281 | 17.6882 | -360.642 | 18.0147 | -360.9189 | 18.142 | -361.0174 | 17.5363 | -352.9398 | 18.7826 | -352.946 | 16.7889
11:30 | 595 | 18.2983 | 192.1898 | 434.041 | 438.8109 | -21.3946 | -48.5674 | 0.1879 | -0.8112 | -8.1637 | -8.3531 | -3.7073 | -4.3549 | 1.3355 | -5.5589 | 0.5795 | 0.6111 | 0.9574 | 0.6867 | -132.4794 | -8.8099 | -1.7874 | -2.916 | -10.9955 | -9.6771 | -1.7257 |  | -5.4377 | -4.8301 | 4.046 | 3.3742 | 3.3583 | 0.9633 | 10.6076 | 13.9247 | 14.5603 | 10.8515 | 0.0001 | -0.0031 | 0.0007 | 0.004 | 0.0008 | -0.0009 | 0.0127 | -0.0037 | -0.0032 | -360.1158 | 17.7108 | -360.6758 | 18.0516 | -360.9866 | 18.142 | -360.9589 | 17.5342 | -352.9244 | 18.8031 | -352.9706 | 16.8074
11:30 | 596 | 18.3437 | 192.2304 | 434.1508 | 438.8297 | -21.4702 | -48.5414 | 0.2447 | -0.7604 | -8.181 | -8.4452 | -3.6437 | -4.2801 | 1.3467 | -5.6741 | 0.5813 | 0.6099 | 0.954 | 0.6867 | -132.5397 | -8.8845 | -1.8669 | -2.8241 | -10.9444 | -9.7816 | -1.7256 |  | -5.284 | -4.8755 | 4.0473 | 3.3749 | 3.36 | 0.9644 | 10.5973 | 13.9545 | 14.548 | 10.8649 | -0.0004 | -0.0029 | 0.0003 | 0.0038 | 0.0003 | -0.0004 | 0.0068 | -0.0106 | -0.0103 | -360.1742 | 17.7026 | -360.6789 | 18.0496 | -360.9774 | 18.1399 | -361.002 | 17.5342 | -352.9152 | 18.7887 | -352.9798 | 16.8094
11:30 | 597 | 18.3361 | 192.2937 | 434.0179 | 438.8615 | -21.4488 | -48.5521 | 0.207 | -0.7803 | -8.1334 | -8.4817 | -3.6727 | -4.2837 | 1.4921 | -5.6044 | 0.5802 | 0.6165 | 0.9535 | 0.6867 | -132.5798 | -8.8811 | -1.7519 | -2.86 | -10.9354 | -9.7443 | -1.6737 |  | -5.3813 | -4.9186 | 4.0466 | 3.3765 | 3.3599 | 0.9637 | 10.5809 | 13.9503 | 14.5236 | 10.8706 | -0.0002 | -0.0022 | 0.0002 | 0.0036 | 0.0006 | -0.0008 | 0.0061 | 0.0071 | -0.0081 | -360.0942 | 17.6615 | -360.6235 | 18.0331 | -360.9466 | 18.1502 | -361.0266 | 17.5404 | -352.9029 | 18.7682 | -352.9429 | 16.7971
11:30 | 598 | 18.316 | 192.2503 | 434.0391 | 438.8451 | -21.3952 | -48.5268 | 0.2649 | -0.8551 | -8.1841 | -8.3676 | -3.6854 | -4.3351 | 1.5203 | -5.5624 | 0.5783 | 0.6182 | 0.9559 | 0.6882 | -132.6321 | -8.85 | -1.8936 | -2.8945 | -10.9501 | -9.7744 | -1.776 |  | -5.4434 | -4.8854 | 4.0459 | 3.374 | 3.358 | 0.9647 | 10.6053 | 13.9511 | 14.5334 | 10.8844 | -0.0003 | -0.0027 | 0.0002 | 0.0033 | 0.0003 | -0.0004 | 0.0097 | -0.003 | -0.0179 | -360.1373 | 17.6718 | -360.5773 | 18.0188 | -360.9435 | 18.1604 | -361.0635 | 17.5691 | -352.946 | 18.7703 | -352.9244 | 16.7745
11:30 | 599 | 18.3149 | 192.2184 | 433.9545 | 438.7782 | -21.5162 | -48.5649 | 0.1756 | -0.8463 | -8.1256 | -8.4544 | -3.6864 | -4.2681 | 1.4696 | -5.5435 | 0.5799 | 0.6155 | 0.9551 | 0.687 | -132.5428 | -8.8028 | -1.7784 | -2.8577 | -10.941 | -9.7356 | -1.6893 |  | -5.4083 | -4.8622 | 4.0445 | 3.3709 | 3.357 | 0.9648 | 10.581 | 13.9211 | 14.4752 | 10.8194 | 0.0007 | -0.0026 | 0.0012 | 0.0035 | 0.0007 | -0.0005 | 0.0079 | -0.0047 | -0.0092 | -360.1342 | 17.6759 | -360.5989 | 18.0126 | -360.9251 | 18.1604 | -361.0512 | 17.5568 | -352.9429 | 18.7723 | -352.9152 | 16.7766
11:30 | 600 | 18.3657 | 192.1568 | 433.9939 | 438.7767 | -21.4991 | -48.5509 | 0.1525 | -0.8389 | -8.0517 | -8.369 | -3.6284 | -4.2386 | 1.5179 | -5.5434 | 0.5803 | 0.6158 | 0.9543 | 0.6858 | -132.5919 | -8.7417 | -1.8902 | -2.8196 | -10.9747 | -9.7454 | -1.7296 |  | -5.398 | -4.8485 | 4.0454 | 3.373 | 3.359 | 0.9622 | 10.5811 | 13.9268 | 14.5321 | 10.8486 | -0.0003 | -0.0031 | 0.0008 | 0.0034 | 0.0005 | -0.001 | 0.0017 | -0.011 | -0.0154 | -360.1219 | 17.6841 | -360.6266 | 18.027 | -360.9466 | 18.1337 | -360.9712 | 17.5404 | -352.9214 | 18.7764 | -352.9398 | 16.793
11:30 | 601 | 18.2993 | 192.2388 | 434.005 | 438.7787 | -21.5062 | -48.5248 | 0.2223 | -0.8737 | -8.0784 | -8.3605 | -3.6901 | -4.253 | 1.4949 | -5.5018 | 0.5807 | 0.6121 | 0.9564 | 0.6867 | -132.6019 | -8.8752 | -1.8745 | -2.8096 | -10.9689 | -9.7852 | -1.7304 |  | -5.4271 | -4.8926 | 4.0477 | 3.3723 | 3.3592 | 0.9648 | 10.5881 | 13.9394 | 14.544 | 10.8501 | -0.0009 | -0.0029 | 0.0004 | 0.0036 | 0.0005 | -0.0005 | 0.0112 | -0.008 | -0.0123 | -360.1496 | 17.7005 | -360.6943 | 18.0721 | -361.0081 | 18.1481 | -360.9804 | 17.5342 | -352.9552 | 18.7949 | -352.9952 | 16.8258
11:30 | 602 | 18.242 | 192.2361 | 434.0661 | 438.7641 | -21.4829 | -48.6136 | 0.2181 | -0.9137 | -8.1164 | -8.4012 | -3.6991 | -4.2423 | 1.4534 | -5.5359 | 0.5806 | 0.6162 | 0.9556 | 0.6872 | -132.6657 | -8.8912 | -1.918 | -2.8187 | -10.989 | -9.6851 | -1.6603 |  | -5.3529 | -4.8317 | 4.0466 | 3.3736 | 3.3589 | 0.9656 | 10.5729 | 13.9478 | 14.5256 | 10.8746 | -0.0003 | -0.0028 | 0.0012 | 0.0041 | 0.001 | -0.001 | 0.0145 | -0.0085 | -0.0203 | -360.0911 | 17.6882 | -360.6666 | 18.0372 | -360.9497 | 18.1502 | -360.9897 | 17.5178 | -352.9244 | 18.7846 | -352.9737 | 16.8053
11:30 | 603 | 18.2815 | 192.2291 | 433.9127 | 438.8118 | -21.4737 | -48.5059 | 0.2187 | -0.8269 | -8.1596 | -8.3372 | -3.6757 | -4.2727 | 1.3408 | -5.5934 | 0.5794 | 0.6152 | 0.9579 | 0.6857 | -132.5849 | -8.8929 | -1.9556 | -2.8528 | -11.0198 | -9.7568 | -1.7598 |  | -5.3517 | -4.8318 | 4.047 | 3.3717 | 3.3575 | 0.9664 | 10.6087 | 13.949 | 14.5096 | 10.9046 | -0.0002 | -0.0031 | 0.0004 | 0.0036 | 0.0007 | -0.0003 | -0.0026 | 0.0035 | -0.0086 | -360.1342 | 17.6718 | -360.6143 | 18.0188 | -360.9651 | 18.1543 | -361.0081 | 17.5445 | -352.9367 | 18.7641 | -352.9152 | 16.7827
11:30 | 604 | 18.3906 | 192.2255 | 433.9646 | 438.8524 | -21.4897 | -48.4965 | 0.2388 | -0.8766 | -8.1981 | -8.3193 | -3.7793 | -4.3643 | 1.4372 | -5.6363 | 0.579 | 0.6192 | 0.9578 | 0.6869 | -132.5928 | -8.904 | -1.9876 | -2.8375 | -11.006 | -9.7414 | -1.7075 |  | -5.3655 | -4.7507 | 4.0454 | 3.3731 | 3.3577 | 0.9667 | 10.612 | 13.9643 | 14.5621 | 10.8666 | 0.0001 | -0.0029 | 0.0008 | 0.004 | 0.0008 | -0.0005 | -0.0043 | 0.0026 | -0.0253 | -360.1711 | 17.6779 | -360.6173 | 18.0188 | -360.9527 | 18.1522 | -361.0574 | 17.5773 | -352.9768 | 18.7723 | -352.9152 | 16.7807
11:30 | 605 | 18.3654 | 192.304 | 434.0131 | 438.8487 | -21.4814 | -48.5889 | 0.1635 | -0.8267 | -8.2651 | -8.2656 | -3.7069 | -4.2833 | 1.3993 | -5.6547 | 0.5793 | 0.6172 | 0.9575 | 0.6874 | -132.5665 | -8.865 | -1.9987 | -2.8217 | -10.9219 | -9.8254 | -1.6648 |  | -5.3535 | -4.8207 | 4.0465 | 3.3723 | 3.3618 | 0.9656 | 10.6191 | 13.9653 | 14.5845 | 10.9089 | -0.0001 | -0.0027 | 0.0006 | 0.0043 | 0 | -0.0007 | 0.0137 | -0.0127 | -0.0095 | -360.1281 | 17.6841 | -360.6389 | 18.0126 | -360.922 | 18.1399 | -360.9958 | 17.5445 | -352.9275 | 18.7846 | -352.9429 | 16.7807
11:30 | 606 | 18.4026 | 192.2489 | 434.0141 | 438.8203 | -21.4983 | -48.5039 | 0.2057 | -0.9503 | -8.2216 | -8.3814 | -3.6719 | -4.2559 | 1.4733 | -5.5216 | 0.5793 | 0.6191 | 0.9593 | 0.6892 | -132.4572 | -8.8347 | -1.8808 | -2.7721 | -10.9104 | -9.7289 | -1.5942 |  | -5.3091 | -4.8233 | 4.046 | 3.3736 | 3.3573 | 0.9656 | 10.6364 | 13.9596 | 14.5856 | 10.8796 | -0.0004 | -0.0026 | 0.0004 | 0.0036 | 0.0012 | -0.0002 | 0.0124 | -0.0194 | -0.0175 | -360.0973 | 17.6861 | -360.642 | 18.0331 | -360.9835 | 18.1502 | -361.0266 | 17.5424 | -352.9121 | 18.7826 | -352.9675 | 16.8053
11:30 | 607 | 18.3085 | 192.1955 | 434.0208 | 438.8738 | -21.5008 | -48.59 | 0.1734 | -0.8621 | -8.2763 | -8.3286 | -3.6799 | -4.2413 | 1.4817 | -5.5362 | 0.5787 | 0.6228 | 0.9568 | 0.6876 | -132.4812 | -8.787 | -1.8006 | -2.8348 | -10.954 | -9.7378 | -1.6407 |  | -5.3415 | -4.8657 | 4.0467 | 3.3748 | 3.3547 | 0.967 | 10.5891 | 13.9293 | 14.5358 | 10.8562 | 0 | -0.0032 | 0.0009 | 0.004 | 0.0008 | -0.0003 | 0.0077 | -0.0173 | -0.0123 | -360.1742 | 17.6779 | -360.6173 | 18.0229 | -360.9527 | 18.1584 | -360.9866 | 17.5445 | -352.9152 | 18.7744 | -352.9367 | 16.793
11:30 | 608 | 18.3623 | 192.3243 | 433.9582 | 438.9275 | -21.5194 | -48.5776 | 0.1886 | -0.8603 | -8.2403 | -8.4318 | -3.7474 | -4.3128 | 1.4998 | -5.594 | 0.5788 | 0.6182 | 0.9551 | 0.6854 | -132.5354 | -8.7974 | -1.9294 | -2.9937 | -10.9817 | -9.7988 | -1.6252 |  | -5.4223 | -4.8117 | 4.0468 | 3.373 | 3.3608 | 0.9677 | 10.5881 | 13.9394 | 14.5555 | 10.8501 | -0.0001 | -0.0031 | 0.0006 | 0.0034 | 0.0006 | -0.0008 | 0.0074 | 0.003 | 0.0125 | -360.1311 | 17.6841 | -360.6635 | 18.0167 | -360.9189 | 18.1461 | -361.0143 | 17.5383 | -352.8752 | 18.7682 | -352.9367 | 16.7909
11:30 | 609 | 18.3853 | 192.2005 | 433.8602 | 438.9085 | -21.3757 | -48.4878 | 0.2537 | -0.8269 | -8.2615 | -8.3573 | -3.7538 | -4.1825 | 1.4273 | -5.5585 | 0.5806 | 0.6185 | 0.9584 | 0.6896 | -132.5557 | -8.7667 | -2.0354 | -3.078 | -10.9415 | -9.8064 | -1.7281 |  | -5.4162 | -4.8229 | 4.0464 | 3.3726 | 3.3581 | 0.9668 | 10.6237 | 13.9584 | 14.5495 | 10.8612 | -0.0003 | -0.0029 | 0.0009 | 0.0037 | 0.0013 | -0.0005 | -0.0014 | -0.0048 | -0.0367 | -360.1435 | 17.682 | -360.645 | 18.0331 | -360.962 | 18.1543 | -361.0328 | 17.5445 | -352.9367 | 18.7928 | -352.9644 | 16.7991
11:30 | 610 | 18.3704 | 192.2724 | 434.0054 | 438.8545 | -21.356 | -48.3631 | 0.3376 | -0.8124 | -8.3065 | -8.4623 | -3.7087 | -4.2021 | 1.4742 | -5.5974 | 0.5812 | 0.6187 | 0.9548 | 0.6869 | -132.4699 | -8.7928 | -1.8425 | -3.1074 | -10.9032 | -9.7887 | -1.7722 |  | -5.3836 | -4.8317 | 4.0463 | 3.3754 | 3.3579 | 0.9657 | 10.5869 | 13.9324 | 14.531 | 10.8317 | -0.0009 | -0.0029 | 0.0011 | 0.0039 | 0.0004 | -0.0007 | 0.0066 | -0.0091 | -0.0077 | -360.1373 | 17.68 | -360.6019 | 18.0229 | -360.9681 | 18.1337 | -361.0143 | 17.5691 | -352.9306 | 18.7661 | -352.9275 | 16.7848
11:30 | 611 | 18.3692 | 192.2345 | 434.0823 | 438.8641 | -21.2964 | -48.4191 | 0.3393 | -0.8708 | -8.299 | -8.4817 | -3.8061 | -4.1956 | 1.4553 | -5.6159 | 0.5801 | 0.6182 | 0.9557 | 0.6882 | -132.5398 | -8.8426 | -1.9093 | -2.9752 | -10.9544 | -9.7733 | -1.7209 |  | -5.3621 | -4.8339 | 4.046 | 3.3736 | 3.3586 | 0.9675 | 10.582 | 13.9515 | 14.5481 | 10.8601 | -0.0002 | -0.0027 | 0.0008 | 0.0035 | 0.0008 | -0.0009 | -0.0061 | -0.0002 | -0.0312 | -360.165 | 17.6759 | -360.6266 | 18.0085 | -360.9004 | 18.1666 | -361.0481 | 17.5465 | -352.9244 | 18.7785 | -352.9244 | 16.7704
11:30 | 612 | 18.3648 | 192.2435 | 433.9965 | 438.9381 | -21.3606 | -48.3916 | 0.2364 | -0.7494 | -8.2556 | -8.4047 | -3.78 | -4.2426 | 1.5217 | -5.6043 | 0.5795 | 0.6205 | 0.9561 | 0.6869 | -132.534 | -8.8386 | -1.9205 | -2.8396 | -10.894 | -9.855 | -1.7234 |  | -5.3374 | -4.8188 | 4.0444 | 3.3755 | 3.3586 | 0.9664 | 10.604 | 13.9561 | 14.5352 | 10.8706 | 0 | -0.0031 | 0.0006 | 0.0037 | 0.0004 | -0.0001 | -0.0023 | 0.0058 | 0.0081 | -360.1465 | 17.6861 | -360.6389 | 18.027 | -360.9651 | 18.1481 | -360.9897 | 17.5547 | -352.9244 | 18.7969 | -352.9552 | 16.7868
11:30 | 613 | 18.3463 | 192.2457 | 433.97 | 438.8542 | -21.4112 | -48.5042 | 0.2876 | -0.67 | -8.2516 | -8.4166 | -3.7012 | -4.237 | 1.4412 | -5.6337 | 0.5796 | 0.6166 | 0.9558 | 0.6876 | -132.4897 | -8.7641 | -1.8849 | -2.8263 | -10.8979 | -9.8716 | -1.7279 |  | -5.3251 | -4.8244 | 4.0457 | 3.3741 | 3.3614 | 0.9654 | 10.604 | 13.9792 | 14.5757 | 10.8648 | 0 | -0.003 | 0.0007 | 0.0036 | 0.0008 | -0.0006 | -0.0079 | -0.0157 | -0.0212 | -360.0788 | 17.6779 | -360.6389 | 18.0516 | -361.002 | 18.1522 | -360.9958 | 17.5383 | -352.9244 | 18.7785 | -352.9337 | 16.8176
11:30 | 614 | 18.3882 | 192.1986 | 433.9748 | 438.8344 | -21.4203 | -48.5572 | 0.1769 | -0.8373 | -8.2315 | -8.3818 | -3.6716 | -4.2872 | 1.473 | -5.6239 | 0.5798 | 0.6172 | 0.9536 | 0.6881 | -132.5263 | -8.8543 | -1.9172 | -2.9451 | -10.8915 | -9.8369 | -1.7461 |  | -5.423 | -4.8465 | 4.0457 | 3.3792 | 3.3617 | 0.968 | 10.6006 | 13.9525 | 14.5079 | 10.8558 | 0.0002 | -0.0024 | 0.0006 | 0.0038 | 0.0005 | -0.0005 | -0.0088 | -0.0142 | -0.0125 | -360.1619 | 17.68 | -360.6573 | 18.0331 | -360.9681 | 18.142 | -360.962 | 17.5219 | -352.9091 | 18.7826 | -352.9521 | 16.8012
11:30 | 615 | 18.374 | 192.3024 | 434.0048 | 438.924 | -21.4143 | -48.385 | 0.2662 | -0.7909 | -8.1791 | -8.2443 | -3.7303 | -4.1732 | 1.4771 | -5.5007 | 0.579 | 0.6188 | 0.9535 | 0.6882 | -132.5417 | -8.908 | -1.8826 | -3.0117 | -10.9003 | -9.8106 | -1.7823 |  | -5.5167 | -4.8813 | 4.0459 | 3.3769 | 3.3578 | 0.9676 | 10.6134 | 13.965 | 14.5477 | 10.875 | -0.0003 | -0.0028 | 0.0007 | 0.0038 | 0.0005 | -0.0005 | 0.0036 | -0.011 | -0.0082 | -360.1404 | 17.6738 | -360.6327 | 18.0352 | -360.9804 | 18.1481 | -361.0143 | 17.5486 | -352.9367 | 18.7785 | -352.9491 | 16.795
11:30 | 616 | 18.2729 | 192.1607 | 434.0715 | 438.8654 | -21.3758 | -48.4809 | 0.2722 | -0.8381 | -8.1146 | -8.2537 | -3.6507 | -4.2191 | 1.5241 | -5.5794 | 0.5797 | 0.6174 | 0.9555 | 0.6874 | -132.4243 | -8.8113 | -1.8157 | -3.077 | -11.0176 | -9.9652 | -1.8844 |  | -5.4337 | -4.7971 | 4.0466 | 3.3758 | 3.3594 | 0.9685 | 10.5752 | 13.9385 | 14.5331 | 10.8598 | 0.0003 | -0.0031 | 0.0007 | 0.0036 | 0.0006 | -0.0007 | 0.0155 | -0.003 | 0.0012 | -360.1527 | 17.6636 | -360.6019 | 18.0126 | -360.922 | 18.1317 | -361.0389 | 17.565 | -352.9491 | 18.7744 | -352.8844 | 16.7663
11:30 | 617 | 18.3457 | 192.3408 | 434.1057 | 438.9768 | -21.3585 | -48.4434 | 0.2948 | -0.9072 | -8.1387 | -8.3361 | -3.6948 | -4.2138 | 1.5255 | -5.5811 | 0.5794 | 0.6133 | 0.9546 | 0.6873 | -132.4316 | -8.8499 | -1.8238 | -2.9459 | -10.9842 | -9.893 | -1.9048 |  | -5.4302 | -4.744 | 4.0455 | 3.3752 | 3.3571 | 0.9675 | 10.5948 | 13.9583 | 14.56 | 10.8731 | -0.0001 | -0.0033 | 0.0008 | 0.0035 | 0.0005 | -0.0008 | 0.0054 | -0.0116 | -0.0059 | -360.1465 | 17.6779 | -360.6143 | 18.0023 | -360.9097 | 18.1214 | -361.0235 | 17.5588 | -352.946 | 18.7867 | -352.9244 | 16.7724
11:30 | 618 | 18.334 | 192.3493 | 433.9907 | 439.0002 | -21.404 | -48.5024 | 0.2874 | -0.818 | -8.1248 | -8.2684 | -3.682 | -4.2555 | 1.5161 | -5.6041 | 0.5802 | 0.6136 | 0.9541 | 0.6856 | -132.4775 | -8.9045 | -1.8892 | -2.885 | -10.9622 | -10.0289 | -1.8168 |  | -5.498 | -4.7858 | 4.0454 | 3.3737 | 3.3563 | 0.9675 | 10.5982 | 13.9676 | 14.5352 | 10.8821 | 0 | -0.0025 | 0.0011 | 0.0037 | 0.0011 | -0.0009 | 0.0086 | 0.0043 | -0.0065 | -360.1465 | 17.6902 | -360.6389 | 18.027 | -360.9312 | 18.1194 | -361.0204 | 17.5547 | -352.9029 | 18.7785 | -352.9337 | 16.7807
11:30 | 619 | 18.2958 | 192.3224 | 433.9836 | 439.0016 | -21.3879 | -48.5031 | 0.2954 | -0.8151 | -8.1734 | -8.382 | -3.6636 | -4.3481 | 1.4668 | -5.6288 | 0.5791 | 0.6145 | 0.9517 | 0.6866 | -132.4526 | -8.9093 | -1.8577 | -2.9415 | -10.9805 | -9.8857 | -1.8587 |  | -5.4878 | -4.8148 | 4.0455 | 3.3763 | 3.3593 | 0.9686 | 10.5809 | 13.9502 | 14.5399 | 10.8652 | -0.0002 | -0.0026 | 0.0005 | 0.0036 | 0.0004 | -0.0007 | 0.0025 | -0.0169 | -0.0126 | -360.0758 | 17.6779 | -360.6358 | 18.0455 | -360.9897 | 18.1091 | -360.962 | 17.5301 | -352.9214 | 18.7805 | -352.9583 | 16.8053
11:30 | 620 | 18.3504 | 192.2878 | 434.0644 | 438.9455 | -21.3495 | -48.4436 | 0.3176 | -0.8332 | -8.0729 | -8.2336 | -3.7023 | -4.3487 | 1.4284 | -5.5889 | 0.5788 | 0.6131 | 0.9543 | 0.686 | -132.5228 | -8.9436 | -1.91 | -2.9327 | -10.8769 | -9.7974 | -1.817 |  | -5.4229 | -4.8022 | 4.0449 | 3.3741 | 3.3565 | 0.9672 | 10.6099 | 13.95 | 14.5157 | 10.8714 | 0 | -0.0027 | 0.0005 | 0.0035 | 0.0009 | -0.0008 | 0.0038 | -0.007 | -0.0004 | -360.125 | 17.682 | -360.682 | 18.0619 | -361.0112 | 18.1276 | -360.9835 | 17.528 | -352.8875 | 18.7764 | -352.9583 | 16.8156
11:30 | 621 | 18.3399 | 192.3166 | 433.9929 | 438.8576 | -21.3982 | -48.5203 | 0.2491 | -0.853 | -8.1595 | -8.4536 | -3.7941 | -4.2988 | 1.4898 | -5.5859 | 0.5789 | 0.6113 | 0.9531 | 0.687 | -132.4626 | -8.9155 | -1.8415 | -2.9035 | -10.9937 | -9.8732 | -1.8477 |  | -5.4076 | -4.7921 | 4.044 | 3.3741 | 3.3567 | 0.9669 | 10.5706 | 13.957 | 14.5287 | 10.8724 | 0.0002 | -0.0031 | 0.0004 | 0.0039 | 0.0004 | -0.0004 | 0.0008 | -0.0044 | -0.0161 | -360.1404 | 17.6677 | -360.6358 | 18.027 | -360.962 | 18.1112 | -360.9897 | 17.5178 | -352.8444 | 18.7805 | -352.9398 | 16.7868
11:30 | 622 | 18.2929 | 192.2987 | 434.0581 | 438.9143 | -21.4339 | -48.5995 | 0.2058 | -0.8623 | -8.1406 | -8.3608 | -3.6855 | -4.2882 | 1.4962 | -5.6857 | 0.5792 | 0.6127 | 0.9564 | 0.6875 | -132.546 | -8.9484 | -1.8877 | -2.7171 | -10.9678 | -9.8055 | -1.861 |  | -5.399 | -4.6889 | 4.0449 | 3.3752 | 3.3561 | 0.9679 | 10.5811 | 13.9499 | 14.5494 | 10.8891 | -0.0003 | -0.0033 | 0.0003 | 0.0037 | 0.0003 | -0.001 | 0.0043 | -0.015 | -0.0212 | -360.1527 | 17.6861 | -360.6327 | 18.0249 | -360.9835 | 18.1235 | -361.042 | 17.5773 | -352.9891 | 18.7867 | -352.9644 | 16.793
11:30 | 623 | 18.3365 | 192.2563 | 434.0722 | 439.0122 | -21.565 | -48.5668 | 0.1888 | -0.8923 | -8.2109 | -8.3786 | -3.6977 | -4.2721 | 1.5465 | -5.6956 | 0.5799 | 0.6155 | 0.9566 | 0.6859 | -132.5005 | -8.9426 | -1.7809 | -2.7908 | -11.0253 | -9.9802 | -1.8886 |  | -5.4713 | -4.7673 | 4.0455 | 3.3746 | 3.3583 | 0.9692 | 10.5705 | 13.9398 | 14.5413 | 10.8432 | -0.0005 | -0.0027 | 0.0007 | 0.004 | 0.0008 | -0.0001 | -0.0023 | -0.0189 | -0.0006 | -360.1127 | 17.6718 | -360.6296 | 17.9982 | -360.9189 | 18.0886 | -361.0112 | 17.5732 | -352.9183 | 18.7764 | -352.9244 | 16.7601
11:30 | 624 | 18.3642 | 192.1992 | 434.021 | 438.9347 | -21.4634 | -48.5473 | 0.1816 | -0.9186 | -8.1989 | -8.366 | -3.7828 | -4.2916 | 1.504 | -5.7085 | 0.579 | 0.6152 | 0.9554 | 0.6874 | -132.4658 | -9.0096 | -1.8157 | -2.8119 | -11.0408 | -9.8805 | -1.9311 |  | -5.4253 | -4.6937 | 4.0461 | 3.3765 | 3.3592 | 0.969 | 10.5961 | 13.9418 | 14.512 | 10.8696 | -0.0009 | -0.003 | 0.0005 | 0.0035 | 0.0004 | -0.0007 | 0.0078 | -0.0093 | -0.0036 | -360.1927 | 17.6985 | -360.6266 | 18.0147 | -360.9527 | 18.1214 | -361.0328 | 17.5753 | -352.946 | 18.8072 | -352.9614 | 16.7745
11:30 | 625 | 18.3237 | 192.2489 | 434.0683 | 439.0261 | -21.4814 | -48.5265 | 0.2623 | -0.9589 | -8.2791 | -8.5022 | -3.7957 | -4.2891 | 1.5654 | -5.6529 | 0.5797 | 0.6113 | 0.9547 | 0.6865 | -132.4453 | -8.9092 | -1.8799 | -2.8118 | -11.0401 | -9.904 | -1.8452 |  | -5.4525 | -4.7285 | 4.0446 | 3.3742 | 3.358 | 0.9692 | 10.5983 | 13.9559 | 14.5515 | 10.8421 | -0.0002 | -0.003 | 0.0008 | 0.0037 | 0.0006 | -0.0009 | 0.0158 | -0.0066 | 0.0034 | -360.0881 | 17.6718 | -360.6235 | 18.0372 | -360.962 | 18.105 | -361.002 | 17.5465 | -352.8998 | 18.7764 | -352.9583 | 16.7991
11:30 | 626 | 18.3298 | 192.208 | 434.1537 | 439.014 | -21.5429 | -48.5623 | 0.2107 | -0.9056 | -8.2631 | -8.3959 | -3.7745 | -4.2951 | 1.4906 | -5.6422 | 0.5797 | 0.6126 | 0.9578 | 0.6872 | -132.4446 | -8.8698 | -1.846 | -2.8376 | -11.0558 | -9.8733 | -1.9579 |  | -5.4229 | -4.6575 | 4.0456 | 3.3735 | 3.3573 | 0.9694 | 10.603 | 13.972 | 14.5491 | 10.8587 | 0 | -0.003 | 0.001 | 0.0037 | -0.0001 | -0.0007 | 0.0192 | -0.0083 | 0.0183 | -360.1496 | 17.6656 | -360.6266 | 18.0414 | -360.9651 | 18.1214 | -361.0051 | 17.5773 | -352.8906 | 18.7703 | -352.946 | 16.8053
11:30 | 627 | 18.2854 | 192.3256 | 434.0979 | 439.0795 | -21.412 | -48.5477 | 0.187 | -0.9038 | -8.1564 | -8.3517 | -3.7354 | -4.2394 | 1.4597 | -5.6302 | 0.579 | 0.6151 | 0.9619 | 0.6866 | -132.4276 | -8.8492 | -1.8343 | -2.7423 | -11.0403 | -9.8372 | -1.8425 |  | -5.5033 | -4.6586 | 4.0447 | 3.373 | 3.3574 | 0.9674 | 10.5971 | 13.9837 | 14.5212 | 10.8468 | -0.0006 | -0.003 | 0.0006 | 0.0031 | 0.0009 | -0.0011 | 0.0003 | -0.0015 | -0.0166 | -360.0942 | 17.6697 | -360.6666 | 18.0188 | -360.9435 | 18.1112 | -361.0143 | 17.565 | -352.8783 | 18.7641 | -352.9398 | 16.7889
11:30 | 628 | 18.343 | 192.2281 | 434.1412 | 439.0484 | -21.4971 | -48.6504 | 0.1593 | -0.803 | -8.2071 | -8.4099 | -3.7548 | -4.1632 | 1.537 | -5.6674 | 0.5799 | 0.6158 | 0.9572 | 0.6863 | -132.4174 | -8.8586 | -1.8213 | -2.7797 | -11.0778 | -9.8446 | -1.8862 |  | -5.4391 | -4.7112 | 4.0449 | 3.373 | 3.3595 | 0.9688 | 10.6075 | 13.9596 | 14.5277 | 10.8449 | -0.0003 | -0.0025 | 0.001 | 0.0039 | 0.0006 | -0.0003 | 0.0121 | -0.0024 | -0.0075 | -360.1373 | 17.682 | -360.6327 | 18.0229 | -360.9435 | 18.1194 | -361.0143 | 17.5712 | -352.946 | 18.7846 | -352.946 | 16.795
11:30 | 629 | 18.3368 | 192.1826 | 434.0166 | 438.9999 | -21.5258 | -48.534 | 0.1657 | -0.7933 | -8.1836 | -8.3814 | -3.7369 | -4.227 | 1.5524 | -5.6332 | 0.5794 | 0.6174 | 0.9554 | 0.6857 | -132.464 | -8.9111 | -1.8648 | -2.6748 | -11.0042 | -9.7743 | -1.8436 |  | -5.4069 | -4.7376 | 4.0439 | 3.3731 | 3.3582 | 0.9693 | 10.626 | 14.0128 | 14.5522 | 10.8807 | -0.0001 | -0.0029 | 0.0009 | 0.0039 | 0.0006 | -0.0007 | 0.0187 | 0.0043 | -0.0117 | -360.1496 | 17.6738 | -360.6389 | 18.027 | -360.9343 | 18.1091 | -361.0328 | 17.5732 | -352.9121 | 18.7661 | -352.9398 | 16.7971
11:30 | 630 | 18.3276 | 192.1993 | 434.1494 | 438.9905 | -21.4151 | -48.3652 | 0.3673 | -0.8485 | -8.2121 | -8.4401 | -3.8125 | -4.2689 | 1.528 | -5.6115 | 0.5791 | 0.6168 | 0.9539 | 0.6868 | -132.4682 | -8.913 | -1.8293 | -2.7232 | -11.0178 | -9.7849 | -1.8865 |  | -5.4019 | -4.6572 | 4.045 | 3.3756 | 3.3557 | 0.9674 | 10.6132 | 13.9885 | 14.5566 | 10.8796 | 0.0001 | -0.0031 | 0.0006 | 0.0036 | 0.0005 | -0.0005 | 0.0066 | -0.0139 | -0.012 | -360.1527 | 17.6718 | -360.6173 | 18.0147 | -360.9343 | 18.1009 | -360.9958 | 17.5671 | -352.9367 | 18.7641 | -352.9706 | 16.7868
11:30 | 631 | 18.3708 | 192.1787 | 434.0024 | 439.0604 | -21.4154 | -48.2819 | 0.373 | -0.8837 | -8.209 | -8.4411 | -3.8327 | -4.3121 | 1.4598 | -5.7295 | 0.5781 | 0.6147 | 0.9556 | 0.6855 | -132.4308 | -8.7852 | -1.9074 | -2.719 | -10.9929 | -9.7839 | -1.838 |  | -5.357 | -4.7471 | 4.0436 | 3.3756 | 3.3572 | 0.9688 | 10.6272 | 14.0023 | 14.5815 | 10.8879 | 0 | -0.0031 | 0.0007 | 0.0038 | 0.001 | -0.0004 | 0.0023 | 0.0006 | 0.0131 | -360.1742 | 17.68 | -360.6327 | 18.0311 | -360.962 | 18.1132 | -360.9866 | 17.5753 | -352.9429 | 18.7682 | -352.9367 | 16.8053
11:30 | 632 | 18.3894 | 192.2627 | 434.064 | 439.0565 | -21.4707 | -48.3972 | 0.3672 | -1.0266 | -8.2513 | -8.57 | -3.7933 | -4.3497 | 1.4283 | -5.7067 | 0.5794 | 0.6185 | 0.9578 | 0.6864 | -132.3757 | -8.7913 | -1.8509 | -2.7911 | -11.0537 | -9.8603 | -1.8695 |  | -5.4205 | -4.7749 | 4.0452 | 3.3753 | 3.3562 | 0.9683 | 10.611 | 13.963 | 14.5828 | 10.8659 | -0.0006 | -0.0029 | 0.0005 | 0.0037 | 0.0004 | -0.0008 | 0.0257 | -0.0109 | 0.0119 | -360.1065 | 17.6615 | -360.6327 | 18.0249 | -360.9404 | 18.1194 | -361.0297 | 17.5547 | -352.8906 | 18.7703 | -352.9706 | 16.7971
11:30 | 633 | 18.3305 | 192.2514 | 434.0436 | 439.0435 | -21.4372 | -48.3138 | 0.3465 | -0.8722 | -8.2441 | -8.4598 | -3.7095 | -4.2814 | 1.4412 | -5.6315 | 0.5807 | 0.6195 | 0.956 | 0.6868 | -132.3266 | -8.8453 | -1.9044 | -2.7116 | -10.9823 | -9.8443 | -1.8627 |  | -5.408 | -4.6791 | 4.0438 | 3.3712 | 3.359 | 0.9698 | 10.6006 | 13.9871 | 14.559 | 10.8562 | 0 | -0.0027 | 0.0007 | 0.0032 | 0.0006 | -0.0006 | 0.0027 | -0.0095 | -0.0052 | -360.1034 | 17.6615 | -360.6235 | 18.027 | -360.9804 | 18.1358 | -361.0451 | 17.5609 | -352.9244 | 18.7518 | -352.9306 | 16.793
11:30 | 634 | 18.4049 | 192.3246 | 434.0426 | 438.9868 | -21.474 | -48.4008 | 0.3242 | -0.7572 | -8.1613 | -8.3843 | -3.5948 | -4.1763 | 1.5025 | -5.5416 | 0.5805 | 0.6146 | 0.9548 | 0.6853 | -132.3807 | -8.925 | -1.8811 | -2.7491 | -11.0616 | -9.8435 | -1.8933 |  | -5.3536 | -4.7169 | 4.0425 | 3.375 | 3.3579 | 0.9695 | 10.5602 | 13.9407 | 14.5116 | 10.845 | -0.0001 | -0.0033 | 0.0007 | 0.0037 | 0.001 | -0.0007 | 0.0085 | 0.007 | -0.0232 | -360.1096 | 17.6451 | -360.6081 | 18.0167 | -360.9712 | 18.0988 | -360.9958 | 17.5629 | -352.8721 | 18.7333 | -352.8937 | 16.793
11:30 | 635 | 18.4136 | 192.4145 | 434.144 | 439.0174 | -21.4742 | -48.3599 | 0.3322 | -0.859 | -8.2393 | -8.4599 | -3.6745 | -4.1786 | 1.5458 | -5.5614 | 0.58 | 0.6149 | 0.9532 | 0.6864 | -132.403 | -8.9237 | -1.896 | -2.807 | -10.9277 | -9.7796 | -1.8299 |  | -5.3762 | -4.5324 | 4.0435 | 3.3713 | 3.357 | 0.9686 | 10.5844 | 13.9651 | 14.5488 | 10.8515 | 0 | -0.0031 | 0.0014 | 0.0039 | 0.0002 | -0.0005 | 0.0205 | -0.0051 | -0.007 | -360.1958 | 17.6861 | -360.642 | 18.0249 | -360.962 | 18.1214 | -361.0235 | 17.5794 | -352.9337 | 18.7826 | -352.9398 | 16.793
11:30 | 636 | 18.3978 | 192.3169 | 434.1539 | 439.0887 | -21.5269 | -48.39 | 0.3927 | -0.8042 | -8.2598 | -8.4215 | -3.7054 | -4.1803 | 1.4513 | -5.7273 | 0.58 | 0.6154 | 0.9558 | 0.6853 | -132.4898 | -8.9185 | -1.886 | -2.8022 | -10.9352 | -9.7813 | -1.7759 |  | -5.4041 | -4.6486 | 4.0436 | 3.3723 | 3.3593 | 0.9678 | 10.5972 | 13.9777 | 14.5375 | 10.8934 | -0.0003 | -0.0027 | 0.0007 | 0.0038 | 0.0007 | -0.0009 | 0.0008 | -0.0154 | -0.0172 | -360.1835 | 17.6882 | -360.6696 | 18.0167 | -360.9343 | 18.0865 | -360.9435 | 17.5445 | -352.9244 | 18.7764 | -352.9367 | 16.7848
11:30 | 637 | 18.3992 | 192.4059 | 434.1886 | 438.9845 | -21.5212 | -48.4395 | 0.2616 | -0.8074 | -8.1835 | -8.2712 | -3.6724 | -4.2473 | 1.4592 | -5.5971 | 0.5797 | 0.6145 | 0.9547 | 0.6872 | -132.4618 | -8.9925 | -1.841 | -2.7647 | -10.9546 | -9.7511 | -1.8037 |  | -5.4182 | -4.7385 | 4.0437 | 3.376 | 3.3605 | 0.9699 | 10.6156 | 13.985 | 14.5525 | 10.8648 | -0.0003 | -0.0023 | 0.0008 | 0.0043 | 0.0003 | -0.0005 | 0.02 | -0.0086 | 0.0067 | -360.1619 | 17.6779 | -360.6635 | 18.0414 | -360.9589 | 18.0886 | -360.9804 | 17.565 | -352.906 | 18.7723 | -352.946 | 16.8032
11:30 | 638 | 18.492 | 192.3752 | 434.2248 | 439.0677 | -21.448 | -48.437 | 0.3564 | -0.7877 | -8.224 | -8.3608 | -3.6157 | -4.1763 | 1.5226 | -5.6605 | 0.5788 | 0.6136 | 0.9549 | 0.6864 | -132.5382 | -8.9271 | -1.7942 | -2.8306 | -10.9721 | -9.7929 | -1.7986 |  | -5.4155 | -4.6832 | 4.0431 | 3.3752 | 3.3598 | 0.9699 | 10.6202 | 14.007 | 14.5464 | 10.9096 | 0.0002 | -0.0029 | 0.0005 | 0.004 | 0.0005 | -0.0008 | 0.0156 | 0.0061 | -0.0071 | -360.1435 | 17.6677 | -360.6266 | 18.0434 | -360.9835 | 18.1399 | -361.0174 | 17.5609 | -352.9091 | 18.7641 | -352.9552 | 16.8074
11:30 | 639 | 18.4188 | 192.362 | 434.2278 | 439.1495 | -21.4874 | -48.2978 | 0.3373 | -0.7729 | -8.2054 | -8.39 | -3.6133 | -4.206 | 1.4682 | -5.7797 | 0.5796 | 0.6157 | 0.9548 | 0.6853 | -132.4677 | -8.943 | -1.9846 | -2.8185 | -11.0328 | -9.7121 | -1.7983 |  | -5.5023 | -4.8082 | 4.0438 | 3.3744 | 3.359 | 0.97 | 10.6169 | 13.9686 | 14.5576 | 10.884 | 0.0001 | -0.0031 | 0.0002 | 0.0037 | 0.0004 | -0.0006 | 0.0053 | -0.0145 | 0.0046 | -360.1065 | 17.641 | -360.5496 | 17.9982 | -360.9281 | 18.144 | -361.0297 | 17.565 | -352.9121 | 18.7415 | -352.8875 | 16.7642
11:30 | 640 | 18.4803 | 192.2856 | 434.1482 | 439.1074 | -21.4966 | -48.3245 | 0.3774 | -0.8666 | -8.2409 | -8.3861 | -3.62 | -4.1244 | 1.5072 | -5.7546 | 0.5807 | 0.6187 | 0.9598 | 0.6879 | -132.3235 | -8.8442 | -1.8697 | -2.8023 | -10.9913 | -9.834 | -1.7965 |  | -5.452 | -4.7571 | 4.0443 | 3.3737 | 3.3598 | 0.9705 | 10.603 | 13.9777 | 14.5722 | 10.8761 | 0.0003 | -0.0024 | 0.0006 | 0.0037 | 0 | -0.0011 | 0.0066 | -0.0049 | -0.0186 | -360.1373 | 17.6533 | -360.5896 | 18.0126 | -360.9497 | 18.1214 | -361.0235 | 17.5732 | -352.9367 | 18.7497 | -352.8967 | 16.7827
11:30 | 641 | 18.3962 | 192.3651 | 434.2262 | 439.1102 | -21.5105 | -48.3743 | 0.4293 | -0.7699 | -8.2088 | -8.3401 | -3.5903 | -4.1968 | 1.4837 | -5.746 | 0.5798 | 0.6154 | 0.9603 | 0.6871 | -132.3701 | -8.8497 | -1.8738 | -2.8314 | -10.9772 | -9.8622 | -1.8075 |  | -5.4604 | -4.7373 | 4.0432 | 3.3728 | 3.3575 | 0.9703 | 10.6088 | 13.9835 | 14.5607 | 10.8645 | -0.0002 | -0.0028 | 0.0007 | 0.0033 | 0.0007 | -0.0004 | 0.0102 | 0.0098 | -0.0018 | -360.1558 | 17.7005 | -360.6696 | 18.0229 | -360.9497 | 18.1132 | -360.9958 | 17.5794 | -352.9521 | 18.7785 | -352.9614 | 16.7868
11:30 | 642 | 18.5424 | 192.5032 | 434.2049 | 439.2528 | -21.4354 | -48.3289 | 0.3983 | -0.8208 | -8.2956 | -8.4445 | -3.6243 | -4.1669 | 1.5002 | -5.6784 | 0.5789 | 0.6165 | 0.9564 | 0.6852 | -132.3361 | -8.8746 | -1.931 | -2.769 | -10.937 | -9.8619 | -1.8088 |  | -5.433 | -4.6611 | 4.0436 | 3.3752 | 3.3603 | 0.9716 | 10.6007 | 13.9812 | 14.5348 | 10.8797 | -0.0001 | -0.0028 | 0.0005 | 0.0034 | 0 | -0.0009 | -0.0054 | -0.0138 | -0.0242 | -360.1404 | 17.682 | -360.6573 | 18.0229 | -360.9558 | 18.0906 | -360.9589 | 17.5363 | -352.906 | 18.7805 | -352.9367 | 16.7971
11:30 | 643 | 18.4231 | 192.4171 | 434.2557 | 439.1415 | -21.5122 | -48.3753 | 0.3001 | -0.8007 | -8.2847 | -8.3757 | -3.6669 | -4.1287 | 1.4595 | -5.677 | 0.579 | 0.6191 | 0.96 | 0.6871 | -132.4553 | -9.0155 | -1.9709 | -2.7672 | -10.8389 | -9.7834 | -1.764 |  | -5.361 | -4.7102 | 4.0429 | 3.3759 | 3.3584 | 0.9713 | 10.5718 | 13.9696 | 14.5232 | 10.8335 | 0 | -0.0033 | 0.0009 | 0.0037 | 0.0004 | -0.001 | 0.0197 | 0.0022 | -0.0242 | -360.1188 | 17.6697 | -360.6204 | 18.0249 | -360.9558 | 18.0947 | -360.9897 | 17.5609 | -352.9121 | 18.7723 | -352.9429 | 16.8053
11:30 | 644 | 18.3751 | 192.3073 | 434.2612 | 439.2102 | -21.4389 | -48.3026 | 0.4235 | -0.8131 | -8.2818 | -8.443 | -3.714 | -4.1682 | 1.3523 | -5.7187 | 0.5798 | 0.6161 | 0.9551 | 0.6864 | -132.4713 | -8.9775 | -1.9166 | -2.8439 | -10.8631 | -9.7873 | -1.8047 |  | -5.4134 | -4.6857 | 4.0435 | 3.3723 | 3.3587 | 0.9704 | 10.5937 | 14.0092 | 14.5644 | 10.8489 | -0.0003 | -0.0029 | 0.0008 | 0.0039 | 0.0002 | -0.0005 | 0.015 | -0.0038 | 0.0202 | -360.1342 | 17.6615 | -360.6112 | 18.0208 | -360.9558 | 18.1399 | -361.0112 | 17.5794 | -352.8967 | 18.7477 | -352.9183 | 16.7909
11:30 | 645 | 18.3906 | 192.4 | 434.3543 | 439.2564 | -21.4633 | -48.3465 | 0.2793 | -0.8608 | -8.2716 | -8.3892 | -3.7036 | -4.1295 | 1.4312 | -5.6616 | 0.5802 | 0.6196 | 0.9566 | 0.6867 | -132.3911 | -9.0123 | -1.8819 | -2.8239 | -10.9583 | -9.8205 | -1.7665 |  | -5.3838 | -4.7648 | 4.043 | 3.3722 | 3.3574 | 0.9706 | 10.5844 | 13.9767 | 14.5603 | 10.8746 | -0.0004 | -0.0027 | 0.0008 | 0.0038 | 0.0008 | -0.0008 | 0.0004 | -0.0063 | -0.0046 | -360.1404 | 17.643 | -360.5773 | 17.9982 | -360.9558 | 18.1296 | -361.042 | 17.5794 | -352.9183 | 18.7353 | -352.8721 | 16.7683
11:30 | 646 | 18.4129 | 192.3626 | 434.3116 | 439.2237 | -21.5989 | -48.3515 | 0.2347 | -0.9064 | -8.2177 | -8.2057 | -3.6617 | -4.1975 | 1.3953 | -5.6457 | 0.5808 | 0.6175 | 0.9555 | 0.6866 | -132.4524 | -8.9549 | -1.9138 | -2.8009 | -10.9714 | -9.8358 | -1.7871 |  | -5.4008 | -4.8293 | 4.0433 | 3.3717 | 3.3568 | 0.9713 | 10.6029 | 14.0185 | 14.5685 | 10.8984 | -0.0005 | -0.003 | 0.0006 | 0.0038 | 0.001 | 0 | 0.0053 | -0.0057 | -0.0116 | -360.1281 | 17.6677 | -360.6389 | 18.027 | -360.9497 | 18.1214 | -361.0574 | 17.5773 | -352.9183 | 18.7641 | -352.9367 | 16.7909
11:30 | 647 | 18.3244 | 192.3551 | 434.3473 | 439.1866 | -21.6209 | -48.3792 | 0.1329 | -0.8772 | -8.2052 | -8.2497 | -3.6837 | -4.2307 | 1.4535 | -5.6336 | 0.5796 | 0.6134 | 0.9557 | 0.6867 | -132.5045 | -9.0023 | -1.967 | -2.8333 | -10.992 | -9.7955 | -1.834 |  | -5.4755 | -4.8188 | 4.043 | 3.3752 | 3.3584 | 0.9716 | 10.6317 | 13.9956 | 14.6054 | 10.9092 | 0.0002 | -0.0032 | 0.0003 | 0.0039 | 0.0004 | -0.0006 | 0.019 | 0.0012 | -0.0087 | -360.1342 | 17.6677 | -360.642 | 18.0106 | -360.9527 | 18.1071 | -360.9589 | 17.5506 | -352.9244 | 18.7744 | -352.9367 | 16.7827
11:31 | 648 | 18.3346 | 192.3828 | 434.2353 | 439.1489 | -21.6004 | -48.5067 | 0.2609 | -0.824 | -8.1035 | -8.2744 | -3.605 | -4.2564 | 1.4051 | -5.6788 | 0.5812 | 0.6161 | 0.959 | 0.6866 | -132.431 | -8.9711 | -1.9032 | -2.6554 | -10.944 | -9.8692 | -1.7657 |  | -5.3462 | -4.765 | 4.0416 | 3.3754 | 3.3615 | 0.9714 | 10.5753 | 13.9845 | 14.5542 | 10.8721 | -0.0004 | -0.0037 | 0.0004 | 0.0035 | 0.0002 | -0.0007 | 0.0136 | -0.0134 | -0.0195 | -360.1188 | 17.6697 | -360.6604 | 18.0352 | -360.9866 | 18.0886 | -360.9589 | 17.5383 | -352.9275 | 18.7723 | -352.9921 | 16.8032
11:31 | 649 | 18.3412 | 192.464 | 434.2272 | 439.238 | -21.6964 | -48.4247 | 0.1656 | -0.8146 | -8.1064 | -8.2957 | -3.6227 | -4.2616 | 1.3971 | -5.6983 | 0.5806 | 0.6194 | 0.9562 | 0.687 | -132.3981 | -8.96 | -1.9485 | -2.628 | -10.9259 | -9.938 | -1.766 |  | -5.4201 | -4.813 | 4.0419 | 3.377 | 3.359 | 0.9726 | 10.5683 | 13.972 | 14.5375 | 10.8934 | -0.0003 | -0.0027 | 0.0005 | 0.0032 | 0.0006 | -0.0006 | 0.0104 | -0.0068 | -0.0167 | -360.1219 | 17.6594 | -360.6389 | 18.0352 | -360.9466 | 18.1358 | -361.0266 | 17.5753 | -352.906 | 18.76 | -352.9367 | 16.793
11:31 | 650 | 18.3216 | 192.3959 | 434.2338 | 439.2011 | -21.592 | -48.3325 | 0.2799 | -0.8483 | -8.1263 | -8.3421 | -3.63 | -4.2946 | 1.3561 | -5.6885 | 0.5805 | 0.6162 | 0.9551 | 0.6875 | -132.3001 | -8.9697 | -1.9883 | -2.5892 | -10.9455 | -9.8028 | -1.7951 |  | -5.3647 | -4.8048 | 4.0424 | 3.3746 | 3.3582 | 0.9698 | 10.5996 | 13.98 | 14.5797 | 10.8844 | -0.0007 | -0.0029 | 0.0006 | 0.0035 | 0.0005 | -0.0012 | 0.0024 | -0.004 | 0.0094 | -360.1188 | 17.6594 | -360.6204 | 18.0064 | -360.9435 | 18.1112 | -361.0266 | 17.5712 | -352.9275 | 18.7579 | -352.9121 | 16.7683
11:31 | 651 | 18.3804 | 192.4534 | 434.0998 | 439.1469 | -21.5565 | -48.4664 | 0.1925 | -0.826 | -8.2249 | -8.3338 | -3.7654 | -4.2521 | 1.313 | -5.7103 | 0.5799 | 0.6189 | 0.9566 | 0.688 | -132.3871 | -9.0613 | -1.9814 | -2.6175 | -10.879 | -9.7502 | -1.7879 |  | -5.3708 | -4.7607 | 4.0434 | 3.3752 | 3.3576 | 0.9718 | 10.6017 | 13.9595 | 14.5672 | 10.88 | 0.0001 | -0.0029 | 0.0012 | 0.0037 | 0.0004 | -0.0004 | -0.0007 | -0.0175 | -0.0148 | -360.1342 | 17.6759 | -360.6112 | 18.0229 | -360.9466 | 18.1091 | -360.9989 | 17.5753 | -352.9306 | 18.7764 | -352.9244 | 16.7868
11:31 | 652 | 18.4032 | 192.3789 | 434.0433 | 439.1001 | -21.5455 | -48.476 | 0.1273 | -0.876 | -8.2817 | -8.319 | -3.7664 | -4.2223 | 1.3266 | -5.7451 | 0.5806 | 0.6186 | 0.9559 | 0.687 | -132.4238 | -9.0131 | -1.9022 | -2.7004 | -11.0432 | -9.8883 | -1.8598 |  | -5.3525 | -4.7579 | 4.0421 | 3.3761 | 3.3564 | 0.9725 | 10.6085 | 13.9783 | 14.5648 | 10.8745 | 0.0004 | -0.003 | 0.0008 | 0.0037 | 0.0008 | -0.001 | -0.0096 | -0.0168 | -0.0097 | -360.125 | 17.6615 | -360.6512 | 18.0331 | -360.9497 | 18.1153 | -361.0389 | 17.5588 | -352.8691 | 18.7559 | -352.9367 | 16.7868
11:31 | 653 | 18.4045 | 192.4043 | 433.9669 | 439.0682 | -21.6253 | -48.5477 | 0.1737 | -0.9184 | -8.3494 | -8.358 | -3.7463 | -4.2014 | 1.346 | -5.7605 | 0.5808 | 0.6175 | 0.9563 | 0.6852 | -132.479 | -9.1169 | -1.9454 | -2.7427 | -10.9702 | -9.8411 | -1.9385 |  | -5.3967 | -4.8339 | 4.0418 | 3.3759 | 3.3574 | 0.9722 | 10.6087 | 13.9837 | 14.608 | 10.8872 | -0.0003 | -0.0031 | 0.0003 | 0.0035 | 0.0002 | -0.0003 | -0.0056 | -0.0117 | -0.002 | -360.0942 | 17.6533 | -360.6235 | 18.0352 | -360.9527 | 18.1091 | -360.9989 | 17.5506 | -352.9152 | 18.7641 | -352.9214 | 16.7868
11:31 | 654 | 18.4519 | 192.4163 | 433.9643 | 439.0637 | -21.6494 | -48.5643 | 0.0885 | -0.938 | -8.3637 | -8.3396 | -3.7103 | -4.2593 | 1.2254 | -5.8263 | 0.5795 | 0.6206 | 0.9569 | 0.6845 | -132.4738 | -9.0371 | -1.9715 | -2.7453 | -11.0004 | -9.8805 | -1.8451 |  | -5.3425 | -4.7471 | 4.0414 | 3.3749 | 3.3598 | 0.972 | 10.6108 | 14.0328 | 14.6034 | 10.9225 | -0.0001 | -0.0025 | 0.0006 | 0.004 | 0.0009 | -0.0007 | 0.013 | 0.0015 | 0.0024 | -360.1281 | 17.6718 | -360.6481 | 18.0496 | -360.9497 | 18.1276 | -361.0235 | 17.5712 | -352.9121 | 18.7661 | -352.9275 | 16.795
11:31 | 655 | 18.4514 | 192.6058 | 433.9964 | 439.0775 | -21.7011 | -48.6023 | 0.1483 | -0.8927 | -8.3797 | -8.3134 | -3.7342 | -4.1878 | 1.3896 | -5.732 | 0.5794 | 0.6224 | 0.9548 | 0.6863 | -132.4691 | -9.1135 | -1.8318 | -2.8095 | -10.941 | -9.8475 | -1.8345 |  | -5.3787 | -4.8212 | 4.0424 | 3.3758 | 3.3575 | 0.9719 | 10.5879 | 14.0264 | 14.5345 | 10.8898 | 0 | -0.0028 | 0 | 0.0034 | 0.0004 | -0.0006 | 0.006 | 0.0001 | -0.0027 | -360.1188 | 17.6553 | -360.642 | 18.029 | -360.922 | 18.1153 | -360.9958 | 17.5424 | -352.8629 | 18.76 | -352.9183 | 16.7766
11:31 | 656 | 18.4367 | 192.5769 | 434.0566 | 439.1849 | -21.5334 | -48.523 | 0.1787 | -0.9841 | -8.3009 | -8.3769 | -3.7425 | -4.2297 | 1.3855 | -5.6838 | 0.5797 | 0.6214 | 0.9581 | 0.6855 | -132.4108 | -8.97 | -1.8604 | -2.7273 | -10.9636 | -9.8087 | -1.8501 |  | -5.3688 | -4.7393 | 4.0429 | 3.3743 | 3.3565 | 0.9728 | 10.5926 | 13.9788 | 14.5552 | 10.8891 | 0.0002 | -0.0032 | 0.0007 | 0.0039 | 0.0008 | -0.0002 | 0.0047 | 0.005 | -0.0215 | -360.1281 | 17.6574 | -360.6235 | 18.0311 | -360.9527 | 18.1235 | -360.9927 | 17.5712 | -352.9091 | 18.7723 | -352.9244 | 16.795
11:31 | 657 | 18.4287 | 192.5721 | 434.0791 | 439.2172 | -21.4493 | -48.3155 | 0.3201 | -0.9414 | -8.2793 | -8.1844 | -3.7921 | -4.2069 | 1.3196 | -5.678 | 0.579 | 0.6207 | 0.9596 | 0.6866 | -132.3872 | -8.9667 | -1.8422 | -2.74 | -11.039 | -9.808 | -1.9019 |  | -5.3845 | -4.7686 | 4.0415 | 3.3772 | 3.3547 | 0.9712 | 10.5867 | 13.9792 | 14.5352 | 10.8764 | 0.0002 | -0.0027 | 0.0012 | 0.0037 | 0.0006 | -0.0009 | 0.0117 | -0.0086 | -0.0106 | -360.1804 | 17.6718 | -360.642 | 18.0331 | -360.9281 | 18.1153 | -361.0328 | 17.5794 | -352.8998 | 18.7641 | -352.9275 | 16.7909
11:31 | 658 | 18.4335 | 192.5344 | 434.1143 | 439.204 | -21.469 | -48.209 | 0.3355 | -0.976 | -8.2977 | -8.2872 | -3.7813 | -4.1504 | 1.3151 | -5.6546 | 0.579 | 0.623 | 0.9605 | 0.6837 | -132.3621 | -9.044 | -1.8031 | -2.8162 | -10.9828 | -9.8456 | -1.9365 |  | -5.3933 | -4.8048 | 4.0434 | 3.3769 | 3.3575 | 0.9721 | 10.5986 | 13.99 | 14.5521 | 10.9133 | -0.0006 | -0.003 | 0.0008 | 0.0035 | 0 | -0.0008 | 0.0088 | -0.0099 | 0.0058 | -360.1158 | 17.6594 | -360.6173 | 18.0106 | -360.9343 | 18.1194 | -360.9835 | 17.5486 | -352.8814 | 18.7641 | -352.9029 | 16.7704
11:31 | 659 | 18.3962 | 192.5204 | 434.0616 | 439.2116 | -21.4427 | -48.3875 | 0.3774 | -1.0041 | -8.2852 | -8.2803 | -3.7824 | -4.1501 | 1.2715 | -5.6729 | 0.5792 | 0.6208 | 0.9584 | 0.6856 | -132.3506 | -8.9774 | -1.805 | -2.91 | -10.9746 | -9.8919 | -1.8699 |  | -5.4815 | -4.9133 | 4.0421 | 3.3761 | 3.3559 | 0.9719 | 10.5659 | 13.9871 | 14.5532 | 10.8677 | 0.0001 | -0.0024 | 0.001 | 0.0043 | 0.0006 | -0.0009 | 0.0108 | -0.0121 | 0.0039 | -360.1404 | 17.6738 | -360.6512 | 18.0372 | -360.9774 | 18.1235 | -360.9958 | 17.5691 | -352.8967 | 18.7723 | -352.9552 | 16.793
11:31 | 660 | 18.439 | 192.4592 | 434.0065 | 439.1861 | -21.5001 | -48.4097 | 0.3202 | -0.9913 | -8.2957 | -8.4142 | -3.7795 | -4.1646 | 1.2969 | -5.6443 | 0.5797 | 0.624 | 0.9551 | 0.6853 | -132.3842 | -8.9489 | -1.7139 | -3.0022 | -11.0778 | -9.9099 | -1.8922 |  | -5.4301 | -4.884 | 4.0429 | 3.3781 | 3.3554 | 0.9716 | 10.5774 | 14.0162 | 14.5726 | 10.919 | 0.0002 | -0.0029 | 0.0012 | 0.0037 | 0.0003 | -0.0008 | -0.0046 | -0.0091 | -0.0234 | -360.1188 | 17.6574 | -360.6389 | 18.0249 | -360.9527 | 18.1235 | -360.9897 | 17.5486 | -352.8906 | 18.7579 | -352.9214 | 16.7889
11:31 | 661 | 18.3992 | 192.5981 | 433.9549 | 439.1381 | -21.3512 | -48.3723 | 0.4437 | -0.9287 | -8.2984 | -8.3867 | -3.6881 | -4.1901 | 1.3561 | -5.6926 | 0.5789 | 0.6219 | 0.9581 | 0.685 | -132.3764 | -8.9982 | -1.8085 | -2.9564 | -10.9447 | -9.8188 | -1.8973 |  | -5.4386 | -4.7966 | 4.0425 | 3.3747 | 3.3624 | 0.9713 | 10.6296 | 13.9927 | 14.5984 | 10.8912 | 0.0001 | -0.0027 | 0.0004 | 0.0034 | 0.0004 | -0.001 | 0.0055 | -0.0124 | -0.005 | -360.1496 | 17.6677 | -360.6296 | 18.0229 | -360.962 | 18.1296 | -361.0174 | 17.5629 | -352.9029 | 18.7703 | -352.9398 | 16.7848
11:31 | 662 | 18.5094 | 192.5956 | 434.0113 | 439.1876 | -21.4465 | -48.3367 | 0.3317 | -0.9491 | -8.3081 | -8.3219 | -3.6899 | -4.1461 | 1.3249 | -5.6161 | 0.5795 | 0.6235 | 0.9584 | 0.6861 | -132.4497 | -8.9422 | -1.713 | -2.9236 | -10.9521 | -9.8709 | -1.8978 |  | -5.437 | -4.8141 | 4.0407 | 3.3721 | 3.357 | 0.9716 | 10.62 | 14.0306 | 14.6075 | 10.9199 | -0.0001 | -0.0027 | 0.0006 | 0.0039 | 0.0006 | -0.0004 | -0.0039 | -0.007 | -0.0229 | -360.125 | 17.6615 | -360.6389 | 18.0126 | -360.9127 | 18.1194 | -361.0081 | 17.5712 | -352.8998 | 18.7703 | -352.9275 | 16.7848
11:31 | 663 | 18.5165 | 192.547 | 433.9091 | 439.2759 | -21.3799 | -48.3442 | 0.3315 | -0.8815 | -8.2907 | -8.3996 | -3.7048 | -4.1955 | 1.3417 | -5.6758 | 0.5791 | 0.6215 | 0.9553 | 0.6856 | -132.2494 | -8.9204 | -1.7424 | -2.9193 | -11.0061 | -9.9122 | -1.9412 |  | -5.4363 | -4.8027 | 4.042 | 3.3721 | 3.358 | 0.9732 | 10.6238 | 14.0391 | 14.6226 | 10.9428 | -0.0006 | -0.0028 | 0 | 0.0028 | 0.0005 | -0.001 | -0.0076 | -0.0139 | -0.0172 | -360.1496 | 17.6656 | -360.6266 | 17.9818 | -360.9004 | 18.1112 | -361.0051 | 17.5671 | -352.8875 | 18.7764 | -352.906 | 16.7724
11:31 | 664 | 18.5049 | 192.5545 | 433.9602 | 439.2723 | -21.3632 | -48.2943 | 0.3661 | -0.9029 | -8.3925 | -8.3383 | -3.7646 | -4.1611 | 1.3136 | -5.7202 | 0.5793 | 0.62 | 0.9558 | 0.6859 | -132.3266 | -8.9614 | -1.8156 | -3.0623 | -11.0115 | -9.9123 | -1.8983 |  | -5.4188 | -4.8287 | 4.0415 | 3.3767 | 3.3554 | 0.9717 | 10.6145 | 14.0126 | 14.5849 | 10.8872 | 0 | -0.0029 | 0.0006 | 0.0037 | 0.0004 | -0.0007 | 0.0131 | -0.0036 | -0.0102 | -360.1865 | 17.6738 | -360.645 | 18.0208 | -360.9651 | 18.1337 | -361.0389 | 17.5753 | -352.9521 | 18.7826 | -352.9214 | 16.8012
11:31 | 665 | 18.5297 | 192.5476 | 434.0088 | 439.1522 | -21.42 | -48.404 | 0.3155 | -0.9107 | -8.3825 | -8.3941 | -3.7197 | -4.3076 | 1.3698 | -5.6636 | 0.5804 | 0.6197 | 0.9596 | 0.6856 | -132.3724 | -8.9641 | -1.8206 | -2.8999 | -11.0129 | -9.8525 | -1.9326 |  | -5.4213 | -4.833 | 4.0423 | 3.3767 | 3.3572 | 0.9728 | 10.5915 | 14.0007 | 14.5365 | 10.888 | 0 | -0.0032 | 0.0011 | 0.0039 | 0.0004 | -0.0005 | 0.016 | 0.0015 | -0.004 | -360.0973 | 17.6574 | -360.645 | 18.0126 | -360.9343 | 18.1214 | -361.0081 | 17.5547 | -352.8567 | 18.7579 | -352.9306 | 16.7848
11:31 | 666 | 18.3969 | 192.5392 | 433.9548 | 439.1637 | -21.3888 | -48.4068 | 0.3473 | -0.8907 | -8.3231 | -8.4333 | -3.7857 | -4.2642 | 1.3883 | -5.5795 | 0.5796 | 0.6206 | 0.9578 | 0.6851 | -132.2809 | -8.9808 | -1.8253 | -2.8485 | -11.0032 | -9.8529 | -1.8821 |  | -5.3627 | -4.7906 | 4.0415 | 3.3736 | 3.3564 | 0.9736 | 10.573 | 13.9822 | 14.5698 | 10.8754 | 0 | -0.003 | 0.0003 | 0.0035 | 0.0005 | -0.0009 | -0.0016 | 0.002 | -0.0047 | -360.0973 | 17.6492 | -360.5866 | 18.0023 | -360.9497 | 18.1173 | -360.9989 | 17.5506 | -352.8998 | 18.7641 | -352.9091 | 16.7786
11:31 | 667 | 18.5059 | 192.5664 | 434.0337 | 439.2229 | -21.4447 | -48.4173 | 0.3319 | -0.8402 | -8.3545 | -8.3604 | -3.7166 | -4.2864 | 1.3712 | -5.697 | 0.5796 | 0.6202 | 0.9556 | 0.6862 | -132.3433 | -9.0042 | -1.9206 | -2.8343 | -11.0578 | -9.8756 | -1.917 |  | -5.2943 | -4.7772 | 4.0424 | 3.3766 | 3.3593 | 0.9734 | 10.5649 | 13.9683 | 14.5266 | 10.8559 | -0.0005 | -0.0032 | 0.0013 | 0.0039 | 0.0005 | -0.0003 | 0.0111 | -0.004 | -0.0165 | -360.1311 | 17.6656 | -360.6358 | 18.0126 | -360.9743 | 18.105 | -361.0051 | 17.5712 | -352.9306 | 18.7723 | -352.9091 | 16.7868
11:31 | 668 | 18.5256 | 192.5794 | 434.0397 | 439.2197 | -21.471 | -48.3734 | 0.2408 | -0.8009 | -8.3396 | -8.3996 | -3.6929 | -4.2271 | 1.4014 | -5.6208 | 0.5798 | 0.6216 | 0.956 | 0.6879 | -132.3268 | -9.0082 | -1.8618 | -2.9162 | -11.0604 | -9.8431 | -1.879 |  | -5.3848 | -4.8717 | 4.0418 | 3.376 | 3.3586 | 0.9741 | 10.5926 | 13.9789 | 14.5736 | 10.8945 | -0.0002 | -0.0027 | 0.0009 | 0.0036 | 0.0009 | -0.0009 | 0.0184 | -0.0096 | 0.0107 | -360.165 | 17.6697 | -360.6266 | 17.988 | -360.9127 | 18.0804 | -360.9897 | 17.5588 | -352.8906 | 18.7723 | -352.9644 | 16.7704
11:31 | 669 | 18.4111 | 192.4431 | 433.9456 | 439.1095 | -21.4447 | -48.4488 | 0.306 | -0.8582 | -8.303 | -8.4269 | -3.6854 | -4.1644 | 1.4097 | -5.6582 | 0.5806 | 0.624 | 0.9578 | 0.6863 | -132.4176 | -8.9804 | -1.8646 | -3.0329 | -10.9881 | -9.8612 | -1.9636 |  | -5.4014 | -4.8205 | 4.0403 | 3.3752 | 3.359 | 0.9725 | 10.5786 | 13.9942 | 14.5788 | 10.8973 | 0.0004 | -0.0029 | 0.0005 | 0.0034 | 0.0006 | -0.0003 | 0.0187 | 0.0046 | 0.0102 | -360.1435 | 17.6779 | -360.6604 | 18.0126 | -360.962 | 18.1009 | -361.0143 | 17.5732 | -352.9214 | 18.7744 | -352.9367 | 16.7971
11:31 | 670 | 18.4344 | 192.3758 | 433.894 | 439.1606 | -21.5152 | -48.3758 | 0.2661 | -0.9847 | -8.3029 | -8.3256 | -3.7783 | -4.2769 | 1.4108 | -5.6571 | 0.5803 | 0.6251 | 0.9575 | 0.686 | -132.4289 | -8.9642 | -1.7965 | -2.9679 | -11.0266 | -9.9132 | -1.9914 |  | -5.4565 | -4.8109 | 4.0423 | 3.3808 | 3.361 | 0.9736 | 10.634 | 14.0441 | 14.6244 | 10.9522 | 0 | -0.0031 | 0.0006 | 0.0038 | 0.0007 | -0.0006 | 0.0027 | -0.0062 | -0.005 | -360.1619 | 17.6574 | -360.6173 | 18.0023 | -360.9312 | 18.0824 | -361.002 | 17.565 | -352.8906 | 18.7559 | -352.9091 | 16.7848
11:31 | 671 | 18.4452 | 192.5162 | 433.8741 | 439.187 | -21.5731 | -48.4165 | 0.2765 | -0.9083 | -8.312 | -8.3038 | -3.7578 | -4.237 | 1.3639 | -5.6732 | 0.5798 | 0.6252 | 0.9619 | 0.6855 | -132.3589 | -8.9385 | -1.8232 | -3.0258 | -11.1358 | -10.0204 | -1.9666 |  | -5.4227 | -4.7804 | 4.0414 | 3.3771 | 3.3569 | 0.9736 | 10.6305 | 14.058 | 14.6387 | 10.937 | -0.0001 | -0.0026 | 0.0008 | 0.0042 | 0.0005 | -0.0003 | 0.0046 | -0.0053 | -0.002 | -360.1034 | 17.6533 | -360.6389 | 17.9962 | -360.9035 | 18.0927 | -360.9927 | 17.5588 | -352.866 | 18.7682 | -352.9398 | 16.7766
11:31 | 672 | 18.4288 | 192.6068 | 433.9085 | 439.19 | -21.4292 | -48.4205 | 0.241 | -0.8848 | -8.2501 | -8.3106 | -3.7456 | -4.2398 | 1.3551 | -5.68 | 0.5802 | 0.6232 | 0.9579 | 0.686 | -132.4172 | -9.0337 | -1.9605 | -3.0336 | -11.03 | -9.9178 | -1.969 |  | -5.4508 | -4.7684 | 4.0423 | 3.372 | 3.358 | 0.9736 | 10.6237 | 14.0046 | 14.6005 | 10.8847 | -0.0007 | -0.0028 | 0.0007 | 0.0042 | 0.0006 | -0.0006 | 0.0041 | -0.0083 | 0.0054 | -360.1188 | 17.6697 | -360.645 | 18.0064 | -360.9466 | 18.1112 | -361.0266 | 17.5753 | -352.9306 | 18.7744 | -352.9121 | 16.793
11:31 | 673 | 18.4886 | 192.6092 | 433.8589 | 439.2422 | -21.4146 | -48.3199 | 0.3349 | -0.9097 | -8.3309 | -8.3691 | -3.8087 | -4.202 | 1.3072 | -5.7582 | 0.5797 | 0.6231 | 0.9578 | 0.687 | -132.4092 | -8.9357 | -1.8569 | -2.9911 | -11.1274 | -9.9559 | -1.9988 |  | -5.4064 | -4.7419 | 4.0412 | 3.3775 | 3.3584 | 0.974 | 10.5579 | 14.031 | 14.562 | 10.9002 | 0.0001 | -0.0032 | 0.0006 | 0.0042 | 0.0002 | -0.001 | 0.0166 | 0.0008 | -0.0021 | -360.1281 | 17.6533 | -360.6296 | 18.0044 | -360.9374 | 18.0783 | -361.002 | 17.5753 | -352.8814 | 18.7579 | -352.9152 | 16.7848
11:31 | 674 | 18.373 | 192.4911 | 433.8213 | 439.2208 | -21.4565 | -48.3102 | 0.1968 | -0.8371 | -8.3164 | -8.3684 | -3.776 | -4.3019 | 1.288 | -5.7062 | 0.5787 | 0.6184 | 0.9557 | 0.6869 | -132.3698 | -9.0005 | -1.8354 | -2.9806 | -11.1183 | -9.952 | -1.9896 |  | -5.3932 | -4.7501 | 4.0415 | 3.3795 | 3.3602 | 0.9737 | 10.5868 | 14.0194 | 14.5736 | 10.8771 | 0.0002 | -0.0034 | 0.0007 | 0.0037 | 0.0002 | -0.0003 | -0.0041 | -0.0085 | -0.0198 | -360.1496 | 17.6738 | -360.6512 | 17.9921 | -360.9404 | 18.1029 | -361.0081 | 17.5691 | -352.906 | 18.7826 | -352.9521 | 16.795
11:31 | 675 | 18.4714 | 192.5282 | 433.9039 | 439.316 | -21.4373 | -48.485 | 0.2334 | -0.798 | -8.2883 | -8.3565 | -3.7447 | -4.2649 | 1.265 | -5.7571 | 0.5797 | 0.6216 | 0.9545 | 0.6854 | -132.3495 | -9.0671 | -1.8036 | -3.0818 | -11.0655 | -9.8763 | -1.9558 |  | -5.3813 | -4.8336 | 4.0414 | 3.3775 | 3.3595 | 0.9743 | 10.6052 | 13.986 | 14.5471 | 10.8894 | 0 | -0.0028 | 0.0011 | 0.0039 | 0.001 | -0.0008 | 0.0002 | 0.0025 | -0.0169 | -360.1188 | 17.6512 | -360.6358 | 18.0044 | -360.9435 | 18.0906 | -361.0051 | 17.5712 | -352.9091 | 18.7764 | -352.9029 | 16.7889
11:31 | 676 | 18.453 | 192.4899 | 433.8122 | 439.3197 | -21.4783 | -48.4593 | 0.2862 | -0.8277 | -8.3268 | -8.3268 | -3.7123 | -4.2195 | 1.3117 | -5.7365 | 0.5787 | 0.6186 | 0.9546 | 0.6869 | -132.4308 | -9.0123 | -1.7959 | -2.9527 | -11.0945 | -9.8575 | -1.9412 |  | -5.3178 | -4.8076 | 4.0416 | 3.3751 | 3.3576 | 0.9741 | 10.5671 | 14.0113 | 14.5882 | 10.9096 | -0.0001 | -0.0029 | 0.0007 | 0.0035 | 0.0001 | -0.0008 | 0.0046 | -0.009 | 0.0025 | -360.1188 | 17.6512 | -360.6235 | 17.9818 | -360.9312 | 18.0845 | -360.9681 | 17.5958 | -352.8906 | 18.7538 | -352.9029 | 16.7704
11:31 | 677 | 18.5235 | 192.5049 | 433.9506 | 439.3402 | -21.4933 | -48.4427 | 0.2612 | -0.8517 | -8.3227 | -8.4167 | -3.7848 | -4.2762 | 1.3883 | -5.7132 | 0.5806 | 0.6234 | 0.957 | 0.6862 | -132.3861 | -9.0887 | -1.8103 | -2.9698 | -11.0744 | -9.8687 | -1.9607 |  | -5.3621 | -4.8556 | 4.0424 | 3.3784 | 3.357 | 0.9759 | 10.6018 | 14.0287 | 14.6066 | 10.9324 | -0.0002 | -0.0028 | 0.0002 | 0.0032 | 0.0012 | -0.0011 | 0.0096 | -0.0138 | -0.0155 | -360.1588 | 17.6738 | -360.6235 | 17.9777 | -360.962 | 18.1071 | -361.0481 | 17.5978 | -352.946 | 18.7682 | -352.8998 | 16.7766
11:31 | 678 | 18.547 | 192.4669 | 433.8558 | 439.2454 | -21.4136 | -48.3784 | 0.2669 | -0.7611 | -8.3217 | -8.3891 | -3.6889 | -4.2806 | 1.3354 | -5.6674 | 0.5793 | 0.6212 | 0.9549 | 0.6849 | -132.442 | -9.0721 | -1.8458 | -2.9648 | -11.1028 | -9.8245 | -1.9596 |  | -5.3614 | -4.7611 | 4.0404 | 3.3744 | 3.358 | 0.9753 | 10.6445 | 14.0487 | 14.5999 | 10.9395 | 0.0001 | -0.003 | 0.0007 | 0.0035 | 0.0005 | -0.0002 | 0.0101 | -0.0077 | 0.0076 | -360.1588 | 17.6615 | -360.5989 | 17.9798 | -360.9189 | 18.0947 | -361.0143 | 17.5814 | -352.8844 | 18.7703 | -352.9152 | 16.7663
11:31 | 679 | 18.5421 | 192.4829 | 433.8705 | 439.2701 | -21.4445 | -48.3828 | 0.2014 | -0.8179 | -8.3856 | -8.3882 | -3.7726 | -4.2464 | 1.2447 | -5.6077 | 0.5781 | 0.6198 | 0.9513 | 0.6836 | -132.4159 | -8.9675 | -1.857 | -2.8665 | -11.1259 | -9.8063 | -1.9617 |  | -5.383 | -4.7924 | 4.0399 | 3.3746 | 3.3556 | 0.9755 | 10.6284 | 14.0207 | 14.6281 | 10.9009 | 0 | -0.0032 | 0.0009 | 0.004 | 0.0005 | -0.0006 | 0.0137 | -0.0072 | -0.0166 | -360.1496 | 17.6574 | -360.6543 | 18.0167 | -360.9743 | 18.0701 | -360.9681 | 17.5732 | -352.8998 | 18.7641 | -352.9398 | 16.8032
11:31 | 680 | 18.5372 | 192.5421 | 433.8958 | 439.2219 | -21.5308 | -48.4947 | 0.1808 | -0.8625 | -8.3687 | -8.4301 | -3.7528 | -4.1667 | 1.3269 | -5.6395 | 0.5806 | 0.6184 | 0.9564 | 0.6843 | -132.4033 | -8.9873 | -1.7876 | -2.9404 | -11.0358 | -9.9052 | -1.9463 |  | -5.3799 | -4.7268 | 4.0396 | 3.3758 | 3.3585 | 0.9755 | 10.5753 | 13.9846 | 14.5668 | 10.8833 | -0.0002 | -0.0024 | 0.0003 | 0.0037 | 0.0005 | -0.0008 | -0.0002 | -0.0081 | 0.0101 | -360.0911 | 17.6553 | -360.6358 | 18.0208 | -361.0112 | 18.1132 | -360.9804 | 17.565 | -352.8752 | 18.7477 | -352.9367 | 16.8115
11:31 | 681 | 18.4735 | 192.5177 | 433.8209 | 439.1974 | -21.4696 | -48.3922 | 0.3716 | -0.8133 | -8.3117 | -8.3123 | -3.655 | -4.2623 | 1.2476 | -5.7383 | 0.5792 | 0.6214 | 0.9575 | 0.6841 | -132.3734 | -9.02 | -1.8502 | -2.9607 | -11.0984 | -9.9017 | -1.9884 |  | -5.4736 | -4.7405 | 4.039 | 3.3743 | 3.3562 | 0.9748 | 10.6019 | 14.0113 | 14.5824 | 10.8865 | -0.0001 | -0.0027 | 0.0013 | 0.0043 | 0.0001 | -0.0004 | -0.0007 | -0.0101 | -0.0199 | -360.1373 | 17.6369 | -360.5773 | 17.9798 | -360.9527 | 18.0845 | -360.9989 | 17.5732 | -352.8937 | 18.7456 | -352.8875 | 16.7745
11:31 | 682 | 18.4918 | 192.6253 | 433.9454 | 439.283 | -21.4816 | -48.3896 | 0.3356 | -0.7908 | -8.2648 | -8.2846 | -3.648 | -4.2746 | 1.3072 | -5.7589 | 0.5806 | 0.6212 | 0.9559 | 0.6842 | -132.2987 | -8.9625 | -1.8227 | -2.9106 | -11.0929 | -9.8843 | -1.9235 |  | -5.4403 | -4.8048 | 4.0415 | 3.3723 | 3.3587 | 0.974 | 10.6099 | 13.9847 | 14.5562 | 10.8714 | -0.0002 | -0.0033 | 0.0004 | 0.0031 | 0.0008 | -0.0005 | 0.008 | -0.0085 | -0.0089 | -360.1958 | 17.6779 | -360.642 | 17.9818 | -360.8943 | 18.0824 | -361.0297 | 17.5978 | -352.9552 | 18.7703 | -352.9367 | 16.7724
11:31 | 683 | 18.4244 | 192.5585 | 433.9025 | 439.3051 | -21.5124 | -48.4172 | 0.2901 | -0.8062 | -8.3806 | -8.2693 | -3.7332 | -4.2918 | 1.3468 | -5.7657 | 0.58 | 0.6205 | 0.9536 | 0.6839 | -132.4091 | -9.0472 | -1.7538 | -2.9581 | -11.0789 | -9.8933 | -1.9376 |  | -5.4438 | -4.8666 | 4.0394 | 3.3732 | 3.353 | 0.9751 | 10.5914 | 14.0068 | 14.5906 | 10.9161 | 0.0003 | -0.003 | 0.0008 | 0.0037 | 0.0002 | -0.0009 | 0.0074 | -0.0162 | -0.0276 | -360.1742 | 17.6738 | -360.6204 | 17.9736 | -360.9004 | 18.0721 | -360.9774 | 17.5773 | -352.9275 | 18.7826 | -352.9091 | 16.7766
11:31 | 684 | 18.4707 | 192.5689 | 433.8073 | 439.3518 | -21.4715 | -48.2783 | 0.4058 | -0.8069 | -8.337 | -8.2322 | -3.6929 | -4.2995 | 1.3432 | -5.7922 | 0.5806 | 0.6197 | 0.9538 | 0.684 | -132.4181 | -9.0232 | -1.8157 | -2.9379 | -11.0831 | -9.9437 | -1.9117 |  | -5.4177 | -4.8953 | 4.0404 | 3.3745 | 3.3588 | 0.9753 | 10.5995 | 14.0437 | 14.5518 | 10.9013 | -0.0004 | -0.003 | 0.0008 | 0.0037 | 0.0006 | -0.001 | 0.0049 | -0.0128 | -0.0113 | -360.1496 | 17.6553 | -360.6389 | 17.9859 | -360.9497 | 18.0947 | -361.0266 | 17.5712 | -352.9091 | 18.762 | -352.9398 | 16.7991
11:31 | 685 | 18.4662 | 192.5591 | 433.793 | 439.3659 | -21.4903 | -48.3548 | 0.3601 | -0.9087 | -8.3436 | -8.3288 | -3.5974 | -4.2248 | 1.3767 | -5.7373 | 0.5801 | 0.6217 | 0.9577 | 0.6848 | -132.4006 | -9.008 | -1.8196 | -2.9068 | -11.0323 | -9.8845 | -1.8876 |  | -5.4235 | -4.8512 | 4.0397 | 3.3719 | 3.3586 | 0.974 | 10.6225 | 14.0093 | 14.6176 | 10.8948 | -0.0004 | -0.0026 | 0.0003 | 0.0035 | 0 | -0.0006 | 0.0011 | -0.0148 | -0.0287 | -360.1127 | 17.6369 | -360.6204 | 18.0126 | -360.9835 | 18.1173 | -361.0358 | 17.5732 | -352.9091 | 18.7477 | -352.9306 | 16.8012
11:31 | 686 | 18.503 | 192.5956 | 433.9531 | 439.4444 | -21.6094 | -48.4848 | 0.1785 | -0.9559 | -8.3752 | -8.3217 | -3.6949 | -4.2026 | 1.358 | -5.6749 | 0.58 | 0.6214 | 0.9553 | 0.6849 | -132.3467 | -9.0382 | -1.8046 | -2.8496 | -11.1288 | -9.9485 | -1.9858 |  | -5.4531 | -4.8226 | 4.0394 | 3.3739 | 3.3573 | 0.9757 | 10.5959 | 14.0115 | 14.5961 | 10.8915 | -0.0003 | -0.0028 | 0.0008 | 0.0036 | 0.0008 | -0.0009 | 0.0139 | 0.009 | 0.0002 | -360.0881 | 17.6184 | -360.5896 | 17.9859 | -360.9466 | 18.1029 | -361.0051 | 17.565 | -352.866 | 18.721 | -352.8875 | 16.793
11:31 | 687 | 18.5054 | 192.5043 | 433.9386 | 439.4103 | -21.4487 | -48.4245 | 0.2869 | -0.9244 | -8.3843 | -8.3678 | -3.695 | -4.1482 | 1.4036 | -5.6247 | 0.5795 | 0.6233 | 0.9566 | 0.6854 | -132.3856 | -9.0047 | -1.7901 | -2.7483 | -11.0937 | -9.9762 | -1.9425 |  | -5.4872 | -4.8128 | 4.0386 | 3.3762 | 3.3594 | 0.9757 | 10.6478 | 14.0525 | 14.6292 | 10.9189 | 0 | -0.0031 | 0.0006 | 0.0038 | 0.0004 | -0.0001 | 0.0233 | -0.0115 | -0.0316 | -360.1496 | 17.6533 | -360.6235 | 17.9982 | -360.962 | 18.0988 | -361.0574 | 17.5855 | -352.9367 | 18.7641 | -352.9214 | 16.7971
11:31 | 688 | 18.4659 | 192.5604 | 433.9501 | 439.434 | -21.535 | -48.3469 | 0.3777 | -0.8628 | -8.3404 | -8.2634 | -3.6667 | -4.2082 | 1.4147 | -5.6016 | 0.5799 | 0.6225 | 0.956 | 0.6861 | -132.3634 | -9.0701 | -1.7509 | -2.8723 | -11.0868 | -9.8631 | -1.9161 |  | -5.3974 | -4.9178 | 4.0392 | 3.3785 | 3.3587 | 0.9751 | 10.5786 | 14.0056 | 14.5951 | 10.9093 | -0.0003 | -0.0033 | 0.0002 | 0.0031 | 0.0006 | -0.001 | 0.0059 | -0.0021 | -0.0291 | -360.1188 | 17.6861 | -360.645 | 17.9777 | -360.9312 | 18.0763 | -360.9866 | 17.5835 | -352.9275 | 18.7703 | -352.9152 | 16.7704
11:31 | 689 | 18.4587 | 192.4914 | 433.7916 | 439.3891 | -21.4716 | -48.2652 | 0.3689 | -0.8594 | -8.3467 | -8.2704 | -3.6828 | -4.2182 | 1.3231 | -5.6828 | 0.579 | 0.62 | 0.9523 | 0.6855 | -132.3832 | -8.9852 | -1.8395 | -2.8047 | -11.0094 | -9.6775 | -1.921 |  | -5.4126 | -4.837 | 4.0377 | 3.3757 | 3.3609 | 0.9748 | 10.64 | 14.0206 | 14.6155 | 10.8955 | -0.0007 | -0.0028 | 0.0005 | 0.0038 | 0.0005 | -0.0005 | 0.0186 | -0.0027 | 0.0107 | -360.1958 | 17.6615 | -360.6143 | 18.0023 | -360.9435 | 18.0742 | -360.9897 | 17.5835 | -352.9552 | 18.7723 | -352.9275 | 16.795
11:31 | 690 | 18.4476 | 192.5584 | 433.815 | 439.4291 | -21.4931 | -48.3705 | 0.4031 | -0.9055 | -8.3748 | -8.2368 | -3.6372 | -4.1982 | 1.3099 | -5.7427 | 0.58 | 0.6293 | 0.9566 | 0.687 | -132.4651 | -8.9999 | -1.864 | -2.7191 | -11.1041 | -9.7514 | -1.973 |  | -5.3901 | -4.8448 | 4.0392 | 3.3776 | 3.3581 | 0.9754 | 10.6099 | 14.0022 | 14.6094 | 10.8941 | -0.0002 | -0.0026 | 0.0005 | 0.0037 | 0.0006 | -0.0006 | -0.0005 | -0.0051 | -0.0089 | -360.125 | 17.6553 | -360.6358 | 18.0044 | -360.9651 | 18.1009 | -361.0328 | 17.5814 | -352.8721 | 18.7477 | -352.9306 | 16.8012
11:31 | 691 | 18.4381 | 192.644 | 433.8739 | 439.4197 | -21.5503 | -48.5085 | 0.3464 | -0.8683 | -8.3501 | -8.2677 | -3.6183 | -4.3569 | 1.3436 | -5.6635 | 0.5804 | 0.6226 | 0.9568 | 0.684 | -132.4702 | -9.0028 | -1.8428 | -2.7652 | -11.092 | -9.7639 | -1.9002 |  | -5.3316 | -4.7055 | 4.0372 | 3.3743 | 3.3565 | 0.9758 | 10.566 | 14.0043 | 14.5348 | 10.8855 | -0.0001 | -0.0034 | 0.0008 | 0.0036 | 0.0011 | -0.0008 | 0.0085 | -0.012 | -0.0079 | -360.0881 | 17.6307 | -360.5866 | 17.9674 | -360.9435 | 18.1091 | -361.002 | 17.5568 | -352.8906 | 18.7333 | -352.8629 | 16.7766
11:31 | 692 | 18.5387 | 192.5841 | 433.8602 | 439.4333 | -21.5809 | -48.4715 | 0.3685 | -0.7811 | -8.2778 | -8.2601 | -3.6044 | -4.2053 | 1.4184 | -5.5953 | 0.579 | 0.6264 | 0.9556 | 0.6855 | -132.3628 | -8.913 | -1.858 | -2.8473 | -11.1262 | -9.7194 | -1.9371 |  | -5.4148 | -4.7778 | 4.0389 | 3.3815 | 3.3575 | 0.9776 | 10.5799 | 13.9893 | 14.5259 | 10.8992 | 0.0002 | -0.0031 | 0.0009 | 0.004 | 0.0006 | -0.0002 | -0.0001 | -0.0048 | -0.009 | -360.1527 | 17.6471 | -360.6389 | 18.0003 | -360.9435 | 18.0927 | -361.0358 | 17.5917 | -352.946 | 18.7518 | -352.9337 | 16.8115
11:31 | 693 | 18.5625 | 192.6221 | 433.8958 | 439.5183 | -21.5071 | -48.414 | 0.3219 | -0.7866 | -8.3587 | -8.3426 | -3.6443 | -4.2401 | 1.3144 | -5.7497 | 0.5799 | 0.6263 | 0.9544 | 0.6841 | -132.3952 | -9.0391 | -1.8035 | -2.7673 | -11.179 | -9.6905 | -1.9642 |  | -5.4492 | -4.8146 | 4.0387 | 3.3811 | 3.3565 | 0.9758 | 10.6006 | 14.0044 | 14.5763 | 10.9024 | -0.0005 | -0.0031 | 0.0005 | 0.0037 | 0.0007 | -0.001 | -0.0035 | 0.0025 | -0.0118 | -360.1773 | 17.6656 | -360.6573 | 17.988 | -360.9404 | 18.0865 | -361.0051 | 17.5773 | -352.8937 | 18.7579 | -352.9552 | 16.7889
11:31 | 694 | 18.6123 | 192.6836 | 433.9067 | 439.506 | -21.4352 | -48.3514 | 0.2994 | -0.8179 | -8.3313 | -8.3038 | -3.6817 | -4.3083 | 1.3433 | -5.7452 | 0.5793 | 0.6247 | 0.9556 | 0.6853 | -132.2946 | -8.9482 | -1.6885 | -2.7068 | -11.1686 | -9.7536 | -1.9242 |  | -5.43 | -4.8149 | 4.0383 | 3.3785 | 3.3578 | 0.9765 | 10.6075 | 14 | 14.6251 | 10.9089 | -0.0003 | -0.0026 | 0.0008 | 0.0039 | 0.0004 | -0.0002 | 0.0105 | 0.0025 | -0.0195 | -360.1281 | 17.6533 | -360.6235 | 17.9859 | -360.9312 | 18.0906 | -360.9897 | 17.5588 | -352.8814 | 18.7641 | -352.9244 | 16.7909
11:31 | 695 | 18.5168 | 192.6513 | 433.8945 | 439.484 | -21.5229 | -48.419 | 0.3591 | -0.9077 | -8.3132 | -8.2074 | -3.7171 | -4.2146 | 1.3551 | -5.6757 | 0.579 | 0.6195 | 0.9541 | 0.6835 | -132.3079 | -8.7967 | -1.7006 | -2.7223 | -11.0925 | -9.7085 | -1.8702 |  | -5.4706 | -4.8427 | 4.0378 | 3.374 | 3.3559 | 0.9751 | 10.6131 | 14.0352 | 14.5945 | 10.942 | 0.001 | -0.0028 | 0.0008 | 0.0039 | 0.0008 | -0.0008 | -0.0041 | -0.0162 | -0.0185 | -360.1558 | 17.6574 | -360.6389 | 18.0106 | -360.9743 | 18.0947 | -360.9989 | 17.5835 | -352.9091 | 18.7497 | -352.9306 | 16.8135
11:31 | 696 | 18.497 | 192.6639 | 433.9294 | 439.5431 | -21.4873 | -48.3555 | 0.3351 | -0.8733 | -8.404 | -8.181 | -3.6798 | -4.1911 | 1.4141 | -5.6864 | 0.5777 | 0.6196 | 0.9563 | 0.6828 | -132.1992 | -8.8963 | -1.7312 | -2.687 | -11.0299 | -9.7034 | -1.8397 |  | -5.3828 | -4.7256 | 4.0378 | 3.3767 | 3.3567 | 0.976 | 10.6215 | 14.0136 | 14.562 | 10.9176 | 0.0001 | -0.0032 | 0.0006 | 0.0036 | 0.0003 | -0.0008 | -0.0018 | 0.0039 | -0.0179 | -360.1158 | 17.6512 | -360.6327 | 17.9798 | -360.9497 | 18.0886 | -361.002 | 17.5958 | -352.8752 | 18.7497 | -352.8967 | 16.7807
11:31 | 697 | 18.5338 | 192.6507 | 433.8843 | 439.64 | -21.4707 | -48.3324 | 0.3498 | -0.877 | -8.3605 | -8.2081 | -3.7076 | -4.2061 | 1.38 | -5.5831 | 0.5789 | 0.6237 | 0.9585 | 0.685 | -132.1406 | -8.8242 | -1.7442 | -2.7037 | -11.0004 | -9.7645 | -1.8969 |  | -5.4129 | -4.5992 | 4.0388 | 3.3742 | 3.3569 | 0.9761 | 10.6155 | 14.0084 | 14.6299 | 10.8987 | 0 | -0.0028 | 0.0009 | 0.0041 | 0.0009 | -0.0004 | 0.0072 | -0.0136 | 0.0015 | -360.1342 | 17.6348 | -360.6081 | 17.9674 | -360.9251 | 18.1029 | -361.0358 | 17.5876 | -352.9152 | 18.7538 | -352.8844 | 16.7786
11:31 | 698 | 18.5856 | 192.7041 | 433.8234 | 439.4402 | -21.5459 | -48.5378 | 0.2175 | -0.8721 | -8.4678 | -8.196 | -3.8006 | -4.2857 | 1.359 | -5.6756 | 0.5796 | 0.6219 | 0.9586 | 0.6847 | -132.2354 | -8.9394 | -1.7012 | -2.6877 | -10.9553 | -9.7357 | -1.8515 |  | -5.4468 | -4.6893 | 4.0373 | 3.3767 | 3.357 | 0.9773 | 10.6006 | 14.0161 | 14.5947 | 10.8905 | -0.0002 | -0.0026 | 0.0006 | 0.0035 | 0.0006 | -0.0009 | -0.0028 | -0.0145 | -0.025 | -360.1373 | 17.6594 | -360.6481 | 17.9777 | -360.9497 | 18.1112 | -361.0235 | 17.5917 | -352.8967 | 18.7579 | -352.9306 | 16.795
11:31 | 699 | 18.5602 | 192.7995 | 433.7614 | 439.4017 | -21.5649 | -48.5152 | 0.145 | -0.9146 | -8.3636 | -8.2658 | -3.7595 | -4.3097 | 1.3354 | -5.7682 | 0.5784 | 0.619 | 0.958 | 0.6869 | -132.2607 | -9.0176 | -1.7546 | -2.7536 | -11.0671 | -9.7329 | -1.9216 |  | -5.4729 | -4.6797 | 4.037 | 3.3717 | 3.3557 | 0.9763 | 10.5995 | 14.0148 | 14.6039 | 10.9071 | -0.0002 | -0.0028 | 0.0007 | 0.0035 | 0.0003 | -0.0007 | 0.0046 | -0.0167 | -0.016 | -360.1681 | 17.6677 | -360.6327 | 17.988 | -360.9681 | 18.0783 | -360.9743 | 17.5691 | -352.9429 | 18.7641 | -352.9398 | 16.7971
11:31 | 700 | 18.4903 | 192.7691 | 433.7638 | 439.3039 | -21.5581 | -48.4581 | 0.2397 | -0.8865 | -8.3888 | -8.4103 | -3.7628 | -4.273 | 1.2687 | -5.6209 | 0.5794 | 0.6249 | 0.9561 | 0.6869 | -132.2396 | -8.8964 | -1.681 | -2.705 | -11.0204 | -9.6905 | -1.8885 |  | -5.4766 | -4.6587 | 4.0371 | 3.378 | 3.3557 | 0.9772 | 10.6031 | 13.9603 | 14.577 | 10.8938 | 0.0003 | -0.0031 | 0.0006 | 0.0034 | 0.0007 | -0.0011 | 0.0341 | 0.0003 | 0.0077 | -360.1127 | 17.6533 | -360.6573 | 17.9941 | -360.9466 | 18.0824 | -360.9497 | 17.5424 | -352.8691 | 18.7559 | -352.946 | 16.8094
11:31 | 701 | 18.5429 | 192.8287 | 433.701 | 439.3487 | -21.5997 | -48.5713 | 0.2017 | -0.8758 | -8.3538 | -8.3733 | -3.6499 | -4.2685 | 1.3616 | -5.6216 | 0.5778 | 0.6216 | 0.958 | 0.6859 | -132.3002 | -9.0057 | -1.7436 | -2.7724 | -11.0587 | -9.743 | -1.8884 |  | -5.3534 | -4.6987 | 4.038 | 3.3732 | 3.358 | 0.977 | 10.5697 | 13.99 | 14.5636 | 10.896 | -0.0004 | -0.0035 | 0.0008 | 0.0033 | 0.0003 | -0.0009 | 0.011 | 0.0018 | -0.0116 | -360.1065 | 17.641 | -360.6143 | 17.9859 | -360.9681 | 18.1112 | -361.0112 | 17.5814 | -352.9214 | 18.7538 | -352.9244 | 16.7909
11:31 | 702 | 18.4982 | 192.714 | 433.6984 | 439.309 | -21.644 | -48.5759 | 0.0754 | -0.9036 | -8.3845 | -8.3277 | -3.5688 | -4.3025 | 1.316 | -5.6777 | 0.5783 | 0.6212 | 0.9586 | 0.6846 | -132.2916 | -8.996 | -1.7916 | -2.7562 | -11.004 | -9.7209 | -1.8936 |  | -5.4189 | -4.6934 | 4.0366 | 3.3726 | 3.3581 | 0.9778 | 10.5568 | 13.9602 | 14.5239 | 10.8884 | -0.0002 | -0.0029 | 0.0008 | 0.0035 | 0.001 | -0.0006 | 0.0003 | -0.0127 | -0.0073 | -360.1711 | 17.6451 | -360.5773 | 17.9613 | -360.922 | 18.0886 | -361.0235 | 17.6102 | -352.9675 | 18.7538 | -352.9091 | 16.7622
11:31 | 703 | 18.5685 | 192.7327 | 433.7792 | 439.3129 | -21.5252 | -48.5396 | 0.1502 | -0.8254 | -8.3713 | -8.1781 | -3.5322 | -4.2568 | 1.4079 | -5.6077 | 0.5788 | 0.6193 | 0.9588 | 0.6854 | -132.2918 | -8.994 | -1.7279 | -2.7997 | -11.0245 | -9.7557 | -1.9027 |  | -5.4536 | -4.6486 | 4.0396 | 3.3767 | 3.358 | 0.977 | 10.6065 | 14.0101 | 14.61 | 10.897 | -0.0005 | -0.0028 | 0.0005 | 0.0033 | 0.0002 | -0.0008 | 0.001 | -0.0028 | -0.0221 | -360.165 | 17.6533 | -360.605 | 17.9551 | -360.8974 | 18.0906 | -360.9835 | 17.5937 | -352.9306 | 18.76 | -352.8998 | 16.7622
11:31 | 704 | 18.579 | 192.8509 | 433.6839 | 439.3805 | -21.5856 | -48.6092 | 0.1611 | -0.8609 | -8.3847 | -8.336 | -3.5783 | -4.2301 | 1.3047 | -5.6514 | 0.5794 | 0.6227 | 0.9577 | 0.6859 | -132.362 | -9.0118 | -1.7627 | -2.9171 | -11.027 | -9.7771 | -1.8756 |  | -5.5018 | -4.6806 | 4.0374 | 3.3752 | 3.3562 | 0.9775 | 10.6191 | 14.0172 | 14.5835 | 10.8804 | 0.0002 | -0.0026 | 0.0003 | 0.0033 | 0.0007 | -0.0004 | 0.0024 | -0.0024 | -0.0012 | -360.165 | 17.6574 | -360.6696 | 18.0167 | -361.0081 | 18.0968 | -361.0112 | 17.5794 | -352.9183 | 18.7785 | -352.9521 | 16.7991
11:31 | 705 | 18.6115 | 192.8589 | 433.6667 | 439.3553 | -21.4988 | -48.5747 | 0.2032 | -0.9134 | -8.4038 | -8.3241 | -3.528 | -4.2337 | 1.3228 | -5.6847 | 0.5791 | 0.6205 | 0.9532 | 0.6868 | -132.3378 | -9.0397 | -1.8127 | -2.9197 | -11.003 | -9.7408 | -1.8789 |  | -5.4857 | -4.7728 | 4.0389 | 3.3754 | 3.3564 | 0.9767 | 10.6168 | 13.986 | 14.5876 | 10.9067 | 0.0002 | -0.0031 | 0.0006 | 0.0036 | 0.0008 | -0.0003 | 0.0064 | -0.0117 | -0.0284 | -360.0758 | 17.6307 | -360.6173 | 18.0064 | -361.0112 | 18.0988 | -360.9866 | 17.5629 | -352.8537 | 18.7374 | -352.9152 | 16.8074
11:31 | 706 | 18.5659 | 192.7937 | 433.6977 | 439.284 | -21.4207 | -48.4996 | 0.3619 | -0.8884 | -8.338 | -8.2933 | -3.5406 | -4.3196 | 1.328 | -5.6647 | 0.5782 | 0.6247 | 0.9526 | 0.6862 | -132.1775 | -8.8822 | -1.7206 | -2.883 | -10.9446 | -9.6683 | -1.8679 |  | -5.5259 | -4.8143 | 4.0378 | 3.3743 | 3.3553 | 0.9775 | 10.6296 | 14.016 | 14.5995 | 10.9313 | -0.0006 | -0.003 | 0.0001 | 0.0031 | 0.0003 | -0.0006 | 0.0001 | -0.0171 | -0.015 | -360.0911 | 17.6286 | -360.6081 | 17.9777 | -360.9589 | 18.105 | -361.0204 | 17.5671 | -352.8752 | 18.7456 | -352.8937 | 16.7991
11:31 | 707 | 18.5509 | 192.8192 | 433.663 | 439.2728 | -21.4884 | -48.4911 | 0.3051 | -0.8799 | -8.3337 | -8.1692 | -3.5645 | -4.2652 | 1.365 | -5.6819 | 0.5799 | 0.624 | 0.9578 | 0.6874 | -132.2353 | -8.9259 | -1.7203 | -2.9044 | -10.9002 | -9.7144 | -1.9154 |  | -5.4263 | -4.8091 | 4.0377 | 3.3758 | 3.3554 | 0.977 | 10.6249 | 14.0231 | 14.6482 | 10.9146 | -0.0002 | -0.0025 | 0.0007 | 0.0037 | 0.0006 | -0.0007 | 0.0228 | -0.0177 | -0.0193 | -360.1619 | 17.6471 | -360.6266 | 17.9839 | -360.9281 | 18.0988 | -361.0481 | 17.5958 | -352.9275 | 18.7661 | -352.9244 | 16.7766
11:32 | 708 | 18.5192 | 192.7119 | 433.6187 | 439.2726 | -21.4887 | -48.4707 | 0.3132 | -0.8325 | -8.3667 | -8.176 | -3.6121 | -4.2201 | 1.3771 | -5.6041 | 0.5794 | 0.6207 | 0.9561 | 0.6847 | -132.1963 | -9.0056 | -1.7836 | -2.91 | -10.9131 | -9.7301 | -1.9073 |  | -5.4775 | -4.8199 | 4.0379 | 3.3752 | 3.3573 | 0.9768 | 10.5788 | 14.0111 | 14.5988 | 10.91 | -0.0003 | -0.0031 | 0.0005 | 0.0037 | -0.0002 | -0.0011 | 0.0157 | -0.0076 | -0.0042 | -360.1773 | 17.6533 | -360.6112 | 17.9654 | -360.9189 | 18.0639 | -360.9835 | 17.5814 | -352.9214 | 18.7744 | -352.8906 | 16.7683
11:32 | 709 | 18.5318 | 192.6854 | 433.5295 | 439.3194 | -21.4581 | -48.5508 | 0.2494 | -0.8348 | -8.4232 | -8.2784 | -3.545 | -4.1663 | 1.4013 | -5.5949 | 0.5788 | 0.6204 | 0.9553 | 0.686 | -132.2132 | -8.9545 | -1.7582 | -2.8598 | -10.9036 | -9.796 | -1.9107 |  | -5.5146 | -4.7872 | 4.0383 | 3.3793 | 3.3595 | 0.9779 | 10.6386 | 14.0548 | 14.6367 | 10.9387 | 0.0003 | -0.0029 | 0.0011 | 0.004 | 0.0009 | -0.0006 | -0.0051 | -0.0069 | -0.0137 | -360.1896 | 17.6553 | -360.6358 | 17.9941 | -360.9589 | 18.0927 | -361.0143 | 17.5794 | -352.946 | 18.7764 | -352.9214 | 16.8012
11:32 | 710 | 18.5123 | 192.7538 | 433.5776 | 439.2458 | -21.4167 | -48.4824 | 0.3138 | -0.7968 | -8.3644 | -8.3005 | -3.5646 | -4.1997 | 1.4312 | -5.6486 | 0.5777 | 0.6194 | 0.9554 | 0.6881 | -132.2878 | -8.8873 | -1.7749 | -2.9084 | -10.9395 | -9.8107 | -1.9119 |  | -5.4433 | -4.8315 | 4.0363 | 3.3766 | 3.3572 | 0.9775 | 10.6065 | 14.0101 | 14.5869 | 10.9086 | -0.0004 | -0.0033 | 0.0003 | 0.0036 | 0.0007 | -0.0004 | 0.0106 | -0.0167 | -0.0226 | -360.0911 | 17.6266 | -360.6358 | 17.988 | -360.9404 | 18.0988 | -361.0143 | 17.565 | -352.8629 | 18.7477 | -352.9275 | 16.7909
11:32 | 711 | 18.5485 | 192.8494 | 433.5216 | 439.2895 | -21.5083 | -48.4592 | 0.2755 | -0.8247 | -8.2852 | -8.2909 | -3.4618 | -4.1607 | 1.4005 | -5.6942 | 0.5803 | 0.6206 | 0.9546 | 0.6878 | -132.2434 | -8.8642 | -1.7225 | -2.8634 | -10.9841 | -9.7947 | -1.8853 |  | -5.4911 | -4.761 | 4.0367 | 3.3783 | 3.3587 | 0.9781 | 10.6075 | 14.0057 | 14.5903 | 10.9146 | -0.0003 | -0.0026 | 0.0008 | 0.0035 | 0.0013 | -0.0007 | 0.0009 | 0.0008 | -0.0297 | -360.085 | 17.6204 | -360.5896 | 17.9839 | -360.9681 | 18.1112 | -361.042 | 17.5671 | -352.8967 | 18.7374 | -352.8937 | 16.8053
11:32 | 712 | 18.528 | 192.9125 | 433.6094 | 439.3008 | -21.4783 | -48.5194 | 0.2924 | -0.904 | -8.3448 | -8.3203 | -3.5967 | -4.1237 | 1.4479 | -5.6244 | 0.5785 | 0.6215 | 0.9536 | 0.6857 | -132.2317 | -8.8094 | -1.742 | -2.8338 | -11.0112 | -9.768 | -1.8676 |  | -5.4297 | -4.7466 | 4.0372 | 3.3762 | 3.3625 | 0.9775 | 10.6017 | 14.0289 | 14.5961 | 10.932 | -0.0001 | -0.0029 | 0.0006 | 0.0036 | 0.0004 | -0.0002 | 0.0075 | -0.0029 | 0.0105 | -360.1527 | 17.6348 | -360.6143 | 17.9777 | -360.9435 | 18.0865 | -360.9866 | 17.5835 | -352.9091 | 18.7477 | -352.9275 | 16.7909
11:32 | 713 | 18.5296 | 192.8261 | 433.5802 | 439.1569 | -21.5348 | -48.5248 | 0.2207 | -0.8833 | -8.3039 | -8.3342 | -3.5907 | -4.1036 | 1.3341 | -5.5648 | 0.5792 | 0.6217 | 0.9557 | 0.6863 | -132.1703 | -8.8577 | -1.7336 | -2.7111 | -11.0755 | -9.7976 | -1.9177 |  | -5.4053 | -4.7582 | 4.0382 | 3.3776 | 3.357 | 0.9792 | 10.6088 | 14.0356 | 14.5954 | 10.8992 | -0.0003 | -0.0031 | 0.0003 | 0.0035 | 0.0004 | -0.0007 | 0.0251 | -0.0212 | -0.0224 | -360.1588 | 17.6553 | -360.6266 | 17.9407 | -360.9004 | 18.0947 | -360.9927 | 17.5629 | -352.8998 | 18.7764 | -352.9152 | 16.7766
11:32 | 714 | 18.5101 | 192.9305 | 433.5964 | 439.2694 | -21.5184 | -48.5099 | 0.1653 | -0.8843 | -8.2773 | -8.2541 | -3.5915 | -4.1207 | 1.377 | -5.7246 | 0.5796 | 0.6225 | 0.9528 | 0.6845 | -132.1547 | -8.8793 | -1.7045 | -2.765 | -11.0576 | -9.9475 | -1.9395 |  | -5.4869 | -4.8027 | 4.0382 | 3.3766 | 3.3576 | 0.9781 | 10.6063 | 14.0105 | 14.6074 | 10.867 | 0.0001 | -0.0031 | 0.001 | 0.004 | 0.0005 | -0.0003 | -0.0019 | -0.0142 | -0.0126 | -360.1835 | 17.6451 | -360.6512 | 17.9818 | -360.9497 | 18.0845 | -360.9958 | 17.5814 | -352.9183 | 18.7764 | -352.9644 | 16.8053
11:32 | 715 | 18.5685 | 192.9836 | 433.7308 | 439.1981 | -21.475 | -48.555 | 0.2054 | -0.8827 | -8.3524 | -8.2643 | -3.5459 | -4.1324 | 1.3483 | -5.6642 | 0.5801 | 0.6237 | 0.9589 | 0.6861 | -132.1532 | -8.9063 | -1.6396 | -2.7462 | -10.9871 | -9.912 | -1.928 |  | -5.4699 | -4.7818 | 4.0356 | 3.3725 | 3.3555 | 0.9781 | 10.6031 | 14.0239 | 14.5886 | 10.9169 | -0.0006 | -0.003 | 0.0003 | 0.0034 | 0.0003 | -0.0008 | 0.02 | -0.0236 | 0.0102 | -360.0911 | 17.6163 | -360.6143 | 17.9572 | -360.9343 | 18.0947 | -360.9927 | 17.565 | -352.8475 | 18.7374 | -352.9029 | 16.7909
11:32 | 716 | 18.521 | 192.9406 | 433.6392 | 439.2124 | -21.5053 | -48.476 | 0.2504 | -0.9421 | -8.2933 | -8.2558 | -3.539 | -4.1234 | 1.3746 | -5.6552 | 0.5776 | 0.6207 | 0.9571 | 0.6862 | -132.132 | -8.9683 | -1.7243 | -2.7821 | -11.0382 | -9.8212 | -2.0001 |  | -5.4622 | -4.7692 | 4.0366 | 3.3779 | 3.3629 | 0.9796 | 10.6041 | 14.0253 | 14.592 | 10.9403 | -0.0003 | -0.0026 | 0.0008 | 0.0044 | 0.0008 | -0.0006 | 0.0074 | -0.0061 | -0.0049 | -360.1496 | 17.6389 | -360.6235 | 17.9695 | -360.9558 | 18.1071 | -361.0266 | 17.5753 | -352.9214 | 18.7744 | -352.9275 | 16.7889
11:32 | 717 | 18.5312 | 192.9404 | 433.6725 | 439.2037 | -21.5487 | -48.4494 | 0.202 | -0.8562 | -8.223 | -8.2368 | -3.4272 | -4.1751 | 1.2726 | -5.646 | 0.5797 | 0.6204 | 0.956 | 0.6859 | -132.1787 | -9.0158 | -1.7007 | -2.8143 | -11.0427 | -9.7831 | -1.8865 |  | -5.5221 | -4.7918 | 4.038 | 3.3758 | 3.3585 | 0.9781 | 10.6087 | 14.0069 | 14.5859 | 10.8811 | 0.0003 | -0.0028 | 0.0009 | 0.0041 | 0.0003 | -0.0003 | 0.0038 | -0.0198 | 0.0094 | -360.1311 | 17.6266 | -360.605 | 17.9592 | -360.9127 | 18.0824 | -360.9866 | 17.565 | -352.8721 | 18.7436 | -352.8783 | 16.7848
11:32 | 718 | 18.5494 | 192.9591 | 433.6079 | 439.3006 | -21.5015 | -48.4647 | 0.2322 | -0.7817 | -8.3171 | -8.214 | -3.4314 | -4.1295 | 1.3492 | -5.6523 | 0.5804 | 0.6247 | 0.9563 | 0.6878 | -132.1733 | -8.93 | -1.7325 | -2.8535 | -11.064 | -9.646 | -1.8918 |  | -5.5386 | -4.7025 | 4.036 | 3.377 | 3.3573 | 0.9786 | 10.6018 | 14.0403 | 14.6009 | 10.9093 | 0.0001 | -0.003 | 0.0006 | 0.0036 | 0.0008 | -0.0012 | 0.0028 | -0.0132 | -0.0281 | -360.1588 | 17.6492 | -360.6296 | 17.9674 | -360.9527 | 18.0927 | -361.042 | 17.5917 | -352.9183 | 18.7682 | -352.9398 | 16.7971
11:32 | 719 | 18.5867 | 192.8422 | 433.6099 | 439.2302 | -21.5698 | -48.5932 | 0.2402 | -0.8458 | -8.3211 | -8.265 | -3.5761 | -4.2017 | 1.3334 | -5.5461 | 0.5799 | 0.6192 | 0.9535 | 0.6861 | -132.188 | -8.8975 | -1.7674 | -2.8345 | -11.0474 | -9.8775 | -1.8281 |  | -5.424 | -4.6646 | 4.0366 | 3.377 | 3.3604 | 0.978 | 10.5855 | 13.9896 | 14.6322 | 10.9157 | 0 | -0.0032 | 0.0009 | 0.0037 | 0.0007 | -0.0002 | 0.0177 | -0.0094 | 0.0147 | -360.1588 | 17.6389 | -360.6081 | 17.9818 | -360.9651 | 18.0947 | -360.9897 | 17.5629 | -352.8752 | 18.7641 | -352.8844 | 16.793
11:32 | 720 | 18.5846 | 192.9362 | 433.6382 | 439.2981 | -21.53 | -48.4999 | 0.2021 | -0.8701 | -8.3597 | -8.344 | -3.6616 | -4.162 | 1.3267 | -5.5526 | 0.5791 | 0.6243 | 0.9528 | 0.6874 | -132.254 | -9.017 | -1.7436 | -2.8639 | -10.987 | -9.7479 | -1.9209 |  | -5.4783 | -4.8436 | 4.0364 | 3.3759 | 3.3618 | 0.9789 | 10.6213 | 14.0082 | 14.6288 | 10.9164 | -0.0003 | -0.0027 | 0.0006 | 0.0033 | 0.0006 | -0.0006 | 0.009 | -0.0051 | -0.0243 | -360.1527 | 17.6348 | -360.6173 | 17.9756 | -360.9743 | 18.0865 | -360.9835 | 17.5855 | -352.906 | 18.7641 | -352.9214 | 16.793
11:32 | 721 | 18.553 | 192.944 | 433.7034 | 439.2934 | -21.5959 | -48.6707 | 0.0654 | -0.8252 | -8.3149 | -8.1763 | -3.6889 | -4.1738 | 1.3766 | -5.674 | 0.5801 | 0.6218 | 0.9541 | 0.6858 | -132.2555 | -8.9872 | -1.8075 | -2.8273 | -10.9211 | -9.7239 | -1.9075 |  | -5.4388 | -4.7614 | 4.0364 | 3.3759 | 3.3577 | 0.9788 | 10.5764 | 14.0032 | 14.5692 | 10.9129 | -0.0001 | -0.0026 | 0.0007 | 0.0039 | 0.0004 | -0.0005 | 0.0013 | -0.0081 | -0.0286 | -360.1681 | 17.6553 | -360.6604 | 17.9654 | -360.9066 | 18.0968 | -361.042 | 17.5855 | -352.8875 | 18.762 | -352.9337 | 16.7889
11:32 | 722 | 18.5204 | 192.9323 | 433.6487 | 439.3014 | -21.6423 | -48.609 | 0.0668 | -0.8853 | -8.4172 | -8.2484 | -3.7429 | -4.2858 | 1.359 | -5.6361 | 0.5792 | 0.6235 | 0.9557 | 0.6853 | -132.2389 | -9.0089 | -1.7481 | -2.9405 | -10.8976 | -9.7433 | -1.9066 |  | -5.4035 | -4.822 | 4.0372 | 3.3732 | 3.3577 | 0.9788 | 10.5717 | 14.0218 | 14.5763 | 10.914 | 0 | -0.0033 | 0.0005 | 0.0041 | 0.0004 | -0.0004 | 0.005 | 0.0003 | 0.0021 | -360.1373 | 17.6389 | -360.5804 | 17.9407 | -360.9189 | 18.0701 | -360.9712 | 17.5855 | -352.9121 | 18.762 | -352.9121 | 16.7745
11:32 | 723 | 18.5435 | 192.8818 | 433.6038 | 439.2725 | -21.5878 | -48.5909 | 0.1076 | -0.8053 | -8.3035 | -8.3378 | -3.6962 | -4.2438 | 1.412 | -5.6719 | 0.5815 | 0.6247 | 0.9548 | 0.6861 | -132.2364 | -8.9679 | -1.7182 | -3.0565 | -10.9366 | -9.8186 | -1.9519 |  | -5.4012 | -4.7842 | 4.0357 | 3.3772 | 3.3563 | 0.9788 | 10.6155 | 14.0371 | 14.5999 | 10.8933 | 0.0003 | -0.0026 | 0.0008 | 0.0042 | 0.0007 | -0.0008 | 0.0091 | -0.0146 | -0.0014 | -360.2142 | 17.643 | -360.6266 | 17.9756 | -360.9497 | 18.0906 | -360.9989 | 17.5876 | -352.9337 | 18.7703 | -352.9337 | 16.7889
11:32 | 724 | 18.5832 | 192.8734 | 433.6409 | 439.2228 | -21.6515 | -48.5384 | 0.1221 | -0.7977 | -8.3413 | -8.2879 | -3.6577 | -4.2256 | 1.341 | -5.7046 | 0.5793 | 0.6237 | 0.9547 | 0.6864 | -132.2658 | -8.9784 | -1.7477 | -2.9945 | -10.902 | -9.7973 | -1.8977 |  | -5.4568 | -4.7764 | 4.0348 | 3.3727 | 3.3571 | 0.9782 | 10.6123 | 13.9984 | 14.5685 | 10.8743 | -0.0005 | -0.003 | 0.0008 | 0.004 | 0.0004 | -0.0005 | -0.0032 | -0.007 | 0.0079 | -360.1188 | 17.6225 | -360.6081 | 17.9592 | -360.9312 | 18.0763 | -360.9804 | 17.5671 | -352.8691 | 18.7497 | -352.9214 | 16.7971
11:32 | 725 | 18.6437 | 192.897 | 433.7036 | 439.2559 | -21.6517 | -48.5567 | 0.1525 | -0.9266 | -8.4181 | -8.3175 | -3.6389 | -4.1076 | 1.3939 | -5.6167 | 0.581 | 0.6227 | 0.9547 | 0.6879 | -132.1917 | -8.9392 | -1.7518 | -3.0176 | -10.9753 | -9.8807 | -1.9994 |  | -5.4855 | -4.7806 | 4.0367 | 3.377 | 3.3554 | 0.9791 | 10.5994 | 14.0265 | 14.6223 | 10.9471 | -0.0003 | -0.0028 | 0.0006 | 0.0035 | 0.0008 | -0.0007 | 0.0119 | -0.0111 | -0.0013 | -360.1034 | 17.6245 | -360.6019 | 17.9756 | -360.9774 | 18.1153 | -361.0389 | 17.5732 | -352.8783 | 18.7477 | -352.9306 | 16.8032
11:32 | 726 | 18.5313 | 192.8631 | 433.6347 | 439.2487 | -21.6363 | -48.5859 | 0.1359 | -0.9197 | -8.3133 | -8.2534 | -3.6704 | -4.1373 | 1.3787 | -5.6159 | 0.58 | 0.6225 | 0.955 | 0.687 | -132.2242 | -8.9779 | -1.6852 | -3.0224 | -11.0095 | -9.8842 | -2.0087 |  | -5.457 | -4.8065 | 4.0356 | 3.3765 | 3.3579 | 0.9787 | 10.5868 | 14.0194 | 14.5794 | 10.9176 | 0.0003 | -0.0027 | 0.0003 | 0.0036 | 0.0007 | -0.0003 | 0.0066 | -0.0017 | -0.0175 | -360.1588 | 17.6184 | -360.5804 | 17.9551 | -360.9404 | 18.0906 | -361.0174 | 17.5835 | -352.8906 | 18.7353 | -352.8691 | 16.7827
11:32 | 727 | 18.5269 | 192.8129 | 433.7245 | 439.2402 | -21.7311 | -48.6367 | 0.0807 | -0.9275 | -8.2686 | -8.33 | -3.6328 | -4.0916 | 1.4422 | -5.6365 | 0.58 | 0.6256 | 0.9499 | 0.6865 | -132.3108 | -9.0425 | -1.8302 | -2.9599 | -11.0416 | -10.0782 | -1.9948 |  | -5.5005 | -4.8375 | 4.0353 | 3.3747 | 3.3602 | 0.9791 | 10.5962 | 13.9994 | 14.5977 | 10.9104 | 0 | -0.0032 | 0.0007 | 0.0035 | 0.001 | -0.0008 | -0.0016 | -0.0051 | -0.0263 | -360.1465 | 17.6594 | -360.6204 | 17.9448 | -360.9097 | 18.0865 | -361.0143 | 17.5835 | -352.906 | 18.7826 | -352.9275 | 16.7889
11:32 | 728 | 18.5844 | 192.9242 | 433.6687 | 439.3246 | -21.6958 | -48.6136 | 0.0462 | -0.9602 | -8.2978 | -8.2782 | -3.6598 | -4.0633 | 1.4278 | -5.6676 | 0.581 | 0.628 | 0.9582 | 0.6872 | -132.3328 | -9.0119 | -1.9467 | -2.9753 | -11.0515 | -9.923 | -1.8987 |  | -5.4964 | -4.8548 | 4.0364 | 3.3774 | 3.3592 | 0.9804 | 10.6144 | 14.0127 | 14.6206 | 10.9099 | -0.0002 | -0.003 | 0.0011 | 0.0039 | 0.0005 | -0.0001 | 0.0073 | -0.0173 | 0.0002 | -360.1373 | 17.6656 | -360.6727 | 17.9715 | -360.9527 | 18.0701 | -360.9558 | 17.5691 | -352.8937 | 18.7805 | -352.9644 | 16.8032
11:32 | 729 | 18.5479 | 192.8499 | 433.6453 | 439.2672 | -21.6805 | -48.722 | 0.0768 | -0.8574 | -8.27 | -8.2143 | -3.6238 | -4.1129 | 1.4494 | -5.6648 | 0.5798 | 0.6262 | 0.9585 | 0.6879 | -132.2694 | -9.0036 | -1.9476 | -2.914 | -11.0808 | -9.7988 | -1.9394 |  | -5.5523 | -4.8709 | 4.037 | 3.3745 | 3.3616 | 0.9804 | 10.5948 | 14.0277 | 14.6237 | 10.9251 | -0.0004 | -0.0029 | 0.0007 | 0.0036 | 0.0001 | -0.0008 | 0.0163 | -0.0157 | 0.007 | -360.1404 | 17.6286 | -360.6204 | 17.9695 | -360.9466 | 18.0845 | -360.9835 | 17.5712 | -352.8752 | 18.7661 | -352.9491 | 16.8012
11:32 | 730 | 18.6812 | 192.8631 | 433.6938 | 439.2981 | -21.6888 | -48.6658 | 0.0407 | -0.8234 | -8.2266 | -8.2744 | -3.598 | -4.1631 | 1.4644 | -5.6351 | 0.5804 | 0.6243 | 0.9521 | 0.6877 | -132.2972 | -8.9548 | -1.7355 | -2.7187 | -11.0332 | -9.8438 | -1.8391 |  | -5.4756 | -4.942 | 4.0364 | 3.3753 | 3.3578 | 0.9804 | 10.626 | 14.007 | 14.5985 | 10.9211 | -0.0003 | -0.0028 | 0.001 | 0.0037 | 0.0008 | -0.0004 | 0.0052 | -0.0151 | -0.0218 | -360.1188 | 17.6122 | -360.5835 | 17.9551 | -360.9343 | 18.1173 | -361.0328 | 17.5855 | -352.9152 | 18.7477 | -352.866 | 16.7807
11:32 | 731 | 18.5891 | 192.8682 | 433.7398 | 439.2916 | -21.7422 | -48.715 | 0.0559 | -0.8692 | -8.2403 | -8.2292 | -3.6768 | -4.1369 | 1.4388 | -5.6124 | 0.5812 | 0.6235 | 0.9546 | 0.6877 | -132.3373 | -9.1025 | -1.8291 | -2.9655 | -11.1153 | -9.958 | -1.9597 |  | -5.4446 | -4.8328 | 4.0367 | 3.3738 | 3.3566 | 0.9796 | 10.6422 | 14.052 | 14.6135 | 10.8973 | 0.0002 | -0.003 | 0.0005 | 0.0036 | 0.0001 | -0.0007 | 0.0081 | 0.0034 | 0.0019 | -360.1527 | 17.6143 | -360.5804 | 17.914 | -360.8912 | 18.0804 | -361.0143 | 17.5855 | -352.9244 | 18.7579 | -352.866 | 16.7581
11:32 | 732 | 18.6362 | 192.9693 | 433.7705 | 439.3498 | -21.7205 | -48.6363 | 0.0461 | -0.8828 | -8.2946 | -8.3054 | -3.7197 | -4.1218 | 1.3961 | -5.6775 | 0.5798 | 0.6212 | 0.9539 | 0.6864 | -132.1948 | -8.9594 | -1.7783 | -2.8627 | -11.0301 | -9.8233 | -1.9183 |  | -5.4687 | -4.7883 | 4.036 | 3.3756 | 3.3593 | 0.98 | 10.6029 | 14.0358 | 14.638 | 10.9157 | -0.0005 | -0.0033 | 0.0004 | 0.0038 | 0.001 | -0.0006 | -0.0001 | -0.0011 | -0.0162 | -360.165 | 17.6471 | -360.642 | 17.9695 | -360.9404 | 18.0988 | -361.0328 | 17.5835 | -352.9029 | 18.7682 | -352.9337 | 16.7909
11:32 | 733 | 18.7002 | 192.8929 | 433.7148 | 439.2621 | -21.5108 | -48.4559 | 0.1934 | -0.8569 | -8.2812 | -8.3129 | -3.6447 | -4.1652 | 1.3507 | -5.7037 | 0.5794 | 0.6248 | 0.9529 | 0.6868 | -132.2757 | -8.9653 | -1.7941 | -2.7867 | -10.9358 | -9.7955 | -1.8811 |  | -5.4276 | -4.9018 | 4.0345 | 3.3752 | 3.3595 | 0.9806 | 10.5902 | 14.0173 | 14.5903 | 10.9262 | -0.0005 | -0.0025 | 0.0005 | 0.0039 | 0.0006 | -0.0004 | 0.0126 | 0.0016 | -0.0195 | -360.125 | 17.6266 | -360.6327 | 17.988 | -360.9804 | 18.0763 | -360.9497 | 17.5547 | -352.8721 | 18.7436 | -352.9429 | 16.8176
11:32 | 734 | 18.6301 | 192.8759 | 433.617 | 439.2049 | -21.5676 | -48.3996 | 0.2268 | -0.926 | -8.3191 | -8.2635 | -3.6176 | -4.1988 | 1.3247 | -5.643 | 0.5788 | 0.6265 | 0.9574 | 0.6865 | -132.2713 | -8.9805 | -1.8289 | -2.7274 | -10.9011 | -9.7609 | -1.8385 |  | -5.4867 | -4.8454 | 4.035 | 3.3741 | 3.3598 | 0.9799 | 10.5881 | 14.0088 | 14.6018 | 10.9137 | -0.0005 | -0.0031 | 0.0001 | 0.003 | 0.0009 | -0.0008 | 0.0088 | 0.0009 | 0.006 | -360.1158 | 17.641 | -360.642 | 17.9921 | -361.0143 | 18.1153 | -361.0112 | 17.5732 | -352.8598 | 18.7579 | -352.9398 | 16.8197
11:32 | 735 | 18.6272 | 192.9375 | 433.6451 | 439.3159 | -21.5362 | -48.4209 | 0.155 | -0.9231 | -8.3328 | -8.4721 | -3.692 | -4.2783 | 1.285 | -5.7557 | 0.581 | 0.622 | 0.9521 | 0.6846 | -132.223 | -9.0035 | -1.772 | -2.7506 | -10.9993 | -9.8753 | -1.8855 |  | -5.4871 | -4.8424 | 4.0355 | 3.3741 | 3.3603 | 0.9801 | 10.5903 | 14.017 | 14.5651 | 10.8923 | -0.0001 | -0.0032 | 0.001 | 0.0035 | 0.0007 | -0.0002 | 0.012 | 0.004 | 0.0039 | -360.1373 | 17.6122 | -360.5835 | 17.951 | -360.9343 | 18.0988 | -361.0112 | 17.5732 | -352.8721 | 18.7518 | -352.8906 | 16.7868
11:32 | 736 | 18.6612 | 192.9402 | 433.7196 | 439.3334 | -21.5469 | -48.5168 | 0.1097 | -0.9837 | -8.2549 | -8.348 | -3.7327 | -4.1341 | 1.3723 | -5.6954 | 0.5805 | 0.6254 | 0.9549 | 0.6877 | -132.2297 | -9.0084 | -1.7998 | -2.8094 | -11.1011 | -9.9039 | -1.8799 |  | -5.4895 | -4.8748 | 4.0359 | 3.3749 | 3.358 | 0.9799 | 10.5833 | 14.0102 | 14.559 | 10.9082 | -0.0001 | -0.0034 | 0.0015 | 0.0039 | 0.0006 | -0.0008 | 0.0115 | -0.0059 | -0.0077 | -360.1681 | 17.6574 | -360.6358 | 17.9428 | -360.9004 | 18.0763 | -361.0143 | 17.604 | -352.9429 | 18.7805 | -352.9244 | 16.7971
11:32 | 737 | 18.766 | 192.9138 | 433.72 | 439.3857 | -21.5709 | -48.5248 | 0.1626 | -0.8862 | -8.3163 | -8.3439 | -3.8178 | -4.2822 | 1.3268 | -5.7613 | 0.5798 | 0.6252 | 0.9566 | 0.6862 | -132.2299 | -9.0598 | -1.7963 | -2.8839 | -11.0964 | -10.0492 | -1.9843 |  | -5.3962 | -4.7925 | 4.0348 | 3.3746 | 3.358 | 0.9804 | 10.5961 | 14.0228 | 14.5882 | 10.8981 | -0.0005 | -0.0029 | 0.0008 | 0.0038 | 0.0009 | -0.0002 | -0.0004 | -0.0215 | -0.0102 | -360.1558 | 17.6574 | -360.6143 | 17.9551 | -360.9127 | 18.0701 | -360.9712 | 17.5855 | -352.9337 | 18.7805 | -352.9152 | 16.795
11:32 | 738 | 18.6621 | 192.8375 | 433.8005 | 439.2614 | -21.5537 | -48.5053 | 0.2757 | -0.876 | -8.3463 | -8.3838 | -3.7284 | -4.3362 | 1.3819 | -5.68 | 0.58 | 0.6261 | 0.9562 | 0.6874 | -132.2352 | -8.9534 | -1.7645 | -2.7671 | -11.1077 | -9.9042 | -1.872 |  | -5.4657 | -4.7865 | 4.0359 | 3.375 | 3.3597 | 0.9807 | 10.6247 | 14.0582 | 14.6224 | 10.9424 | -0.0001 | -0.0024 | 0.001 | 0.0045 | 0.0009 | -0.0005 | 0.0117 | -0.0162 | -0.0009 | -360.1219 | 17.6225 | -360.6235 | 17.9654 | -360.9466 | 18.0906 | -360.9743 | 17.5609 | -352.8783 | 18.7559 | -352.9214 | 16.8074
11:32 | 739 | 18.5902 | 192.9288 | 433.7153 | 439.289 | -21.592 | -48.4284 | 0.2186 | -0.9693 | -8.3665 | -8.321 | -3.6501 | -4.3078 | 1.3658 | -5.7313 | 0.5797 | 0.6257 | 0.9547 | 0.6857 | -132.19 | -9.0123 | -1.8072 | -2.7963 | -11.0725 | -9.9076 | -1.8616 |  | -5.4191 | -4.8522 | 4.0358 | 3.3761 | 3.3581 | 0.979 | 10.6178 | 14.0453 | 14.6374 | 10.9417 | 0 | -0.0032 | 0.0006 | 0.0038 | 0.0008 | -0.0005 | 0.0023 | -0.0066 | -0.0123 | -360.1342 | 17.6143 | -360.6204 | 17.9798 | -360.9712 | 18.1214 | -361.0389 | 17.5794 | -352.8814 | 18.7497 | -352.8967 | 16.8115
11:32 | 740 | 18.6927 | 192.9019 | 433.7138 | 439.2733 | -21.4733 | -48.5197 | 0.2303 | -0.9002 | -8.327 | -8.3067 | -3.666 | -4.3217 | 1.3966 | -5.6348 | 0.5797 | 0.6287 | 0.9558 | 0.6863 | -132.2574 | -9.0839 | -1.8107 | -2.8189 | -11.0014 | -9.8693 | -1.8796 |  | -5.3974 | -4.8082 | 4.0354 | 3.3747 | 3.3584 | 0.9806 | 10.611 | 14.0208 | 14.606 | 10.9237 | 0.0002 | -0.0029 | 0.0005 | 0.0039 | 0.0008 | -0.0004 | -0.0054 | -0.0049 | -0.0138 | -360.1188 | 17.602 | -360.5989 | 17.9572 | -360.9374 | 18.1029 | -360.9897 | 17.5712 | -352.8875 | 18.7271 | -352.8506 | 16.8074
11:32 | 741 | 18.6392 | 192.9903 | 433.6859 | 439.3545 | -21.453 | -48.4561 | 0.1867 | -0.9126 | -8.3055 | -8.3956 | -3.766 | -4.3311 | 1.3421 | -5.6563 | 0.5798 | 0.6301 | 0.9556 | 0.6871 | -132.2158 | -9.0105 | -1.8042 | -2.7274 | -11.0196 | -9.7726 | -1.8393 |  | -5.304 | -4.7684 | 4.0361 | 3.3735 | 3.3572 | 0.9816 | 10.6063 | 14.0337 | 14.62 | 10.9301 | 0.0001 | -0.003 | 0.0007 | 0.0041 | 0.0004 | -0.001 | 0.0173 | -0.006 | 0.0104 | -360.1588 | 17.6533 | -360.6266 | 17.9613 | -360.9435 | 18.0906 | -361.0143 | 17.5978 | -352.9398 | 18.7846 | -352.9337 | 16.8032
11:32 | 742 | 18.667 | 192.8561 | 433.6002 | 439.2898 | -21.615 | -48.5374 | 0.1283 | -0.8667 | -8.2622 | -8.3351 | -3.6963 | -4.3825 | 1.3768 | -5.5397 | 0.5819 | 0.629 | 0.9509 | 0.6872 | -132.2101 | -8.9208 | -1.9004 | -2.7365 | -10.9731 | -9.7865 | -1.8508 |  | -5.467 | -4.8095 | 4.0365 | 3.3752 | 3.3589 | 0.982 | 10.6296 | 14.0275 | 14.6284 | 10.9313 | -0.0003 | -0.0025 | 0 | 0.003 | 0.0006 | -0.0001 | 0.0099 | -0.0044 | -0.0151 | -360.1527 | 17.6471 | -360.645 | 17.9592 | -360.9312 | 18.066 | -360.9589 | 17.5547 | -352.8906 | 18.7846 | -352.9244 | 16.8012
11:32 | 743 | 18.6847 | 192.9856 | 433.7495 | 439.3954 | -21.5285 | -48.4743 | 0.2543 | -0.8581 | -8.3132 | -8.3495 | -3.6557 | -4.3165 | 1.4039 | -5.6397 | 0.5802 | 0.6266 | 0.9531 | 0.6864 | -132.2492 | -8.9642 | -1.9406 | -2.9085 | -11.0633 | -9.8846 | -1.9122 |  | -5.3916 | -4.7626 | 4.0361 | 3.3721 | 3.3609 | 0.9811 | 10.588 | 14.0031 | 14.5739 | 10.8959 | 0.0001 | -0.0028 | 0.0009 | 0.0038 | 0.0006 | -0.0012 | 0.0065 | -0.0147 | 0.0016 | -360.1435 | 17.6328 | -360.6512 | 17.9695 | -360.9466 | 18.0783 | -360.9897 | 17.5794 | -352.9029 | 18.7579 | -352.9614 | 16.8176
11:32 | 744 | 18.6339 | 192.9415 | 433.7412 | 439.3149 | -21.5721 | -48.4417 | 0.1767 | -0.9084 | -8.3614 | -8.2346 | -3.7083 | -4.4054 | 1.3282 | -5.6731 | 0.58 | 0.6227 | 0.9553 | 0.6856 | -132.1939 | -8.9871 | -1.9033 | -2.9079 | -11.0406 | -9.9009 | -1.9001 |  | -5.3725 | -4.6595 | 4.0354 | 3.3729 | 3.3594 | 0.9816 | 10.6111 | 14.0148 | 14.5981 | 10.9302 | 0.0002 | -0.0031 | 0.0011 | 0.0041 | 0.0002 | -0.0007 | 0.021 | -0.0045 | -0.0219 | -360.1681 | 17.6348 | -360.6143 | 17.9592 | -360.9497 | 18.1132 | -360.9989 | 17.5712 | -352.9029 | 18.76 | -352.8814 | 16.8012
11:32 | 745 | 18.6553 | 193.0391 | 433.6746 | 439.3361 | -21.5162 | -48.4039 | 0.1708 | -0.7958 | -8.2741 | -8.0891 | -3.681 | -4.4274 | 1.3672 | -5.7434 | 0.581 | 0.6265 | 0.9543 | 0.6861 | -132.1299 | -8.9677 | -1.8454 | -2.9666 | -11.1233 | -9.8912 | -1.9034 |  | -5.3847 | -4.6696 | 4.0355 | 3.3746 | 3.3593 | 0.9822 | 10.5959 | 14.0173 | 14.5903 | 10.8973 | 0.0003 | -0.0027 | 0.001 | 0.0039 | 0.0006 | -0.0006 | 0.0013 | -0.0149 | -0.0175 | -360.1219 | 17.5978 | -360.5804 | 17.9387 | -360.9251 | 18.1029 | -361.0266 | 17.5835 | -352.906 | 18.7292 | -352.8721 | 16.7889
11:32 | 746 | 18.7057 | 192.889 | 433.7344 | 439.3713 | -21.5817 | -48.4588 | 0.1267 | -0.844 | -8.3264 | -8.2462 | -3.6014 | -4.4678 | 1.3051 | -5.706 | 0.5805 | 0.6265 | 0.9571 | 0.6883 | -132.1587 | -8.96 | -1.8493 | -2.8771 | -11.0592 | -9.7979 | -1.878 |  | -5.3321 | -4.7082 | 4.0337 | 3.3752 | 3.356 | 0.9811 | 10.6134 | 14.0114 | 14.5951 | 10.8977 | -0.0001 | -0.0025 | 0.0009 | 0.0044 | 0.0006 | -0.0006 | 0.0134 | -0.0022 | -0.0003 | -360.1342 | 17.6471 | -360.6481 | 17.9654 | -360.9404 | 18.0988 | -361.0143 | 17.5917 | -352.9121 | 18.7682 | -352.9398 | 16.8032
11:32 | 747 | 18.7882 | 192.9647 | 433.7493 | 439.3397 | -21.6135 | -48.5357 | 0.0539 | -0.7809 | -8.2359 | -8.1862 | -3.3536 | -4.4419 | 1.2979 | -5.8274 | 0.5809 | 0.628 | 0.9542 | 0.6864 | -132.1925 | -8.9779 | -1.7805 | -2.8526 | -10.9962 | -9.8187 | -1.812 |  | -5.3812 | -4.7048 | 4.0352 | 3.3717 | 3.3581 | 0.9815 | 10.6179 | 14.0567 | 14.5726 | 10.9247 | -0.0002 | -0.0024 | 0.0005 | 0.0041 | 0.0006 | 0 | 0.0028 | -0.0016 | -0.0055 | -360.1711 | 17.6328 | -360.6019 | 17.9551 | -360.9281 | 18.0742 | -360.9527 | 17.5671 | -352.8906 | 18.7436 | -352.9029 | 16.7991
11:32 | 748 | 18.8008 | 192.8869 | 433.7792 | 439.3098 | -21.689 | -48.5545 | 0.0636 | -0.85 | -8.2461 | -8.2467 | -3.4769 | -4.3933 | 1.3319 | -5.7551 | 0.5796 | 0.6276 | 0.9541 | 0.6863 | -132.1109 | -9.0234 | -1.7537 | -2.8823 | -10.9555 | -9.8003 | -1.9065 |  | -5.4798 | -4.6966 | 4.0353 | 3.3725 | 3.3592 | 0.982 | 10.6041 | 14.06 | 14.6094 | 10.9172 | 0 | -0.0031 | -0.0001 | 0.0035 | 0.0008 | -0.0009 | 0.0104 | -0.0102 | -0.0175 | -360.1588 | 17.6245 | -360.6112 | 17.9674 | -360.9374 | 18.0824 | -361.0051 | 17.5896 | -352.8844 | 18.7579 | -352.8937 | 16.8115
11:32 | 749 | 18.7383 | 192.912 | 433.8603 | 439.414 | -21.6605 | -48.4177 | 0.1166 | -0.8363 | -8.2657 | -8.2389 | -3.476 | -4.4116 | 1.3262 | -5.7319 | 0.5794 | 0.627 | 0.9544 | 0.6876 | -132.1821 | -8.9904 | -1.8145 | -2.8464 | -10.9655 | -9.8576 | -1.7932 |  | -5.4753 | -4.8319 | 4.0344 | 3.3722 | 3.3586 | 0.981 | 10.595 | 14.0272 | 14.6021 | 10.892 | -0.0005 | -0.0043 | 0.0007 | 0.0038 | 0.0004 | -0.0006 | -0.0028 | -0.013 | -0.0321 | -360.1311 | 17.6307 | -360.6296 | 17.9551 | -360.9158 | 18.1009 | -361.0081 | 17.5609 | -352.8475 | 18.7559 | -352.8906 | 16.8012
11:32 | 750 | 18.7187 | 192.9323 | 433.7551 | 439.3955 | -21.7157 | -48.4928 | 0.1275 | -0.815 | -8.3182 | -8.2341 | -3.479 | -4.3019 | 1.3192 | -5.7171 | 0.5795 | 0.624 | 0.9535 | 0.686 | -132.2183 | -9.0003 | -1.7914 | -2.9519 | -10.965 | -9.7476 | -1.8047 |  | -5.393 | -4.7815 | 4.0343 | 3.374 | 3.3579 | 0.9816 | 10.5845 | 14.0344 | 14.5767 | 10.927 | -0.0003 | -0.003 | 0.0007 | 0.0037 | 0.0005 | -0.001 | 0.0055 | -0.0163 | -0.01 | -360.165 | 17.6204 | -360.5927 | 17.9366 | -360.9066 | 18.068 | -360.9958 | 17.5835 | -352.9152 | 18.7559 | -352.8783 | 16.8074
11:32 | 751 | 18.666 | 192.9001 | 433.7984 | 439.3936 | -21.6777 | -48.5469 | 0.1529 | -0.7781 | -8.326 | -8.2882 | -3.4514 | -4.3178 | 1.2838 | -5.7821 | 0.5814 | 0.628 | 0.9518 | 0.687 | -132.1699 | -8.9597 | -1.8653 | -2.9284 | -10.9482 | -9.7826 | -1.8208 |  | -5.4992 | -4.7301 | 4.0354 | 3.3726 | 3.354 | 0.9813 | 10.58 | 14.0294 | 14.5807 | 10.9177 | -0.0005 | -0.0028 | 0.0005 | 0.0036 | 0.0001 | -0.0009 | 0.0009 | -0.0072 | -0.0141 | -360.1711 | 17.643 | -360.6389 | 17.9551 | -360.9374 | 18.0824 | -360.9866 | 17.5958 | -352.9121 | 18.7723 | -352.9183 | 16.8115
11:32 | 752 | 18.735 | 192.9706 | 433.6987 | 439.4653 | -21.6286 | -48.6172 | 0.1074 | -0.7654 | -8.2804 | -8.2387 | -3.4826 | -4.2692 | 1.2834 | -5.7759 | 0.5817 | 0.6279 | 0.9563 | 0.6873 | -132.14 | -8.8952 | -1.7913 | -2.9244 | -10.9939 | -9.8817 | -1.8708 |  | -5.4202 | -4.8273 | 4.0344 | 3.373 | 3.3556 | 0.9815 | 10.5868 | 14.0367 | 14.5736 | 10.9291 | 0 | -0.0028 | 0.0013 | 0.0041 | 0.0009 | -0.0008 | -0.0053 | -0.0099 | -0.0125 | -360.1127 | 17.6286 | -360.6081 | 17.9428 | -360.9158 | 18.0886 | -360.9774 | 17.5629 | -352.8383 | 18.7538 | -352.9152 | 16.8032
11:32 | 753 | 18.7932 | 192.972 | 433.7849 | 439.4832 | -21.6729 | -48.6039 | 0.222 | -0.7628 | -8.2964 | -8.1281 | -3.5117 | -4.355 | 1.1887 | -5.7882 | 0.5802 | 0.6247 | 0.9501 | 0.685 | -132.1148 | -8.8226 | -1.7842 | -2.9914 | -11.0113 | -9.8309 | -1.917 |  | -5.4602 | -4.7082 | 4.0333 | 3.3747 | 3.3551 | 0.9806 | 10.6041 | 14.0195 | 14.6036 | 10.9172 | 0.0008 | -0.0034 | 0.0008 | 0.0034 | 0.0005 | -0.0006 | 0.0139 | -0.0107 | -0.0072 | -360.1496 | 17.6328 | -360.6204 | 17.9715 | -360.9681 | 18.1153 | -361.0297 | 17.5753 | -352.8906 | 18.76 | -352.9337 | 16.8115
11:32 | 754 | 18.7545 | 192.9559 | 433.7639 | 439.467 | -21.5676 | -48.505 | 0.157 | -0.864 | -8.3165 | -8.2595 | -3.4723 | -4.3355 | 1.1702 | -5.7805 | 0.5799 | 0.6254 | 0.9555 | 0.6873 | -132.0823 | -8.9486 | -1.8902 | -2.9979 | -10.9735 | -9.8942 | -1.8515 |  | -5.4797 | -4.7859 | 4.0337 | 3.3748 | 3.3543 | 0.9814 | 10.6076 | 14.0286 | 14.6172 | 10.9154 | -0.0003 | -0.0029 | 0.0007 | 0.0036 | 0.0007 | -0.0007 | -0.0004 | -0.0034 | -0.0152 | -360.1404 | 17.6122 | -360.5804 | 17.951 | -360.9743 | 18.1029 | -360.9989 | 17.5753 | -352.8537 | 18.7353 | -352.8752 | 16.8135
11:32 | 755 | 18.713 | 192.9409 | 433.7231 | 439.3956 | -21.6852 | -48.5798 | 0.142 | -0.8217 | -8.3276 | -8.2042 | -3.4107 | -4.3187 | 1.2695 | -5.6801 | 0.5805 | 0.6266 | 0.9543 | 0.687 | -132.154 | -9.0148 | -1.9098 | -2.9765 | -11.0634 | -9.8184 | -1.8266 |  | -5.3745 | -4.7934 | 4.0339 | 3.3781 | 3.3577 | 0.9821 | 10.6511 | 14.0796 | 14.6712 | 10.9441 | 0 | -0.0023 | 0.0007 | 0.0041 | 0.0008 | -0.0003 | -0.0033 | -0.0057 | -0.0136 | -360.1496 | 17.6266 | -360.6204 | 17.9387 | -360.8727 | 18.0865 | -361.002 | 17.5773 | -352.8783 | 18.7641 | -352.9214 | 16.7991
11:32 | 756 | 18.6645 | 192.9629 | 433.6502 | 439.374 | -21.6988 | -48.5576 | 0.1053 | -0.9053 | -8.2895 | -8.1754 | -3.4935 | -4.2593 | 1.2073 | -5.6247 | 0.5784 | 0.6261 | 0.9538 | 0.6869 | -132.1167 | -9.0086 | -1.89 | -3.0553 | -11.0444 | -9.9385 | -1.8354 |  | -5.4075 | -4.7338 | 4.0332 | 3.3754 | 3.3554 | 0.9813 | 10.6076 | 14.0634 | 14.6356 | 10.9381 | -0.0007 | -0.003 | 0.0001 | 0.0034 | 0.0007 | -0.0002 | 0.0102 | 0.0127 | -0.024 | -360.1835 | 17.6615 | -360.6573 | 17.9592 | -360.9435 | 18.068 | -360.9527 | 17.5794 | -352.9306 | 18.7867 | -352.9491 | 16.8074
11:32 | 757 | 18.738 | 192.8904 | 433.6351 | 439.4489 | -21.7271 | -48.6491 | 0.0853 | -0.8382 | -8.1893 | -8.118 | -3.4614 | -4.3355 | 1.2851 | -5.6714 | 0.5788 | 0.6244 | 0.952 | 0.6866 | -132.2014 | -8.9825 | -1.8181 | -2.982 | -11.0176 | -9.8634 | -1.8333 |  | -5.4503 | -4.8058 | 4.0325 | 3.375 | 3.3539 | 0.9808 | 10.6133 | 14.0462 | 14.573 | 10.8915 | 0.0001 | -0.0029 | 0.0004 | 0.0041 | 0.0007 | -0.0005 | 0.0098 | -0.0116 | -0.0201 | -360.1558 | 17.6266 | -360.6296 | 17.9531 | -360.9466 | 18.068 | -360.9435 | 17.5609 | -352.8414 | 18.7538 | -352.9183 | 16.8115
11:32 | 758 | 18.7675 | 192.9087 | 433.6062 | 439.3808 | -21.7255 | -48.4694 | 0.1962 | -0.8965 | -8.1916 | -8.1228 | -3.5369 | -4.3313 | 1.2512 | -5.6709 | 0.5795 | 0.6244 | 0.952 | 0.6873 | -132.1748 | -8.9679 | -1.8538 | -2.9768 | -10.9968 | -9.8146 | -1.8537 |  | -5.5006 | -4.7752 | 4.0339 | 3.3761 | 3.362 | 0.9816 | 10.626 | 14.0243 | 14.5975 | 10.9273 | -0.0003 | -0.0036 | 0.001 | 0.0037 | 0.001 | -0.0001 | -0.0004 | -0.0056 | -0.0186 | -360.165 | 17.6184 | -360.6235 | 17.9756 | -360.9681 | 18.1173 | -361.0297 | 17.5896 | -352.8783 | 18.7477 | -352.9029 | 16.8094
11:32 | 759 | 18.7547 | 193.0811 | 433.5269 | 439.4008 | -21.7251 | -48.6081 | 0.124 | -0.9921 | -8.3157 | -8.1963 | -3.4897 | -4.3549 | 1.2883 | -5.6442 | 0.5786 | 0.6248 | 0.9585 | 0.6855 | -132.1759 | -8.9943 | -1.8716 | -2.8579 | -11.0823 | -9.9255 | -1.8703 |  | -5.4736 | -4.8626 | 4.0324 | 3.3754 | 3.3607 | 0.9824 | 10.58 | 14.0063 | 14.5807 | 10.8888 | -0.0004 | -0.0029 | 0.0005 | 0.0033 | 0.0007 | -0.0008 | -0.0029 | 0.0027 | -0.0121 | -360.1496 | 17.6061 | -360.5435 | 17.9223 | -360.9343 | 18.1029 | -361.0174 | 17.5999 | -352.8783 | 18.7292 | -352.8198 | 16.7766
11:32 | 760 | 18.7643 | 193.026 | 433.6453 | 439.4046 | -21.7761 | -48.5395 | 0.1473 | -0.9134 | -8.2861 | -8.218 | -3.4116 | -4.311 | 1.2336 | -5.6222 | 0.5812 | 0.6232 | 0.9527 | 0.6876 | -132.1359 | -8.9271 | -1.8802 | -2.9144 | -11.1043 | -9.8723 | -1.8674 |  | -5.4679 | -4.7964 | 4.0334 | 3.3738 | 3.357 | 0.9816 | 10.5856 | 13.9779 | 14.5791 | 10.8872 | -0.0001 | -0.0027 | 0.0013 | 0.0038 | 0.0007 | -0.0003 | 0.0028 | -0.0171 | -0.0216 | -360.165 | 17.6328 | -360.6266 | 17.951 | -360.9251 | 18.0886 | -361.0112 | 17.5937 | -352.8937 | 18.762 | -352.9306 | 16.8032
11:32 | 761 | 18.6626 | 192.9489 | 433.5694 | 439.3789 | -21.7814 | -48.4732 | 0.0621 | -0.9184 | -8.2618 | -8.2089 | -3.5249 | -4.2818 | 1.2402 | -5.7095 | 0.5813 | 0.623 | 0.9571 | 0.6874 | -132.1445 | -8.8926 | -1.8411 | -2.8559 | -11.0659 | -9.8793 | -1.8662 |  | -5.4832 | -4.7011 | 4.0342 | 3.3755 | 3.3539 | 0.9822 | 10.6248 | 14.0754 | 14.6098 | 10.9254 | 0.0001 | -0.0029 | 0.001 | 0.0036 | 0.0005 | -0.0008 | 0.0111 | -0.0082 | -0.0062 | -360.1219 | 17.643 | -360.6573 | 17.9695 | -360.9835 | 18.0845 | -360.9435 | 17.5506 | -352.866 | 18.762 | -352.946 | 16.8217
11:32 | 762 | 18.7056 | 193.0742 | 433.5854 | 439.4336 | -21.8702 | -48.5503 | 0.022 | -0.8439 | -8.3023 | -8.2988 | -3.5182 | -4.2809 | 1.3333 | -5.6465 | 0.5795 | 0.6246 | 0.9551 | 0.688 | -132.1677 | -8.9481 | -1.8723 | -2.8698 | -11.0472 | -9.9018 | -1.8292 |  | -5.4103 | -4.8297 | 4.033 | 3.3721 | 3.3571 | 0.9815 | 10.5926 | 14.0252 | 14.5447 | 10.906 | 0.0003 | -0.003 | 0.0006 | 0.0034 | 0.0005 | -0.0004 | -0.0062 | -0.0099 | -0.0214 | -360.1096 | 17.6245 | -360.6296 | 17.951 | -360.9558 | 18.0947 | -360.9466 | 17.5486 | -352.8691 | 18.7415 | -352.9244 | 16.8299
11:32 | 763 | 18.687 | 192.9837 | 433.595 | 439.3741 | -21.7898 | -48.5743 | 0.0252 | -0.898 | -8.2679 | -8.2013 | -3.5319 | -4.3291 | 1.2603 | -5.6231 | 0.5802 | 0.6239 | 0.955 | 0.6867 | -132.1987 | -9.0621 | -1.8669 | -2.7946 | -10.9519 | -9.8674 | -1.824 |  | -5.41 | -4.8052 | 4.033 | 3.3759 | 3.3568 | 0.983 | 10.604 | 14.0256 | 14.6346 | 10.928 | 0 | -0.0032 | 0.0007 | 0.0039 | 0.0008 | -0.0003 | 0.0092 | -0.0024 | -0.0203 | -360.165 | 17.6328 | -360.5866 | 17.9346 | -360.9374 | 18.105 | -361.0389 | 17.5958 | -352.9121 | 18.7559 | -352.906 | 16.7991
11:32 | 764 | 18.7469 | 192.9925 | 433.6715 | 439.4412 | -21.6698 | -48.5743 | 0.086 | -0.8825 | -8.2756 | -8.3313 | -3.5022 | -4.3423 | 1.3084 | -5.6977 | 0.5803 | 0.626 | 0.9571 | 0.6882 | -132.1985 | -8.9379 | -1.831 | -2.9091 | -10.9269 | -9.8562 | -1.9013 |  | -5.5014 | -4.7737 | 4.0328 | 3.3736 | 3.3568 | 0.9819 | 10.6352 | 14.0741 | 14.6305 | 10.9247 | -0.0001 | -0.0024 | -0.0002 | 0.0034 | 0.0002 | -0.001 | 0.0007 | -0.0033 | -0.0251 | -360.1619 | 17.6266 | -360.5773 | 17.8956 | -360.8789 | 18.0578 | -361.002 | 17.5876 | -352.9275 | 18.7559 | -352.8937 | 16.7909
11:32 | 765 | 18.7964 | 193.0326 | 433.7039 | 439.5174 | -21.6561 | -48.5039 | 0.1002 | -0.8607 | -8.243 | -8.2299 | -3.4461 | -4.3154 | 1.3091 | -5.8146 | 0.5812 | 0.6235 | 0.9566 | 0.6882 | -132.0912 | -8.9348 | -1.8002 | -2.9586 | -10.9428 | -9.7753 | -1.9251 |  | -5.4343 | -4.8055 | 4.032 | 3.3756 | 3.3583 | 0.9827 | 10.5879 | 14.0612 | 14.5992 | 10.924 | -0.0002 | -0.0028 | 0.0008 | 0.0039 | 0.0005 | -0.0006 | 0.0039 | 0.0026 | -0.0103 | -360.2019 | 17.6471 | -360.6481 | 17.9346 | -360.9251 | 18.0783 | -360.9835 | 17.5773 | -352.9583 | 18.7805 | -352.9306 | 16.8156
11:32 | 766 | 18.7441 | 192.9883 | 433.7775 | 439.5457 | -21.6528 | -48.6145 | 0.0964 | -0.8874 | -8.3069 | -8.2303 | -3.4716 | -4.4151 | 1.2238 | -5.7858 | 0.58 | 0.6257 | 0.9552 | 0.6875 | -132.1416 | -8.8922 | -1.7544 | -2.9936 | -10.8926 | -9.7292 | -1.9294 |  | -5.5113 | -4.9086 | 4.0314 | 3.3754 | 3.3577 | 0.9838 | 10.5926 | 14.0367 | 14.6141 | 10.8829 | 0.0002 | -0.0027 | 0.0005 | 0.0038 | 0.0007 | -0.0013 | 0.0127 | 0.0048 | 0.014 | -360.125 | 17.604 | -360.5989 | 17.9325 | -360.9497 | 18.0865 | -360.9774 | 17.5486 | -352.8537 | 18.7312 | -352.8783 | 16.8135
11:32 | 767 | 18.8083 | 193.0347 | 433.7456 | 439.4668 | -21.6006 | -48.5 | 0.1396 | -0.9281 | -8.3301 | -8.187 | -3.4379 | -4.3593 | 1.2579 | -5.7695 | 0.5808 | 0.625 | 0.9547 | 0.6872 | -132.1595 | -8.8697 | -1.8105 | -2.9695 | -10.9314 | -9.801 | -2.0103 |  | -5.5009 | -4.9584 | 4.0313 | 3.377 | 3.3569 | 0.9827 | 10.61 | 14.0424 | 14.5784 | 10.8833 | -0.0001 | -0.0032 | 0.0008 | 0.0034 | 0 | -0.0007 | 0.0126 | 0.0025 | 0.0002 | -360.1681 | 17.5999 | -360.6081 | 17.9366 | -360.9681 | 18.1358 | -361.042 | 17.5917 | -352.8721 | 18.7395 | -352.8814 | 16.8197
11:33 | 768 | 18.7703 | 192.9838 | 433.6744 | 439.4883 | -21.7603 | -48.5366 | 0.0866 | -0.8281 | -8.3535 | -8.0648 | -3.4611 | -4.2942 | 1.1915 | -5.7383 | 0.5798 | 0.6271 | 0.9553 | 0.6876 | -132.1246 | -8.9279 | -1.7765 | -2.8519 | -10.9845 | -9.8421 | -1.9568 |  | -5.5425 | -4.8581 | 4.0324 | 3.3762 | 3.3593 | 0.9838 | 10.5706 | 14.009 | 14.5808 | 10.8898 | -0.0004 | -0.0026 | 0.0016 | 0.0047 | 0.0007 | -0.001 | 0.007 | 0.0047 | -0.0193 | -360.1188 | 17.6061 | -360.5866 | 17.9099 | -360.885 | 18.105 | -361.0051 | 17.5773 | -352.8906 | 18.7456 | -352.8629 | 16.793
11:33 | 769 | 18.8844 | 192.9865 | 433.6922 | 439.4519 | -21.748 | -48.6817 | 0.0354 | -0.8824 | -8.2811 | -8.1915 | -3.4928 | -4.269 | 1.3605 | -5.6688 | 0.5813 | 0.6282 | 0.9553 | 0.6886 | -132.2285 | -8.9351 | -1.8331 | -2.8418 | -11.0588 | -9.9594 | -1.9419 |  | -5.4309 | -4.7957 | 4.0319 | 3.3765 | 3.3569 | 0.9837 | 10.5867 | 14.0311 | 14.5978 | 10.9287 | 0 | -0.0023 | 0.0008 | 0.0037 | 0.0004 | -0.0006 | 0.0141 | -0.0091 | -0.0007 | -360.2204 | 17.6533 | -360.6635 | 17.9387 | -360.9589 | 18.0927 | -360.9651 | 17.5876 | -352.9244 | 18.7949 | -352.9244 | 16.8135
11:33 | 770 | 18.8386 | 192.9881 | 433.6491 | 439.4974 | -21.8078 | -48.6265 | 0.0469 | -0.8625 | -8.3521 | -8.2597 | -3.4763 | -4.3578 | 1.3804 | -5.7074 | 0.5805 | 0.6286 | 0.9577 | 0.6872 | -132.1173 | -8.8372 | -1.7837 | -2.8595 | -10.9746 | -9.9057 | -1.9681 |  | -5.5259 | -4.9064 | 4.0329 | 3.3762 | 3.3595 | 0.9839 | 10.5972 | 14.0182 | 14.578 | 10.928 | 0.0001 | -0.0032 | 0.0007 | 0.0038 | 0.001 | -0.0002 | 0.0214 | -0.0118 | -0.0178 | -360.0973 | 17.6348 | -360.6327 | 17.9448 | -360.9589 | 18.0886 | -360.922 | 17.5547 | -352.8567 | 18.7559 | -352.9306 | 16.8176
11:33 | 771 | 18.7817 | 193.0029 | 433.7112 | 439.4549 | -21.8244 | -48.6292 | -0.0274 | -0.8691 | -8.3857 | -8.2487 | -3.5718 | -4.3799 | 1.3613 | -5.8288 | 0.5803 | 0.6271 | 0.9565 | 0.6887 | -132.1124 | -8.8679 | -1.8258 | -2.8268 | -11.0409 | -9.8927 | -1.9623 |  | -5.419 | -4.7919 | 4.0318 | 3.3755 | 3.3642 | 0.983 | 10.6179 | 14.0392 | 14.589 | 10.9482 | 0.0002 | -0.0028 | 0.0006 | 0.0041 | 0.0005 | -0.0003 | 0.0127 | 0.0008 | 0.0007 | -360.1711 | 17.6204 | -360.6481 | 17.9448 | -360.9466 | 18.1337 | -361.0266 | 17.5753 | -352.8721 | 18.7723 | -352.9306 | 16.8115
11:33 | 772 | 18.7794 | 193.0222 | 433.6755 | 439.4253 | -21.7251 | -48.4927 | 0.0692 | -0.8675 | -8.3309 | -8.1898 | -3.4961 | -4.4123 | 1.2791 | -5.8806 | 0.5791 | 0.6223 | 0.9564 | 0.6868 | -132.0901 | -8.9671 | -1.8222 | -2.7217 | -10.9973 | -9.8469 | -1.9709 |  | -5.4157 | -4.7514 | 4.0323 | 3.3778 | 3.3617 | 0.9837 | 10.5845 | 14.0402 | 14.5998 | 10.9443 | -0.0003 | -0.0031 | 0.0005 | 0.0038 | 0.0005 | -0.0004 | -0.0003 | -0.0122 | -0.0061 | -360.1835 | 17.6122 | -360.5527 | 17.8956 | -360.8943 | 18.1132 | -361.0112 | 17.5978 | -352.9121 | 18.7415 | -352.8475 | 16.7807
11:33 | 773 | 18.8362 | 193.0795 | 433.6948 | 439.5346 | -21.6571 | -48.4825 | 0.1913 | -0.8552 | -8.4068 | -8.2156 | -3.524 | -4.4137 | 1.2541 | -5.7709 | 0.5806 | 0.6292 | 0.9574 | 0.6877 | -132.1376 | -8.8946 | -1.8269 | -2.7686 | -11.0326 | -9.8789 | -1.8738 |  | -5.3598 | -4.789 | 4.0339 | 3.377 | 3.3619 | 0.9839 | 10.6433 | 14.0766 | 14.6459 | 10.9265 | -0.0003 | -0.0027 | 0.0009 | 0.0041 | 0.0007 | -0.0008 | -0.0065 | -0.0105 | -0.0003 | -360.1988 | 17.643 | -360.6266 | 17.9058 | -360.9189 | 18.1276 | -361.042 | 17.5937 | -352.9521 | 18.7785 | -352.9244 | 16.795
11:33 | 774 | 18.8037 | 193.015 | 433.6333 | 439.4343 | -21.6678 | -48.4238 | 0.1114 | -0.904 | -8.342 | -8.1923 | -3.4507 | -4.4347 | 1.3497 | -5.8105 | 0.5813 | 0.6277 | 0.9572 | 0.6847 | -132.0547 | -8.8817 | -1.8033 | -2.8952 | -11.1099 | -9.9554 | -2.036 |  | -5.4 | -4.7766 | 4.0313 | 3.3727 | 3.3599 | 0.9832 | 10.6063 | 14.0509 | 14.6305 | 10.9594 | -0.0001 | -0.0029 | 0.0005 | 0.0039 | 0.0005 | -0.0007 | 0.0053 | -0.0136 | -0.0036 | -360.1835 | 17.6307 | -360.6112 | 17.9182 | -360.9343 | 18.1029 | -360.9558 | 17.5486 | -352.8537 | 18.7641 | -352.906 | 16.795
11:33 | 775 | 18.7129 | 193.0493 | 433.5506 | 439.417 | -21.6223 | -48.5241 | 0.1703 | -0.9261 | -8.3916 | -8.2191 | -3.5355 | -4.3665 | 1.3268 | -5.8134 | 0.581 | 0.6264 | 0.9563 | 0.6846 | -132.0319 | -8.7915 | -1.8825 | -2.8927 | -11.0954 | -10.0285 | -2.0149 |  | -5.3723 | -4.7698 | 4.032 | 3.3751 | 3.3612 | 0.9847 | 10.6121 | 14.0452 | 14.6247 | 10.9247 | -0.0002 | -0.0033 | 0.0009 | 0.0039 | 0.0009 | -0.0008 | 0.0185 | 0.0006 | -0.0291 | -360.1096 | 17.6184 | -360.6204 | 17.9469 | -361.002 | 18.1379 | -361.0051 | 17.5547 | -352.866 | 18.7436 | -352.9275 | 16.8279
11:33 | 776 | 18.796 | 192.9675 | 433.6348 | 439.3616 | -21.6539 | -48.4461 | 0.1363 | -0.9226 | -8.3858 | -8.2457 | -3.5411 | -4.4086 | 1.3262 | -5.744 | 0.5805 | 0.628 | 0.9555 | 0.6843 | -132.0108 | -8.8367 | -1.8272 | -2.8512 | -11.0676 | -9.9218 | -2.0288 |  | -5.4027 | -4.8281 | 4.0315 | 3.3753 | 3.3593 | 0.9845 | 10.596 | 14.0461 | 14.6356 | 10.9612 | -0.0002 | -0.0029 | 0.0007 | 0.0034 | 0 | -0.0011 | 0.0094 | -0.0143 | -0.0046 | -360.1034 | 17.5896 | -360.5958 | 17.9058 | -360.9312 | 18.1255 | -360.9589 | 17.5404 | -352.8752 | 18.7312 | -352.8475 | 16.793
11:33 | 777 | 18.8121 | 192.9541 | 433.5907 | 439.425 | -21.6304 | -48.3554 | 0.1683 | -0.8861 | -8.2857 | -8.1084 | -3.5621 | -4.3372 | 1.4034 | -5.6561 | 0.5792 | 0.6254 | 0.9537 | 0.6845 | -131.9737 | -8.76 | -1.9004 | -2.7568 | -11.0006 | -9.9296 | -2.0024 |  | -5.4259 | -4.7773 | 4.0312 | 3.3759 | 3.3628 | 0.9845 | 10.6052 | 14.0207 | 14.6107 | 10.9298 | -0.0004 | -0.0032 | 0.0008 | 0.0031 | 0.0009 | -0.0006 | 0.0101 | 0.0033 | -0.017 | -360.2019 | 17.6328 | -360.6081 | 17.9161 | -360.9312 | 18.1194 | -361.0328 | 17.5896 | -352.9183 | 18.7682 | -352.9183 | 16.795
11:33 | 778 | 18.7915 | 192.9326 | 433.7046 | 439.4631 | -21.6184 | -48.4195 | 0.1988 | -0.8954 | -8.367 | -8.2023 | -3.5844 | -4.3693 | 1.3895 | -5.6586 | 0.5808 | 0.625 | 0.9528 | 0.6863 | -132.0692 | -8.8394 | -1.8427 | -2.8477 | -11.0864 | -9.8466 | -2.0145 |  | -5.4804 | -4.8506 | 4.0321 | 3.3752 | 3.3586 | 0.9856 | 10.6213 | 14.0431 | 14.6183 | 10.9102 | -0.0001 | -0.0027 | 0.0011 | 0.0038 | 0.0008 | -0.0004 | 0.0197 | -0.0061 | -0.0039 | -360.1527 | 17.6307 | -360.6327 | 17.8997 | -360.9097 | 18.0906 | -360.9404 | 17.5383 | -352.8814 | 18.7764 | -352.8937 | 16.795
11:33 | 779 | 18.8367 | 192.9817 | 433.7291 | 439.4749 | -21.6426 | -48.5356 | 0.1403 | -0.8669 | -8.2616 | -8.2699 | -3.4434 | -4.3266 | 1.4048 | -5.7636 | 0.5804 | 0.6242 | 0.953 | 0.686 | -132.0398 | -8.8354 | -1.8544 | -2.9037 | -11.1111 | -9.8573 | -2.0027 |  | -5.367 | -4.8509 | 4.0317 | 3.3736 | 3.3582 | 0.9856 | 10.5891 | 14.0449 | 14.6169 | 10.9544 | -0.0002 | -0.0035 | 0.0008 | 0.0041 | 0.0008 | -0.0006 | 0.0121 | -0.0021 | -0.0122 | -360.1404 | 17.643 | -360.6604 | 17.9407 | -360.9958 | 18.1173 | -360.9743 | 17.5568 | -352.8967 | 18.7826 | -352.9675 | 16.8176
11:33 | 780 | 18.774 | 192.9887 | 433.7773 | 439.4659 | -21.6916 | -48.4211 | 0.1047 | -0.8666 | -8.3132 | -8.1352 | -3.4581 | -4.2608 | 1.3588 | -5.7637 | 0.5787 | 0.6236 | 0.9511 | 0.6854 | -131.9993 | -8.9238 | -1.871 | -3.0248 | -11.0254 | -9.9305 | -2.0462 |  | -5.3795 | -4.916 | 4.0314 | 3.3749 | 3.3557 | 0.9848 | 10.6064 | 14.0391 | 14.5879 | 10.9255 | 0 | -0.003 | 0.0006 | 0.0036 | 0.0011 | -0.0003 | -0.0015 | -0.0051 | -0.0185 | -360.0758 | 17.5999 | -360.5804 | 17.9099 | -360.9189 | 18.1255 | -360.9897 | 17.5424 | -352.8475 | 18.7559 | -352.8691 | 16.7991
11:33 | 781 | 18.8067 | 193.0377 | 433.8317 | 439.5439 | -21.653 | -48.3949 | 0.1554 | -0.8559 | -8.2585 | -8.2815 | -3.4539 | -4.3631 | 1.3433 | -5.8399 | 0.5793 | 0.6241 | 0.9529 | 0.6879 | -132.0639 | -8.8476 | -1.9125 | -2.9611 | -11.0401 | -9.9213 | -2.0517 |  | -5.391 | -4.8628 | 4.0305 | 3.3771 | 3.3615 | 0.9855 | 10.6444 | 14.0604 | 14.6357 | 10.9276 | 0 | -0.0027 | 0.0009 | 0.0041 | 0.0003 | -0.0005 | 0.0083 | -0.0109 | 0.0054 | -360.2081 | 17.6245 | -360.5866 | 17.9058 | -360.9527 | 18.1317 | -361.042 | 17.604 | -352.9244 | 18.7785 | -352.866 | 16.7807
11:33 | 782 | 18.7709 | 193.0666 | 433.6595 | 439.5263 | -21.6719 | -48.3338 | 0.1395 | -0.8876 | -8.335 | -8.2618 | -3.4924 | -4.2063 | 1.4507 | -5.7265 | 0.579 | 0.6207 | 0.9533 | 0.6861 | -131.9666 | -8.8619 | -1.9304 | -2.9584 | -10.9819 | -9.8716 | -1.9498 |  | -5.3248 | -4.727 | 4.0321 | 3.3736 | 3.359 | 0.986 | 10.6111 | 14.0379 | 14.6039 | 10.9187 | -0.0005 | -0.0028 | 0.0007 | 0.0037 | 0.0007 | -0.0011 | 0.0152 | -0.0062 | 0.0075 | -360.1958 | 17.6184 | -360.5743 | 17.875 | -360.8912 | 18.1009 | -361.0143 | 17.5691 | -352.8998 | 18.7703 | -352.8721 | 16.7724
11:33 | 783 | 18.8142 | 193.0336 | 433.6593 | 439.4236 | -21.7642 | -48.4681 | 0.0985 | -0.9287 | -8.3589 | -8.2065 | -3.537 | -4.2334 | 1.4409 | -5.6917 | 0.5804 | 0.6252 | 0.9559 | 0.686 | -132.0422 | -8.8131 | -1.939 | -2.9192 | -10.9523 | -9.8567 | -2.0151 |  | -5.3777 | -4.7106 | 4.0305 | 3.3763 | 3.3588 | 0.9848 | 10.5958 | 14.035 | 14.6166 | 10.925 | 0.0001 | -0.0027 | 0.0009 | 0.0039 | 0.0013 | 0.0004 | 0.0011 | -0.0044 | 0.0019 | -360.1465 | 17.6451 | -360.6358 | 17.9161 | -360.9404 | 18.1153 | -360.9897 | 17.5629 | -352.8967 | 18.7846 | -352.9306 | 16.8197
11:33 | 784 | 18.8529 | 193.0385 | 433.7593 | 439.4954 | -21.7096 | -48.4428 | 0.0992 | -0.9463 | -8.3061 | -8.2311 | -3.4619 | -4.2642 | 1.4373 | -5.6762 | 0.5815 | 0.6253 | 0.9535 | 0.6877 | -132.0641 | -8.8524 | -1.8631 | -2.8277 | -11.089 | -9.9417 | -2.0881 |  | -5.4836 | -4.8315 | 4.0295 | 3.376 | 3.3624 | 0.9846 | 10.6042 | 14.0135 | 14.5784 | 10.9064 | 0 | -0.003 | 0.0005 | 0.0036 | 0.0005 | -0.0012 | 0.0086 | 0.0045 | -0.0055 | -360.0819 | 17.5896 | -360.5989 | 17.9284 | -360.9651 | 18.1173 | -360.9466 | 17.528 | -352.829 | 18.7456 | -352.8998 | 16.8279
11:33 | 785 | 18.787 | 193.0288 | 433.6472 | 439.5493 | -21.7682 | -48.4535 | 0.1065 | -0.9775 | -8.3841 | -8.3261 | -3.5298 | -4.2156 | 1.3393 | -5.6985 | 0.5804 | 0.6257 | 0.954 | 0.6862 | -132.0869 | -8.8714 | -1.7095 | -2.8972 | -11.0636 | -9.8352 | -2.0179 |  | -5.4766 | -4.8885 | 4.0299 | 3.3765 | 3.357 | 0.9861 | 10.5961 | 14.0228 | 14.6114 | 10.9385 | -0.0002 | -0.0031 | 0.0004 | 0.0032 | 0.0003 | -0.0004 | 0.0028 | 0.0058 | -0.0036 | -360.1281 | 17.6184 | -360.6266 | 17.9243 | -360.9958 | 18.1379 | -361.0081 | 17.5527 | -352.8721 | 18.7559 | -352.8783 | 16.8176
11:33 | 786 | 18.8074 | 193.0726 | 433.7344 | 439.4535 | -21.6631 | -48.4287 | 0.1534 | -0.8212 | -8.3466 | -8.3354 | -3.5979 | -4.3767 | 1.3257 | -5.7469 | 0.5806 | 0.6265 | 0.9519 | 0.6864 | -132.0301 | -8.8466 | -1.8166 | -2.8618 | -10.9433 | -9.8728 | -2.0311 |  | -5.4032 | -4.9098 | 4.0294 | 3.376 | 3.3585 | 0.9837 | 10.6132 | 14.0174 | 14.6319 | 10.9027 | 0.0001 | -0.0024 | 0.0008 | 0.0037 | 0.0006 | -0.001 | 0.0012 | -0.0181 | 0.0175 | -360.1404 | 17.6061 | -360.565 | 17.8915 | -360.9189 | 18.1112 | -361.0051 | 17.5691 | -352.8814 | 18.7641 | -352.8721 | 16.7991
11:33 | 787 | 18.7287 | 193.0382 | 433.6944 | 439.5035 | -21.7495 | -48.5133 | 0.1133 | -0.8048 | -8.2498 | -8.2966 | -3.5687 | -4.3137 | 1.3444 | -5.7159 | 0.5798 | 0.6227 | 0.9539 | 0.686 | -132.0519 | -8.801 | -1.8921 | -2.9125 | -10.9236 | -9.8913 | -1.9848 |  | -5.3844 | -4.7959 | 4.0301 | 3.373 | 3.3566 | 0.9851 | 10.6181 | 14.0448 | 14.5811 | 10.9374 | -0.0002 | -0.0027 | 0.0008 | 0.0039 | 0.0005 | -0.0006 | -0.001 | -0.0103 | -0.0333 | -360.205 | 17.6512 | -360.645 | 17.914 | -360.9466 | 18.1009 | -360.9866 | 17.5773 | -352.9275 | 18.7949 | -352.9552 | 16.8135
11:33 | 788 | 18.7816 | 193.0704 | 433.7058 | 439.447 | -21.6896 | -48.4343 | 0.1169 | -0.9308 | -8.3286 | -8.231 | -3.6108 | -4.3399 | 1.4353 | -5.6977 | 0.5794 | 0.6256 | 0.9556 | 0.6858 | -132.0604 | -8.8095 | -1.7984 | -2.881 | -11.0619 | -9.8643 | -2.0076 |  | -5.4555 | -4.8181 | 4.0305 | 3.3741 | 3.3583 | 0.9852 | 10.6248 | 14.0291 | 14.6329 | 10.9023 | 0.0005 | -0.0029 | 0.0006 | 0.0036 | 0.0009 | -0.0006 | 0.0108 | -0.0133 | 0.0012 | -360.1219 | 17.6266 | -360.6358 | 17.8935 | -360.9097 | 18.0865 | -360.9774 | 17.5568 | -352.9029 | 18.7867 | -352.9337 | 16.8238
11:33 | 789 | 18.9274 | 193.1859 | 433.7262 | 439.533 | -21.7314 | -48.4992 | 0.0423 | -0.8753 | -8.2875 | -8.2475 | -3.4337 | -4.2832 | 1.3852 | -5.8219 | 0.5804 | 0.6261 | 0.9526 | 0.6858 | -132.0865 | -8.8561 | -1.9086 | -2.864 | -11.0775 | -9.9854 | -2.0121 |  | -5.4923 | -4.9582 | 4.0302 | 3.3742 | 3.3589 | 0.9858 | 10.6215 | 14.0367 | 14.6373 | 10.9291 | -0.0002 | -0.0032 | 0.0003 | 0.0038 | 0.0008 | -0.0008 | 0.0088 | -0.0124 | 0.0118 | -360.1281 | 17.6163 | -360.6235 | 17.9243 | -360.9651 | 18.1194 | -361.0081 | 17.5527 | -352.8937 | 18.7682 | -352.9121 | 16.8258
11:33 | 790 | 18.8315 | 193.049 | 433.7593 | 439.5354 | -21.6662 | -48.4357 | 0.2561 | -0.9097 | -8.2788 | -8.3012 | -3.4786 | -4.279 | 1.3241 | -5.7756 | 0.5792 | 0.6241 | 0.9542 | 0.6884 | -132.1452 | -8.9233 | -1.9098 | -2.9757 | -11.0607 | -9.8931 | -1.928 |  | -5.4357 | -4.8935 | 4.0295 | 3.3779 | 3.3624 | 0.9854 | 10.5962 | 14.0168 | 14.5572 | 10.8989 | -0.0005 | -0.0025 | 0.0005 | 0.0037 | 0.0003 | -0.0005 | 0.0199 | -0.0145 | 0.0045 | -360.1496 | 17.5917 | -360.5373 | 17.8853 | -360.9158 | 18.1317 | -361.0266 | 17.5629 | -352.8783 | 18.7353 | -352.8629 | 16.7971
11:33 | 791 | 18.8041 | 193.0645 | 433.7374 | 439.4668 | -21.5761 | -48.4172 | 0.2525 | -0.939 | -8.3609 | -8.233 | -3.5571 | -4.3258 | 1.3961 | -5.7446 | 0.5785 | 0.6273 | 0.9553 | 0.6861 | -132.0034 | -8.9103 | -1.8919 | -2.9182 | -11.0542 | -9.8591 | -2.0344 |  | -5.4214 | -4.8195 | 4.03 | 3.3776 | 3.3576 | 0.9856 | 10.5844 | 14.0578 | 14.5845 | 10.9031 | -0.0004 | -0.0026 | 0.0002 | 0.0035 | 0.0011 | -0.0007 | 0.0079 | -0.0036 | -0.0038 | -360.1465 | 17.6184 | -360.5927 | 17.8997 | -360.9435 | 18.1379 | -361.0235 | 17.5855 | -352.8783 | 18.7641 | -352.8814 | 16.8115
11:33 | 792 | 18.7804 | 193.0044 | 433.6797 | 439.418 | -21.6267 | -48.4085 | 0.3183 | -0.9842 | -8.3645 | -8.2623 | -3.4875 | -4.3012 | 1.3033 | -5.7769 | 0.5803 | 0.6279 | 0.9522 | 0.6864 | -131.974 | -8.8389 | -1.7935 | -2.94 | -11.0065 | -9.8058 | -1.9903 |  | -5.5097 | -4.8708 | 4.0304 | 3.379 | 3.3589 | 0.9853 | 10.5905 | 14.0398 | 14.614 | 10.8935 | -0.0002 | -0.0032 | 0.0007 | 0.0036 | -0.0002 | -0.0008 | -0.0004 | -0.0055 | -0.0034 | -360.1465 | 17.6204 | -360.5958 | 17.9058 | -360.9004 | 18.0927 | -360.9804 | 17.5568 | -352.866 | 18.76 | -352.8937 | 16.8094
11:33 | 793 | 18.7299 | 193.0797 | 433.7328 | 439.4438 | -21.5378 | -48.4127 | 0.3409 | -1.0075 | -8.3266 | -8.2416 | -3.5259 | -4.3395 | 1.3109 | -5.7606 | 0.5804 | 0.6294 | 0.9588 | 0.6853 | -131.9733 | -8.8612 | -1.8106 | -2.9123 | -11.003 | -9.812 | -1.9574 |  | -5.4327 | -4.8196 | 4.0294 | 3.3726 | 3.3565 | 0.9854 | 10.5832 | 14.0683 | 14.6132 | 10.9305 | 0.0002 | -0.0031 | 0.001 | 0.0037 | 0.001 | -0.0007 | 0.0056 | -0.0094 | -0.0181 | -360.1496 | 17.6451 | -360.6635 | 17.9448 | -360.9927 | 18.1235 | -360.9897 | 17.5486 | -352.8906 | 18.7846 | -352.9552 | 16.8443
11:33 | 794 | 18.8216 | 193.0116 | 433.6504 | 439.5162 | -21.4898 | -48.3983 | 0.3057 | -1.0175 | -8.3084 | -8.3022 | -3.603 | -4.3833 | 1.2807 | -5.8709 | 0.58 | 0.6283 | 0.9548 | 0.6841 | -132.0132 | -8.9826 | -1.8704 | -2.8342 | -11.1074 | -9.8889 | -2.0348 |  | -5.4958 | -4.8429 | 4.0288 | 3.3733 | 3.3592 | 0.9868 | 10.6042 | 14.0308 | 14.6131 | 10.9353 | -0.0004 | -0.0031 | 0.0005 | 0.0033 | -0.0001 | -0.0006 | 0.0247 | -0.0133 | -0.0242 | -360.0881 | 17.6061 | -360.6081 | 17.9182 | -360.9435 | 18.1112 | -360.9774 | 17.528 | -352.8198 | 18.7538 | -352.8998 | 16.8361
11:33 | 795 | 18.805 | 193.0306 | 433.7795 | 439.4709 | -21.6088 | -48.3544 | 0.297 | -0.9187 | -8.2538 | -8.3143 | -3.5865 | -4.262 | 1.3573 | -5.7674 | 0.58 | 0.6301 | 0.9555 | 0.6857 | -131.9509 | -8.9507 | -1.8276 | -2.8628 | -11.1098 | -9.7948 | -2.0334 |  | -5.4659 | -4.7517 | 4.0293 | 3.377 | 3.3612 | 0.9865 | 10.6134 | 14.0345 | 14.624 | 10.9439 | -0.0002 | -0.0027 | 0.0007 | 0.0036 | 0.0004 | -0.0006 | 0.0038 | -0.0079 | 0.0199 | -360.1527 | 17.6061 | -360.6204 | 17.9161 | -360.9404 | 18.1399 | -361.0266 | 17.5732 | -352.8691 | 18.762 | -352.906 | 16.8217
11:33 | 796 | 18.7802 | 193.0515 | 433.6506 | 439.4446 | -21.6295 | -48.4468 | 0.2385 | -1.0056 | -8.3819 | -8.2858 | -3.6055 | -4.3752 | 1.2555 | -5.7626 | 0.5808 | 0.6301 | 0.953 | 0.686 | -132.052 | -8.8168 | -1.7946 | -2.8012 | -10.9886 | -9.8169 | -1.9958 |  | -5.5338 | -4.8305 | 4.0293 | 3.3766 | 3.3587 | 0.9867 | 10.5947 | 14.0683 | 14.6189 | 10.9074 | -0.0002 | -0.0031 | 0.0005 | 0.0038 | 0.0006 | -0.0008 | -0.0039 | -0.01 | -0.0083 | -360.1804 | 17.6225 | -360.5866 | 17.8853 | -360.8881 | 18.0886 | -360.9897 | 17.5753 | -352.9091 | 18.76 | -352.8814 | 16.7889
11:33 | 797 | 18.7977 | 193.0355 | 433.8445 | 439.4501 | -21.6596 | -48.3796 | 0.2481 | -0.9976 | -8.4185 | -8.282 | -3.6174 | -4.2644 | 1.3189 | -5.7546 | 0.5794 | 0.628 | 0.9527 | 0.6853 | -132.0361 | -8.8729 | -1.7945 | -2.848 | -11.1059 | -9.8715 | -1.9816 |  | -5.5684 | -4.8857 | 4.029 | 3.3751 | 3.3542 | 0.9859 | 10.6158 | 14.0424 | 14.6304 | 10.9353 | 0.0001 | -0.0031 | 0.0005 | 0.0037 | 0.0003 | -0.0007 | -0.0029 | -0.0142 | -0.0124 | -360.1742 | 17.6348 | -360.6296 | 17.912 | -360.9158 | 18.1029 | -360.9897 | 17.5773 | -352.9275 | 18.7846 | -352.9121 | 16.8156
11:33 | 798 | 18.807 | 193.0483 | 433.7775 | 439.4905 | -21.5621 | -48.4623 | 0.212 | -0.9501 | -8.39 | -8.2726 | -3.55 | -4.2743 | 1.3128 | -5.796 | 0.5801 | 0.6322 | 0.953 | 0.6866 | -132.0088 | -8.8637 | -1.7697 | -2.8582 | -11.1157 | -9.8061 | -2.0437 |  | -5.5847 | -4.8463 | 4.0304 | 3.3765 | 3.3593 | 0.9861 | 10.6075 | 14.0404 | 14.6193 | 10.9377 | 0.0002 | -0.0031 | 0.0008 | 0.004 | 0.0008 | -0.0008 | 0.0034 | 0.0023 | -0.0007 | -360.1096 | 17.6143 | -360.6143 | 17.9284 | -360.962 | 18.105 | -360.9374 | 17.5404 | -352.8629 | 18.7559 | -352.9029 | 16.8197
11:33 | 799 | 18.8014 | 193.0366 | 433.7575 | 439.4749 | -21.6289 | -48.4184 | 0.3076 | -0.9321 | -8.4569 | -8.2741 | -3.5522 | -4.3206 | 1.308 | -5.8297 | 0.5795 | 0.6292 | 0.9529 | 0.6859 | -131.962 | -8.8761 | -1.7714 | -2.9203 | -11.1874 | -9.8872 | -2.04 |  | -5.5064 | -4.7497 | 4.0303 | 3.3778 | 3.357 | 0.9867 | 10.6099 | 14.0252 | 14.6199 | 10.9291 | -0.0007 | -0.003 | 0.0005 | 0.0035 | 0.0002 | -0.0007 | -0.0002 | -0.0045 | -0.0136 | -360.1004 | 17.5978 | -360.6173 | 17.9407 | -361.002 | 18.1481 | -361.0451 | 17.5609 | -352.8844 | 18.7518 | -352.8875 | 16.832
11:33 | 800 | 18.8524 | 193.1203 | 433.8314 | 439.4986 | -21.617 | -48.479 | 0.2715 | -0.9228 | -8.4332 | -8.3009 | -3.5505 | -4.3827 | 1.3347 | -5.8313 | 0.5806 | 0.6284 | 0.9523 | 0.6853 | -132.0288 | -8.9427 | -1.931 | -2.8815 | -11.1433 | -9.7737 | -1.9269 |  | -5.4928 | -4.7914 | 4.0296 | 3.3761 | 3.3577 | 0.9872 | 10.5614 | 14.0286 | 14.5593 | 10.9096 | -0.0003 | -0.0027 | 0.0006 | 0.0034 | 0.0007 | -0.001 | 0.0023 | -0.0077 | 0.0036 | -360.1311 | 17.5876 | -360.5496 | 17.9099 | -360.9435 | 18.1112 | -361.0174 | 17.5547 | -352.8567 | 18.7436 | -352.8598 | 16.8094
11:33 | 801 | 18.8098 | 193.0704 | 433.7693 | 439.5605 | -21.5531 | -48.3742 | 0.2806 | -1.0521 | -8.4767 | -8.3607 | -3.6108 | -4.349 | 1.3324 | -5.8074 | 0.58 | 0.6262 | 0.9516 | 0.6859 | -132.0614 | -8.9688 | -1.8176 | -2.8828 | -11.1105 | -9.7757 | -1.933 |  | -5.4951 | -4.7265 | 4.0295 | 3.3756 | 3.3598 | 0.9863 | 10.6099 | 14.0367 | 14.5736 | 10.9118 | -0.0002 | -0.0032 | 0.0011 | 0.0041 | 0.0005 | -0.0003 | 0.017 | 0.0052 | -0.018 | -360.205 | 17.6369 | -360.6173 | 17.9038 | -360.9404 | 18.1112 | -361.0174 | 17.5773 | -352.9244 | 18.7826 | -352.9121 | 16.8074
11:33 | 802 | 18.8564 | 193.1246 | 433.8366 | 439.5059 | -21.6138 | -48.3921 | 0.361 | -1.0189 | -8.3926 | -8.3241 | -3.5562 | -4.3114 | 1.3971 | -5.8393 | 0.5797 | 0.6294 | 0.9522 | 0.6836 | -132.0476 | -8.986 | -1.8028 | -2.87 | -10.9809 | -9.8394 | -1.9476 |  | -5.5537 | -4.7654 | 4.0299 | 3.3768 | 3.3585 | 0.987 | 10.6156 | 14.0486 | 14.6336 | 10.9515 | 0.0002 | -0.0029 | 0.0007 | 0.0035 | 0.0007 | -0.0011 | 0.0121 | -0.0006 | -0.0172 | -360.2019 | 17.6369 | -360.6327 | 17.9202 | -360.9497 | 18.0824 | -360.9251 | 17.5424 | -352.8721 | 18.7785 | -352.9337 | 16.8217
11:33 | 803 | 18.8342 | 193.1569 | 433.8858 | 439.5176 | -21.7219 | -48.3508 | 0.3113 | -0.9939 | -8.4265 | -8.3195 | -3.561 | -4.2839 | 1.4527 | -5.7891 | 0.5799 | 0.632 | 0.9544 | 0.6873 | -132.0183 | -8.8888 | -1.8007 | -2.8813 | -11.061 | -9.8082 | -2.0586 |  | -5.501 | -4.7909 | 4.0288 | 3.3767 | 3.359 | 0.9866 | 10.5694 | 13.9963 | 14.591 | 10.9233 | -0.0001 | -0.0029 | 0.0008 | 0.0035 | 0.0008 | 0 | 0.0239 | -0.0129 | -0.0044 | -360.125 | 17.6184 | -360.645 | 17.9366 | -360.9681 | 18.105 | -360.962 | 17.5486 | -352.8844 | 18.7785 | -352.9491 | 16.8402
11:33 | 804 | 18.8032 | 193.0519 | 433.8119 | 439.4659 | -21.7098 | -48.3267 | 0.3619 | -0.9343 | -8.4047 | -8.2691 | -3.5826 | -4.3722 | 1.3651 | -5.8414 | 0.5811 | 0.628 | 0.9528 | 0.6862 | -132.1058 | -8.9546 | -1.7991 | -2.9266 | -11.0759 | -9.8137 | -2.0568 |  | -5.4719 | -4.7219 | 4.0297 | 3.3724 | 3.3563 | 0.9861 | 10.5971 | 14.0647 | 14.6148 | 10.9504 | -0.0003 | -0.0026 | 0.0009 | 0.0036 | 0.0008 | -0.0005 | 0.0047 | -0.0066 | -0.0142 | -360.1619 | 17.5937 | -360.5835 | 17.8976 | -360.9281 | 18.1337 | -361.0266 | 17.5588 | -352.8598 | 18.7497 | -352.8629 | 16.8074
11:33 | 805 | 18.8858 | 193.0437 | 433.8301 | 439.5602 | -21.6346 | -48.3085 | 0.3858 | -0.8644 | -8.3766 | -8.2473 | -3.5352 | -4.3188 | 1.4184 | -5.763 | 0.5808 | 0.6307 | 0.953 | 0.6849 | -132.0675 | -8.9286 | -1.8042 | -2.9681 | -11.1834 | -9.8661 | -2.0788 |  | -5.4868 | -4.7982 | 4.0274 | 3.3751 | 3.3579 | 0.987 | 10.6157 | 14.0658 | 14.6267 | 10.9114 | 0 | -0.0027 | 0.0001 | 0.0032 | 0.0008 | -0.0001 | -0.0021 | -0.0099 | -0.0068 | -360.1835 | 17.6122 | -360.5619 | 17.8833 | -360.922 | 18.1317 | -361.0266 | 17.5835 | -352.9367 | 18.76 | -352.8598 | 16.7991
11:33 | 806 | 18.9095 | 192.9845 | 433.7789 | 439.5681 | -21.7209 | -48.361 | 0.3906 | -0.9768 | -8.5217 | -8.3575 | -3.6186 | -4.3157 | 1.3584 | -5.7192 | 0.5805 | 0.6315 | 0.9542 | 0.6841 | -132.013 | -8.8655 | -1.7594 | -2.9091 | -11.1178 | -9.7818 | -2.0199 |  | -5.4942 | -4.7473 | 4.0285 | 3.3749 | 3.3587 | 0.9873 | 10.6076 | 14.0344 | 14.5998 | 10.9385 | -0.0002 | -0.0032 | 0.0004 | 0.0035 | 0.0006 | -0.0005 | 0.0011 | -0.0074 | -0.0014 | -360.165 | 17.6245 | -360.605 | 17.9038 | -360.9066 | 18.1173 | -361.0143 | 17.5671 | -352.8844 | 18.7723 | -352.8998 | 16.8074
11:33 | 807 | 18.7441 | 192.9521 | 433.783 | 439.5859 | -21.723 | -48.3695 | 0.2361 | -0.949 | -8.4037 | -8.2539 | -3.5962 | -4.3103 | 1.3554 | -5.7758 | 0.5798 | 0.6297 | 0.9578 | 0.6846 | -132.0584 | -8.9151 | -1.7188 | -2.9963 | -11.0775 | -9.8521 | -2.0392 |  | -5.4743 | -4.8162 | 4.0284 | 3.376 | 3.356 | 0.9859 | 10.6214 | 14.0428 | 14.6104 | 10.9572 | -0.0001 | -0.0026 | 0.0005 | 0.0035 | 0.0007 | -0.0012 | 0.0185 | -0.0035 | -0.0099 | -360.125 | 17.6204 | -360.642 | 17.9325 | -360.9651 | 18.1071 | -360.9743 | 17.5547 | -352.8752 | 18.7744 | -352.9337 | 16.8361
11:33 | 808 | 18.7522 | 192.925 | 433.8053 | 439.6189 | -21.6502 | -48.3412 | 0.2213 | -0.9003 | -8.5564 | -8.2865 | -3.6401 | -4.3549 | 1.3954 | -5.7579 | 0.5795 | 0.6318 | 0.9564 | 0.686 | -132.0732 | -9.0575 | -1.8111 | -2.9348 | -11.0921 | -9.8367 | -2.0772 |  | -5.4186 | -4.8138 | 4.0283 | 3.3753 | 3.3561 | 0.9865 | 10.5984 | 14.0714 | 14.6199 | 10.906 | -0.0007 | -0.0027 | 0.0006 | 0.0039 | 0.0003 | -0.0005 | 0.0106 | 0.002 | 0.0074 | -360.1065 | 17.602 | -360.6143 | 17.9366 | -360.9866 | 18.1255 | -360.9589 | 17.5301 | -352.826 | 18.7497 | -352.8998 | 16.832
11:33 | 809 | 18.8383 | 192.9616 | 433.7516 | 439.6546 | -21.6536 | -48.3686 | 0.3265 | -0.843 | -8.5653 | -8.1933 | -3.6931 | -4.3337 | 1.3692 | -5.8299 | 0.5789 | 0.6296 | 0.9538 | 0.6833 | -132.0387 | -9.0043 | -1.7717 | -2.9607 | -11.0987 | -9.7423 | -2.0281 |  | -5.4784 | -4.7976 | 4.0281 | 3.3766 | 3.3576 | 0.9873 | 10.6179 | 14.0452 | 14.6305 | 10.8901 | -0.0002 | -0.0023 | 0.0011 | 0.004 | 0.001 | -0.0011 | 0.005 | -0.0047 | -0.0119 | -360.1404 | 17.6081 | -360.5896 | 17.9202 | -360.9527 | 18.1379 | -361.0112 | 17.5629 | -352.8598 | 18.7661 | -352.8967 | 16.8279
11:33 | 810 | 18.8407 | 193.0343 | 433.8343 | 439.6826 | -21.7483 | -48.494 | 0.2674 | -0.8401 | -8.504 | -8.284 | -3.7378 | -4.3712 | 1.4374 | -5.8364 | 0.5802 | 0.6283 | 0.9527 | 0.6843 | -132.1283 | -9.0379 | -1.7996 | -2.9262 | -11.1 | -9.7868 | -2.0297 |  | -5.5043 | -4.7976 | 4.0287 | 3.3759 | 3.3594 | 0.9871 | 10.6132 | 14.029 | 14.6377 | 10.9374 | 0.0001 | -0.0031 | 0.001 | 0.0038 | 0.0006 | -0.0003 | 0.0009 | -0.0088 | -0.0147 | -360.1742 | 17.6122 | -360.605 | 17.8791 | -360.8727 | 18.1091 | -360.9989 | 17.5629 | -352.8814 | 18.7744 | -352.8506 | 16.7971
11:33 | 811 | 18.9428 | 193.0329 | 433.749 | 439.6436 | -21.7368 | -48.4543 | 0.2763 | -0.9358 | -8.5501 | -8.2384 | -3.6687 | -4.4378 | 1.3445 | -5.8373 | 0.58 | 0.6297 | 0.9523 | 0.6849 | -132.175 | -9.0068 | -1.8275 | -3.0015 | -11.1019 | -9.8244 | -2.0291 |  | -5.4679 | -4.7487 | 4.0298 | 3.3758 | 3.3583 | 0.987 | 10.6018 | 14.0634 | 14.6298 | 10.9381 | 0.0001 | -0.0031 | 0.0002 | 0.0032 | 0.0007 | -0.0007 | -0.0038 | -0.0096 | -0.0174 | -360.1927 | 17.6471 | -360.6389 | 17.9161 | -360.9035 | 18.1091 | -360.9866 | 17.5671 | -352.9429 | 18.8072 | -352.9337 | 16.8156
11:33 | 812 | 18.8608 | 193.0162 | 433.6959 | 439.6477 | -21.7509 | -48.3261 | 0.2883 | -0.9289 | -8.5053 | -8.263 | -3.7122 | -4.3845 | 1.4689 | -5.771 | 0.5799 | 0.629 | 0.9547 | 0.6858 | -132.0968 | -8.9028 | -1.6965 | -2.9493 | -11.0502 | -9.7923 | -2.0615 |  | -5.4729 | -4.8548 | 4.0279 | 3.3736 | 3.3567 | 0.9876 | 10.5971 | 14.0068 | 14.6254 | 10.893 | -0.0001 | -0.0025 | 0.0003 | 0.0035 | 0.0005 | -0.0006 | -0.0007 | -0.0071 | 0.003 | -360.1496 | 17.6163 | -360.6081 | 17.912 | -360.9589 | 18.1009 | -360.9312 | 17.5506 | -352.8814 | 18.7682 | -352.9183 | 16.8135
11:33 | 813 | 18.8234 | 193.0402 | 433.5981 | 439.6379 | -21.7783 | -48.4416 | 0.2608 | -0.8781 | -8.5003 | -8.155 | -3.5944 | -4.3317 | 1.4225 | -5.7505 | 0.5793 | 0.6265 | 0.9524 | 0.6852 | -131.9906 | -8.9604 | -1.7215 | -2.935 | -11.1199 | -9.7797 | -2.0256 |  | -5.468 | -4.8146 | 4.0282 | 3.3723 | 3.3578 | 0.987 | 10.6308 | 14.0575 | 14.6056 | 10.9443 | -0.0003 | -0.0027 | -0.0003 | 0.0032 | 0.0005 | -0.0004 | 0.0092 | 0.0012 | -0.0234 | -360.1188 | 17.5958 | -360.605 | 17.912 | -360.9743 | 18.1399 | -361.0358 | 17.5629 | -352.8691 | 18.7641 | -352.8937 | 16.8279
11:33 | 814 | 18.881 | 193.0429 | 433.7475 | 439.6579 | -21.7405 | -48.4294 | 0.2152 | -0.8702 | -8.4964 | -8.1575 | -3.617 | -4.3208 | 1.4483 | -5.723 | 0.5791 | 0.6306 | 0.9573 | 0.6859 | -131.9928 | -8.9918 | -1.7567 | -2.9363 | -11.0924 | -9.7089 | -1.9922 |  | -5.4305 | -4.8664 | 4.0282 | 3.3721 | 3.355 | 0.986 | 10.603 | 14.0413 | 14.6243 | 10.928 | 0.0002 | -0.0031 | 0.0006 | 0.0038 | 0.0005 | -0.001 | -0.0081 | -0.0186 | -0.0115 | -360.1404 | 17.5835 | -360.5527 | 17.8833 | -360.8943 | 18.1153 | -361.0297 | 17.565 | -352.8721 | 18.7415 | -352.8321 | 16.795
11:33 | 815 | 18.8244 | 192.9567 | 433.7926 | 439.6078 | -21.7184 | -48.3602 | 0.3529 | -0.8718 | -8.3986 | -8.1262 | -3.6554 | -4.3337 | 1.4191 | -5.6974 | 0.5803 | 0.6275 | 0.9535 | 0.6852 | -132.0094 | -8.9711 | -1.7656 | -2.9189 | -11.0997 | -9.6845 | -1.9278 |  | -5.4385 | -4.8689 | 4.0288 | 3.3743 | 3.3547 | 0.9872 | 10.5718 | 14.0448 | 14.5984 | 10.9317 | 0.0001 | -0.0029 | 0.0009 | 0.0039 | 0.0003 | -0.0005 | -0.0017 | -0.0125 | -0.0243 | -360.1988 | 17.6266 | -360.6173 | 17.9079 | -360.9374 | 18.1235 | -361.042 | 17.5814 | -352.9337 | 18.7723 | -352.8967 | 16.8156
11:33 | 816 | 18.829 | 192.9908 | 433.7998 | 439.62 | -21.6907 | -48.357 | 0.3238 | -0.9186 | -8.4889 | -8.1817 | -3.6759 | -4.3381 | 1.3991 | -5.7683 | 0.5804 | 0.6253 | 0.9548 | 0.6858 | -132.0074 | -9.0054 | -1.8057 | -2.9142 | -11.0433 | -9.592 | -2.0061 |  | -5.4125 | -4.802 | 4.0288 | 3.3769 | 3.3554 | 0.9863 | 10.5799 | 14.0298 | 14.5954 | 10.9338 | -0.0003 | -0.003 | 0.0005 | 0.0036 | 0.0009 | -0.0007 | -0.0023 | -0.0061 | -0.0348 | -360.1373 | 17.6122 | -360.6112 | 17.9079 | -360.9374 | 18.0886 | -360.9435 | 17.5301 | -352.866 | 18.7744 | -352.8998 | 16.8197
11:33 | 817 | 18.856 | 192.9375 | 433.7795 | 439.5898 | -21.6401 | -48.3803 | 0.3753 | -0.8799 | -8.3729 | -8.2364 | -3.6862 | -4.4173 | 1.3593 | -5.862 | 0.5813 | 0.6277 | 0.954 | 0.6872 | -132.0049 | -8.9856 | -1.8909 | -2.9346 | -11.1804 | -9.7876 | -2.0855 |  | -5.4379 | -4.725 | 4.0287 | 3.3763 | 3.3559 | 0.9872 | 10.5972 | 14.024 | 14.6128 | 10.9165 | -0.0005 | -0.0028 | 0.0009 | 0.004 | 0.0003 | -0.0006 | 0.0035 | -0.0048 | -0.0201 | -360.1404 | 17.6184 | -360.6604 | 17.951 | -361.0204 | 18.1337 | -360.9897 | 17.5486 | -352.8691 | 18.7703 | -352.9214 | 16.8443
11:33 | 818 | 18.8531 | 192.93 | 433.8478 | 439.5861 | -21.6719 | -48.4162 | 0.2911 | -0.8632 | -8.3906 | -8.1348 | -3.6914 | -4.4151 | 1.3805 | -5.7888 | 0.5794 | 0.6278 | 0.952 | 0.6859 | -132.1615 | -8.9997 | -1.8259 | -2.9359 | -11.1509 | -9.7235 | -1.9558 |  | -5.4847 | -4.875 | 4.0284 | 3.3764 | 3.3545 | 0.9869 | 10.6157 | 14.06 | 14.6152 | 10.9576 | -0.0003 | -0.0028 | 0.001 | 0.0036 | 0.0008 | -0.0008 | 0.0035 | -0.0041 | -0.0041 | -360.0942 | 17.5999 | -360.5835 | 17.9017 | -360.9404 | 18.1337 | -360.9281 | 17.5424 | -352.8198 | 18.7415 | -352.906 | 16.8156
11:33 | 819 | 18.8238 | 193.0418 | 433.7727 | 439.6566 | -21.7009 | -48.4834 | 0.3022 | -0.8167 | -8.3859 | -8.1378 | -3.634 | -4.4578 | 1.3731 | -5.8176 | 0.5816 | 0.6295 | 0.9547 | 0.6885 | -132.2352 | -9.0109 | -1.817 | -2.9907 | -11.1063 | -9.7056 | -1.9781 |  | -5.4683 | -4.8441 | 4.0283 | 3.3738 | 3.3556 | 0.9862 | 10.6352 | 14.0798 | 14.671 | 10.9536 | 0.0003 | -0.003 | 0.0002 | 0.0034 | 0.0004 | -0.0003 | 0.0135 | -0.0196 | -0.0009 | -360.1804 | 17.6245 | -360.5989 | 17.9058 | -360.9158 | 18.1399 | -361.0451 | 17.5917 | -352.9183 | 18.7723 | -352.9214 | 16.8032
11:33 | 820 | 18.778 | 192.9989 | 433.7611 | 439.6195 | -21.7538 | -48.4767 | 0.2012 | -0.7879 | -8.4361 | -8.1902 | -3.7114 | -4.4244 | 1.369 | -5.777 | 0.5793 | 0.6264 | 0.948 | 0.6866 | -132.2763 | -9.0769 | -1.8462 | -3.0831 | -11.1277 | -9.8001 | -1.9864 |  | -5.4856 | -4.8931 | 4.028 | 3.3763 | 3.3543 | 0.9883 | 10.626 | 14.0705 | 14.6206 | 10.9562 | -0.0002 | -0.0032 | 0.001 | 0.0039 | 0.0004 | -0.0009 | 0.0022 | -0.0053 | -0.021 | -360.1527 | 17.6328 | -360.5927 | 17.8833 | -360.9097 | 18.1153 | -360.9804 | 17.5671 | -352.906 | 18.7682 | -352.8875 | 16.8032
11:33 | 821 | 18.8159 | 192.972 | 433.7183 | 439.6375 | -21.8043 | -48.5011 | 0.1935 | -0.8849 | -8.4455 | -8.2665 | -3.7734 | -4.3542 | 1.424 | -5.7631 | 0.5805 | 0.6298 | 0.9515 | 0.6863 | -132.2328 | -9.0071 | -1.7463 | -2.9427 | -11.1246 | -9.6701 | -1.9518 |  | -5.4319 | -4.7809 | 4.0262 | 3.3735 | 3.3538 | 0.9882 | 10.6411 | 14.0508 | 14.6642 | 10.954 | -0.0002 | -0.0028 | 0.0004 | 0.0032 | 0.0005 | -0.0007 | 0.01 | 0.0062 | -0.0161 | -360.1558 | 17.6266 | -360.6481 | 17.9223 | -360.9651 | 18.1461 | -360.9927 | 17.565 | -352.8906 | 18.7805 | -352.9306 | 16.832
11:33 | 822 | 18.8233 | 192.998 | 433.8062 | 439.6328 | -21.907 | -48.5021 | 0.2134 | -0.9393 | -8.4207 | -8.2214 | -3.7033 | -4.3915 | 1.3729 | -5.7873 | 0.5796 | 0.6274 | 0.9533 | 0.6853 | -132.2239 | -8.9335 | -1.797 | -2.9786 | -11.1328 | -9.7314 | -1.9515 |  | -5.4761 | -4.8188 | 4.0293 | 3.3774 | 3.355 | 0.9888 | 10.5938 | 14.032 | 14.6087 | 10.919 | -0.0006 | -0.0032 | 0.0006 | 0.0034 | 0.0004 | -0.0007 | 0.0228 | -0.0134 | -0.0061 | -360.0819 | 17.5917 | -360.5743 | 17.9017 | -360.962 | 18.1666 | -361.0051 | 17.5445 | -352.8352 | 18.7312 | -352.8629 | 16.8156
11:33 | 823 | 18.7007 | 192.921 | 433.7769 | 439.5488 | -21.8056 | -48.4863 | 0.1583 | -0.8705 | -8.4003 | -8.2741 | -3.6414 | -4.4244 | 1.3763 | -5.7697 | 0.58 | 0.6277 | 0.9515 | 0.6861 | -132.1629 | -8.9231 | -1.7738 | -3.039 | -11.1728 | -9.7892 | -2.0119 |  | -5.4636 | -4.847 | 4.0278 | 3.3741 | 3.3551 | 0.9894 | 10.5937 | 14.0264 | 14.6155 | 10.9187 | 0.0001 | -0.0032 | 0.001 | 0.0043 | 0.0007 | -0.0005 | -0.0014 | -0.0099 | -0.0181 | -360.1465 | 17.5999 | -360.5989 | 17.9058 | -360.9281 | 18.1748 | -361.0574 | 17.5753 | -352.9214 | 18.7518 | -352.8691 | 16.8197
11:33 | 824 | 18.805 | 192.9971 | 433.8401 | 439.7264 | -21.8396 | -48.4637 | 0.2573 | -0.8638 | -8.4164 | -8.2114 | -3.7031 | -4.3619 | 1.3827 | -5.7723 | 0.5804 | 0.6332 | 0.9545 | 0.687 | -132.2242 | -8.9935 | -1.8186 | -3.091 | -11.0811 | -9.7185 | -2.0123 |  | -5.4286 | -4.862 | 4.0273 | 3.3742 | 3.3542 | 0.9876 | 10.5982 | 14.0428 | 14.6336 | 10.9515 | 0.0001 | -0.0031 | 0.0004 | 0.0035 | 0.0007 | -0.0006 | 0.0006 | -0.0091 | -0.0265 | -360.1496 | 17.6204 | -360.5958 | 17.8956 | -360.9035 | 18.1358 | -360.9651 | 17.5465 | -352.8814 | 18.7661 | -352.8752 | 16.7991
11:33 | 825 | 18.8585 | 192.9306 | 433.731 | 439.5775 | -21.8595 | -48.407 | 0.2556 | -0.8724 | -8.3905 | -8.2811 | -3.745 | -4.4112 | 1.3753 | -5.8317 | 0.5798 | 0.6254 | 0.9499 | 0.6852 | -132.2347 | -8.9797 | -1.8199 | -3.0234 | -11.0293 | -9.7546 | -1.9553 |  | -5.394 | -4.7843 | 4.0265 | 3.372 | 3.3559 | 0.9874 | 10.5996 | 14.0436 | 14.5855 | 10.9075 | -0.0004 | -0.003 | 0.0009 | 0.0041 | 0.0006 | -0.0009 | 0.0096 | 0.0005 | -0.0186 | -360.1804 | 17.6328 | -360.645 | 17.9448 | -360.9558 | 18.1379 | -360.9558 | 17.5342 | -352.9121 | 18.7867 | -352.9367 | 16.8381
11:33 | 826 | 18.8975 | 192.9705 | 433.6926 | 439.6726 | -21.714 | -48.4233 | 0.1981 | -0.8403 | -8.3964 | -8.2208 | -3.705 | -4.3801 | 1.3895 | -5.7959 | 0.5804 | 0.6268 | 0.9538 | 0.6867 | -132.2841 | -9.0474 | -1.8004 | -2.8965 | -11.0574 | -9.6816 | -1.8674 |  | -5.3915 | -4.8602 | 4.029 | 3.3708 | 3.3524 | 0.9879 | 10.6073 | 14.0466 | 14.6224 | 10.9424 | 0.0001 | -0.0022 | 0.0009 | 0.0042 | 0.0007 | 0.0001 | 0.0066 | -0.009 | -0.0008 | -360.0942 | 17.6143 | -360.6358 | 17.9202 | -360.9189 | 18.1399 | -360.9712 | 17.5178 | -352.8352 | 18.7682 | -352.8998 | 16.8258
11:33 | 827 | 18.8697 | 192.9923 | 433.6222 | 439.7356 | -21.8269 | -48.5764 | 0.1512 | -0.8787 | -8.3825 | -8.0944 | -3.6764 | -4.374 | 1.35 | -5.7405 | 0.5811 | 0.6266 | 0.9507 | 0.6858 | -132.2914 | -9.0477 | -1.8341 | -2.8208 | -10.9739 | -9.6774 | -1.8914 |  | -5.4389 | -4.8593 | 4.0281 | 3.375 | 3.3566 | 0.9886 | 10.6387 | 14.0601 | 14.6278 | 10.9399 | 0.0001 | -0.0026 | 0.0004 | 0.0035 | 0.0011 | -0.0005 | 0.0123 | 0.0005 | -0.0232 | -360.165 | 17.5917 | -360.5743 | 17.9202 | -360.922 | 18.1563 | -361.0174 | 17.5424 | -352.906 | 18.762 | -352.8537 | 16.8156
11:34 | 828 | 18.9176 | 193.0202 | 433.6084 | 439.6756 | -21.8498 | -48.5001 | 0.1803 | -0.9763 | -8.4791 | -8.1517 | -3.7163 | -4.3705 | 1.3108 | -5.7815 | 0.5816 | 0.6243 | 0.9526 | 0.6856 | -132.1946 | -8.9835 | -1.75 | -2.7884 | -11.0377 | -9.6809 | -1.8526 |  | -5.4239 | -4.8741 | 4.0276 | 3.3722 | 3.3572 | 0.9875 | 10.6123 | 14.0505 | 14.6332 | 10.9259 | -0.0002 | -0.0032 | 0.0009 | 0.0037 | 0.0002 | -0.0003 | -0.0034 | 0.0003 | 0.0001 | -360.1558 | 17.6245 | -360.5989 | 17.8935 | -360.922 | 18.1522 | -361.0266 | 17.5671 | -352.9275 | 18.7661 | -352.8814 | 16.7848
11:34 | 829 | 18.8538 | 193.0265 | 433.5686 | 439.7005 | -21.8402 | -48.5341 | 0.1437 | -0.9543 | -8.4365 | -8.068 | -3.5872 | -4.3701 | 1.3644 | -5.8217 | 0.5796 | 0.6306 | 0.9555 | 0.6849 | -132.1346 | -8.9629 | -1.6634 | -2.9304 | -11.0982 | -9.7791 | -1.8837 |  | -5.4938 | -4.907 | 4.0276 | 3.3736 | 3.3549 | 0.9878 | 10.6155 | 14.0256 | 14.6404 | 10.9511 | 0.0001 | -0.0027 | 0.0005 | 0.0034 | 0.0008 | -0.0005 | 0.0077 | -0.0121 | -0.0285 | -360.1527 | 17.6081 | -360.6081 | 17.9099 | -360.9189 | 18.1399 | -360.9435 | 17.5219 | -352.8844 | 18.7661 | -352.9029 | 16.8115
11:34 | 830 | 18.9377 | 193.0949 | 433.6886 | 439.6827 | -21.8377 | -48.6464 | 0.1638 | -0.9553 | -8.448 | -8.212 | -3.6163 | -4.4186 | 1.351 | -5.7941 | 0.5805 | 0.6322 | 0.9488 | 0.6849 | -132.2325 | -8.9982 | -1.8386 | -3.0568 | -11.1797 | -9.8465 | -1.9631 |  | -5.4673 | -4.8407 | 4.0277 | 3.376 | 3.3558 | 0.9874 | 10.5755 | 14.042 | 14.5926 | 10.9018 | -0.0003 | -0.0028 | 0.0008 | 0.0036 | 0.0007 | -0.0007 | 0.0126 | -0.0107 | -0.0012 | -360.0911 | 17.604 | -360.645 | 17.9613 | -360.9743 | 18.1769 | -361.0266 | 17.528 | -352.8598 | 18.7805 | -352.9367 | 16.8443
11:34 | 831 | 18.8358 | 192.9889 | 433.7007 | 439.664 | -21.8546 | -48.5135 | 0.2281 | -0.9441 | -8.3251 | -7.9558 | -3.6088 | -4.4085 | 1.3971 | -5.8302 | 0.5796 | 0.6272 | 0.9508 | 0.6853 | -132.1688 | -9.0447 | -1.8332 | -2.9686 | -11.1802 | -9.816 | -1.9879 |  | -5.4457 | -4.7914 | 4.0292 | 3.3737 | 3.3582 | 0.9871 | 10.5706 | 14.0264 | 14.5865 | 10.9129 | 0 | -0.0026 | 0.0014 | 0.0041 | 0.0005 | -0.0005 | 0.0107 | -0.0098 | -0.02 | -360.1281 | 17.5917 | -360.565 | 17.9223 | -360.9435 | 18.1563 | -360.9774 | 17.5301 | -352.8383 | 18.7518 | -352.8537 | 16.8094
11:34 | 832 | 18.8413 | 193.0011 | 433.7792 | 439.7012 | -21.8791 | -48.5114 | 0.2142 | -0.8518 | -8.4102 | -8.2305 | -3.7193 | -4.2819 | 1.4661 | -5.7664 | 0.5806 | 0.63 | 0.9512 | 0.6847 | -132.3019 | -9.1252 | -1.8311 | -3.027 | -11.0662 | -9.8908 | -1.9068 |  | -5.4326 | -4.8247 | 4.0277 | 3.3729 | 3.3611 | 0.9894 | 10.6006 | 14.0622 | 14.6516 | 10.9313 | -0.0001 | -0.0033 | 0.0007 | 0.0038 | 0.001 | -0.001 | 0.0122 | -0.0168 | 0.0153 | -360.165 | 17.6451 | -360.6327 | 17.912 | -360.9374 | 18.142 | -360.9897 | 17.5568 | -352.9398 | 18.799 | -352.9152 | 16.8115
11:34 | 833 | 18.8042 | 193.0097 | 433.6338 | 439.6099 | -21.8522 | -48.4809 | 0.1973 | -0.8554 | -8.4084 | -8.2565 | -3.628 | -4.3769 | 1.4275 | -5.6718 | 0.5801 | 0.6281 | 0.9499 | 0.6866 | -132.1889 | -9.0181 | -1.8299 | -3.0402 | -11.0757 | -9.8003 | -1.8744 |  | -5.4332 | -4.9063 | 4.0286 | 3.3723 | 3.357 | 0.9884 | 10.6017 | 14.0521 | 14.6261 | 10.9605 | 0.0001 | -0.0026 | 0.0007 | 0.0038 | 0.0008 | -0.0001 | 0.0144 | -0.0116 | -0.0027 | -360.165 | 17.6245 | -360.6296 | 17.9182 | -360.9158 | 18.1276 | -360.9681 | 17.5239 | -352.8721 | 18.7887 | -352.9091 | 16.8135
11:34 | 834 | 18.7985 | 193.0022 | 433.604 | 439.6241 | -21.8939 | -48.551 | 0.1927 | -0.8942 | -8.4316 | -8.1625 | -3.6583 | -4.3431 | 1.4526 | -5.7534 | 0.581 | 0.6334 | 0.9547 | 0.6876 | -132.1934 | -8.9683 | -1.8674 | -3.1654 | -11.0992 | -9.8526 | -2.0243 |  | -5.4386 | -4.8348 | 4.0285 | 3.375 | 3.3604 | 0.9874 | 10.6087 | 14.0532 | 14.6322 | 10.9388 | -0.0005 | -0.0028 | 0.0005 | 0.0036 | 0.001 | -0.001 | -0.0041 | -0.0057 | -0.0164 | -360.1558 | 17.602 | -360.5896 | 17.9284 | -360.9558 | 18.1645 | -360.9927 | 17.5424 | -352.9029 | 18.7723 | -352.8906 | 16.8238
11:34 | 835 | 18.8232 | 192.9092 | 433.6047 | 439.6848 | -22.0458 | -48.4922 | 0.1086 | -0.9484 | -8.4246 | -8.3233 | -3.6547 | -4.3566 | 1.3257 | -5.7492 | 0.5814 | 0.6339 | 0.9534 | 0.688 | -132.344 | -9.0697 | -1.9341 | -2.9835 | -11.1235 | -9.862 | -1.963 |  | -5.47 | -4.8914 | 4.0275 | 3.375 | 3.3533 | 0.9886 | 10.633 | 14.0369 | 14.6557 | 10.9692 | -0.0006 | -0.0029 | 0.0003 | 0.003 | 0.0006 | -0.0003 | -0.0001 | -0.0175 | -0.0056 | -360.1927 | 17.6081 | -360.605 | 17.9017 | -360.9097 | 18.1543 | -361.0204 | 17.5547 | -352.8691 | 18.7867 | -352.8783 | 16.7889
11:34 | 836 | 18.8349 | 192.9578 | 433.6929 | 439.6338 | -21.9273 | -48.5245 | 0.1634 | -0.9116 | -8.4554 | -8.401 | -3.68 | -4.3908 | 1.381 | -5.6749 | 0.5811 | 0.6314 | 0.952 | 0.6875 | -132.3577 | -9.0009 | -1.9573 | -3.1121 | -11.2105 | -9.7892 | -1.9665 |  | -5.4121 | -4.8612 | 4.0275 | 3.3716 | 3.3562 | 0.9867 | 10.6041 | 14.0483 | 14.6431 | 10.906 | 0.0001 | -0.0029 | 0.001 | 0.0036 | 0.0005 | -0.0008 | 0.0098 | -0.002 | -0.0216 | -360.1558 | 17.6184 | -360.6081 | 17.914 | -360.9312 | 18.1379 | -360.9897 | 17.5383 | -352.8967 | 18.7928 | -352.8906 | 16.8115
11:34 | 837 | 18.7952 | 192.9255 | 433.6686 | 439.5863 | -21.938 | -48.5044 | 0.0757 | -0.9483 | -8.4301 | -8.2966 | -3.6691 | -4.3216 | 1.3933 | -5.718 | 0.5803 | 0.6343 | 0.9535 | 0.6857 | -132.3512 | -8.9948 | -1.931 | -3.0312 | -11.0661 | -9.7464 | -1.8908 |  | -5.5092 | -4.9836 | 4.0266 | 3.3752 | 3.3571 | 0.9894 | 10.6008 | 14.0446 | 14.5916 | 10.9263 | 0 | -0.0033 | 0.0007 | 0.0035 | 0.0002 | -0.0007 | 0.0016 | -0.0014 | -0.0202 | -360.1373 | 17.6225 | -360.6235 | 17.9202 | -360.9404 | 18.1461 | -360.9866 | 17.5239 | -352.8383 | 18.7846 | -352.9152 | 16.8135
11:34 | 838 | 18.8112 | 193.0008 | 433.6567 | 439.6749 | -21.9564 | -48.528 | 0.0009 | -0.9674 | -8.4515 | -8.2228 | -3.6235 | -4.3962 | 1.3732 | -5.738 | 0.58 | 0.6311 | 0.9514 | 0.6875 | -132.2732 | -9.0236 | -1.9644 | -2.8869 | -11.0419 | -9.7628 | -1.9315 |  | -5.4628 | -4.9314 | 4.0274 | 3.373 | 3.3547 | 0.9893 | 10.5938 | 14.0147 | 14.626 | 10.9941 | 0.0001 | -0.0027 | 0.0004 | 0.0036 | 0.0009 | -0.0004 | 0.0173 | -0.0103 | 0.0156 | -360.1096 | 17.5937 | -360.5835 | 17.9223 | -360.9374 | 18.1543 | -360.9866 | 17.5363 | -352.8598 | 18.7723 | -352.8814 | 16.8361
11:34 | 839 | 18.8563 | 193.0644 | 433.5783 | 439.6514 | -21.8566 | -48.5045 | 0.0068 | -0.9519 | -8.3899 | -8.3072 | -3.5793 | -4.2732 | 1.442 | -5.6778 | 0.5819 | 0.6306 | 0.954 | 0.6875 | -132.1875 | -8.9644 | -1.8108 | -2.9154 | -11.0399 | -9.7506 | -1.8946 |  | -5.4294 | -4.913 | 4.0269 | 3.3735 | 3.3547 | 0.9895 | 10.5788 | 14.0283 | 14.6324 | 10.9162 | -0.0006 | -0.0033 | 0.0008 | 0.0041 | 0.0001 | -0.0011 | 0.0069 | -0.0091 | -0.0211 | -360.1558 | 17.6122 | -360.5989 | 17.9038 | -360.9066 | 18.1563 | -360.9958 | 17.5404 | -352.8783 | 18.7785 | -352.8937 | 16.8094
11:34 | 840 | 18.8795 | 193.0715 | 433.7367 | 439.6476 | -22.0039 | -48.5734 | -0.0395 | -0.9539 | -8.3857 | -8.358 | -3.6399 | -4.2139 | 1.5063 | -5.6984 | 0.5816 | 0.6309 | 0.9525 | 0.6882 | -132.2 | -8.9845 | -1.7911 | -2.9696 | -11.0345 | -9.7911 | -1.9278 |  | -5.4934 | -4.9948 | 4.0268 | 3.3726 | 3.3554 | 0.9901 | 10.5811 | 14.0365 | 14.5947 | 10.9299 | -0.0003 | -0.003 | 0.0003 | 0.0032 | 0 | -0.0007 | 0.0087 | 0.0091 | -0.0172 | -360.1558 | 17.6184 | -360.6173 | 17.9202 | -360.9527 | 18.1461 | -360.9804 | 17.5424 | -352.8937 | 18.7867 | -352.9121 | 16.8217
11:34 | 841 | 18.8238 | 193.0376 | 433.731 | 439.6402 | -21.9446 | -48.5573 | 0.0432 | -0.9215 | -8.4162 | -8.3981 | -3.6211 | -4.2594 | 1.3928 | -5.6479 | 0.5817 | 0.6322 | 0.953 | 0.6879 | -132.2543 | -8.9526 | -1.8332 | -3.0342 | -11.0943 | -9.7461 | -1.9224 |  | -5.5058 | -4.9944 | 4.0269 | 3.3746 | 3.357 | 0.9893 | 10.6144 | 14.0416 | 14.6206 | 10.9504 | 0.0002 | -0.0032 | 0.0005 | 0.0038 | 0.0007 | -0.001 | 0.0014 | -0.009 | 0.0084 | -360.1219 | 17.6102 | -360.5989 | 17.914 | -360.9158 | 18.1337 | -360.9774 | 17.5239 | -352.8537 | 18.7826 | -352.8752 | 16.8135
11:34 | 842 | 18.854 | 193.2377 | 433.777 | 439.6713 | -21.9339 | -48.5185 | 0.0196 | -0.9958 | -8.459 | -8.2812 | -3.6727 | -4.3167 | 1.3875 | -5.6203 | 0.582 | 0.6337 | 0.952 | 0.6873 | -132.2283 | -9.0122 | -1.8658 | -3.0561 | -11.0635 | -9.7826 | -1.9808 |  | -5.4751 | -4.9945 | 4.0283 | 3.3731 | 3.3545 | 0.9897 | 10.6364 | 14.0753 | 14.655 | 10.9778 | -0.0001 | -0.003 | 0.0006 | 0.0041 | 0.0003 | -0.0005 | 0.0063 | -0.0074 | -0.0223 | -360.1435 | 17.6102 | -360.6112 | 17.9264 | -360.9281 | 18.1563 | -361.0081 | 17.5527 | -352.8783 | 18.7846 | -352.9244 | 16.8381
11:34 | 843 | 18.7942 | 193.1429 | 433.7277 | 439.658 | -21.8925 | -48.5298 | 0.0165 | -0.9761 | -8.4122 | -8.2221 | -3.6988 | -4.279 | 1.3997 | -5.6327 | 0.5812 | 0.6324 | 0.9528 | 0.6879 | -132.2369 | -8.9988 | -1.9511 | -3.0575 | -11.0473 | -9.7313 | -1.9663 |  | -5.4062 | -4.8971 | 4.0265 | 3.3743 | 3.355 | 0.9889 | 10.6225 | 14.0846 | 14.6649 | 10.9753 | 0 | -0.0025 | 0.0004 | 0.0032 | 0.0005 | -0.0011 | 0.0062 | -0.0135 | -0.0333 | -360.1404 | 17.6061 | -360.605 | 17.9079 | -360.9374 | 18.1358 | -360.9466 | 17.5321 | -352.829 | 18.7641 | -352.8537 | 16.8094
11:34 | 844 | 18.8196 | 193.1629 | 433.7055 | 439.7212 | -21.9796 | -48.455 | 0.0033 | -1.0134 | -8.4328 | -8.3508 | -3.7628 | -4.3255 | 1.3483 | -5.5801 | 0.5791 | 0.6325 | 0.9522 | 0.6882 | -132.2247 | -9.0014 | -1.9503 | -2.8803 | -10.9829 | -9.6971 | -1.9324 |  | -5.4273 | -4.901 | 4.0273 | 3.3741 | 3.3569 | 0.9892 | 10.604 | 14.0661 | 14.6404 | 10.9569 | -0.0007 | -0.0029 | 0.0009 | 0.0036 | 0.0005 | -0.0004 | -0.0041 | 0.0008 | -0.0155 | -360.1373 | 17.6245 | -360.6235 | 17.9264 | -360.9435 | 18.1543 | -361.0389 | 17.5506 | -352.866 | 18.7908 | -352.9091 | 16.8299
11:34 | 845 | 18.9366 | 193.1442 | 433.793 | 439.7936 | -21.847 | -48.3323 | 0.1512 | -0.9257 | -8.4236 | -8.2156 | -3.6379 | -4.2889 | 1.4282 | -5.6706 | 0.5816 | 0.6332 | 0.9552 | 0.6881 | -132.2837 | -9.0277 | -1.9134 | -2.8613 | -10.8581 | -9.6476 | -1.9028 |  | -5.3772 | -4.9192 | 4.0268 | 3.375 | 3.3565 | 0.9903 | 10.6261 | 14.0471 | 14.6359 | 10.9396 | 0 | -0.0031 | 0.0007 | 0.0036 | 0.0003 | -0.0008 | 0.0286 | -0.0047 | 0.001 | -360.1711 | 17.6122 | -360.5866 | 17.8997 | -360.9066 | 18.1358 | -360.9804 | 17.5301 | -352.8691 | 18.7764 | -352.8783 | 16.8156
11:34 | 846 | 18.9216 | 193.2328 | 433.6989 | 439.7834 | -21.7965 | -48.2787 | 0.2273 | -0.8884 | -8.5221 | -8.3131 | -3.7468 | -4.1827 | 1.4976 | -5.6146 | 0.5806 | 0.6317 | 0.9514 | 0.6878 | -132.2748 | -9.0298 | -1.9061 | -2.8447 | -10.9175 | -9.6704 | -1.9584 |  | -5.3945 | -4.8958 | 4.0264 | 3.3776 | 3.3582 | 0.99 | 10.604 | 14.0371 | 14.6462 | 10.9684 | 0.0005 | -0.003 | 0.0008 | 0.0037 | 0.0008 | -0.0006 | -0.0006 | -0.0075 | -0.0116 | -360.1496 | 17.6102 | -360.6358 | 17.9284 | -360.9743 | 18.1645 | -361.0051 | 17.5404 | -352.866 | 18.7867 | -352.8906 | 16.832
11:34 | 847 | 18.9014 | 193.1113 | 433.7999 | 439.7824 | -21.8463 | -48.3488 | 0.1701 | -0.8127 | -8.4478 | -8.268 | -3.775 | -4.2843 | 1.3372 | -5.6332 | 0.5799 | 0.6338 | 0.9521 | 0.6878 | -132.281 | -8.9742 | -1.9419 | -2.8694 | -10.9135 | -9.5699 | -1.9007 |  | -5.4308 | -4.9373 | 4.026 | 3.3725 | 3.3584 | 0.9889 | 10.5902 | 14.0289 | 14.6424 | 10.9377 | -0.0002 | -0.0027 | 0.0013 | 0.0045 | 0.0005 | -0.0004 | 0.0073 | -0.0114 | -0.0082 | -360.1311 | 17.5855 | -360.5927 | 17.9202 | -360.9343 | 18.1481 | -360.9804 | 17.5239 | -352.866 | 18.7723 | -352.8537 | 16.8115
11:34 | 848 | 18.9279 | 193.1362 | 433.7206 | 439.7708 | -21.85 | -48.2726 | 0.2019 | -0.8089 | -8.4717 | -8.2221 | -3.7293 | -4.352 | 1.4652 | -5.6458 | 0.58 | 0.6346 | 0.9508 | 0.6875 | -132.306 | -9.0444 | -1.9958 | -2.8 | -10.9178 | -9.6759 | -1.9132 |  | -5.4168 | -4.9553 | 4.0266 | 3.3711 | 3.3567 | 0.9901 | 10.5683 | 14.0065 | 14.6059 | 10.9342 | -0.0003 | -0.0028 | 0.0002 | 0.0035 | 0.0006 | -0.001 | 0.0115 | -0.0213 | 0.0051 | -360.1096 | 17.6225 | -360.6327 | 17.9161 | -360.922 | 18.1604 | -361.0081 | 17.5527 | -352.8844 | 18.799 | -352.9214 | 16.8197
11:34 | 849 | 18.8964 | 193.1348 | 433.8219 | 439.712 | -21.8211 | -48.4185 | 0.2582 | -0.8182 | -8.3973 | -8.2916 | -3.6849 | -4.2163 | 1.5177 | -5.5573 | 0.5807 | 0.6346 | 0.9518 | 0.6899 | -132.2634 | -8.9785 | -1.9737 | -2.8102 | -10.9473 | -9.7235 | -1.9125 |  | -5.4362 | -4.9499 | 4.0273 | 3.3744 | 3.3578 | 0.9898 | 10.5903 | 14.0228 | 14.6288 | 10.9212 | -0.0002 | -0.0029 | 0.0006 | 0.0039 | 0.0005 | -0.0007 | 0.0127 | -0.0122 | -0.001 | -360.1465 | 17.6225 | -360.6235 | 17.914 | -360.9343 | 18.1255 | -360.9404 | 17.5239 | -352.866 | 18.7867 | -352.8937 | 16.8156
11:34 | 850 | 18.8566 | 193.061 | 433.8611 | 439.7137 | -21.8769 | -48.329 | 0.2381 | -0.8334 | -8.418 | -8.2212 | -3.7349 | -4.2462 | 1.4141 | -5.6501 | 0.5806 | 0.6335 | 0.9538 | 0.6892 | -132.194 | -8.9159 | -1.9683 | -3.0443 | -10.8256 | -9.7044 | -1.8681 |  | -5.4199 | -4.847 | 4.0283 | 3.3722 | 3.3566 | 0.9904 | 10.6132 | 14.0926 | 14.6608 | 10.9663 | 0.0003 | -0.003 | 0.001 | 0.0042 | 0.001 | -0.0007 | 0.0014 | 0.0098 | -0.0191 | -360.1373 | 17.6266 | -360.6543 | 17.9264 | -360.9466 | 18.1563 | -360.9897 | 17.5363 | -352.8752 | 18.7805 | -352.9275 | 16.8381
11:34 | 851 | 18.915 | 193.0446 | 433.8072 | 439.7542 | -21.814 | -48.3309 | 0.25 | -0.9183 | -8.4582 | -8.3655 | -3.8227 | -4.2421 | 1.4259 | -5.5856 | 0.5806 | 0.6312 | 0.9512 | 0.6887 | -132.1459 | -8.9208 | -1.8454 | -2.96 | -10.8643 | -9.6915 | -1.9231 |  | -5.4405 | -4.8477 | 4.0274 | 3.3719 | 3.3558 | 0.9893 | 10.5879 | 14.0264 | 14.5981 | 10.936 | -0.0003 | -0.0033 | 0.0006 | 0.0036 | 0.001 | 0.0001 | 0.0177 | 0.0027 | -0.0043 | -360.1219 | 17.5876 | -360.5404 | 17.8935 | -360.9435 | 18.1522 | -360.9835 | 17.5424 | -352.8721 | 18.7477 | -352.8321 | 16.8115
11:34 | 852 | 18.944 | 193.0164 | 433.849 | 439.7616 | -21.8867 | -48.3311 | 0.2529 | -0.9584 | -8.393 | -8.3512 | -3.6675 | -4.3118 | 1.4259 | -5.6946 | 0.5801 | 0.6298 | 0.9507 | 0.6883 | -132.1703 | -8.8781 | -1.8241 | -2.9704 | -10.8527 | -9.7927 | -1.8639 |  | -5.4623 | -4.8688 | 4.0268 | 3.3729 | 3.3537 | 0.9902 | 10.6005 | 14.0798 | 14.6189 | 10.9305 | -0.0005 | -0.0023 | 0.0008 | 0.0037 | 0.0007 | -0.0009 | 0.0144 | 0.0001 | -0.0255 | -360.2019 | 17.6307 | -360.6143 | 17.914 | -360.9158 | 18.1584 | -361.0266 | 17.5547 | -352.8906 | 18.7949 | -352.8906 | 16.8094
11:34 | 853 | 18.9586 | 193.0655 | 433.9809 | 439.7482 | -21.8314 | -48.396 | 0.2314 | -0.9171 | -8.4188 | -8.2251 | -3.5785 | -4.3157 | 1.4246 | -5.8024 | 0.5807 | 0.6327 | 0.9522 | 0.6891 | -132.2381 | -8.945 | -1.917 | -3.0273 | -10.8479 | -9.7343 | -1.8247 |  | -5.4425 | -4.8381 | 4.0261 | 3.3742 | 3.3583 | 0.99 | 10.6272 | 14.0716 | 14.6557 | 10.9518 | -0.0003 | -0.0029 | 0.001 | 0.0037 | 0.0004 | -0.0004 | 0.0148 | -0.0077 | -0.0108 | -360.1681 | 17.6143 | -360.6081 | 17.9182 | -360.9158 | 18.1317 | -360.9589 | 17.528 | -352.8537 | 18.7805 | -352.906 | 16.8156
11:34 | 854 | 18.8881 | 192.9859 | 433.821 | 439.7248 | -21.8374 | -48.3665 | 0.2076 | -0.8801 | -8.3247 | -8.2196 | -3.5102 | -4.3044 | 1.4715 | -5.7537 | 0.5811 | 0.6296 | 0.9529 | 0.6897 | -132.3254 | -8.938 | -1.9692 | -3.0547 | -10.9358 | -9.8393 | -1.8981 |  | -5.4153 | -4.7246 | 4.0262 | 3.373 | 3.356 | 0.9901 | 10.5902 | 14.0692 | 14.6182 | 10.9208 | 0 | -0.0032 | 0.0004 | 0.0031 | 0.0008 | -0.0005 | -0.0069 | -0.0007 | -0.0261 | -360.0819 | 17.6081 | -360.645 | 17.9387 | -360.9774 | 18.1666 | -360.9866 | 17.5383 | -352.829 | 18.7723 | -352.9121 | 16.8402
11:34 | 855 | 18.8694 | 192.9658 | 433.8398 | 439.7745 | -21.8647 | -48.4184 | 0.1736 | -0.962 | -8.4038 | -8.2775 | -3.5807 | -4.2514 | 1.4101 | -5.7082 | 0.5811 | 0.6299 | 0.9529 | 0.6908 | -132.2291 | -8.9443 | -1.9907 | -3.1515 | -11.008 | -9.7998 | -1.9372 |  | -5.375 | -4.8285 | 4.0261 | 3.3703 | 3.3587 | 0.9886 | 10.6029 | 14.0763 | 14.6785 | 10.9504 | 0.0002 | -0.0029 | 0.0005 | 0.004 | 0.0004 | -0.0005 | 0.0248 | -0.0042 | -0.0249 | -360.1127 | 17.5917 | -360.5773 | 17.9305 | -360.9558 | 18.1543 | -360.9835 | 17.5239 | -352.8444 | 18.7641 | -352.8629 | 16.8217
11:34 | 856 | 18.8677 | 192.9777 | 433.8887 | 439.8139 | -21.8765 | -48.4539 | 0.1583 | -0.9264 | -8.3776 | -8.2149 | -3.5684 | -4.2591 | 1.4236 | -5.6218 | 0.581 | 0.6309 | 0.9516 | 0.6911 | -132.1581 | -8.9074 | -1.9905 | -3.1155 | -10.9309 | -9.8104 | -1.9358 |  | -5.4541 | -4.8343 | 4.0266 | 3.3709 | 3.3595 | 0.9914 | 10.6134 | 14.0402 | 14.6519 | 10.9385 | -0.0003 | -0.0026 | 0.0002 | 0.0034 | 0.0004 | -0.0005 | 0.0073 | -0.0209 | -0.0177 | -360.1527 | 17.6245 | -360.5989 | 17.8976 | -360.9127 | 18.1461 | -360.9958 | 17.5568 | -352.8844 | 18.7826 | -352.906 | 16.8094
11:34 | 857 | 18.9248 | 192.9692 | 433.77 | 439.8544 | -21.9465 | -48.564 | 0.124 | -0.9586 | -8.3622 | -8.2705 | -3.5775 | -4.2935 | 1.3622 | -5.7451 | 0.5814 | 0.6323 | 0.9536 | 0.6904 | -132.1735 | -8.9403 | -1.9725 | -3.0991 | -11.1255 | -9.966 | -1.9604 |  | -5.3791 | -4.8228 | 4.0263 | 3.3707 | 3.3596 | 0.9903 | 10.5949 | 14.0218 | 14.6284 | 10.9313 | -0.0005 | -0.003 | 0.0005 | 0.0035 | 0.0007 | -0.0012 | 0.0129 | -0.0088 | 0.0003 | -360.1865 | 17.6451 | -360.6543 | 17.9202 | -360.922 | 18.1255 | -360.9558 | 17.528 | -352.8691 | 18.8134 | -352.9214 | 16.8176
11:34 | 858 | 18.9055 | 192.9668 | 433.9031 | 439.818 | -21.9104 | -48.3828 | 0.0759 | -0.9163 | -8.4476 | -8.1615 | -3.5532 | -4.2364 | 1.4121 | -5.7374 | 0.5793 | 0.6307 | 0.952 | 0.6884 | -132.0826 | -8.9191 | -1.9437 | -2.9526 | -11.1344 | -9.8147 | -1.976 |  | -5.4 | -4.8408 | 4.0265 | 3.3704 | 3.3573 | 0.9912 | 10.6006 | 14.0622 | 14.6805 | 10.9602 | 0.0002 | -0.0029 | 0.0003 | 0.0041 | 0.0004 | -0.0006 | 0.0045 | -0.0076 | -0.0031 | -360.1158 | 17.6122 | -360.6389 | 17.9325 | -360.9158 | 18.1296 | -360.9681 | 17.526 | -352.8321 | 18.7764 | -352.9183 | 16.8443
11:34 | 859 | 18.8866 | 192.9013 | 433.7876 | 439.7921 | -21.8166 | -48.3355 | 0.2084 | -0.8369 | -8.3908 | -8.2833 | -3.5749 | -4.238 | 1.3595 | -5.8439 | 0.5796 | 0.6289 | 0.9522 | 0.6893 | -132.1097 | -8.886 | -1.9323 | -2.9128 | -11.0603 | -9.7529 | -1.8969 |  | -5.4192 | -4.7136 | 4.0245 | 3.3732 | 3.3577 | 0.9904 | 10.6052 | 14.0727 | 14.6397 | 10.924 | -0.0003 | -0.0031 | 0.0008 | 0.0035 | 0.001 | -0.0007 | 0.0118 | -0.0005 | -0.0185 | -360.1681 | 17.5999 | -360.5927 | 17.9079 | -360.9466 | 18.1707 | -360.9804 | 17.5383 | -352.8691 | 18.762 | -352.8383 | 16.8299
11:34 | 860 | 18.928 | 193.1079 | 433.8746 | 439.7911 | -21.8271 | -48.4758 | 0.0966 | -0.9099 | -8.3972 | -8.2619 | -3.6205 | -4.1762 | 1.4707 | -5.7396 | 0.5798 | 0.6291 | 0.9515 | 0.6883 | -132.1714 | -8.9772 | -1.953 | -3.0878 | -11.0844 | -9.8619 | -1.8853 |  | -5.419 | -4.7605 | 4.0263 | 3.3714 | 3.3542 | 0.989 | 10.6192 | 14.0402 | 14.6577 | 10.9616 | -0.0004 | -0.0032 | 0.0007 | 0.0037 | 0.0007 | -0.0005 | -0.0061 | 0.0024 | -0.0099 | -360.1619 | 17.5999 | -360.5619 | 17.8791 | -360.9035 | 18.1563 | -361.0143 | 17.5568 | -352.8875 | 18.7579 | -352.8783 | 16.793
11:34 | 861 | 18.85 | 193.0492 | 433.8321 | 439.6717 | -21.7685 | -48.3933 | 0.1629 | -0.9702 | -8.4116 | -8.1515 | -3.5766 | -4.179 | 1.3725 | -5.7093 | 0.5799 | 0.6324 | 0.9504 | 0.6892 | -132.1832 | -8.9123 | -1.897 | -3.0469 | -11.0807 | -9.8691 | -1.9407 |  | -5.4183 | -4.7389 | 4.0241 | 3.3694 | 3.3554 | 0.9873 | 10.6169 | 14.0726 | 14.6502 | 10.9591 | -0.0009 | -0.003 | 0.0007 | 0.0038 | 0.0009 | -0.0003 | 0.0064 | -0.006 | 0.0057 | -360.1927 | 17.6328 | -360.645 | 17.9223 | -360.922 | 18.1543 | -360.9743 | 17.5424 | -352.8967 | 18.7908 | -352.9152 | 16.8176
11:34 | 862 | 18.87 | 193.0645 | 433.8117 | 439.7967 | -21.7928 | -48.3423 | 0.1949 | -1.0193 | -8.4705 | -8.2875 | -3.5935 | -4.1601 | 1.4207 | -5.7396 | 0.58 | 0.6276 | 0.9509 | 0.6882 | -132.141 | -9.0031 | -1.9415 | -2.8983 | -11.0051 | -9.8658 | -1.8648 |  | -5.4973 | -4.841 | 4.0247 | 3.3748 | 3.3567 | 0.9907 | 10.6156 | 14.1122 | 14.6625 | 10.9572 | -0.0001 | -0.0027 | 0.0006 | 0.0035 | 0.0006 | -0.0004 | 0.0029 | -0.0043 | -0.0213 | -360.1188 | 17.5835 | -360.6112 | 17.9469 | -360.9651 | 18.142 | -360.9466 | 17.5075 | -352.8229 | 18.7661 | -352.9152 | 16.8484
11:34 | 863 | 18.9331 | 192.9669 | 433.8154 | 439.7917 | -21.8713 | -48.4246 | 0.1576 | -0.9405 | -8.3527 | -8.0928 | -3.5855 | -4.155 | 1.3932 | -5.6888 | 0.5803 | 0.6308 | 0.9496 | 0.6863 | -132.1701 | -8.9642 | -1.9701 | -2.8624 | -11.0589 | -9.8673 | -1.9146 |  | -5.5198 | -4.8132 | 4.0262 | 3.3734 | 3.353 | 0.9894 | 10.6053 | 14.0609 | 14.6202 | 10.9479 | 0 | -0.0036 | 0.0006 | 0.0037 | 0.0005 | -0.0002 | 0.0043 | -0.0091 | -0.0179 | -360.1311 | 17.5978 | -360.605 | 17.9407 | -360.9835 | 18.1769 | -360.9897 | 17.5383 | -352.8506 | 18.7826 | -352.9121 | 16.8423
11:34 | 864 | 18.9258 | 193.0561 | 433.826 | 439.8584 | -21.8409 | -48.5094 | 0.0707 | -0.9642 | -8.3833 | -8.2824 | -3.5325 | -4.1432 | 1.3974 | -5.6966 | 0.5801 | 0.6286 | 0.9508 | 0.6874 | -132.2058 | -9.0274 | -2.0471 | -2.8631 | -11.0911 | -9.8485 | -1.9015 |  | -5.4672 | -4.8059 | 4.0254 | 3.376 | 3.3581 | 0.9913 | 10.6087 | 14.0646 | 14.6543 | 10.9392 | 0 | -0.003 | 0.0006 | 0.0033 | 0.001 | -0.0005 | 0.0179 | -0.0018 | -0.0122 | -360.1588 | 17.604 | -360.5743 | 17.9017 | -360.882 | 18.1214 | -361.002 | 17.5465 | -352.8844 | 18.7785 | -352.8444 | 16.795
11:34 | 865 | 19.0429 | 193.204 | 433.8718 | 439.8052 | -21.8927 | -48.4101 | 0.0812 | -1.0272 | -8.3871 | -8.245 | -3.6023 | -4.2096 | 1.4094 | -5.7384 | 0.5792 | 0.6319 | 0.9504 | 0.6889 | -132.2432 | -8.981 | -2.008 | -2.8155 | -11.0048 | -9.956 | -1.941 |  | -5.448 | -4.8564 | 4.025 | 3.3728 | 3.357 | 0.9902 | 10.6272 | 14.0427 | 14.6788 | 10.923 | -0.0003 | -0.0028 | 0.0006 | 0.0039 | 0.0003 | -0.0005 | 0.0003 | 0.0041 | 0.0025 | -360.1988 | 17.6533 | -360.6604 | 17.9387 | -360.9281 | 18.1194 | -360.9804 | 17.5506 | -352.9244 | 18.8216 | -352.9675 | 16.8279
11:34 | 866 | 18.9944 | 193.1355 | 433.9307 | 439.8897 | -21.8284 | -48.362 | 0.1704 | -0.9723 | -8.4607 | -8.1603 | -3.6356 | -4.2269 | 1.415 | -5.7153 | 0.5804 | 0.6353 | 0.9552 | 0.6894 | -132.2534 | -8.9626 | -1.8729 | -2.8072 | -11.0298 | -9.8047 | -1.8896 |  | -5.4649 | -4.7999 | 4.0253 | 3.3723 | 3.356 | 0.9912 | 10.6214 | 14.037 | 14.6336 | 10.963 | -0.0002 | -0.0028 | 0.0009 | 0.0039 | 0.0013 | -0.0005 | 0.0156 | -0.0167 | -0.0074 | -360.1281 | 17.6122 | -360.6173 | 17.9325 | -360.9251 | 18.1214 | -360.9435 | 17.5219 | -352.8383 | 18.7785 | -352.8814 | 16.8279
11:34 | 867 | 19.027 | 193.1398 | 434.0737 | 439.877 | -21.8808 | -48.4123 | 0.0608 | -0.9389 | -8.4303 | -8.2476 | -3.5461 | -4.2192 | 1.41 | -5.7491 | 0.5802 | 0.6325 | 0.9555 | 0.6882 | -132.1891 | -8.9509 | -1.9654 | -2.847 | -10.9833 | -9.7388 | -1.9035 |  | -5.4936 | -4.8872 | 4.0259 | 3.3727 | 3.3553 | 0.993 | 10.619 | 14.0523 | 14.6387 | 10.9716 | 0.0002 | -0.0029 | 0.0008 | 0.004 | 0.0003 | -0.0008 | 0.0088 | -0.0105 | 0.0028 | -360.1681 | 17.5937 | -360.5743 | 17.9325 | -360.9743 | 18.1769 | -361.0297 | 17.5506 | -352.8844 | 18.7764 | -352.8875 | 16.8279
11:34 | 868 | 19.0405 | 193.1813 | 433.9536 | 439.8662 | -21.9087 | -48.4297 | 0.0799 | -0.9466 | -8.4062 | -8.0963 | -3.5574 | -4.1553 | 1.3206 | -5.6856 | 0.5802 | 0.6322 | 0.9467 | 0.6868 | -132.1869 | -8.8989 | -1.9903 | -2.9584 | -10.9711 | -9.7514 | -1.8524 |  | -5.4686 | -4.7483 | 4.0264 | 3.3732 | 3.3575 | 0.9914 | 10.6226 | 14.0611 | 14.6965 | 10.9706 | -0.0001 | -0.0032 | 0.0002 | 0.0037 | 0.0007 | -0.0008 | 0.0058 | 0.0004 | -0.0148 | -360.1465 | 17.5917 | -360.5527 | 17.8833 | -360.9004 | 18.1522 | -360.9897 | 17.5568 | -352.8783 | 18.76 | -352.8229 | 16.7807
11:34 | 869 | 18.9818 | 193.0466 | 433.8359 | 439.7114 | -21.9301 | -48.5179 | 0.0559 | -0.9621 | -8.3216 | -7.9091 | -3.5569 | -4.1783 | 1.3556 | -5.7649 | 0.5798 | 0.6362 | 0.9506 | 0.6866 | -132.223 | -8.9114 | -1.8403 | -2.8017 | -10.926 | -9.7779 | -1.8066 |  | -5.4682 | -4.8097 | 4.026 | 3.375 | 3.3569 | 0.9923 | 10.6097 | 14.0545 | 14.6694 | 10.9742 | -0.0002 | -0.0029 | 0.001 | 0.0038 | 0.0003 | -0.0004 | 0.0085 | 0.0056 | 0.005 | -360.1927 | 17.6245 | -360.6358 | 17.9182 | -360.9066 | 18.1502 | -361.0143 | 17.5465 | -352.9183 | 18.8031 | -352.9244 | 16.834
11:34 | 870 | 18.9249 | 193.0282 | 433.8705 | 439.7359 | -22.0301 | -48.5489 | -0.0296 | -0.9386 | -8.43 | -8.2172 | -3.587 | -4.1977 | 1.4487 | -5.6622 | 0.5789 | 0.6346 | 0.9504 | 0.6868 | -132.2526 | -8.973 | -1.8736 | -2.817 | -10.9625 | -9.7534 | -1.8517 |  | -5.5105 | -4.8036 | 4.0275 | 3.375 | 3.3557 | 0.9929 | 10.6353 | 14.0682 | 14.6642 | 10.9482 | -0.0004 | -0.0027 | 0.0004 | 0.003 | 0.0009 | -0.0005 | 0.0066 | -0.0043 | 0.0067 | -360.0696 | 17.5978 | -360.6296 | 17.9387 | -360.9589 | 18.1543 | -360.9466 | 17.5075 | -352.8444 | 18.7785 | -352.9029 | 16.8361
11:34 | 871 | 18.9875 | 193.0594 | 433.8323 | 439.7967 | -21.9873 | -48.521 | 0.0451 | -0.9663 | -8.3852 | -8.181 | -3.5448 | -4.1778 | 1.3781 | -5.7541 | 0.5815 | 0.6325 | 0.9494 | 0.6865 | -132.3631 | -8.9767 | -1.9171 | -2.8702 | -10.9854 | -9.7186 | -1.8413 |  | -5.4422 | -4.7985 | 4.0262 | 3.3734 | 3.3582 | 0.9923 | 10.6019 | 14.0691 | 14.6519 | 10.9616 | -0.0002 | -0.0031 | 0.0006 | 0.0037 | 0.0009 | -0.0005 | 0.026 | -0.0169 | -0.0033 | -360.1127 | 17.6102 | -360.6081 | 17.949 | -360.9743 | 18.1912 | -360.962 | 17.5363 | -352.8721 | 18.7785 | -352.8937 | 16.8423
11:34 | 872 | 18.9873 | 193.056 | 433.922 | 439.8627 | -21.8873 | -48.5315 | -0.0128 | -0.9415 | -8.4241 | -8.0839 | -3.4924 | -4.1823 | 1.4373 | -5.6217 | 0.5805 | 0.6354 | 0.9498 | 0.6882 | -132.3252 | -9.0573 | -1.8823 | -2.9411 | -10.9606 | -9.848 | -1.8668 |  | -5.4724 | -4.8583 | 4.0262 | 3.376 | 3.3577 | 0.9922 | 10.5995 | 14.0437 | 14.5981 | 10.9418 | 0.0001 | -0.0032 | 0.0009 | 0.0038 | 0.0004 | -0.0005 | 0.0086 | 0.0052 | -0.0252 | -360.1865 | 17.6061 | -360.5743 | 17.9099 | -360.8943 | 18.1728 | -361.002 | 17.5465 | -352.8783 | 18.7661 | -352.8567 | 16.793
11:34 | 873 | 18.9314 | 192.9973 | 433.8536 | 439.7676 | -21.9804 | -48.523 | 0.0335 | -0.9303 | -8.3786 | -8.1551 | -3.5277 | -4.1812 | 1.4865 | -5.7929 | 0.5818 | 0.6359 | 0.9513 | 0.6884 | -132.261 | -8.9143 | -1.8347 | -2.8988 | -10.9207 | -9.791 | -1.8678 |  | -5.4272 | -4.8652 | 4.0251 | 3.3733 | 3.3569 | 0.99 | 10.5731 | 14.0571 | 14.5967 | 10.9281 | -0.0002 | -0.0031 | 0.0005 | 0.0036 | 0.0004 | -0.0012 | -0.0108 | -0.0232 | -0.0014 | -360.1958 | 17.6451 | -360.6512 | 17.9264 | -360.9004 | 18.1461 | -360.9989 | 17.5568 | -352.9214 | 18.8134 | -352.9491 | 16.8176
11:34 | 874 | 18.9004 | 193.0744 | 433.9212 | 439.7731 | -21.9939 | -48.4292 | 0.0594 | -0.8745 | -8.2246 | -8.2376 | -3.5969 | -4.1649 | 1.4412 | -5.7749 | 0.5805 | 0.6342 | 0.9514 | 0.687 | -132.2407 | -8.7824 | -1.8294 | -2.9553 | -10.8731 | -9.8137 | -1.8373 |  | -5.4199 | -4.8745 | 4.0263 | 3.3729 | 3.3556 | 0.9938 | 10.5879 | 14.0554 | 14.6397 | 10.9356 | -0.0001 | -0.0025 | 0.0003 | 0.0037 | 0.0007 | 0 | 0.0161 | -0.0156 | -0.0019 | -360.1588 | 17.6225 | -360.6266 | 17.9243 | -360.9312 | 18.1481 | -360.9251 | 17.526 | -352.8721 | 18.7908 | -352.8967 | 16.8176
11:34 | 875 | 18.9311 | 193.0096 | 434.0079 | 439.7784 | -21.9548 | -48.3457 | 0.0798 | -0.9506 | -8.3953 | -8.2572 | -3.5937 | -4.1695 | 1.4448 | -5.7677 | 0.5805 | 0.6375 | 0.9526 | 0.6886 | -132.2655 | -8.918 | -1.8898 | -2.8841 | -10.7994 | -9.7311 | -1.8915 |  | -5.3913 | -4.7798 | 4.0273 | 3.3752 | 3.3571 | 0.9932 | 10.6259 | 14.1055 | 14.6748 | 10.9669 | -0.0002 | -0.0029 | 0.0009 | 0.004 | 0.0009 | -0.0009 | -0.0077 | -0.0022 | -0.0118 | -360.1465 | 17.602 | -360.6081 | 17.9387 | -360.9558 | 18.1953 | -361.0143 | 17.526 | -352.8629 | 18.7764 | -352.8937 | 16.8443
11:34 | 876 | 18.9456 | 192.9533 | 433.9016 | 439.7243 | -21.9768 | -48.4511 | 0.022 | -0.9526 | -8.3967 | -8.3138 | -3.627 | -4.1479 | 1.3947 | -5.6588 | 0.5804 | 0.6339 | 0.9498 | 0.6867 | -132.2321 | -8.8326 | -1.8687 | -3.0216 | -10.9456 | -9.7226 | -1.8909 |  | -5.4008 | -4.8073 | 4.0244 | 3.3733 | 3.3589 | 0.9908 | 10.6019 | 14.0633 | 14.6635 | 10.9327 | 0 | -0.0031 | 0.0003 | 0.0033 | 0.0002 | -0.0006 | 0.006 | -0.0128 | 0.0073 | -360.125 | 17.5794 | -360.5681 | 17.9099 | -360.9158 | 18.1933 | -361.0451 | 17.5342 | -352.8629 | 18.7559 | -352.8414 | 16.8053
11:34 | 877 | 18.9795 | 193.0037 | 433.974 | 439.7955 | -21.9371 | -48.4049 | 0.1056 | -0.995 | -8.3569 | -8.2567 | -3.5733 | -4.1517 | 1.4589 | -5.7223 | 0.5801 | 0.6333 | 0.9498 | 0.6877 | -132.2129 | -8.8717 | -1.8688 | -3.0848 | -10.977 | -9.7991 | -1.9021 |  | -5.427 | -4.8519 | 4.0246 | 3.3767 | 3.3524 | 0.9918 | 10.6225 | 14.096 | 14.6581 | 10.9872 | 0 | -0.003 | 0.0009 | 0.0039 | 0.0009 | -0.0005 | -0.0016 | -0.0007 | -0.0003 | -360.1558 | 17.6204 | -360.5958 | 17.912 | -360.8912 | 18.1666 | -360.9989 | 17.5424 | -352.8998 | 18.7805 | -352.8906 | 16.8115
11:34 | 878 | 19.0454 | 193.1198 | 433.9018 | 439.9436 | -21.9811 | -48.4261 | 0.0083 | -0.9796 | -8.441 | -8.1522 | -3.6376 | -4.2124 | 1.4432 | -5.8129 | 0.5808 | 0.6349 | 0.9473 | 0.6881 | -132.1902 | -8.884 | -1.8156 | -2.9564 | -10.9705 | -9.8012 | -1.954 |  | -5.3574 | -4.766 | 4.0258 | 3.374 | 3.3533 | 0.9911 | 10.6296 | 14.1085 | 14.6458 | 10.9602 | -0.0005 | -0.0026 | 0.0002 | 0.0031 | 0.0001 | -0.0009 | -0.0036 | -0.0215 | -0.0099 | -360.1588 | 17.6184 | -360.6604 | 17.949 | -360.9651 | 18.1502 | -360.922 | 17.5096 | -352.8752 | 18.7928 | -352.9214 | 16.8423
11:34 | 879 | 19.0424 | 193.1156 | 433.9088 | 439.8975 | -21.9683 | -48.3382 | 0.0601 | -0.9393 | -8.4395 | -8.2995 | -3.6321 | -4.162 | 1.4776 | -5.7076 | 0.5809 | 0.6332 | 0.9481 | 0.6872 | -132.1985 | -8.7614 | -1.7491 | -2.8908 | -10.9875 | -9.7416 | -1.9265 |  | -5.3989 | -4.8149 | 4.0252 | 3.3749 | 3.352 | 0.9933 | 10.6122 | 14.0682 | 14.6816 | 10.9598 | -0.0004 | -0.0028 | 0.001 | 0.0042 | 0.001 | -0.0003 | 0.0135 | 0.0089 | 0.0066 | -360.1188 | 17.6122 | -360.6235 | 17.9387 | -360.9374 | 18.183 | -360.9866 | 17.5013 | -352.8506 | 18.7805 | -352.8937 | 16.8381
11:34 | 880 | 18.9989 | 193.022 | 433.9287 | 439.8343 | -21.9644 | -48.4426 | 0.036 | -0.841 | -8.3524 | -8.1213 | -3.5846 | -4.1606 | 1.438 | -5.7696 | 0.5809 | 0.6357 | 0.9489 | 0.6878 | -132.1179 | -8.8464 | -1.76 | -2.9543 | -11.0209 | -9.7226 | -1.9566 |  | -5.3762 | -4.7976 | 4.0252 | 3.3778 | 3.3573 | 0.9922 | 10.5926 | 14.0308 | 14.6073 | 10.9295 | -0.0007 | -0.0033 | 0.0008 | 0.0038 | 0.0005 | -0.0009 | 0.0072 | 0.0027 | -0.0233 | -360.1158 | 17.6061 | -360.5835 | 17.912 | -360.9189 | 18.1728 | -361.0081 | 17.5424 | -352.866 | 18.7723 | -352.8444 | 16.8135
11:34 | 881 | 18.9177 | 193.064 | 433.9416 | 439.8871 | -22.0298 | -48.6072 | -0.0226 | -0.9049 | -8.3061 | -8.2125 | -3.5017 | -4.1921 | 1.4505 | -5.6638 | 0.5808 | 0.6341 | 0.9502 | 0.6878 | -132.1486 | -8.788 | -1.7747 | -2.8645 | -11.0783 | -9.7677 | -1.8995 |  | -5.3918 | -4.6779 | 4.0256 | 3.376 | 3.357 | 0.9919 | 10.5984 | 14.0424 | 14.642 | 10.9642 | 0.0001 | -0.0032 | 0.0003 | 0.0033 | 0.0003 | -0.0005 | 0.0002 | -0.0144 | -0.0044 | -360.1711 | 17.6286 | -360.6112 | 17.9058 | -360.882 | 18.1502 | -360.9989 | 17.5404 | -352.9275 | 18.8052 | -352.9214 | 16.8053
11:34 | 882 | 18.856 | 192.9958 | 433.9127 | 439.838 | -21.9414 | -48.5113 | 0.0157 | -0.8826 | -8.3193 | -8.1441 | -3.5592 | -4.2546 | 1.4081 | -5.7465 | 0.58 | 0.6319 | 0.9495 | 0.6865 | -132.1425 | -8.6858 | -1.7891 | -2.9397 | -11.0064 | -9.7867 | -1.9287 |  | -5.3957 | -4.7179 | 4.0273 | 3.3742 | 3.3563 | 0.9929 | 10.5778 | 14.027 | 14.6011 | 10.9155 | -0.0005 | -0.0035 | 0.0005 | 0.0039 | 0.0005 | -0.001 | -0.0028 | -0.0011 | -0.002 | -360.1773 | 17.6266 | -360.6235 | 17.9182 | -360.9404 | 18.1604 | -360.9435 | 17.5239 | -352.8814 | 18.7908 | -352.8721 | 16.8156
11:34 | 883 | 18.9524 | 192.9888 | 433.9221 | 439.855 | -22.0196 | -48.5266 | 0.0158 | -0.9186 | -8.3337 | -8.1206 | -3.5463 | -4.2529 | 1.4689 | -5.7809 | 0.579 | 0.6334 | 0.9503 | 0.6875 | -132.1861 | -8.7814 | -1.7729 | -2.9586 | -10.8916 | -9.7138 | -1.9109 |  | -5.4176 | -4.7909 | 4.0251 | 3.3749 | 3.3561 | 0.9924 | 10.6295 | 14.0741 | 14.7058 | 10.9767 | -0.0002 | -0.0026 | 0.0009 | 0.0041 | 0.0003 | -0.0004 | 0.0087 | 0.0001 | -0.0214 | -360.0881 | 17.5917 | -360.5989 | 17.9161 | -360.9281 | 18.183 | -360.9774 | 17.5096 | -352.8567 | 18.7805 | -352.8814 | 16.834
11:34 | 884 | 18.8677 | 193.0203 | 433.8573 | 439.8805 | -22.0704 | -48.4616 | 0.0102 | -0.9285 | -8.406 | -8.2318 | -3.5563 | -4.2726 | 1.4263 | -5.6624 | 0.5792 | 0.6336 | 0.9517 | 0.6884 | -132.1793 | -8.8527 | -1.7779 | -3.0323 | -11.0434 | -9.7146 | -1.9154 |  | -5.4446 | -4.698 | 4.0258 | 3.3744 | 3.3623 | 0.9922 | 10.6515 | 14.0787 | 14.6928 | 10.9525 | -0.0002 | -0.0029 | 0.0006 | 0.0039 | 0.0008 | -0.0006 | -0.0068 | 0.0011 | -0.0258 | -360.1435 | 17.5876 | -360.5958 | 17.9161 | -360.9251 | 18.1953 | -361.0481 | 17.5404 | -352.8598 | 18.7723 | -352.8567 | 16.8197
11:34 | 885 | 18.975 | 193.0709 | 433.988 | 439.8873 | -22.0561 | -48.6045 | -0.0175 | -0.9448 | -8.3282 | -8.1554 | -3.5026 | -4.2012 | 1.4869 | -5.6593 | 0.5813 | 0.631 | 0.9515 | 0.6875 | -132.3108 | -8.7782 | -1.8203 | -2.9887 | -10.9813 | -9.6822 | -1.911 |  | -5.392 | -4.7787 | 4.0269 | 3.3738 | 3.356 | 0.9932 | 10.6283 | 14.096 | 14.6813 | 10.9872 | -0.0002 | -0.0032 | 0.0006 | 0.0034 | 0.0007 | -0.0004 | 0.0058 | 0.0004 | -0.0085 | -360.1773 | 17.6102 | -360.5958 | 17.9223 | -360.8974 | 18.144 | -360.9497 | 17.5321 | -352.8967 | 18.7846 | -352.8844 | 16.8176
11:34 | 886 | 18.984 | 193.1804 | 433.9509 | 439.8161 | -22.0451 | -48.5119 | 0.0099 | -0.971 | -8.3501 | -8.073 | -3.5528 | -4.1876 | 1.5157 | -5.627 | 0.5801 | 0.6334 | 0.9517 | 0.6891 | -132.2002 | -8.6849 | -1.7755 | -3.0213 | -10.9536 | -9.7254 | -1.9033 |  | -5.3876 | -4.7524 | 4.0265 | 3.3779 | 3.3588 | 0.9919 | 10.6097 | 14.095 | 14.6752 | 10.9626 | 0 | -0.0029 | 0.0005 | 0.003 | 0.0004 | -0.0008 | 0.0169 | -0.0113 | -0.0206 | -360.1435 | 17.6307 | -360.6573 | 17.9428 | -360.9712 | 18.1871 | -360.9743 | 17.5178 | -352.8629 | 18.8011 | -352.9306 | 16.8402
11:34 | 887 | 18.944 | 193.1595 | 433.8678 | 439.8383 | -22.0647 | -48.5262 | -0.02 | -0.9686 | -8.3499 | -8.16 | -3.574 | -4.1951 | 1.4074 | -5.7369 | 0.5806 | 0.6318 | 0.9527 | 0.6875 | -132.2443 | -8.7417 | -1.7565 | -3.0524 | -10.9071 | -9.7797 | -1.9087 |  | -5.4113 | -4.8188 | 4.0257 | 3.3745 | 3.356 | 0.992 | 10.6354 | 14.0854 | 14.6921 | 10.989 | -0.0005 | -0.0031 | 0.0006 | 0.0031 | 0.0003 | -0.001 | 0.007 | -0.0015 | -0.0142 | -360.1342 | 17.5896 | -360.5896 | 17.912 | -360.9158 | 18.1728 | -360.9466 | 17.5157 | -352.8475 | 18.7764 | -352.8783 | 16.8197
11:35 | 888 | 18.9281 | 193.212 | 433.9129 | 439.8504 | -22.094 | -48.617 | 0.0399 | -0.9037 | -8.2484 | -8.1412 | -3.4705 | -4.277 | 1.4161 | -5.7553 | 0.5797 | 0.6312 | 0.9511 | 0.6876 | -132.2536 | -8.7696 | -1.8038 | -3.0427 | -10.8922 | -9.7358 | -1.9456 |  | -5.4154 | -4.9221 | 4.0256 | 3.3772 | 3.3558 | 0.9923 | 10.6076 | 14.0865 | 14.6356 | 10.9381 | -0.0002 | -0.0027 | 0.0011 | 0.0037 | 0.0001 | -0.0007 | -0.0018 | -0.0163 | 0.0057 | -360.2081 | 17.6184 | -360.6266 | 17.9305 | -360.922 | 18.1789 | -361.0174 | 17.5424 | -352.8752 | 18.8031 | -352.8906 | 16.7991
11:35 | 889 | 18.9047 | 193.1076 | 433.9466 | 439.7896 | -22.0411 | -48.6209 | 0.0439 | -0.9545 | -8.3459 | -8.0947 | -3.5123 | -4.1956 | 1.3625 | -5.7662 | 0.5802 | 0.6261 | 0.9517 | 0.6883 | -132.269 | -8.7358 | -1.7304 | -2.9761 | -10.975 | -9.8816 | -1.8729 |  | -5.4524 | -4.8173 | 4.0261 | 3.3783 | 3.3583 | 0.992 | 10.5866 | 14.0718 | 14.652 | 10.98 | 0.0003 | -0.003 | 0.0007 | 0.0036 | 0.0013 | -0.0005 | 0.0174 | -0.0038 | -0.0072 | -360.1373 | 17.5978 | -360.5712 | 17.912 | -360.8881 | 18.1461 | -360.9497 | 17.526 | -352.8844 | 18.7744 | -352.8691 | 16.8135
11:35 | 890 | 18.8779 | 193.0244 | 433.8686 | 439.743 | -22.0384 | -48.6021 | 0.0332 | -0.9455 | -8.3944 | -8.1971 | -3.5438 | -4.3866 | 1.3703 | -5.8143 | 0.5802 | 0.6256 | 0.9544 | 0.6889 | -132.1783 | -8.7633 | -1.6924 | -3.0249 | -10.949 | -9.8095 | -1.9487 |  | -5.4436 | -4.7792 | 4.0233 | 3.3771 | 3.3584 | 0.9917 | 10.6075 | 14.0404 | 14.6424 | 10.9493 | -0.0001 | -0.0031 | 0.0008 | 0.0041 | 0.0002 | -0.0008 | 0.0121 | -0.014 | 0.0007 | -360.1896 | 17.6225 | -360.6019 | 17.9264 | -360.9527 | 18.1933 | -360.9897 | 17.5239 | -352.8998 | 18.7949 | -352.8967 | 16.8197
11:35 | 891 | 18.8916 | 193.0685 | 433.8798 | 439.7105 | -21.8196 | -48.4451 | 0.2742 | -0.9089 | -8.4163 | -8.2517 | -3.5603 | -4.274 | 1.4472 | -5.7296 | 0.581 | 0.6296 | 0.9525 | 0.6868 | -132.1997 | -8.8284 | -1.6584 | -2.9835 | -10.9874 | -9.8337 | -1.9355 |  | -5.3925 | -4.8764 | 4.0237 | 3.3763 | 3.3586 | 0.993 | 10.6306 | 14.0753 | 14.6724 | 10.9778 | 0.0001 | -0.0027 | 0.0006 | 0.0037 | 0.001 | -0.0008 | -0.0034 | -0.0058 | -0.016 | -360.0911 | 17.5999 | -360.5989 | 17.9161 | -360.8974 | 18.1604 | -360.962 | 17.526 | -352.8444 | 18.7764 | -352.8783 | 16.8176
11:35 | 892 | 18.8877 | 193.1566 | 433.8925 | 439.7849 | -21.8283 | -48.5135 | 0.1296 | -0.897 | -8.4323 | -8.1154 | -3.5304 | -4.2964 | 1.4472 | -5.7992 | 0.5806 | 0.6294 | 0.9509 | 0.6886 | -132.1799 | -8.8128 | -1.7729 | -2.9616 | -11.0306 | -9.777 | -1.9988 |  | -5.4558 | -4.8758 | 4.0252 | 3.3762 | 3.3575 | 0.9922 | 10.612 | 14.0569 | 14.6837 | 10.9706 | -0.0003 | -0.0025 | 0.0003 | 0.0035 | 0.0007 | -0.0003 | 0.0079 | -0.009 | 0.0052 | -360.1588 | 17.6184 | -360.6112 | 17.9284 | -360.9374 | 18.1871 | -361.0051 | 17.5321 | -352.8352 | 18.7846 | -352.9029 | 16.8094
11:35 | 893 | 18.9077 | 193.06 | 433.8774 | 439.8142 | -21.8973 | -48.509 | 0.2157 | -0.8693 | -8.3657 | -8.1725 | -3.5355 | -4.193 | 1.3728 | -5.7324 | 0.5807 | 0.6298 | 0.9516 | 0.6883 | -132.2774 | -8.8503 | -1.6186 | -2.8859 | -11.008 | -9.8006 | -1.9093 |  | -5.391 | -4.817 | 4.0261 | 3.3772 | 3.3596 | 0.9918 | 10.6007 | 14.0621 | 14.6621 | 10.9548 | -0.0001 | -0.0029 | 0.0005 | 0.0034 | 0.0006 | -0.001 | 0.0113 | -0.0032 | -0.0035 | -360.1373 | 17.5958 | -360.5835 | 17.9202 | -360.9127 | 18.1707 | -360.9897 | 17.5321 | -352.8783 | 18.7723 | -352.8752 | 16.8156
11:35 | 894 | 18.9599 | 193.1162 | 433.8752 | 439.7757 | -21.8919 | -48.43 | 0.1802 | -0.8117 | -8.2962 | -8.104 | -3.5533 | -4.2114 | 1.3564 | -5.7659 | 0.5801 | 0.6275 | 0.9534 | 0.6879 | -132.2026 | -8.7463 | -1.6337 | -2.8898 | -10.9438 | -9.8621 | -1.9528 |  | -5.3725 | -4.8083 | 4.024 | 3.3781 | 3.3623 | 0.9928 | 10.6029 | 14.0647 | 14.6264 | 10.9619 | 0 | -0.003 | 0.0011 | 0.0041 | 0.0008 | 0.0001 | -0.0007 | 0.0005 | -0.0095 | -360.1865 | 17.6204 | -360.6081 | 17.912 | -360.9127 | 18.183 | -360.962 | 17.5178 | -352.8567 | 18.7908 | -352.8967 | 16.8032
11:35 | 895 | 18.9993 | 193.1293 | 433.9202 | 439.7875 | -21.8631 | -48.4547 | 0.1854 | -0.9495 | -8.389 | -8.1993 | -3.5267 | -4.1314 | 1.3862 | -5.7147 | 0.58 | 0.6272 | 0.9523 | 0.6875 | -132.2362 | -8.9084 | -1.73 | -2.8785 | -11.0023 | -9.8079 | -1.9388 |  | -5.408 | -4.7661 | 4.0236 | 3.3749 | 3.3599 | 0.9912 | 10.5903 | 14.0575 | 14.6345 | 10.9674 | 0 | -0.0029 | 0.0011 | 0.0038 | 0.001 | -0.0004 | 0.0062 | -0.007 | -0.0128 | -360.1773 | 17.6225 | -360.6296 | 17.949 | -360.9466 | 18.1584 | -360.9774 | 17.5219 | -352.8691 | 18.8052 | -352.8937 | 16.8423
11:35 | 896 | 18.9665 | 193.0538 | 433.8068 | 439.7681 | -21.8888 | -48.4475 | 0.0437 | -0.815 | -8.3306 | -8.2103 | -3.4815 | -4.1685 | 1.3678 | -5.6904 | 0.5801 | 0.6331 | 0.9554 | 0.6879 | -132.1945 | -8.7806 | -1.7395 | -2.8875 | -10.9547 | -9.784 | -1.9751 |  | -5.3875 | -4.7882 | 4.0245 | 3.3751 | 3.3596 | 0.9928 | 10.5729 | 14.0517 | 14.6519 | 10.9501 | -0.0003 | -0.0028 | 0.0013 | 0.0039 | 0.0004 | -0.0006 | 0.0175 | -0.0177 | -0.0194 | -360.1342 | 17.6081 | -360.5866 | 17.9305 | -360.9189 | 18.1789 | -360.9774 | 17.4993 | -352.8106 | 18.7867 | -352.8691 | 16.8074
11:35 | 897 | 19.0126 | 193.14 | 433.9853 | 439.8781 | -21.9262 | -48.4469 | 0.0445 | -0.8456 | -8.3118 | -8.0861 | -3.5037 | -4.2288 | 1.338 | -5.7958 | 0.5791 | 0.6268 | 0.9519 | 0.6871 | -132.2012 | -8.8427 | -1.7241 | -2.782 | -10.918 | -9.7845 | -2.0134 |  | -5.413 | -4.7771 | 4.0228 | 3.375 | 3.3577 | 0.9925 | 10.6029 | 14.0877 | 14.6543 | 10.9797 | -0.0002 | -0.003 | 0.0009 | 0.0037 | 0.0004 | -0.0003 | 0.0041 | -0.0089 | -0.0186 | -360.1804 | 17.604 | -360.5958 | 17.9325 | -360.9343 | 18.181 | -360.9989 | 17.5506 | -352.9121 | 18.7826 | -352.8844 | 16.8258
11:35 | 898 | 19.0135 | 193.0457 | 433.8022 | 439.7515 | -21.969 | -48.6465 | 0.018 | -0.9062 | -8.3462 | -8.1916 | -3.4616 | -4.3354 | 1.3236 | -5.7248 | 0.5812 | 0.6296 | 0.953 | 0.6884 | -132.1266 | -8.7591 | -1.6803 | -2.8404 | -10.9667 | -9.7371 | -1.9068 |  | -5.4414 | -4.7551 | 4.0235 | 3.3776 | 3.3607 | 0.9929 | 10.603 | 14.0645 | 14.6359 | 10.9512 | 0.0004 | -0.0028 | 0.0005 | 0.0037 | 0.0003 | -0.0015 | -0.0013 | -0.0134 | -0.003 | -360.1373 | 17.6204 | -360.5896 | 17.8976 | -360.8481 | 18.1522 | -360.9897 | 17.5301 | -352.9029 | 18.8011 | -352.8444 | 16.7848
11:35 | 899 | 18.9776 | 193.0165 | 433.8161 | 439.6644 | -21.9197 | -48.4533 | 0.0065 | -0.8488 | -8.1971 | -8.0964 | -3.4702 | -4.3556 | 1.4228 | -5.6977 | 0.5808 | 0.6325 | 0.9524 | 0.6883 | -132.1729 | -8.7879 | -1.715 | -2.8597 | -10.9934 | -9.7931 | -1.9284 |  | -5.3804 | -4.748 | 4.0239 | 3.3763 | 3.3579 | 0.9925 | 10.6006 | 14.068 | 14.6226 | 10.9602 | -0.0001 | -0.003 | 0.0006 | 0.0041 | 0.0004 | -0.0006 | 0.0159 | 0.004 | 0.0001 | -360.1619 | 17.6348 | -360.6296 | 17.9387 | -360.9404 | 18.1584 | -360.9866 | 17.5424 | -352.9152 | 18.8072 | -352.9152 | 16.8238
11:35 | 900 | 18.9875 | 193.048 | 433.8976 | 439.6424 | -21.9117 | -48.4512 | 0.0476 | -0.8527 | -8.2981 | -8.0509 | -3.6028 | -4.3409 | 1.3935 | -5.6612 | 0.581 | 0.6263 | 0.9513 | 0.686 | -132.081 | -8.8228 | -1.6759 | -2.837 | -11.0489 | -9.8799 | -2.0082 |  | -5.3876 | -4.7079 | 4.0246 | 3.3747 | 3.3542 | 0.993 | 10.6122 | 14.0797 | 14.7047 | 10.9887 | -0.0003 | -0.0028 | 0.0002 | 0.0034 | 0.0006 | -0.0015 | 0.008 | 0.0062 | -0.0134 | -360.1004 | 17.5958 | -360.6173 | 17.9264 | -360.9404 | 18.1871 | -360.9927 | 17.4993 | -352.8321 | 18.7661 | -352.8998 | 16.8156
11:35 | 901 | 19.0208 | 193.0986 | 433.9103 | 439.6621 | -21.8986 | -48.5116 | 0.058 | -0.8276 | -8.2338 | -8.0968 | -3.4514 | -4.3091 | 1.4124 | -5.6318 | 0.58 | 0.6316 | 0.9506 | 0.6885 | -132.1913 | -8.8482 | -1.6181 | -2.8655 | -11.0052 | -9.8696 | -1.9684 |  | -5.387 | -4.8185 | 4.0246 | 3.3753 | 3.3552 | 0.9929 | 10.6099 | 14.0656 | 14.6836 | 10.9869 | -0.0006 | -0.0027 | 0.0003 | 0.0035 | 0.0003 | -0.0003 | 0.0132 | -0.0027 | 0.0043 | -360.1435 | 17.5855 | -360.5527 | 17.9161 | -360.9466 | 18.1974 | -361.0266 | 17.5363 | -352.8967 | 18.7661 | -352.8414 | 16.8176
11:35 | 902 | 18.9631 | 193.1458 | 433.9106 | 439.7116 | -21.9283 | -48.4663 | 0.1053 | -0.8308 | -8.2644 | -8.1688 | -3.4731 | -4.2606 | 1.5027 | -5.6937 | 0.5814 | 0.6345 | 0.9512 | 0.6882 | -132.2381 | -8.8001 | -1.6356 | -2.8876 | -10.9195 | -9.7071 | -1.9251 |  | -5.365 | -4.8356 | 4.0236 | 3.376 | 3.356 | 0.9932 | 10.6132 | 14.0868 | 14.655 | 10.9663 | -0.0004 | -0.0032 | 0.0009 | 0.0039 | 0.0008 | -0.0008 | 0.0079 | -0.0076 | 0.0003 | -360.1988 | 17.604 | -360.5773 | 17.9079 | -360.9004 | 18.1625 | -360.9927 | 17.5383 | -352.8629 | 18.7846 | -352.8875 | 16.7991
11:35 | 903 | 18.9975 | 193.1796 | 434.0002 | 439.6752 | -21.9578 | -48.4209 | 0.0956 | -0.874 | -8.3284 | -8.3823 | -3.4849 | -4.2386 | 1.4799 | -5.7084 | 0.5808 | 0.6327 | 0.9461 | 0.6873 | -132.2841 | -8.7624 | -1.6189 | -2.8948 | -10.9776 | -9.8356 | -1.9976 |  | -5.3507 | -4.7605 | 4.0232 | 3.3772 | 3.3539 | 0.9932 | 10.5846 | 14.0516 | 14.6509 | 10.9562 | 0.0001 | -0.0032 | 0.0007 | 0.0036 | 0.0004 | -0.0005 | -0.0015 | -0.0179 | -0.01 | -360.1804 | 17.6307 | -360.6543 | 17.9284 | -360.9374 | 18.1543 | -360.9251 | 17.5137 | -352.8844 | 18.8113 | -352.9091 | 16.8217
11:35 | 904 | 18.9971 | 193.1379 | 433.9173 | 439.6782 | -21.9581 | -48.4466 | 0.1293 | -0.9035 | -8.2867 | -8.3301 | -3.5797 | -4.2203 | 1.4972 | -5.7093 | 0.5809 | 0.6358 | 0.9478 | 0.6863 | -132.23 | -8.8238 | -1.7114 | -2.9842 | -10.9823 | -9.7935 | -2.0093 |  | -5.4131 | -4.7842 | 4.024 | 3.378 | 3.3554 | 0.993 | 10.6064 | 14.0796 | 14.6516 | 10.9717 | -0.0003 | -0.003 | 0.0013 | 0.0043 | 0.0006 | -0.0003 | -0.0095 | -0.008 | -0.0042 | -360.165 | 17.6204 | -360.6666 | 17.9448 | -360.9497 | 18.1645 | -360.9466 | 17.5239 | -352.8721 | 18.799 | -352.9367 | 16.8279
11:35 | 905 | 18.8923 | 193.1265 | 433.8917 | 439.7541 | -21.9494 | -48.4906 | 0.1497 | -0.9262 | -8.1988 | -8.226 | -3.4706 | -4.2492 | 1.5396 | -5.8098 | 0.5794 | 0.6337 | 0.9513 | 0.6873 | -132.1942 | -8.782 | -1.7059 | -2.9561 | -10.9161 | -9.876 | -1.986 |  | -5.3698 | -4.848 | 4.0231 | 3.3747 | 3.3594 | 0.9929 | 10.5959 | 14.0753 | 14.6493 | 10.9605 | 0 | -0.0026 | 0.0009 | 0.0037 | 0.0006 | -0.0007 | 0.0153 | -0.0198 | 0.0112 | -360.125 | 17.5814 | -360.5558 | 17.912 | -360.9127 | 18.1707 | -360.9866 | 17.5219 | -352.8321 | 18.7682 | -352.8383 | 16.8074
11:35 | 906 | 18.9706 | 193.1404 | 433.8208 | 439.8271 | -21.9189 | -48.5575 | 0.0978 | -0.9266 | -8.2839 | -8.2628 | -3.4551 | -4.2382 | 1.5467 | -5.7114 | 0.5797 | 0.6268 | 0.9521 | 0.6876 | -132.1792 | -8.7885 | -1.6868 | -2.8734 | -10.9085 | -9.8039 | -1.917 |  | -5.3207 | -4.825 | 4.0232 | 3.3761 | 3.3568 | 0.9936 | 10.6366 | 14.0691 | 14.6693 | 10.9847 | -0.0004 | -0.0033 | 0.0005 | 0.0034 | 0.0003 | -0.0007 | 0.0018 | -0.0073 | -0.0051 | -360.2142 | 17.6122 | -360.5804 | 17.9079 | -360.922 | 18.181 | -361.002 | 17.5671 | -352.9152 | 18.799 | -352.8875 | 16.7991
11:35 | 907 | 18.9804 | 193.0923 | 433.8665 | 439.7716 | -21.9014 | -48.4852 | 0.1268 | -0.8883 | -8.3009 | -8.2792 | -3.5111 | -4.2886 | 1.5278 | -5.7957 | 0.5799 | 0.6309 | 0.9515 | 0.6855 | -132.3012 | -8.8617 | -1.8323 | -3.1045 | -10.9241 | -9.7456 | -1.9063 |  | -5.375 | -4.7905 | 4.0239 | 3.3771 | 3.3565 | 0.9935 | 10.5798 | 14.0935 | 14.6601 | 10.9854 | 0.0001 | -0.003 | 0.0007 | 0.0041 | 0.0009 | -0.0009 | 0.0065 | -0.003 | -0.0127 | -360.1281 | 17.6102 | -360.5835 | 17.9079 | -360.885 | 18.1625 | -360.962 | 17.5321 | -352.8844 | 18.7908 | -352.8752 | 16.7889
11:35 | 908 | 18.9667 | 193.1022 | 433.8963 | 439.7096 | -21.9436 | -48.4584 | 0.2232 | -0.8876 | -8.3431 | -8.293 | -3.4502 | -4.3179 | 1.4715 | -5.7756 | 0.58 | 0.6264 | 0.9539 | 0.6857 | -132.2102 | -8.8787 | -1.8188 | -3.0824 | -10.9679 | -9.7244 | -1.9092 |  | -5.2711 | -4.768 | 4.0233 | 3.3704 | 3.3549 | 0.9932 | 10.6111 | 14.0494 | 14.6492 | 10.9364 | -0.0003 | -0.0033 | 0.0003 | 0.0036 | 0.0001 | -0.0005 | 0.0088 | -0.0077 | -0.01 | -360.0665 | 17.6061 | -360.6573 | 17.9346 | -360.9497 | 18.1666 | -360.9527 | 17.5055 | -352.8567 | 18.7846 | -352.8906 | 16.8361
11:35 | 909 | 18.9379 | 193.0986 | 433.8416 | 439.7148 | -21.8765 | -48.3959 | 0.1608 | -0.9241 | -8.3439 | -8.3479 | -3.4937 | -4.3274 | 1.5302 | -5.6852 | 0.5821 | 0.6327 | 0.9501 | 0.6861 | -132.1902 | -8.8502 | -1.7938 | -3.0355 | -11.0161 | -9.7171 | -1.9358 |  | -5.312 | -4.8074 | 4.0238 | 3.3738 | 3.3542 | 0.9919 | 10.5845 | 14.098 | 14.6519 | 10.9501 | -0.0003 | -0.0027 | 0.001 | 0.004 | 0.0008 | -0.0009 | 0.0037 | -0.0024 | -0.0316 | -360.1065 | 17.604 | -360.6143 | 17.9448 | -360.9989 | 18.1974 | -360.9743 | 17.5055 | -352.8444 | 18.7785 | -352.8998 | 16.8423
11:35 | 910 | 18.9257 | 193.1219 | 433.8875 | 439.7848 | -21.973 | -48.4404 | 0.0399 | -0.9114 | -8.3629 | -8.3267 | -3.5383 | -4.331 | 1.5135 | -5.7423 | 0.5821 | 0.6304 | 0.9512 | 0.6871 | -132.209 | -8.8351 | -1.811 | -3.048 | -10.9905 | -9.7724 | -1.9253 |  | -5.3645 | -4.8151 | 4.0224 | 3.3761 | 3.3575 | 0.9938 | 10.6063 | 14.0858 | 14.6605 | 10.9879 | -0.0001 | -0.0025 | 0.0007 | 0.0041 | 0.0007 | -0.0002 | -0.0023 | -0.0097 | -0.016 | -360.1527 | 17.5978 | -360.5681 | 17.9058 | -360.9097 | 18.1789 | -360.9897 | 17.5301 | -352.8629 | 18.7723 | -352.8629 | 16.8053
11:35 | 911 | 19.0145 | 193.1153 | 433.8382 | 439.7789 | -21.9335 | -48.476 | 0.1363 | -0.8877 | -8.3107 | -8.3315 | -3.5132 | -4.3637 | 1.5544 | -5.7358 | 0.5805 | 0.6315 | 0.9499 | 0.6861 | -132.1803 | -8.8004 | -1.7317 | -3.028 | -10.9461 | -9.769 | -1.9537 |  | -5.366 | -4.7824 | 4.0241 | 3.3778 | 3.3558 | 0.9937 | 10.6215 | 14.1119 | 14.672 | 10.9869 | -0.0001 | -0.0032 | 0.0007 | 0.0038 | 0.0002 | -0.0008 | -0.0017 | -0.0015 | 0.0174 | -360.1681 | 17.6163 | -360.6081 | 17.8997 | -360.8789 | 18.1543 | -360.9774 | 17.5424 | -352.9214 | 18.8093 | -352.8752 | 16.7889
11:35 | 912 | 18.998 | 193.1222 | 433.9175 | 439.7316 | -21.9029 | -48.4486 | 0.1475 | -0.8664 | -8.2488 | -8.282 | -3.5021 | -4.2752 | 1.5709 | -5.7041 | 0.5814 | 0.6311 | 0.9513 | 0.687 | -132.2478 | -8.8722 | -1.7965 | -3.0225 | -10.9511 | -9.8223 | -1.8929 |  | -5.4176 | -4.8305 | 4.0229 | 3.3773 | 3.3589 | 0.9945 | 10.612 | 14.0975 | 14.6847 | 10.9817 | 0.0002 | -0.0028 | 0.0009 | 0.0038 | 0.0007 | -0.0006 | 0.0115 | -0.0011 | -0.019 | -360.205 | 17.6307 | -360.605 | 17.912 | -360.9343 | 18.1707 | -360.9558 | 17.5342 | -352.9029 | 18.8011 | -352.8967 | 16.8115
11:35 | 913 | 18.9475 | 193.1403 | 433.9645 | 439.8687 | -21.9492 | -48.3621 | 0.2335 | -1.0061 | -8.3275 | -8.3261 | -3.5142 | -4.3984 | 1.4875 | -5.6725 | 0.5814 | 0.6338 | 0.9527 | 0.6878 | -132.217 | -8.8273 | -1.75 | -3.0863 | -10.9359 | -9.8306 | -1.9306 |  | -5.4332 | -4.86 | 4.0235 | 3.3769 | 3.3576 | 0.9951 | 10.6352 | 14.0914 | 14.6653 | 10.9941 | -0.0002 | -0.0027 | 0.0006 | 0.0037 | 0 | -0.0006 | 0.0057 | -0.0101 | -0.0058 | -360.0573 | 17.5917 | -360.605 | 17.9284 | -360.9404 | 18.1789 | -360.9497 | 17.5013 | -352.8167 | 18.7682 | -352.8998 | 16.8238
11:35 | 914 | 18.959 | 193.1042 | 433.9036 | 439.8123 | -21.9036 | -48.4397 | 0.2144 | -0.9018 | -8.3936 | -8.2233 | -3.4484 | -4.3923 | 1.4562 | -5.7433 | 0.5815 | 0.6329 | 0.9526 | 0.6881 | -132.1796 | -8.7807 | -1.6601 | -3.083 | -10.899 | -9.6976 | -1.8747 |  | -5.4052 | -4.8474 | 4.0244 | 3.3743 | 3.3571 | 0.9934 | 10.6133 | 14.0751 | 14.7003 | 10.9551 | -0.0001 | -0.0026 | 0.0005 | 0.0037 | 0.0008 | -0.0009 | 0.0075 | -0.0174 | -0.0041 | -360.1281 | 17.5896 | -360.5804 | 17.9428 | -360.9097 | 18.1769 | -361.0451 | 17.5301 | -352.8567 | 18.7744 | -352.866 | 16.8279
11:35 | 915 | 19.0652 | 193.1814 | 433.9829 | 439.9414 | -21.9016 | -48.3808 | 0.2503 | -0.9839 | -8.4019 | -8.2543 | -3.4591 | -4.3114 | 1.5472 | -5.7323 | 0.581 | 0.6362 | 0.9524 | 0.6872 | -132.202 | -8.8115 | -1.6769 | -3.1198 | -10.9716 | -9.8469 | -1.9477 |  | -5.3444 | -4.8236 | 4.0229 | 3.3764 | 3.3577 | 0.9947 | 10.6167 | 14.0729 | 14.6639 | 10.9583 | 0.0001 | -0.0026 | 0.001 | 0.0041 | 0.0004 | -0.0006 | 0.0094 | -0.0088 | -0.0034 | -360.165 | 17.6204 | -360.5958 | 17.9366 | -360.9497 | 18.1728 | -360.9774 | 17.526 | -352.8937 | 18.8134 | -352.8937 | 16.8012
11:35 | 916 | 19.0404 | 193.0909 | 433.9576 | 439.9357 | -21.8822 | -48.3196 | 0.2359 | -0.9431 | -8.3745 | -8.3544 | -3.5271 | -4.3005 | 1.5247 | -5.6906 | 0.5795 | 0.6306 | 0.9491 | 0.6869 | -132.2185 | -8.8765 | -1.7061 | -3.0744 | -10.9774 | -9.7361 | -1.8998 |  | -5.3269 | -4.7795 | 4.0224 | 3.3742 | 3.3544 | 0.9937 | 10.5812 | 14.0652 | 14.6226 | 10.9534 | 0 | -0.0032 | 0.0003 | 0.0037 | 0.0004 | -0.0008 | 0.024 | -0.0107 | -0.0336 | -360.125 | 17.6061 | -360.6143 | 17.9366 | -360.8789 | 18.1563 | -361.0081 | 17.5178 | -352.8444 | 18.7969 | -352.8875 | 16.8094
11:35 | 917 | 19.1297 | 193.2109 | 433.9789 | 439.9137 | -21.8934 | -48.3004 | 0.2472 | -0.9445 | -8.3792 | -8.3082 | -3.6209 | -4.2808 | 1.5242 | -5.6721 | 0.5812 | 0.6261 | 0.9476 | 0.685 | -132.279 | -8.8265 | -1.6778 | -3.0259 | -10.9428 | -9.7893 | -1.8782 |  | -5.3664 | -4.8698 | 4.0229 | 3.3746 | 3.3564 | 0.995 | 10.6076 | 14.0575 | 14.6577 | 10.9443 | 0.0001 | -0.0029 | 0.0006 | 0.0038 | 0.0002 | -0.0005 | -0.0044 | -0.0081 | 0.001 | -360.1896 | 17.6184 | -360.6266 | 17.949 | -360.9281 | 18.1666 | -360.9712 | 17.526 | -352.8844 | 18.8134 | -352.8998 | 16.8258
11:35 | 918 | 19.1427 | 193.2288 | 434.0746 | 439.9174 | -21.8287 | -48.3104 | 0.2604 | -1.0139 | -8.3814 | -8.3125 | -3.5826 | -4.3229 | 1.5324 | -5.5095 | 0.5809 | 0.6315 | 0.9473 | 0.6873 | -132.2053 | -8.8323 | -1.8324 | -2.9226 | -10.8246 | -9.7214 | -1.8718 |  | -5.3623 | -4.9245 | 4.0242 | 3.3768 | 3.3569 | 0.9951 | 10.5902 | 14.0636 | 14.6598 | 10.9493 | -0.0004 | -0.0028 | 0.0006 | 0.0041 | 0.0008 | -0.0009 | 0.0082 | -0.0159 | -0.0106 | -360.1342 | 17.6184 | -360.6327 | 17.9407 | -360.9374 | 18.1748 | -360.9927 | 17.528 | -352.8752 | 18.7969 | -352.9029 | 16.8135
11:35 | 919 | 19.0187 | 193.2689 | 433.914 | 439.8607 | -21.7398 | -48.2735 | 0.2724 | -0.9967 | -8.4296 | -8.4478 | -3.5747 | -4.2404 | 1.5613 | -5.6225 | 0.5803 | 0.6346 | 0.9466 | 0.6867 | -132.2583 | -8.824 | -1.8183 | -2.8626 | -10.8639 | -9.6653 | -1.8925 |  | -5.2923 | -4.8235 | 4.0239 | 3.3758 | 3.3545 | 0.9936 | 10.6122 | 14.0971 | 14.67 | 10.9829 | 0.0002 | -0.0025 | 0.0011 | 0.004 | 0.0005 | 0 | -0.0054 | 0.0018 | 0.0065 | -360.1619 | 17.5999 | -360.5773 | 17.9264 | -360.9435 | 18.181 | -360.9681 | 17.5198 | -352.8352 | 18.7826 | -352.8444 | 16.8032
11:35 | 920 | 18.9891 | 193.2145 | 433.9764 | 439.8542 | -21.7403 | -48.2786 | 0.3291 | -0.9541 | -8.3528 | -8.4463 | -3.6539 | -4.2078 | 1.6106 | -5.5855 | 0.5806 | 0.6314 | 0.9464 | 0.6865 | -132.2735 | -8.8093 | -1.7918 | -2.918 | -10.9246 | -9.6394 | -1.8763 |  | -5.3958 | -4.7649 | 4.0221 | 3.3774 | 3.3566 | 0.9932 | 10.6272 | 14.1122 | 14.6857 | 10.9746 | 0.0002 | -0.0031 | 0.0011 | 0.0041 | 0.0003 | -0.0009 | -0.0042 | -0.0053 | 0.0125 | -360.1373 | 17.604 | -360.5896 | 17.9387 | -360.9312 | 18.1789 | -361.0235 | 17.5445 | -352.8567 | 18.7764 | -352.8875 | 16.8156
11:35 | 921 | 18.8622 | 193.088 | 433.8992 | 439.8634 | -21.8342 | -48.2727 | 0.1573 | -0.9586 | -8.4207 | -8.253 | -3.599 | -4.2474 | 1.5615 | -5.728 | 0.58 | 0.6316 | 0.9477 | 0.6856 | -132.1958 | -8.8043 | -1.7483 | -2.8362 | -10.9251 | -9.6713 | -1.8111 |  | -5.3615 | -4.8208 | 4.0225 | 3.3723 | 3.3562 | 0.9926 | 10.619 | 14.1157 | 14.7129 | 11.0067 | -0.0001 | -0.0032 | 0.001 | 0.004 | 0.0008 | -0.0003 | 0.0154 | 0 | -0.0157 | -360.1465 | 17.6225 | -360.5958 | 17.9346 | -360.9158 | 18.1563 | -360.9404 | 17.5096 | -352.8506 | 18.7928 | -352.8752 | 16.8032
11:35 | 922 | 19.016 | 193.0798 | 434.0006 | 439.9021 | -21.9179 | -48.3531 | 0.1715 | -0.9564 | -8.4099 | -8.3189 | -3.6746 | -4.2651 | 1.5513 | -5.6037 | 0.5806 | 0.633 | 0.9482 | 0.686 | -132.1903 | -8.8398 | -1.7024 | -2.9977 | -10.9959 | -9.8228 | -1.9045 |  | -5.2936 | -4.7888 | 4.0228 | 3.3767 | 3.3577 | 0.9931 | 10.6146 | 14.0645 | 14.6822 | 10.9974 | -0.0002 | -0.003 | 0.0001 | 0.003 | 0.0002 | -0.0008 | 0.0123 | -0.0096 | -0.0128 | -360.125 | 17.6122 | -360.6481 | 17.9654 | -360.9589 | 18.1604 | -360.9558 | 17.4952 | -352.8567 | 18.7949 | -352.9398 | 16.8443
11:35 | 923 | 19.0908 | 193.1587 | 434.0418 | 439.8822 | -21.8391 | -48.2819 | 0.2448 | -0.9386 | -8.3535 | -8.3379 | -3.6064 | -4.3386 | 1.5245 | -5.6072 | 0.5797 | 0.6333 | 0.9477 | 0.6845 | -132.2563 | -8.9253 | -1.7232 | -2.9221 | -10.891 | -9.7158 | -1.8639 |  | -5.338 | -4.7052 | 4.0233 | 3.375 | 3.3553 | 0.9942 | 10.6089 | 14.0642 | 14.6396 | 10.9577 | -0.0008 | -0.0031 | 0.0004 | 0.0034 | 0.0005 | -0.0014 | 0.0056 | -0.0196 | -0.0043 | -360.1619 | 17.6102 | -360.6266 | 17.9551 | -360.9374 | 18.181 | -360.9712 | 17.5157 | -352.8475 | 18.7826 | -352.8844 | 16.8217
11:35 | 924 | 19.0988 | 193.1947 | 433.9399 | 439.9315 | -21.8261 | -48.3272 | 0.2411 | -0.9717 | -8.3361 | -8.352 | -3.5705 | -4.2854 | 1.4773 | -5.6331 | 0.5804 | 0.6303 | 0.9481 | 0.6871 | -132.2598 | -9.0758 | -1.703 | -2.8064 | -10.9467 | -9.7757 | -1.9432 |  | -5.3673 | -4.7762 | 4.0236 | 3.378 | 3.3544 | 0.9937 | 10.6018 | 14.0692 | 14.6414 | 10.9728 | 0 | -0.003 | 0.0004 | 0.0039 | 0.0002 | -0.0006 | 0.0066 | -0.0062 | -0.0086 | -360.1681 | 17.5917 | -360.5835 | 17.9161 | -360.8758 | 18.1645 | -360.9804 | 17.5486 | -352.8814 | 18.7785 | -352.8598 | 16.7971
11:35 | 925 | 19.1052 | 193.1591 | 434.0356 | 439.9237 | -21.7789 | -48.3056 | 0.2613 | -0.9377 | -8.3235 | -8.246 | -3.5508 | -4.2375 | 1.4379 | -5.613 | 0.5803 | 0.6324 | 0.953 | 0.6865 | -132.2219 | -8.9287 | -1.689 | -2.7441 | -10.9709 | -9.6787 | -1.8412 |  | -5.3527 | -4.8589 | 4.0228 | 3.3765 | 3.3573 | 0.9946 | 10.572 | 14.0444 | 14.6069 | 10.9328 | -0.0003 | -0.0035 | 0.0006 | 0.0034 | 0.0006 | -0.0014 | 0.0173 | -0.0048 | -0.0264 | -360.2081 | 17.6389 | -360.6204 | 17.951 | -360.9127 | 18.1645 | -361.0051 | 17.5527 | -352.9214 | 18.8154 | -352.866 | 16.8053
11:35 | 926 | 19.081 | 193.1805 | 433.9972 | 439.9757 | -21.86 | -48.3371 | 0.1708 | -0.9852 | -8.2953 | -8.2822 | -3.6261 | -4.2639 | 1.4557 | -5.6005 | 0.5806 | 0.6311 | 0.9484 | 0.6859 | -132.2629 | -9.0222 | -1.7421 | -2.757 | -10.9637 | -9.7414 | -1.9162 |  | -5.306 | -4.8636 | 4.0234 | 3.3725 | 3.3556 | 0.9946 | 10.5821 | 14.0784 | 14.6155 | 10.9533 | -0.0004 | -0.0032 | 0.0012 | 0.0041 | 0.0002 | -0.0005 | 0.0254 | -0.0007 | -0.0321 | -360.1127 | 17.6061 | -360.6204 | 17.9387 | -360.9312 | 18.1543 | -360.9189 | 17.5137 | -352.8629 | 18.7846 | -352.8752 | 16.8156
11:35 | 927 | 19.1603 | 193.2047 | 433.9133 | 440.0203 | -21.9232 | -48.2757 | 0.2135 | -0.9052 | -8.3428 | -8.219 | -3.6303 | -4.354 | 1.3383 | -5.6259 | 0.5806 | 0.6318 | 0.9498 | 0.6863 | -132.225 | -8.919 | -1.6962 | -2.7137 | -10.9592 | -9.9577 | -1.8929 |  | -5.397 | -4.8987 | 4.0222 | 3.3761 | 3.3569 | 0.9938 | 10.6387 | 14.1065 | 14.6983 | 10.9915 | 0 | -0.0025 | 0.0006 | 0.0037 | 0.0005 | -0.0007 | 0.0039 | -0.004 | 0.002 | -360.1158 | 17.5855 | -360.6081 | 17.9674 | -360.9589 | 18.2015 | -361.0297 | 17.5178 | -352.829 | 18.7682 | -352.8844 | 16.8525
11:35 | 928 | 19.1284 | 193.1754 | 434.004 | 440.0561 | -21.8586 | -48.2522 | 0.2901 | -0.9333 | -8.2438 | -8.1933 | -3.536 | -4.4044 | 1.3215 | -5.6981 | 0.5811 | 0.6327 | 0.9495 | 0.6862 | -132.2022 | -8.8872 | -1.6677 | -2.6928 | -10.975 | -9.7499 | -1.9134 |  | -5.311 | -4.8103 | 4.023 | 3.3727 | 3.356 | 0.994 | 10.6272 | 14.0773 | 14.6904 | 11.0212 | -0.0002 | -0.0031 | 0.0006 | 0.0034 | 0.0007 | -0.0005 | 0.0058 | -0.0105 | -0.0037 | -360.1004 | 17.5712 | -360.5681 | 17.9531 | -360.9374 | 18.1871 | -360.9897 | 17.5239 | -352.8537 | 18.7661 | -352.8352 | 16.8115
11:35 | 929 | 19.1592 | 193.1935 | 433.9423 | 439.9834 | -21.9334 | -48.2763 | 0.3062 | -0.9656 | -8.3572 | -8.1404 | -3.6128 | -4.3822 | 1.2697 | -5.6253 | 0.5821 | 0.6334 | 0.9508 | 0.6858 | -132.1166 | -8.8585 | -1.7471 | -2.6877 | -10.9586 | -9.7832 | -1.8609 |  | -5.2806 | -4.8424 | 4.022 | 3.374 | 3.3566 | 0.9941 | 10.6075 | 14.052 | 14.6598 | 10.9609 | -0.0001 | -0.003 | 0.0006 | 0.0031 | 0.0004 | -0.0002 | 0.0194 | -0.0005 | -0.0219 | -360.2081 | 17.6245 | -360.5958 | 17.9387 | -360.8943 | 18.1645 | -360.9958 | 17.5445 | -352.8814 | 18.8113 | -352.8906 | 16.8094
11:35 | 930 | 19.1163 | 193.1841 | 433.9899 | 439.9607 | -21.859 | -48.2998 | 0.3516 | -1.0173 | -8.3107 | -8.2375 | -3.4946 | -4.4148 | 1.242 | -5.6977 | 0.5818 | 0.6325 | 0.9494 | 0.6873 | -132.1762 | -8.9007 | -1.7414 | -2.712 | -10.8632 | -9.7747 | -1.7992 |  | -5.3226 | -4.8114 | 4.0232 | 3.3738 | 3.3563 | 0.994 | 10.6226 | 14.1015 | 14.6965 | 10.9706 | -0.0002 | -0.003 | 0 | 0.0031 | 0.0006 | -0.0007 | 0.0055 | -0.0038 | -0.0039 | -360.1681 | 17.6328 | -360.6543 | 17.949 | -360.9097 | 18.144 | -360.922 | 17.5198 | -352.8567 | 18.8195 | -352.9029 | 16.8053
11:35 | 931 | 19.0887 | 193.2217 | 433.8806 | 439.9289 | -21.9141 | -48.2494 | 0.2751 | -0.9998 | -8.3047 | -8.2853 | -3.5035 | -4.3351 | 1.2355 | -5.6056 | 0.5813 | 0.6358 | 0.9539 | 0.6862 | -132.1177 | -8.8204 | -1.7617 | -2.7018 | -10.9033 | -9.7893 | -1.8582 |  | -5.2699 | -4.7966 | 4.0219 | 3.3754 | 3.3599 | 0.9956 | 10.5961 | 14.0805 | 14.6566 | 10.9851 | -0.0005 | -0.0027 | 0.0005 | 0.0036 | 0.0002 | -0.0006 | 0.0175 | -0.0077 | -0.0089 | -360.1681 | 17.604 | -360.6019 | 17.9448 | -360.9158 | 18.1502 | -360.9681 | 17.526 | -352.8598 | 18.8052 | -352.9214 | 16.8238
11:35 | 932 | 19.1493 | 193.2815 | 433.9694 | 439.9522 | -21.9428 | -48.4771 | 0.3388 | -0.9513 | -8.3136 | -8.2816 | -3.4729 | -4.3544 | 1.2431 | -5.6949 | 0.5815 | 0.636 | 0.9491 | 0.6844 | -132.1765 | -8.8187 | -1.7419 | -2.6236 | -10.885 | -9.6905 | -1.8002 |  | -5.298 | -4.727 | 4.0218 | 3.372 | 3.3588 | 0.9938 | 10.6087 | 14.0646 | 14.689 | 10.997 | -0.0003 | -0.0025 | 0.0005 | 0.0037 | 0.0007 | -0.0012 | 0.0167 | -0.0089 | -0.0082 | -360.165 | 17.602 | -360.5743 | 17.9325 | -360.9558 | 18.1892 | -360.9958 | 17.528 | -352.8537 | 18.7867 | -352.8444 | 16.8074
11:35 | 933 | 19.1294 | 193.246 | 433.9948 | 439.9208 | -21.9294 | -48.2492 | 0.3272 | -0.8511 | -8.2834 | -8.1049 | -3.4098 | -4.2188 | 1.3564 | -5.6355 | 0.582 | 0.633 | 0.9508 | 0.6865 | -132.1458 | -8.9271 | -1.7536 | -2.6848 | -10.903 | -9.768 | -1.8187 |  | -5.3681 | -4.7832 | 4.0221 | 3.3721 | 3.3575 | 0.994 | 10.6122 | 14.0738 | 14.6863 | 10.9717 | 0 | -0.0031 | 0.0003 | 0.004 | 0.0001 | -0.0008 | 0.0124 | -0.0028 | 0.0106 | -360.1127 | 17.5917 | -360.5712 | 17.9058 | -360.8789 | 18.1728 | -360.9958 | 17.528 | -352.8598 | 18.7744 | -352.8414 | 16.7909
11:35 | 934 | 19.0709 | 193.2466 | 433.9877 | 439.962 | -21.9821 | -48.2346 | 0.1607 | -0.846 | -8.2471 | -8.0502 | -3.5067 | -4.2815 | 1.3312 | -5.6265 | 0.5825 | 0.6352 | 0.9516 | 0.6869 | -132.1556 | -8.8863 | -1.6656 | -2.6963 | -10.8272 | -9.7656 | -1.8081 |  | -5.3135 | -4.8113 | 4.0225 | 3.3702 | 3.357 | 0.994 | 10.6052 | 14.0554 | 14.6628 | 10.9703 | 0.0003 | -0.0031 | 0.0004 | 0.0034 | 0.0004 | -0.0008 | 0.0053 | -0.0044 | -0.0041 | -360.1835 | 17.6102 | -360.6543 | 17.9531 | -360.9374 | 18.1645 | -360.962 | 17.5383 | -352.8567 | 18.7949 | -352.9306 | 16.8299
11:35 | 935 | 19.139 | 193.2044 | 433.9356 | 440.0357 | -21.8411 | -48.3194 | 0.2345 | -0.8337 | -8.3634 | -8.2153 | -3.449 | -4.3381 | 1.3213 | -5.6291 | 0.5824 | 0.6366 | 0.9509 | 0.6879 | -132.1478 | -8.8335 | -1.6398 | -2.705 | -10.8869 | -9.842 | -1.8087 |  | -5.3585 | -4.8336 | 4.0226 | 3.3749 | 3.3636 | 0.9964 | 10.6363 | 14.0927 | 14.6619 | 10.9832 | -0.0001 | -0.0028 | 0.0008 | 0.0034 | 0.0004 | -0.0004 | -0.0008 | 0.0111 | 0.0055 | -360.0942 | 17.5855 | -360.5743 | 17.9387 | -360.9035 | 18.1625 | -360.9681 | 17.5096 | -352.8444 | 18.7764 | -352.8844 | 16.8197
11:35 | 936 | 19.1316 | 193.2043 | 434.0541 | 440.0365 | -21.8717 | -48.1513 | 0.3207 | -0.8377 | -8.3914 | -8.1871 | -3.4899 | -4.2614 | 1.3567 | -5.5836 | 0.5812 | 0.6343 | 0.9503 | 0.6858 | -132.1423 | -8.8247 | -1.763 | -2.6371 | -10.9608 | -9.7054 | -1.7812 |  | -5.3703 | -4.8639 | 4.0215 | 3.3755 | 3.3576 | 0.9954 | 10.6202 | 14.1053 | 14.6969 | 10.9789 | 0 | -0.0025 | 0.0009 | 0.0038 | 0.0005 | -0.0006 | 0.0006 | -0.0091 | -0.0145 | -360.1742 | 17.6122 | -360.6112 | 17.9531 | -360.9281 | 18.1769 | -361.0112 | 17.5445 | -352.8721 | 18.7949 | -352.906 | 16.8217
11:35 | 937 | 19.1594 | 193.2261 | 434.0121 | 440.009 | -21.9159 | -48.2161 | 0.2867 | -0.8226 | -8.3558 | -8.3145 | -3.5316 | -4.2394 | 1.3929 | -5.6126 | 0.5802 | 0.6346 | 0.9512 | 0.6865 | -132.1563 | -8.8524 | -1.803 | -2.6609 | -10.9219 | -9.8571 | -1.7938 |  | -5.321 | -4.8209 | 4.0216 | 3.3712 | 3.3605 | 0.9956 | 10.626 | 14.088 | 14.6912 | 11.0078 | 0 | -0.0026 | 0.001 | 0.0041 | 0.0009 | -0.0003 | 0.0175 | -0.0083 | -0.0105 | -360.0881 | 17.604 | -360.5743 | 17.9264 | -360.8912 | 18.1563 | -360.9681 | 17.5116 | -352.8414 | 18.7805 | -352.8567 | 16.795
11:35 | 938 | 19.22 | 193.1765 | 433.9057 | 440.0312 | -21.9204 | -48.2279 | 0.2335 | -0.8262 | -8.446 | -8.2124 | -3.5146 | -4.2249 | 1.4083 | -5.5904 | 0.5792 | 0.6305 | 0.9502 | 0.6862 | -132.1139 | -8.7768 | -1.7235 | -2.6551 | -10.9298 | -9.759 | -1.8058 |  | -5.3083 | -4.8751 | 4.0228 | 3.3728 | 3.3554 | 0.995 | 10.6202 | 14.0705 | 14.6843 | 10.9908 | 0.0004 | -0.0029 | 0.0004 | 0.0036 | 0.0006 | -0.0004 | 0.0155 | 0.0012 | -0.0164 | -360.1804 | 17.6143 | -360.6327 | 17.9551 | -360.9374 | 18.1728 | -361.0051 | 17.5486 | -352.8814 | 18.799 | -352.8998 | 16.8115
11:35 | 939 | 19.2395 | 193.2451 | 433.9706 | 440.0614 | -21.8536 | -48.2884 | 0.2951 | -0.8515 | -8.4067 | -8.2586 | -3.5061 | -4.2076 | 1.4307 | -5.567 | 0.5804 | 0.634 | 0.9475 | 0.6873 | -132.144 | -8.8332 | -1.6775 | -2.6465 | -10.8724 | -9.7267 | -1.8002 |  | -5.2957 | -4.9047 | 4.021 | 3.3733 | 3.3603 | 0.9962 | 10.6076 | 14.0748 | 14.6461 | 10.979 | -0.0004 | -0.003 | 0.0008 | 0.004 | 0.001 | -0.0005 | 0.0182 | 0.0063 | -0.0071 | -360.1619 | 17.5999 | -360.5773 | 17.9223 | -360.882 | 18.1481 | -360.9435 | 17.5342 | -352.8691 | 18.7764 | -352.8567 | 16.7827
11:35 | 940 | 19.1401 | 193.1388 | 434.0303 | 440.0364 | -21.8995 | -48.289 | 0.2684 | -0.9703 | -8.4316 | -8.2385 | -3.5694 | -4.1865 | 1.2311 | -5.5498 | 0.5796 | 0.6327 | 0.9499 | 0.6876 | -132.2283 | -8.7557 | -1.6905 | -2.71 | -10.89 | -9.7792 | -1.8071 |  | -5.3037 | -4.8651 | 4.0202 | 3.3738 | 3.3588 | 0.9955 | 10.5868 | 14.0366 | 14.6246 | 10.9468 | -0.0005 | -0.0031 | 0.0008 | 0.0036 | 0.0008 | -0.0003 | 0.0022 | -0.0148 | -0.0208 | -360.1435 | 17.6163 | -360.6112 | 17.9592 | -360.9589 | 18.1666 | -360.9835 | 17.5383 | -352.8721 | 18.7928 | -352.9214 | 16.8135
11:35 | 941 | 19.1023 | 193.1516 | 434.1015 | 440.0645 | -21.9394 | -48.2597 | 0.3392 | -0.9185 | -8.4392 | -8.0847 | -3.4889 | -4.1667 | 1.3535 | -5.5251 | 0.5815 | 0.6315 | 0.9511 | 0.6884 | -132.2008 | -8.766 | -1.7456 | -2.6586 | -10.839 | -9.6961 | -1.812 |  | -5.3056 | -4.8082 | 4.0201 | 3.3719 | 3.3575 | 0.9947 | 10.5926 | 14.0888 | 14.6546 | 10.9522 | 0.0001 | -0.0026 | 0.0011 | 0.004 | 0.0007 | -0.0008 | -0.0007 | 0.0052 | 0.003 | -360.1188 | 17.5794 | -360.5435 | 17.9161 | -360.9066 | 18.1769 | -360.9835 | 17.5116 | -352.8537 | 18.7723 | -352.8537 | 16.7807
11:35 | 942 | 19.0526 | 193.2098 | 434.0666 | 439.9946 | -22.0699 | -48.2972 | 0.2087 | -0.9095 | -8.3514 | -8.2455 | -3.4519 | -4.1763 | 1.3695 | -5.471 | 0.5812 | 0.6345 | 0.9494 | 0.6867 | -132.2401 | -8.7779 | -1.6994 | -2.7118 | -10.8407 | -9.6507 | -1.8032 |  | -5.2738 | -4.9604 | 4.0199 | 3.3721 | 3.3567 | 0.9944 | 10.5672 | 14.0574 | 14.6509 | 10.9505 | 0 | -0.0034 | 0.0007 | 0.004 | 0.0003 | -0.0003 | 0.0143 | -0.006 | -0.0175 | -360.1281 | 17.5958 | -360.6173 | 17.9407 | -360.9158 | 18.181 | -361.0235 | 17.5506 | -352.8598 | 18.7661 | -352.8998 | 16.8074
11:35 | 943 | 19.1772 | 193.2398 | 434.0577 | 440.068 | -22.0073 | -48.2397 | 0.2248 | -0.8965 | -8.3744 | -8.2221 | -3.5014 | -4.1332 | 1.3893 | -5.5718 | 0.5811 | 0.6325 | 0.9501 | 0.6858 | -132.2678 | -8.8087 | -1.7238 | -2.6402 | -10.7913 | -9.705 | -1.805 |  | -5.1991 | -4.7934 | 4.0209 | 3.3712 | 3.3577 | 0.9953 | 10.6305 | 14.087 | 14.6966 | 11.0236 | 0.0002 | -0.0032 | 0.0007 | 0.0038 | 0.001 | -0.0005 | 0.016 | -0.0219 | -0.0062 | -360.1804 | 17.604 | -360.5773 | 17.912 | -360.8666 | 18.144 | -360.9435 | 17.5198 | -352.8598 | 18.7908 | -352.8721 | 16.7766
11:35 | 944 | 19.0812 | 193.1452 | 434.0524 | 440.0202 | -21.9333 | -48.2499 | 0.2802 | -0.8191 | -8.2841 | -8.1234 | -3.3704 | -4.1862 | 1.4186 | -5.5679 | 0.5818 | 0.6321 | 0.9538 | 0.6884 | -132.2449 | -8.7561 | -1.6155 | -2.7076 | -10.9116 | -9.7792 | -1.8761 |  | -5.2522 | -4.8334 | 4.0215 | 3.3713 | 3.3584 | 0.9953 | 10.6214 | 14.1295 | 14.6799 | 11.0092 | -0.0004 | -0.0029 | 0.0006 | 0.0038 | 0.0004 | -0.0003 | 0.0057 | -0.0009 | -0.008 | -360.1311 | 17.6225 | -360.642 | 17.9777 | -360.9958 | 18.1687 | -360.9466 | 17.5219 | -352.9029 | 18.799 | -352.9275 | 16.834
11:35 | 945 | 19.1544 | 193.1771 | 434.0677 | 440.0356 | -21.9443 | -48.1843 | 0.2465 | -0.8465 | -8.3605 | -8.1793 | -3.4521 | -4.1815 | 1.3847 | -5.5371 | 0.5804 | 0.6333 | 0.9514 | 0.6887 | -132.2177 | -8.7699 | -1.6976 | -2.6756 | -10.9002 | -9.6972 | -1.8711 |  | -5.2383 | -4.8082 | 4.0224 | 3.3712 | 3.3556 | 0.9941 | 10.6052 | 14.0785 | 14.6976 | 11.0107 | -0.0006 | -0.0029 | 0.0008 | 0.0037 | 0.0006 | -0.0007 | 0.0129 | 0.01 | 0.0003 | -360.0942 | 17.5958 | -360.5958 | 17.9366 | -360.9158 | 18.1645 | -360.9404 | 17.4993 | -352.7952 | 18.7723 | -352.8814 | 16.8032
11:35 | 946 | 19.1827 | 193.2655 | 434.0258 | 439.9244 | -21.9101 | -48.1312 | 0.2972 | -0.8592 | -8.3363 | -8.0121 | -3.5245 | -4.2011 | 1.4099 | -5.5434 | 0.5812 | 0.6322 | 0.9495 | 0.6882 | -132.1302 | -8.7086 | -1.6478 | -2.672 | -10.9315 | -9.772 | -1.8763 |  | -5.1716 | -4.751 | 4.0215 | 3.3739 | 3.3574 | 0.9967 | 10.6329 | 14.0775 | 14.6799 | 11.0035 | 0 | -0.003 | 0.0008 | 0.0038 | 0.0004 | -0.0005 | -0.0007 | -0.0083 | -0.0028 | -360.1773 | 17.5958 | -360.5804 | 17.9305 | -360.9312 | 18.1851 | -361.0389 | 17.5629 | -352.8967 | 18.7969 | -352.8875 | 16.7889
11:35 | 947 | 19.1763 | 193.1356 | 434.102 | 439.9537 | -21.9438 | -48.0348 | 0.3596 | -0.8037 | -8.3434 | -8.2108 | -3.4358 | -4.1613 | 1.4405 | -5.6545 | 0.5812 | 0.634 | 0.9496 | 0.6892 | -132.1271 | -8.7235 | -1.5614 | -2.6995 | -10.9362 | -9.7962 | -1.9239 |  | -5.1921 | -4.8977 | 4.0226 | 3.3755 | 3.3594 | 0.9959 | 10.6202 | 14.0764 | 14.7027 | 11.0251 | -0.0002 | -0.0032 | 0.001 | 0.0038 | 0.0008 | -0.0003 | 0.0172 | -0.0145 | -0.0149 | -360.1558 | 17.6102 | -360.5743 | 17.9099 | -360.8543 | 18.1337 | -360.9651 | 17.5383 | -352.8783 | 18.7949 | -352.8906 | 16.7766
11:36 | 948 | 19.1722 | 193.2273 | 434.1254 | 439.9834 | -21.9621 | -48.15 | 0.3021 | -0.878 | -8.3425 | -8.089 | -3.4633 | -4.1861 | 1.4719 | -5.6267 | 0.5816 | 0.6344 | 0.953 | 0.688 | -132.2129 | -8.667 | -1.6306 | -2.6818 | -10.8576 | -9.5793 | -1.8641 |  | -5.1858 | -4.9453 | 4.0206 | 3.3727 | 3.36 | 0.9974 | 10.5879 | 14.0785 | 14.6513 | 11.0165 | -0.0002 | -0.0031 | 0.0006 | 0.0037 | 0.0011 | -0.0009 | 0.0158 | -0.0123 | -0.0279 | -360.1865 | 17.6225 | -360.6543 | 17.949 | -360.9435 | 18.1707 | -360.9866 | 17.5363 | -352.906 | 18.8052 | -352.9337 | 16.8135
11:36 | 949 | 19.2398 | 193.1455 | 434.0245 | 440.0896 | -21.9862 | -48.1615 | 0.2893 | -0.8287 | -8.2814 | -8.0613 | -3.4449 | -4.2536 | 1.4065 | -5.6062 | 0.5826 | 0.6341 | 0.9505 | 0.6883 | -132.1285 | -8.712 | -1.6284 | -2.7086 | -10.8047 | -9.6199 | -1.8417 |  | -5.2141 | -4.8381 | 4.0208 | 3.3744 | 3.3592 | 0.9972 | 10.5914 | 14.0645 | 14.6822 | 10.98 | -0.0004 | -0.0028 | 0.0003 | 0.0037 | 0.0005 | -0.0004 | 0.0046 | -0.0034 | -0.0227 | -360.0727 | 17.5732 | -360.5712 | 17.9428 | -360.9497 | 18.1687 | -360.9804 | 17.5075 | -352.8106 | 18.76 | -352.8598 | 16.795
11:36 | 950 | 19.2895 | 193.2142 | 434.0725 | 440.0946 | -22.0596 | -48.2457 | 0.2271 | -0.8068 | -8.2094 | -8.0484 | -3.3447 | -4.2412 | 1.3719 | -5.6139 | 0.5824 | 0.6351 | 0.9506 | 0.6874 | -132.1637 | -8.7299 | -1.5615 | -2.6718 | -10.855 | -9.6713 | -1.8992 |  | -5.1832 | -4.7999 | 4.0211 | 3.373 | 3.3593 | 0.9963 | 10.5776 | 14.0505 | 14.6621 | 10.9374 | -0.0002 | -0.0028 | 0.0003 | 0.0038 | 0.001 | -0.001 | 0.0051 | -0.0071 | -0.0177 | -360.1496 | 17.5896 | -360.565 | 17.9346 | -360.9281 | 18.1974 | -361.0635 | 17.5486 | -352.8814 | 18.7908 | -352.8475 | 16.7909
11:36 | 951 | 19.2779 | 193.2233 | 434.1144 | 440.0256 | -21.9518 | -48.2967 | 0.2693 | -0.9228 | -8.3837 | -8.1964 | -3.4857 | -4.2444 | 1.4384 | -5.7053 | 0.5821 | 0.6372 | 0.9514 | 0.6894 | -132.2027 | -8.6683 | -1.5497 | -2.6067 | -10.8043 | -9.6068 | -1.7089 |  | -5.1542 | -4.8675 | 4.0216 | 3.3728 | 3.358 | 0.9969 | 10.5971 | 14.0588 | 14.6543 | 10.997 | 0 | -0.0034 | 0.0007 | 0.0035 | 0.0003 | -0.0003 | 0.029 | 0.0021 | -0.0052 | -360.1219 | 17.5917 | -360.5866 | 17.9223 | -360.8727 | 18.144 | -360.9681 | 17.5301 | -352.8475 | 18.7867 | -352.866 | 16.7868
11:36 | 952 | 19.2043 | 193.2277 | 433.9839 | 440.0542 | -22.013 | -48.2486 | 0.2502 | -0.8769 | -8.3492 | -7.9835 | -3.4747 | -4.1727 | 1.4905 | -5.5926 | 0.5817 | 0.6353 | 0.9514 | 0.6883 | -132.2094 | -8.7045 | -1.644 | -2.7818 | -10.8964 | -9.5419 | -1.7488 |  | -5.1932 | -4.9015 | 4.0215 | 3.371 | 3.3579 | 0.9961 | 10.6202 | 14.0879 | 14.6959 | 10.9735 | -0.0001 | -0.003 | 0.0006 | 0.0039 | 0.0011 | -0.0002 | 0.0245 | 0.004 | -0.0127 | -360.1496 | 17.6245 | -360.645 | 17.9633 | -360.9835 | 18.1625 | -360.9435 | 17.5096 | -352.8721 | 18.8134 | -352.9214 | 16.832
11:36 | 953 | 19.2695 | 193.1581 | 433.9711 | 440.0679 | -22.0606 | -48.2904 | 0.1609 | -0.973 | -8.3146 | -8.089 | -3.5263 | -4.2542 | 1.4158 | -5.5521 | 0.5822 | 0.6343 | 0.9477 | 0.6875 | -132.1745 | -8.7157 | -1.5709 | -2.6881 | -10.8271 | -9.5105 | -1.7025 |  | -5.1747 | -4.8588 | 4.0212 | 3.3716 | 3.3594 | 0.9968 | 10.6237 | 14.1088 | 14.6942 | 10.9941 | -0.0004 | -0.0026 | 0.0009 | 0.0039 | 0.0008 | -0.0004 | 0.0024 | -0.0144 | -0.0179 | -360.0819 | 17.5937 | -360.5958 | 17.9531 | -360.9312 | 18.1563 | -360.9497 | 17.4993 | -352.8014 | 18.7764 | -352.8814 | 16.8094
11:36 | 954 | 19.1985 | 193.1601 | 434.0812 | 440.0527 | -22.1402 | -48.3676 | 0.1651 | -0.9238 | -8.316 | -8.1365 | -3.4494 | -4.2748 | 1.4034 | -5.6824 | 0.5818 | 0.6354 | 0.9514 | 0.6884 | -132.1981 | -8.6768 | -1.5789 | -2.7556 | -10.7522 | -9.5028 | -1.7384 |  | -5.1702 | -4.8227 | 4.0203 | 3.3732 | 3.3592 | 0.9965 | 10.6261 | 14.1051 | 14.6833 | 10.997 | -0.0004 | -0.0027 | 0.0009 | 0.004 | 0.0006 | -0.0003 | -0.0041 | -0.0104 | -0.0336 | -360.165 | 17.5917 | -360.5804 | 17.951 | -360.922 | 18.1851 | -361.0297 | 17.5506 | -352.8998 | 18.7826 | -352.8721 | 16.7848
11:36 | 955 | 19.1809 | 193.1832 | 434.055 | 440.0306 | -22.1504 | -48.2792 | 0.1272 | -0.9229 | -8.344 | -8.0437 | -3.4702 | -4.2812 | 1.4308 | -5.7193 | 0.5823 | 0.637 | 0.9491 | 0.6873 | -132.1213 | -8.6933 | -1.5023 | -2.8439 | -10.859 | -9.7013 | -1.8056 |  | -5.1842 | -4.789 | 4.0202 | 3.374 | 3.359 | 0.9976 | 10.6214 | 14.0889 | 14.6731 | 11.0038 | 0 | -0.0028 | 0.0004 | 0.0038 | 0.001 | -0.0006 | 0.0111 | -0.0012 | 0.0007 | -360.165 | 17.5978 | -360.5866 | 17.9099 | -360.8543 | 18.144 | -360.9435 | 17.5445 | -352.8844 | 18.7826 | -352.8537 | 16.7724
11:36 | 956 | 19.1644 | 193.1457 | 434.0832 | 439.9942 | -22.1685 | -48.3648 | 0.2022 | -0.9122 | -8.2586 | -8.014 | -3.4855 | -4.253 | 1.4807 | -5.6056 | 0.5829 | 0.6403 | 0.9507 | 0.6885 | -132.1225 | -8.6536 | -1.5977 | -2.7489 | -10.8899 | -9.6274 | -1.8148 |  | -5.2707 | -4.8172 | 4.0198 | 3.3745 | 3.3603 | 0.9968 | 10.6064 | 14.0797 | 14.6816 | 11.006 | 0.0002 | -0.0031 | 0.0009 | 0.0036 | 0.0002 | -0.0007 | 0.0008 | -0.0034 | -0.0225 | -360.2173 | 17.6266 | -360.6235 | 17.951 | -360.9404 | 18.1584 | -360.9589 | 17.5445 | -352.906 | 18.8093 | -352.8875 | 16.7991
11:36 | 957 | 19.2401 | 193.0962 | 434.0242 | 440.0057 | -22.1296 | -48.2798 | 0.1856 | -1.0094 | -8.3488 | -8.1102 | -3.5322 | -4.2539 | 1.4814 | -5.7161 | 0.5817 | 0.6336 | 0.9488 | 0.6879 | -132.2898 | -8.6766 | -1.6124 | -2.8468 | -10.9123 | -9.5265 | -1.7849 |  | -5.2664 | -4.8858 | 4.0214 | 3.3746 | 3.3592 | 0.9965 | 10.6134 | 14.0922 | 14.6635 | 10.9963 | -0.0002 | -0.0031 | 0.0004 | 0.0034 | 0.0007 | -0.0008 | 0.0043 | -0.0082 | -0.0209 | -360.0665 | 17.5896 | -360.5958 | 17.951 | -360.9374 | 18.1563 | -360.9774 | 17.5137 | -352.8321 | 18.7826 | -352.8937 | 16.7991
11:36 | 958 | 19.2179 | 193.1913 | 434.0166 | 440.0109 | -22.0461 | -48.2107 | 0.31 | -1.0215 | -8.2948 | -8.0033 | -3.5506 | -4.3577 | 1.4501 | -5.6594 | 0.5811 | 0.637 | 0.9455 | 0.6885 | -132.2771 | -8.6829 | -1.6319 | -2.5621 | -10.8818 | -9.4773 | -1.8017 |  | -5.249 | -4.7733 | 4.0203 | 3.3754 | 3.3604 | 0.9962 | 10.6099 | 14.0599 | 14.6604 | 10.9869 | -0.0001 | -0.0025 | 0.0008 | 0.0039 | 0.0003 | -0.0008 | -0.0015 | -0.0049 | -0.0113 | -360.1188 | 17.5917 | -360.5835 | 17.9366 | -360.9558 | 18.2077 | -361.0051 | 17.5219 | -352.8691 | 18.7641 | -352.866 | 16.795
11:36 | 959 | 19.3192 | 193.1515 | 434.0498 | 439.9919 | -22.0371 | -48.225 | 0.2806 | -1.0529 | -8.2959 | -8.0582 | -3.6185 | -4.2939 | 1.3788 | -5.7901 | 0.5819 | 0.6353 | 0.9492 | 0.6877 | -132.1852 | -8.6215 | -1.5392 | -2.7225 | -10.9046 | -9.6255 | -1.8483 |  | -5.2175 | -4.8488 | 4.0216 | 3.3744 | 3.3594 | 0.9979 | 10.6042 | 14.0597 | 14.6536 | 10.9468 | -0.0003 | -0.0031 | 0.0011 | 0.0039 | 0.0007 | -0.0008 | 0.0127 | -0.0096 | -0.0174 | -360.1465 | 17.5835 | -360.565 | 17.9366 | -360.9035 | 18.1625 | -361.0266 | 17.5404 | -352.8598 | 18.7682 | -352.8567 | 16.8053
11:36 | 960 | 19.2996 | 193.2438 | 434.0648 | 440.0874 | -22.1589 | -48.246 | 0.184 | -1.0382 | -8.3315 | -8.1364 | -3.5929 | -4.3357 | 1.3538 | -5.7197 | 0.5818 | 0.6388 | 0.9458 | 0.6872 | -132.0671 | -8.5715 | -1.5417 | -2.7271 | -10.8956 | -9.586 | -1.8315 |  | -5.2177 | -4.7889 | 4.0187 | 3.3716 | 3.3557 | 0.9973 | 10.619 | 14.1101 | 14.685 | 11.0179 | 0.0003 | -0.003 | 0.0008 | 0.0038 | 0.0008 | -0.0001 | 0.0152 | -0.0001 | -0.0215 | -360.1588 | 17.6102 | -360.6327 | 17.9366 | -360.8943 | 18.1563 | -360.9527 | 17.5178 | -352.8783 | 18.8052 | -352.8875 | 16.7848
11:36 | 961 | 19.2963 | 193.1983 | 433.9805 | 440.0757 | -22.175 | -48.3383 | 0.1649 | -1.0212 | -8.2627 | -8.0915 | -3.5725 | -4.3381 | 1.3799 | -5.6704 | 0.5812 | 0.6391 | 0.9507 | 0.6872 | -132.0897 | -8.6306 | -1.6131 | -2.7303 | -10.8911 | -9.7221 | -1.7414 |  | -5.2071 | -4.8014 | 4.0199 | 3.3742 | 3.3553 | 0.9968 | 10.6145 | 14.0993 | 14.6601 | 10.9854 | -0.0001 | -0.003 | 0.0009 | 0.004 | 0.0008 | -0.0005 | 0.0041 | 0.003 | -0.0045 | -360.1373 | 17.6163 | -360.6204 | 17.9531 | -360.9558 | 18.1769 | -360.9589 | 17.5239 | -352.8352 | 18.7949 | -352.9152 | 16.8176
11:36 | 962 | 19.3065 | 193.2193 | 434.031 | 440.1145 | -22.1326 | -48.3459 | 0.2446 | -1.0319 | -8.3674 | -8.1186 | -3.6616 | -4.3084 | 1.4183 | -5.7207 | 0.5823 | 0.6384 | 0.9506 | 0.6885 | -132.0979 | -8.5854 | -1.587 | -2.65 | -10.8958 | -9.6436 | -1.7876 |  | -5.1661 | -4.8052 | 4.0189 | 3.3776 | 3.3613 | 0.9968 | 10.6398 | 14.0847 | 14.6949 | 11.0096 | 0.0001 | -0.0022 | 0.0008 | 0.0035 | 0.0005 | -0.0004 | -0.0066 | -0.0181 | -0.0057 | -360.1127 | 17.5794 | -360.5743 | 17.9407 | -360.9066 | 18.1707 | -360.9927 | 17.5301 | -352.8506 | 18.7703 | -352.8537 | 16.793
11:36 | 963 | 19.357 | 193.2345 | 434.0823 | 440.1294 | -22.1904 | -48.3787 | 0.191 | -1.0056 | -8.3219 | -8.1 | -3.6022 | -4.2623 | 1.4046 | -5.6905 | 0.5835 | 0.6393 | 0.9508 | 0.6883 | -132.1954 | -8.6066 | -1.5071 | -2.7131 | -10.8198 | -9.5046 | -1.7337 |  | -5.2217 | -4.7082 | 4.0199 | 3.381 | 3.3573 | 0.9975 | 10.6342 | 14.0901 | 14.686 | 11.0165 | 0 | -0.0025 | 0.0004 | 0.0035 | 0.0007 | -0.0005 | 0.0191 | -0.0171 | -0.0102 | -360.1835 | 17.6061 | -360.6143 | 17.9387 | -360.8974 | 18.1687 | -360.9835 | 17.5404 | -352.8937 | 18.799 | -352.9029 | 16.7868
11:36 | 964 | 19.2981 | 193.2885 | 434.0111 | 440.14 | -22.1214 | -48.2795 | 0.249 | -0.9843 | -8.2684 | -8.0886 | -3.5222 | -4.3067 | 1.4731 | -5.6029 | 0.5821 | 0.6398 | 0.949 | 0.6879 | -132.1953 | -8.6415 | -1.5693 | -2.6574 | -10.8528 | -9.6078 | -1.7938 |  | -5.2291 | -4.7595 | 4.0191 | 3.3743 | 3.357 | 0.996 | 10.6226 | 14.09 | 14.6676 | 10.9649 | -0.0001 | -0.003 | 0.0007 | 0.0039 | 0.0004 | -0.0007 | -0.0021 | -0.007 | -0.0108 | -360.1927 | 17.5978 | -360.5866 | 17.9551 | -360.9189 | 18.1481 | -360.9497 | 17.5404 | -352.8444 | 18.7908 | -352.8937 | 16.7827
11:36 | 965 | 19.2375 | 193.1876 | 434.0033 | 440.0015 | -22.0933 | -48.2637 | 0.3235 | -1.0208 | -8.3641 | -8.0916 | -3.5944 | -4.3071 | 1.4049 | -5.6112 | 0.5821 | 0.6352 | 0.9454 | 0.6871 | -132.2535 | -8.6976 | -1.5483 | -2.6665 | -10.7857 | -9.5449 | -1.7733 |  | -5.227 | -4.8559 | 4.0191 | 3.3762 | 3.3606 | 0.9963 | 10.626 | 14.0647 | 14.6554 | 10.9908 | 0 | -0.0032 | 0.0006 | 0.0034 | 0.0008 | -0.0001 | -0.0009 | -0.0075 | -0.0191 | -360.1373 | 17.5958 | -360.605 | 17.9448 | -360.9158 | 18.1789 | -360.9897 | 17.5137 | -352.8444 | 18.7949 | -352.8844 | 16.8012
11:36 | 966 | 19.3256 | 193.2223 | 434.1466 | 440.1321 | -22.0974 | -48.2691 | 0.2364 | -1.005 | -8.3285 | -8.0918 | -3.6567 | -4.3944 | 1.328 | -5.6885 | 0.5816 | 0.6375 | 0.95 | 0.6875 | -132.2318 | -8.7129 | -1.572 | -2.6629 | -10.761 | -9.5032 | -1.7558 |  | -5.2567 | -4.758 | 4.0201 | 3.3722 | 3.3628 | 0.9967 | 10.5904 | 14.0746 | 14.6614 | 10.9739 | -0.0005 | -0.0031 | 0.0005 | 0.0038 | 0.0008 | -0.0011 | 0.0047 | 0.0027 | -0.0102 | -360.1373 | 17.5917 | -360.5958 | 17.9654 | -360.9189 | 18.1769 | -361.0081 | 17.5383 | -352.8629 | 18.7826 | -352.8752 | 16.795
11:36 | 967 | 19.3627 | 193.3269 | 434.0604 | 440.0854 | -22.0945 | -48.3115 | 0.2883 | -0.9856 | -8.3178 | -8.142 | -3.6142 | -4.338 | 1.4192 | -5.6755 | 0.5816 | 0.6359 | 0.9527 | 0.6871 | -132.2306 | -8.6765 | -1.5354 | -2.6877 | -10.861 | -9.716 | -1.7358 |  | -5.2267 | -4.7928 | 4.0199 | 3.3764 | 3.358 | 0.9971 | 10.5902 | 14.0867 | 14.6772 | 10.9955 | -0.0006 | -0.003 | 0.0011 | 0.0039 | 0.0004 | -0.0004 | 0.008 | -0.0071 | -0.0084 | -360.125 | 17.5876 | -360.6081 | 17.949 | -360.9158 | 18.1707 | -360.9774 | 17.5219 | -352.8567 | 18.7826 | -352.8844 | 16.7909
11:36 | 968 | 19.3658 | 193.2856 | 434.0027 | 440.1213 | -22.1412 | -48.2746 | 0.2388 | -0.9735 | -8.3294 | -8.181 | -3.6167 | -4.3235 | 1.4115 | -5.6504 | 0.5816 | 0.6374 | 0.9522 | 0.6885 | -132.1669 | -8.5876 | -1.5626 | -2.5539 | -10.8175 | -9.5528 | -1.7445 |  | -5.2587 | -4.7365 | 4.0205 | 3.3747 | 3.3577 | 0.9959 | 10.627 | 14.1009 | 14.6994 | 10.9854 | 0.0001 | -0.0031 | 0.0006 | 0.004 | 0.0005 | -0.0006 | -0.0015 | -0.0065 | -0.0049 | -360.1742 | 17.604 | -360.6143 | 17.9777 | -360.9435 | 18.1687 | -360.9989 | 17.5445 | -352.8506 | 18.7805 | -352.9183 | 16.7991
11:36 | 969 | 19.3068 | 193.2691 | 434.0796 | 440.1732 | -22.0948 | -48.236 | 0.3688 | -0.9732 | -8.3604 | -8.1126 | -3.6509 | -4.4517 | 1.421 | -5.6265 | 0.581 | 0.6375 | 0.9495 | 0.6876 | -132.1695 | -8.6168 | -1.5289 | -2.6556 | -10.8224 | -9.5432 | -1.8014 |  | -5.2073 | -4.702 | 4.0207 | 3.378 | 3.3576 | 0.9967 | 10.6167 | 14.0844 | 14.6581 | 11.0219 | 0.0005 | -0.0031 | 0.0011 | 0.0045 | 0.0001 | -0.0008 | -0.0056 | -0.0216 | -0.0087 | -360.1188 | 17.5978 | -360.5804 | 17.9448 | -360.8881 | 18.1461 | -360.9866 | 17.5157 | -352.8229 | 18.7744 | -352.8691 | 16.7827
11:36 | 970 | 19.3557 | 193.2047 | 434.1505 | 440.1889 | -22.0378 | -48.203 | 0.3592 | -0.8785 | -8.2807 | -8.1891 | -3.6007 | -4.3302 | 1.5053 | -5.5772 | 0.5817 | 0.6384 | 0.9527 | 0.6895 | -132.2572 | -8.6501 | -1.4769 | -2.5706 | -10.8444 | -9.5613 | -1.7737 |  | -5.1967 | -4.7768 | 4.019 | 3.3783 | 3.3578 | 0.9953 | 10.627 | 14.0952 | 14.7178 | 11.0023 | 0.0001 | -0.0029 | 0.0011 | 0.0038 | 0.0007 | -0.0003 | -0.0037 | -0.0138 | -0.008 | -360.1835 | 17.604 | -360.6173 | 17.9674 | -360.922 | 18.1604 | -361.002 | 17.5424 | -352.8691 | 18.7908 | -352.8998 | 16.8156
11:36 | 971 | 19.3891 | 193.2253 | 433.9897 | 440.1605 | -22.0383 | -48.2475 | 0.3348 | -0.9403 | -8.3435 | -8.0912 | -3.6528 | -4.3213 | 1.4753 | -5.6028 | 0.5799 | 0.6377 | 0.9521 | 0.6878 | -132.3227 | -8.6223 | -1.5037 | -2.6395 | -10.8465 | -9.5075 | -1.7723 |  | -5.1705 | -4.8123 | 4.0195 | 3.3791 | 3.3602 | 0.9979 | 10.6318 | 14.1168 | 14.7133 | 11.0428 | -0.0005 | -0.0028 | 0.0004 | 0.0038 | 0.0007 | -0.0004 | 0.0021 | -0.0066 | -0.016 | -360.125 | 17.5773 | -360.5527 | 17.9387 | -360.9066 | 18.1399 | -360.9558 | 17.5137 | -352.8198 | 18.7682 | -352.8506 | 16.7827
11:36 | 972 | 19.3954 | 193.2355 | 434.0639 | 440.1325 | -22.0121 | -48.101 | 0.2999 | -0.9799 | -8.4105 | -8.0849 | -3.5747 | -4.2959 | 1.4266 | -5.6411 | 0.5812 | 0.6371 | 0.9498 | 0.6884 | -132.2373 | -8.6559 | -1.544 | -2.6122 | -10.823 | -9.5031 | -1.7556 |  | -5.2253 | -4.7761 | 4.0202 | 3.3755 | 3.3557 | 0.9984 | 10.6111 | 14.0725 | 14.6376 | 10.9768 | -0.0003 | -0.0031 | 0.0004 | 0.0034 | 0.0005 | -0.0004 | -0.0012 | -0.0047 | -0.0147 | -360.2081 | 17.5876 | -360.6204 | 17.9674 | -360.9312 | 18.1584 | -361.0081 | 17.5527 | -352.9183 | 18.7928 | -352.8629 | 16.8053
11:36 | 973 | 19.3172 | 193.2473 | 434.0419 | 440.0603 | -22.1504 | -48.2123 | 0.2366 | -0.9877 | -8.3545 | -8.1628 | -3.6096 | -4.3975 | 1.3464 | -5.6123 | 0.5816 | 0.6373 | 0.9498 | 0.6877 | -132.1824 | -8.6629 | -1.5746 | -2.6045 | -10.8327 | -9.4853 | -1.6985 |  | -5.188 | -4.7246 | 4.0211 | 3.3764 | 3.3593 | 0.9964 | 10.6237 | 14.0566 | 14.67 | 10.9829 | -0.0001 | -0.0033 | 0.0007 | 0.0037 | 0.0008 | -0.0009 | 0.0043 | -0.021 | -0.0199 | -360.1619 | 17.5937 | -360.5896 | 17.9284 | -360.8697 | 18.1399 | -360.9774 | 17.5157 | -352.8044 | 18.7846 | -352.8506 | 16.7724
11:36 | 974 | 19.3944 | 193.2136 | 434.0929 | 440.1605 | -22.1072 | -48.2545 | 0.3279 | -0.972 | -8.3795 | -8.2167 | -3.6465 | -4.3829 | 1.3974 | -5.6265 | 0.5812 | 0.6364 | 0.95 | 0.6876 | -132.158 | -8.5765 | -1.574 | -2.6221 | -10.7499 | -9.5576 | -1.7828 |  | -5.2716 | -4.8712 | 4.0198 | 3.3769 | 3.3576 | 0.9969 | 10.5742 | 14.07 | 14.6396 | 10.9981 | 0 | -0.003 | 0.0003 | 0.0035 | 0.0005 | -0.0007 | 0.0027 | -0.0075 | -0.0106 | -360.1619 | 17.6061 | -360.645 | 17.988 | -360.9589 | 18.1358 | -360.9774 | 17.5383 | -352.8752 | 18.7949 | -352.8998 | 16.8279
11:36 | 975 | 19.3966 | 193.2267 | 434.1425 | 440.2289 | -22.1046 | -48.3976 | 0.2346 | -0.8965 | -8.3091 | -8.1145 | -3.609 | -4.4084 | 1.3829 | -5.5697 | 0.5817 | 0.6381 | 0.95 | 0.6884 | -132.1117 | -8.6237 | -1.4901 | -2.6829 | -10.8485 | -9.6678 | -1.779 |  | -5.1702 | -4.7265 | 4.0187 | 3.3743 | 3.3567 | 0.9973 | 10.5532 | 14.0148 | 14.6329 | 10.9533 | -0.0001 | -0.0026 | 0.0007 | 0.0042 | 0.0011 | -0.0004 | 0.0071 | -0.0096 | -0.0005 | -360.1004 | 17.5773 | -360.5866 | 17.9572 | -360.9281 | 18.1399 | -360.962 | 17.5013 | -352.8137 | 18.7723 | -352.906 | 16.8074
11:36 | 976 | 19.3821 | 193.2021 | 434.1012 | 440.2358 | -22.1846 | -48.3496 | 0.1573 | -0.8714 | -8.3281 | -8.177 | -3.5898 | -4.3644 | 1.3854 | -5.5233 | 0.5807 | 0.6356 | 0.9505 | 0.6877 | -132.1954 | -8.7211 | -1.5523 | -2.755 | -10.8016 | -9.6227 | -1.7841 |  | -5.1635 | -4.7735 | 4.02 | 3.3785 | 3.3571 | 0.9983 | 10.6237 | 14.0856 | 14.6826 | 10.9998 | 0 | -0.0024 | 0.0007 | 0.0038 | 0.0008 | 0 | 0.0084 | -0.0096 | -0.0096 | -360.1896 | 17.5896 | -360.6143 | 17.9715 | -360.9404 | 18.1563 | -360.9927 | 17.5404 | -352.8844 | 18.7908 | -352.8752 | 16.8074
11:36 | 977 | 19.4606 | 193.179 | 434.1654 | 440.2086 | -22.1448 | -48.2847 | 0.0573 | -0.8425 | -8.3792 | -8.1285 | -3.5961 | -4.3927 | 1.4197 | -5.5126 | 0.5821 | 0.6362 | 0.9512 | 0.6872 | -132.064 | -8.6194 | -1.5945 | -2.7812 | -10.8173 | -9.5472 | -1.8091 |  | -5.1695 | -4.7678 | 4.0201 | 3.3768 | 3.3583 | 0.9993 | 10.6007 | 14.1026 | 14.6621 | 10.9894 | 0.0001 | -0.0029 | 0.0005 | 0.004 | 0.0003 | -0.0007 | 0.0151 | -0.0055 | -0.0053 | -360.1404 | 17.5896 | -360.5804 | 17.9264 | -360.8666 | 18.1296 | -360.9774 | 17.5465 | -352.8567 | 18.7846 | -352.866 | 16.7807
11:36 | 978 | 19.4329 | 193.2392 | 434.237 | 440.1719 | -22.1809 | -48.3494 | 0.1889 | -0.8326 | -8.3518 | -8.074 | -3.6679 | -4.3898 | 1.4112 | -5.5268 | 0.5822 | 0.6349 | 0.9498 | 0.6876 | -132.1575 | -8.623 | -1.5581 | -2.7665 | -10.8387 | -9.4645 | -1.8352 |  | -5.2379 | -4.8095 | 4.0184 | 3.3758 | 3.3561 | 0.9979 | 10.6317 | 14.0997 | 14.6922 | 11.0074 | 0 | -0.0029 | 0.0008 | 0.0038 | 0.0008 | -0.0004 | 0.0093 | -0.0168 | -0.0043 | -360.1958 | 17.6286 | -360.6389 | 17.9654 | -360.922 | 18.1194 | -360.9558 | 17.5568 | -352.9337 | 18.8134 | -352.9244 | 16.7991
11:36 | 979 | 19.3796 | 193.1639 | 434.1209 | 440.1359 | -22.216 | -48.3679 | 0.1871 | -0.8628 | -8.3482 | -8.1268 | -3.6776 | -4.3562 | 1.4605 | -5.4611 | 0.581 | 0.6359 | 0.9495 | 0.6887 | -132.1015 | -8.5459 | -1.4889 | -2.75 | -10.8765 | -9.5849 | -1.8302 |  | -5.2471 | -4.7544 | 4.0188 | 3.3773 | 3.3603 | 0.9988 | 10.6318 | 14.0936 | 14.7017 | 11.0139 | 0 | -0.0028 | 0.0004 | 0.0034 | 0.0005 | -0.0005 | 0.0065 | 0.004 | -0.0129 | -360.1219 | 17.5814 | -360.6019 | 17.9592 | -360.9004 | 18.1235 | -360.9527 | 17.5342 | -352.8044 | 18.7661 | -352.8537 | 16.8115
11:36 | 980 | 19.4154 | 193.1971 | 434.1248 | 440.1433 | -22.1305 | -48.2384 | 0.2371 | -0.8612 | -8.354 | -8.1743 | -3.6764 | -4.2797 | 1.4243 | -5.5514 | 0.5808 | 0.6351 | 0.9482 | 0.6878 | -132.1824 | -8.6196 | -1.5459 | -2.753 | -10.8126 | -9.5321 | -1.7507 |  | -5.2457 | -4.7424 | 4.02 | 3.3776 | 3.358 | 0.9981 | 10.6285 | 14.0956 | 14.6781 | 11.0115 | -0.0006 | -0.0028 | 0.0008 | 0.0036 | 0.0007 | -0.0008 | 0.001 | -0.0068 | -0.0105 | -360.1465 | 17.5814 | -360.5773 | 17.9613 | -360.9466 | 18.1748 | -361.0081 | 17.5547 | -352.8906 | 18.7785 | -352.8475 | 16.8074
11:36 | 981 | 19.4542 | 193.1588 | 434.163 | 440.1882 | -22.1752 | -48.238 | 0.2433 | -0.847 | -8.3674 | -8.1412 | -3.6728 | -4.3118 | 1.4421 | -5.5784 | 0.5806 | 0.6376 | 0.946 | 0.6897 | -132.1249 | -8.6874 | -1.5454 | -2.7365 | -10.8712 | -9.5641 | -1.7508 |  | -5.1549 | -4.7697 | 4.0182 | 3.3765 | 3.3574 | 0.9999 | 10.596 | 14.0692 | 14.6587 | 10.9555 | 0 | -0.0027 | 0.001 | 0.0039 | 0.0003 | -0.0007 | 0.0017 | -0.0122 | -0.0139 | -360.1496 | 17.5712 | -360.5404 | 17.912 | -360.8789 | 18.1337 | -360.9927 | 17.5609 | -352.8506 | 18.7641 | -352.826 | 16.7642
11:36 | 982 | 19.3627 | 193.2483 | 434.1109 | 440.152 | -22.1853 | -48.2651 | 0.2157 | -0.8258 | -8.3529 | -8.1762 | -3.5857 | -4.3202 | 1.4324 | -5.5525 | 0.5797 | 0.6353 | 0.9501 | 0.6882 | -132.1767 | -8.6187 | -1.5561 | -2.7295 | -10.8659 | -9.5442 | -1.8156 |  | -5.1121 | -4.7077 | 4.018 | 3.3734 | 3.3597 | 0.9978 | 10.5984 | 14.0713 | 14.6709 | 10.9873 | -0.0001 | -0.0032 | 0.0005 | 0.0037 | 0.0003 | -0.001 | 0.0022 | -0.0051 | -0.0004 | -360.205 | 17.6102 | -360.6296 | 17.9448 | -360.9066 | 18.1317 | -360.9743 | 17.5629 | -352.8691 | 18.799 | -352.8998 | 16.8012
11:36 | 983 | 19.3439 | 193.194 | 434.123 | 440.1105 | -22.0396 | -48.1359 | 0.3604 | -0.8808 | -8.3928 | -8.1373 | -3.6886 | -4.3934 | 1.2897 | -5.705 | 0.5821 | 0.6388 | 0.9501 | 0.6892 | -132.031 | -8.5995 | -1.397 | -2.7173 | -10.882 | -9.5904 | -1.7899 |  | -5.0972 | -4.7539 | 4.02 | 3.3736 | 3.3607 | 0.9965 | 10.595 | 14.0329 | 14.66 | 10.9729 | -0.0003 | -0.0033 | 0.0006 | 0.004 | 0.0003 | -0.0006 | 0.0014 | -0.0123 | -0.0186 | -360.1096 | 17.5671 | -360.5989 | 17.9592 | -360.9435 | 18.1255 | -360.9158 | 17.5096 | -352.8075 | 18.7661 | -352.8906 | 16.8176
11:36 | 984 | 19.4384 | 193.1966 | 434.1929 | 440.2003 | -22.0113 | -48.1533 | 0.4043 | -0.9429 | -8.42 | -8.1326 | -3.6543 | -4.4839 | 1.2455 | -5.6416 | 0.5817 | 0.6365 | 0.9481 | 0.6877 | -132.1582 | -8.5948 | -1.4922 | -2.7798 | -10.8795 | -9.5796 | -1.8539 |  | -5.1171 | -4.7654 | 4.0199 | 3.3767 | 3.3599 | 0.9973 | 10.6109 | 14.0904 | 14.6765 | 10.9926 | 0.0002 | -0.0024 | 0.0008 | 0.004 | 0.0008 | -0.0007 | -0.0028 | -0.0021 | -0.0001 | -360.1127 | 17.5814 | -360.6143 | 17.9674 | -360.9681 | 18.1707 | -361.0081 | 17.5424 | -352.8691 | 18.7785 | -352.9091 | 16.8238
11:36 | 985 | 19.372 | 193.2335 | 434.1428 | 440.1675 | -22.0987 | -48.2071 | 0.4121 | -0.9676 | -8.4291 | -7.9924 | -3.6361 | -4.3279 | 1.3928 | -5.549 | 0.5825 | 0.6353 | 0.9501 | 0.688 | -132.1331 | -8.4896 | -1.3921 | -2.7228 | -10.7643 | -9.4573 | -1.719 |  | -5.1255 | -4.6408 | 4.0183 | 3.3762 | 3.3606 | 0.9987 | 10.5984 | 14.0944 | 14.6362 | 10.9815 | -0.0004 | -0.0029 | 0 | 0.0033 | 0.0004 | -0.0001 | 0.002 | 0.0009 | 0.0058 | -360.1588 | 17.5835 | -360.5435 | 17.9182 | -360.8881 | 18.1235 | -360.9835 | 17.5568 | -352.8475 | 18.7579 | -352.8352 | 16.7848
11:36 | 986 | 19.3896 | 193.247 | 434.1635 | 440.1354 | -22.1331 | -48.2501 | 0.3429 | -0.9293 | -8.3665 | -8.0336 | -3.6635 | -4.3583 | 1.3761 | -5.5088 | 0.5821 | 0.636 | 0.9517 | 0.6889 | -132.1799 | -8.5435 | -1.4062 | -2.8056 | -10.7789 | -9.5172 | -1.76 |  | -5.1204 | -4.6004 | 4.0182 | 3.3763 | 3.3574 | 0.9968 | 10.6134 | 14.0748 | 14.6751 | 10.9847 | 0.0001 | -0.0029 | 0.0007 | 0.0041 | 0.0003 | -0.0009 | 0.0074 | -0.0128 | -0.0031 | -360.205 | 17.6286 | -360.6389 | 17.9469 | -360.9035 | 18.1173 | -360.9651 | 17.5691 | -352.906 | 18.8031 | -352.9367 | 16.8074
11:36 | 987 | 19.4183 | 193.2692 | 434.1893 | 440.1831 | -22.1364 | -48.3013 | 0.3305 | -1.051 | -8.4243 | -8.0969 | -3.6664 | -4.296 | 1.4312 | -5.4947 | 0.5832 | 0.6359 | 0.9545 | 0.6886 | -132.1353 | -8.641 | -1.489 | -2.8042 | -10.7676 | -9.6096 | -1.7204 |  | -5.1444 | -4.715 | 4.0182 | 3.3719 | 3.357 | 0.998 | 10.633 | 14.1005 | 14.6673 | 11.0269 | 0 | -0.0033 | 0.0004 | 0.0029 | 0.0007 | -0.0001 | 0.0105 | -0.0112 | -0.013 | -360.1496 | 17.5937 | -360.5958 | 17.9366 | -360.9312 | 18.1112 | -360.9127 | 17.5342 | -352.8506 | 18.7703 | -352.8906 | 16.8032
11:36 | 988 | 19.3781 | 193.2477 | 434.1424 | 440.2086 | -22.0879 | -48.0755 | 0.3452 | -1.1297 | -8.4046 | -8.1611 | -3.639 | -4.2409 | 1.3691 | -5.5188 | 0.5806 | 0.6341 | 0.9523 | 0.6878 | -132.1142 | -8.5626 | -1.5311 | -2.8023 | -10.8386 | -9.4876 | -1.8043 |  | -5.1502 | -4.7142 | 4.0188 | 3.379 | 3.3576 | 0.9982 | 10.6043 | 14.1001 | 14.6815 | 10.9992 | -0.0007 | -0.0031 | 0.0005 | 0.0034 | 0 | -0.0007 | 0.013 | -0.0076 | -0.0061 | -360.1188 | 17.5814 | -360.5866 | 17.951 | -360.9712 | 18.1666 | -360.9989 | 17.5547 | -352.8537 | 18.7703 | -352.8967 | 16.8074
11:36 | 989 | 19.2949 | 193.2302 | 434.1776 | 440.2377 | -22.082 | -48.2169 | 0.3781 | -1.0258 | -8.2855 | -8.0058 | -3.6704 | -4.2058 | 1.324 | -5.5355 | 0.5816 | 0.6407 | 0.9509 | 0.6878 | -132.0861 | -8.5466 | -1.4244 | -2.8788 | -10.8332 | -9.6723 | -1.7977 |  | -5.1231 | -4.725 | 4.0171 | 3.3743 | 3.3575 | 0.9978 | 10.5879 | 14.067 | 14.6976 | 10.976 | -0.0002 | -0.0027 | 0.0012 | 0.004 | 0.001 | -0.0008 | 0.0134 | -0.0132 | -0.0224 | -360.1219 | 17.5547 | -360.5343 | 17.8997 | -360.8912 | 18.1522 | -361.0081 | 17.5671 | -352.866 | 18.7477 | -352.7983 | 16.754
11:36 | 990 | 19.3559 | 193.2462 | 434.2545 | 440.3302 | -22.0992 | -48.1693 | 0.445 | -0.9714 | -8.3315 | -8.0505 | -3.6483 | -4.3449 | 1.3508 | -5.5024 | 0.5813 | 0.6389 | 0.9496 | 0.6884 | -132.0615 | -8.6065 | -1.5361 | -2.8592 | -10.7155 | -9.4866 | -1.8148 |  | -5.1251 | -4.7679 | 4.0185 | 3.3732 | 3.3588 | 0.9981 | 10.6214 | 14.0889 | 14.7078 | 11.0212 | -0.0002 | -0.003 | 0.0007 | 0.0034 | 0.0004 | -0.0005 | 0.0004 | -0.0198 | -0.0218 | -360.1773 | 17.5917 | -360.605 | 17.9325 | -360.9066 | 18.1522 | -361.0112 | 17.5609 | -352.8937 | 18.7908 | -352.8906 | 16.7868
11:36 | 991 | 19.3812 | 193.3034 | 434.115 | 440.3355 | -22.1449 | -48.1624 | 0.3885 | -0.9398 | -8.318 | -8.1374 | -3.6697 | -4.2983 | 1.3912 | -5.4406 | 0.5811 | 0.6359 | 0.9524 | 0.6884 | -132.1218 | -8.536 | -1.4975 | -2.7994 | -10.7362 | -9.6157 | -1.7813 |  | -5.179 | -4.7701 | 4.0185 | 3.3755 | 3.3551 | 1.0001 | 10.6134 | 14.0981 | 14.6993 | 11.019 | -0.0001 | -0.0032 | 0.0007 | 0.0037 | 0.0009 | -0.0011 | 0.0134 | -0.0147 | -0.0123 | -360.125 | 17.5855 | -360.6481 | 17.9572 | -360.9743 | 18.1276 | -360.9127 | 17.5239 | -352.826 | 18.7744 | -352.906 | 16.7991
11:36 | 992 | 19.3661 | 193.3013 | 434.1445 | 440.336 | -22.0764 | -48.1248 | 0.4311 | -1.0313 | -8.3465 | -8.1899 | -3.6743 | -4.3637 | 1.3781 | -5.4895 | 0.5811 | 0.6354 | 0.9523 | 0.6886 | -132.0174 | -8.5991 | -1.4067 | -2.807 | -10.8026 | -9.6067 | -1.7741 |  | -5.1361 | -4.6717 | 4.0173 | 3.375 | 3.3576 | 0.9993 | 10.6295 | 14.0856 | 14.6768 | 11.0229 | -0.0003 | -0.0032 | 0.0006 | 0.004 | 0.0006 | -0.0002 | -0.0083 | -0.0016 | -0.0268 | -360.0942 | 17.5773 | -360.6389 | 17.9551 | -360.9527 | 18.1543 | -360.9497 | 17.5178 | -352.8475 | 18.7723 | -352.8844 | 16.8217
11:36 | 993 | 19.352 | 193.2132 | 434.1458 | 440.1759 | -22.0838 | -48.1936 | 0.4582 | -0.9768 | -8.2415 | -8.1084 | -3.6141 | -4.3367 | 1.3985 | -5.4332 | 0.5831 | 0.6354 | 0.9492 | 0.6893 | -132.0936 | -8.6587 | -1.4426 | -2.8277 | -10.7928 | -9.6874 | -1.8105 |  | -5.12 | -4.7218 | 4.018 | 3.379 | 3.3541 | 0.9974 | 10.6282 | 14.1252 | 14.7065 | 11.0269 | -0.0001 | -0.0024 | 0.0002 | 0.0033 | 0.001 | -0.0009 | 0.0053 | 0.0037 | -0.0075 | -360.1773 | 17.5814 | -360.5866 | 17.9428 | -360.9097 | 18.1563 | -361.0143 | 17.5629 | -352.8537 | 18.7703 | -352.8691 | 16.7724
11:36 | 994 | 19.4151 | 193.3599 | 434.1322 | 440.2926 | -22.0476 | -48.1319 | 0.4805 | -0.9499 | -8.3224 | -8.1651 | -3.6462 | -4.2935 | 1.3983 | -5.3988 | 0.5809 | 0.638 | 0.9513 | 0.6885 | -132.1108 | -8.6507 | -1.5323 | -2.7105 | -10.7849 | -9.5381 | -1.8039 |  | -5.1283 | -4.6763 | 4.0183 | 3.3745 | 3.3548 | 0.9981 | 10.6019 | 14.0748 | 14.6982 | 10.9732 | -0.0006 | -0.0033 | 0.0006 | 0.0036 | 0.0001 | -0.0006 | 0.0117 | 0.0023 | -0.0286 | -360.1681 | 17.5835 | -360.5804 | 17.9161 | -360.8635 | 18.1194 | -360.9897 | 17.565 | -352.9091 | 18.7805 | -352.8567 | 16.7581
11:36 | 995 | 19.3032 | 193.2624 | 434.1495 | 440.206 | -22.038 | -48.1961 | 0.4203 | -0.974 | -8.3312 | -8.1373 | -3.5952 | -4.3518 | 1.4174 | -5.4501 | 0.5817 | 0.6355 | 0.9509 | 0.6885 | -132.0783 | -8.5124 | -1.4181 | -2.7036 | -10.7349 | -9.4839 | -1.7135 |  | -5.1968 | -4.6639 | 4.0181 | 3.3773 | 3.358 | 0.9985 | 10.5994 | 14.1017 | 14.6686 | 10.9529 | 0 | -0.0032 | 0.0005 | 0.0035 | 0.0007 | -0.0004 | 0.014 | -0.0044 | -0.015 | -360.1927 | 17.6122 | -360.605 | 17.9366 | -360.9312 | 18.1379 | -360.9497 | 17.5609 | -352.9244 | 18.7867 | -352.8906 | 16.7807
11:36 | 996 | 19.4845 | 193.2877 | 434.1675 | 440.3238 | -22.0708 | -48.1791 | 0.4284 | -1.0294 | -8.2975 | -8.059 | -3.6314 | -4.3615 | 1.4042 | -5.5148 | 0.5821 | 0.6383 | 0.9526 | 0.6887 | -132.0476 | -8.5813 | -1.4659 | -2.6717 | -10.7927 | -9.5522 | -1.8091 |  | -5.1681 | -4.6619 | 4.0171 | 3.3758 | 3.3564 | 0.9991 | 10.604 | 14.1122 | 14.6625 | 10.963 | 0.0001 | -0.0029 | 0.0007 | 0.0037 | 0.0004 | -0.0005 | 0.0051 | -0.0083 | -0.0135 | -360.1219 | 17.5732 | -360.5804 | 17.9469 | -360.9097 | 18.1317 | -360.9558 | 17.528 | -352.8075 | 18.762 | -352.8937 | 16.795
11:36 | 997 | 19.4327 | 193.299 | 434.1646 | 440.2725 | -21.9431 | -48.1092 | 0.4364 | -1.0559 | -8.3522 | -8.2888 | -3.6927 | -4.4269 | 1.3278 | -5.5432 | 0.5813 | 0.6367 | 0.9524 | 0.6884 | -132.0835 | -8.5522 | -1.4994 | -2.5934 | -10.8177 | -9.5169 | -1.8128 |  | -5.1095 | -4.5337 | 4.0179 | 3.3756 | 3.3541 | 0.9989 | 10.6041 | 14.0714 | 14.6836 | 10.9753 | -0.0005 | -0.0027 | 0.001 | 0.0038 | 0.0003 | -0.0007 | 0.0074 | -0.0004 | 0.0128 | -360.1681 | 17.5671 | -360.5773 | 17.951 | -360.9527 | 18.1645 | -361.0143 | 17.5465 | -352.8691 | 18.7497 | -352.8537 | 16.7971
11:36 | 998 | 19.4195 | 193.3431 | 434.214 | 440.3143 | -22.0209 | -48.1315 | 0.4326 | -0.9668 | -8.3185 | -8.278 | -3.6056 | -4.3602 | 1.5312 | -5.4933 | 0.5816 | 0.634 | 0.9518 | 0.6886 | -132.0515 | -8.6107 | -1.4989 | -2.6931 | -10.7611 | -9.4849 | -1.8206 |  | -5.1187 | -4.5523 | 4.0178 | 3.3777 | 3.3575 | 0.9988 | 10.612 | 14.08 | 14.6953 | 11.0283 | 0 | -0.0023 | 0.0014 | 0.004 | 0.0009 | -0.0007 | 0.0118 | -0.0197 | -0.0248 | -360.1742 | 17.5609 | -360.5712 | 17.9407 | -360.8974 | 18.1317 | -360.9835 | 17.5465 | -352.8352 | 18.7477 | -352.8629 | 16.7766
11:36 | 999 | 19.4498 | 193.3208 | 434.1906 | 440.2668 | -22.0297 | -48.1026 | 0.4474 | -0.9706 | -8.3539 | -8.2926 | -3.6573 | -4.2815 | 1.4187 | -5.5952 | 0.5809 | 0.6363 | 0.9536 | 0.6885 | -132.0223 | -8.6426 | -1.4808 | -2.8309 | -10.8342 | -9.6015 | -1.8139 |  | -5.1349 | -4.6598 | 4.0178 | 3.3791 | 3.3568 | 0.9994 | 10.5938 | 14.0667 | 14.6607 | 10.9595 | -0.0002 | -0.0031 | 0.0005 | 0.0037 | 0.0003 | -0.0006 | -0.0082 | -0.0018 | -0.0011 | -360.1896 | 17.602 | -360.6358 | 17.9305 | -360.9035 | 18.1337 | -360.9558 | 17.5486 | -352.9152 | 18.8052 | -352.9152 | 16.7807
11:36 | 1000 | 19.4644 | 193.3619 | 434.2409 | 440.2672 | -22.0664 | -48.1878 | 0.3415 | -0.9615 | -8.344 | -8.2975 | -3.6568 | -4.2907 | 1.4125 | -5.4829 | 0.581 | 0.6341 | 0.9516 | 0.6885 | -132.025 | -8.6976 | -1.4815 | -2.7573 | -10.7569 | -9.4473 | -1.7791 |  | -5.095 | -4.6541 | 4.0175 | 3.3784 | 3.3561 | 0.9994 | 10.6179 | 14.0741 | 14.6826 | 11.0056 | 0.0002 | -0.0029 | 0.0006 | 0.004 | 0.0008 | -0.001 | 0.0153 | -0.0078 | 0.0014 | -360.1681 | 17.5978 | -360.6235 | 17.9572 | -360.9312 | 18.1091 | -360.962 | 17.5363 | -352.8444 | 18.7846 | -352.9244 | 16.8012
11:36 | 1001 | 19.5232 | 193.3471 | 434.17 | 440.3586 | -21.9902 | -48.1755 | 0.4013 | -1.0018 | -8.3796 | -8.2253 | -3.6822 | -4.3267 | 1.3799 | -5.4554 | 0.5814 | 0.6375 | 0.9497 | 0.6872 | -131.9877 | -8.5545 | -1.4645 | -2.8461 | -10.8341 | -9.5698 | -1.8006 |  | -5.1144 | -4.5807 | 4.017 | 3.375 | 3.3576 | 0.999 | 10.604 | 14.1065 | 14.7041 | 11.032 | 0.0001 | -0.0028 | 0.0001 | 0.0033 | 0.0006 | -0.0003 | 0.003 | -0.0134 | -0.0097 | -360.0973 | 17.5712 | -360.5989 | 17.9469 | -360.9312 | 18.1502 | -360.9681 | 17.5363 | -352.8414 | 18.7744 | -352.8967 | 16.7991
11:36 | 1002 | 19.6153 | 193.2791 | 434.2233 | 440.2835 | -21.8955 | -48.1958 | 0.4782 | -0.9164 | -8.3739 | -8.2617 | -3.6223 | -4.3353 | 1.3497 | -5.4343 | 0.582 | 0.6344 | 0.9514 | 0.6873 | -132.0036 | -8.6143 | -1.4345 | -2.7688 | -10.7789 | -9.603 | -1.8428 |  | -5.124 | -4.6734 | 4.0169 | 3.378 | 3.3558 | 0.999 | 10.6008 | 14.0851 | 14.69 | 10.9898 | -0.0004 | -0.003 | 0.0009 | 0.0041 | 0.0005 | -0.0006 | 0.021 | 0.009 | 0.0003 | -360.2019 | 17.5712 | -360.565 | 17.9305 | -360.9404 | 18.1604 | -361.0266 | 17.5712 | -352.8875 | 18.76 | -352.8321 | 16.7807
11:36 | 1003 | 19.5123 | 193.2469 | 434.0948 | 440.2825 | -21.8869 | -48.0085 | 0.4486 | -0.919 | -8.3667 | -8.2423 | -3.603 | -4.3614 | 1.3543 | -5.4771 | 0.5812 | 0.6328 | 0.9487 | 0.6878 | -132.1119 | -8.5371 | -1.3789 | -2.8079 | -10.7783 | -9.7372 | -1.862 |  | -5.2014 | -4.7702 | 4.0165 | 3.3774 | 3.3555 | 0.999 | 10.5982 | 14.0775 | 14.6683 | 10.9977 | 0 | -0.0026 | 0.0012 | 0.004 | 0.0011 | -0.0002 | -0.0068 | -0.0064 | -0.0244 | -360.1681 | 17.5691 | -360.5681 | 17.9099 | -360.8604 | 18.144 | -361.0081 | 17.5568 | -352.8414 | 18.7641 | -352.8414 | 16.7683
11:36 | 1004 | 19.4712 | 193.3016 | 434.1799 | 440.2619 | -21.9177 | -48.0437 | 0.4832 | -0.934 | -8.3792 | -8.2915 | -3.6207 | -4.389 | 1.3432 | -5.4996 | 0.582 | 0.6326 | 0.9491 | 0.6866 | -132.1359 | -8.6078 | -1.5005 | -2.6776 | -10.7135 | -9.5112 | -1.7142 |  | -5.1367 | -4.6872 | 4.0176 | 3.3752 | 3.3542 | 0.9991 | 10.6401 | 14.0897 | 14.7118 | 11.0003 | 0 | -0.0033 | 0.0007 | 0.0033 | 0.0003 | -0.0009 | 0.0215 | -0.0077 | -0.0183 | -360.1742 | 17.5958 | -360.6204 | 17.9551 | -360.9404 | 18.1379 | -360.962 | 17.5506 | -352.9029 | 18.7908 | -352.9152 | 16.8053
11:36 | 1005 | 19.5046 | 193.2727 | 434.2213 | 440.3225 | -21.9183 | -47.9926 | 0.3589 | -0.9749 | -8.3006 | -8.3362 | -3.5861 | -4.336 | 1.3493 | -5.5048 | 0.5818 | 0.6356 | 0.9488 | 0.6875 | -132.0597 | -8.545 | -1.4303 | -2.6435 | -10.67 | -9.5601 | -1.7378 |  | -5.0676 | -4.6296 | 4.016 | 3.3736 | 3.3577 | 0.999 | 10.6121 | 14.0856 | 14.6826 | 10.9998 | 0.0001 | -0.0026 | 0.0012 | 0.0038 | 0.001 | -0.0005 | 0.0038 | 0.0107 | 0.0001 | -360.1342 | 17.5527 | -360.6112 | 17.949 | -360.9497 | 18.1379 | -360.9466 | 17.5137 | -352.8229 | 18.7559 | -352.8967 | 16.8135
11:36 | 1006 | 19.542 | 193.3299 | 434.3633 | 440.391 | -22.021 | -47.9836 | 0.2978 | -0.958 | -8.3389 | -8.2063 | -3.6436 | -4.3135 | 1.2974 | -5.5048 | 0.5819 | 0.633 | 0.9492 | 0.6879 | -132.0696 | -8.5764 | -1.4866 | -2.6574 | -10.7652 | -9.5151 | -1.7792 |  | -5.1432 | -4.6223 | 4.0156 | 3.3758 | 3.3612 | 1.0004 | 10.5983 | 14.0716 | 14.6788 | 11.0154 | -0.0003 | -0.0027 | 0.0006 | 0.0037 | 0.0003 | -0.0006 | 0.0058 | 0.0011 | -0.016 | -360.1558 | 17.5712 | -360.5927 | 17.9366 | -360.9435 | 18.1543 | -360.9651 | 17.5301 | -352.8537 | 18.7744 | -352.8844 | 16.795
11:36 | 1007 | 19.4483 | 193.2972 | 434.1791 | 440.287 | -21.9928 | -48.1592 | 0.4219 | -0.94 | -8.3872 | -8.2157 | -3.56 | -4.2653 | 1.3552 | -5.3927 | 0.5819 | 0.6308 | 0.9476 | 0.6883 | -132.0384 | -8.6696 | -1.4459 | -2.6009 | -10.7657 | -9.4318 | -1.7189 |  | -5.1084 | -4.6965 | 4.0162 | 3.3761 | 3.3603 | 0.9983 | 10.6019 | 14.0863 | 14.6914 | 10.9909 | -0.0008 | -0.003 | 0.0005 | 0.0037 | 0.0006 | -0.0007 | 0.0131 | -0.0124 | -0.0082 | -360.1804 | 17.5773 | -360.5866 | 17.9264 | -360.8789 | 18.1379 | -360.9989 | 17.5609 | -352.8383 | 18.7641 | -352.8721 | 16.7766
11:37 | 1008 | 19.4942 | 193.3507 | 434.1867 | 440.2536 | -21.9395 | -48.125 | 0.3876 | -0.9797 | -8.4216 | -8.2675 | -3.541 | -4.2738 | 1.3839 | -5.4441 | 0.5824 | 0.6315 | 0.9504 | 0.6889 | -132.0008 | -8.6137 | -1.5257 | -2.6524 | -10.8037 | -9.4446 | -1.7184 |  | -5.1324 | -4.6962 | 4.016 | 3.3764 | 3.3554 | 0.999 | 10.6341 | 14.096 | 14.6755 | 11.0103 | 0 | -0.0029 | 0.0006 | 0.0039 | 0.0006 | -0.0003 | 0.0172 | -0.0107 | 0.0103 | -360.1619 | 17.5876 | -360.5989 | 17.914 | -360.882 | 18.1276 | -360.9435 | 17.5445 | -352.9152 | 18.7867 | -352.8875 | 16.7724
11:37 | 1009 | 19.5408 | 193.3298 | 434.1985 | 440.2456 | -21.9337 | -48.0623 | 0.407 | -0.9342 | -8.3082 | -8.1252 | -3.6314 | -4.3799 | 1.3219 | -5.5573 | 0.5822 | 0.6323 | 0.95 | 0.6886 | -131.9816 | -8.5216 | -1.4713 | -2.7255 | -10.7575 | -9.5336 | -1.7213 |  | -5.1683 | -4.7859 | 4.0163 | 3.3738 | 3.3558 | 0.9994 | 10.6308 | 14.1095 | 14.6693 | 11.0194 | -0.0001 | -0.0032 | -0.0001 | 0.0031 | 0.001 | -0.0006 | 0.0055 | -0.0035 | -0.0094 | -360.1588 | 17.5896 | -360.5989 | 17.9407 | -360.9466 | 18.142 | -360.9774 | 17.5568 | -352.8721 | 18.7805 | -352.8967 | 16.8012
11:37 | 1010 | 19.5437 | 193.3532 | 434.2054 | 440.2411 | -22.0515 | -48.1134 | 0.2865 | -1.0036 | -8.2702 | -8.1983 | -3.5693 | -4.2613 | 1.3983 | -5.4043 | 0.5812 | 0.6341 | 0.9517 | 0.6864 | -131.9806 | -8.4693 | -1.5004 | -2.9486 | -10.7163 | -9.4373 | -1.7696 |  | -5.1751 | -4.7678 | 4.0176 | 3.3717 | 3.3538 | 0.9979 | 10.6076 | 14.0575 | 14.6403 | 10.979 | -0.0006 | -0.003 | 0.0007 | 0.0038 | 0.0009 | 0.0002 | 0.0208 | -0.0029 | -0.0127 | -360.1465 | 17.5609 | -360.5619 | 17.9223 | -360.9097 | 18.1502 | -360.9958 | 17.5321 | -352.8383 | 18.7682 | -352.8814 | 16.7909
11:37 | 1011 | 19.523 | 193.3289 | 434.1947 | 440.2862 | -21.9753 | -48.1302 | 0.3623 | -0.9812 | -8.2659 | -8.1342 | -3.6298 | -4.1873 | 1.4162 | -5.3966 | 0.5816 | 0.6332 | 0.9492 | 0.6883 | -132.0304 | -8.5204 | -1.57 | -2.9798 | -10.7097 | -9.4896 | -1.7346 |  | -5.0602 | -4.689 | 4.0167 | 3.3765 | 3.3545 | 0.9982 | 10.6064 | 14.1028 | 14.6989 | 10.9829 | -0.0006 | -0.0031 | 0.0006 | 0.0038 | 0.0006 | -0.0006 | -0.0077 | -0.0078 | 0.0157 | -360.1527 | 17.5527 | -360.565 | 17.9387 | -360.9466 | 18.1625 | -361.0266 | 17.5609 | -352.8906 | 18.76 | -352.8752 | 16.7909
11:37 | 1012 | 19.5367 | 193.2434 | 434.1813 | 440.3324 | -22.0363 | -48.057 | 0.3531 | -0.9062 | -8.2857 | -8.1213 | -3.6259 | -4.2727 | 1.4355 | -5.3918 | 0.5807 | 0.6353 | 0.9515 | 0.6868 | -131.9337 | -8.5483 | -1.5651 | -2.9359 | -10.7986 | -9.5498 | -1.7227 |  | -5.1398 | -4.6391 | 4.0147 | 3.3727 | 3.3585 | 0.9994 | 10.6411 | 14.1144 | 14.7337 | 11.0002 | 0 | -0.0029 | 0.0011 | 0.0038 | 0.0005 | -0.0004 | -0.0034 | -0.0133 | -0.0059 | -360.1588 | 17.5527 | -360.5773 | 17.9161 | -360.8727 | 18.1276 | -360.9866 | 17.5506 | -352.8414 | 18.76 | -352.8352 | 16.7827
11:37 | 1013 | 19.5995 | 193.3801 | 434.2436 | 440.3004 | -22.1006 | -48.1876 | 0.3615 | -0.8914 | -8.3915 | -8.1566 | -3.6899 | -4.3224 | 1.3834 | -5.3931 | 0.5814 | 0.6341 | 0.9499 | 0.6879 | -131.8035 | -8.5648 | -1.5503 | -2.9767 | -10.8543 | -9.5837 | -1.8323 |  | -5.1224 | -4.6356 | 4.0163 | 3.377 | 3.356 | 1.0002 | 10.611 | 14.1076 | 14.687 | 11.0045 | 0.0002 | -0.003 | 0.0008 | 0.0039 | 0.0001 | -0.0008 | 0.0108 | 0.0028 | 0.0038 | -360.205 | 17.5917 | -360.6296 | 17.9264 | -360.9312 | 18.1317 | -360.9558 | 17.5445 | -352.8691 | 18.8031 | -352.8906 | 16.7848
11:37 | 1014 | 19.5771 | 193.3054 | 434.2085 | 440.2767 | -22.1527 | -48.2425 | 0.3267 | -0.9056 | -8.4077 | -8.2498 | -3.7248 | -4.2549 | 1.4723 | -5.4163 | 0.581 | 0.6355 | 0.9489 | 0.6878 | -131.9459 | -8.6903 | -1.5381 | -2.9915 | -10.885 | -9.6851 | -1.856 |  | -5.0879 | -4.6409 | 4.0151 | 3.3722 | 3.3564 | 0.9991 | 10.6215 | 14.0772 | 14.7125 | 10.9811 | -0.0004 | -0.0032 | 0.0002 | 0.0033 | 0.0008 | -0.0013 | 0.0159 | -0.0113 | -0.0157 | -360.1496 | 17.5814 | -360.6389 | 17.9428 | -360.9312 | 18.1091 | -360.9343 | 17.5301 | -352.8414 | 18.7826 | -352.8937 | 16.8012
11:37 | 1015 | 19.6381 | 193.4392 | 434.2529 | 440.3629 | -21.9976 | -48.2508 | 0.2204 | -0.9283 | -8.3612 | -8.2618 | -3.7244 | -4.2618 | 1.5122 | -5.4024 | 0.5806 | 0.6334 | 0.9482 | 0.6884 | -131.906 | -8.7031 | -1.5886 | -2.9438 | -10.8932 | -9.6217 | -1.906 |  | -5.0322 | -4.6327 | 4.0155 | 3.3726 | 3.3556 | 0.9995 | 10.626 | 14.1111 | 14.7375 | 11.002 | -0.0003 | -0.0027 | 0.0007 | 0.004 | 0.0005 | 0 | 0.0076 | -0.0218 | -0.0067 | -360.1527 | 17.5588 | -360.5804 | 17.9223 | -360.922 | 18.1522 | -360.9589 | 17.5363 | -352.8198 | 18.7661 | -352.8691 | 16.793
11:37 | 1016 | 19.6861 | 193.4305 | 434.2507 | 440.3962 | -22.0846 | -48.195 | 0.2183 | -0.8869 | -8.3289 | -8.2038 | -3.6699 | -4.2786 | 1.3874 | -5.4781 | 0.581 | 0.631 | 0.9505 | 0.6873 | -131.8842 | -8.6214 | -1.5695 | -3.0215 | -10.8895 | -9.6003 | -1.9113 |  | -5.0546 | -4.6131 | 4.0154 | 3.373 | 3.3525 | 1.0001 | 10.6099 | 14.0889 | 14.6846 | 11.0096 | -0.0007 | -0.0031 | 0.0007 | 0.004 | 0.0011 | -0.0009 | 0.0151 | -0.016 | -0.0181 | -360.1927 | 17.5629 | -360.5681 | 17.914 | -360.9435 | 18.1625 | -361.0081 | 17.5753 | -352.8752 | 18.7559 | -352.8414 | 16.7766
11:37 | 1017 | 19.6356 | 193.3744 | 434.3213 | 440.3206 | -22.0424 | -48.1912 | 0.2522 | -0.9974 | -8.3188 | -8.1577 | -3.7028 | -4.3932 | 1.3747 | -5.4169 | 0.5806 | 0.6296 | 0.9466 | 0.6864 | -131.8272 | -8.64 | -1.5454 | -2.9857 | -10.8742 | -9.6511 | -1.8698 |  | -5.0506 | -4.5329 | 4.0155 | 3.374 | 3.3602 | 1.0021 | 10.6134 | 14.0923 | 14.6877 | 11.0017 | 0.0001 | -0.003 | 0.0008 | 0.004 | 0.0004 | -0.0006 | 0.013 | -0.0039 | -0.0167 | -360.1404 | 17.5609 | -360.5773 | 17.8976 | -360.8635 | 18.1399 | -360.9989 | 17.5486 | -352.8721 | 18.7785 | -352.8475 | 16.7622
11:37 | 1018 | 19.7177 | 193.4277 | 434.4122 | 440.4397 | -21.998 | -48.1244 | 0.4592 | -0.7725 | -8.221 | -8.0581 | -3.6219 | -4.2865 | 1.4685 | -5.5021 | 0.5806 | 0.6348 | 0.9517 | 0.6872 | -131.8647 | -8.5992 | -1.561 | -2.9168 | -10.8561 | -9.5817 | -1.8499 |  | -5.0525 | -4.4827 | 4.0136 | 3.3739 | 3.3585 | 0.9999 | 10.6075 | 14.0982 | 14.6829 | 11.0013 | 0.0001 | -0.0032 | 0.0006 | 0.0043 | 0.0013 | -0.0004 | -0.0001 | 0.0052 | 0.0068 | -360.1958 | 17.5835 | -360.6389 | 17.9387 | -360.9466 | 18.1461 | -360.9558 | 17.5527 | -352.8906 | 18.7908 | -352.906 | 16.8074
11:37 | 1019 | 19.6926 | 193.4088 | 434.3151 | 440.416 | -21.9793 | -48.1053 | 0.4235 | -0.8699 | -8.2825 | -8.0617 | -3.6702 | -4.4451 | 1.4078 | -5.5817 | 0.5809 | 0.6333 | 0.9528 | 0.6866 | -131.8148 | -8.587 | -1.5932 | -2.9903 | -10.8673 | -9.5834 | -1.9387 |  | -5.1348 | -4.5968 | 4.0152 | 3.3754 | 3.3566 | 1.0019 | 10.5868 | 14.0771 | 14.6825 | 10.9873 | -0.0004 | -0.003 | 0.0005 | 0.0034 | 0.0005 | -0.0008 | 0.0153 | -0.0117 | -0.0172 | -360.1127 | 17.5506 | -360.5896 | 17.9325 | -360.9404 | 18.1337 | -360.9589 | 17.5178 | -352.789 | 18.7559 | -352.8629 | 16.8074
11:37 | 1020 | 19.7011 | 193.3629 | 434.2691 | 440.4006 | -22.0342 | -48.1436 | 0.4108 | -0.8784 | -8.247 | -8.1123 | -3.6077 | -4.4265 | 1.3653 | -5.4586 | 0.5817 | 0.6352 | 0.9515 | 0.6882 | -131.8672 | -8.543 | -1.5625 | -2.9541 | -10.7959 | -9.5024 | -1.8736 |  | -5.0687 | -4.5568 | 4.0129 | 3.3727 | 3.3546 | 1.0005 | 10.6041 | 14.0542 | 14.6557 | 10.9865 | 0 | -0.0024 | 0.0007 | 0.0034 | 0.0005 | -0.0004 | 0.0043 | -0.0068 | -0.0205 | -360.1773 | 17.5732 | -360.5773 | 17.9366 | -360.962 | 18.1522 | -360.9927 | 17.5424 | -352.8906 | 18.7785 | -352.8844 | 16.8012
11:37 | 1021 | 19.7671 | 193.4621 | 434.1699 | 440.3442 | -21.9607 | -48.0942 | 0.2859 | -0.9531 | -8.385 | -8.13 | -3.709 | -4.4727 | 1.3542 | -5.5448 | 0.5816 | 0.6333 | 0.9498 | 0.6878 | -131.7528 | -8.5161 | -1.5779 | -2.9605 | -10.7543 | -9.5231 | -1.9035 |  | -5.1447 | -4.5352 | 4.0139 | 3.3709 | 3.3547 | 1.0002 | 10.5995 | 14.09 | 14.6734 | 11.0053 | 0 | -0.0029 | 0.0008 | 0.0038 | 0.0008 | -0.0007 | 0.0042 | -0.0067 | 0.0041 | -360.1711 | 17.5568 | -360.5681 | 17.9017 | -360.8666 | 18.1194 | -361.002 | 17.5547 | -352.8506 | 18.7641 | -352.8444 | 16.7581
11:37 | 1022 | 19.738 | 193.4483 | 434.3887 | 440.438 | -22.035 | -48.0522 | 0.3226 | -0.9076 | -8.3452 | -8.0715 | -3.6599 | -4.3285 | 1.4367 | -5.4354 | 0.5818 | 0.6309 | 0.9494 | 0.6885 | -131.7749 | -8.5478 | -1.5472 | -2.9539 | -10.718 | -9.5322 | -1.753 |  | -5.1053 | -4.6364 | 4.0149 | 3.3697 | 3.3536 | 1.0003 | 10.6305 | 14.0927 | 14.7024 | 11.0005 | 0.0003 | -0.0029 | 0.0007 | 0.0035 | 0.0007 | -0.0001 | 0.0046 | -0.0075 | -0.0035 | -360.2235 | 17.5876 | -360.6173 | 17.9058 | -360.8727 | 18.0968 | -360.9651 | 17.5568 | -352.9398 | 18.799 | -352.906 | 16.7807
11:37 | 1023 | 19.7561 | 193.4232 | 434.3292 | 440.4213 | -22.0347 | -48.0327 | 0.4265 | -0.8657 | -8.3221 | -8.1422 | -3.6738 | -4.2785 | 1.4608 | -5.4377 | 0.5824 | 0.6284 | 0.9476 | 0.6885 | -131.8164 | -8.4937 | -1.4913 | -3.1054 | -10.7021 | -9.6309 | -1.8193 |  | -4.9928 | -4.6875 | 4.0131 | 3.3727 | 3.3522 | 1.0018 | 10.6307 | 14.1039 | 14.6935 | 10.9728 | -0.0005 | -0.003 | 0.0008 | 0.0036 | 0.0009 | -0.0008 | 0.0015 | -0.0016 | 0.0046 | -360.1958 | 17.565 | -360.5896 | 17.9325 | -360.9158 | 18.0906 | -360.9558 | 17.5568 | -352.8506 | 18.7785 | -352.8875 | 16.7991
11:37 | 1024 | 19.7154 | 193.4071 | 434.305 | 440.4128 | -22.0846 | -48.1706 | 0.2236 | -0.8814 | -8.3404 | -7.9817 | -3.6261 | -4.381 | 1.3705 | -5.4743 | 0.5817 | 0.6345 | 0.95 | 0.688 | -131.8227 | -8.5197 | -1.4841 | -3.059 | -10.6612 | -9.4664 | -1.7038 |  | -5.0448 | -4.6195 | 4.013 | 3.377 | 3.3563 | 1.0017 | 10.6364 | 14.104 | 14.6887 | 11.0013 | -0.0003 | -0.0023 | 0.0008 | 0.0038 | 0 | -0.0007 | 0.0105 | -0.0088 | -0.0268 | -360.1496 | 17.5465 | -360.5835 | 17.9161 | -360.9251 | 18.142 | -360.9866 | 17.5239 | -352.8352 | 18.762 | -352.8598 | 16.7971
11:37 | 1025 | 19.6519 | 193.3026 | 434.3107 | 440.428 | -22.079 | -48.0306 | 0.3294 | -0.9029 | -8.3432 | -8.1267 | -3.5921 | -4.3134 | 1.3769 | -5.4109 | 0.5807 | 0.6329 | 0.9498 | 0.6878 | -131.7953 | -8.5346 | -1.437 | -3.0617 | -10.6964 | -9.4553 | -1.6992 |  | -5.052 | -4.6374 | 4.0137 | 3.3737 | 3.356 | 1.001 | 10.6018 | 14.0692 | 14.6645 | 10.9959 | -0.0002 | -0.0027 | 0.0005 | 0.0039 | 0.0013 | -0.0007 | 0.0116 | -0.0015 | -0.0223 | -360.1865 | 17.5404 | -360.5619 | 17.9182 | -360.922 | 18.1317 | -361.002 | 17.5609 | -352.8629 | 18.7538 | -352.8383 | 16.7868
11:37 | 1026 | 19.7759 | 193.3892 | 434.3257 | 440.5105 | -22.0284 | -48.1365 | 0.3007 | -0.8911 | -8.3264 | -8.0255 | -3.6104 | -4.2157 | 1.3943 | -5.5564 | 0.5821 | 0.6329 | 0.9515 | 0.6863 | -131.8277 | -8.5969 | -1.4586 | -2.8612 | -10.6857 | -9.3129 | -1.7034 |  | -5.0704 | -4.6444 | 4.0143 | 3.3734 | 3.354 | 1.0015 | 10.6179 | 14.0913 | 14.6758 | 11.0118 | 0.0002 | -0.0031 | 0.0009 | 0.0046 | 0.0003 | -0.0004 | 0.0099 | 0.0101 | 0.0136 | -360.1311 | 17.5547 | -360.5896 | 17.9058 | -360.882 | 18.0968 | -360.9989 | 17.5568 | -352.8844 | 18.7744 | -352.8721 | 16.7786
11:37 | 1027 | 19.7932 | 193.3765 | 434.462 | 440.5173 | -21.992 | -48.1135 | 0.3601 | -0.8814 | -8.3464 | -7.9738 | -3.5771 | -4.347 | 1.4316 | -5.5393 | 0.5808 | 0.632 | 0.9501 | 0.6865 | -131.7718 | -8.4839 | -1.469 | -2.9012 | -10.7376 | -9.4562 | -1.7016 |  | -5.0821 | -4.6759 | 4.0136 | 3.3734 | 3.357 | 1.0018 | 10.618 | 14.0738 | 14.6863 | 10.989 | 0.0002 | -0.0028 | 0.0002 | 0.0037 | 0.0005 | -0.0012 | -0.0008 | -0.0162 | -0.0269 | -360.2204 | 17.5876 | -360.6235 | 17.9305 | -360.9466 | 18.0886 | -360.9343 | 17.5527 | -352.8814 | 18.7969 | -352.9029 | 16.7971
11:37 | 1028 | 19.7355 | 193.2687 | 434.3766 | 440.5009 | -21.9717 | -48.1873 | 0.3818 | -0.8613 | -8.2732 | -8.0796 | -3.5729 | -4.252 | 1.4971 | -5.469 | 0.5812 | 0.6335 | 0.9457 | 0.6878 | -131.7449 | -8.5043 | -1.4451 | -2.9483 | -10.6947 | -9.4142 | -1.7433 |  | -5.0638 | -4.7426 | 4.0135 | 3.3757 | 3.355 | 1.0007 | 10.6549 | 14.0996 | 14.6969 | 11.0193 | -0.0003 | -0.0026 | 0.0008 | 0.0035 | 0.0009 | -0.0002 | -0.0009 | -0.0217 | -0.0265 | -360.1342 | 17.5588 | -360.6235 | 17.9264 | -360.9404 | 18.0947 | -360.9466 | 17.5321 | -352.8229 | 18.7703 | -352.9029 | 16.8094
11:37 | 1029 | 19.794 | 193.3265 | 434.3825 | 440.4254 | -21.9242 | -47.9772 | 0.4105 | -0.8338 | -8.3281 | -8.0315 | -3.5955 | -4.2514 | 1.534 | -5.4557 | 0.5805 | 0.6367 | 0.9512 | 0.6873 | -131.7112 | -8.4904 | -1.3585 | -2.9784 | -10.7219 | -9.365 | -1.7713 |  | -5.0901 | -4.7055 | 4.0139 | 3.3765 | 3.3519 | 1.0014 | 10.6145 | 14.0762 | 14.6833 | 10.9912 | -0.0003 | -0.0029 | 0.0009 | 0.0038 | 0.0009 | -0.0004 | 0.0083 | -0.0226 | 0.0002 | -360.165 | 17.565 | -360.5989 | 17.9161 | -360.9435 | 18.1317 | -360.9958 | 17.5712 | -352.866 | 18.7846 | -352.8937 | 16.7827
11:37 | 1030 | 19.788 | 193.4578 | 434.3872 | 440.3851 | -21.9974 | -48.077 | 0.351 | -0.8709 | -8.308 | -8.0769 | -3.6394 | -4.3331 | 1.4937 | -5.4112 | 0.5806 | 0.6334 | 0.9494 | 0.6899 | -131.7029 | -8.4598 | -1.4036 | -3.0439 | -10.7187 | -9.3875 | -1.7168 |  | -5.0316 | -4.6837 | 4.0137 | 3.3747 | 3.3563 | 1.0028 | 10.588 | 14.084 | 14.6723 | 10.9884 | -0.0001 | -0.0033 | 0.0004 | 0.0032 | 0.0006 | -0.001 | 0.0189 | -0.0014 | 0.0068 | -360.1865 | 17.5321 | -360.5496 | 17.8894 | -360.8727 | 18.0927 | -360.9958 | 17.5876 | -352.8844 | 18.7579 | -352.8321 | 16.7724
11:37 | 1031 | 19.8197 | 193.4631 | 434.3145 | 440.4468 | -21.9906 | -48.1024 | 0.3118 | -0.9024 | -8.3256 | -8.1798 | -3.6793 | -4.3607 | 1.4504 | -5.49 | 0.5799 | 0.6324 | 0.9472 | 0.6869 | -131.6861 | -8.5261 | -1.399 | -3.058 | -10.7713 | -9.5952 | -1.6711 |  | -5.028 | -4.7373 | 4.0128 | 3.3712 | 3.3554 | 1.0013 | 10.6249 | 14.0923 | 14.6819 | 10.9959 | -0.0003 | -0.0035 | 0.0006 | 0.0036 | 0.0005 | -0.0002 | -0.0054 | 0.0042 | -0.0036 | -360.2481 | 17.5855 | -360.6019 | 17.9017 | -360.8974 | 18.1153 | -360.9866 | 17.5958 | -352.8906 | 18.8011 | -352.8567 | 16.7766
11:37 | 1032 | 19.8241 | 193.4871 | 434.3946 | 440.3887 | -22.033 | -48.0078 | 0.3231 | -0.8571 | -8.2514 | -8.0411 | -3.6851 | -4.3665 | 1.4819 | -5.4038 | 0.5802 | 0.6359 | 0.9484 | 0.6864 | -131.6929 | -8.4084 | -1.4254 | -3.0481 | -10.7561 | -9.4425 | -1.7602 |  | -5.0289 | -4.702 | 4.0125 | 3.3715 | 3.3541 | 1.0022 | 10.6029 | 14.0877 | 14.6601 | 10.9854 | 0 | -0.0027 | 0.0008 | 0.004 | 0.0007 | -0.0009 | 0.0034 | -0.0072 | -0.0228 | -360.1281 | 17.5465 | -360.5712 | 17.9161 | -360.9251 | 18.0968 | -360.9404 | 17.5568 | -352.8567 | 18.7703 | -352.866 | 16.793
11:37 | 1033 | 19.873 | 193.4887 | 434.354 | 440.4293 | -22.0474 | -48.1442 | 0.2849 | -0.8612 | -8.2145 | -7.9732 | -3.6308 | -4.4257 | 1.5033 | -5.4869 | 0.5808 | 0.6339 | 0.9458 | 0.6876 | -131.6461 | -8.4277 | -1.3807 | -3.1198 | -10.7299 | -9.4262 | -1.7439 |  | -5.0416 | -4.5788 | 4.0136 | 3.371 | 3.3553 | 1.0028 | 10.6213 | 14.0834 | 14.6809 | 11.0146 | -0.0007 | -0.0029 | 0.0009 | 0.0039 | 0.0006 | 0 | -0.0074 | -0.0056 | -0.0195 | -360.1342 | 17.5506 | -360.6235 | 17.9305 | -360.9681 | 18.1461 | -361.0204 | 17.5609 | -352.8352 | 18.7661 | -352.8998 | 16.8053
11:37 | 1034 | 19.8963 | 193.5808 | 434.3928 | 440.4828 | -21.9281 | -48.05 | 0.4021 | -0.96 | -8.2579 | -8.0096 | -3.6434 | -4.4168 | 1.4907 | -5.4821 | 0.5818 | 0.6362 | 0.9493 | 0.6892 | -131.6626 | -8.4604 | -1.3389 | -3.1595 | -10.7751 | -9.5406 | -1.7829 |  | -5.0271 | -4.7154 | 4.0129 | 3.3742 | 3.357 | 1.0025 | 10.6514 | 14.1193 | 14.7286 | 11.0273 | 0.0002 | -0.0029 | 0.0002 | 0.0038 | 0.0013 | -0.0006 | -0.0005 | 0.0031 | 0.004 | -360.1219 | 17.528 | -360.5343 | 17.9079 | -360.9374 | 18.1071 | -360.9589 | 17.5588 | -352.826 | 18.7374 | -352.8383 | 16.7786
11:37 | 1035 | 19.9668 | 193.4986 | 434.3667 | 440.4956 | -21.9893 | -47.9346 | 0.4129 | -0.9925 | -8.3669 | -8.0064 | -3.7015 | -4.4661 | 1.4596 | -5.4865 | 0.5816 | 0.6374 | 0.9468 | 0.6873 | -131.7042 | -8.3276 | -1.3594 | -2.9871 | -10.704 | -9.4155 | -1.7754 |  | -5.0427 | -4.7076 | 4.0132 | 3.3708 | 3.3532 | 1.0031 | 10.6237 | 14.0971 | 14.6989 | 11.0233 | 0.0001 | -0.0035 | 0.0007 | 0.0039 | 0.0003 | -0.0003 | 0.0076 | 0.0025 | -0.014 | -360.1804 | 17.5609 | -360.605 | 17.912 | -360.9312 | 18.1214 | -360.9866 | 17.5896 | -352.906 | 18.7764 | -352.8752 | 16.7827
11:37 | 1036 | 19.8222 | 193.3945 | 434.4423 | 440.3886 | -21.9649 | -47.9568 | 0.4462 | -1.0256 | -8.3764 | -8.0902 | -3.7065 | -4.4602 | 1.3807 | -5.4909 | 0.5822 | 0.6351 | 0.9516 | 0.6887 | -131.7246 | -8.375 | -1.396 | -2.9324 | -10.688 | -9.4364 | -1.7207 |  | -5.0717 | -4.7441 | 4.0122 | 3.3744 | 3.3555 | 1.0019 | 10.6491 | 14.088 | 14.6912 | 11.0309 | 0 | -0.0028 | 0.0006 | 0.0035 | 0.0006 | -0.0009 | 0.0156 | -0.0053 | -0.0179 | -360.2081 | 17.5712 | -360.5989 | 17.8915 | -360.9127 | 18.0763 | -360.9066 | 17.5506 | -352.8475 | 18.7805 | -352.8937 | 16.7683
11:37 | 1037 | 19.8936 | 193.4729 | 434.5062 | 440.4651 | -21.9407 | -48.0123 | 0.4242 | -0.9916 | -8.3063 | -8.0533 | -3.6213 | -4.5212 | 1.3582 | -5.4911 | 0.582 | 0.6358 | 0.9523 | 0.6883 | -131.6778 | -8.3955 | -1.4829 | -3.1457 | -10.7433 | -9.5619 | -1.7916 |  | -4.969 | -4.7544 | 4.014 | 3.3736 | 3.3535 | 1.0019 | 10.5985 | 14.0596 | 14.641 | 10.9819 | -0.0006 | -0.0033 | 0.0005 | 0.0034 | 0.0001 | -0.0009 | -0.0045 | 0.0067 | -0.0122 | -360.1988 | 17.5609 | -360.6235 | 17.9305 | -360.9404 | 18.0886 | -360.9866 | 17.5814 | -352.8598 | 18.7764 | -352.9183 | 16.8074
11:37 | 1038 | 19.9122 | 193.5496 | 434.4678 | 440.5396 | -21.9738 | -48.0147 | 0.3585 | -0.9335 | -8.3004 | -8.0138 | -3.6048 | -4.4737 | 1.3261 | -5.5192 | 0.5827 | 0.6375 | 0.9532 | 0.6873 | -131.6159 | -8.3972 | -1.4939 | -3.1868 | -10.7529 | -9.5117 | -1.7317 |  | -4.988 | -4.7115 | 4.0132 | 3.3717 | 3.3539 | 1.0016 | 10.6237 | 14.0913 | 14.6526 | 11.0118 | -0.0002 | -0.0028 | 0.001 | 0.004 | 0.0009 | -0.0002 | 0.01 | -0.0082 | -0.0187 | -360.1435 | 17.5363 | -360.5619 | 17.8915 | -360.9189 | 18.1173 | -361.0051 | 17.5568 | -352.8352 | 18.7415 | -352.866 | 16.7827
11:37 | 1039 | 19.8599 | 193.4753 | 434.3947 | 440.4586 | -21.9852 | -48.048 | 0.4046 | -0.9066 | -8.2892 | -8.0731 | -3.6752 | -4.5451 | 1.3962 | -5.4679 | 0.5817 | 0.6337 | 0.9521 | 0.6886 | -131.6997 | -8.4266 | -1.4302 | -3.0609 | -10.7745 | -9.5592 | -1.8001 |  | -4.9133 | -4.6311 | 4.0136 | 3.3756 | 3.3547 | 1.0023 | 10.6122 | 14.0797 | 14.6989 | 10.9771 | 0.0002 | -0.0032 | 0.0008 | 0.0038 | 0.0007 | -0.0008 | 0.0027 | -0.0025 | -0.0045 | -360.2204 | 17.5465 | -360.5681 | 17.8894 | -360.9404 | 18.1337 | -360.9989 | 17.5917 | -352.8875 | 18.7559 | -352.8598 | 16.7807
11:37 | 1040 | 19.843 | 193.4517 | 434.3876 | 440.4881 | -21.9786 | -48.0244 | 0.3641 | -0.9565 | -8.3697 | -8.0761 | -3.6882 | -4.545 | 1.4168 | -5.4635 | 0.5809 | 0.633 | 0.9507 | 0.6871 | -131.6693 | -8.4114 | -1.483 | -2.9288 | -10.7073 | -9.6371 | -1.8555 |  | -4.9544 | -4.5576 | 4.0115 | 3.3766 | 3.35 | 1.0027 | 10.6078 | 14.0457 | 14.6614 | 10.9855 | -0.0003 | -0.0033 | 0.0007 | 0.004 | 0.0006 | -0.0004 | 0.0002 | -0.017 | -0.0059 | -360.1896 | 17.5609 | -360.5958 | 17.8976 | -360.8789 | 18.1009 | -360.9866 | 17.5794 | -352.8752 | 18.7723 | -352.8598 | 16.7642
11:37 | 1041 | 19.8186 | 193.4148 | 434.34 | 440.3989 | -22.0284 | -47.9939 | 0.2958 | -0.8968 | -8.3632 | -8.0338 | -3.679 | -4.4904 | 1.479 | -5.4532 | 0.5798 | 0.6368 | 0.9533 | 0.689 | -131.6352 | -8.2912 | -1.4786 | -2.94 | -10.659 | -9.4974 | -1.8328 |  | -5.0448 | -4.6618 | 4.013 | 3.3764 | 3.3544 | 1.003 | 10.6073 | 14.0987 | 14.6861 | 11.0117 | 0 | -0.0025 | 0.0011 | 0.004 | 0.001 | -0.0005 | 0.0115 | -0.0179 | -0.0165 | -360.1435 | 17.5506 | -360.5958 | 17.9264 | -360.9312 | 18.0906 | -360.9589 | 17.5712 | -352.8691 | 18.7661 | -352.8844 | 16.793
11:37 | 1042 | 19.8171 | 193.358 | 434.3193 | 440.4602 | -21.9071 | -47.9498 | 0.3572 | -0.9129 | -8.3603 | -8.0708 | -3.6194 | -4.4742 | 1.466 | -5.4757 | 0.5796 | 0.6373 | 0.9509 | 0.6882 | -131.6914 | -8.3173 | -1.4701 | -2.9607 | -10.6712 | -9.5254 | -1.8098 |  | -4.9453 | -4.605 | 4.0129 | 3.3762 | 3.3546 | 1.0022 | 10.6411 | 14.0738 | 14.7095 | 10.989 | -0.0005 | -0.0028 | 0.0004 | 0.0036 | 0.0005 | -0.0004 | 0.0163 | 0.0085 | 0.0113 | -360.1188 | 17.5445 | -360.6173 | 17.9161 | -360.9312 | 18.1255 | -360.9466 | 17.5465 | -352.8352 | 18.7682 | -352.8906 | 16.8094
11:37 | 1043 | 19.8059 | 193.489 | 434.3411 | 440.4281 | -22.0224 | -48.0104 | 0.3727 | -0.9397 | -8.3141 | -8.0002 | -3.5869 | -4.3858 | 1.4466 | -5.5019 | 0.5813 | 0.6379 | 0.9495 | 0.6889 | -131.8013 | -8.3723 | -1.5408 | -3.0077 | -10.6538 | -9.5619 | -1.7706 |  | -4.9947 | -4.5375 | 4.013 | 3.374 | 3.3503 | 1.0031 | 10.5799 | 14.076 | 14.6822 | 10.9974 | -0.0003 | -0.0032 | 0.0007 | 0.004 | 0.0011 | -0.0004 | 0.0113 | -0.003 | -0.0154 | -360.1681 | 17.5363 | -360.5558 | 17.8915 | -360.9035 | 18.0988 | -360.9804 | 17.5732 | -352.826 | 18.7538 | -352.8598 | 16.7724
11:37 | 1044 | 19.8629 | 193.6027 | 434.3877 | 440.5394 | -21.8391 | -47.9599 | 0.4683 | -0.9232 | -8.3692 | -8.1948 | -3.5261 | -4.4195 | 1.4715 | -5.553 | 0.5809 | 0.6357 | 0.9529 | 0.6896 | -131.7593 | -8.2822 | -1.4596 | -2.9444 | -10.6945 | -9.4383 | -1.7381 |  | -5.0532 | -4.6769 | 4.0129 | 3.3748 | 3.3554 | 1.0032 | 10.5948 | 14.0566 | 14.67 | 10.9887 | 0.0004 | -0.0028 | 0.0006 | 0.0038 | 0.0004 | -0.0003 | 0.023 | -0.0078 | 0.0223 | -360.2235 | 17.5547 | -360.5866 | 17.9038 | -360.9066 | 18.1029 | -360.9958 | 17.5753 | -352.8721 | 18.7744 | -352.8537 | 16.7663
11:37 | 1045 | 19.8473 | 193.5529 | 434.3653 | 440.4571 | -22.0097 | -48.1403 | 0.3657 | -0.8525 | -8.304 | -8.0512 | -3.5632 | -4.4192 | 1.5203 | -5.4756 | 0.5809 | 0.6353 | 0.95 | 0.689 | -131.7323 | -8.3261 | -1.4869 | -2.9175 | -10.6304 | -9.4781 | -1.7628 |  | -4.9586 | -4.5228 | 4.0137 | 3.3749 | 3.3541 | 1.0025 | 10.6124 | 14.0734 | 14.6542 | 11.0017 | -0.0004 | -0.003 | 0.0003 | 0.0034 | 0.0001 | -0.0008 | 0.007 | -0.0049 | -0.0142 | -360.1927 | 17.5342 | -360.5896 | 17.8997 | -360.8881 | 18.0804 | -360.9435 | 17.5691 | -352.8629 | 18.7661 | -352.8691 | 16.7745
11:37 | 1046 | 19.9645 | 193.4908 | 434.3419 | 440.4712 | -21.9966 | -48.0738 | 0.3231 | -0.9157 | -8.3659 | -7.9479 | -3.6183 | -4.414 | 1.5338 | -5.4757 | 0.5808 | 0.6331 | 0.9489 | 0.6885 | -131.7077 | -8.2519 | -1.5115 | -2.8625 | -10.5943 | -9.4214 | -1.7845 |  | -5.1021 | -4.713 | 4.0124 | 3.3732 | 3.3534 | 1.0027 | 10.6132 | 14.0754 | 14.6677 | 10.9716 | 0 | -0.0026 | 0.001 | 0.0039 | 0.0006 | -0.0006 | -0.0039 | -0.0098 | -0.0083 | -360.1711 | 17.565 | -360.6143 | 17.9182 | -360.922 | 18.1214 | -360.9774 | 17.565 | -352.8567 | 18.7805 | -352.8721 | 16.793
11:37 | 1047 | 19.9983 | 193.5612 | 434.3775 | 440.479 | -22.0926 | -48.2114 | 0.3192 | -0.9005 | -8.348 | -8.0823 | -3.6564 | -4.3982 | 1.4339 | -5.4464 | 0.582 | 0.6353 | 0.9516 | 0.689 | -131.7228 | -8.2136 | -1.4162 | -2.8837 | -10.5542 | -9.4249 | -1.7129 |  | -5.147 | -4.7656 | 4.0117 | 3.3732 | 3.3558 | 1.0032 | 10.5959 | 14.0693 | 14.7061 | 10.984 | -0.0002 | -0.0027 | 0.0005 | 0.0032 | 0.0002 | -0.001 | 0.0094 | -0.0114 | -0.0162 | -360.1527 | 17.5198 | -360.5527 | 17.8976 | -360.8943 | 18.1173 | -360.962 | 17.5629 | -352.8414 | 18.7415 | -352.829 | 16.7827
11:37 | 1048 | 19.9549 | 193.6074 | 434.4029 | 440.5488 | -22.0231 | -48.1169 | 0.359 | -0.8506 | -8.347 | -8.1692 | -3.6238 | -4.3408 | 1.5135 | -5.5005 | 0.5801 | 0.634 | 0.9491 | 0.6874 | -131.7433 | -8.205 | -1.3759 | -2.8586 | -10.5189 | -9.456 | -1.7013 |  | -5.0818 | -4.7489 | 4.0128 | 3.3734 | 3.352 | 1.003 | 10.6342 | 14.0727 | 14.6976 | 11.028 | 0.0002 | -0.0025 | 0.0008 | 0.0039 | 0.0007 | -0.0008 | 0.0045 | -0.0211 | -0.0009 | -360.1496 | 17.5486 | -360.5927 | 17.9058 | -360.9251 | 18.1255 | -361.0297 | 17.5794 | -352.8475 | 18.7579 | -352.8598 | 16.7786
11:37 | 1049 | 19.887 | 193.5873 | 434.3617 | 440.4534 | -22.0227 | -48.1414 | 0.3519 | -0.7909 | -8.3394 | -8.167 | -3.6344 | -4.359 | 1.5814 | -5.4813 | 0.5818 | 0.633 | 0.9479 | 0.6877 | -131.6456 | -8.2169 | -1.3617 | -2.8833 | -10.5817 | -9.5742 | -1.7845 |  | -5.0742 | -4.7201 | 4.0134 | 3.3745 | 3.3544 | 1.0056 | 10.6133 | 14.104 | 14.6945 | 11.0186 | -0.0001 | -0.003 | 0.0007 | 0.0039 | 0.0003 | -0.0009 | 0.0029 | -0.0094 | -0.0205 | -360.1619 | 17.5404 | -360.5527 | 17.8874 | -360.8881 | 18.0927 | -360.9497 | 17.5629 | -352.8444 | 18.76 | -352.8537 | 16.7745
11:37 | 1050 | 19.9163 | 193.5502 | 434.349 | 440.5233 | -22.0771 | -48.1928 | 0.3797 | -0.7023 | -8.3134 | -8.0563 | -3.6359 | -4.3891 | 1.513 | -5.466 | 0.5793 | 0.6329 | 0.9508 | 0.6856 | -131.6395 | -8.232 | -1.4063 | -2.9942 | -10.6179 | -9.5047 | -1.7638 |  | -5.0263 | -4.6622 | 4.0137 | 3.3735 | 3.3538 | 1.0041 | 10.6331 | 14.1235 | 14.6836 | 10.9753 | -0.0006 | -0.0027 | 0.0002 | 0.0034 | 0.0011 | -0.001 | 0.008 | -0.0148 | 0.0175 | -360.205 | 17.5506 | -360.6327 | 17.9325 | -360.9343 | 18.0968 | -360.9774 | 17.5691 | -352.866 | 18.7785 | -352.9121 | 16.795
11:37 | 1051 | 19.8227 | 193.5812 | 434.3682 | 440.4555 | -22.02 | -48.1564 | 0.3685 | -0.7785 | -8.3115 | -8.1062 | -3.6344 | -4.3737 | 1.547 | -5.4638 | 0.5805 | 0.6299 | 0.9556 | 0.6854 | -131.7127 | -8.1899 | -1.383 | -2.9987 | -10.722 | -9.4644 | -1.7263 |  | -5.0522 | -4.6491 | 4.0128 | 3.3754 | 3.3576 | 1.0061 | 10.6202 | 14.0938 | 14.7143 | 11.002 | -0.0002 | -0.0028 | 0.001 | 0.0043 | 0.0006 | -0.0002 | 0.0053 | 0.0072 | -0.0173 | -360.1496 | 17.5465 | -360.5989 | 17.8956 | -360.9251 | 18.0988 | -360.9343 | 17.5445 | -352.8352 | 18.7682 | -352.8814 | 16.7807
11:37 | 1052 | 19.8911 | 193.6586 | 434.4211 | 440.4776 | -22.1351 | -48.1948 | 0.2485 | -0.8253 | -8.312 | -8.1467 | -3.6032 | -4.4203 | 1.4807 | -5.5675 | 0.5819 | 0.6337 | 0.9483 | 0.6862 | -131.8532 | -8.3528 | -1.4159 | -2.9626 | -10.7596 | -9.4814 | -1.743 |  | -5.0536 | -4.5814 | 4.0117 | 3.3711 | 3.3559 | 1.0051 | 10.5961 | 14.0633 | 14.6635 | 10.9732 | 0.0002 | -0.0029 | 0.0007 | 0.0038 | 0.001 | -0.0007 | 0.0148 | -0.0062 | -0.0003 | -360.1742 | 17.5465 | -360.5958 | 17.9182 | -360.9343 | 18.1235 | -361.0112 | 17.5896 | -352.8783 | 18.7579 | -352.8814 | 16.7991
11:37 | 1053 | 19.8518 | 193.7156 | 434.3868 | 440.5698 | -22.065 | -48.0777 | 0.3228 | -0.8489 | -8.2386 | -8.0359 | -3.6445 | -4.3903 | 1.5056 | -5.5899 | 0.5819 | 0.6315 | 0.9508 | 0.6868 | -131.6522 | -8.2277 | -1.3714 | -2.8515 | -10.7419 | -9.4159 | -1.6642 |  | -5.0297 | -4.5071 | 4.0121 | 3.3725 | 3.3569 | 1.0047 | 10.6042 | 14.0713 | 14.6594 | 10.993 | -0.0002 | -0.0033 | 0.0005 | 0.0036 | 0.0006 | -0.0002 | 0.0075 | -0.009 | -0.0184 | -360.1773 | 17.5342 | -360.5743 | 17.8853 | -360.8758 | 18.1029 | -360.9835 | 17.5732 | -352.8691 | 18.7497 | -352.8598 | 16.7704
11:37 | 1054 | 19.9052 | 193.6578 | 434.4687 | 440.5668 | -21.9967 | -48.1038 | 0.3743 | -0.9687 | -8.3112 | -8.1172 | -3.6877 | -4.27 | 1.5804 | -5.4756 | 0.5804 | 0.6366 | 0.9508 | 0.6865 | -131.7755 | -8.2129 | -1.3469 | -2.8441 | -10.653 | -9.3622 | -1.7331 |  | -5.034 | -4.6083 | 4.0118 | 3.3747 | 3.3532 | 1.0042 | 10.6169 | 14.0611 | 14.6849 | 10.9995 | -0.0004 | -0.003 | 0.0016 | 0.0043 | 0.0009 | -0.0006 | 0.0087 | -0.0084 | -0.0025 | -360.2142 | 17.5609 | -360.5804 | 17.9058 | -360.9374 | 18.1071 | -360.9958 | 17.5917 | -352.906 | 18.7867 | -352.8414 | 16.7868
11:37 | 1055 | 19.8668 | 193.5941 | 434.3811 | 440.5245 | -22.097 | -48.19 | 0.3878 | -0.9743 | -8.3746 | -8.2341 | -3.5334 | -4.2712 | 1.5645 | -5.5151 | 0.5813 | 0.6344 | 0.9514 | 0.6851 | -131.7797 | -8.1672 | -1.3399 | -2.998 | -10.6702 | -9.4365 | -1.7578 |  | -5.0521 | -4.545 | 4.0121 | 3.3738 | 3.3522 | 1.0039 | 10.6087 | 14.0935 | 14.7064 | 11.0259 | -0.0001 | -0.0025 | 0.0012 | 0.0038 | 0.0009 | -0.0006 | 0.0025 | -0.0049 | -0.0209 | -360.1711 | 17.526 | -360.5835 | 17.8915 | -360.8635 | 18.0906 | -360.9527 | 17.5547 | -352.8106 | 18.7497 | -352.8752 | 16.7786
11:37 | 1056 | 19.8585 | 193.5875 | 434.5382 | 440.613 | -22.1397 | -48.1531 | 0.4367 | -0.8926 | -8.3425 | -7.9802 | -3.6064 | -4.3352 | 1.5557 | -5.5769 | 0.5807 | 0.6331 | 0.9486 | 0.6856 | -131.7408 | -8.2062 | -1.2978 | -2.9032 | -10.6541 | -9.413 | -1.7364 |  | -5.0172 | -4.5285 | 4.0123 | 3.3724 | 3.3516 | 1.0042 | 10.6122 | 14.0797 | 14.6758 | 11.0118 | 0.0001 | -0.0028 | 0.0005 | 0.0034 | 0.0007 | 0.0002 | 0.0182 | -0.0041 | 0.004 | -360.1742 | 17.5609 | -360.5835 | 17.9202 | -360.9497 | 18.1235 | -360.9866 | 17.5814 | -352.8598 | 18.762 | -352.8875 | 16.7889
11:37 | 1057 | 19.8217 | 193.5984 | 434.3781 | 440.5351 | -22.0496 | -48.0935 | 0.3695 | -0.9845 | -8.363 | -8.2318 | -3.6364 | -4.3851 | 1.5082 | -5.6489 | 0.5811 | 0.6356 | 0.9533 | 0.6859 | -131.6561 | -8.1832 | -1.3565 | -2.9319 | -10.5967 | -9.4269 | -1.6936 |  | -5.0205 | -4.5127 | 4.0108 | 3.3719 | 3.3527 | 1.0027 | 10.6237 | 14.0972 | 14.7 | 11.0229 | -0.0002 | -0.0036 | 0.0008 | 0.0036 | 0.0009 | -0.001 | 0.0117 | -0.0145 | 0.0069 | -360.1219 | 17.5137 | -360.5712 | 17.8997 | -360.9127 | 18.0988 | -360.9835 | 17.5629 | -352.8198 | 18.7374 | -352.8598 | 16.7991
11:37 | 1058 | 19.8223 | 193.562 | 434.4635 | 440.5484 | -22.0643 | -48.0848 | 0.3453 | -0.9489 | -8.392 | -8.2946 | -3.6048 | -4.4403 | 1.4912 | -5.5975 | 0.5816 | 0.6351 | 0.9505 | 0.6877 | -131.6441 | -8.2543 | -1.3207 | -3.0116 | -10.5734 | -9.4676 | -1.6825 |  | -4.9749 | -4.5282 | 4.0117 | 3.376 | 3.355 | 1.0034 | 10.6515 | 14.1249 | 14.7218 | 10.993 | -0.0001 | -0.0032 | 0.0004 | 0.0038 | 0.0001 | -0.0005 | -0.0038 | -0.0063 | -0.0197 | -360.1804 | 17.5547 | -360.5958 | 17.8956 | -360.9035 | 18.1173 | -360.9774 | 17.5814 | -352.8875 | 18.7661 | -352.8998 | 16.7786
11:37 | 1059 | 19.8752 | 193.5637 | 434.4979 | 440.592 | -22.0333 | -48.2237 | 0.3139 | -0.92 | -8.4221 | -8.1833 | -3.7395 | -4.413 | 1.4805 | -5.5704 | 0.582 | 0.636 | 0.9499 | 0.6888 | -131.754 | -8.1417 | -1.3876 | -2.8537 | -10.6296 | -9.3876 | -1.6945 |  | -4.9819 | -4.5829 | 4.0113 | 3.3704 | 3.3523 | 1.0038 | 10.6133 | 14.0982 | 14.6829 | 10.9897 | -0.0005 | -0.0029 | 0.0004 | 0.004 | 0.0008 | -0.0009 | 0.0082 | -0.0185 | -0.015 | -360.1927 | 17.5506 | -360.5866 | 17.8874 | -360.9158 | 18.0927 | -360.9558 | 17.5671 | -352.8444 | 18.7641 | -352.8598 | 16.7786
11:37 | 1060 | 19.7767 | 193.6833 | 434.4597 | 440.5754 | -22.0707 | -48.153 | 0.2853 | -0.7661 | -8.2404 | -8.0791 | -3.4904 | -4.4147 | 1.4906 | -5.59 | 0.5812 | 0.6346 | 0.9494 | 0.6872 | -131.7145 | -8.1926 | -1.4612 | -2.6974 | -10.5565 | -9.3198 | -1.619 |  | -4.9623 | -4.6147 | 4.011 | 3.3724 | 3.3589 | 1.0029 | 10.6365 | 14.0865 | 14.6877 | 11.0248 | -0.0005 | -0.003 | 0.0011 | 0.0041 | 0.0004 | -0.0004 | 0.0072 | -0.0037 | -0.0063 | -360.1742 | 17.5404 | -360.605 | 17.9099 | -360.9004 | 18.0865 | -360.9435 | 17.5835 | -352.8475 | 18.762 | -352.8998 | 16.7868
11:37 | 1061 | 19.776 | 193.6176 | 434.3654 | 440.5856 | -21.9608 | -48.0712 | 0.3811 | -0.8317 | -8.2344 | -7.9745 | -3.5095 | -4.4066 | 1.5966 | -5.4851 | 0.5813 | 0.6308 | 0.9464 | 0.6862 | -131.7762 | -8.1017 | -1.4716 | -2.74 | -10.6167 | -9.3577 | -1.6462 |  | -5.0597 | -4.6425 | 4.0106 | 3.3747 | 3.3573 | 1.0037 | 10.6087 | 14.0763 | 14.6727 | 10.985 | 0.0001 | -0.0032 | 0.0003 | 0.0037 | 0.0004 | -0.0007 | 0.0112 | -0.001 | -0.0164 | -360.1835 | 17.5363 | -360.5866 | 17.9079 | -360.9435 | 18.1194 | -360.9743 | 17.565 | -352.866 | 18.7661 | -352.8691 | 16.7868
11:37 | 1062 | 19.7662 | 193.5915 | 434.3869 | 440.5849 | -22.0049 | -48.1603 | 0.3224 | -0.8774 | -8.2832 | -8.0467 | -3.4489 | -4.3875 | 1.5412 | -5.5144 | 0.5829 | 0.6378 | 0.9513 | 0.6888 | -131.7699 | -8.178 | -1.4424 | -2.7136 | -10.5661 | -9.3038 | -1.6177 |  | -5.0609 | -4.607 | 4.0111 | 3.374 | 3.3584 | 1.0033 | 10.6053 | 14.0726 | 14.6676 | 11.0053 | -0.0001 | -0.003 | 0.001 | 0.0039 | 0.0006 | -0.0006 | 0.0049 | -0.0048 | -0.0202 | -360.1711 | 17.5157 | -360.5466 | 17.9017 | -360.9127 | 18.1112 | -360.9989 | 17.5794 | -352.8444 | 18.7538 | -352.8414 | 16.7848
11:37 | 1063 | 19.7694 | 193.5631 | 434.4846 | 440.5527 | -22.1229 | -48.1041 | 0.4061 | -0.9222 | -8.2599 | -8.0484 | -3.5284 | -4.4009 | 1.516 | -5.4947 | 0.5812 | 0.6352 | 0.9463 | 0.6868 | -131.7138 | -8.1051 | -1.4217 | -2.8093 | -10.6371 | -9.3371 | -1.717 |  | -5.0245 | -4.5852 | 4.0102 | 3.3721 | 3.3533 | 1.0043 | 10.604 | 14.0717 | 14.6799 | 11.0092 | -0.0001 | -0.0026 | 0.0005 | 0.0038 | 0.0008 | -0.0003 | 0.003 | -0.0156 | -0.006 | -360.1681 | 17.5321 | -360.605 | 17.8935 | -360.882 | 18.1235 | -361.0081 | 17.5753 | -352.8475 | 18.7518 | -352.9029 | 16.7704
11:37 | 1064 | 19.9096 | 193.6367 | 434.4831 | 440.4754 | -22.0528 | -48.009 | 0.4846 | -0.8072 | -8.2095 | -8.065 | -3.5239 | -4.3682 | 1.5216 | -5.4816 | 0.5823 | 0.6333 | 0.951 | 0.6864 | -131.7648 | -8.053 | -1.3831 | -2.8359 | -10.565 | -9.4312 | -1.5837 |  | -4.9928 | -4.493 | 4.0105 | 3.3711 | 3.3541 | 1.0049 | 10.5994 | 14.0727 | 14.6802 | 10.9818 | -0.0002 | -0.0028 | 0.0004 | 0.0034 | 0.0008 | -0.001 | 0.0012 | -0.0092 | -0.0145 | -360.1619 | 17.5301 | -360.5743 | 17.8894 | -360.9035 | 18.0906 | -360.9497 | 17.5691 | -352.8752 | 18.7518 | -352.8598 | 16.7807
11:37 | 1065 | 19.904 | 193.6907 | 434.3777 | 440.4529 | -22.0883 | -47.9962 | 0.4265 | -0.8499 | -8.2474 | -8.2654 | -3.5781 | -4.3478 | 1.4921 | -5.5392 | 0.5803 | 0.6316 | 0.9487 | 0.6862 | -131.6458 | -8.1175 | -1.3851 | -2.7972 | -10.6285 | -9.4519 | -1.6473 |  | -4.9995 | -4.5248 | 4.0108 | 3.373 | 3.3518 | 1.0048 | 10.6271 | 14.0892 | 14.7157 | 11.032 | 0.0004 | -0.0026 | 0.0008 | 0.0035 | 0.0004 | -0.0004 | 0.0117 | -0.0124 | -0.0108 | -360.1588 | 17.5568 | -360.6204 | 17.914 | -360.9251 | 18.1009 | -360.9804 | 17.5712 | -352.8506 | 18.7703 | -352.9183 | 16.795
11:37 | 1066 | 19.9318 | 193.6187 | 434.384 | 440.5092 | -22.0426 | -47.9269 | 0.4326 | -0.8461 | -8.2365 | -8.1399 | -3.5254 | -4.4366 | 1.4873 | -5.5087 | 0.5823 | 0.6348 | 0.9508 | 0.6856 | -131.6332 | -8.0926 | -1.3067 | -2.8258 | -10.6882 | -9.4766 | -1.7424 |  | -5.0364 | -4.6297 | 4.0105 | 3.376 | 3.3537 | 1.0059 | 10.6261 | 14.1051 | 14.6775 | 11.0316 | -0.0002 | -0.0033 | 0.0001 | 0.0033 | 0.0013 | -0.0006 | 0.0053 | -0.0181 | -0.0039 | -360.1619 | 17.5404 | -360.5866 | 17.8771 | -360.9127 | 18.105 | -360.9251 | 17.5486 | -352.829 | 18.7682 | -352.8721 | 16.7807
11:37 | 1067 | 19.8808 | 193.7015 | 434.4585 | 440.4718 | -22.0465 | -47.8177 | 0.4982 | -0.8442 | -8.3073 | -8.2382 | -3.6221 | -4.4271 | 1.4496 | -5.5496 | 0.5805 | 0.6332 | 0.9488 | 0.6858 | -131.6425 | -8.0915 | -1.3361 | -2.8151 | -10.6274 | -9.5056 | -1.6537 |  | -5.0584 | -4.7306 | 4.0106 | 3.3755 | 3.3531 | 1.0044 | 10.6249 | 14.0923 | 14.6877 | 11.0132 | 0.0001 | -0.0027 | 0.001 | 0.004 | 0.0003 | -0.0004 | 0.0051 | 0.0105 | -0.0016 | -360.1988 | 17.5363 | -360.6081 | 17.8976 | -360.9466 | 18.1194 | -361.0143 | 17.5753 | -352.866 | 18.7579 | -352.8967 | 16.7991
11:38 | 1068 | 19.9356 | 193.6017 | 434.4807 | 440.6034 | -21.999 | -47.8685 | 0.5127 | -0.8076 | -8.2175 | -8.1803 | -3.5637 | -4.3992 | 1.5287 | -5.6016 | 0.5811 | 0.6339 | 0.95 | 0.6861 | -131.6845 | -8.0481 | -1.2658 | -2.8639 | -10.595 | -9.3789 | -1.687 |  | -5.0605 | -4.7315 | 4.0123 | 3.3712 | 3.3554 | 1.0047 | 10.6064 | 14.0913 | 14.6932 | 11.0233 | -0.0003 | -0.0025 | 0.0007 | 0.0039 | 0.001 | -0.0005 | 0.0268 | -0.008 | 0.0185 | -360.1588 | 17.528 | -360.5435 | 17.8566 | -360.8727 | 18.0947 | -361.002 | 17.5814 | -352.826 | 18.7312 | -352.866 | 16.7642
11:38 | 1069 | 19.9447 | 193.6539 | 434.5163 | 440.6396 | -22.0066 | -47.9547 | 0.3953 | -0.8749 | -8.2453 | -8.2699 | -3.5084 | -4.4088 | 1.4937 | -5.5399 | 0.5815 | 0.6317 | 0.9493 | 0.6882 | -131.6061 | -8.0023 | -1.3095 | -2.8698 | -10.537 | -9.5319 | -1.5849 |  | -5.0599 | -4.7218 | 4.0104 | 3.3704 | 3.3511 | 1.0054 | 10.6204 | 14.0818 | 14.6648 | 10.9974 | -0.0002 | -0.0029 | 0.0007 | 0.0039 | 0.0008 | -0.0005 | 0.0168 | -0.0075 | 0.0006 | -360.2327 | 17.5568 | -360.5712 | 17.8709 | -360.9343 | 18.1255 | -361.0143 | 17.5958 | -352.9091 | 18.7744 | -352.8721 | 16.7766
11:38 | 1070 | 20.0162 | 193.6472 | 434.4295 | 440.5888 | -21.908 | -47.9121 | 0.485 | -0.8553 | -8.2809 | -8.1125 | -3.4754 | -4.4882 | 1.4447 | -5.5863 | 0.5826 | 0.6321 | 0.9518 | 0.689 | -131.5025 | -8.1418 | -1.2654 | -2.85 | -10.5493 | -9.4184 | -1.7008 |  | -4.9548 | -4.7263 | 4.0115 | 3.3748 | 3.3519 | 1.007 | 10.5983 | 14.0773 | 14.6962 | 10.9923 | 0.0003 | -0.003 | 0.0009 | 0.0043 | 0.0002 | -0.001 | -0.0057 | -0.0095 | -0.0064 | -360.1404 | 17.5198 | -360.5404 | 17.8689 | -360.8666 | 18.0906 | -360.9589 | 17.5547 | -352.8383 | 18.7518 | -352.866 | 16.7683
11:38 | 1071 | 19.9966 | 193.6658 | 434.431 | 440.5447 | -22.0077 | -47.9616 | 0.5032 | -0.8404 | -8.3164 | -8.2033 | -3.5714 | -4.4102 | 1.4726 | -5.5596 | 0.581 | 0.6363 | 0.9493 | 0.6878 | -131.6244 | -8.219 | -1.3005 | -2.8749 | -10.5821 | -9.5386 | -1.8007 |  | -5.0469 | -4.6033 | 4.0115 | 3.377 | 3.3554 | 1.0055 | 10.6261 | 14.0993 | 14.7064 | 10.997 | -0.0001 | -0.0031 | 0.001 | 0.0037 | 0.0005 | -0.0008 | 0.0067 | 0.0091 | -0.0067 | -360.1435 | 17.5445 | -360.6143 | 17.8956 | -360.9558 | 18.1029 | -360.9958 | 17.5732 | -352.8721 | 18.76 | -352.8937 | 16.8053
11:38 | 1072 | 19.9233 | 193.6879 | 434.4214 | 440.5668 | -21.984 | -47.9703 | 0.5013 | -0.9061 | -8.3469 | -8.2939 | -3.6438 | -4.3935 | 1.547 | -5.4906 | 0.5813 | 0.6367 | 0.9487 | 0.689 | -131.6252 | -8.1361 | -1.4404 | -2.9483 | -10.519 | -9.5666 | -1.7958 |  | -5.0076 | -4.5906 | 4.0096 | 3.3705 | 3.3526 | 1.0054 | 10.6353 | 14.0971 | 14.6932 | 10.9944 | -0.0004 | -0.0027 | 0.0004 | 0.0032 | 0.0003 | -0.0007 | 0.0068 | -0.0102 | -0.0164 | -360.1342 | 17.5157 | -360.5589 | 17.8771 | -360.9343 | 18.0968 | -360.9743 | 17.5465 | -352.8106 | 18.7353 | -352.8752 | 16.793
11:38 | 1073 | 19.9236 | 193.6624 | 434.4317 | 440.609 | -21.9794 | -47.8884 | 0.4595 | -0.8271 | -8.2775 | -8.303 | -3.5756 | -4.4322 | 1.4236 | -5.5392 | 0.5825 | 0.6377 | 0.9515 | 0.6877 | -131.5896 | -8.1878 | -1.3265 | -2.9249 | -10.4507 | -9.4189 | -1.6389 |  | -4.9213 | -4.6114 | 4.0103 | 3.3709 | 3.3531 | 1.0056 | 10.6317 | 14.1055 | 14.7269 | 11.0016 | -0.0002 | -0.0027 | 0.0011 | 0.0039 | 0.0008 | -0.0006 | 0.0249 | -0.0228 | 0.0091 | -360.2419 | 17.5465 | -360.6019 | 17.8956 | -360.9681 | 18.0947 | -360.9804 | 17.5876 | -352.8752 | 18.7641 | -352.8783 | 16.795
11:38 | 1074 | 19.8993 | 193.648 | 434.4356 | 440.567 | -21.9838 | -48.0014 | 0.5176 | -0.8214 | -8.3078 | -8.2877 | -3.5541 | -4.3955 | 1.4755 | -5.4118 | 0.5816 | 0.6338 | 0.9494 | 0.6873 | -131.5339 | -8.0359 | -1.3446 | -2.8715 | -10.4668 | -9.3862 | -1.6573 |  | -4.9401 | -4.5513 | 4.0102 | 3.3746 | 3.3533 | 1.005 | 10.611 | 14.0843 | 14.7091 | 10.9876 | 0 | -0.0031 | 0.0004 | 0.0035 | 0.0006 | -0.0001 | 0.0181 | -0.0027 | 0.0096 | -360.1835 | 17.5239 | -360.5896 | 17.8586 | -360.8543 | 18.0906 | -360.9958 | 17.565 | -352.8506 | 18.7497 | -352.8752 | 16.7745
11:38 | 1075 | 19.9261 | 193.5798 | 434.3631 | 440.5741 | -21.9712 | -48.024 | 0.4551 | -0.8713 | -8.2659 | -8.1661 | -3.5489 | -4.2878 | 1.4926 | -5.3974 | 0.58 | 0.6378 | 0.9517 | 0.6876 | -131.5597 | -8.0522 | -1.2924 | -2.788 | -10.5246 | -9.3501 | -1.7628 |  | -4.934 | -4.5027 | 4.0101 | 3.3704 | 3.3513 | 1.0057 | 10.603 | 14.0702 | 14.6938 | 10.98 | 0.0001 | -0.0033 | 0.0006 | 0.0039 | 0.0004 | -0.0009 | 0.0065 | -0.0066 | -0.0122 | -360.2296 | 17.565 | -360.6173 | 17.873 | -360.8943 | 18.0721 | -360.9558 | 17.5773 | -352.8752 | 18.7887 | -352.8998 | 16.7868
11:38 | 1076 | 19.9686 | 193.555 | 434.4107 | 440.5156 | -22.0025 | -47.9587 | 0.4611 | -0.8946 | -8.2514 | -8.2519 | -3.5797 | -4.4635 | 1.4635 | -5.4929 | 0.5817 | 0.6319 | 0.9495 | 0.6873 | -131.5913 | -8.1176 | -1.3501 | -2.784 | -10.5624 | -9.2931 | -1.7223 |  | -4.9765 | -4.564 | 4.011 | 3.3752 | 3.3542 | 1.0058 | 10.5984 | 14.0714 | 14.6778 | 11.01 | -0.0003 | -0.0028 | 0.0007 | 0.0042 | 0.0005 | -0.0003 | 0.0157 | -0.0015 | -0.009 | -360.1804 | 17.5301 | -360.5896 | 17.8812 | -360.9189 | 18.0598 | -360.9589 | 17.565 | -352.829 | 18.7579 | -352.8598 | 16.7786
11:38 | 1077 | 19.9552 | 193.6649 | 434.3436 | 440.5359 | -22.1007 | -48.0734 | 0.3938 | -0.8522 | -8.3282 | -8.2059 | -3.5277 | -4.3205 | 1.4944 | -5.3819 | 0.5818 | 0.6352 | 0.9507 | 0.6876 | -131.5601 | -7.9819 | -1.2364 | -2.8603 | -10.6262 | -9.3491 | -1.8035 |  | -4.9433 | -4.56 | 4.0107 | 3.3743 | 3.3566 | 1.0055 | 10.6203 | 14.0935 | 14.6775 | 11.0085 | -0.0003 | -0.0028 | 0.0005 | 0.0035 | 0.0005 | -0.001 | 0.011 | -0.0015 | 0.0064 | -360.1465 | 17.5363 | -360.6112 | 17.8812 | -360.9189 | 18.105 | -361.0081 | 17.5732 | -352.8475 | 18.7682 | -352.8906 | 16.795
11:38 | 1078 | 19.9657 | 193.6894 | 434.5065 | 440.6069 | -22.0154 | -48.0824 | 0.3506 | -0.7824 | -8.2699 | -8.2397 | -3.5429 | -4.3421 | 1.5206 | -5.4757 | 0.5811 | 0.6365 | 0.9466 | 0.6896 | -131.5818 | -8.0224 | -1.2441 | -2.7689 | -10.5245 | -9.2644 | -1.6791 |  | -4.8583 | -4.4423 | 4.0083 | 3.3713 | 3.3561 | 1.0054 | 10.6122 | 14.0854 | 14.6805 | 11.0122 | -0.0004 | -0.0034 | 0.0008 | 0.0037 | 0.0009 | -0.0001 | 0.0076 | -0.0105 | -0.0325 | -360.1373 | 17.5178 | -360.5435 | 17.8709 | -360.9527 | 18.1029 | -360.9835 | 17.5835 | -352.8506 | 18.7312 | -352.8383 | 16.7745
11:38 | 1079 | 20.0674 | 193.6361 | 434.3836 | 440.6624 | -22.0037 | -48.0569 | 0.3985 | -0.7889 | -8.2391 | -8.0893 | -3.4901 | -4.3505 | 1.5132 | -5.4706 | 0.5803 | 0.6356 | 0.9495 | 0.6875 | -131.5682 | -7.9466 | -1.1054 | -2.7508 | -10.6156 | -9.3148 | -1.811 |  | -4.9581 | -4.6083 | 4.0095 | 3.3755 | 3.3552 | 1.0056 | 10.6075 | 14.0809 | 14.6772 | 10.9897 | -0.0001 | -0.0032 | 0.0004 | 0.0037 | 0.0006 | -0.0006 | 0.0227 | 0.004 | -0.0019 | -360.1927 | 17.5075 | -360.5527 | 17.8791 | -360.9035 | 18.0763 | -360.9866 | 17.5896 | -352.8383 | 18.7333 | -352.8506 | 16.7909
11:38 | 1080 | 20.0889 | 193.6591 | 434.4031 | 440.6249 | -22.118 | -48.0049 | 0.401 | -0.7107 | -8.1624 | -8.1276 | -3.5966 | -4.3221 | 1.4862 | -5.3724 | 0.5806 | 0.6378 | 0.9496 | 0.6878 | -131.5866 | -7.9795 | -1.2664 | -2.8272 | -10.5542 | -9.4122 | -1.7633 |  | -4.9234 | -4.5069 | 4.01 | 3.3744 | 3.3583 | 1.0067 | 10.6122 | 14.1085 | 14.6689 | 11.0237 | -0.0004 | -0.0032 | 0.0004 | 0.0034 | 0.0005 | -0.001 | 0.01 | 0.0021 | -0.0066 | -360.1988 | 17.5588 | -360.6081 | 17.8771 | -360.922 | 18.0845 | -360.962 | 17.5896 | -352.8783 | 18.7764 | -352.8752 | 16.7786
11:38 | 1081 | 20.0505 | 193.6109 | 434.6149 | 440.6981 | -22.155 | -48.006 | 0.37 | -0.694 | -8.2046 | -8.0869 | -3.5395 | -4.3474 | 1.479 | -5.3703 | 0.5812 | 0.6355 | 0.9507 | 0.6901 | -131.5705 | -8.1158 | -1.1581 | -2.8566 | -10.5292 | -9.3125 | -1.7222 |  | -4.9631 | -4.5815 | 4.0106 | 3.3755 | 3.3557 | 1.0068 | 10.6099 | 14.0889 | 14.7367 | 11.0154 | -0.0004 | -0.0027 | 0.0007 | 0.0039 | 0.0003 | -0.0003 | 0.0066 | -0.0088 | 0 | -360.1865 | 17.5445 | -360.5989 | 17.875 | -360.9004 | 18.068 | -360.9312 | 17.5629 | -352.8598 | 18.7641 | -352.8783 | 16.7889
11:38 | 1082 | 20.0497 | 193.6793 | 434.4147 | 440.6584 | -22.0451 | -48.0033 | 0.3755 | -0.7772 | -8.2543 | -8.0715 | -3.6288 | -4.196 | 1.4933 | -5.2929 | 0.581 | 0.635 | 0.9478 | 0.6891 | -131.6178 | -8.0937 | -1.3138 | -2.7919 | -10.5418 | -9.2589 | -1.7023 |  | -4.8261 | -4.5944 | 4.0106 | 3.3725 | 3.3554 | 1.006 | 10.6513 | 14.0964 | 14.7076 | 11.0612 | 0.0002 | -0.0024 | 0.0008 | 0.0037 | 0.0012 | -0.0006 | 0.0005 | -0.0089 | -0.0194 | -360.1773 | 17.5424 | -360.6173 | 17.8976 | -360.9035 | 18.066 | -360.9743 | 17.5896 | -352.8721 | 18.7641 | -352.8998 | 16.8032
11:38 | 1083 | 20.0893 | 193.6741 | 434.5479 | 440.6973 | -22.0122 | -47.9962 | 0.4864 | -0.7627 | -8.2963 | -8.1321 | -3.6963 | -4.1928 | 1.4725 | -5.3605 | 0.5801 | 0.6353 | 0.947 | 0.6888 | -131.5307 | -8.098 | -1.3385 | -2.8832 | -10.4899 | -9.2298 | -1.6323 |  | -4.8294 | -4.6394 | 4.0101 | 3.3767 | 3.3568 | 1.0068 | 10.5881 | 14.0434 | 14.6828 | 10.9887 | 0 | -0.0033 | 0.0005 | 0.0035 | 0.0001 | -0.0005 | 0.0137 | -0.0054 | -0.0301 | -360.165 | 17.5178 | -360.5681 | 17.873 | -360.8943 | 18.0865 | -360.9835 | 17.5732 | -352.8506 | 18.7415 | -352.866 | 16.7848
11:38 | 1084 | 20.0619 | 193.7223 | 434.5264 | 440.7221 | -22.0791 | -48.0667 | 0.4048 | -0.8226 | -8.2634 | -8.1824 | -3.6614 | -4.2627 | 1.5064 | -5.4048 | 0.58 | 0.6334 | 0.9498 | 0.6879 | -131.5322 | -8.0803 | -1.365 | -2.7535 | -10.4268 | -9.3476 | -1.6654 |  | -4.9241 | -4.7068 | 4.0105 | 3.3728 | 3.3535 | 1.0059 | 10.6456 | 14.1136 | 14.7239 | 11.0269 | 0 | -0.003 | 0.0012 | 0.0044 | 0.0014 | -0.0005 | 0.0144 | -0.0083 | 0.0022 | -360.2111 | 17.526 | -360.5558 | 17.873 | -360.9281 | 18.105 | -360.9958 | 17.5978 | -352.8783 | 18.7518 | -352.8198 | 16.7807
11:38 | 1085 | 20.0738 | 193.6347 | 434.5506 | 440.6862 | -21.9658 | -47.9799 | 0.4732 | -0.8255 | -8.2401 | -8.202 | -3.6766 | -4.2967 | 1.4772 | -5.4739 | 0.5797 | 0.6344 | 0.9508 | 0.6887 | -131.428 | -8.0586 | -1.3031 | -2.7853 | -10.5435 | -9.2586 | -1.6225 |  | -4.9803 | -4.6383 | 4.012 | 3.3721 | 3.354 | 1.0052 | 10.618 | 14.0969 | 14.7095 | 10.9948 | -0.0006 | -0.003 | 0.0007 | 0.0035 | 0.0005 | -0.0004 | 0.0137 | 0.0041 | -0.0261 | -360.1896 | 17.5157 | -360.5589 | 17.8668 | -360.9004 | 18.0988 | -361.0358 | 17.5876 | -352.829 | 18.7312 | -352.8321 | 16.7724
11:38 | 1086 | 20.0651 | 193.6364 | 434.5643 | 440.6415 | -22.0434 | -48.0957 | 0.4896 | -0.8078 | -8.264 | -8.0983 | -3.6103 | -4.269 | 1.4315 | -5.4967 | 0.5803 | 0.6311 | 0.9493 | 0.6888 | -131.4811 | -8.0624 | -1.2705 | -2.797 | -10.4809 | -9.296 | -1.7042 |  | -4.8944 | -4.6558 | 4.011 | 3.3747 | 3.3553 | 1.007 | 10.5948 | 14.0913 | 14.6526 | 10.9713 | -0.0004 | -0.0028 | 0.0007 | 0.0039 | 0.0007 | -0.0005 | -0.0068 | -0.0058 | -0.0208 | -360.1527 | 17.5424 | -360.5804 | 17.8689 | -360.8758 | 18.0824 | -360.9681 | 17.5876 | -352.8567 | 18.762 | -352.8752 | 16.7807
11:38 | 1087 | 20.1599 | 193.7219 | 434.666 | 440.6854 | -22.0254 | -47.9677 | 0.5043 | -0.9366 | -8.2497 | -8.2209 | -3.6623 | -4.3068 | 1.4028 | -5.4358 | 0.5815 | 0.6356 | 0.9497 | 0.6876 | -131.4691 | -8.0817 | -1.2757 | -2.8482 | -10.5771 | -9.2714 | -1.7056 |  | -4.8821 | -4.6529 | 4.01 | 3.3707 | 3.3518 | 1.0057 | 10.6329 | 14.0775 | 14.6799 | 11.0266 | 0.0001 | -0.0031 | 0.0008 | 0.0037 | 0.0009 | -0.0004 | 0.0118 | -0.0037 | -0.0207 | -360.2081 | 17.5568 | -360.6235 | 17.8976 | -360.9743 | 18.0783 | -360.9435 | 17.5835 | -352.9029 | 18.7723 | -352.8998 | 16.8032
11:38 | 1088 | 20.1898 | 193.6719 | 434.6179 | 440.7407 | -21.9703 | -47.9699 | 0.6244 | -0.8464 | -8.2877 | -8.138 | -3.6288 | -4.3256 | 1.4607 | -5.4206 | 0.5805 | 0.6357 | 0.9491 | 0.6879 | -131.4673 | -8.1096 | -1.2911 | -2.7586 | -10.5192 | -9.2185 | -1.628 |  | -4.9486 | -4.6741 | 4.0107 | 3.373 | 3.3574 | 1.007 | 10.6193 | 14.0804 | 14.6845 | 11.0144 | -0.0001 | -0.0033 | 0.0001 | 0.0031 | 0.0003 | -0.0007 | 0.001 | -0.0159 | -0.0012 | -360.1496 | 17.5239 | -360.6081 | 17.8791 | -360.8974 | 18.0721 | -360.9404 | 17.5527 | -352.8014 | 18.7538 | -352.9091 | 16.7991
11:38 | 1089 | 20.1242 | 193.7866 | 434.6352 | 440.7747 | -21.9755 | -47.8726 | 0.5982 | -0.8387 | -8.2538 | -8.2049 | -3.6478 | -4.2093 | 1.5193 | -5.2895 | 0.5806 | 0.6363 | 0.9484 | 0.6882 | -131.4704 | -8.1577 | -1.3011 | -2.8462 | -10.5006 | -9.1696 | -1.6456 |  | -4.8692 | -4.6515 | 4.0096 | 3.3727 | 3.3521 | 1.0053 | 10.5856 | 14.0646 | 14.6601 | 10.9681 | 0.0001 | -0.0027 | 0.0008 | 0.0037 | 0.0008 | -0.0008 | 0.0202 | -0.0098 | -0.001 | -360.1958 | 17.5342 | -360.6019 | 17.8874 | -360.9343 | 18.105 | -361.0358 | 17.5794 | -352.8537 | 18.7723 | -352.8844 | 16.795
11:38 | 1090 | 20.1118 | 193.6061 | 434.4892 | 440.7809 | -22.0773 | -47.9555 | 0.5786 | -0.9026 | -8.2057 | -8.0857 | -3.6284 | -4.2398 | 1.4755 | -5.3722 | 0.5808 | 0.6354 | 0.9523 | 0.6885 | -131.4596 | -8.0716 | -1.279 | -2.8881 | -10.5278 | -9.2189 | -1.6142 |  | -4.8875 | -4.6209 | 4.0088 | 3.3735 | 3.3535 | 1.0047 | 10.5995 | 14.0957 | 14.6734 | 11.0053 | -0.0003 | -0.0026 | 0.0006 | 0.0035 | 0 | -0.0005 | 0.0103 | -0.0113 | -0.0161 | -360.1896 | 17.5198 | -360.5589 | 17.8627 | -360.8789 | 18.0865 | -360.9804 | 17.5917 | -352.8783 | 18.7312 | -352.826 | 16.7724
11:38 | 1091 | 20.2304 | 193.7212 | 434.5625 | 440.8257 | -22.0722 | -47.997 | 0.4721 | -0.8345 | -8.2075 | -8.0413 | -3.6595 | -4.2767 | 1.4131 | -5.3358 | 0.5806 | 0.6337 | 0.9488 | 0.6875 | -131.4278 | -8.1328 | -1.1905 | -2.888 | -10.5651 | -9.2059 | -1.6419 |  | -4.8611 | -4.604 | 4.0102 | 3.3743 | 3.3596 | 1.0063 | 10.626 | 14.0821 | 14.6901 | 11.0139 | 0 | -0.0024 | 0.0009 | 0.0036 | 0.0007 | -0.0012 | -0.0014 | -0.0081 | -0.0085 | -360.2204 | 17.5609 | -360.5773 | 17.8791 | -360.8881 | 18.1009 | -361.0328 | 17.5999 | -352.8814 | 18.7661 | -352.8691 | 16.7766
11:38 | 1092 | 20.1553 | 193.6891 | 434.6821 | 440.8244 | -22.0392 | -47.9171 | 0.437 | -0.9314 | -8.199 | -8.1063 | -3.7029 | -4.2946 | 1.4941 | -5.3569 | 0.5815 | 0.6339 | 0.9486 | 0.6891 | -131.4693 | -8.1175 | -1.1956 | -2.9442 | -10.5014 | -9.1764 | -1.6061 |  | -4.8822 | -4.609 | 4.0106 | 3.3733 | 3.355 | 1.0069 | 10.6121 | 14.1088 | 14.6768 | 10.9941 | 0.0001 | -0.0032 | 0.0011 | 0.0045 | 0.0004 | -0.0003 | 0.0001 | -0.0028 | -0.0082 | -360.1711 | 17.5383 | -360.5927 | 17.8709 | -360.9035 | 18.0845 | -360.9497 | 17.5691 | -352.8537 | 18.7559 | -352.8598 | 16.7868
11:38 | 1093 | 20.1368 | 193.728 | 434.6048 | 440.7492 | -21.9945 | -47.872 | 0.5304 | -0.8376 | -8.1416 | -8.091 | -3.7025 | -4.2873 | 1.531 | -5.3241 | 0.5822 | 0.6342 | 0.9514 | 0.6882 | -131.3724 | -8.0582 | -1.1507 | -2.9105 | -10.4682 | -9.0573 | -1.6138 |  | -4.8942 | -4.5405 | 4.0093 | 3.3747 | 3.3556 | 1.0077 | 10.6492 | 14.1224 | 14.6775 | 11.0085 | -0.0004 | -0.0034 | 0.0007 | 0.0036 | 0.0004 | -0.0008 | -0.0118 | 0.0021 | -0.0162 | -360.1711 | 17.526 | -360.6019 | 17.8976 | -360.9558 | 18.0824 | -360.9774 | 17.5691 | -352.8044 | 18.7559 | -352.8937 | 16.8135
11:38 | 1094 | 20.0295 | 193.6016 | 434.537 | 440.8596 | -22.034 | -47.8688 | 0.5166 | -0.8781 | -8.1444 | -8.0262 | -3.702 | -4.2793 | 1.5184 | -5.3433 | 0.583 | 0.6356 | 0.9511 | 0.6885 | -131.3935 | -8.1113 | -1.1559 | -2.773 | -10.4025 | -9.2237 | -1.6 |  | -4.8859 | -4.5789 | 4.0096 | 3.3736 | 3.3542 | 1.0063 | 10.634 | 14.0961 | 14.6707 | 11.0099 | -0.0004 | -0.0025 | 0.0007 | 0.0039 | 0.0006 | -0.0003 | 0.0113 | -0.007 | -0.0002 | -360.205 | 17.528 | -360.5866 | 17.8894 | -360.9312 | 18.105 | -360.9774 | 17.5691 | -352.8506 | 18.7538 | -352.8537 | 16.7971
11:38 | 1095 | 20.1393 | 193.6967 | 434.4993 | 440.8662 | -21.9747 | -47.8345 | 0.5606 | -0.9058 | -8.2716 | -8.1323 | -3.6928 | -4.2714 | 1.583 | -5.345 | 0.5808 | 0.6327 | 0.9487 | 0.6873 | -131.3168 | -7.9552 | -1.1427 | -2.7534 | -10.4816 | -9.2515 | -1.6619 |  | -4.8644 | -4.6932 | 4.01 | 3.3705 | 3.3558 | 1.0057 | 10.6435 | 14.1049 | 14.7227 | 11.0205 | -0.0002 | -0.0028 | 0.0004 | 0.0038 | 0.0005 | -0.0008 | 0.0069 | -0.0021 | -0.0054 | -360.165 | 17.5383 | -360.5773 | 17.8566 | -360.8943 | 18.0886 | -360.9558 | 17.5896 | -352.866 | 18.7559 | -352.8721 | 16.7848
11:38 | 1096 | 20.2281 | 193.7188 | 434.6039 | 440.7621 | -22.0096 | -47.9011 | 0.5684 | -0.8956 | -8.2232 | -8.1526 | -3.7474 | -4.214 | 1.6 | -5.2578 | 0.5818 | 0.6315 | 0.9489 | 0.6885 | -131.4092 | -8.0289 | -1.1776 | -2.8073 | -10.4887 | -9.2616 | -1.7124 |  | -4.8503 | -4.6254 | 4.0083 | 3.3739 | 3.356 | 1.0074 | 10.633 | 14.0716 | 14.6788 | 10.9807 | 0 | -0.0032 | 0.0006 | 0.0036 | 0.0004 | -0.0008 | 0.0026 | -0.01 | -0.0045 | -360.2173 | 17.5568 | -360.6204 | 17.8812 | -360.8943 | 18.0865 | -360.9774 | 17.5917 | -352.9029 | 18.7723 | -352.8906 | 16.7909
11:38 | 1097 | 20.1683 | 193.6819 | 434.6269 | 440.7814 | -22.038 | -47.8592 | 0.4565 | -0.91 | -8.2671 | -8.1613 | -3.7813 | -4.2097 | 1.5859 | -5.3419 | 0.5826 | 0.6322 | 0.9489 | 0.6899 | -131.4101 | -8.0256 | -1.18 | -2.8559 | -10.454 | -9.2632 | -1.742 |  | -4.9229 | -4.6274 | 4.0087 | 3.371 | 3.3579 | 1.008 | 10.5857 | 14.0643 | 14.6406 | 11.0035 | 0 | -0.0034 | 0.0006 | 0.0038 | 0.0004 | -0.0007 | 0.0185 | -0.0064 | 0.0029 | -360.1742 | 17.528 | -360.5866 | 17.8689 | -360.9127 | 18.068 | -360.9312 | 17.5814 | -352.8537 | 18.7477 | -352.8875 | 16.7827
11:38 | 1098 | 20.1541 | 193.6537 | 434.6308 | 440.8051 | -22.0372 | -47.9237 | 0.4814 | -0.863 | -8.165 | -8.0562 | -3.6533 | -4.2237 | 1.5544 | -5.2759 | 0.5818 | 0.6344 | 0.9487 | 0.6879 | -131.36 | -7.9765 | -1.135 | -2.7396 | -10.4772 | -9.192 | -1.6357 |  | -4.8701 | -4.5557 | 4.0106 | 3.372 | 3.3573 | 1.0085 | 10.6111 | 14.084 | 14.6665 | 10.9826 | -0.0003 | -0.0029 | 0.0005 | 0.0033 | 0.0007 | -0.001 | 0.015 | -0.0168 | -0.009 | -360.1865 | 17.5486 | -360.6081 | 17.8689 | -360.9466 | 18.1071 | -360.9466 | 17.5753 | -352.8537 | 18.762 | -352.8875 | 16.795
11:38 | 1099 | 20.1376 | 193.7023 | 434.5143 | 440.7824 | -22.0468 | -47.9844 | 0.424 | -0.856 | -8.2168 | -8.0369 | -3.6105 | -4.1813 | 1.5852 | -5.2807 | 0.5807 | 0.6371 | 0.9496 | 0.6898 | -131.3153 | -7.998 | -1.1306 | -2.7837 | -10.4627 | -9.2013 | -1.6191 |  | -4.868 | -4.6358 | 4.0105 | 3.3716 | 3.3576 | 1.008 | 10.6064 | 14.0855 | 14.67 | 11.0176 | -0.0004 | -0.0028 | 0.0009 | 0.0037 | 0.0006 | -0.0004 | 0.0129 | -0.0096 | -0.0337 | -360.1619 | 17.5178 | -360.5804 | 17.8874 | -360.9404 | 18.1009 | -360.9897 | 17.5896 | -352.8444 | 18.7415 | -352.866 | 16.7991
11:38 | 1100 | 20.1813 | 193.6166 | 434.5747 | 440.7587 | -22.0166 | -47.9344 | 0.4164 | -0.8814 | -8.1694 | -8.0953 | -3.6648 | -4.2845 | 1.445 | -5.4093 | 0.5804 | 0.6294 | 0.9494 | 0.6873 | -131.3644 | -7.9603 | -1.2027 | -2.7838 | -10.4272 | -9.2556 | -1.7228 |  | -4.8355 | -4.6887 | 4.0109 | 3.3705 | 3.3567 | 1.0069 | 10.6457 | 14.067 | 14.6802 | 11.0107 | -0.0002 | -0.0031 | 0.0009 | 0.0039 | 0.0008 | -0.0008 | -0.0021 | -0.0019 | -0.0359 | -360.165 | 17.5219 | -360.5589 | 17.8648 | -360.8666 | 18.0824 | -360.962 | 17.5876 | -352.8198 | 18.7456 | -352.8691 | 16.7766
11:38 | 1101 | 20.2038 | 193.7266 | 434.6958 | 440.8557 | -21.9853 | -47.8235 | 0.4648 | -0.8435 | -8.1587 | -7.9711 | -3.5461 | -4.2321 | 1.4603 | -5.377 | 0.5797 | 0.6333 | 0.9493 | 0.6903 | -131.3971 | -8.0101 | -1.1777 | -2.7398 | -10.4416 | -9.1622 | -1.6866 |  | -4.9028 | -4.7027 | 4.0091 | 3.3696 | 3.3558 | 1.0059 | 10.6121 | 14.103 | 14.7058 | 11.0056 | -0.0005 | -0.003 | 0.0007 | 0.0037 | 0.0009 | 0.0001 | 0.0142 | -0.0094 | -0.0023 | -360.1958 | 17.5383 | -360.5927 | 17.8791 | -360.9374 | 18.0906 | -360.9681 | 17.5896 | -352.8967 | 18.7703 | -352.8691 | 16.7909
11:38 | 1102 | 20.185 | 193.7636 | 434.6804 | 440.8 | -22.0357 | -47.9499 | 0.5636 | -0.9374 | -8.1936 | -8.1467 | -3.5983 | -4.2724 | 1.4787 | -5.4173 | 0.5801 | 0.6331 | 0.9493 | 0.6887 | -131.3134 | -8.0011 | -1.1806 | -2.7694 | -10.5156 | -9.1064 | -1.6303 |  | -4.9267 | -4.6774 | 4.0091 | 3.3696 | 3.3545 | 1.0069 | 10.641 | 14.1088 | 14.6942 | 11.0114 | -0.0004 | -0.0032 | 0.0004 | 0.0038 | 0.0005 | -0.0008 | -0.001 | -0.0001 | -0.0081 | -360.1742 | 17.5321 | -360.5989 | 17.8791 | -360.8727 | 18.0783 | -360.9712 | 17.5691 | -352.8106 | 18.7559 | -352.8783 | 16.7848
11:38 | 1103 | 20.2822 | 193.6288 | 434.5713 | 440.7693 | -22.0898 | -47.9445 | 0.5517 | -0.8993 | -8.1283 | -8.1186 | -3.5715 | -4.2325 | 1.5263 | -5.4101 | 0.5808 | 0.633 | 0.9464 | 0.6888 | -131.3635 | -8.0448 | -1.1212 | -2.8192 | -10.5516 | -9.2047 | -1.6818 |  | -4.8348 | -4.7124 | 4.0103 | 3.3689 | 3.3504 | 1.0071 | 10.6157 | 14.083 | 14.6894 | 10.9811 | -0.0003 | -0.0027 | 0.0005 | 0.0038 | 0.0002 | -0.0008 | 0.0155 | -0.0053 | 0.0141 | -360.1373 | 17.5404 | -360.5681 | 17.8812 | -360.9127 | 18.0988 | -360.9743 | 17.5814 | -352.8444 | 18.7538 | -352.8721 | 16.7971
11:38 | 1104 | 20.234 | 193.6852 | 434.4034 | 440.6787 | -22.1493 | -47.9822 | 0.4015 | -0.8714 | -8.1489 | -8.1564 | -3.5888 | -4.2252 | 1.5651 | -5.3469 | 0.5816 | 0.6341 | 0.9473 | 0.6882 | -131.3752 | -8.0795 | -1.0902 | -2.7699 | -10.5687 | -9.133 | -1.6785 |  | -4.8653 | -4.7224 | 4.009 | 3.3675 | 3.354 | 1.0059 | 10.5567 | 14.0702 | 14.6648 | 10.9512 | -0.0001 | -0.0028 | 0.0007 | 0.0038 | 0.0005 | -0.0006 | 0.0005 | -0.0128 | -0.0062 | -360.1958 | 17.5301 | -360.5896 | 17.8812 | -360.922 | 18.0906 | -360.9835 | 17.5917 | -352.866 | 18.7538 | -352.8444 | 16.7909
11:38 | 1105 | 20.3584 | 193.7518 | 434.6369 | 440.7682 | -22.1801 | -48.1069 | 0.4009 | -0.8969 | -8.1143 | -8.0804 | -3.5992 | -4.3039 | 1.4903 | -5.3787 | 0.5811 | 0.634 | 0.9502 | 0.6872 | -131.3206 | -7.907 | -1.0945 | -2.7125 | -10.5605 | -9.1613 | -1.5944 |  | -4.8494 | -4.6552 | 4.0094 | 3.3697 | 3.3547 | 1.0079 | 10.603 | 14.1049 | 14.6764 | 11.0031 | -0.0001 | -0.0033 | 0.0008 | 0.0038 | 0.0007 | -0.001 | 0.0054 | -0.0078 | -0.0122 | -360.1281 | 17.5301 | -360.5712 | 17.8627 | -360.882 | 18.0845 | -360.9835 | 17.5712 | -352.8352 | 18.7538 | -352.8567 | 16.7786
11:38 | 1106 | 20.2856 | 193.6776 | 434.608 | 440.7861 | -22.1041 | -48.0148 | 0.3056 | -0.868 | -8.2365 | -8.0306 | -3.5612 | -4.2818 | 1.5707 | -5.2736 | 0.5799 | 0.6335 | 0.9491 | 0.6885 | -131.2916 | -7.9335 | -1.0179 | -2.797 | -10.6265 | -9.1907 | -1.6264 |  | -4.8147 | -4.5686 | 4.0087 | 3.3715 | 3.356 | 1.0079 | 10.603 | 14.0934 | 14.6706 | 10.9743 | 0.0002 | -0.0034 | 0.0008 | 0.0037 | 0.0005 | -0.0002 | 0.0108 | -0.0003 | -0.0158 | -360.1896 | 17.5342 | -360.5804 | 17.8915 | -360.9281 | 18.0845 | -360.9897 | 17.5978 | -352.8567 | 18.7579 | -352.8906 | 16.7971
11:38 | 1107 | 20.2761 | 193.7387 | 434.6096 | 440.7046 | -22.1209 | -47.949 | 0.4389 | -0.8052 | -8.218 | -8.0241 | -3.4907 | -4.2185 | 1.579 | -5.2942 | 0.5821 | 0.6349 | 0.9491 | 0.6901 | -131.3198 | -7.9445 | -1.0277 | -2.7641 | -10.6808 | -9.2451 | -1.6311 |  | -4.9308 | -4.6312 | 4.0091 | 3.3708 | 3.3528 | 1.0082 | 10.6123 | 14.0794 | 14.6621 | 10.9721 | -0.0005 | -0.0028 | 0.0006 | 0.0033 | 0.0005 | -0.0013 | 0.0083 | -0.0109 | -0.0291 | -360.1742 | 17.5301 | -360.5712 | 17.8627 | -360.8881 | 18.0845 | -360.9712 | 17.5732 | -352.8475 | 18.7436 | -352.8598 | 16.7807
11:38 | 1108 | 20.1902 | 193.6353 | 434.5102 | 440.6511 | -22.1398 | -48.0058 | 0.3597 | -0.8311 | -8.2028 | -8.1222 | -3.6407 | -4.2673 | 1.4998 | -5.29 | 0.5789 | 0.6336 | 0.9477 | 0.6871 | -131.3288 | -7.9284 | -1.0605 | -2.7292 | -10.5684 | -9.166 | -1.6848 |  | -4.8985 | -4.6019 | 4.0097 | 3.372 | 3.3559 | 1.0068 | 10.6006 | 14.0796 | 14.6574 | 11.0122 | -0.0001 | -0.0023 | 0.0006 | 0.0037 | 0.0003 | -0.0002 | 0.0197 | -0.0097 | 0.0032 | -360.1619 | 17.5486 | -360.5927 | 17.8771 | -360.9189 | 18.0988 | -360.9927 | 17.5794 | -352.8814 | 18.7661 | -352.8937 | 16.7971
11:38 | 1109 | 20.1902 | 193.6673 | 434.5047 | 440.7516 | -22.1709 | -47.9763 | 0.3682 | -0.8005 | -8.1741 | -8.1374 | -3.5297 | -4.2647 | 1.5317 | -5.2671 | 0.5811 | 0.6384 | 0.9498 | 0.6897 | -131.3032 | -7.987 | -1.0332 | -2.744 | -10.5958 | -9.4426 | -1.6694 |  | -4.8565 | -4.6206 | 4.01 | 3.3674 | 3.3571 | 1.0077 | 10.6238 | 14.0796 | 14.6574 | 11.0064 | -0.0001 | -0.0029 | 0.0005 | 0.0033 | 0.0009 | -0.0005 | 0.0133 | 0.0007 | 0.0023 | -360.1681 | 17.5424 | -360.5989 | 17.8833 | -360.9189 | 18.0886 | -360.9651 | 17.5773 | -352.8198 | 18.7538 | -352.8721 | 16.793
11:38 | 1110 | 20.2888 | 193.6739 | 434.5203 | 440.7923 | -22.0676 | -47.8825 | 0.4181 | -0.8317 | -8.135 | -8.1152 | -3.6538 | -4.2972 | 1.5126 | -5.2989 | 0.582 | 0.6353 | 0.9517 | 0.6901 | -131.3936 | -7.9507 | -1.1666 | -2.7044 | -10.5817 | -9.2198 | -1.6735 |  | -4.805 | -4.5207 | 4.0091 | 3.3701 | 3.3536 | 1.0071 | 10.6214 | 14.0947 | 14.702 | 11.0212 | 0.0002 | -0.0028 | 0.0005 | 0.0038 | 0.0003 | -0.0005 | 0.0257 | -0.0062 | 0.0199 | -360.1773 | 17.528 | -360.5312 | 17.8668 | -360.8974 | 18.0804 | -360.9589 | 17.5753 | -352.829 | 18.7518 | -352.8537 | 16.7807
11:38 | 1111 | 20.2326 | 193.7057 | 434.4699 | 440.7778 | -22.0693 | -47.8028 | 0.4258 | -0.8037 | -8.1782 | -8.0746 | -3.6039 | -4.3538 | 1.4764 | -5.3401 | 0.5801 | 0.6382 | 0.9491 | 0.6885 | -131.2349 | -7.9188 | -1.0716 | -2.7437 | -10.5622 | -9.1775 | -1.6451 |  | -4.8143 | -4.5487 | 4.0083 | 3.3722 | 3.3562 | 1.0069 | 10.6075 | 14.0925 | 14.6945 | 11.0013 | -0.0002 | -0.0028 | 0.0006 | 0.0038 | 0.0006 | -0.0008 | 0.0089 | -0.0065 | 0.0091 | -360.1988 | 17.5239 | -360.5804 | 17.8771 | -360.9343 | 18.0886 | -361.0235 | 17.5978 | -352.866 | 18.7538 | -352.8598 | 16.7807
11:38 | 1112 | 20.1745 | 193.6929 | 434.4992 | 440.7355 | -22.0789 | -47.8306 | 0.3739 | -0.7579 | -8.1172 | -8.0273 | -3.6366 | -4.2915 | 1.4873 | -5.3155 | 0.5795 | 0.6346 | 0.9472 | 0.6889 | -131.3335 | -7.9732 | -1.0397 | -2.6875 | -10.4944 | -9.1809 | -1.5655 |  | -4.7791 | -4.4923 | 4.008 | 3.3713 | 3.3537 | 1.0074 | 10.6295 | 14.1144 | 14.7337 | 11.0176 | -0.0001 | -0.0027 | 0.0007 | 0.0037 | 0.0004 | -0.0007 | -0.003 | 0.0002 | -0.0242 | -360.205 | 17.5342 | -360.5712 | 17.8483 | -360.8758 | 18.0865 | -360.9774 | 17.5732 | -352.8444 | 18.7559 | -352.8506 | 16.7683
11:38 | 1113 | 20.2237 | 193.7893 | 434.5512 | 440.8353 | -22.1675 | -47.9075 | 0.3715 | -0.7554 | -8.1358 | -8.0087 | -3.6367 | -4.2558 | 1.4527 | -5.2887 | 0.581 | 0.633 | 0.9489 | 0.6885 | -131.3381 | -7.9636 | -1.1452 | -2.7727 | -10.4717 | -9.1129 | -1.6057 |  | -4.8145 | -4.6244 | 4.0088 | 3.3699 | 3.3561 | 1.0088 | 10.6042 | 14.0886 | 14.7057 | 10.9815 | 0 | -0.0027 | 0.0001 | 0.0032 | 0.0001 | -0.0008 | 0.0099 | -0.0076 | -0.0089 | -360.1927 | 17.5445 | -360.5989 | 17.8956 | -360.9251 | 18.0906 | -360.9835 | 17.5855 | -352.8875 | 18.7764 | -352.8875 | 16.8012
11:38 | 1114 | 20.2187 | 193.7319 | 434.3773 | 440.7647 | -22.1161 | -47.9661 | 0.4086 | -0.6921 | -8.0956 | -8.0038 | -3.6242 | -4.2089 | 1.5405 | -5.2419 | 0.5814 | 0.6384 | 0.9484 | 0.6899 | -131.3443 | -7.9402 | -1.1556 | -2.794 | -10.4903 | -9.1729 | -1.5981 |  | -4.7468 | -4.6011 | 4.0104 | 3.3698 | 3.3531 | 1.0078 | 10.6053 | 14.0783 | 14.655 | 10.9884 | -0.0001 | -0.0033 | 0.0004 | 0.0034 | 0.0006 | -0.0007 | 0.03 | 0.0071 | -0.0183 | -360.1465 | 17.5239 | -360.6143 | 17.8894 | -360.9312 | 18.0763 | -360.9651 | 17.5629 | -352.8044 | 18.7415 | -352.8783 | 16.795
11:38 | 1115 | 20.2141 | 193.7392 | 434.4458 | 440.775 | -22.1364 | -47.9055 | 0.467 | -0.7419 | -8.1301 | -8.0974 | -3.6471 | -4.2437 | 1.4986 | -5.2642 | 0.5815 | 0.6362 | 0.9496 | 0.689 | -131.3572 | -7.998 | -1.1056 | -2.7926 | -10.4668 | -9.2042 | -1.6153 |  | -4.7723 | -4.5981 | 4.0089 | 3.3722 | 3.353 | 1.0078 | 10.6352 | 14.0856 | 14.7 | 11.0345 | 0.0001 | -0.0029 | 0.0009 | 0.0036 | 0.0003 | -0.0007 | 0.008 | -0.0121 | 0.0022 | -360.1527 | 17.5363 | -360.5989 | 17.8791 | -360.9558 | 18.0947 | -360.9589 | 17.5629 | -352.8321 | 18.7559 | -352.8721 | 16.7909
11:38 | 1116 | 20.2346 | 193.7279 | 434.4389 | 440.7714 | -22.1737 | -47.9674 | 0.4516 | -0.8326 | -8.167 | -8.1003 | -3.666 | -4.2716 | 1.5791 | -5.1752 | 0.5811 | 0.6375 | 0.9493 | 0.6896 | -131.3271 | -7.9566 | -1.2513 | -2.8698 | -10.5331 | -9.1822 | -1.5341 |  | -4.7574 | -4.6027 | 4.0092 | 3.3698 | 3.3555 | 1.008 | 10.6041 | 14.0946 | 14.6604 | 10.9984 | -0.0005 | -0.0029 | 0.0005 | 0.0034 | 0.0006 | -0.0008 | -0.0036 | -0.0126 | 0.006 | -360.2142 | 17.5239 | -360.5835 | 17.873 | -360.9097 | 18.0906 | -360.9866 | 17.5999 | -352.8783 | 18.7518 | -352.8721 | 16.7889
11:38 | 1117 | 20.2855 | 193.778 | 434.5198 | 440.9461 | -22.1107 | -47.9751 | 0.4158 | -0.8522 | -8.1988 | -8.0145 | -3.6453 | -4.1611 | 1.5233 | -5.2318 | 0.5806 | 0.6339 | 0.9479 | 0.6892 | -131.3676 | -8.1118 | -1.2769 | -2.7484 | -10.4426 | -9.1037 | -1.5463 |  | -4.6557 | -4.3757 | 4.0091 | 3.3669 | 3.3553 | 1.0073 | 10.648 | 14.0926 | 14.6782 | 11.0356 | -0.0005 | -0.0026 | 0.0012 | 0.0041 | 0.0004 | -0.0003 | -0.0025 | -0.0065 | -0.0169 | -360.165 | 17.5301 | -360.5773 | 17.8381 | -360.8604 | 18.0763 | -361.0051 | 17.5835 | -352.8691 | 18.7538 | -352.8783 | 16.7807
11:38 | 1118 | 20.3917 | 193.7602 | 434.6217 | 440.9517 | -22.1142 | -47.9594 | 0.4592 | -0.7392 | -8.0905 | -8.0145 | -3.5488 | -4.1514 | 1.5735 | -5.2218 | 0.5816 | 0.6368 | 0.9506 | 0.6884 | -131.4208 | -8.0428 | -1.2005 | -2.766 | -10.484 | -9.2733 | -1.6013 |  | -4.7925 | -4.4878 | 4.0095 | 3.3683 | 3.3522 | 1.0081 | 10.6261 | 14.1051 | 14.7006 | 11.0201 | 0 | -0.0031 | 0.0007 | 0.004 | 0.0007 | -0.0008 | 0.006 | -0.001 | -0.0066 | -360.2296 | 17.5568 | -360.5589 | 17.8463 | -360.9374 | 18.0865 | -360.9958 | 17.5958 | -352.8998 | 18.762 | -352.8906 | 16.7868
11:38 | 1119 | 20.3134 | 193.7942 | 434.55 | 440.9264 | -22.123 | -48.0222 | 0.404 | -0.7615 | -8.1046 | -7.886 | -3.6418 | -4.1877 | 1.483 | -5.2132 | 0.5819 | 0.6358 | 0.9473 | 0.6885 | -131.3558 | -7.954 | -1.0797 | -2.8182 | -10.4572 | -9.1703 | -1.5141 |  | -4.7924 | -4.5083 | 4.0088 | 3.3691 | 3.3544 | 1.0074 | 10.6398 | 14.1135 | 14.7228 | 11.0273 | -0.0004 | -0.0034 | 0.0007 | 0.004 | 0.0008 | -0.0002 | 0.0001 | -0.0117 | -0.007 | -360.1065 | 17.5239 | -360.5866 | 17.8504 | -360.8943 | 18.0742 | -360.9435 | 17.5629 | -352.8229 | 18.7292 | -352.8906 | 16.7991
11:38 | 1120 | 20.3871 | 193.7733 | 434.5509 | 440.8887 | -22.134 | -47.9985 | 0.3701 | -0.8384 | -8.1122 | -7.985 | -3.745 | -4.1446 | 1.5585 | -5.1932 | 0.5814 | 0.6378 | 0.9491 | 0.6887 | -131.3551 | -8.0126 | -1.1467 | -2.9033 | -10.3933 | -9.1576 | -1.5543 |  | -4.7397 | -4.5437 | 4.009 | 3.3741 | 3.3545 | 1.0078 | 10.6306 | 14.0926 | 14.6666 | 11.0067 | -0.0003 | -0.003 | 0.0007 | 0.0038 | 0.0007 | -0.0003 | 0.0009 | -0.0026 | -0.0096 | -360.1742 | 17.5198 | -360.5866 | 17.8627 | -360.9527 | 18.1194 | -360.9958 | 17.565 | -352.8506 | 18.7415 | -352.8814 | 16.8032
11:38 | 1121 | 20.3037 | 193.8017 | 434.6296 | 440.9638 | -21.994 | -47.885 | 0.5999 | -0.6985 | -8.143 | -7.9525 | -3.56 | -4.2293 | 1.5186 | -5.2571 | 0.5801 | 0.6354 | 0.9479 | 0.6895 | -131.3106 | -7.9578 | -1.2441 | -2.7413 | -10.2591 | -9.213 | -1.565 |  | -4.7626 | -4.4951 | 4.0081 | 3.3762 | 3.3588 | 1.0076 | 10.5984 | 14.0944 | 14.6652 | 10.993 | -0.0004 | -0.003 | 0.0004 | 0.0035 | 0.0005 | -0.0009 | 0.0241 | 0.0078 | 0.0047 | -360.165 | 17.5116 | -360.5527 | 17.8566 | -360.962 | 18.0988 | -360.9497 | 17.5814 | -352.8721 | 18.7395 | -352.8506 | 16.793
11:38 | 1122 | 20.3477 | 193.7701 | 434.6158 | 440.9273 | -22.0372 | -47.8743 | 0.6356 | -0.7012 | -8.0366 | -7.894 | -3.5427 | -4.2369 | 1.5028 | -5.2408 | 0.5808 | 0.6334 | 0.9492 | 0.6889 | -131.3655 | -7.9638 | -1.084 | -2.7395 | -10.3277 | -9.2683 | -1.5797 |  | -4.7715 | -4.6033 | 4.0093 | 3.3738 | 3.3559 | 1.0084 | 10.6018 | 14.0634 | 14.6761 | 11.019 | -0.0001 | -0.0028 | 0.0008 | 0.0034 | 0.0006 | -0.0005 | 0.0085 | -0.011 | -0.0187 | -360.1773 | 17.5321 | -360.5743 | 17.8319 | -360.8666 | 18.0947 | -360.9804 | 17.5814 | -352.8383 | 18.762 | -352.8598 | 16.7807
11:38 | 1123 | 20.2678 | 193.6469 | 434.5619 | 440.8343 | -21.9365 | -47.788 | 0.5728 | -0.7454 | -7.9969 | -7.9122 | -3.5722 | -4.1861 | 1.5752 | -5.257 | 0.5808 | 0.634 | 0.9482 | 0.6898 | -131.3836 | -8.0191 | -1.0904 | -2.7984 | -10.3345 | -9.2347 | -1.5649 |  | -4.7783 | -4.5748 | 4.0089 | 3.372 | 3.3533 | 1.0092 | 10.58 | 14.0758 | 14.657 | 10.9981 | -0.0001 | -0.0037 | 0.0005 | 0.0034 | 0.0008 | -0.0007 | -0.0033 | -0.0174 | -0.0209 | -360.2019 | 17.5568 | -360.6235 | 17.8463 | -360.9004 | 18.0804 | -360.9527 | 17.5773 | -352.8814 | 18.7805 | -352.8937 | 16.7848
11:38 | 1124 | 20.2759 | 193.7192 | 434.6147 | 440.8913 | -21.9335 | -47.8093 | 0.5786 | -0.801 | -7.982 | -8.0147 | -3.5921 | -4.0861 | 1.5379 | -5.2441 | 0.5799 | 0.6296 | 0.948 | 0.6875 | -131.2956 | -7.9441 | -1.0576 | -2.858 | -10.3449 | -9.2188 | -1.5489 |  | -4.7006 | -4.5477 | 4.008 | 3.3719 | 3.3551 | 1.0088 | 10.6111 | 14.0726 | 14.6907 | 10.9995 | -0.0002 | -0.0031 | 0.0003 | 0.0035 | 0.0011 | 0.0002 | 0.0018 | -0.0092 | -0.0086 | -360.1773 | 17.528 | -360.5804 | 17.8586 | -360.8974 | 18.066 | -360.962 | 17.5712 | -352.8383 | 18.7538 | -352.9029 | 16.7971
11:38 | 1125 | 20.3133 | 193.7448 | 434.6241 | 440.8572 | -21.9189 | -47.7405 | 0.5695 | -0.7317 | -8.0199 | -7.9475 | -3.6401 | -4.1135 | 1.5702 | -5.1766 | 0.5815 | 0.6362 | 0.9505 | 0.6901 | -131.366 | -7.9736 | -1.0282 | -2.9421 | -10.3133 | -9.2632 | -1.5856 |  | -4.6761 | -4.521 | 4.0085 | 3.369 | 3.3547 | 1.0075 | 10.6085 | 14.0825 | 14.6933 | 11.0128 | -0.0001 | -0.0025 | 0.0012 | 0.0038 | 0.0007 | -0.0008 | 0.0167 | -0.0083 | -0.0042 | -360.1773 | 17.5404 | -360.5773 | 17.8504 | -360.9374 | 18.1112 | -360.9866 | 17.5773 | -352.8629 | 18.7497 | -352.8752 | 16.7971
11:38 | 1126 | 20.2537 | 193.7411 | 434.5408 | 440.8518 | -21.9182 | -47.6587 | 0.6065 | -0.7351 | -7.98 | -7.881 | -3.6615 | -4.1708 | 1.6147 | -5.1353 | 0.5825 | 0.6321 | 0.9471 | 0.6888 | -131.4207 | -7.9092 | -1.1651 | -3.0441 | -10.2944 | -9.2049 | -1.6187 |  | -4.7167 | -4.5509 | 4.0097 | 3.3693 | 3.3558 | 1.0083 | 10.6445 | 14.1297 | 14.733 | 11.0551 | -0.0002 | -0.0027 | 0.0006 | 0.0039 | 0.0001 | -0.0003 | 0.0157 | -0.0065 | -0.0109 | -360.1435 | 17.4972 | -360.525 | 17.8299 | -360.9158 | 18.0968 | -360.9989 | 17.5794 | -352.8598 | 18.7312 | -352.826 | 16.7683
11:38 | 1127 | 20.3211 | 193.7519 | 434.5902 | 440.8853 | -21.9691 | -47.6414 | 0.6206 | -0.7793 | -8.1348 | -7.9608 | -3.8066 | -4.1437 | 1.6172 | -5.1504 | 0.5814 | 0.6322 | 0.9523 | 0.6908 | -131.3541 | -7.9885 | -1.1332 | -2.9116 | -10.3041 | -9.1786 | -1.6107 |  | -4.745 | -4.5538 | 4.0095 | 3.369 | 3.3582 | 1.0094 | 10.6351 | 14.0917 | 14.7021 | 11.0049 | 0.0003 | -0.0028 | 0.0005 | 0.0041 | 0.0008 | -0.0005 | 0.0114 | -0.0121 | -0.0243 | -360.2142 | 17.5301 | -360.5958 | 17.8504 | -360.8974 | 18.1112 | -361.0235 | 17.602 | -352.8691 | 18.7559 | -352.8691 | 16.795
11:39 | 1128 | 20.3482 | 193.7926 | 434.6915 | 440.9062 | -21.9782 | -47.7951 | 0.6092 | -0.684 | -8.0431 | -7.9355 | -3.7508 | -4.1852 | 1.5718 | -5.1652 | 0.5803 | 0.6353 | 0.9461 | 0.689 | -131.3606 | -7.8731 | -1.0993 | -2.9117 | -10.3132 | -9.1132 | -1.5715 |  | -4.7906 | -4.6011 | 4.0086 | 3.3685 | 3.3549 | 1.0084 | 10.6213 | 14.1123 | 14.7273 | 11.0493 | 0 | -0.0028 | 0.0004 | 0.0037 | 0.0004 | -0.0007 | 0.0159 | -0.0086 | 0.0119 | -360.1527 | 17.5424 | -360.5804 | 17.8401 | -360.9097 | 18.068 | -360.9127 | 17.565 | -352.8444 | 18.7497 | -352.8752 | 16.7889
11:39 | 1129 | 20.3048 | 193.7349 | 434.547 | 440.7817 | -21.9162 | -47.8952 | 0.5857 | -0.7225 | -7.9983 | -7.9264 | -3.789 | -4.0902 | 1.649 | -5.1229 | 0.5801 | 0.633 | 0.9512 | 0.6886 | -131.2781 | -7.9751 | -1.0955 | -2.9596 | -10.4165 | -9.1753 | -1.6302 |  | -4.7919 | -4.613 | 4.0092 | 3.3715 | 3.3534 | 1.0094 | 10.6158 | 14.0829 | 14.6652 | 10.9873 | -0.0006 | -0.0025 | 0.0002 | 0.0034 | 0.0007 | -0.0007 | 0.0068 | -0.0135 | -0.0194 | -360.1773 | 17.5424 | -360.642 | 17.8874 | -360.9681 | 18.0804 | -360.9466 | 17.5691 | -352.866 | 18.7641 | -352.906 | 16.8217
11:39 | 1130 | 20.303 | 193.7671 | 434.615 | 440.7987 | -21.9553 | -47.7312 | 0.594 | -0.7767 | -8.0163 | -8.0218 | -3.8255 | -4.0861 | 1.5892 | -5.2138 | 0.5816 | 0.6373 | 0.9506 | 0.6888 | -131.3062 | -7.8722 | -1.0515 | -2.9153 | -10.411 | -9.2477 | -1.6214 |  | -4.7871 | -4.572 | 4.0096 | 3.3686 | 3.3556 | 1.0085 | 10.5765 | 14.0664 | 14.6644 | 10.9718 | -0.0002 | -0.0023 | 0.0008 | 0.0038 | 0.0007 | -0.0012 | 0.0071 | -0.0086 | -0.0162 | -360.1435 | 17.5198 | -360.5558 | 17.8463 | -360.8974 | 18.0906 | -360.9681 | 17.5568 | -352.8044 | 18.7415 | -352.8506 | 16.7766
11:39 | 1131 | 20.2852 | 193.7959 | 434.6208 | 440.9488 | -21.9591 | -47.6996 | 0.6212 | -0.7771 | -7.9958 | -8.0527 | -3.7306 | -3.8985 | 1.6654 | -5.0705 | 0.5809 | 0.6351 | 0.9479 | 0.689 | -131.2911 | -7.7966 | -1.1926 | -2.795 | -10.4201 | -9.1597 | -1.6011 |  | -4.6653 | -4.4747 | 4.0083 | 3.3738 | 3.3576 | 1.011 | 10.5939 | 14.078 | 14.6471 | 11.0007 | -0.0001 | -0.0031 | 0.0008 | 0.0034 | 0.0005 | -0.0007 | -0.0036 | -0.0087 | -0.0066 | -360.2081 | 17.5301 | -360.5835 | 17.8525 | -360.9035 | 18.0968 | -361.0297 | 17.604 | -352.9214 | 18.7497 | -352.8783 | 16.795
11:39 | 1132 | 20.2908 | 193.8352 | 434.7069 | 440.9976 | -21.9856 | -47.8095 | 0.6257 | -0.8121 | -8.0388 | -7.9573 | -3.7628 | -3.9963 | 1.5809 | -5.1615 | 0.5803 | 0.6351 | 0.9507 | 0.6885 | -131.3226 | -7.9182 | -1.114 | -2.6319 | -10.3839 | -9.0519 | -1.5345 |  | -4.6982 | -4.4294 | 4.0091 | 3.3738 | 3.3529 | 1.0092 | 10.6111 | 14.0551 | 14.655 | 10.9652 | 0.0001 | -0.0027 | 0.0005 | 0.0037 | 0.0007 | -0.0009 | 0.0159 | -0.003 | 0.0066 | -360.2265 | 17.5506 | -360.5773 | 17.8258 | -360.8943 | 18.0763 | -360.9281 | 17.5814 | -352.8937 | 18.7579 | -352.8691 | 16.7642
11:39 | 1133 | 20.2964 | 193.8546 | 434.6911 | 440.9117 | -21.9899 | -47.7771 | 0.6124 | -0.7643 | -8.109 | -7.9968 | -3.7664 | -4.0599 | 1.5721 | -5.2236 | 0.5821 | 0.6358 | 0.949 | 0.6892 | -131.3774 | -7.8811 | -1.0282 | -2.6405 | -10.3057 | -9.0225 | -1.4749 |  | -4.705 | -4.4214 | 4.009 | 3.372 | 3.3562 | 1.0093 | 10.6087 | 14.0762 | 14.7064 | 10.9912 | -0.0005 | -0.003 | 0.001 | 0.0039 | 0.0004 | -0.0005 | 0.0126 | -0.0098 | -0.0114 | -360.1711 | 17.5301 | -360.6327 | 17.8689 | -360.9281 | 18.0763 | -360.9804 | 17.5794 | -352.8506 | 18.7559 | -352.8906 | 16.8053
11:39 | 1134 | 20.3709 | 193.7776 | 434.7877 | 440.9451 | -21.9727 | -47.6982 | 0.656 | -0.8038 | -8.0357 | -7.9579 | -3.8353 | -4.0211 | 1.6583 | -5.1659 | 0.5818 | 0.6371 | 0.9506 | 0.6896 | -131.2473 | -7.8713 | -0.9719 | -2.6476 | -10.3644 | -9.1045 | -1.4685 |  | -4.6225 | -4.3897 | 4.0091 | 3.3711 | 3.3526 | 1.0095 | 10.6132 | 14.1043 | 14.6966 | 11.0352 | -0.0002 | -0.002 | 0.0005 | 0.0037 | 0.0011 | -0.0005 | 0.0255 | -0.007 | -0.0181 | -360.1527 | 17.5137 | -360.5743 | 17.8607 | -360.9374 | 18.1091 | -360.9897 | 17.5609 | -352.8567 | 18.7374 | -352.8537 | 16.7868
11:39 | 1135 | 20.3071 | 193.7805 | 434.5833 | 440.9551 | -21.9445 | -47.7003 | 0.6323 | -0.7998 | -8.1483 | -7.7959 | -3.8255 | -4.0528 | 1.6409 | -5.2289 | 0.5815 | 0.6312 | 0.9475 | 0.6892 | -131.2491 | -7.7863 | -0.9728 | -2.6586 | -10.3247 | -9.0522 | -1.4689 |  | -4.6573 | -4.373 | 4.0073 | 3.3724 | 3.3561 | 1.01 | 10.6584 | 14.0914 | 14.7116 | 11.0056 | -0.0002 | -0.0033 | 0.0002 | 0.0038 | 0.0005 | 0 | -0.0036 | -0.0066 | 0.0085 | -360.165 | 17.5116 | -360.5466 | 17.8545 | -360.9312 | 18.1009 | -360.9897 | 17.5937 | -352.8475 | 18.7271 | -352.8598 | 16.795
11:39 | 1136 | 20.2786 | 193.6839 | 434.6407 | 440.9985 | -21.9839 | -47.787 | 0.5594 | -0.8526 | -8.1319 | -7.8717 | -3.7433 | -4.0349 | 1.6087 | -5.2837 | 0.5821 | 0.6331 | 0.9503 | 0.6898 | -131.2271 | -7.9293 | -0.965 | -2.7124 | -10.4484 | -9.0915 | -1.5248 |  | -4.5906 | -4.3441 | 4.0086 | 3.3721 | 3.354 | 1.0089 | 10.6341 | 14.1018 | 14.716 | 11.0508 | 0.0001 | -0.003 | 0.0004 | 0.0036 | 0.0004 | -0.0008 | 0.004 | -0.0212 | -0.008 | -360.1958 | 17.5527 | -360.5927 | 17.8463 | -360.9004 | 18.0906 | -360.9774 | 17.5814 | -352.8814 | 18.762 | -352.8906 | 16.7889
11:39 | 1137 | 20.3594 | 193.7701 | 434.6574 | 440.9917 | -21.864 | -47.7961 | 0.659 | -0.7064 | -8.048 | -7.684 | -3.7262 | -3.9934 | 1.6374 | -5.2859 | 0.582 | 0.6349 | 0.9542 | 0.6884 | -131.2912 | -7.8335 | -0.9922 | -2.6645 | -10.3854 | -9.0397 | -1.5362 |  | -4.6299 | -4.3569 | 4.0083 | 3.3684 | 3.3551 | 1.0095 | 10.64 | 14.1073 | 14.7139 | 11.0342 | 0 | -0.003 | 0.0001 | 0.0036 | 0.0007 | -0.0004 | 0.0042 | 0.0026 | -0.0104 | -360.1619 | 17.5465 | -360.605 | 17.8463 | -360.9343 | 18.0701 | -360.8943 | 17.5527 | -352.8475 | 18.7641 | -352.8814 | 16.7971
11:39 | 1138 | 20.4129 | 193.7882 | 434.5697 | 440.9491 | -21.8491 | -47.7354 | 0.6974 | -0.757 | -8.146 | -7.8149 | -3.7975 | -4.0802 | 1.6194 | -5.2354 | 0.5819 | 0.6364 | 0.9537 | 0.6921 | -131.3648 | -7.8238 | -1.0386 | -2.7035 | -10.3355 | -9.0098 | -1.529 |  | -4.6247 | -4.3694 | 4.0085 | 3.3694 | 3.354 | 1.0077 | 10.6204 | 14.1049 | 14.688 | 11.0205 | -0.0004 | -0.0029 | 0.0007 | 0.0034 | 0.0002 | -0.0008 | -0.0042 | -0.0086 | 0.0007 | -360.1588 | 17.5404 | -360.6081 | 17.8627 | -360.9374 | 18.0927 | -361.0051 | 17.5835 | -352.8475 | 18.7682 | -352.906 | 16.8032
11:39 | 1139 | 20.4315 | 193.8442 | 434.718 | 440.9776 | -21.9349 | -47.7282 | 0.6417 | -0.7526 | -8.1866 | -7.8771 | -3.8099 | -4.0955 | 1.685 | -5.3275 | 0.5809 | 0.635 | 0.9444 | 0.6895 | -131.3323 | -7.745 | -0.9888 | -2.8031 | -10.3347 | -9.0288 | -1.5004 |  | -4.6184 | -4.3918 | 4.0082 | 3.3723 | 3.3581 | 1.0092 | 10.6179 | 14.0913 | 14.6642 | 11.0176 | -0.0003 | -0.0027 | 0.0013 | 0.0039 | 0.0006 | -0.0009 | 0.0159 | -0.0164 | -0.0083 | -360.1619 | 17.5239 | -360.5219 | 17.8299 | -360.9404 | 18.0988 | -360.9712 | 17.5773 | -352.8198 | 18.7395 | -352.8321 | 16.7827
11:39 | 1140 | 20.4564 | 193.8589 | 434.6229 | 440.963 | -21.998 | -47.6779 | 0.5989 | -0.6968 | -8.1853 | -7.8623 | -3.7522 | -4.0319 | 1.6741 | -5.2962 | 0.5827 | 0.6368 | 0.9475 | 0.6913 | -131.2856 | -7.7532 | -0.9382 | -2.8119 | -10.2431 | -9.0429 | -1.4217 |  | -4.6252 | -4.4052 | 4.0073 | 3.3725 | 3.3584 | 1.0095 | 10.6077 | 14.0921 | 14.6624 | 11.0024 | -0.0002 | -0.0035 | 0.0006 | 0.0035 | 0.0001 | -0.001 | 0.0097 | 0.0032 | -0.0146 | -360.2111 | 17.5219 | -360.565 | 17.8278 | -360.8881 | 18.1009 | -360.9927 | 17.5978 | -352.8629 | 18.762 | -352.8783 | 16.7827
11:39 | 1141 | 20.4241 | 193.8708 | 434.6245 | 440.9652 | -21.9658 | -47.6003 | 0.5998 | -0.7805 | -8.1736 | -7.796 | -3.7524 | -4.1295 | 1.5445 | -5.3811 | 0.5817 | 0.6377 | 0.9496 | 0.6914 | -131.313 | -7.6981 | -0.8836 | -2.69 | -10.3559 | -9.0937 | -1.5169 |  | -4.6542 | -4.4053 | 4.0065 | 3.3702 | 3.3593 | 1.0095 | 10.6041 | 14.0658 | 14.6557 | 11.0038 | 0.0002 | -0.003 | 0.0006 | 0.0035 | 0.0007 | -0.0008 | 0.0028 | -0.0151 | -0.0195 | -360.2019 | 17.5404 | -360.5927 | 17.8422 | -360.9281 | 18.0906 | -360.962 | 17.5712 | -352.8414 | 18.7661 | -352.8906 | 16.793
11:39 | 1142 | 20.4853 | 193.8295 | 434.691 | 440.998 | -21.9482 | -47.7138 | 0.5453 | -0.7778 | -8.2062 | -7.8911 | -3.8206 | -4.2074 | 1.5603 | -5.3442 | 0.5825 | 0.6355 | 0.9507 | 0.6903 | -131.3774 | -7.7509 | -0.9562 | -2.5416 | -10.2809 | -9.0219 | -1.4375 |  | -4.6107 | -4.3924 | 4.0074 | 3.3703 | 3.3546 | 1.0098 | 10.657 | 14.1198 | 14.7444 | 11.0431 | 0.0001 | -0.0022 | 0.0006 | 0.0041 | 0.0009 | 0.0003 | 0.0143 | -0.0138 | -0.0192 | -360.1588 | 17.5116 | -360.5866 | 17.8525 | -360.922 | 18.0721 | -360.9527 | 17.565 | -352.8198 | 18.7415 | -352.8629 | 16.8156
11:39 | 1143 | 20.393 | 193.9325 | 434.6418 | 441.0587 | -21.9312 | -47.6918 | 0.6744 | -0.7661 | -8.1791 | -8.0468 | -3.796 | -4.1182 | 1.6636 | -5.2412 | 0.5792 | 0.6386 | 0.9443 | 0.6898 | -131.302 | -7.6631 | -0.9086 | -2.5443 | -10.2763 | -9.0114 | -1.4935 |  | -4.6511 | -4.463 | 4.0065 | 3.3703 | 3.3568 | 1.0096 | 10.6422 | 14.1098 | 14.7292 | 11.0417 | -0.0006 | -0.003 | 0 | 0.0036 | 0.0009 | -0.0009 | 0.0009 | -0.0225 | 0.004 | -360.1958 | 17.5465 | -360.5989 | 17.8381 | -360.9343 | 18.1029 | -360.9804 | 17.5773 | -352.8567 | 18.762 | -352.8629 | 16.8115
11:39 | 1144 | 20.3541 | 193.8427 | 434.5764 | 440.9938 | -22.0003 | -47.6047 | 0.6114 | -0.7761 | -8.2694 | -7.8903 | -3.7249 | -4.2423 | 1.8094 | -5.2805 | 0.5805 | 0.6329 | 0.9478 | 0.6899 | -131.3657 | -7.7427 | -0.9873 | -2.5512 | -10.3354 | -9.1786 | -1.4461 |  | -4.5731 | -4.237 | 4.0059 | 3.3701 | 3.3571 | 1.0115 | 10.6444 | 14.1067 | 14.6994 | 11.0431 | 0 | -0.0025 | 0.0008 | 0.0041 | 0.0005 | -0.0002 | 0.012 | -0.0022 | -0.0057 | -360.1588 | 17.5219 | -360.5404 | 17.8155 | -360.9066 | 18.0783 | -360.9743 | 17.5753 | -352.8414 | 18.7477 | -352.8383 | 16.7909
11:39 | 1145 | 20.3273 | 193.8711 | 434.5759 | 441.0123 | -21.9228 | -47.6475 | 0.6732 | -0.7441 | -8.2254 | -7.9985 | -3.7566 | -4.2091 | 1.683 | -5.343 | 0.5816 | 0.6337 | 0.9475 | 0.6897 | -131.3223 | -7.7109 | -0.9208 | -2.6606 | -10.3978 | -9.1547 | -1.4953 |  | -4.6309 | -4.2904 | 4.0066 | 3.3696 | 3.3578 | 1.0095 | 10.625 | 14.1211 | 14.6866 | 11.0252 | -0.0003 | -0.0037 | 0.0003 | 0.0033 | 0.0007 | -0.0007 | -0.0009 | -0.0039 | -0.0295 | -360.1865 | 17.5404 | -360.6019 | 17.8504 | -360.9066 | 18.0968 | -360.9743 | 17.5835 | -352.866 | 18.7703 | -352.9091 | 16.8094
11:39 | 1146 | 20.3486 | 193.7747 | 434.6197 | 440.9511 | -22.054 | -47.7708 | 0.7139 | -0.7202 | -8.2331 | -8.0231 | -3.7668 | -4.2531 | 1.6679 | -5.2886 | 0.582 | 0.6345 | 0.9457 | 0.6878 | -131.3416 | -7.7338 | -1.0205 | -2.6146 | -10.341 | -9.0993 | -1.513 |  | -4.6364 | -4.3982 | 4.0072 | 3.3705 | 3.3571 | 1.0092 | 10.5928 | 14.0537 | 14.6746 | 10.988 | -0.0004 | -0.0032 | 0.0005 | 0.0038 | 0.0003 | -0.0008 | 0.0293 | -0.011 | 0.0037 | -360.1588 | 17.5198 | -360.5496 | 17.8401 | -360.9127 | 18.0865 | -360.9435 | 17.565 | -352.8598 | 18.7456 | -352.8444 | 16.8074
11:39 | 1147 | 20.4439 | 193.8629 | 434.6851 | 441.0646 | -22.0632 | -47.7949 | 0.4657 | -0.6674 | -8.2767 | -7.9981 | -3.7409 | -4.2607 | 1.6446 | -5.3016 | 0.5819 | 0.6329 | 0.9492 | 0.691 | -131.3205 | -7.7022 | -0.9775 | -2.61 | -10.2756 | -9.0534 | -1.4377 |  | -4.6205 | -4.451 | 4.0088 | 3.373 | 3.3548 | 1.0098 | 10.5844 | 14.0809 | 14.6714 | 10.9897 | -0.0002 | -0.0027 | 0.0016 | 0.0041 | 0.0009 | 0 | 0.0028 | -0.0153 | -0.0005 | -360.2327 | 17.5342 | -360.5896 | 17.8463 | -360.9127 | 18.0947 | -360.9866 | 17.5876 | -352.8598 | 18.7538 | -352.8906 | 16.8115
11:39 | 1148 | 20.3975 | 193.9135 | 434.6892 | 441.021 | -22.0721 | -47.7351 | 0.5387 | -0.7348 | -8.2267 | -7.955 | -3.7463 | -4.2619 | 1.6679 | -5.2332 | 0.5813 | 0.6346 | 0.9482 | 0.6919 | -131.3707 | -7.6029 | -0.9008 | -2.6744 | -10.29 | -9.1053 | -1.5157 |  | -4.6281 | -4.344 | 4.0078 | 3.3692 | 3.3531 | 1.0093 | 10.6088 | 14.0645 | 14.6533 | 11.0031 | -0.0005 | -0.0028 | 0.0005 | 0.0035 | 0.0007 | -0.001 | 0.0193 | -0.0023 | 0 | -360.2019 | 17.5301 | -360.5866 | 17.8422 | -360.9189 | 18.0845 | -360.9835 | 17.5691 | -352.8229 | 18.7497 | -352.8444 | 16.793
11:39 | 1149 | 20.3961 | 193.8793 | 434.7593 | 441.0574 | -21.9545 | -47.7222 | 0.5337 | -0.7936 | -8.2573 | -7.9389 | -3.7556 | -4.1978 | 1.7055 | -5.3091 | 0.5823 | 0.634 | 0.947 | 0.689 | -131.3358 | -7.6376 | -0.8824 | -2.5936 | -10.4116 | -9.1139 | -1.5934 |  | -4.638 | -4.5112 | 4.0068 | 3.3729 | 3.3573 | 1.0111 | 10.5972 | 14.0645 | 14.6475 | 11.0031 | 0.0002 | -0.0032 | 0.001 | 0.0041 | 0.0004 | -0.0004 | 0.0078 | -0.0019 | -0.0144 | -360.1927 | 17.5219 | -360.5804 | 17.8442 | -360.8881 | 18.0804 | -361.002 | 17.5835 | -352.8352 | 18.7538 | -352.8875 | 16.8094
11:39 | 1150 | 20.381 | 193.9283 | 434.7886 | 441.076 | -22.0865 | -47.8845 | 0.53 | -0.808 | -8.2035 | -8.0164 | -3.7983 | -4.1792 | 1.6575 | -5.3093 | 0.5811 | 0.6339 | 0.9449 | 0.688 | -131.407 | -7.7278 | -0.8753 | -2.6225 | -10.3603 | -9.0628 | -1.5411 |  | -4.7072 | -4.4316 | 4.0071 | 3.3728 | 3.3581 | 1.0099 | 10.6455 | 14.1311 | 14.7307 | 11.0727 | 0.0002 | -0.0028 | 0.0005 | 0.0035 | 0.0007 | -0.0007 | 0.0127 | -0.0076 | -0.0136 | -360.2296 | 17.5445 | -360.605 | 17.8607 | -360.9527 | 18.0927 | -360.9589 | 17.5691 | -352.8352 | 18.762 | -352.9091 | 16.8197
11:39 | 1151 | 20.3813 | 193.9361 | 434.7077 | 441.1112 | -22.0828 | -47.853 | 0.562 | -0.7958 | -8.2465 | -7.9785 | -3.7856 | -4.2187 | 1.6848 | -5.2949 | 0.5813 | 0.6349 | 0.9478 | 0.6907 | -131.4261 | -7.6689 | -0.8882 | -2.6434 | -10.3174 | -9.0663 | -1.5035 |  | -4.7217 | -4.5426 | 4.0071 | 3.369 | 3.3563 | 1.0101 | 10.6469 | 14.0971 | 14.7395 | 10.9944 | -0.0004 | -0.0027 | 0.0003 | 0.0032 | 0.0002 | -0.0007 | 0.0089 | -0.0096 | -0.0056 | -360.1496 | 17.5157 | -360.565 | 17.8401 | -360.9189 | 18.0763 | -360.9712 | 17.5588 | -352.8321 | 18.7436 | -352.8506 | 16.8074
11:39 | 1152 | 20.4228 | 193.9836 | 434.8689 | 441.1272 | -22.0244 | -47.8157 | 0.506 | -0.8266 | -8.2151 | -8.0089 | -3.8839 | -4.1845 | 1.6565 | -5.34 | 0.5811 | 0.6359 | 0.9458 | 0.6901 | -131.442 | -7.7045 | -0.9541 | -2.5993 | -10.2602 | -9.1812 | -1.4623 |  | -4.7363 | -4.4385 | 4.006 | 3.3699 | 3.352 | 1.0118 | 10.6121 | 14.0798 | 14.7116 | 11.0172 | -0.0001 | -0.0027 | 0.0002 | 0.0036 | 0.0009 | -0.0009 | 0.0261 | -0.0134 | -0.0033 | -360.2081 | 17.5321 | -360.5927 | 17.8463 | -360.9004 | 18.0988 | -361.0051 | 17.5978 | -352.8875 | 18.7538 | -352.8721 | 16.8053
11:39 | 1153 | 20.3892 | 193.9092 | 434.8318 | 441.1297 | -22.109 | -47.8391 | 0.4728 | -0.8415 | -8.1921 | -7.9318 | -3.8597 | -4.0768 | 1.7403 | -5.2462 | 0.5811 | 0.6354 | 0.9474 | 0.6908 | -131.4301 | -7.739 | -0.8983 | -2.5837 | -10.2114 | -9.0709 | -1.4783 |  | -4.7165 | -4.5938 | 4.0053 | 3.3676 | 3.3551 | 1.0114 | 10.6041 | 14.112 | 14.6673 | 10.9981 | 0 | -0.0025 | 0 | 0.0034 | 0.0001 | -0.0005 | 0.0197 | -0.0031 | -0.0047 | -360.1711 | 17.5321 | -360.5773 | 17.8134 | -360.8727 | 18.0886 | -360.9804 | 17.5773 | -352.8598 | 18.7538 | -352.8629 | 16.7868
11:39 | 1154 | 20.3339 | 193.8919 | 434.735 | 441.1241 | -21.8823 | -47.786 | 0.7154 | -0.8022 | -8.2639 | -7.8822 | -3.7761 | -4.1499 | 1.7136 | -5.2118 | 0.5823 | 0.635 | 0.9495 | 0.6903 | -131.3577 | -7.7044 | -0.8868 | -2.5686 | -10.3166 | -9.0457 | -1.4803 |  | -4.6726 | -4.5414 | 4.0058 | 3.3686 | 3.3492 | 1.0102 | 10.5996 | 14.0723 | 14.6828 | 11.0234 | -0.0002 | -0.0032 | 0.0004 | 0.0034 | 0.0006 | -0.0009 | 0.0107 | -0.0074 | -0.0103 | -360.2388 | 17.5383 | -360.5835 | 17.836 | -360.8912 | 18.0865 | -360.9466 | 17.5794 | -352.906 | 18.7641 | -352.8691 | 16.793
11:39 | 1155 | 20.4728 | 193.9322 | 434.8164 | 441.2039 | -21.9163 | -47.7455 | 0.5453 | -0.7222 | -8.245 | -7.8641 | -3.8041 | -4.1358 | 1.7149 | -5.2828 | 0.5822 | 0.6339 | 0.95 | 0.6896 | -131.2989 | -7.6618 | -0.9616 | -2.5508 | -10.1661 | -8.9751 | -1.4896 |  | -4.6056 | -4.5049 | 4.0067 | 3.3716 | 3.3543 | 1.0109 | 10.5833 | 14.0854 | 14.6574 | 10.9948 | 0 | -0.003 | 0.0011 | 0.0038 | 0.0007 | -0.0008 | -0.0004 | -0.0065 | -0.0175 | -360.1619 | 17.5239 | -360.6235 | 17.8648 | -360.9558 | 18.0906 | -360.9866 | 17.5568 | -352.8014 | 18.7436 | -352.8937 | 16.8238
11:39 | 1156 | 20.4882 | 193.9068 | 434.8015 | 441.151 | -21.9169 | -47.7919 | 0.6485 | -0.6851 | -8.2363 | -7.9863 | -3.7735 | -4.2517 | 1.6399 | -5.3133 | 0.5809 | 0.6348 | 0.9446 | 0.6914 | -131.2704 | -7.7191 | -0.8789 | -2.5582 | -10.1778 | -9.0515 | -1.4319 |  | -4.6437 | -4.4901 | 4.006 | 3.3684 | 3.3533 | 1.0109 | 10.6193 | 14.0631 | 14.7029 | 11.014 | -0.0005 | -0.0023 | 0.0004 | 0.0032 | 0.0002 | -0.0004 | 0.0129 | -0.0098 | -0.0104 | -360.1281 | 17.487 | -360.5343 | 17.8422 | -360.922 | 18.1091 | -360.9927 | 17.565 | -352.8075 | 18.7189 | -352.789 | 16.8176
11:39 | 1157 | 20.4804 | 193.9857 | 434.7521 | 441.1275 | -21.8757 | -47.7262 | 0.6777 | -0.7804 | -8.171 | -7.934 | -3.6767 | -4.1212 | 1.6749 | -5.2771 | 0.5805 | 0.6354 | 0.9473 | 0.6902 | -131.2799 | -7.712 | -0.9099 | -2.4901 | -10.2371 | -9.0209 | -1.4624 |  | -4.6923 | -4.4864 | 4.0068 | 3.3671 | 3.3559 | 1.0101 | 10.5926 | 14.0424 | 14.6883 | 10.9988 | -0.0005 | -0.003 | 0.0009 | 0.0036 | 0.0011 | -0.0006 | -0.0031 | 0.0102 | -0.0255 | -360.1896 | 17.5342 | -360.5835 | 17.8483 | -360.9251 | 18.0968 | -360.9989 | 17.5978 | -352.8691 | 18.7538 | -352.8691 | 16.8032
11:39 | 1158 | 20.4561 | 193.9373 | 434.7814 | 441.1827 | -21.8677 | -47.7428 | 0.5811 | -0.7377 | -8.154 | -7.9436 | -3.6832 | -4.057 | 1.6995 | -5.1754 | 0.5802 | 0.6354 | 0.9434 | 0.6899 | -131.3479 | -7.6303 | -0.891 | -2.4375 | -10.2589 | -8.8354 | -1.4576 |  | -4.575 | -4.4512 | 4.0068 | 3.3736 | 3.3525 | 1.0098 | 10.6364 | 14.0926 | 14.7129 | 11.0067 | 0.0002 | -0.0028 | 0.0009 | 0.0036 | 0.0006 | -0.0002 | 0.0093 | 0.0012 | -0.0141 | -360.2296 | 17.5465 | -360.605 | 17.8442 | -360.8974 | 18.0578 | -360.9343 | 17.5588 | -352.8444 | 18.7764 | -352.8814 | 16.8012
11:39 | 1159 | 20.4961 | 193.9885 | 434.7893 | 441.1516 | -21.8892 | -47.7149 | 0.6516 | -0.7225 | -8.1975 | -7.8257 | -3.7118 | -4.2222 | 1.7051 | -5.2614 | 0.5808 | 0.6337 | 0.943 | 0.689 | -131.2946 | -7.6676 | -0.884 | -2.5131 | -10.2403 | -8.9961 | -1.5179 |  | -4.646 | -4.5534 | 4.007 | 3.3716 | 3.3555 | 1.01 | 10.6422 | 14.1446 | 14.7303 | 11.0182 | 0.0001 | -0.003 | -0.0001 | 0.0036 | 0.0006 | -0.0008 | 0.0003 | -0.0016 | 0.0045 | -360.2081 | 17.5445 | -360.6296 | 17.8689 | -360.962 | 18.0721 | -360.9435 | 17.5671 | -352.8537 | 18.7559 | -352.9091 | 16.8197
11:39 | 1160 | 20.519 | 194.0476 | 434.8532 | 441.186 | -21.9343 | -47.6199 | 0.6949 | -0.7769 | -8.1662 | -7.9181 | -3.7303 | -4.2503 | 1.6936 | -5.2763 | 0.5806 | 0.6321 | 0.9479 | 0.6899 | -131.3483 | -7.5791 | -0.8869 | -2.4885 | -10.1861 | -9.0226 | -1.4636 |  | -4.6262 | -4.4269 | 4.0054 | 3.3702 | 3.3574 | 1.0115 | 10.6444 | 14.1298 | 14.7457 | 11.0258 | -0.0002 | -0.0026 | 0.0007 | 0.0042 | 0.0004 | -0.0002 | 0.0054 | -0.0027 | -0.0133 | -360.1804 | 17.5157 | -360.5804 | 17.8442 | -360.9404 | 18.105 | -360.9927 | 17.5855 | -352.8475 | 18.7333 | -352.7983 | 16.8053
11:39 | 1161 | 20.5316 | 194.0455 | 434.8076 | 441.2301 | -21.9666 | -47.6419 | 0.5966 | -0.7429 | -8.1296 | -7.9621 | -3.7433 | -4.2827 | 1.6572 | -5.3576 | 0.5801 | 0.6315 | 0.9422 | 0.6899 | -131.3587 | -7.6275 | -0.8928 | -2.4637 | -10.2087 | -8.9989 | -1.5091 |  | -4.6914 | -4.4211 | 4.0055 | 3.3726 | 3.3561 | 1.0114 | 10.6076 | 14.1039 | 14.6877 | 11.0132 | -0.0002 | -0.003 | 0.0007 | 0.004 | 0.0003 | -0.001 | -0.0006 | -0.0048 | -0.0377 | -360.1711 | 17.5157 | -360.5343 | 17.8032 | -360.8974 | 18.0988 | -361.0204 | 17.602 | -352.8752 | 18.7353 | -352.7983 | 16.7807
11:39 | 1162 | 20.598 | 194.0223 | 434.9055 | 441.1686 | -21.9367 | -47.6686 | 0.6194 | -0.7737 | -8.0824 | -7.808 | -3.6947 | -4.3348 | 1.6809 | -5.2766 | 0.5802 | 0.6324 | 0.9448 | 0.6911 | -131.338 | -7.6667 | -0.8707 | -2.3294 | -10.1112 | -8.9556 | -1.437 |  | -4.7195 | -4.4778 | 4.0062 | 3.3723 | 3.3589 | 1.0112 | 10.6239 | 14.0793 | 14.6842 | 11.0129 | -0.0007 | -0.0034 | 0.0004 | 0.0034 | 0.0003 | -0.0006 | 0.0035 | -0.0008 | -0.0229 | -360.1865 | 17.5404 | -360.6358 | 17.8525 | -360.9035 | 18.0927 | -361.002 | 17.5937 | -352.8691 | 18.7682 | -352.8937 | 16.8094
11:39 | 1163 | 20.584 | 194.0785 | 434.8435 | 441.1089 | -21.8963 | -47.6237 | 0.6083 | -0.6943 | -8.1106 | -7.8981 | -3.7967 | -4.3322 | 1.6657 | -5.2404 | 0.5813 | 0.6345 | 0.9463 | 0.6888 | -131.2876 | -7.6344 | -0.9308 | -2.3689 | -10.2616 | -8.8944 | -1.4895 |  | -4.5842 | -4.5037 | 4.0061 | 3.3721 | 3.3541 | 1.0125 | 10.6017 | 14.0636 | 14.6829 | 11.0013 | 0.0001 | -0.0031 | 0.0008 | 0.0038 | 0.0007 | -0.0007 | 0.0018 | -0.0016 | -0.013 | -360.1188 | 17.5301 | -360.6235 | 17.8668 | -360.9312 | 18.0783 | -360.9158 | 17.5445 | -352.8106 | 18.7436 | -352.8906 | 16.8299
11:39 | 1164 | 20.5795 | 194.0541 | 434.7851 | 441.144 | -21.8656 | -47.663 | 0.6366 | -0.717 | -8.1276 | -7.8928 | -3.703 | -4.3507 | 1.6456 | -5.2757 | 0.5812 | 0.6355 | 0.9478 | 0.6892 | -131.2979 | -7.5639 | -0.8977 | -2.317 | -10.3082 | -8.9354 | -1.4839 |  | -4.5488 | -4.49 | 4.0039 | 3.3707 | 3.3541 | 1.011 | 10.6214 | 14.1064 | 14.6741 | 11.0035 | -0.0003 | -0.0031 | 0.001 | 0.0037 | 0.0009 | -0.0008 | 0.0252 | 0.0106 | 0.0016 | -360.165 | 17.5239 | -360.5927 | 17.8771 | -360.9558 | 18.105 | -360.9681 | 17.565 | -352.8475 | 18.7538 | -352.8752 | 16.834
11:39 | 1165 | 20.5084 | 194.0398 | 434.886 | 441.2179 | -21.8971 | -47.6584 | 0.6518 | -0.7607 | -8.2166 | -7.9217 | -3.8038 | -4.3038 | 1.7375 | -5.2247 | 0.5799 | 0.6355 | 0.9456 | 0.6886 | -131.3072 | -7.634 | -0.8745 | -2.4595 | -10.3397 | -8.8727 | -1.5099 |  | -4.571 | -4.4487 | 4.0044 | 3.3714 | 3.3535 | 1.011 | 10.619 | 14.0926 | 14.6608 | 10.9778 | -0.0005 | -0.0027 | 0.0008 | 0.0035 | 0.0009 | -0.0002 | 0.0073 | 0.0001 | -0.0155 | -360.1988 | 17.528 | -360.565 | 17.8422 | -360.9004 | 18.0886 | -361.0204 | 17.5999 | -352.8383 | 18.7374 | -352.8537 | 16.793
11:39 | 1166 | 20.5802 | 194.1016 | 434.8018 | 441.1712 | -21.9108 | -47.7283 | 0.6437 | -0.7537 | -8.1513 | -7.9413 | -3.728 | -4.2498 | 1.8337 | -5.12 | 0.5818 | 0.6348 | 0.9474 | 0.6888 | -131.2392 | -7.6138 | -0.8971 | -2.4345 | -10.3164 | -9.0278 | -1.4665 |  | -4.5558 | -4.5552 | 4.0058 | 3.3725 | 3.3542 | 1.0134 | 10.6295 | 14.0971 | 14.6758 | 10.9829 | -0.0001 | -0.003 | 0.0012 | 0.004 | 0.0014 | -0.0005 | 0.0132 | -0.011 | -0.0093 | -360.2173 | 17.5465 | -360.5712 | 17.836 | -360.8512 | 18.0721 | -360.9743 | 17.5917 | -352.9152 | 18.7785 | -352.8691 | 16.793
11:39 | 1167 | 20.5729 | 194.0953 | 434.9107 | 441.1989 | -21.9111 | -47.7491 | 0.6713 | -0.7089 | -8.2077 | -8.1076 | -3.6656 | -4.3455 | 1.7339 | -5.1755 | 0.5802 | 0.6327 | 0.9479 | 0.6883 | -131.2489 | -7.6459 | -0.8639 | -2.419 | -10.3069 | -8.9292 | -1.4171 |  | -4.5903 | -4.5521 | 4.0073 | 3.3719 | 3.353 | 1.0123 | 10.6076 | 14.0691 | 14.704 | 11.0078 | 0.0002 | -0.0032 | 0.0001 | 0.0032 | 0.0007 | -0.0002 | 0.0136 | -0.0074 | -0.0062 | -360.2019 | 17.5383 | -360.5866 | 17.8586 | -360.9158 | 18.0763 | -360.9281 | 17.5937 | -352.8629 | 18.7661 | -352.8721 | 16.8094
11:39 | 1168 | 20.559 | 194.0976 | 434.8779 | 441.1663 | -21.9319 | -47.709 | 0.6752 | -0.6994 | -8.1627 | -7.993 | -3.726 | -4.3239 | 1.7005 | -5.1949 | 0.5804 | 0.6321 | 0.9454 | 0.69 | -131.2477 | -7.6393 | -0.9334 | -2.5043 | -10.2927 | -8.984 | -1.5519 |  | -4.4964 | -4.4249 | 4.0058 | 3.3706 | 3.3524 | 1.011 | 10.6168 | 14.1132 | 14.686 | 10.9876 | -0.0002 | -0.0031 | 0.0007 | 0.0041 | 0.0009 | -0.0007 | 0.0069 | -0.0026 | 0.0151 | -360.1527 | 17.5137 | -360.5589 | 17.8422 | -360.9004 | 18.0968 | -360.9804 | 17.5506 | -352.8044 | 18.7518 | -352.8537 | 16.8094
11:39 | 1169 | 20.6019 | 194.1454 | 434.8313 | 441.1766 | -21.9433 | -47.7309 | 0.5886 | -0.7201 | -8.1471 | -7.837 | -3.6745 | -4.3442 | 1.6636 | -5.1379 | 0.5811 | 0.6343 | 0.9459 | 0.6896 | -131.2594 | -7.6314 | -0.857 | -2.5584 | -10.276 | -8.8743 | -1.5163 |  | -4.4388 | -4.4975 | 4.005 | 3.3699 | 3.3573 | 1.013 | 10.6434 | 14.0704 | 14.7296 | 10.9912 | -0.0003 | -0.0028 | 0.0006 | 0.004 | 0.0006 | 0.0001 | 0.0092 | -0.0203 | 0.0044 | -360.1465 | 17.5178 | -360.5558 | 17.8483 | -360.9435 | 18.105 | -360.9866 | 17.5978 | -352.8598 | 18.7374 | -352.8352 | 16.8053
11:39 | 1170 | 20.6328 | 194.1845 | 434.8277 | 441.1901 | -21.8494 | -47.5896 | 0.6744 | -0.8044 | -8.2621 | -8.0774 | -3.7256 | -4.4388 | 1.6773 | -5.12 | 0.5812 | 0.6342 | 0.9456 | 0.6883 | -131.3065 | -7.6711 | -0.9072 | -2.6414 | -10.1952 | -8.9948 | -1.5758 |  | -4.4477 | -4.4223 | 4.0056 | 3.3719 | 3.3545 | 1.0136 | 10.6398 | 14.1135 | 14.7228 | 11.0099 | -0.0002 | -0.0029 | 0.0008 | 0.0039 | 0.001 | -0.0006 | 0.0069 | -0.004 | -0.0211 | -360.1773 | 17.5321 | -360.5989 | 17.834 | -360.8543 | 18.0763 | -360.962 | 17.5794 | -352.8352 | 18.7559 | -352.8814 | 16.8012
11:39 | 1171 | 20.6154 | 194.1051 | 434.7231 | 441.1137 | -21.8511 | -47.6655 | 0.6794 | -0.7579 | -8.0498 | -7.9313 | -3.6679 | -4.3952 | 1.661 | -5.1745 | 0.5804 | 0.6345 | 0.9491 | 0.6902 | -131.2535 | -7.6494 | -0.8606 | -2.6346 | -10.2021 | -9.0936 | -1.5366 |  | -4.4947 | -4.4128 | 4.005 | 3.3699 | 3.3514 | 1.0109 | 10.6029 | 14.0935 | 14.6833 | 11.0259 | 0 | -0.0033 | 0.0008 | 0.0039 | 0.0007 | -0.0006 | 0.0011 | -0.0083 | -0.0061 | -360.2111 | 17.5568 | -360.6143 | 17.8689 | -360.9497 | 18.0804 | -360.9404 | 17.5835 | -352.8906 | 18.7785 | -352.8875 | 16.8074
11:39 | 1172 | 20.5425 | 194.0405 | 434.7204 | 441.0848 | -21.9675 | -47.6669 | 0.6895 | -0.8281 | -8.1306 | -7.9986 | -3.7538 | -4.2867 | 1.6166 | -5.159 | 0.5803 | 0.6326 | 0.9474 | 0.6894 | -131.1876 | -7.6302 | -0.7067 | -2.6599 | -10.2501 | -9.0694 | -1.5837 |  | -4.4883 | -4.4025 | 4.0078 | 3.3723 | 3.3543 | 1.0119 | 10.5937 | 14.0957 | 14.6907 | 10.9995 | 0 | -0.0031 | 0.0007 | 0.0034 | 0.0004 | -0.0007 | -0.005 | -0.0158 | 0.0015 | -360.1311 | 17.526 | -360.5866 | 17.8299 | -360.9004 | 18.0804 | -360.9435 | 17.5588 | -352.8014 | 18.7579 | -352.8629 | 16.7971
11:39 | 1173 | 20.5057 | 194.1102 | 434.7774 | 441.1263 | -21.9083 | -47.6662 | 0.6834 | -0.7909 | -8.1399 | -8.0198 | -3.753 | -4.2574 | 1.6661 | -5.1757 | 0.5808 | 0.633 | 0.9445 | 0.6892 | -131.2127 | -7.6854 | -0.7521 | -2.5753 | -10.2694 | -9.0483 | -1.5571 |  | -4.5245 | -4.3223 | 4.0053 | 3.3718 | 3.3562 | 1.0108 | 10.6168 | 14.0785 | 14.686 | 11.028 | -0.0002 | -0.0026 | 0.0008 | 0.0036 | 0.0009 | -0.0008 | 0.0079 | -0.0086 | -0.0166 | -360.2173 | 17.5363 | -360.5866 | 17.836 | -360.9374 | 18.1173 | -360.9743 | 17.5937 | -352.8783 | 18.7559 | -352.8629 | 16.795
11:39 | 1174 | 20.5178 | 194.0303 | 434.7951 | 441.1823 | -21.9218 | -47.695 | 0.7766 | -0.7369 | -8.1324 | -7.9165 | -3.681 | -4.2498 | 1.6207 | -5.2801 | 0.5807 | 0.6347 | 0.9433 | 0.6888 | -131.2669 | -7.7284 | -0.7514 | -2.5155 | -10.1885 | -8.8905 | -1.4837 |  | -4.4635 | -4.4404 | 4.0058 | 3.3717 | 3.3565 | 1.0116 | 10.6041 | 14.0772 | 14.7009 | 11.0273 | -0.0004 | -0.0025 | 0.0003 | 0.0035 | 0.0003 | -0.0006 | 0.0128 | -0.0148 | 0.0157 | -360.1711 | 17.5239 | -360.5496 | 17.8258 | -360.8697 | 18.0906 | -360.9712 | 17.5773 | -352.829 | 18.7395 | -352.8444 | 16.8012
11:39 | 1175 | 20.5026 | 194.0164 | 434.7279 | 441.1935 | -21.9587 | -47.7181 | 0.6564 | -0.6435 | -8.1196 | -7.9348 | -3.7453 | -4.1931 | 1.7031 | -5.0932 | 0.5818 | 0.6361 | 0.9436 | 0.6878 | -131.2458 | -7.7791 | -0.7349 | -2.6058 | -10.2688 | -8.89 | -1.5364 |  | -4.5027 | -4.4469 | 4.0066 | 3.3714 | 3.3521 | 1.0116 | 10.6305 | 14.0754 | 14.685 | 11.0005 | 0.0004 | -0.0028 | 0.0009 | 0.0037 | 0.0009 | -0.0003 | 0.0176 | -0.0021 | -0.021 | -360.1804 | 17.5383 | -360.6112 | 17.8381 | -360.9404 | 18.1255 | -360.9774 | 17.5876 | -352.8383 | 18.7785 | -352.8783 | 16.8074
11:39 | 1176 | 20.5789 | 194.1042 | 434.794 | 441.2212 | -22.0086 | -47.7014 | 0.7469 | -0.6417 | -8.0202 | -7.828 | -3.6695 | -4.3545 | 1.6004 | -5.1483 | 0.5824 | 0.6324 | 0.9461 | 0.6891 | -131.2696 | -7.6894 | -0.7752 | -2.5744 | -10.1994 | -8.8563 | -1.5827 |  | -4.4531 | -4.4517 | 4.0078 | 3.3756 | 3.3555 | 1.0117 | 10.6296 | 14.091 | 14.6621 | 11.001 | 0.0001 | -0.0032 | 0.0009 | 0.004 | 0.0001 | -0.0004 | 0.004 | 0.0014 | -0.0053 | -360.1588 | 17.5178 | -360.5496 | 17.8258 | -360.9127 | 18.1029 | -360.9558 | 17.5753 | -352.829 | 18.7436 | -352.8321 | 16.795
11:39 | 1177 | 20.6089 | 194.0088 | 434.7325 | 441.1747 | -21.946 | -47.7267 | 0.7733 | -0.5664 | -8.0882 | -7.7314 | -3.5914 | -4.2854 | 1.7169 | -5.128 | 0.5817 | 0.6335 | 0.9454 | 0.6891 | -131.3634 | -7.7361 | -0.7517 | -2.532 | -10.1492 | -8.869 | -1.511 |  | -4.4367 | -4.326 | 4.0076 | 3.3707 | 3.3559 | 1.0105 | 10.6216 | 14.0597 | 14.6999 | 11.0219 | -0.0003 | -0.0027 | 0.0003 | 0.0034 | 0.0006 | -0.0006 | 0.0163 | -0.0155 | -0.014 | -360.1804 | 17.5363 | -360.6173 | 17.8401 | -360.9158 | 18.1296 | -361.0081 | 17.5876 | -352.8567 | 18.762 | -352.9091 | 16.8053
11:39 | 1178 | 20.7191 | 194.0807 | 434.9318 | 441.3316 | -21.9466 | -47.7924 | 0.7651 | -0.5811 | -8.1437 | -7.8735 | -3.6936 | -4.2814 | 1.7148 | -5.1335 | 0.5811 | 0.6346 | 0.9458 | 0.6896 | -131.2306 | -7.6595 | -0.7435 | -2.4919 | -10.22 | -8.9975 | -1.5271 |  | -4.471 | -4.4938 | 4.0072 | 3.3752 | 3.3561 | 1.0119 | 10.6006 | 14.0911 | 14.6979 | 10.9948 | -0.0002 | -0.0026 | 0.0008 | 0.0039 | 0.0006 | -0.0003 | 0.0103 | -0.0063 | -0.0216 | -360.1958 | 17.5239 | -360.5527 | 17.8155 | -360.8943 | 18.1132 | -360.9497 | 17.5732 | -352.8444 | 18.7497 | -352.8383 | 16.7889
11:39 | 1179 | 20.5391 | 194.1317 | 434.9142 | 441.1985 | -21.8891 | -47.7525 | 0.7822 | -0.6249 | -8.07 | -7.8561 | -3.5924 | -4.2287 | 1.729 | -5.131 | 0.5804 | 0.6319 | 0.9485 | 0.69 | -131.1899 | -7.6776 | -0.6138 | -2.5834 | -10.1728 | -8.9327 | -1.5186 |  | -4.5085 | -4.4375 | 4.0061 | 3.3712 | 3.3557 | 1.012 | 10.6088 | 14.0759 | 14.6812 | 11.0151 | -0.0005 | -0.0029 | 0.0004 | 0.0034 | 0.0006 | -0.0008 | 0.0114 | -0.0163 | -0.02 | -360.1588 | 17.5404 | -360.6235 | 17.8525 | -360.9312 | 18.1276 | -360.9651 | 17.5773 | -352.8506 | 18.7723 | -352.8937 | 16.8156
11:39 | 1180 | 20.5952 | 194.0457 | 434.9704 | 441.2049 | -21.8377 | -47.6535 | 0.9116 | -0.6425 | -8.122 | -7.9522 | -3.5985 | -4.2124 | 1.882 | -5.0913 | 0.5802 | 0.6318 | 0.9476 | 0.6897 | -131.2227 | -7.6101 | -0.6315 | -2.6418 | -10.1368 | -9.0202 | -1.5338 |  | -4.6059 | -4.3949 | 4.0054 | 3.3739 | 3.3588 | 1.0119 | 10.6318 | 14.0705 | 14.6496 | 10.9966 | 0.0002 | -0.0032 | 0.001 | 0.0036 | 0.001 | -0.0004 | 0.0029 | -0.0135 | -0.0044 | -360.1404 | 17.5424 | -360.5989 | 17.8258 | -360.9004 | 18.1153 | -360.9374 | 17.5404 | -352.8229 | 18.7661 | -352.9029 | 16.8053
11:39 | 1181 | 20.6914 | 194.0858 | 434.9788 | 441.2285 | -21.8443 | -47.6034 | 0.8059 | -0.7208 | -8.1164 | -7.8432 | -3.5779 | -4.3198 | 1.7396 | -5.1748 | 0.5808 | 0.6351 | 0.9479 | 0.6898 | -131.1751 | -7.5496 | -0.6555 | -2.6793 | -10.226 | -8.9079 | -1.6045 |  | -4.5403 | -4.3134 | 4.0059 | 3.371 | 3.3575 | 1.0134 | 10.6112 | 14.0897 | 14.6944 | 11.0292 | -0.0001 | -0.0033 | 0.0006 | 0.0034 | 0 | -0.0007 | 0.0127 | 0.0077 | -0.0109 | -360.1804 | 17.5301 | -360.5896 | 17.8525 | -360.9281 | 18.1296 | -360.9804 | 17.5629 | -352.8906 | 18.7641 | -352.8844 | 16.8135
11:39 | 1182 | 20.6189 | 194.1167 | 434.8783 | 441.1877 | -21.8755 | -47.6986 | 0.8083 | -0.8099 | -8.2284 | -7.82 | -3.6512 | -4.2655 | 1.7426 | -5.254 | 0.5807 | 0.6345 | 0.9472 | 0.6886 | -131.2411 | -7.5864 | -0.8054 | -2.6756 | -10.2373 | -8.9598 | -1.5612 |  | -4.5654 | -4.3318 | 4.0068 | 3.3741 | 3.3549 | 1.0125 | 10.6087 | 14.0935 | 14.6948 | 11.0316 | -0.0005 | -0.0026 | 0.0007 | 0.0035 | 0.001 | -0.0008 | 0.0115 | -0.0128 | -0.0032 | -360.165 | 17.526 | -360.5527 | 17.8217 | -360.9066 | 18.1132 | -360.962 | 17.5527 | -352.8229 | 18.7271 | -352.8137 | 16.7971
11:39 | 1183 | 20.6445 | 194.1155 | 434.9006 | 441.1931 | -21.846 | -47.5702 | 0.884 | -0.7669 | -8.246 | -7.7127 | -3.6236 | -4.2527 | 1.6987 | -5.2365 | 0.5811 | 0.6316 | 0.9453 | 0.6883 | -131.2098 | -7.5701 | -0.6654 | -2.5404 | -10.1263 | -8.8565 | -1.4711 |  | -4.4602 | -4.4621 | 4.0056 | 3.3726 | 3.3556 | 1.0109 | 10.6549 | 14.1169 | 14.7201 | 11.0424 | -0.0002 | -0.0026 | 0.0007 | 0.0036 | 0.0001 | -0.0004 | 0.0077 | 0.0039 | -0.0074 | -360.1835 | 17.5198 | -360.5558 | 17.8175 | -360.8943 | 18.1276 | -361.042 | 17.5855 | -352.8691 | 18.7436 | -352.8414 | 16.7909
11:39 | 1184 | 20.6633 | 194.0857 | 434.8214 | 441.2238 | -21.9068 | -47.6966 | 0.847 | -0.7125 | -8.1944 | -7.7704 | -3.5908 | -4.2059 | 1.6949 | -5.198 | 0.5788 | 0.6299 | 0.9453 | 0.6902 | -131.2024 | -7.5534 | -0.7866 | -2.4452 | -10.1538 | -8.9392 | -1.5198 |  | -4.4073 | -4.4455 | 4.0061 | 3.3725 | 3.3549 | 1.0117 | 10.6272 | 14.1005 | 14.7136 | 11.0154 | 0.0003 | -0.0028 | 0.0006 | 0.0039 | 0.0003 | -0.001 | 0.0205 | -0.0023 | -0.0015 | -360.205 | 17.5506 | -360.5589 | 17.8073 | -360.8727 | 18.105 | -360.9589 | 17.5609 | -352.8598 | 18.762 | -352.8537 | 16.7807
11:39 | 1185 | 20.6904 | 194.0926 | 435.0143 | 441.1685 | -21.8102 | -47.7253 | 0.8661 | -0.6903 | -8.1729 | -7.8993 | -3.594 | -4.3195 | 1.645 | -5.2684 | 0.5806 | 0.6336 | 0.9427 | 0.6891 | -131.2395 | -7.6682 | -0.7981 | -2.4516 | -10.1328 | -8.8978 | -1.4533 |  | -4.5088 | -4.51 | 4.0055 | 3.3729 | 3.3524 | 1.0126 | 10.6455 | 14.1138 | 14.7134 | 11.0265 | 0.0002 | -0.003 | 0.0007 | 0.0038 | 0.0005 | -0.0004 | 0.0037 | 0.0075 | 0.0043 | -360.1896 | 17.5363 | -360.6173 | 17.8566 | -360.9435 | 18.1071 | -360.9589 | 17.5547 | -352.8229 | 18.7641 | -352.8967 | 16.8299
11:39 | 1186 | 20.6167 | 194.2001 | 435.0096 | 441.1879 | -21.8458 | -47.6762 | 0.6879 | -0.6967 | -8.1699 | -7.8883 | -3.5985 | -4.312 | 1.6979 | -5.1947 | 0.5805 | 0.6371 | 0.9477 | 0.6889 | -131.2687 | -7.7758 | -0.7159 | -2.5109 | -10.1786 | -8.8578 | -1.5141 |  | -4.4976 | -4.41 | 4.0051 | 3.3708 | 3.3569 | 1.0121 | 10.6296 | 14.1143 | 14.6921 | 11.0064 | -0.0008 | -0.0031 | 0.0006 | 0.0034 | 0.0005 | -0.0012 | -0.0004 | 0.0011 | -0.0189 | -360.1096 | 17.5157 | -360.5927 | 17.8463 | -360.9497 | 18.1296 | -360.9589 | 17.5424 | -352.7829 | 18.7456 | -352.8721 | 16.8156
11:39 | 1187 | 20.7073 | 194.1235 | 434.9368 | 441.1845 | -21.9651 | -47.8449 | 0.7468 | -0.7687 | -8.1732 | -7.8468 | -3.7548 | -4.3575 | 1.6917 | -5.2317 | 0.5796 | 0.6339 | 0.9475 | 0.69 | -131.2782 | -7.7102 | -0.8381 | -2.2806 | -10.1313 | -8.8902 | -1.4403 |  | -4.4947 | -4.5334 | 4.0059 | 3.3682 | 3.3541 | 1.0114 | 10.6202 | 14.1052 | 14.6785 | 11.0082 | -0.0001 | -0.0023 | 0.0007 | 0.0039 | 0.0008 | -0.0004 | 0.0049 | -0.0204 | -0.0124 | -360.1619 | 17.5219 | -360.5681 | 17.8237 | -360.9466 | 18.1276 | -360.9866 | 17.5527 | -352.866 | 18.7497 | -352.8506 | 16.8053
11:40 | 1188 | 20.6467 | 194.1226 | 434.9868 | 441.2256 | -21.965 | -47.8764 | 0.7092 | -0.7494 | -8.1639 | -7.8098 | -3.6708 | -4.3172 | 1.7309 | -5.2296 | 0.581 | 0.6333 | 0.9469 | 0.6881 | -131.2398 | -7.6383 | -0.7488 | -2.2943 | -10.2375 | -8.8603 | -1.4509 |  | -4.4983 | -4.4012 | 4.0063 | 3.3721 | 3.3573 | 1.0122 | 10.6295 | 14.0739 | 14.6584 | 11.006 | -0.0004 | -0.0031 | 0.0004 | 0.0033 | 0.001 | -0.0006 | 0.0112 | -0.005 | -0.0192 | -360.2296 | 17.5445 | -360.5989 | 17.8134 | -360.9004 | 18.1091 | -360.9835 | 17.5753 | -352.8506 | 18.7723 | -352.8598 | 16.7827
11:40 | 1189 | 20.6241 | 194.0167 | 434.8449 | 441.2601 | -21.8428 | -47.9183 | 0.6895 | -0.7921 | -8.0985 | -7.8272 | -3.5795 | -4.3547 | 1.6348 | -5.2689 | 0.58 | 0.6363 | 0.9445 | 0.688 | -131.3229 | -7.676 | -0.7361 | -2.3182 | -10.1346 | -8.8057 | -1.423 |  | -4.4306 | -4.4062 | 4.0044 | 3.3727 | 3.3553 | 1.0108 | 10.6261 | 14.0993 | 14.6659 | 11.0028 | 0.0002 | -0.0031 | 0.0005 | 0.0034 | 0.0007 | -0.0007 | 0.0121 | -0.0133 | -0.0139 | -360.1958 | 17.5568 | -360.5989 | 17.8155 | -360.8789 | 18.0824 | -360.9466 | 17.5588 | -352.866 | 18.7887 | -352.8875 | 16.8012
11:40 | 1190 | 20.7101 | 194.1916 | 434.9734 | 441.2632 | -21.7806 | -47.7289 | 0.7194 | -0.7432 | -8.1232 | -7.7978 | -3.6196 | -4.3454 | 1.6966 | -5.1808 | 0.5792 | 0.6339 | 0.9459 | 0.6902 | -131.1771 | -7.6114 | -0.6532 | -2.1457 | -10.1322 | -8.7919 | -1.4263 |  | -4.5202 | -4.3832 | 4.0065 | 3.3735 | 3.3553 | 1.0127 | 10.5729 | 14.0575 | 14.6519 | 10.9674 | 0.0002 | -0.003 | 0.0009 | 0.0038 | 0.0004 | -0.0005 | 0.0034 | 0.0007 | -0.0098 | -360.2173 | 17.5486 | -360.5989 | 17.8442 | -360.9497 | 18.1132 | -360.9312 | 17.565 | -352.8598 | 18.7703 | -352.8937 | 16.8176
11:40 | 1191 | 20.8492 | 194.2142 | 434.9835 | 441.2465 | -21.7444 | -47.7065 | 0.8422 | -0.6835 | -8.1346 | -7.7419 | -3.6532 | -4.2656 | 1.7408 | -5.1881 | 0.5804 | 0.6349 | 0.9471 | 0.6898 | -131.1822 | -7.6539 | -0.6788 | -2.1834 | -10.1076 | -8.8077 | -1.3671 |  | -4.4871 | -4.3509 | 4.0059 | 3.3729 | 3.3525 | 1.0122 | 10.641 | 14.1147 | 14.7184 | 11.0226 | -0.0003 | -0.0023 | 0.0008 | 0.0037 | 0.0008 | -0.0006 | 0.0052 | -0.012 | -0.0074 | -360.1158 | 17.5013 | -360.5343 | 17.8196 | -360.9312 | 18.1317 | -360.9835 | 17.5486 | -352.8137 | 18.7415 | -352.8414 | 16.8094
11:40 | 1192 | 20.8475 | 194.2192 | 434.9903 | 441.2501 | -21.8417 | -47.6511 | 0.8814 | -0.6701 | -8.1083 | -7.849 | -3.658 | -4.251 | 1.6928 | -5.2816 | 0.5802 | 0.6373 | 0.949 | 0.6899 | -131.1803 | -7.5299 | -0.6714 | -2.3272 | -10.036 | -8.8463 | -1.3722 |  | -4.4014 | -4.3783 | 4.0058 | 3.3716 | 3.3551 | 1.0117 | 10.6145 | 14.0877 | 14.689 | 10.9797 | -0.0002 | -0.0027 | 0.0009 | 0.004 | 0.0008 | 0.0002 | 0.0138 | -0.0035 | 0.0079 | -360.1958 | 17.526 | -360.565 | 17.8217 | -360.9281 | 18.1399 | -361.0358 | 17.5876 | -352.8721 | 18.7497 | -352.8321 | 16.8012
11:40 | 1193 | 20.7151 | 194.1043 | 434.8917 | 441.218 | -21.8248 | -47.7153 | 0.8406 | -0.7595 | -8.1301 | -7.815 | -3.6449 | -4.3332 | 1.6854 | -5.2768 | 0.5818 | 0.6345 | 0.943 | 0.6875 | -131.2455 | -7.702 | -0.6601 | -2.291 | -10.1142 | -8.8679 | -1.439 |  | -4.421 | -4.3607 | 4.005 | 3.3734 | 3.3564 | 1.013 | 10.6097 | 14.1065 | 14.6752 | 11.0262 | 0.0003 | -0.0031 | 0.0008 | 0.0038 | 0.0013 | -0.0007 | 0.0007 | -0.0037 | -0.0148 | -360.1927 | 17.526 | -360.5589 | 17.8175 | -360.882 | 18.105 | -360.9743 | 17.565 | -352.8506 | 18.7518 | -352.8506 | 16.8156
11:40 | 1194 | 20.6766 | 194.0791 | 434.9008 | 441.1843 | -21.7252 | -47.6501 | 0.9617 | -0.8127 | -8.1478 | -7.8024 | -3.7385 | -4.3382 | 1.6958 | -5.3017 | 0.5816 | 0.6342 | 0.9441 | 0.6883 | -131.1891 | -7.5826 | -0.6994 | -2.2399 | -10.1413 | -8.8336 | -1.42 |  | -4.449 | -4.3936 | 4.0041 | 3.3712 | 3.3577 | 1.0119 | 10.6491 | 14.1227 | 14.7375 | 11.0309 | 0 | -0.0029 | 0.0005 | 0.0034 | 0.0003 | -0.0005 | 0.0039 | -0.0159 | -0.0172 | -360.1988 | 17.565 | -360.642 | 17.8525 | -360.9466 | 18.1132 | -360.962 | 17.5506 | -352.8598 | 18.7887 | -352.9152 | 16.8361
11:40 | 1195 | 20.7425 | 194.062 | 434.9544 | 441.1929 | -21.678 | -47.5882 | 0.9394 | -0.7814 | -8.142 | -7.7232 | -3.7145 | -4.3443 | 1.7041 | -5.2355 | 0.5809 | 0.6338 | 0.9414 | 0.6902 | -131.1965 | -7.5422 | -0.7198 | -2.2718 | -10.1512 | -8.8212 | -1.3147 |  | -4.4196 | -4.3589 | 4.0054 | 3.372 | 3.3554 | 1.0115 | 10.5788 | 14.0688 | 14.6614 | 10.9682 | -0.0005 | -0.0027 | 0.0008 | 0.0039 | 0.0004 | -0.001 | 0.0053 | -0.0136 | -0.0124 | -360.1711 | 17.528 | -360.6019 | 17.8422 | -360.9404 | 18.0988 | -360.9281 | 17.5239 | -352.8198 | 18.7538 | -352.8691 | 16.834
11:40 | 1196 | 20.8551 | 194.0998 | 434.8893 | 441.2363 | -21.7412 | -47.5339 | 0.9413 | -0.7562 | -8.145 | -7.8713 | -3.6499 | -4.1987 | 1.6534 | -5.2091 | 0.5809 | 0.6375 | 0.9417 | 0.6884 | -131.2209 | -7.5784 | -0.7603 | -2.2769 | -10.2524 | -8.8119 | -1.4428 |  | -4.4577 | -4.3162 | 4.0064 | 3.3711 | 3.3553 | 1.0134 | 10.6296 | 14.0621 | 14.691 | 11.0068 | -0.0002 | -0.0024 | 0.001 | 0.0037 | 0.0006 | -0.001 | 0.0027 | 0.0028 | 0.001 | -360.1527 | 17.5404 | -360.5958 | 17.836 | -360.9497 | 18.1276 | -360.9804 | 17.5691 | -352.8475 | 18.76 | -352.8783 | 16.834
11:40 | 1197 | 20.8344 | 194.2098 | 434.9417 | 441.298 | -21.7783 | -47.6588 | 0.9613 | -0.6935 | -8.0628 | -7.7649 | -3.5358 | -4.2677 | 1.6416 | -5.1383 | 0.5817 | 0.6345 | 0.9444 | 0.6881 | -131.1809 | -7.4878 | -0.8189 | -2.1484 | -10.0807 | -8.721 | -1.3433 |  | -4.4155 | -4.2853 | 4.0056 | 3.3684 | 3.3543 | 1.0124 | 10.6399 | 14.0844 | 14.7102 | 11.0276 | 0.0001 | -0.0033 | 0.001 | 0.004 | 0.0005 | -0.0005 | 0.0148 | -0.0001 | 0.0012 | -360.1804 | 17.5075 | -360.5096 | 17.8073 | -360.8943 | 18.105 | -361.0081 | 17.5732 | -352.8598 | 18.7538 | -352.7983 | 16.793
11:40 | 1198 | 20.9425 | 194.2696 | 435.0677 | 441.2654 | -21.8031 | -47.6325 | 0.9179 | -0.7253 | -8.0634 | -7.8563 | -3.6647 | -4.263 | 1.6518 | -5.1045 | 0.5816 | 0.6343 | 0.9476 | 0.6896 | -131.2104 | -7.5335 | -0.738 | -2.1334 | -9.9932 | -8.7337 | -1.3143 |  | -4.4195 | -4.321 | 4.0048 | 3.3666 | 3.3541 | 1.0111 | 10.5985 | 14.0307 | 14.6583 | 10.9703 | 0 | -0.0033 | 0.0005 | 0.0034 | 0.0006 | -0.0012 | 0.0149 | -0.0123 | -0.0356 | -360.2542 | 17.5588 | -360.5835 | 17.8217 | -360.8912 | 18.1173 | -360.9958 | 17.5876 | -352.9183 | 18.7846 | -352.8567 | 16.8053
11:40 | 1199 | 20.7975 | 194.2369 | 435.1231 | 441.2367 | -21.6921 | -47.6649 | 0.9576 | -0.6772 | -8.1113 | -7.8973 | -3.7298 | -4.2061 | 1.7559 | -5.1358 | 0.5811 | 0.6316 | 0.9489 | 0.6891 | -131.2502 | -7.5313 | -0.7277 | -2.1095 | -10.0016 | -8.6848 | -1.3386 |  | -4.3662 | -4.369 | 4.0064 | 3.3726 | 3.3557 | 1.012 | 10.6283 | 14.0961 | 14.6997 | 10.9926 | 0.0002 | -0.0024 | 0.0008 | 0.0037 | 0.0005 | -0.0001 | 0.0163 | -0.0112 | -0.0008 | -360.165 | 17.528 | -360.5619 | 17.8299 | -360.8943 | 18.1091 | -360.9374 | 17.5445 | -352.8444 | 18.7538 | -352.8444 | 16.8135
11:40 | 1200 | 20.9143 | 194.2534 | 435.0571 | 441.3132 | -21.7169 | -47.5894 | 0.894 | -0.6336 | -8.0941 | -7.7352 | -3.5742 | -4.1884 | 1.656 | -5.122 | 0.5805 | 0.6294 | 0.9497 | 0.6876 | -131.1935 | -7.5495 | -0.635 | -2.1892 | -10.0809 | -8.8318 | -1.3437 |  | -4.4173 | -4.4063 | 4.005 | 3.3701 | 3.355 | 1.0115 | 10.6019 | 14.0921 | 14.6971 | 10.9967 | -0.0005 | -0.0029 | 0.0004 | 0.0036 | 0.0011 | -0.0005 | 0.0342 | -0.0125 | -0.0354 | -360.1127 | 17.526 | -360.6112 | 17.8627 | -360.9712 | 18.1235 | -360.9651 | 17.5465 | -352.8106 | 18.7538 | -352.906 | 16.8484
11:40 | 1201 | 20.7753 | 194.166 | 435.071 | 441.2792 | -21.7051 | -47.6396 | 0.8738 | -0.6837 | -8.0806 | -7.6234 | -3.5901 | -4.2514 | 1.6572 | -5.1489 | 0.5801 | 0.6313 | 0.9468 | 0.6891 | -131.1935 | -7.5031 | -0.5829 | -2.2388 | -10.0907 | -8.761 | -1.3723 |  | -4.4198 | -4.3434 | 4.0045 | 3.37 | 3.3553 | 1.0125 | 10.6169 | 14.0842 | 14.6792 | 10.9937 | -0.0002 | -0.003 | 0.0005 | 0.0038 | 0.0004 | -0.0002 | 0.0121 | -0.0158 | 0.0004 | -360.1527 | 17.5219 | -360.5743 | 17.836 | -360.9466 | 18.1296 | -360.9651 | 17.5363 | -352.829 | 18.7518 | -352.8352 | 16.8299
11:40 | 1202 | 20.7752 | 194.2021 | 435.0843 | 441.2663 | -21.7502 | -47.6064 | 0.9272 | -0.6372 | -8.0423 | -7.6631 | -3.5878 | -4.257 | 1.6974 | -5.0293 | 0.5799 | 0.6341 | 0.9483 | 0.6906 | -131.135 | -7.5005 | -0.6409 | -2.1126 | -10.0459 | -8.6979 | -1.31 |  | -4.3878 | -4.2918 | 4.0037 | 3.3694 | 3.3531 | 1.0136 | 10.6307 | 14.0925 | 14.6945 | 11.0013 | -0.0001 | -0.0033 | 0.0004 | 0.0037 | 0.0008 | -0.0006 | -0.0095 | -0.0001 | -0.0293 | -360.165 | 17.5157 | -360.5496 | 17.8217 | -360.885 | 18.105 | -360.9743 | 17.5732 | -352.8383 | 18.7497 | -352.8844 | 16.8135
11:40 | 1203 | 20.7387 | 194.2018 | 435.1568 | 441.2176 | -21.7401 | -47.502 | 0.9205 | -0.6701 | -8.0662 | -7.7616 | -3.6154 | -4.2697 | 1.6987 | -5.1343 | 0.5809 | 0.6349 | 0.9466 | 0.6907 | -131.1609 | -7.4679 | -0.723 | -2.1773 | -10.0345 | -8.733 | -1.331 |  | -4.3251 | -4.3449 | 4.0047 | 3.3728 | 3.3572 | 1.013 | 10.6296 | 14.1141 | 14.691 | 11.0183 | -0.0002 | -0.0032 | 0.0007 | 0.0036 | 0.0003 | -0.0006 | 0.0121 | -0.0047 | -0.0133 | -360.245 | 17.5568 | -360.6327 | 17.834 | -360.8974 | 18.105 | -360.9804 | 17.5691 | -352.8721 | 18.7887 | -352.8752 | 16.8135
11:40 | 1204 | 20.8583 | 194.2437 | 435.1573 | 441.273 | -21.7554 | -47.4905 | 0.9154 | -0.6417 | -8.1045 | -7.8276 | -3.6825 | -4.1944 | 1.759 | -5.1527 | 0.5821 | 0.6357 | 0.9441 | 0.6916 | -131.0915 | -7.4744 | -0.7326 | -2.1742 | -10.0437 | -8.7375 | -1.296 |  | -4.3958 | -4.3916 | 4.003 | 3.3695 | 3.3559 | 1.0125 | 10.6146 | 14.0876 | 14.6706 | 11.0031 | -0.0005 | -0.0028 | 0.0007 | 0.0041 | 0.0005 | -0.0008 | 0.0002 | -0.0028 | -0.0197 | -360.1527 | 17.5301 | -360.5619 | 17.8278 | -360.8943 | 18.0865 | -360.9035 | 17.565 | -352.8475 | 18.76 | -352.8321 | 16.8197
11:40 | 1205 | 20.8712 | 194.1846 | 435.0839 | 441.2566 | -21.7568 | -47.4685 | 0.9785 | -0.6419 | -8.0982 | -7.7459 | -3.6752 | -4.1176 | 1.8059 | -5.102 | 0.5809 | 0.6359 | 0.9503 | 0.69 | -131.0876 | -7.439 | -0.7732 | -2.2442 | -10.0369 | -8.6863 | -1.295 |  | -4.3581 | -4.4725 | 4.0027 | 3.3698 | 3.354 | 1.0135 | 10.6319 | 14.0646 | 14.6717 | 11.0259 | -0.0004 | -0.0028 | 0.0009 | 0.004 | 0.0011 | -0.0005 | 0.0106 | -0.022 | -0.0124 | -360.1558 | 17.5321 | -360.605 | 17.8545 | -360.9251 | 18.1255 | -361.0081 | 17.565 | -352.8383 | 18.7723 | -352.8906 | 16.8423
11:40 | 1206 | 20.8969 | 194.1916 | 435.0973 | 441.3301 | -21.7316 | -47.5378 | 0.9511 | -0.6643 | -8.1286 | -7.7616 | -3.6878 | -4.1235 | 1.6754 | -5.1581 | 0.5809 | 0.6338 | 0.9515 | 0.6887 | -131.0041 | -7.4652 | -0.7163 | -2.1925 | -10.098 | -8.6896 | -1.3202 |  | -4.284 | -4.3339 | 4.0042 | 3.3712 | 3.3577 | 1.013 | 10.6296 | 14.0911 | 14.6979 | 10.9948 | 0 | -0.0031 | 0.0009 | 0.0038 | -0.0001 | -0.0009 | 0.0181 | -0.024 | -0.0142 | -360.1311 | 17.5137 | -360.5404 | 17.8155 | -360.8912 | 18.1235 | -360.9681 | 17.5465 | -352.8106 | 18.7477 | -352.829 | 16.8053
11:40 | 1207 | 20.9683 | 194.2573 | 435.1691 | 441.2855 | -21.6785 | -47.5186 | 1.0439 | -0.658 | -8.0852 | -7.7516 | -3.6126 | -4.1442 | 1.7498 | -5.1374 | 0.5804 | 0.6291 | 0.945 | 0.688 | -131.0699 | -7.448 | -0.6837 | -2.1601 | -10.0817 | -8.7624 | -1.3164 |  | -4.3582 | -4.4434 | 4.0042 | 3.3725 | 3.3548 | 1.0122 | 10.6248 | 14.081 | 14.7071 | 11.0356 | 0 | -0.0035 | 0.0008 | 0.0038 | 0.0008 | -0.0007 | 0.0038 | -0.0043 | -0.0003 | -360.1804 | 17.5198 | -360.5773 | 17.8381 | -360.9281 | 18.1029 | -360.9835 | 17.5671 | -352.8814 | 18.7682 | -352.866 | 16.8279
11:40 | 1208 | 20.9076 | 194.2535 | 435.0905 | 441.2156 | -21.7823 | -47.5573 | 0.9723 | -0.7034 | -8.0804 | -7.6954 | -3.6011 | -4.2117 | 1.7595 | -5.0902 | 0.5798 | 0.6343 | 0.9472 | 0.6883 | -130.9631 | -7.3645 | -0.6252 | -2.1601 | -9.9169 | -8.6878 | -1.2204 |  | -4.3141 | -4.3775 | 4.0045 | 3.3698 | 3.3555 | 1.0144 | 10.6479 | 14.1043 | 14.685 | 11.0236 | -0.0002 | -0.003 | 0 | 0.0031 | 0.0001 | -0.0003 | -0.0052 | -0.0092 | -0.0004 | -360.1835 | 17.5424 | -360.6019 | 17.8196 | -360.9189 | 18.1112 | -360.9251 | 17.5506 | -352.8352 | 18.762 | -352.8598 | 16.8074
11:40 | 1209 | 20.8269 | 194.1709 | 435.044 | 441.2602 | -21.8441 | -47.7276 | 0.7732 | -0.7043 | -8.0964 | -7.6842 | -3.6163 | -4.207 | 1.8022 | -5.0869 | 0.5806 | 0.6343 | 0.9455 | 0.6883 | -131.0477 | -7.4268 | -0.6503 | -2.1493 | -9.9212 | -8.6479 | -1.3108 |  | -4.3591 | -4.3478 | 4.003 | 3.3685 | 3.3568 | 1.0114 | 10.6204 | 14.1049 | 14.688 | 11.0089 | -0.0008 | -0.0032 | 0.0006 | 0.0036 | 0.0005 | -0.0013 | 0.006 | -0.0037 | -0.0074 | -360.1281 | 17.528 | -360.5743 | 17.8299 | -360.9158 | 18.1091 | -360.9712 | 17.5609 | -352.8506 | 18.762 | -352.8814 | 16.8217
11:40 | 1210 | 20.8387 | 194.1652 | 435.073 | 441.3097 | -21.8202 | -47.7308 | 0.8731 | -0.6772 | -8.1178 | -7.6924 | -3.6353 | -4.1402 | 1.7348 | -5.1416 | 0.5802 | 0.6337 | 0.9496 | 0.6887 | -131.0767 | -7.5063 | -0.6644 | -2.22 | -9.9648 | -8.7701 | -1.3398 |  | -4.3487 | -4.3481 | 4.0038 | 3.3716 | 3.3566 | 1.0117 | 10.6342 | 14.0727 | 14.6802 | 11.0222 | -0.0003 | -0.0031 | 0.0006 | 0.0032 | 0.0003 | -0.0005 | -0.0013 | -0.0193 | -0.018 | -360.165 | 17.5321 | -360.6019 | 17.8401 | -360.885 | 18.1214 | -360.9835 | 17.5609 | -352.8044 | 18.7518 | -352.8814 | 16.8258
11:40 | 1211 | 20.859 | 194.1462 | 435.0881 | 441.3027 | -21.7714 | -47.6918 | 0.8217 | -0.7235 | -8.0168 | -7.7106 | -3.6584 | -4.1794 | 1.7491 | -5.0728 | 0.58 | 0.6317 | 0.9468 | 0.6868 | -131.0777 | -7.4297 | -0.6396 | -2.3038 | -9.8886 | -8.8798 | -1.3687 |  | -4.3394 | -4.3141 | 4.0048 | 3.3699 | 3.3536 | 1.0128 | 10.6284 | 14.1132 | 14.6918 | 11.0454 | 0.0003 | -0.003 | 0.0004 | 0.0036 | 0.0005 | -0.0011 | 0.0086 | -0.0082 | -0.0063 | -360.1773 | 17.5363 | -360.5835 | 17.8299 | -360.9189 | 18.1132 | -360.962 | 17.5691 | -352.8567 | 18.7559 | -352.8567 | 16.8238
11:40 | 1212 | 20.7975 | 194.1648 | 435.0449 | 441.2169 | -21.8061 | -47.6837 | 0.8244 | -0.6586 | -7.9911 | -7.5812 | -3.5668 | -4.1305 | 1.7308 | -5.0715 | 0.5815 | 0.6365 | 0.9492 | 0.6863 | -130.9949 | -7.4017 | -0.6715 | -2.2837 | -9.879 | -8.6745 | -1.3317 |  | -4.3531 | -4.3204 | 4.005 | 3.3701 | 3.3529 | 1.012 | 10.5938 | 14.0725 | 14.6665 | 10.9999 | -0.0001 | -0.0034 | 0.0012 | 0.0042 | 0.0006 | -0.0006 | 0.0012 | -0.0058 | 0.0062 | -360.1958 | 17.5363 | -360.565 | 17.8278 | -360.9035 | 18.1009 | -360.9589 | 17.5691 | -352.8537 | 18.76 | -352.8567 | 16.8135
11:40 | 1213 | 20.7814 | 194.1844 | 435.1146 | 441.2227 | -21.7101 | -47.641 | 0.8173 | -0.6563 | -7.9728 | -7.6744 | -3.6168 | -4.1525 | 1.716 | -5.1326 | 0.5815 | 0.632 | 0.9483 | 0.687 | -131.0535 | -7.4552 | -0.6372 | -2.3315 | -9.8686 | -8.7035 | -1.385 |  | -4.3049 | -4.3127 | 4.0041 | 3.3713 | 3.3569 | 1.0126 | 10.6108 | 14.1021 | 14.6834 | 10.9691 | -0.0002 | -0.0025 | 0.0009 | 0.0037 | 0.0012 | -0.0005 | 0.0068 | 0.0019 | -0.0066 | -360.1711 | 17.5321 | -360.5773 | 17.8401 | -360.8727 | 18.1112 | -360.9651 | 17.5609 | -352.8414 | 18.7764 | -352.8906 | 16.8279
11:40 | 1214 | 20.8325 | 194.2734 | 435.087 | 441.2693 | -21.8028 | -47.6859 | 0.7569 | -0.6796 | -8.0357 | -7.6434 | -3.6026 | -4.1098 | 1.7259 | -5.1264 | 0.5814 | 0.6357 | 0.9477 | 0.6894 | -131.0021 | -7.3355 | -0.6118 | -2.3771 | -10.0199 | -8.8472 | -1.379 |  | -4.3639 | -4.3464 | 4.0055 | 3.3724 | 3.353 | 1.0129 | 10.6378 | 14.07 | 14.7148 | 11.0039 | -0.0003 | -0.0027 | 0.0002 | 0.0036 | 0.0007 | -0.0008 | -0.0018 | -0.0097 | -0.0039 | -360.1927 | 17.5219 | -360.5558 | 17.834 | -360.9066 | 18.1194 | -360.9589 | 17.5486 | -352.8383 | 18.7559 | -352.8506 | 16.8115
11:40 | 1215 | 20.8561 | 194.1997 | 435.0909 | 441.2919 | -21.8815 | -47.6928 | 0.8063 | -0.6723 | -7.9889 | -7.743 | -3.6368 | -4.0901 | 1.7158 | -5.2152 | 0.5802 | 0.6306 | 0.9454 | 0.6874 | -131.0049 | -7.3039 | -0.5345 | -2.3021 | -9.9694 | -8.6991 | -1.3096 |  | -4.3548 | -4.3007 | 4.006 | 3.3712 | 3.3534 | 1.0128 | 10.6305 | 14.1332 | 14.685 | 11.0468 | 0 | -0.0029 | 0.0005 | 0.0035 | 0.0007 | 0.0001 | 0.0126 | 0.0024 | -0.0104 | -360.1465 | 17.5219 | -360.5958 | 17.8442 | -360.9312 | 18.1112 | -360.9927 | 17.5691 | -352.8321 | 18.7518 | -352.8506 | 16.8299
11:40 | 1216 | 20.8003 | 194.2018 | 435.0644 | 441.3849 | -21.7766 | -47.6168 | 0.8108 | -0.6951 | -7.9843 | -7.7772 | -3.6036 | -4.1432 | 1.7178 | -5.1068 | 0.5804 | 0.6349 | 0.9495 | 0.6876 | -131.1231 | -7.4271 | -0.6005 | -2.1418 | -9.9313 | -8.6021 | -1.3196 |  | -4.3837 | -4.2927 | 4.0036 | 3.3693 | 3.3567 | 1.0118 | 10.6317 | 14.1169 | 14.6854 | 10.9731 | 0.0001 | -0.003 | 0.0003 | 0.0038 | 0.0012 | -0.0004 | 0.0008 | -0.001 | -0.0208 | -360.1927 | 17.5321 | -360.5619 | 17.8093 | -360.9035 | 18.1153 | -360.962 | 17.5609 | -352.8321 | 18.7538 | -352.826 | 16.8053
11:40 | 1217 | 20.8703 | 194.2346 | 435.1741 | 441.294 | -21.7805 | -47.5932 | 0.9406 | -0.7186 | -7.8885 | -7.6636 | -3.6557 | -4.1436 | 1.6562 | -5.1724 | 0.5804 | 0.6337 | 0.9479 | 0.6874 | -131.0232 | -7.3117 | -0.5332 | -2.1153 | -9.959 | -8.6702 | -1.3432 |  | -4.3265 | -4.2298 | 4.0046 | 3.3703 | 3.3558 | 1.0139 | 10.6298 | 14.0964 | 14.6879 | 10.9906 | -0.0007 | -0.0032 | 0.0001 | 0.0031 | -0.0001 | -0.0004 | -0.0019 | -0.0032 | -0.018 | -360.2173 | 17.5445 | -360.6019 | 17.8442 | -360.9097 | 18.1029 | -360.9558 | 17.5691 | -352.8691 | 18.7867 | -352.9152 | 16.8238
11:40 | 1218 | 20.9279 | 194.3205 | 435.1779 | 441.3619 | -21.6544 | -47.7252 | 0.9355 | -0.7279 | -7.9744 | -7.6633 | -3.6378 | -4.1994 | 1.6487 | -5.1862 | 0.5793 | 0.6298 | 0.9463 | 0.6863 | -131.0092 | -7.2838 | -0.6334 | -2.1918 | -10.004 | -8.7108 | -1.331 |  | -4.3851 | -4.3554 | 4.0053 | 3.3684 | 3.3534 | 1.0132 | 10.6016 | 14.0638 | 14.6793 | 11.0121 | -0.0001 | -0.0026 | 0.0011 | 0.0041 | 0.0009 | -0.0008 | -0.0074 | -0.0141 | -0.0122 | -360.1558 | 17.5404 | -360.6019 | 17.8299 | -360.885 | 18.0927 | -360.9497 | 17.5424 | -352.7767 | 18.7682 | -352.8629 | 16.8197
11:40 | 1219 | 20.9745 | 194.3289 | 435.1447 | 441.3206 | -21.7621 | -47.6637 | 0.9238 | -0.6929 | -7.987 | -7.7001 | -3.6069 | -4.2183 | 1.6441 | -5.1228 | 0.579 | 0.6302 | 0.9446 | 0.687 | -130.9987 | -7.2572 | -0.5686 | -2.1108 | -9.9603 | -8.6369 | -1.3418 |  | -4.3456 | -4.3048 | 4.0045 | 3.3705 | 3.3513 | 1.0134 | 10.6031 | 14.0817 | 14.6927 | 11.0324 | -0.0002 | -0.0033 | 0.0005 | 0.0037 | 0 | -0.0006 | 0.0211 | -0.0161 | -0.0161 | -360.205 | 17.5321 | -360.6081 | 17.8463 | -360.962 | 18.1317 | -361.0051 | 17.5691 | -352.8229 | 18.7744 | -352.8998 | 16.834
11:40 | 1220 | 20.9557 | 194.263 | 435.0604 | 441.3287 | -21.6661 | -47.53 | 1.0039 | -0.7536 | -8.0073 | -7.8172 | -3.6939 | -4.2295 | 1.6483 | -5.0998 | 0.5803 | 0.631 | 0.9461 | 0.6887 | -131.064 | -7.315 | -0.5673 | -2.2007 | -9.8283 | -8.5972 | -1.3243 |  | -4.3318 | -4.3417 | 4.0039 | 3.3671 | 3.3552 | 1.0117 | 10.5937 | 14.0843 | 14.6571 | 10.9876 | 0.0002 | -0.0027 | 0.0009 | 0.0045 | 0.0007 | -0.0008 | 0.015 | -0.0094 | -0.0003 | -360.1927 | 17.5075 | -360.525 | 17.8217 | -360.882 | 18.0927 | -360.9712 | 17.5588 | -352.8198 | 18.7497 | -352.8167 | 16.8053
11:40 | 1221 | 20.9236 | 194.2467 | 435.1984 | 441.2953 | -21.7132 | -47.5835 | 0.931 | -0.649 | -7.9661 | -7.8083 | -3.6152 | -4.3483 | 1.659 | -5.1031 | 0.5798 | 0.6347 | 0.9459 | 0.6896 | -131.0471 | -7.3451 | -0.5946 | -2.19 | -9.9215 | -8.5971 | -1.3044 |  | -4.2643 | -4.2945 | 4.0037 | 3.3676 | 3.3523 | 1.0132 | 10.6155 | 14.1182 | 14.6878 | 11.02 | -0.0002 | -0.0028 | 0.0008 | 0.0039 | 0.0008 | -0.0005 | -0.0038 | -0.0109 | 0.0025 | -360.2081 | 17.5527 | -360.5619 | 17.8114 | -360.9004 | 18.1173 | -361.0297 | 17.5978 | -352.8906 | 18.7661 | -352.826 | 16.8053
11:40 | 1222 | 20.9566 | 194.1947 | 435.1254 | 441.3395 | -21.6748 | -47.5804 | 0.9113 | -0.7006 | -7.9704 | -7.7933 | -3.643 | -4.1537 | 1.7564 | -5.0518 | 0.5796 | 0.6322 | 0.9445 | 0.6877 | -131.0992 | -7.4191 | -0.6247 | -2.2461 | -9.9364 | -8.6127 | -1.2761 |  | -4.2324 | -4.1932 | 4.004 | 3.3655 | 3.3524 | 1.011 | 10.6423 | 14.1153 | 14.7098 | 11.0309 | -0.0008 | -0.0028 | 0.0003 | 0.0036 | 0.0002 | -0.0007 | -0.0005 | -0.0226 | -0.009 | -360.1804 | 17.5321 | -360.5619 | 17.8073 | -360.8727 | 18.0988 | -360.9404 | 17.5424 | -352.829 | 18.7703 | -352.8321 | 16.8032
11:40 | 1223 | 20.877 | 194.1906 | 435.0189 | 441.3458 | -21.8196 | -47.5562 | 0.8888 | -0.7099 | -7.9697 | -7.6884 | -3.5227 | -4.1355 | 1.7419 | -5.0971 | 0.5803 | 0.6349 | 0.9463 | 0.688 | -131.1622 | -7.382 | -0.5505 | -2.0301 | -9.8677 | -8.5472 | -1.2743 |  | -4.2296 | -4.3264 | 4.0043 | 3.3664 | 3.3528 | 1.0136 | 10.6213 | 14.0834 | 14.6809 | 10.9973 | 0 | -0.0028 | 0.0008 | 0.0035 | 0.0013 | -0.0006 | 0.0089 | 0.0048 | -0.0195 | -360.1865 | 17.5404 | -360.6358 | 17.8545 | -360.9527 | 18.1235 | -360.962 | 17.5629 | -352.826 | 18.7703 | -352.9029 | 16.8484
11:40 | 1224 | 20.988 | 194.2104 | 435.1289 | 441.3345 | -21.7621 | -47.5027 | 1.0175 | -0.6992 | -7.9795 | -7.6873 | -3.551 | -4.2006 | 1.6898 | -5.0471 | 0.5813 | 0.6306 | 0.9429 | 0.6882 | -131.1427 | -7.301 | -0.6573 | -2.0375 | -10.0195 | -8.6958 | -1.2995 |  | -4.278 | -4.2646 | 4.0045 | 3.3651 | 3.3523 | 1.013 | 10.6435 | 14.1165 | 14.7111 | 11.0089 | -0.0001 | -0.0034 | 0 | 0.003 | 0.0001 | -0.0008 | 0.014 | 0.0028 | 0.0117 | -360.1435 | 17.5075 | -360.5373 | 17.8175 | -360.9281 | 18.1379 | -360.9497 | 17.5363 | -352.7737 | 18.7333 | -352.8444 | 16.8217
11:40 | 1225 | 20.9985 | 194.2104 | 435.1631 | 441.2922 | -21.6963 | -47.5342 | 1.0205 | -0.6268 | -8.0352 | -7.6754 | -3.5659 | -4.1909 | 1.7422 | -5.0161 | 0.5814 | 0.6348 | 0.9475 | 0.689 | -130.986 | -7.3016 | -0.5793 | -2.0788 | -9.8879 | -8.5974 | -1.2433 |  | -4.2297 | -4.2194 | 4.0049 | 3.3685 | 3.3513 | 1.0137 | 10.6042 | 14.0597 | 14.6767 | 11.0046 | -0.0001 | -0.0033 | 0.0004 | 0.0033 | 0.0007 | -0.0007 | 0.0137 | -0.01 | -0.014 | -360.1865 | 17.5363 | -360.5743 | 17.8381 | -360.9281 | 18.1481 | -361.002 | 17.5814 | -352.8629 | 18.762 | -352.8506 | 16.8238
11:40 | 1226 | 21.0124 | 194.3512 | 435.1912 | 441.2402 | -21.7158 | -47.4766 | 1.0311 | -0.6315 | -8.0157 | -7.8021 | -3.5303 | -4.2094 | 1.7566 | -5.0195 | 0.5814 | 0.6323 | 0.9475 | 0.6886 | -131.0835 | -7.3996 | -0.5385 | -2.1569 | -9.8854 | -8.5088 | -1.2042 |  | -4.3016 | -4.2582 | 4.0053 | 3.3713 | 3.3546 | 1.0136 | 10.6099 | 14.083 | 14.6662 | 11.0158 | -0.0006 | -0.0031 | 0.0009 | 0.0038 | 0.0003 | -0.0007 | 0.0023 | -0.0108 | -0.0191 | -360.2142 | 17.5547 | -360.5989 | 17.8073 | -360.882 | 18.1235 | -360.9281 | 17.5506 | -352.8598 | 18.7826 | -352.8321 | 16.7991
11:40 | 1227 | 20.9496 | 194.3463 | 435.3094 | 441.2768 | -21.7574 | -47.5135 | 1.0216 | -0.7033 | -8.0792 | -7.8218 | -3.5717 | -4.1836 | 1.7018 | -5.0355 | 0.5793 | 0.6339 | 0.9438 | 0.6874 | -131.0227 | -7.3326 | -0.5131 | -2.1032 | -9.9113 | -8.568 | -1.1914 |  | -4.2157 | -4.265 | 4.005 | 3.3667 | 3.3543 | 1.0134 | 10.6493 | 14.0876 | 14.6996 | 11.0436 | -0.0003 | -0.0026 | 0.0006 | 0.0038 | 0.0008 | -0.0008 | 0.0192 | -0.0045 | -0.0181 | -360.2019 | 17.5506 | -360.6389 | 17.8566 | -360.9404 | 18.1358 | -360.9497 | 17.5629 | -352.8629 | 18.7826 | -352.9183 | 16.8402
11:40 | 1228 | 20.9849 | 194.3232 | 435.1136 | 441.2958 | -21.768 | -47.5785 | 0.9125 | -0.6456 | -8.0551 | -7.8191 | -3.5959 | -4.2738 | 1.7017 | -4.9786 | 0.5817 | 0.6303 | 0.9431 | 0.6883 | -131.1357 | -7.2845 | -0.5664 | -2.0782 | -9.964 | -8.5393 | -1.2565 |  | -4.3685 | -4.3625 | 4.0054 | 3.368 | 3.3527 | 1.0136 | 10.6225 | 14.0613 | 14.6986 | 10.9988 | 0.0002 | -0.0031 | 0.001 | 0.0042 | 0.0005 | -0.0004 | 0.0015 | -0.0096 | 0.0143 | -360.1835 | 17.5096 | -360.5312 | 17.8258 | -360.9066 | 18.1604 | -360.9651 | 17.5404 | -352.7983 | 18.7477 | -352.8229 | 16.8094
11:40 | 1229 | 20.9815 | 194.3251 | 435.1293 | 441.383 | -21.8618 | -47.5126 | 0.9942 | -0.676 | -8.0765 | -7.885 | -3.5814 | -4.2425 | 1.7311 | -4.9935 | 0.5811 | 0.6308 | 0.9421 | 0.6891 | -131.0637 | -7.3298 | -0.5654 | -2.0761 | -9.9668 | -8.5829 | -1.2123 |  | -4.2698 | -4.4136 | 4.0041 | 3.3663 | 3.3513 | 1.0146 | 10.6491 | 14.1053 | 14.6912 | 11.0367 | -0.0002 | -0.0035 | 0.0006 | 0.0037 | 0.0005 | -0.0008 | 0.0047 | -0.0061 | 0.0044 | -360.2111 | 17.528 | -360.5466 | 17.8155 | -360.9251 | 18.1687 | -361.0143 | 17.5835 | -352.8721 | 18.7661 | -352.8198 | 16.8032
11:40 | 1230 | 20.9517 | 194.3176 | 435.1798 | 441.3653 | -21.8394 | -47.5829 | 0.9853 | -0.5864 | -8.0346 | -7.9139 | -3.504 | -4.2873 | 1.6546 | -5.0262 | 0.5811 | 0.6354 | 0.9472 | 0.6909 | -130.9937 | -7.2678 | -0.4775 | -2.2442 | -9.9946 | -8.5708 | -1.2958 |  | -4.2661 | -4.5233 | 4.0044 | 3.3694 | 3.3537 | 1.0136 | 10.6237 | 14.0971 | 14.7163 | 11.0176 | -0.0004 | -0.0028 | 0.0002 | 0.0037 | 0.0006 | -0.0006 | 0.0116 | 0.0013 | -0.0127 | -360.1711 | 17.5342 | -360.5558 | 17.8011 | -360.8543 | 18.144 | -360.9589 | 17.5445 | -352.8229 | 18.7682 | -352.8198 | 16.7868
11:40 | 1231 | 20.9954 | 194.3366 | 435.2071 | 441.3394 | -21.7914 | -47.5386 | 0.9805 | -0.6456 | -8.0096 | -7.8961 | -3.5428 | -4.2387 | 1.7911 | -5.029 | 0.5801 | 0.634 | 0.9449 | 0.6874 | -131.0792 | -7.2698 | -0.4264 | -2.1281 | -9.9362 | -8.5543 | -1.2319 |  | -4.2644 | -4.4405 | 4.0045 | 3.37 | 3.3537 | 1.0137 | 10.6515 | 14.1074 | 14.7091 | 11.0222 | -0.0007 | -0.0031 | 0.0009 | 0.0036 | 0.0005 | -0.0009 | 0.0051 | -0.0075 | -0.0131 | -360.1865 | 17.5383 | -360.6512 | 17.8648 | -360.9466 | 18.1481 | -360.9651 | 17.5404 | -352.8198 | 18.7764 | -352.9029 | 16.8505
11:40 | 1232 | 21.0068 | 194.3409 | 435.2173 | 441.3843 | -21.8315 | -47.6594 | 1.0093 | -0.4505 | -7.9494 | -7.7322 | -3.4929 | -4.237 | 1.7814 | -5.0236 | 0.5812 | 0.6358 | 0.9461 | 0.6895 | -131.1174 | -7.2639 | -0.4225 | -2.047 | -9.9804 | -8.5681 | -1.2367 |  | -4.2662 | -4.4667 | 4.0047 | 3.367 | 3.3511 | 1.0116 | 10.6329 | 14.118 | 14.703 | 11.0323 | 0 | -0.0029 | 0.0002 | 0.0032 | 0.0005 | -0.0009 | 0.0059 | -0.004 | -0.0153 | -360.1311 | 17.5137 | -360.5527 | 17.8319 | -360.9251 | 18.1543 | -360.9343 | 17.5116 | -352.8229 | 18.7292 | -352.8198 | 16.8176
11:40 | 1233 | 20.9317 | 194.3875 | 435.2235 | 441.3207 | -21.8704 | -47.6054 | 1.0041 | -0.4984 | -7.9037 | -7.7202 | -3.5049 | -4.1756 | 1.7492 | -5.0868 | 0.5819 | 0.635 | 0.9483 | 0.6894 | -131.112 | -7.3117 | -0.4266 | -2.0179 | -9.9019 | -8.5229 | -1.2377 |  | -4.1704 | -4.4801 | 4.0037 | 3.3672 | 3.3562 | 1.0131 | 10.5949 | 14.091 | 14.691 | 11.0356 | 0.0002 | -0.0032 | 0.001 | 0.0037 | 0.0002 | -0.0006 | 0.0129 | -0.0126 | -0.0107 | -360.2235 | 17.528 | -360.6019 | 17.8319 | -360.9189 | 18.1625 | -361.0174 | 17.5588 | -352.8475 | 18.76 | -352.8752 | 16.8258
11:40 | 1234 | 21.0347 | 194.3527 | 435.1909 | 441.3709 | -21.8249 | -47.5605 | 1.0416 | -0.517 | -7.9407 | -7.7284 | -3.5347 | -4.2254 | 1.8364 | -4.957 | 0.5803 | 0.6269 | 0.9449 | 0.6895 | -131.1123 | -7.3278 | -0.4224 | -2.0977 | -9.9319 | -8.4855 | -1.3059 |  | -4.1816 | -4.3114 | 4.0046 | 3.3686 | 3.3561 | 1.0131 | 10.5902 | 14.0692 | 14.6993 | 11.0306 | -0.0003 | -0.0031 | 0.0014 | 0.0041 | 0.001 | -0.0009 | 0.0184 | -0.015 | -0.0089 | -360.2327 | 17.5486 | -360.5743 | 17.8093 | -360.885 | 18.1194 | -360.9343 | 17.526 | -352.829 | 18.7846 | -352.8721 | 16.7991
11:40 | 1235 | 21.0524 | 194.3472 | 435.2109 | 441.3851 | -21.7965 | -47.5511 | 1.0045 | -0.6024 | -8.0524 | -7.761 | -3.572 | -4.1803 | 1.7929 | -4.9891 | 0.5812 | 0.6324 | 0.9479 | 0.69 | -131.0696 | -7.2594 | -0.4908 | -2.0899 | -9.9025 | -8.5385 | -1.2992 |  | -4.2285 | -4.3304 | 4.0044 | 3.3665 | 3.3527 | 1.0117 | 10.5891 | 14.068 | 14.64 | 10.9833 | -0.0001 | -0.0024 | 0.0005 | 0.004 | 0.0005 | -0.0003 | 0.0033 | -0.0086 | -0.0064 | -360.1927 | 17.5342 | -360.6266 | 17.8483 | -360.9127 | 18.1317 | -360.9404 | 17.5445 | -352.8721 | 18.7805 | -352.8967 | 16.8402
11:40 | 1236 | 21.1571 | 194.3613 | 435.1851 | 441.424 | -21.8687 | -47.5777 | 0.9313 | -0.6083 | -7.9706 | -7.8121 | -3.387 | -4.2786 | 1.7668 | -5.0011 | 0.5814 | 0.6293 | 0.9479 | 0.6899 | -131.0587 | -7.3591 | -0.5301 | -2.0692 | -9.9248 | -8.5235 | -1.3159 |  | -4.2483 | -4.3337 | 4.0041 | 3.3693 | 3.3519 | 1.0112 | 10.633 | 14.0716 | 14.702 | 11.0327 | -0.0001 | -0.0028 | 0.0005 | 0.0036 | 0.0007 | -0.0008 | 0.016 | 0.0028 | -0.0304 | -360.1465 | 17.5198 | -360.565 | 17.8134 | -360.9281 | 18.1584 | -360.9681 | 17.5239 | -352.8075 | 18.762 | -352.8075 | 16.8156
11:40 | 1237 | 21.1026 | 194.4494 | 435.2066 | 441.3631 | -21.8412 | -47.6168 | 0.9492 | -0.586 | -7.9983 | -7.7806 | -3.3891 | -4.3197 | 1.7778 | -5.0994 | 0.5807 | 0.6301 | 0.9467 | 0.6896 | -131.0794 | -7.3818 | -0.4992 | -2.0882 | -9.9891 | -8.5379 | -1.3131 |  | -4.1633 | -4.3581 | 4.0032 | 3.3717 | 3.3539 | 1.0117 | 10.6248 | 14.081 | 14.7129 | 11.0009 | 0.0002 | -0.0028 | 0.0006 | 0.0039 | 0.0003 | -0.0006 | 0.0078 | -0.0118 | 0.0028 | -360.205 | 17.5178 | -360.5527 | 17.8093 | -360.9035 | 18.1625 | -361.0204 | 17.5629 | -352.8629 | 18.7723 | -352.826 | 16.8094
11:40 | 1238 | 21.0844 | 194.3853 | 435.1483 | 441.4088 | -21.7711 | -47.6324 | 1.0712 | -0.5328 | -7.9131 | -7.6921 | -3.3937 | -4.3048 | 1.7304 | -5.1169 | 0.5814 | 0.6341 | 0.9484 | 0.6898 | -131.0584 | -7.2948 | -0.4587 | -2.0372 | -9.9507 | -8.4797 | -1.3171 |  | -4.2315 | -4.3761 | 4.0042 | 3.3689 | 3.3547 | 1.0124 | 10.611 | 14.119 | 14.6802 | 11.0107 | 0 | -0.0031 | 0 | 0.0034 | 0.0008 | -0.0002 | -0.0086 | -0.0102 | 0.0213 | -360.205 | 17.5404 | -360.5958 | 17.8134 | -360.885 | 18.1563 | -360.9743 | 17.5465 | -352.8198 | 18.7805 | -352.8537 | 16.7909
11:40 | 1239 | 21.0814 | 194.3373 | 435.157 | 441.4296 | -21.6934 | -47.5523 | 1.0454 | -0.5773 | -7.9653 | -7.7378 | -3.3871 | -4.2599 | 1.7744 | -5.0613 | 0.5813 | 0.6306 | 0.9474 | 0.6883 | -131.0569 | -7.2964 | -0.5211 | -2.1636 | -9.9459 | -8.4867 | -1.2954 |  | -4.2526 | -4.3218 | 4.0044 | 3.3676 | 3.351 | 1.0141 | 10.6226 | 14.0784 | 14.6849 | 10.9937 | -0.0006 | -0.0024 | 0.0008 | 0.0038 | 0.0009 | -0.0007 | 0.0086 | -0.0046 | -0.0278 | -360.1773 | 17.5342 | -360.5927 | 17.8442 | -360.9281 | 18.1337 | -360.9404 | 17.5342 | -352.8414 | 18.7723 | -352.8783 | 16.8381
11:40 | 1240 | 21.0745 | 194.2893 | 435.1947 | 441.3605 | -21.7333 | -47.5922 | 1.0175 | -0.6526 | -7.9885 | -7.847 | -3.5205 | -4.21 | 1.7936 | -5.0899 | 0.5809 | 0.6337 | 0.9425 | 0.6893 | -131.0936 | -7.2345 | -0.4253 | -2.2555 | -9.8763 | -8.4363 | -1.273 |  | -4.1287 | -4.2054 | 4.0033 | 3.3698 | 3.3522 | 1.0123 | 10.6191 | 14.1212 | 14.6819 | 11.0248 | -0.0002 | -0.0027 | 0.0005 | 0.0034 | 0.0002 | -0.0007 | 0.0156 | -0.0199 | -0.0056 | -360.1711 | 17.5321 | -360.5958 | 17.8504 | -360.9589 | 18.1728 | -360.9589 | 17.528 | -352.8321 | 18.7805 | -352.8721 | 16.8381
11:40 | 1241 | 21.1136 | 194.3406 | 435.1967 | 441.3901 | -21.8315 | -47.5738 | 1.0353 | -0.5241 | -7.9857 | -7.7303 | -3.4903 | -4.2212 | 1.7101 | -5.0598 | 0.5817 | 0.6368 | 0.9438 | 0.6898 | -131.0544 | -7.2593 | -0.4418 | -2.2884 | -9.8633 | -8.4726 | -1.2805 |  | -4.1571 | -4.1566 | 4.0047 | 3.3688 | 3.3507 | 1.0144 | 10.6167 | 14.0844 | 14.7044 | 11.0103 | 0.0002 | -0.003 | 0.0007 | 0.0033 | 0.0006 | -0.001 | 0.003 | -0.0153 | -0.0294 | -360.1773 | 17.5219 | -360.565 | 17.8011 | -360.8943 | 18.1666 | -360.9743 | 17.5383 | -352.8106 | 18.7579 | -352.826 | 16.8156
11:40 | 1242 | 21.0333 | 194.2643 | 435.1584 | 441.429 | -21.7215 | -47.6827 | 0.9542 | -0.5454 | -8.0045 | -7.7766 | -3.4948 | -4.2133 | 1.7682 | -4.9805 | 0.5814 | 0.6346 | 0.9425 | 0.6904 | -130.9946 | -7.301 | -0.4437 | -2.2326 | -9.7981 | -8.3743 | -1.1939 |  | -4.2073 | -4.2457 | 4.0024 | 3.3675 | 3.3498 | 1.0135 | 10.6144 | 14.0994 | 14.6901 | 11.0197 | 0.0004 | -0.0028 | 0.001 | 0.0043 | 0.0002 | -0.0004 | 0.0016 | -0.0086 | -0.0187 | -360.2327 | 17.565 | -360.605 | 17.8299 | -360.922 | 18.144 | -360.9835 | 17.5629 | -352.8629 | 18.7928 | -352.8906 | 16.8135
11:40 | 1243 | 21.0292 | 194.2661 | 435.1399 | 441.3769 | -21.8148 | -47.7064 | 0.9526 | -0.5416 | -7.9796 | -7.6456 | -3.4929 | -4.1925 | 1.8207 | -5.052 | 0.5832 | 0.6377 | 0.9494 | 0.6911 | -130.9781 | -7.2895 | -0.3828 | -2.1966 | -9.7822 | -8.3406 | -1.2045 |  | -4.1818 | -4.2414 | 4.0032 | 3.3662 | 3.3512 | 1.0124 | 10.6389 | 14.0714 | 14.6836 | 11.01 | -0.0005 | -0.003 | 0.0006 | 0.0037 | 0.0008 | -0.0009 | -0.0014 | -0.0028 | -0.0113 | -360.1558 | 17.5198 | -360.565 | 17.8278 | -360.885 | 18.1255 | -360.9343 | 17.5383 | -352.8475 | 18.7723 | -352.8414 | 16.8156
11:40 | 1244 | 21.1032 | 194.3116 | 435.2254 | 441.42 | -21.7936 | -47.6195 | 0.9657 | -0.5671 | -7.9265 | -7.6874 | -3.4565 | -4.236 | 1.845 | -5.0186 | 0.5822 | 0.632 | 0.9469 | 0.6899 | -131.0098 | -7.3319 | -0.4712 | -2.1471 | -9.7842 | -8.4041 | -1.1813 |  | -4.2485 | -4.335 | 4.0033 | 3.3657 | 3.3483 | 1.014 | 10.5949 | 14.0854 | 14.6863 | 10.9833 | -0.0006 | -0.0027 | 0.0008 | 0.0038 | 0.0002 | -0.0006 | 0.0159 | 0.0016 | -0.0037 | -360.1681 | 17.5198 | -360.5712 | 17.8401 | -360.9281 | 18.183 | -360.9835 | 17.528 | -352.829 | 18.7764 | -352.866 | 16.8402
11:40 | 1245 | 21.1887 | 194.3156 | 435.2706 | 441.4282 | -21.6467 | -47.4609 | 0.9642 | -0.4997 | -7.9987 | -7.7571 | -3.4992 | -4.3126 | 1.7322 | -5.0944 | 0.5823 | 0.6342 | 0.9473 | 0.6903 | -131.038 | -7.3336 | -0.3993 | -2.0167 | -9.8758 | -8.5006 | -1.2047 |  | -4.2771 | -4.3137 | 4.0021 | 3.3666 | 3.3497 | 1.0136 | 10.6041 | 14.0773 | 14.6731 | 11.0096 | -0.0002 | -0.0028 | 0.0003 | 0.0038 | 0.0009 | -0.0007 | 0.0213 | 0.006 | -0.0084 | -360.1619 | 17.5075 | -360.5404 | 17.8134 | -360.8943 | 18.1522 | -360.9835 | 17.5404 | -352.8137 | 18.7497 | -352.8352 | 16.8053
11:40 | 1246 | 21.1456 | 194.2986 | 435.3183 | 441.4089 | -21.707 | -47.5903 | 0.9983 | -0.4482 | -7.8428 | -7.694 | -3.4875 | -4.3452 | 1.7634 | -5.1321 | 0.5826 | 0.6343 | 0.947 | 0.6913 | -131.0381 | -7.2493 | -0.4186 | -2.0551 | -9.8071 | -8.4932 | -1.2202 |  | -4.1826 | -4.3947 | 4.0027 | 3.365 | 3.349 | 1.0138 | 10.6134 | 14.0922 | 14.7156 | 11.0078 | -0.0004 | -0.0035 | 0.0003 | 0.0034 | 0.0007 | -0.0006 | 0.0046 | -0.0165 | -0.0057 | -360.1896 | 17.5445 | -360.5804 | 17.836 | -360.9127 | 18.1502 | -360.9743 | 17.5486 | -352.8629 | 18.7867 | -352.8629 | 16.832
11:40 | 1247 | 21.098 | 194.2908 | 435.122 | 441.3405 | -21.7266 | -47.6323 | 1.0117 | -0.4312 | -7.9463 | -7.7501 | -3.45 | -4.3033 | 1.7854 | -5.1924 | 0.5828 | 0.6333 | 0.9489 | 0.6912 | -131.0118 | -7.1833 | -0.3677 | -1.9608 | -9.9294 | -8.4649 | -1.2439 |  | -4.2352 | -4.3759 | 4.0024 | 3.3683 | 3.351 | 1.0123 | 10.6088 | 14.1048 | 14.6696 | 11.0209 | -0.0004 | -0.0032 | 0.0007 | 0.0037 | 0.0003 | -0.0008 | -0.0037 | 0.0052 | -0.0015 | -360.165 | 17.526 | -360.5958 | 17.8463 | -360.9066 | 18.1358 | -360.9497 | 17.5178 | -352.7983 | 18.7805 | -352.8444 | 16.8299
11:41 | 1248 | 21.1677 | 194.277 | 435.1443 | 441.3023 | -21.7179 | -47.5194 | 1.0125 | -0.534 | -7.9116 | -7.6487 | -3.4264 | -4.3649 | 1.8372 | -5.0937 | 0.5823 | 0.6358 | 0.9463 | 0.6914 | -130.9908 | -7.2892 | -0.3482 | -2.2339 | -9.9516 | -8.4891 | -1.2603 |  | -4.1542 | -4.3155 | 4.003 | 3.3692 | 3.3549 | 1.0135 | 10.6226 | 14.0727 | 14.686 | 11.0222 | -0.0006 | -0.0027 | 0.0006 | 0.0035 | 0.001 | -0.0006 | -0.0023 | -0.0138 | -0.0144 | -360.1865 | 17.5321 | -360.565 | 17.836 | -360.9466 | 18.1543 | -360.9651 | 17.526 | -352.8414 | 18.7764 | -352.866 | 16.8381
11:41 | 1249 | 21.0964 | 194.281 | 435.2459 | 441.305 | -21.6457 | -47.6529 | 1.0111 | -0.5417 | -7.9167 | -7.6262 | -3.4013 | -4.3622 | 1.8225 | -5.1682 | 0.582 | 0.6333 | 0.9456 | 0.6915 | -131.0436 | -7.3286 | -0.4173 | -2.2439 | -9.9513 | -8.4831 | -1.2383 |  | -4.1336 | -4.1462 | 4.0024 | 3.3666 | 3.3498 | 1.0135 | 10.6295 | 14.0856 | 14.6942 | 11.0114 | -0.0003 | -0.0026 | 0.0009 | 0.0038 | 0.0005 | -0.0005 | -0.0001 | -0.006 | -0.0082 | -360.1711 | 17.528 | -360.5835 | 17.8278 | -360.882 | 18.1543 | -360.9804 | 17.5465 | -352.8414 | 18.7764 | -352.8229 | 16.8053
11:41 | 1250 | 21.0572 | 194.2781 | 435.2105 | 441.3184 | -21.7025 | -47.5246 | 1.0287 | -0.5247 | -7.9162 | -7.7127 | -3.4183 | -4.2923 | 1.8118 | -5.1188 | 0.5817 | 0.6329 | 0.9478 | 0.6894 | -131.0446 | -7.2116 | -0.3939 | -2.2402 | -10.0307 | -8.4962 | -1.2857 |  | -4.1755 | -4.2271 | 4.0031 | 3.3689 | 3.3513 | 1.0146 | 10.6214 | 14.1006 | 14.7088 | 11.015 | -0.0003 | -0.0033 | 0.0012 | 0.0044 | 0.0009 | -0.0005 | 0.0087 | -0.0097 | -0.0114 | -360.205 | 17.5301 | -360.5712 | 17.8114 | -360.8635 | 18.1399 | -360.9158 | 17.5465 | -352.8444 | 18.7826 | -352.829 | 16.8012
11:41 | 1251 | 21.1077 | 194.3761 | 435.1889 | 441.4255 | -21.5501 | -47.3833 | 1.1702 | -0.5143 | -7.9024 | -7.8092 | -3.4424 | -4.2806 | 1.8856 | -5.1106 | 0.5812 | 0.635 | 0.9497 | 0.6922 | -131.0161 | -7.2898 | -0.3528 | -2.2262 | -10.0373 | -8.3829 | -1.2955 |  | -4.2567 | -4.2349 | 4.0034 | 3.3736 | 3.3532 | 1.0142 | 10.6341 | 14.0787 | 14.7218 | 11.0219 | 0.0002 | -0.0027 | 0.0008 | 0.0035 | 0.0004 | -0.0001 | 0.0178 | -0.0077 | 0.0007 | -360.165 | 17.5424 | -360.5989 | 17.8422 | -360.9004 | 18.1584 | -360.9651 | 17.5301 | -352.8198 | 18.7928 | -352.8721 | 16.8361
11:41 | 1252 | 21.1395 | 194.2759 | 435.1312 | 441.3266 | -21.6354 | -47.4972 | 1.1817 | -0.4629 | -7.9519 | -7.654 | -3.3893 | -4.2397 | 1.8763 | -5.0909 | 0.582 | 0.6342 | 0.9465 | 0.6911 | -131.1353 | -7.3285 | -0.373 | -2.1399 | -10.0227 | -8.3456 | -1.2894 |  | -4.2077 | -4.1452 | 4.003 | 3.3658 | 3.35 | 1.0147 | 10.6319 | 14.0993 | 14.7064 | 11.0201 | -0.0001 | -0.0031 | 0.0007 | 0.0037 | 0.0009 | -0.0008 | 0.0134 | -0.0031 | -0.0252 | -360.1311 | 17.5137 | -360.5435 | 17.8175 | -360.9004 | 18.1604 | -360.9558 | 17.526 | -352.8075 | 18.7538 | -352.8167 | 16.8217
11:41 | 1253 | 21.1113 | 194.2787 | 435.1698 | 441.2731 | -21.5922 | -47.4418 | 1.2139 | -0.4662 | -8.0115 | -7.6516 | -3.4212 | -4.2902 | 1.8587 | -5.1063 | 0.5813 | 0.6348 | 0.9467 | 0.6902 | -131.073 | -7.2328 | -0.373 | -2.1179 | -10.0218 | -8.3762 | -1.2607 |  | -4.2215 | -4.2062 | 4.0024 | 3.3663 | 3.3488 | 1.015 | 10.6157 | 14.1005 | 14.702 | 11.0038 | -0.0005 | -0.0027 | 0.0005 | 0.004 | 0.0007 | -0.0004 | 0.0087 | -0.0123 | -0.0099 | -360.1865 | 17.5342 | -360.5866 | 17.8278 | -360.8912 | 18.1666 | -361.0297 | 17.5527 | -352.8444 | 18.7805 | -352.8506 | 16.8115
11:41 | 1254 | 21.1546 | 194.321 | 435.3241 | 441.3197 | -21.6201 | -47.4565 | 1.1889 | -0.5403 | -7.9668 | -7.6385 | -3.4328 | -4.2388 | 1.8658 | -5.067 | 0.5818 | 0.633 | 0.9476 | 0.6909 | -130.9495 | -7.1578 | -0.2475 | -2.1846 | -9.9972 | -8.3588 | -1.2248 |  | -4.1595 | -4.0899 | 4.0034 | 3.3668 | 3.3502 | 1.0133 | 10.6319 | 14.0877 | 14.7238 | 11.0143 | 0 | -0.0028 | 0.0006 | 0.0041 | 0.0003 | -0.0014 | -0.0055 | -0.0144 | -0.0029 | -360.1435 | 17.5198 | -360.5773 | 17.8134 | -360.8881 | 18.1235 | -360.9312 | 17.526 | -352.8414 | 18.7641 | -352.829 | 16.8176
11:41 | 1255 | 21.0887 | 194.3737 | 435.2044 | 441.311 | -21.5535 | -47.381 | 1.1973 | -0.6058 | -7.9715 | -7.7111 | -3.4438 | -4.3232 | 1.9398 | -4.9894 | 0.5834 | 0.6309 | 0.9461 | 0.6917 | -131.0216 | -7.2292 | -0.3051 | -2.0672 | -9.9339 | -8.2731 | -1.1901 |  | -4.1501 | -4.1764 | 4.0038 | 3.3698 | 3.3553 | 1.0146 | 10.6169 | 14.0609 | 14.6955 | 11.0057 | 0.0001 | -0.0034 | 0.001 | 0.0036 | 0.0006 | -0.0006 | 0.0008 | -0.0069 | -0.0367 | -360.2173 | 17.5486 | -360.6204 | 17.8463 | -360.9527 | 18.1563 | -360.9527 | 17.528 | -352.8629 | 18.7949 | -352.8906 | 16.8361
11:41 | 1256 | 21.1719 | 194.3241 | 435.0925 | 441.32 | -21.5969 | -47.4255 | 1.2062 | -0.5935 | -7.9863 | -7.6492 | -3.4752 | -4.2312 | 1.8932 | -5.0632 | 0.5817 | 0.6334 | 0.9482 | 0.6916 | -131.0818 | -7.2583 | -0.2767 | -1.9755 | -9.9884 | -8.2315 | -1.1286 |  | -4.1656 | -4.2162 | 4.0034 | 3.3714 | 3.3518 | 1.0147 | 10.6052 | 14.0612 | 14.6686 | 10.9876 | 0.0001 | -0.0025 | 0.0008 | 0.0039 | 0.0005 | -0.0006 | 0.017 | -0.0091 | -0.0034 | -360.1527 | 17.5157 | -360.5589 | 17.8175 | -360.9066 | 18.1461 | -360.9466 | 17.5178 | -352.7767 | 18.762 | -352.8598 | 16.8176
11:41 | 1257 | 21.2629 | 194.331 | 435.2502 | 441.463 | -21.66 | -47.3714 | 1.0909 | -0.5403 | -7.9309 | -7.7035 | -3.4917 | -4.2498 | 1.88 | -5.1348 | 0.5816 | 0.6326 | 0.951 | 0.6915 | -131.0612 | -7.1659 | -0.258 | -1.9617 | -9.9873 | -8.3329 | -1.1527 |  | -4.2149 | -4.3099 | 4.0031 | 3.3662 | 3.3514 | 1.0148 | 10.6434 | 14.0821 | 14.6959 | 11.037 | -0.0003 | -0.0024 | 0.0006 | 0.0034 | 0.001 | -0.0007 | 0.0092 | -0.0101 | -0.0249 | -360.1896 | 17.5363 | -360.5681 | 17.8114 | -360.885 | 18.1625 | -361.0051 | 17.5568 | -352.8475 | 18.7867 | -352.8844 | 16.8217
11:41 | 1258 | 21.1771 | 194.3382 | 435.1722 | 441.4261 | -21.6547 | -47.335 | 1.1381 | -0.5984 | -7.8509 | -7.8019 | -3.4647 | -4.2607 | 1.9161 | -5.1192 | 0.5818 | 0.6331 | 0.9518 | 0.6918 | -131.0267 | -7.0944 | -0.2879 | -2.0829 | -9.8174 | -8.2056 | -1.1508 |  | -4.0922 | -4.2403 | 4.0028 | 3.3671 | 3.3554 | 1.0152 | 10.6052 | 14.0959 | 14.6686 | 10.9991 | -0.0001 | -0.0028 | 0.0006 | 0.0035 | 0.0004 | -0.0001 | 0.0117 | -0.0056 | -0.0205 | -360.2173 | 17.5239 | -360.5435 | 17.7909 | -360.8974 | 18.1337 | -360.9558 | 17.5404 | -352.8506 | 18.7744 | -352.826 | 16.7991
11:41 | 1259 | 21.2204 | 194.3494 | 435.1912 | 441.4985 | -21.7166 | -47.4182 | 1.0521 | -0.537 | -7.864 | -7.6569 | -3.4711 | -4.2803 | 1.8488 | -5.0598 | 0.5813 | 0.6344 | 0.9477 | 0.6911 | -131.0309 | -7.1691 | -0.3393 | -2.0363 | -9.9091 | -8.367 | -1.1251 |  | -4.0972 | -4.2783 | 4.0039 | 3.3703 | 3.3555 | 1.0144 | 10.6122 | 14.0682 | 14.6874 | 10.9944 | 0.0002 | -0.003 | 0.0004 | 0.0034 | 0.0004 | -0.0009 | 0.0127 | -0.0138 | -0.0214 | -360.2081 | 17.5383 | -360.5866 | 17.8196 | -360.8758 | 18.1584 | -360.9835 | 17.528 | -352.829 | 18.7805 | -352.8691 | 16.8381
11:41 | 1260 | 21.2066 | 194.4028 | 435.1962 | 441.4944 | -21.6364 | -47.3178 | 1.1165 | -0.6109 | -7.773 | -7.6673 | -3.4335 | -4.3148 | 1.8884 | -5.0685 | 0.581 | 0.6349 | 0.9486 | 0.6915 | -131.0323 | -7.1109 | -0.3629 | -1.9415 | -9.8333 | -8.2475 | -1.0741 |  | -4.0862 | -4.2448 | 4.0031 | 3.3695 | 3.3548 | 1.0136 | 10.6146 | 14.0643 | 14.6927 | 11.0266 | -0.0002 | -0.003 | 0.0003 | 0.0035 | 0.0004 | -0.0002 | 0.0174 | -0.0163 | -0.0116 | -360.1465 | 17.5157 | -360.565 | 17.8032 | -360.9251 | 18.1625 | -360.9435 | 17.5219 | -352.8167 | 18.762 | -352.8352 | 16.8176
11:41 | 1261 | 21.1484 | 194.4065 | 435.1821 | 441.3733 | -21.7205 | -47.42 | 1.0856 | -0.5637 | -7.8052 | -7.8516 | -3.492 | -4.3022 | 1.838 | -5.1766 | 0.5809 | 0.631 | 0.9486 | 0.6916 | -131.0508 | -7.0595 | -0.3787 | -1.935 | -9.8602 | -8.3687 | -1.1838 |  | -4.1126 | -4.158 | 4.0026 | 3.3705 | 3.3573 | 1.0144 | 10.6076 | 14.0865 | 14.6703 | 10.9959 | 0 | -0.0027 | 0.0005 | 0.0038 | 0.0007 | -0.0007 | 0.0139 | -0.0121 | 0.0002 | -360.1527 | 17.5075 | -360.5619 | 17.8258 | -360.9127 | 18.142 | -360.9897 | 17.5383 | -352.8106 | 18.762 | -352.8352 | 16.8299
11:41 | 1262 | 21.1838 | 194.4298 | 435.279 | 441.3931 | -21.7454 | -47.4807 | 1.002 | -0.5412 | -7.859 | -7.7925 | -3.4496 | -4.1887 | 1.8164 | -5.1764 | 0.5822 | 0.6363 | 0.9482 | 0.6921 | -131.0778 | -7.0994 | -0.3885 | -1.8722 | -9.9029 | -8.4323 | -1.0624 |  | -4.1029 | -4.184 | 4.0025 | 3.3679 | 3.353 | 1.0136 | 10.6029 | 14.053 | 14.6427 | 11.0085 | -0.0004 | -0.0029 | 0.0007 | 0.0037 | 0.0008 | -0.0004 | 0.0173 | -0.007 | 0.0165 | -360.1804 | 17.5465 | -360.5773 | 17.8093 | -360.9189 | 18.1502 | -360.9804 | 17.5404 | -352.8721 | 18.7785 | -352.866 | 16.8115
11:41 | 1263 | 21.1034 | 194.444 | 435.2777 | 441.3181 | -21.6979 | -47.5356 | 1.0953 | -0.5248 | -7.8427 | -7.6604 | -3.5036 | -4.3037 | 1.7773 | -5.1853 | 0.5821 | 0.6329 | 0.9472 | 0.6903 | -131.1438 | -7.1658 | -0.4504 | -1.8992 | -9.941 | -8.3902 | -1.0955 |  | -4.1619 | -4.1651 | 4.0008 | 3.3696 | 3.3529 | 1.0129 | 10.5959 | 14.104 | 14.6424 | 11.0013 | 0.0001 | -0.0026 | 0.0006 | 0.0039 | 0.0008 | -0.0007 | 0.0124 | 0.0021 | -0.016 | -360.1619 | 17.5363 | -360.5804 | 17.8175 | -360.8943 | 18.1153 | -360.9343 | 17.5342 | -352.8321 | 18.7908 | -352.8844 | 16.8176
11:41 | 1264 | 21.1925 | 194.4165 | 435.1879 | 441.3678 | -21.768 | -47.4945 | 1.022 | -0.5702 | -7.8061 | -7.7948 | -3.454 | -4.3064 | 1.8275 | -5.1243 | 0.5809 | 0.6323 | 0.9471 | 0.6901 | -131.0527 | -7.0413 | -0.4138 | -2.0067 | -9.997 | -8.3104 | -1.2627 |  | -4.1976 | -4.2149 | 4.0012 | 3.3706 | 3.3556 | 1.0139 | 10.6191 | 14.1098 | 14.6656 | 11.0244 | 0.0001 | -0.0029 | 0.0008 | 0.0037 | 0.0004 | -0.0011 | 0.0021 | -0.0015 | -0.0191 | -360.1865 | 17.5506 | -360.6235 | 17.8258 | -360.9281 | 18.1604 | -360.9681 | 17.5383 | -352.8414 | 18.7928 | -352.8752 | 16.832
11:41 | 1265 | 21.134 | 194.3986 | 435.3001 | 441.3794 | -21.7159 | -47.415 | 0.973 | -0.6424 | -7.8629 | -7.8819 | -3.5292 | -4.3587 | 1.898 | -5.0782 | 0.5814 | 0.6343 | 0.9479 | 0.6909 | -131.1987 | -7.1391 | -0.3987 | -1.872 | -9.8925 | -8.3282 | -1.1537 |  | -4.0827 | -4.1684 | 4.0017 | 3.369 | 3.3547 | 1.0154 | 10.6295 | 14.1088 | 14.7231 | 11.0461 | -0.0006 | -0.0029 | 0.0005 | 0.0034 | 0.0003 | -0.0005 | 0.0048 | -0.0046 | -0.0087 | -360.1681 | 17.4993 | -360.5373 | 17.8114 | -360.9035 | 18.1502 | -360.9281 | 17.5363 | -352.8229 | 18.76 | -352.8414 | 16.8176
11:41 | 1266 | 21.1201 | 194.3569 | 435.2377 | 441.3621 | -21.7824 | -47.4998 | 0.9559 | -0.5436 | -7.8157 | -7.7566 | -3.4365 | -4.2814 | 1.8939 | -5.1282 | 0.5802 | 0.6281 | 0.9462 | 0.6899 | -131.1058 | -7.0829 | -0.3954 | -1.9597 | -9.857 | -8.3296 | -1.0731 |  | -4.1244 | -4.2383 | 4.002 | 3.3663 | 3.355 | 1.0139 | 10.6548 | 14.1055 | 14.6806 | 11.0363 | -0.0003 | -0.0026 | 0.0008 | 0.0038 | 0.0008 | -0.0008 | 0.0086 | -0.0193 | 0.0022 | -360.1865 | 17.528 | -360.5589 | 17.795 | -360.9189 | 18.1625 | -360.9958 | 17.5671 | -352.8906 | 18.7744 | -352.829 | 16.8156
11:41 | 1267 | 21.1417 | 194.3942 | 435.2351 | 441.4111 | -21.7278 | -47.4429 | 0.9515 | -0.5936 | -7.8129 | -7.7278 | -3.456 | -4.228 | 1.8286 | -5.0729 | 0.5817 | 0.6321 | 0.9458 | 0.69 | -131.1828 | -7.0964 | -0.4432 | -1.9313 | -9.9452 | -8.284 | -1.152 |  | -4.0846 | -4.2078 | 4.0018 | 3.3704 | 3.355 | 1.0146 | 10.5868 | 14.0944 | 14.6825 | 11.0219 | -0.0005 | -0.0032 | 0.0007 | 0.0032 | 0.0001 | -0.0009 | 0.0223 | 0.0023 | -0.0177 | -360.1773 | 17.5239 | -360.5466 | 17.7909 | -360.8789 | 18.142 | -360.9897 | 17.5342 | -352.829 | 18.7764 | -352.8321 | 16.8012
11:41 | 1268 | 21.168 | 194.3625 | 435.2166 | 441.4085 | -21.6688 | -47.3269 | 1.0086 | -0.6494 | -7.8827 | -7.724 | -3.506 | -4.2569 | 1.8677 | -5.0944 | 0.5814 | 0.6295 | 0.949 | 0.6905 | -131.1674 | -7.0554 | -0.4369 | -1.9643 | -9.8623 | -8.3915 | -1.1716 |  | -4.1423 | -4.1986 | 4.0025 | 3.3678 | 3.3564 | 1.0155 | 10.6076 | 14.0923 | 14.6703 | 10.9959 | -0.0001 | -0.0031 | 0.0004 | 0.0037 | 0.0011 | -0.0005 | 0.016 | -0.0121 | -0.0111 | -360.165 | 17.528 | -360.5989 | 17.834 | -360.9312 | 18.1399 | -360.9435 | 17.5383 | -352.8321 | 18.7867 | -352.8814 | 16.8381
11:41 | 1269 | 21.2242 | 194.3537 | 435.2257 | 441.4374 | -21.7935 | -47.3169 | 0.9869 | -0.5717 | -7.8668 | -7.6094 | -3.4843 | -4.2077 | 1.818 | -5.071 | 0.5815 | 0.6291 | 0.9499 | 0.6905 | -131.0928 | -7.1053 | -0.3963 | -1.9126 | -9.8443 | -8.3174 | -1.1752 |  | -4.1468 | -4.1975 | 4.0017 | 3.3661 | 3.3528 | 1.0126 | 10.6135 | 14.0863 | 14.6624 | 10.9678 | -0.0003 | -0.003 | 0.0002 | 0.0037 | 0.0002 | -0.0007 | 0.0049 | -0.0032 | -0.0074 | -360.1527 | 17.5321 | -360.6019 | 17.8483 | -360.9312 | 18.1543 | -360.9435 | 17.5219 | -352.8137 | 18.7723 | -352.8875 | 16.8381
11:41 | 1270 | 21.1136 | 194.3106 | 435.2233 | 441.4022 | -21.6795 | -47.3614 | 1.0144 | -0.6135 | -7.8728 | -7.7577 | -3.4765 | -4.2419 | 1.7445 | -5.0934 | 0.5823 | 0.6316 | 0.9479 | 0.6897 | -131.0826 | -7.0868 | -0.3845 | -1.9236 | -9.858 | -8.2696 | -1.1304 |  | -4.152 | -4.1772 | 4.0029 | 3.3676 | 3.3538 | 1.0131 | 10.6527 | 14.0796 | 14.6921 | 11.0179 | -0.0003 | -0.0027 | 0.0003 | 0.0038 | 0.0008 | -0.0009 | 0.0111 | -0.0074 | -0.0074 | -360.1927 | 17.5178 | -360.565 | 17.8175 | -360.9158 | 18.1584 | -360.9558 | 17.5178 | -352.8137 | 18.7538 | -352.8506 | 16.8238
11:41 | 1271 | 21.1361 | 194.292 | 435.1423 | 441.4374 | -21.6225 | -47.3434 | 1.0893 | -0.5198 | -7.7372 | -7.5659 | -3.5186 | -4.1841 | 1.7974 | -5.0325 | 0.581 | 0.6333 | 0.9506 | 0.6904 | -131.0175 | -7.1381 | -0.4029 | -1.8606 | -9.8822 | -8.3336 | -1.1879 |  | -4.0581 | -4.2533 | 4.0022 | 3.3661 | 3.3524 | 1.0149 | 10.6352 | 14.08 | 14.6895 | 10.9937 | -0.0003 | -0.0026 | 0.0017 | 0.0049 | 0.001 | 0 | 0.0066 | 0.0046 | -0.0166 | -360.2235 | 17.526 | -360.5835 | 17.834 | -360.882 | 18.1543 | -361.0081 | 17.5629 | -352.8783 | 18.7703 | -352.8567 | 16.8176
11:41 | 1272 | 21.1734 | 194.3549 | 435.2163 | 441.4298 | -21.6398 | -47.3667 | 1.0666 | -0.5152 | -7.8076 | -7.6579 | -3.4569 | -4.1215 | 1.9191 | -4.9928 | 0.5793 | 0.6312 | 0.9461 | 0.6897 | -130.9691 | -7.0132 | -0.3201 | -1.8907 | -9.8103 | -8.3394 | -1.1548 |  | -4.0757 | -4.1948 | 4.0017 | 3.3675 | 3.3555 | 1.0146 | 10.6087 | 14.1166 | 14.689 | 10.9912 | -0.0002 | -0.0033 | 0.0009 | 0.0039 | 0.0006 | -0.0007 | 0.0007 | -0.0031 | -0.0148 | -360.2296 | 17.5383 | -360.5804 | 17.8032 | -360.8604 | 18.1132 | -360.9404 | 17.5465 | -352.8783 | 18.7785 | -352.8321 | 16.7909
11:41 | 1273 | 21.1525 | 194.3102 | 435.1423 | 441.4133 | -21.6653 | -47.3548 | 1.1166 | -0.4916 | -7.762 | -7.7081 | -3.539 | -4.1803 | 1.8113 | -5.0512 | 0.5803 | 0.632 | 0.9468 | 0.6893 | -131.1242 | -7.1041 | -0.3856 | -1.8393 | -9.8176 | -8.3149 | -1.1868 |  | -4.0596 | -4.2094 | 4.0029 | 3.3701 | 3.3553 | 1.0147 | 10.6006 | 14.0971 | 14.6758 | 11.0176 | 0.0001 | -0.0032 | 0.0008 | 0.0033 | 0.0009 | -0.0006 | 0.0096 | -0.0085 | 0.0048 | -360.2235 | 17.5424 | -360.5896 | 17.8442 | -360.9497 | 18.1399 | -360.9435 | 17.5465 | -352.8567 | 18.7846 | -352.8967 | 16.8464
11:41 | 1274 | 21.2086 | 194.3555 | 435.1839 | 441.3848 | -21.6153 | -47.3189 | 0.9723 | -0.4661 | -7.738 | -7.6447 | -3.4373 | -4.2385 | 1.7233 | -5.0544 | 0.5813 | 0.6322 | 0.9473 | 0.6899 | -131.1436 | -6.9344 | -0.3991 | -1.8096 | -9.8187 | -8.2153 | -1.1845 |  | -4.115 | -4.2144 | 4.0034 | 3.367 | 3.3519 | 1.0134 | 10.6318 | 14.111 | 14.6843 | 11.037 | -0.0004 | -0.0029 | 0.0008 | 0.0035 | 0.0007 | -0.0003 | 0.003 | -0.0063 | -0.0168 | -360.1404 | 17.5034 | -360.565 | 17.8258 | -360.9127 | 18.1748 | -360.9774 | 17.5157 | -352.8198 | 18.7518 | -352.826 | 16.8197
11:41 | 1275 | 21.2853 | 194.3774 | 435.1826 | 441.4606 | -21.6394 | -47.1737 | 1.1005 | -0.5433 | -7.8513 | -7.6658 | -3.5319 | -4.2454 | 1.7949 | -5.1068 | 0.5803 | 0.6295 | 0.9468 | 0.6882 | -131.213 | -6.9409 | -0.4023 | -1.9218 | -9.8176 | -8.2671 | -1.186 |  | -4.0215 | -4.1971 | 4.0021 | 3.3682 | 3.3547 | 1.014 | 10.6376 | 14.111 | 14.7133 | 10.9966 | -0.0005 | -0.0026 | 0.0012 | 0.0038 | 0.0005 | -0.0011 | 0.0173 | -0.0121 | -0.019 | -360.1711 | 17.5075 | -360.5527 | 17.8401 | -360.922 | 18.1748 | -361.002 | 17.5506 | -352.8475 | 18.762 | -352.8383 | 16.8238
11:41 | 1276 | 21.252 | 194.3458 | 435.1724 | 441.4169 | -21.6424 | -47.1899 | 1.134 | -0.5251 | -7.8101 | -7.698 | -3.59 | -4.2751 | 1.8933 | -5.0345 | 0.5809 | 0.6317 | 0.9458 | 0.6882 | -131.2179 | -7.0013 | -0.4486 | -1.9536 | -9.7979 | -8.2804 | -1.0914 |  | -3.9761 | -4.1704 | 4.002 | 3.3671 | 3.3536 | 1.0144 | 10.6237 | 14.0855 | 14.6468 | 11.0233 | 0.0001 | -0.003 | 0.0006 | 0.004 | 0.0006 | 0 | 0.0011 | -0.009 | -0.0142 | -360.1835 | 17.5321 | -360.6019 | 17.8175 | -360.8789 | 18.1461 | -360.9558 | 17.5445 | -352.8506 | 18.7846 | -352.8414 | 16.8115
11:41 | 1277 | 21.3024 | 194.2716 | 435.2685 | 441.4624 | -21.6638 | -47.2914 | 1.1718 | -0.482 | -7.7982 | -7.7217 | -3.5758 | -4.1666 | 1.8868 | -4.9979 | 0.5808 | 0.6306 | 0.9495 | 0.6899 | -131.123 | -6.9524 | -0.4778 | -1.965 | -9.8211 | -8.2786 | -1.0353 |  | -3.9732 | -4.1448 | 4.0012 | 3.3679 | 3.3535 | 1.0146 | 10.6527 | 14.1086 | 14.6989 | 11.0233 | -0.0001 | -0.003 | 0.001 | 0.0044 | 0.0008 | -0.0009 | 0.0121 | 0.0017 | 0.0102 | -360.1835 | 17.5383 | -360.6019 | 17.8566 | -360.9374 | 18.1502 | -360.9189 | 17.5219 | -352.8598 | 18.7826 | -352.8937 | 16.8361
11:41 | 1278 | 21.3561 | 194.4407 | 435.3128 | 441.5017 | -21.6823 | -47.2369 | 1.2335 | -0.4508 | -7.7975 | -7.5536 | -3.4735 | -4.1231 | 1.8795 | -5.1262 | 0.5806 | 0.6342 | 0.9446 | 0.6889 | -131.1817 | -7.0286 | -0.4786 | -1.9367 | -9.7953 | -8.3468 | -1.1209 |  | -3.9656 | -4.1468 | 4.0017 | 3.369 | 3.3518 | 1.0151 | 10.6052 | 14.0785 | 14.6744 | 10.9934 | -0.0001 | -0.003 | 0.0005 | 0.0035 | 0.0004 | -0.0005 | 0.0193 | -0.01 | -0.0059 | -360.1988 | 17.528 | -360.6143 | 17.8463 | -360.9589 | 18.1728 | -360.9497 | 17.5137 | -352.8198 | 18.7744 | -352.866 | 16.8402
11:41 | 1279 | 21.3609 | 194.4999 | 435.2452 | 441.4133 | -21.6777 | -47.2735 | 1.1891 | -0.4462 | -7.7736 | -7.7421 | -3.5052 | -4.1723 | 1.9317 | -5.0847 | 0.5811 | 0.6302 | 0.9453 | 0.6913 | -131.0882 | -6.9906 | -0.365 | -1.8896 | -9.7718 | -8.2314 | -0.9913 |  | -4.0329 | -4.2088 | 4.0018 | 3.3691 | 3.3507 | 1.0153 | 10.6261 | 14.0818 | 14.7054 | 10.9974 | -0.0003 | -0.0027 | 0.0005 | 0.0038 | 0.0007 | -0.0011 | 0.0071 | -0.0097 | -0.0136 | -360.1558 | 17.4993 | -360.5435 | 17.8217 | -360.8943 | 18.1687 | -360.9681 | 17.5424 | -352.8444 | 18.7538 | -352.8137 | 16.8279
11:41 | 1280 | 21.2909 | 194.5719 | 435.2697 | 441.5221 | -21.7057 | -47.3332 | 1.1681 | -0.5145 | -7.7342 | -7.7613 | -3.4741 | -4.2006 | 1.8649 | -5.0499 | 0.5812 | 0.6339 | 0.9455 | 0.69 | -131.1907 | -7.0069 | -0.5143 | -1.935 | -9.7432 | -8.4479 | -1.0216 |  | -4.0476 | -4.0081 | 4.0024 | 3.3712 | 3.3546 | 1.0154 | 10.6099 | 14.0716 | 14.6962 | 11.0385 | -0.0004 | -0.0027 | 0.0004 | 0.0036 | 0.0007 | -0.0005 | 0.0069 | -0.0074 | -0.0123 | -360.2388 | 17.5404 | -360.5619 | 17.797 | -360.8666 | 18.1604 | -360.9804 | 17.5629 | -352.8906 | 18.7805 | -352.8352 | 16.8012
11:41 | 1281 | 21.2496 | 194.5842 | 435.3637 | 441.5068 | -21.7252 | -47.3109 | 1.1151 | -0.5103 | -7.8265 | -7.7658 | -3.4958 | -4.1793 | 1.9556 | -5.0786 | 0.5815 | 0.6315 | 0.9476 | 0.6903 | -131.2026 | -7.0116 | -0.4853 | -1.9515 | -9.7978 | -8.2693 | -1.0565 |  | -3.9458 | -4.0265 | 4.0028 | 3.3709 | 3.3569 | 1.0149 | 10.6352 | 14.1203 | 14.6942 | 10.9825 | 0.0001 | -0.003 | 0.0002 | 0.0031 | 0.0003 | -0.0004 | -0.0066 | -0.0131 | -0.0185 | -360.1619 | 17.5383 | -360.5619 | 17.8237 | -360.8789 | 18.1543 | -360.9404 | 17.5321 | -352.8598 | 18.7928 | -352.8629 | 16.8197
11:41 | 1282 | 21.2984 | 194.6256 | 435.3953 | 441.5402 | -21.6425 | -47.277 | 1.2275 | -0.5556 | -7.74 | -7.6373 | -3.4461 | -4.1224 | 1.8455 | -5.0683 | 0.5813 | 0.6364 | 0.9474 | 0.6893 | -131.148 | -6.9256 | -0.3823 | -1.9691 | -9.7539 | -8.29 | -1.1005 |  | -4.0441 | -4.1015 | 4.003 | 3.3692 | 3.3531 | 1.0154 | 10.61 | 14.0829 | 14.723 | 11.0162 | 0 | -0.0032 | 0.0008 | 0.0037 | 0.0009 | -0.0006 | -0.0008 | -0.0082 | -0.009 | -360.125 | 17.5198 | -360.5958 | 17.8463 | -360.9712 | 18.1892 | -360.9651 | 17.5178 | -352.7921 | 18.7641 | -352.8567 | 16.8443
11:41 | 1283 | 21.3588 | 194.6301 | 435.3972 | 441.4964 | -21.7186 | -47.3237 | 1.1027 | -0.435 | -7.6427 | -7.5667 | -3.536 | -4.2066 | 1.8051 | -5.1129 | 0.5791 | 0.6313 | 0.9454 | 0.6889 | -131.1313 | -7.003 | -0.4675 | -1.9869 | -9.7585 | -8.3389 | -1.0797 |  | -3.9514 | -4.0761 | 4.0006 | 3.3663 | 3.3514 | 1.0151 | 10.6088 | 14.0529 | 14.6533 | 10.98 | -0.0005 | -0.0028 | 0.0006 | 0.0035 | 0.0005 | 0.0002 | 0.0236 | -0.0145 | -0.0096 | -360.1527 | 17.489 | -360.5189 | 17.8196 | -360.9035 | 18.1789 | -360.9558 | 17.5342 | -352.7952 | 18.7436 | -352.8044 | 16.8176
11:41 | 1284 | 21.3541 | 194.6799 | 435.4357 | 441.553 | -21.7008 | -47.3037 | 1.1968 | -0.467 | -7.6485 | -7.6506 | -3.5764 | -4.2613 | 1.8745 | -5.005 | 0.5808 | 0.6336 | 0.9449 | 0.692 | -131.0894 | -6.9001 | -0.4108 | -1.9572 | -9.8058 | -8.4068 | -0.9845 |  | -3.932 | -4.0705 | 4.0007 | 3.3722 | 3.358 | 1.0158 | 10.6399 | 14.1074 | 14.6628 | 10.9934 | -0.0003 | -0.0026 | 0.0008 | 0.0037 | 0.0006 | -0.0011 | 0.0077 | -0.0069 | -0.0028 | -360.2327 | 17.5506 | -360.5927 | 17.8175 | -360.9097 | 18.1563 | -360.9651 | 17.5547 | -352.8783 | 18.7908 | -352.8906 | 16.8115
11:41 | 1285 | 21.3307 | 194.6993 | 435.4236 | 441.5161 | -21.8026 | -47.4565 | 1.0625 | -0.4429 | -7.6168 | -7.5816 | -3.493 | -4.2172 | 1.9063 | -4.9731 | 0.5806 | 0.6325 | 0.9469 | 0.6891 | -131.0534 | -7.0357 | -0.3957 | -1.9032 | -9.7376 | -8.3736 | -1.0869 |  | -3.9566 | -4.1163 | 4.0018 | 3.3698 | 3.3551 | 1.0147 | 10.6204 | 14.076 | 14.6822 | 11.0031 | 0.0004 | -0.0028 | 0.0008 | 0.0042 | 0.0004 | -0.0004 | 0.02 | -0.0062 | -0.0128 | -360.1588 | 17.5404 | -360.6081 | 17.8237 | -360.9004 | 18.144 | -360.8974 | 17.4972 | -352.8229 | 18.799 | -352.8937 | 16.8299
11:41 | 1286 | 21.2727 | 194.7603 | 435.3475 | 441.4995 | -21.8085 | -47.3296 | 1.1335 | -0.438 | -7.6186 | -7.7621 | -3.5332 | -4.1464 | 1.8682 | -4.893 | 0.5811 | 0.6342 | 0.9473 | 0.6909 | -131.1129 | -6.9775 | -0.4503 | -1.8219 | -9.6806 | -8.3837 | -0.9969 |  | -4.035 | -4.1323 | 4.0015 | 3.3708 | 3.355 | 1.015 | 10.6445 | 14.0775 | 14.6683 | 11.0208 | 0.0001 | -0.0032 | 0.0003 | 0.0035 | 0.0007 | -0.0009 | 0.0121 | 0.0108 | -0.0091 | -360.1681 | 17.5445 | -360.6081 | 17.8566 | -360.9743 | 18.1645 | -360.9712 | 17.528 | -352.8198 | 18.7826 | -352.8906 | 16.8381
11:41 | 1287 | 21.342 | 194.8082 | 435.4013 | 441.5091 | -21.7651 | -47.3944 | 1.1376 | -0.3863 | -7.6366 | -7.5157 | -3.534 | -4.1308 | 1.7957 | -4.838 | 0.5797 | 0.6322 | 0.9499 | 0.6902 | -131.0131 | -6.9252 | -0.3501 | -1.823 | -9.6417 | -8.3983 | -0.908 |  | -3.961 | -4.0358 | 4.0012 | 3.3693 | 3.3561 | 1.0149 | 10.6365 | 14.1097 | 14.6877 | 11.0306 | -0.0001 | -0.0028 | 0.0005 | 0.0037 | 0.0004 | -0.0006 | -0.001 | -0.0113 | -0.0076 | -360.1681 | 17.5034 | -360.5035 | 17.8114 | -360.9158 | 18.1728 | -360.9589 | 17.5301 | -352.8229 | 18.7579 | -352.7921 | 16.8135
11:41 | 1288 | 21.2213 | 194.8476 | 435.4657 | 441.4795 | -21.7249 | -47.3503 | 1.094 | -0.4995 | -7.7201 | -7.6214 | -3.6131 | -4.1476 | 1.8251 | -4.9335 | 0.5807 | 0.6309 | 0.9495 | 0.6904 | -131.107 | -6.9699 | -0.4293 | -1.7799 | -9.6633 | -8.2545 | -0.8906 |  | -3.9263 | -4.0343 | 4.0014 | 3.3667 | 3.3574 | 1.0161 | 10.6169 | 14.0609 | 14.6607 | 10.9941 | -0.0005 | -0.003 | 0.0003 | 0.0034 | 0.0008 | -0.0006 | 0.0055 | -0.0032 | -0.0017 | -360.2265 | 17.5445 | -360.5589 | 17.8011 | -360.8758 | 18.1687 | -360.9897 | 17.5588 | -352.9214 | 18.7969 | -352.826 | 16.8074
11:41 | 1289 | 21.2889 | 194.8811 | 435.4657 | 441.518 | -21.7132 | -47.3578 | 1.1554 | -0.4423 | -7.67 | -7.6014 | -3.4976 | -4.1491 | 1.8199 | -5.0282 | 0.5805 | 0.63 | 0.9454 | 0.691 | -131.0531 | -6.9981 | -0.4053 | -1.6994 | -9.6356 | -8.3092 | -0.8937 |  | -3.8924 | -4.169 | 3.9997 | 3.3681 | 3.3531 | 1.0156 | 10.6053 | 14.0957 | 14.6907 | 11.0111 | -0.0007 | -0.0032 | 0.0005 | 0.0032 | 0.001 | -0.0008 | 0.0024 | -0.0059 | -0.0061 | -360.2019 | 17.5301 | -360.5496 | 17.8011 | -360.8604 | 18.1522 | -360.9374 | 17.5239 | -352.8321 | 18.7949 | -352.8321 | 16.8115
11:41 | 1290 | 21.2924 | 194.7839 | 435.3317 | 441.5051 | -21.7479 | -47.3832 | 1.0487 | -0.3972 | -7.6551 | -7.6639 | -3.5681 | -4.1181 | 1.891 | -4.9501 | 0.5813 | 0.6337 | 0.9484 | 0.6915 | -131.0883 | -6.9955 | -0.3389 | -1.7514 | -9.6938 | -8.3351 | -0.9576 |  | -4.0113 | -4.2695 | 4.0018 | 3.3662 | 3.3563 | 1.0161 | 10.6366 | 14.0922 | 14.704 | 10.9905 | -0.0001 | -0.0031 | 0.0005 | 0.0032 | 0.0005 | -0.0003 | 0.0102 | -0.0008 | -0.0177 | -360.1342 | 17.5219 | -360.6081 | 17.8545 | -360.9651 | 18.183 | -360.962 | 17.5219 | -352.8198 | 18.7846 | -352.8629 | 16.8505
11:41 | 1291 | 21.2191 | 194.8082 | 435.372 | 441.5203 | -21.7303 | -47.3079 | 1.1299 | -0.3977 | -7.5054 | -7.6213 | -3.5648 | -4.1505 | 1.8724 | -4.9662 | 0.5817 | 0.6327 | 0.9504 | 0.6902 | -131.0454 | -7.0064 | -0.299 | -1.8072 | -9.6171 | -8.3331 | -1.0373 |  | -3.8964 | -4.2531 | 3.9998 | 3.3685 | 3.3579 | 1.0158 | 10.6272 | 14.0716 | 14.6962 | 11.0212 | -0.0006 | -0.0033 | 0.0013 | 0.0038 | 0.0009 | -0.0007 | 0.0118 | -0.0173 | -0.0223 | -360.0911 | 17.4788 | -360.5281 | 17.8134 | -360.9127 | 18.1892 | -360.9712 | 17.5116 | -352.8075 | 18.7415 | -352.786 | 16.8176
11:41 | 1292 | 21.2509 | 194.8481 | 435.4311 | 441.4735 | -21.7072 | -47.3318 | 1.0819 | -0.5126 | -7.6715 | -7.7453 | -3.5954 | -4.1742 | 1.8266 | -4.9634 | 0.58 | 0.6333 | 0.9458 | 0.6917 | -131.0725 | -7.072 | -0.3669 | -1.8233 | -9.6118 | -8.2977 | -0.9588 |  | -3.8855 | -4.2089 | 4.0009 | 3.3659 | 3.3599 | 1.0164 | 10.641 | 14.1145 | 14.7174 | 11.0287 | -0.0005 | -0.0026 | 0.0005 | 0.0033 | 0.0001 | -0.0004 | 0.0192 | -0.0081 | -0.0151 | -360.2327 | 17.5301 | -360.5804 | 17.8217 | -360.9004 | 18.1789 | -361.0112 | 17.5404 | -352.8598 | 18.7887 | -352.826 | 16.8176
11:41 | 1293 | 21.2643 | 194.8949 | 435.4725 | 441.525 | -21.8406 | -47.4248 | 1.1952 | -0.4307 | -7.6717 | -7.6448 | -3.5644 | -4.2838 | 1.7952 | -4.9763 | 0.5806 | 0.6287 | 0.944 | 0.6912 | -131.0669 | -7.0679 | -0.3858 | -1.8098 | -9.5928 | -8.3824 | -0.9044 |  | -3.821 | -4.198 | 4.0006 | 3.3688 | 3.358 | 1.0156 | 10.6341 | 14.1134 | 14.7507 | 11.0161 | -0.0003 | -0.003 | 0.0001 | 0.0037 | 0.0007 | -0.0006 | -0.0015 | -0.0172 | 0.0061 | -360.1896 | 17.5404 | -360.6081 | 17.8175 | -360.8697 | 18.1296 | -360.9158 | 17.5013 | -352.8167 | 18.8011 | -352.8844 | 16.8156
11:41 | 1294 | 21.2742 | 194.8981 | 435.54 | 441.5789 | -21.839 | -47.3291 | 1.2452 | -0.4692 | -7.7335 | -7.5777 | -3.6101 | -4.2295 | 1.7242 | -4.8996 | 0.5805 | 0.6311 | 0.9434 | 0.6909 | -131.0739 | -6.9791 | -0.3777 | -1.8584 | -9.6384 | -8.2961 | -0.9418 |  | -3.7927 | -4.0619 | 4.0004 | 3.3683 | 3.3552 | 1.0167 | 10.6445 | 14.1064 | 14.6857 | 11.0208 | -0.0001 | -0.0031 | 0.0005 | 0.0037 | 0.0002 | -0.0004 | 0.0127 | 0.001 | 0.0118 | -360.2019 | 17.5527 | -360.6266 | 17.8381 | -360.962 | 18.1604 | -360.9312 | 17.526 | -352.8198 | 18.7908 | -352.8906 | 16.8423
11:41 | 1295 | 21.2506 | 194.8749 | 435.4341 | 441.572 | -21.7792 | -47.4431 | 1.1806 | -0.4262 | -7.6162 | -7.4508 | -3.5547 | -4.1569 | 1.8064 | -4.9038 | 0.5823 | 0.6321 | 0.9451 | 0.6898 | -131.044 | -6.9762 | -0.3404 | -1.9215 | -9.6401 | -8.3255 | -0.8406 |  | -3.9438 | -4.1601 | 4.0002 | 3.3722 | 3.3577 | 1.0151 | 10.595 | 14.0793 | 14.6553 | 11.0014 | -0.0003 | -0.0037 | -0.0001 | 0.0031 | 0.0008 | -0.0009 | 0.0166 | -0.0237 | -0.0022 | -360.1496 | 17.4993 | -360.5219 | 17.8073 | -360.8943 | 18.1748 | -360.9712 | 17.5219 | -352.7614 | 18.7559 | -352.8198 | 16.8197
11:41 | 1296 | 21.1942 | 194.9387 | 435.5029 | 441.6004 | -21.699 | -47.3649 | 1.2376 | -0.3932 | -7.6091 | -7.5497 | -3.5536 | -4.1879 | 1.7376 | -4.8477 | 0.581 | 0.6324 | 0.9456 | 0.6904 | -131.0833 | -6.9616 | -0.343 | -2.0468 | -9.722 | -8.2902 | -0.8813 |  | -3.9528 | -4.0831 | 3.9998 | 3.3689 | 3.3561 | 1.015 | 10.6273 | 14.0599 | 14.6604 | 10.9984 | -0.0003 | -0.0032 | 0.0005 | 0.0038 | 0.0006 | -0.0003 | 0.0117 | -0.0079 | -0.0097 | -360.2512 | 17.5342 | -360.5527 | 17.8073 | -360.8912 | 18.181 | -360.9958 | 17.5588 | -352.8783 | 18.7867 | -352.829 | 16.795
11:41 | 1297 | 21.3302 | 194.8374 | 435.437 | 441.6073 | -21.6945 | -47.3883 | 1.131 | -0.3461 | -7.7095 | -7.4583 | -3.4874 | -4.2255 | 1.6064 | -4.861 | 0.5804 | 0.6309 | 0.9467 | 0.6906 | -131.0428 | -6.9058 | -0.2676 | -1.9169 | -9.7569 | -8.2092 | -0.7975 |  | -3.9024 | -4.1618 | 3.9991 | 3.3682 | 3.3551 | 1.0142 | 10.6156 | 14.0775 | 14.6509 | 11.0035 | -0.0003 | -0.0025 | 0.0011 | 0.0038 | 0.0009 | -0.0006 | 0.0114 | -0.0001 | -0.0048 | -360.1896 | 17.5239 | -360.5619 | 17.7929 | -360.842 | 18.1584 | -360.9774 | 17.5404 | -352.8383 | 18.7846 | -352.8137 | 16.793
11:41 | 1298 | 21.2344 | 194.8537 | 435.4956 | 441.5404 | -21.7111 | -47.3921 | 1.1611 | -0.3257 | -7.7058 | -7.5673 | -3.4969 | -4.2233 | 1.6954 | -4.7662 | 0.5826 | 0.632 | 0.9473 | 0.6909 | -131.1038 | -6.9441 | -0.2914 | -1.9246 | -9.7166 | -8.2472 | -0.8326 |  | -3.9387 | -4.1064 | 4.0009 | 3.3693 | 3.3577 | 1.015 | 10.6423 | 14.0923 | 14.6761 | 11.019 | 0.0001 | -0.0032 | 0.0008 | 0.0038 | 0.0003 | -0.0008 | 0.0148 | -0.0126 | -0.0032 | -360.1804 | 17.528 | -360.5989 | 17.8463 | -360.9589 | 18.1666 | -360.9651 | 17.5157 | -352.829 | 18.7969 | -352.8814 | 16.8381
11:41 | 1299 | 21.2459 | 194.8066 | 435.3835 | 441.4864 | -21.7407 | -47.4004 | 1.1596 | -0.3303 | -7.6592 | -7.6037 | -3.4415 | -4.2722 | 1.7002 | -4.8268 | 0.5805 | 0.6332 | 0.9433 | 0.6897 | -131.1074 | -6.9317 | -0.3981 | -2.0007 | -9.7792 | -8.2217 | -0.8573 |  | -3.8987 | -4.1253 | 4.0016 | 3.3696 | 3.3557 | 1.0155 | 10.6224 | 14.1136 | 14.7065 | 11.0384 | 0.0004 | -0.0028 | 0.0014 | 0.0045 | 0.0004 | -0.0004 | 0.0095 | -0.0056 | -0.0094 | -360.1034 | 17.489 | -360.5404 | 17.8381 | -360.9466 | 18.1851 | -360.962 | 17.5178 | -352.7983 | 18.7538 | -352.8352 | 16.8238
11:41 | 1300 | 21.328 | 194.7787 | 435.4043 | 441.5294 | -21.7714 | -47.4955 | 1.1345 | -0.3724 | -7.6898 | -7.5698 | -3.5098 | -4.3042 | 1.801 | -4.8112 | 0.5807 | 0.6348 | 0.9463 | 0.6894 | -131.0924 | -6.9958 | -0.292 | -2.0191 | -9.7155 | -8.3153 | -0.904 |  | -3.885 | -4.1769 | 4.0004 | 3.3698 | 3.3535 | 1.0156 | 10.6434 | 14.1168 | 14.7133 | 11.0197 | -0.0002 | -0.0028 | 0.0005 | 0.0032 | 0.0007 | -0.0008 | 0.0193 | 0.0035 | -0.0086 | -360.1865 | 17.5096 | -360.5558 | 17.8319 | -360.9343 | 18.1974 | -360.9927 | 17.5445 | -352.8444 | 18.7764 | -352.829 | 16.8074
11:41 | 1301 | 21.4689 | 194.8724 | 435.5332 | 441.629 | -21.8487 | -47.425 | 1.0945 | -0.3653 | -7.5912 | -7.4568 | -3.5089 | -4.2509 | 1.8435 | -4.8459 | 0.5804 | 0.6352 | 0.9483 | 0.6906 | -131.0863 | -6.9491 | -0.1849 | -2.0398 | -9.8407 | -8.2942 | -0.8861 |  | -3.9975 | -4.1274 | 4.0011 | 3.3699 | 3.3558 | 1.0147 | 10.6422 | 14.1157 | 14.7361 | 11.0587 | -0.0005 | -0.003 | 0.0001 | 0.0035 | 0.0006 | -0.0002 | -0.0051 | -0.0016 | -0.022 | -360.1958 | 17.526 | -360.5681 | 17.8032 | -360.8666 | 18.1543 | -360.9743 | 17.5301 | -352.8506 | 18.7928 | -352.8691 | 16.8032
11:41 | 1302 | 21.3652 | 194.8115 | 435.4798 | 441.5544 | -21.7233 | -47.4196 | 1.0462 | -0.4016 | -7.6226 | -7.4964 | -3.5257 | -4.2748 | 1.8477 | -4.8158 | 0.5815 | 0.6336 | 0.9478 | 0.6907 | -131.1592 | -6.9527 | -0.2133 | -1.9296 | -9.6802 | -8.2141 | -0.8174 |  | -3.9377 | -4.1213 | 4.0004 | 3.3676 | 3.3548 | 1.0148 | 10.6305 | 14.1159 | 14.6966 | 11.0121 | 0 | -0.0027 | 0.0005 | 0.0038 | 0.0009 | -0.0005 | 0.0092 | 0.0049 | -0.0119 | -360.2019 | 17.5527 | -360.6543 | 17.8401 | -360.9066 | 18.1502 | -360.9404 | 17.5137 | -352.826 | 18.8052 | -352.8998 | 16.8217
11:41 | 1303 | 21.362 | 194.8128 | 435.5633 | 441.5587 | -21.6191 | -47.3152 | 1.1136 | -0.378 | -7.6269 | -7.5578 | -3.5204 | -4.3143 | 1.8461 | -4.8381 | 0.5794 | 0.6331 | 0.9444 | 0.6902 | -131.0959 | -6.9068 | -0.1994 | -1.934 | -9.6929 | -8.3278 | -0.9158 |  | -3.9754 | -4.2328 | 4.0007 | 3.3693 | 3.3521 | 1.0142 | 10.61 | 14.0713 | 14.6883 | 10.9873 | -0.0001 | -0.0034 | 0.0001 | 0.0034 | 0.0004 | -0.0005 | 0.0075 | 0 | 0.0025 | -360.1558 | 17.5198 | -360.5712 | 17.836 | -360.9127 | 18.1563 | -360.9374 | 17.5198 | -352.829 | 18.7764 | -352.8998 | 16.8279
11:41 | 1304 | 21.3567 | 194.8025 | 435.5184 | 441.6426 | -21.694 | -47.412 | 1.131 | -0.3892 | -7.6831 | -7.5115 | -3.5193 | -4.343 | 1.8333 | -4.902 | 0.5815 | 0.6332 | 0.946 | 0.6903 | -131.0721 | -6.8458 | -0.1538 | -1.9143 | -9.6439 | -8.2178 | -0.8379 |  | -3.9729 | -4.173 | 3.9987 | 3.3673 | 3.3577 | 1.0165 | 10.6041 | 14.0772 | 14.672 | 11.0447 | 0 | -0.0027 | 0.0005 | 0.0038 | 0.0006 | -0.001 | 0.0117 | -0.0078 | -0.0086 | -360.1804 | 17.5055 | -360.5373 | 17.8237 | -360.8974 | 18.1953 | -360.9681 | 17.526 | -352.8137 | 18.7703 | -352.8229 | 16.8074
11:41 | 1305 | 21.332 | 194.829 | 435.4057 | 441.5988 | -21.6738 | -47.3824 | 1.1405 | -0.3891 | -7.7462 | -7.4589 | -3.5542 | -4.1862 | 1.8494 | -4.9044 | 0.5793 | 0.6371 | 0.9429 | 0.6903 | -131.0644 | -6.9446 | -0.1172 | -1.8965 | -9.6127 | -8.2393 | -0.8737 |  | -3.8213 | -4.1016 | 4.0011 | 3.3691 | 3.3576 | 1.0166 | 10.5765 | 14.0839 | 14.6713 | 10.9887 | -0.0005 | -0.0029 | 0.0009 | 0.0037 | 0.0004 | -0.0006 | 0.0104 | -0.0041 | -0.0013 | -360.1588 | 17.5116 | -360.5373 | 17.7929 | -360.882 | 18.1789 | -360.9927 | 17.5547 | -352.8752 | 18.7744 | -352.8106 | 16.795
11:41 | 1306 | 21.3476 | 194.8042 | 435.5026 | 441.6674 | -21.7008 | -47.3313 | 1.0834 | -0.4935 | -7.67 | -7.6693 | -3.5307 | -4.2399 | 1.9433 | -4.899 | 0.5803 | 0.6359 | 0.9457 | 0.6902 | -131.0963 | -6.8969 | -0.202 | -1.9197 | -9.6712 | -8.1964 | -0.8502 |  | -3.9424 | -4.1543 | 4.0018 | 3.3702 | 3.355 | 1.0174 | 10.6054 | 14.0723 | 14.6423 | 10.9772 | -0.0003 | -0.0023 | 0.0008 | 0.0035 | 0.0005 | -0.0006 | -0.0071 | -0.0146 | -0.0188 | -360.2296 | 17.5301 | -360.5743 | 17.8134 | -360.8727 | 18.1728 | -360.962 | 17.5342 | -352.829 | 18.7867 | -352.8383 | 16.793
11:41 | 1307 | 21.2355 | 194.7366 | 435.5351 | 441.5379 | -21.6867 | -47.39 | 1.0811 | -0.4544 | -7.7182 | -7.6078 | -3.5131 | -4.2039 | 1.8985 | -4.8899 | 0.5805 | 0.6376 | 0.948 | 0.6912 | -131.1036 | -6.8363 | -0.1459 | -1.8959 | -9.5805 | -8.1334 | -0.851 |  | -3.8395 | -4.1338 | 4.0014 | 3.3695 | 3.3522 | 1.016 | 10.5844 | 14.0925 | 14.6945 | 11.0244 | -0.0001 | -0.0032 | 0.0013 | 0.004 | 0.0012 | -0.0007 | 0.0025 | -0.0057 | -0.0231 | -360.1896 | 17.526 | -360.6112 | 17.8525 | -360.9312 | 18.1666 | -360.9651 | 17.5239 | -352.8414 | 18.7928 | -352.906 | 16.834
11:42 | 1308 | 21.143 | 194.688 | 435.4816 | 441.4759 | -21.674 | -47.364 | 1.1234 | -0.4145 | -7.7302 | -7.7061 | -3.4969 | -4.1319 | 2.0024 | -4.8413 | 0.5819 | 0.6351 | 0.9434 | 0.6892 | -131.0764 | -6.9295 | -0.1688 | -1.9199 | -9.6281 | -8.1145 | -0.8715 |  | -3.8613 | -4.1178 | 4.0005 | 3.3677 | 3.3545 | 1.0178 | 10.6399 | 14.1076 | 14.7218 | 11.0565 | -0.0001 | -0.0033 | 0.0009 | 0.0041 | 0.0005 | -0.0003 | 0.0031 | -0.003 | -0.0159 | -360.1619 | 17.5075 | -360.565 | 17.8463 | -360.9343 | 18.181 | -360.9558 | 17.5013 | -352.7675 | 18.7579 | -352.8475 | 16.8258
11:42 | 1309 | 21.2612 | 194.8025 | 435.4782 | 441.5369 | -21.6492 | -47.28 | 1.1582 | -0.467 | -7.6679 | -7.5717 | -3.5278 | -4.1609 | 1.9815 | -4.8633 | 0.581 | 0.6355 | 0.9454 | 0.6905 | -131.164 | -6.8556 | -0.2134 | -2.0235 | -9.7114 | -8.2736 | -0.9514 |  | -3.8883 | -4.062 | 4.0014 | 3.3703 | 3.3531 | 1.017 | 10.6248 | 14.0868 | 14.7419 | 11.0587 | -0.0002 | -0.0029 | 0.0002 | 0.0032 | 0.0013 | -0.0008 | 0.0171 | -0.0205 | -0.0211 | -360.1558 | 17.5157 | -360.5589 | 17.8525 | -360.9558 | 18.1851 | -360.9774 | 17.5219 | -352.8198 | 18.7867 | -352.8691 | 16.834
11:42 | 1310 | 21.276 | 194.7954 | 435.4929 | 441.5518 | -21.59 | -47.3205 | 1.1733 | -0.4073 | -7.5909 | -7.5059 | -3.3972 | -4.2052 | 1.9397 | -4.8359 | 0.5816 | 0.6376 | 0.947 | 0.6909 | -131.1322 | -6.8281 | -0.1824 | -1.9042 | -9.7124 | -8.2428 | -0.8557 |  | -3.8625 | -4.0355 | 3.9992 | 3.3666 | 3.3544 | 1.0163 | 10.6123 | 14.1141 | 14.691 | 11.0068 | -0.0007 | -0.003 | 0.0006 | 0.0036 | -0.0002 | -0.0007 | -0.0031 | -0.0231 | -0.01 | -360.1619 | 17.5096 | -360.5466 | 17.8073 | -360.8727 | 18.1625 | -360.9497 | 17.5342 | -352.8075 | 18.7744 | -352.8321 | 16.7868
11:42 | 1311 | 21.2356 | 194.8191 | 435.4345 | 441.4996 | -21.6619 | -47.3706 | 1.1594 | -0.3781 | -7.6832 | -7.6087 | -3.3473 | -4.258 | 2.0574 | -4.8653 | 0.5808 | 0.6348 | 0.946 | 0.692 | -131.112 | -6.86 | -0.2108 | -1.9563 | -9.678 | -8.2357 | -0.8502 |  | -3.8935 | -4.002 | 4.001 | 3.3727 | 3.3557 | 1.0176 | 10.6272 | 14.1063 | 14.7194 | 11.0269 | -0.0001 | -0.0029 | 0.0003 | 0.0034 | 0.0013 | -0.0006 | 0.0065 | -0.0052 | -0.0205 | -360.1896 | 17.5547 | -360.5958 | 17.8237 | -360.8727 | 18.1461 | -360.9466 | 17.5404 | -352.8598 | 18.8093 | -352.8967 | 16.8074
11:42 | 1312 | 21.1668 | 194.7982 | 435.3054 | 441.3826 | -21.6432 | -47.2007 | 1.1995 | -0.3537 | -7.6964 | -7.563 | -3.3441 | -4.2685 | 1.9747 | -4.8767 | 0.5812 | 0.6328 | 0.9495 | 0.6908 | -131.0317 | -6.8296 | -0.1734 | -1.8857 | -9.6759 | -8.1377 | -0.8155 |  | -3.8073 | -4.0828 | 4.0007 | 3.3725 | 3.3572 | 1.0202 | 10.588 | 14.084 | 14.707 | 10.9826 | -0.0001 | -0.0038 | 0.0006 | 0.0039 | 0 | -0.0008 | -0.0011 | -0.011 | -0.0197 | -360.1711 | 17.526 | -360.5835 | 17.834 | -360.922 | 18.1461 | -360.9374 | 17.5219 | -352.8229 | 18.7826 | -352.866 | 16.8094
11:42 | 1313 | 21.2913 | 194.833 | 435.4844 | 441.4267 | -21.5724 | -47.2364 | 1.231 | -0.3421 | -7.6974 | -7.6463 | -3.4059 | -4.2994 | 1.9659 | -4.952 | 0.5803 | 0.6364 | 0.9463 | 0.6911 | -131.1087 | -6.8448 | -0.285 | -1.9176 | -9.6718 | -8.1918 | -0.8553 |  | -3.829 | -4.207 | 4.001 | 3.3701 | 3.3532 | 1.0177 | 10.6019 | 14.0747 | 14.674 | 10.9562 | -0.0001 | -0.0031 | 0.001 | 0.0041 | 0.0009 | -0.0005 | -0.0017 | 0.0011 | -0.0158 | -360.1619 | 17.5157 | -360.5773 | 17.834 | -360.9404 | 18.1892 | -360.9774 | 17.5157 | -352.829 | 18.7846 | -352.8537 | 16.8217
11:42 | 1314 | 21.2814 | 194.8247 | 435.5046 | 441.4411 | -21.6085 | -47.3942 | 1.1584 | -0.332 | -7.6289 | -7.4806 | -3.3269 | -4.2469 | 1.8788 | -4.887 | 0.5814 | 0.6349 | 0.9457 | 0.6913 | -131.1376 | -6.9821 | -0.2471 | -1.9043 | -9.6677 | -8.2546 | -0.8901 |  | -3.8894 | -4.0371 | 4.0004 | 3.3682 | 3.3556 | 1.0167 | 10.6052 | 14.0785 | 14.6976 | 10.9876 | -0.0005 | -0.0027 | 0.0008 | 0.0037 | 0.0008 | -0.0009 | 0.0111 | -0.0002 | -0.0029 | -360.1927 | 17.4993 | -360.5189 | 17.8134 | -360.9066 | 18.1933 | -360.9958 | 17.5342 | -352.8321 | 18.7538 | -352.8106 | 16.7991
11:42 | 1315 | 21.3902 | 194.8301 | 435.4996 | 441.3878 | -21.5909 | -47.2999 | 1.2008 | -0.3129 | -7.6963 | -7.5173 | -3.4281 | -4.2539 | 1.9494 | -4.8184 | 0.582 | 0.6363 | 0.9447 | 0.6914 | -131.1634 | -6.9593 | -0.3691 | -1.8115 | -9.6191 | -8.2958 | -0.8665 |  | -3.8816 | -4.0476 | 3.9995 | 3.3694 | 3.3548 | 1.0179 | 10.6272 | 14.0947 | 14.6846 | 11.0154 | -0.0004 | -0.0029 | 0.0009 | 0.0036 | 0.0006 | -0.0004 | 0.0165 | 0.0022 | -0.0046 | -360.1558 | 17.5301 | -360.5866 | 17.8237 | -360.8912 | 18.1625 | -360.9866 | 17.5321 | -352.8352 | 18.7949 | -352.8383 | 16.8032
11:42 | 1316 | 21.3575 | 194.8111 | 435.5579 | 441.5083 | -21.6353 | -47.3097 | 1.1462 | -0.3338 | -7.6658 | -7.4316 | -3.3592 | -4.365 | 1.8282 | -4.8779 | 0.5807 | 0.6382 | 0.947 | 0.691 | -131.1961 | -6.8947 | -0.4076 | -1.9159 | -9.616 | -8.2455 | -0.8228 |  | -3.8823 | -4.0274 | 4.0005 | 3.3682 | 3.3549 | 1.0194 | 10.6537 | 14.1274 | 14.7429 | 11.0468 | 0.0002 | -0.0031 | 0.0007 | 0.0038 | 0.0007 | -0.0005 | 0.0129 | 0.0006 | -0.0178 | -360.1835 | 17.5363 | -360.5989 | 17.834 | -360.9097 | 18.144 | -360.9251 | 17.5157 | -352.8475 | 18.7908 | -352.826 | 16.8115
11:42 | 1317 | 21.3732 | 194.8021 | 435.536 | 441.4416 | -21.6724 | -47.4186 | 1.1115 | -0.4112 | -7.6852 | -7.4568 | -3.3567 | -4.2725 | 1.8947 | -4.8262 | 0.5808 | 0.632 | 0.9464 | 0.6909 | -131.1009 | -6.8392 | -0.416 | -2.0438 | -9.6295 | -8.2725 | -0.9453 |  | -3.8151 | -4.0849 | 4.0022 | 3.3703 | 3.3558 | 1.0189 | 10.6168 | 14.1074 | 14.6976 | 11.0222 | -0.0002 | -0.0034 | 0.0005 | 0.0033 | 0.0006 | -0.0003 | 0.0107 | -0.0007 | -0.0001 | -360.1773 | 17.5342 | -360.6204 | 17.8586 | -360.9374 | 18.1748 | -360.9435 | 17.5116 | -352.8044 | 18.7908 | -352.9029 | 16.8402
11:42 | 1318 | 21.3933 | 194.876 | 435.4966 | 441.4103 | -21.6525 | -47.3889 | 1.1101 | -0.4028 | -7.7305 | -7.5176 | -3.3516 | -4.3489 | 1.8694 | -4.9335 | 0.58 | 0.6313 | 0.9435 | 0.6899 | -131.1642 | -6.9346 | -0.3311 | -2.0778 | -9.6546 | -8.1963 | -0.8665 |  | -3.7325 | -4.0985 | 4.001 | 3.3712 | 3.354 | 1.0195 | 10.6192 | 14.0748 | 14.7098 | 11.0367 | -0.0003 | -0.0027 | 0.0008 | 0.0036 | 0.0007 | -0.0006 | 0.0163 | -0.0043 | 0.0007 | -360.165 | 17.5034 | -360.5435 | 17.8217 | -360.9004 | 18.1769 | -360.9589 | 17.5137 | -352.8044 | 18.7703 | -352.8075 | 16.7991
11:42 | 1319 | 21.4327 | 194.8666 | 435.4753 | 441.4421 | -21.6595 | -47.323 | 1.0964 | -0.4233 | -7.7253 | -7.3686 | -3.2976 | -4.2558 | 1.9682 | -4.9534 | 0.5822 | 0.6341 | 0.9448 | 0.6916 | -131.1588 | -6.9399 | -0.3203 | -2.1605 | -9.6092 | -8.192 | -0.8989 |  | -3.713 | -3.9997 | 3.9989 | 3.3698 | 3.3569 | 1.0182 | 10.6144 | 14.0763 | 14.6959 | 11.0024 | -0.0001 | -0.0027 | 0.0005 | 0.0041 | 0.0003 | -0.0003 | 0.0139 | -0.0012 | -0.0082 | -360.2265 | 17.5301 | -360.5743 | 17.8278 | -360.8666 | 18.1645 | -360.9958 | 17.5445 | -352.8752 | 18.7908 | -352.8383 | 16.795
11:42 | 1320 | 21.3574 | 194.8553 | 435.5178 | 441.4745 | -21.6113 | -47.347 | 1.0709 | -0.3518 | -7.6361 | -7.4639 | -3.3406 | -4.2957 | 1.9359 | -4.9967 | 0.5823 | 0.6338 | 0.949 | 0.693 | -131.0893 | -6.9071 | -0.2869 | -2.0517 | -9.6369 | -8.3017 | -0.909 |  | -3.7312 | -3.9679 | 4.0007 | 3.3687 | 3.3556 | 1.0179 | 10.6146 | 14.0528 | 14.658 | 10.9862 | 0 | -0.0031 | 0.0008 | 0.0039 | 0.0007 | -0.0012 | -0.0059 | -0.017 | -0.011 | -360.1804 | 17.5342 | -360.5835 | 17.8442 | -360.8912 | 18.1502 | -360.922 | 17.526 | -352.8414 | 18.7908 | -352.8383 | 16.7991
11:42 | 1321 | 21.3751 | 194.8622 | 435.5522 | 441.4782 | -21.599 | -47.3685 | 1.1499 | -0.3638 | -7.6282 | -7.3334 | -3.336 | -4.2201 | 1.9216 | -4.928 | 0.5813 | 0.6333 | 0.9465 | 0.6911 | -131.0834 | -6.9756 | -0.3636 | -2.0826 | -9.6271 | -8.3109 | -0.9268 |  | -3.7253 | -3.9682 | 4.0007 | 3.3689 | 3.3548 | 1.0173 | 10.5799 | 14.0702 | 14.6591 | 11.0147 | 0.0006 | -0.003 | 0.0007 | 0.0039 | 0.0005 | -0.0002 | -0.0004 | -0.0164 | -0.0154 | -360.1435 | 17.5321 | -360.565 | 17.8648 | -360.9374 | 18.1871 | -360.9589 | 17.5137 | -352.8014 | 18.7805 | -352.8475 | 16.8299
11:42 | 1322 | 21.4449 | 194.8079 | 435.511 | 441.4448 | -21.667 | -47.2625 | 1.0978 | -0.3487 | -7.6472 | -7.2615 | -3.4107 | -4.2601 | 1.8984 | -4.9716 | 0.5803 | 0.6355 | 0.9503 | 0.6925 | -130.9686 | -6.9498 | -0.2965 | -2.0255 | -9.6082 | -8.2094 | -0.9024 |  | -3.748 | -3.9279 | 3.9994 | 3.3683 | 3.3521 | 1.0174 | 10.6214 | 14.112 | 14.6962 | 11.0154 | -0.0005 | -0.0031 | 0.0005 | 0.0035 | 0.0006 | -0.0011 | 0.0105 | -0.0175 | -0.0065 | -360.1619 | 17.5096 | -360.565 | 17.8709 | -360.922 | 18.181 | -361.0081 | 17.5404 | -352.8198 | 18.76 | -352.8352 | 16.8053
11:42 | 1323 | 21.435 | 194.7854 | 435.493 | 441.4525 | -21.6684 | -47.3246 | 1.0559 | -0.322 | -7.6666 | -7.4177 | -3.4175 | -4.1813 | 1.9232 | -4.9121 | 0.581 | 0.6348 | 0.9476 | 0.6913 | -131.0264 | -6.9653 | -0.2989 | -2.139 | -9.6256 | -8.2454 | -0.8705 |  | -3.6635 | -3.9417 | 4.0002 | 3.3715 | 3.3553 | 1.0182 | 10.6445 | 14.1297 | 14.7099 | 11.0089 | -0.0004 | -0.0022 | 0.0008 | 0.0035 | 0.0005 | -0.0005 | 0.0037 | -0.0134 | -0.0131 | -360.2019 | 17.5219 | -360.5681 | 17.8607 | -360.882 | 18.1687 | -360.9681 | 17.5239 | -352.829 | 18.7846 | -352.826 | 16.8156
11:42 | 1324 | 21.3752 | 194.7801 | 435.4107 | 441.3349 | -21.6375 | -47.3068 | 1.1309 | -0.312 | -7.7239 | -7.541 | -3.369 | -4.2093 | 1.9644 | -4.8247 | 0.5804 | 0.6276 | 0.9452 | 0.6924 | -131.082 | -6.8921 | -0.2509 | -1.968 | -9.5075 | -8.3306 | -0.8351 |  | -3.6801 | -3.9752 | 4.0007 | 3.368 | 3.3516 | 1.0177 | 10.6339 | 14.1196 | 14.7134 | 11.0323 | 0.0001 | -0.0026 | 0.001 | 0.004 | 0.0002 | -0.0005 | -0.0034 | -0.0096 | -0.0248 | -360.1896 | 17.5383 | -360.6173 | 17.8894 | -360.9251 | 18.1481 | -360.9466 | 17.5342 | -352.826 | 18.7928 | -352.8844 | 16.8176
11:42 | 1325 | 21.4181 | 194.7644 | 435.4464 | 441.3612 | -21.673 | -47.3363 | 1.0633 | -0.4316 | -7.7041 | -7.488 | -3.2509 | -4.1638 | 1.9557 | -4.8412 | 0.5813 | 0.6376 | 0.9471 | 0.6924 | -131.0242 | -6.9019 | -0.282 | -2.0379 | -9.5777 | -8.2935 | -0.8693 |  | -3.6987 | -3.9591 | 4.0022 | 3.3728 | 3.351 | 1.0189 | 10.61 | 14.0829 | 14.6767 | 11.0393 | 0.0002 | -0.003 | 0.0002 | 0.0031 | 0.0006 | -0.001 | 0.0039 | 0.0019 | -0.0079 | -360.1496 | 17.5301 | -360.5927 | 17.8586 | -360.9066 | 18.1604 | -360.9404 | 17.5013 | -352.8044 | 18.7826 | -352.8875 | 16.8156
11:42 | 1326 | 21.4361 | 194.8685 | 435.4576 | 441.3888 | -21.6807 | -47.2069 | 1.1407 | -0.3798 | -7.7145 | -7.6254 | -3.2648 | -4.2041 | 1.9736 | -4.883 | 0.5813 | 0.6371 | 0.9462 | 0.6936 | -130.9727 | -6.8732 | -0.2796 | -1.9426 | -9.5077 | -8.2235 | -0.8729 |  | -3.7027 | -3.9688 | 4 | 3.3696 | 3.3474 | 1.0186 | 10.6214 | 14.0831 | 14.7078 | 10.9865 | -0.0004 | -0.0033 | 0.0006 | 0.0039 | 0.0005 | 0 | 0.0073 | 0.0022 | -0.0153 | -360.1711 | 17.5137 | -360.5712 | 17.8976 | -360.9189 | 18.1666 | -360.9958 | 17.5445 | -352.8414 | 18.7703 | -352.8537 | 16.8258
11:42 | 1327 | 21.4351 | 194.8252 | 435.5449 | 441.4467 | -21.6893 | -47.2098 | 1.0775 | -0.3508 | -7.7846 | -7.6583 | -3.2846 | -4.2568 | 1.906 | -4.916 | 0.5814 | 0.6315 | 0.9445 | 0.6931 | -131.0495 | -6.9481 | -0.2857 | -2.1631 | -9.4861 | -8.2881 | -0.881 |  | -3.7237 | -4.0335 | 4.0001 | 3.3706 | 3.3522 | 1.0182 | 10.5996 | 14.0725 | 14.6781 | 10.9999 | -0.0006 | -0.0028 | 0.0005 | 0.0036 | 0.0007 | -0.001 | 0.0016 | 0.0027 | -0.0136 | -360.1958 | 17.5178 | -360.5527 | 17.836 | -360.8727 | 18.1522 | -360.9774 | 17.5342 | -352.8506 | 18.7661 | -352.8198 | 16.795
11:42 | 1328 | 21.3796 | 194.7962 | 435.5276 | 441.4025 | -21.6501 | -47.3172 | 1.0948 | -0.3468 | -7.7509 | -7.6057 | -3.2853 | -4.2396 | 1.8993 | -4.9126 | 0.5819 | 0.6349 | 0.9429 | 0.6922 | -131.0849 | -6.9714 | -0.3315 | -2.1759 | -9.511 | -8.2095 | -0.8769 |  | -3.653 | -3.9652 | 4.0005 | 3.3691 | 3.3528 | 1.0185 | 10.5788 | 14.0515 | 14.6614 | 10.9739 | -0.0003 | -0.0025 | 0.0002 | 0.0036 | 0.0003 | -0.0007 | -0.0009 | -0.0075 | -0.0167 | -360.2142 | 17.5506 | -360.6019 | 17.8709 | -360.9158 | 18.1584 | -360.9804 | 17.5486 | -352.8721 | 18.7949 | -352.8475 | 16.8135
11:42 | 1329 | 21.2983 | 194.7188 | 435.45 | 441.4042 | -21.6909 | -47.252 | 1.1103 | -0.36 | -7.7619 | -7.634 | -3.2808 | -4.2311 | 1.8634 | -4.8665 | 0.5814 | 0.6363 | 0.95 | 0.6934 | -131.0194 | -6.9079 | -0.2278 | -2.2092 | -9.5122 | -8.2908 | -0.8801 |  | -3.6547 | -4.0148 | 4.003 | 3.373 | 3.3516 | 1.0179 | 10.5984 | 14.0772 | 14.6778 | 10.9927 | 0.0001 | -0.0032 | 0.0011 | 0.0043 | 0.001 | -0.0005 | 0.0035 | 0.0036 | -0.0201 | -360.1219 | 17.5198 | -360.5773 | 17.8586 | -360.8697 | 18.1502 | -360.9343 | 17.5075 | -352.7829 | 18.7764 | -352.8537 | 16.8094
11:42 | 1330 | 21.4361 | 194.743 | 435.5012 | 441.3959 | -21.6526 | -47.2129 | 1.0877 | -0.2294 | -7.7398 | -7.6348 | -3.225 | -4.1463 | 1.9462 | -4.8911 | 0.5793 | 0.6334 | 0.9482 | 0.6911 | -130.9488 | -6.8297 | -0.1323 | -2.1263 | -9.5139 | -8.2029 | -0.7965 |  | -3.5914 | -3.9311 | 4.0023 | 3.3692 | 3.352 | 1.0177 | 10.6319 | 14.0819 | 14.689 | 11.0259 | -0.0002 | -0.0033 | 0.0003 | 0.003 | 0.0003 | -0.0007 | 0.007 | -0.0076 | -0.0115 | -360.1988 | 17.5137 | -360.5804 | 17.8894 | -360.9343 | 18.1748 | -360.9743 | 17.5445 | -352.8383 | 18.7785 | -352.8414 | 16.8279
11:42 | 1331 | 21.4536 | 194.7091 | 435.3943 | 441.3719 | -21.6977 | -47.4029 | 1.1091 | -0.3028 | -7.721 | -7.6905 | -3.248 | -4.2459 | 1.9592 | -4.9156 | 0.5823 | 0.6356 | 0.9468 | 0.6943 | -131.086 | -6.9484 | -0.238 | -2.1778 | -9.5306 | -8.2437 | -0.884 |  | -3.6752 | -3.9609 | 4.0034 | 3.3706 | 3.354 | 1.0195 | 10.6236 | 14.1031 | 14.7184 | 11.0283 | -0.0001 | -0.0028 | 0.0008 | 0.004 | 0.0006 | -0.0004 | -0.0077 | -0.0205 | -0.0293 | -360.1681 | 17.5055 | -360.5589 | 17.8504 | -360.882 | 18.1543 | -360.9558 | 17.5137 | -352.7829 | 18.7682 | -352.8229 | 16.7991
11:42 | 1332 | 21.4617 | 194.7213 | 435.5111 | 441.4419 | -21.7279 | -47.45 | 1.0604 | -0.3864 | -7.7196 | -7.6891 | -3.2763 | -4.2922 | 2.0324 | -4.9375 | 0.581 | 0.635 | 0.9423 | 0.6931 | -131.0714 | -6.9456 | -0.1821 | -2.0938 | -9.474 | -8.1557 | -0.7456 |  | -3.6645 | -3.9507 | 4.0034 | 3.3663 | 3.3536 | 1.0188 | 10.6433 | 14.1111 | 14.7085 | 11.0193 | -0.0005 | -0.0027 | 0.0007 | 0.0039 | 0.0008 | -0.0005 | 0.0164 | -0.0144 | -0.0096 | -360.2111 | 17.5424 | -360.5866 | 17.8709 | -360.9312 | 18.1625 | -360.9527 | 17.5424 | -352.8506 | 18.8011 | -352.8752 | 16.8074
11:42 | 1333 | 21.5352 | 194.7401 | 435.4085 | 441.4298 | -21.7343 | -47.3737 | 1.0753 | -0.4351 | -7.7567 | -7.6725 | -3.4037 | -4.3015 | 1.9927 | -4.946 | 0.5815 | 0.6348 | 0.9474 | 0.6934 | -131.0627 | -6.8458 | -0.1889 | -2.0858 | -9.4836 | -8.1434 | -0.734 |  | -3.6403 | -3.911 | 4.0041 | 3.3681 | 3.352 | 1.0191 | 10.6434 | 14.111 | 14.6959 | 11.0313 | -0.0002 | -0.0029 | 0.0005 | 0.0031 | 0 | -0.0006 | 0.0089 | 0.0095 | -0.0081 | -360.165 | 17.5321 | -360.5896 | 17.8627 | -360.8943 | 18.1543 | -360.9404 | 17.5096 | -352.789 | 18.7928 | -352.8567 | 16.8176
11:42 | 1334 | 21.548 | 194.7335 | 435.5381 | 441.4805 | -21.7243 | -47.3997 | 1.1352 | -0.4604 | -7.7818 | -7.7505 | -3.3363 | -4.2987 | 2.0121 | -4.9492 | 0.5803 | 0.6351 | 0.9439 | 0.6924 | -131.0289 | -6.8459 | -0.1932 | -2.0592 | -9.3166 | -8.1737 | -0.7315 |  | -3.6562 | -3.8963 | 4.0039 | 3.3703 | 3.3566 | 1.0191 | 10.6341 | 14.1076 | 14.6986 | 11.045 | -0.0001 | -0.0034 | 0.0007 | 0.0036 | 0.0013 | -0.0007 | 0.0098 | -0.0027 | -0.0096 | -360.165 | 17.5116 | -360.5558 | 17.8689 | -360.9127 | 18.1666 | -360.9558 | 17.5363 | -352.8321 | 18.7703 | -352.8352 | 16.8197
11:42 | 1335 | 21.4949 | 194.6373 | 435.4108 | 441.4279 | -21.6664 | -47.3329 | 1.1113 | -0.4725 | -7.8054 | -7.6528 | -3.302 | -4.3193 | 2.0814 | -4.8753 | 0.5805 | 0.6375 | 0.9464 | 0.6909 | -131.0556 | -6.7613 | -0.1996 | -1.9133 | -9.3559 | -8.1342 | -0.775 |  | -3.5901 | -3.8487 | 4.003 | 3.3716 | 3.3526 | 1.0182 | 10.6364 | 14.0867 | 14.6829 | 11.036 | -0.0001 | -0.0027 | 0.0007 | 0.0041 | 0.0004 | -0.0002 | 0.0108 | -0.0044 | -0.0098 | -360.1773 | 17.5198 | -360.5619 | 17.8422 | -360.8881 | 18.1645 | -360.9927 | 17.5486 | -352.829 | 18.7805 | -352.829 | 16.7991
11:42 | 1336 | 21.4526 | 194.6495 | 435.4463 | 441.3924 | -21.8013 | -47.3248 | 1.0288 | -0.4261 | -7.7202 | -7.6429 | -3.3381 | -4.1995 | 2.1124 | -4.8922 | 0.5812 | 0.6361 | 0.9445 | 0.6918 | -131.031 | -6.8698 | -0.1915 | -1.9628 | -9.3831 | -8.1062 | -0.7366 |  | -3.6619 | -3.9206 | 4.0035 | 3.3701 | 3.3549 | 1.0186 | 10.6147 | 14.0642 | 14.6801 | 11.0212 | -0.0007 | -0.0032 | 0.0001 | 0.0034 | 0.0008 | -0.0012 | -0.0042 | -0.0053 | 0.0026 | -360.205 | 17.5219 | -360.5466 | 17.8422 | -360.8789 | 18.1481 | -360.9681 | 17.5383 | -352.8383 | 18.7887 | -352.829 | 16.7909
11:42 | 1337 | 21.4548 | 194.5497 | 435.4016 | 441.4734 | -21.7392 | -47.3591 | 1.0828 | -0.3248 | -7.7409 | -7.6766 | -3.2686 | -4.2212 | 2.1567 | -4.864 | 0.5831 | 0.6379 | 0.9497 | 0.6936 | -131.1287 | -6.866 | -0.1441 | -1.9954 | -9.3699 | -8.0609 | -0.716 |  | -3.6272 | -3.9135 | 4.0045 | 3.3694 | 3.3537 | 1.0187 | 10.5994 | 14.0727 | 14.6918 | 10.976 | -0.0001 | -0.0029 | 0.0005 | 0.0038 | 0.0006 | -0.0002 | -0.0014 | -0.0085 | -0.0211 | -360.1404 | 17.5404 | -360.605 | 17.873 | -360.9251 | 18.1625 | -360.9681 | 17.5383 | -352.8321 | 18.7887 | -352.8875 | 16.8197
11:42 | 1338 | 21.6091 | 194.7226 | 435.5696 | 441.4845 | -21.703 | -47.4052 | 1.056 | -0.4315 | -7.7436 | -7.5841 | -3.3353 | -4.2345 | 2.2054 | -4.8332 | 0.5818 | 0.6369 | 0.9491 | 0.6929 | -131.1086 | -6.807 | -0.1873 | -2.0388 | -9.2985 | -8.1569 | -0.7368 |  | -3.6141 | -3.9865 | 4.0038 | 3.3694 | 3.3512 | 1.0186 | 10.6261 | 14.0587 | 14.6938 | 11.0031 | 0 | -0.0035 | 0.0003 | 0.0036 | 0.0008 | -0.0008 | 0.0187 | -0.0102 | 0.0035 | -360.1281 | 17.4993 | -360.5404 | 17.8504 | -360.9004 | 18.1522 | -360.9312 | 17.5157 | -352.7767 | 18.7641 | -352.8229 | 16.8115
11:42 | 1339 | 21.5742 | 194.6306 | 435.5357 | 441.4403 | -21.6939 | -47.3892 | 1.1079 | -0.4105 | -7.7143 | -7.5277 | -3.3348 | -4.2111 | 2.1878 | -4.8569 | 0.5821 | 0.637 | 0.9488 | 0.6944 | -131.0631 | -6.8267 | -0.254 | -1.8878 | -9.2208 | -8.1337 | -0.7717 |  | -3.5763 | -4.0299 | 4.0037 | 3.3652 | 3.3514 | 1.02 | 10.596 | 14.0692 | 14.6761 | 10.9901 | 0 | -0.0031 | 0.0006 | 0.0037 | 0.0008 | -0.0005 | 0.0181 | 0 | 0.0062 | -360.2081 | 17.528 | -360.5773 | 17.8771 | -360.9281 | 18.1707 | -360.9712 | 17.5445 | -352.8414 | 18.7867 | -352.8783 | 16.8279
11:42 | 1340 | 21.5403 | 194.6076 | 435.5573 | 441.4503 | -21.7016 | -47.4039 | 1.0859 | -0.3447 | -7.6246 | -7.626 | -3.2955 | -4.2124 | 2.1167 | -4.7776 | 0.582 | 0.6332 | 0.9491 | 0.6921 | -131.0513 | -6.8292 | -0.2725 | -1.8577 | -9.1792 | -8.0362 | -0.7765 |  | -3.5613 | -3.9963 | 4.0034 | 3.371 | 3.3518 | 1.0205 | 10.6456 | 14.1136 | 14.7123 | 11.0211 | -0.0002 | -0.0026 | 0.0007 | 0.0037 | 0.0005 | -0.0006 | 0.0092 | -0.0083 | 0.012 | -360.1835 | 17.5178 | -360.5558 | 17.834 | -360.8543 | 18.142 | -360.9466 | 17.5321 | -352.8167 | 18.7723 | -352.8229 | 16.7971
11:42 | 1341 | 21.5371 | 194.5912 | 435.4605 | 441.3881 | -21.8137 | -47.4602 | 1.1286 | -0.3122 | -7.5987 | -7.549 | -3.2753 | -4.2478 | 1.9885 | -4.7706 | 0.5814 | 0.6321 | 0.9477 | 0.6928 | -131.0643 | -6.8812 | -0.1621 | -1.8414 | -9.198 | -8.0223 | -0.6661 |  | -3.557 | -4.0124 | 4.0042 | 3.3696 | 3.3496 | 1.0195 | 10.6376 | 14.0936 | 14.719 | 11.0255 | -0.0002 | -0.0027 | 0.0009 | 0.0038 | 0.0006 | -0.0006 | 0.0045 | -0.0115 | -0.0144 | -360.2265 | 17.5568 | -360.5989 | 17.8586 | -360.9004 | 18.1563 | -360.9527 | 17.5486 | -352.8937 | 18.8052 | -352.8937 | 16.8115
11:42 | 1342 | 21.5074 | 194.5906 | 435.5046 | 441.396 | -21.7149 | -47.4479 | 1.1589 | -0.3329 | -7.5148 | -7.5273 | -3.2714 | -4.1817 | 2.071 | -4.7597 | 0.5817 | 0.6326 | 0.947 | 0.6928 | -130.999 | -6.7886 | -0.1156 | -1.9217 | -9.2008 | -8.0565 | -0.6128 |  | -3.5141 | -3.956 | 4.003 | 3.3691 | 3.35 | 1.0181 | 10.6363 | 14.116 | 14.7382 | 11.0406 | 0.0003 | -0.0026 | 0.0012 | 0.0039 | 0.0009 | -0.0002 | 0.0041 | -0.0081 | 0.004 | -360.2111 | 17.5157 | -360.5804 | 17.8525 | -360.9097 | 18.1399 | -360.9189 | 17.5321 | -352.8229 | 18.7744 | -352.829 | 16.8135
11:42 | 1343 | 21.403 | 194.6155 | 435.443 | 441.31 | -21.5877 | -47.3156 | 1.0956 | -0.3422 | -7.4985 | -7.565 | -3.2717 | -4.284 | 2.0336 | -4.8019 | 0.5825 | 0.6344 | 0.95 | 0.6925 | -131.0112 | -6.7811 | -0.1365 | -1.897 | -9.1641 | -7.9401 | -0.5966 |  | -3.6006 | -3.966 | 4.0041 | 3.3701 | 3.3549 | 1.0202 | 10.6261 | 14.1109 | 14.7122 | 11.0548 | -0.0002 | -0.0034 | 0.0006 | 0.0037 | 0.0008 | -0.0007 | -0.0019 | -0.0137 | -0.0215 | -360.1711 | 17.526 | -360.5958 | 17.8709 | -360.9312 | 18.1769 | -361.002 | 17.528 | -352.829 | 18.7867 | -352.8875 | 16.8176
11:42 | 1344 | 21.4747 | 194.6196 | 435.5058 | 441.3358 | -21.5721 | -47.2362 | 1.28 | -0.2586 | -7.5345 | -7.5647 | -3.293 | -4.2305 | 2.0826 | -4.7271 | 0.5825 | 0.6301 | 0.9456 | 0.6913 | -130.9716 | -6.7422 | -0.1127 | -2.062 | -9.1102 | -7.9734 | -0.6513 |  | -3.5415 | -3.8586 | 4.0029 | 3.3669 | 3.3505 | 1.0202 | 10.6169 | 14.09 | 14.7255 | 11.0284 | -0.0004 | -0.003 | 0.0007 | 0.0039 | 0.0004 | -0.0003 | 0.0035 | -0.0138 | -0.0208 | -360.1773 | 17.4972 | -360.5219 | 17.8442 | -360.9127 | 18.1748 | -360.9958 | 17.5465 | -352.829 | 18.7456 | -352.7767 | 16.7848
11:42 | 1345 | 21.5509 | 194.6624 | 435.548 | 441.4074 | -21.5897 | -47.2754 | 1.2467 | -0.329 | -7.6139 | -7.5129 | -3.3381 | -4.3193 | 2.0737 | -4.8489 | 0.5812 | 0.6334 | 0.9472 | 0.6918 | -130.9326 | -6.786 | -0.0338 | -2.0243 | -9.0714 | -7.9296 | -0.5997 |  | -3.572 | -3.9179 | 4.004 | 3.3665 | 3.3503 | 1.0196 | 10.6144 | 14.0994 | 14.6901 | 11.0139 | -0.0002 | -0.0025 | 0.001 | 0.004 | 0.0009 | -0.0012 | 0.0057 | -0.0052 | -0.016 | -360.1896 | 17.5239 | -360.5589 | 17.8525 | -360.882 | 18.1543 | -360.9927 | 17.5568 | -352.8506 | 18.7846 | -352.8752 | 16.7909
11:42 | 1346 | 21.5202 | 194.6464 | 435.5607 | 441.4123 | -21.6462 | -47.2402 | 1.2959 | -0.2926 | -7.5936 | -7.5704 | -3.2947 | -4.277 | 2.0672 | -4.7788 | 0.5804 | 0.6336 | 0.9471 | 0.6916 | -131.0019 | -6.7219 | -0.1416 | -2.017 | -9.1713 | -7.9665 | -0.6583 |  | -3.5451 | -3.9309 | 4.0035 | 3.3662 | 3.3497 | 1.0192 | 10.624 | 14.085 | 14.66 | 11.0248 | -0.0003 | -0.0029 | 0.0005 | 0.0034 | 0.0005 | -0.0004 | 0.0067 | -0.0071 | -0.0115 | -360.205 | 17.5363 | -360.6143 | 17.8689 | -360.9527 | 18.1522 | -360.9035 | 17.5178 | -352.826 | 18.7908 | -352.8629 | 16.8176
11:42 | 1347 | 21.4747 | 194.6428 | 435.5008 | 441.4155 | -21.6176 | -47.3196 | 1.1999 | -0.2869 | -7.5696 | -7.7121 | -3.3241 | -4.2852 | 2.129 | -4.6733 | 0.5827 | 0.6351 | 0.9473 | 0.6933 | -130.9742 | -6.7518 | -0.092 | -1.9644 | -9.1883 | -7.9776 | -0.6558 |  | -3.5423 | -3.94 | 4.0021 | 3.3648 | 3.353 | 1.0188 | 10.6225 | 14.0902 | 14.6928 | 11.0103 | 0.0004 | -0.0025 | 0.0009 | 0.004 | 0.0008 | -0.0007 | 0.005 | -0.0102 | -0.0069 | -360.1188 | 17.5178 | -360.6081 | 17.873 | -360.9527 | 18.1645 | -360.9558 | 17.5055 | -352.786 | 18.7682 | -352.8506 | 16.8156
11:42 | 1348 | 21.5461 | 194.6449 | 435.4449 | 441.4093 | -21.7073 | -47.3537 | 1.2054 | -0.2631 | -7.5857 | -7.7034 | -3.4186 | -4.3045 | 2.1584 | -4.7803 | 0.5822 | 0.6333 | 0.9457 | 0.6925 | -130.9875 | -6.7465 | -0.0596 | -1.861 | -9.175 | -7.9331 | -0.641 |  | -3.6608 | -3.9752 | 4.0037 | 3.3662 | 3.3553 | 1.0199 | 10.6319 | 14.076 | 14.6706 | 11.032 | 0 | -0.0031 | 0.0006 | 0.0039 | 0.0004 | -0.0006 | 0.0046 | -0.0166 | 0.0021 | -360.1988 | 17.5157 | -360.5743 | 17.8525 | -360.9004 | 18.1789 | -360.9927 | 17.5527 | -352.8414 | 18.7682 | -352.8475 | 16.793
11:42 | 1349 | 21.4279 | 194.7835 | 435.5292 | 441.3998 | -21.6749 | -47.3474 | 1.168 | -0.3473 | -7.616 | -7.6696 | -3.4602 | -4.3068 | 2.1446 | -4.789 | 0.5812 | 0.6291 | 0.9473 | 0.6925 | -131.0406 | -6.754 | -0.0815 | -1.8281 | -9.1528 | -7.8858 | -0.5877 |  | -3.6523 | -3.9232 | 4.0029 | 3.366 | 3.3514 | 1.0195 | 10.6375 | 14.1343 | 14.7433 | 11.0713 | -0.0002 | -0.0023 | 0.0008 | 0.0038 | 0.0005 | -0.0004 | 0.0076 | -0.0102 | -0.0075 | -360.245 | 17.5198 | -360.5435 | 17.8237 | -360.8604 | 18.1296 | -360.962 | 17.5547 | -352.8721 | 18.7764 | -352.8383 | 16.7683
11:42 | 1350 | 21.4434 | 194.7574 | 435.6005 | 441.3573 | -21.6798 | -47.3523 | 1.1186 | -0.3223 | -7.5835 | -7.4873 | -3.4506 | -4.2485 | 2.1383 | -4.8011 | 0.5826 | 0.6349 | 0.9496 | 0.693 | -131.0238 | -6.7662 | -0.0432 | -1.7936 | -9.1232 | -7.8739 | -0.6294 |  | -3.6365 | -4.013 | 4.0033 | 3.3656 | 3.3514 | 1.0197 | 10.6018 | 14.1039 | 14.705 | 11.0248 | -0.0004 | -0.0026 | 0.001 | 0.004 | 0.0008 | -0.001 | 0.0159 | -0.0193 | 0.0036 | -360.2604 | 17.5527 | -360.5989 | 17.8627 | -360.9189 | 18.1604 | -360.9774 | 17.5424 | -352.8475 | 18.8052 | -352.8414 | 16.7909
11:42 | 1351 | 21.5234 | 194.7744 | 435.5128 | 441.3546 | -21.6584 | -47.2962 | 1.261 | -0.3651 | -7.7139 | -7.7192 | -3.3892 | -4.3134 | 2.1377 | -4.8206 | 0.5849 | 0.6359 | 0.9479 | 0.6924 | -131.0558 | -6.7131 | -0.0913 | -1.8381 | -9.0658 | -7.9214 | -0.5416 |  | -3.6027 | -3.9284 | 4.0034 | 3.3666 | 3.354 | 1.0194 | 10.6203 | 14.0993 | 14.6659 | 11.0028 | -0.0005 | -0.0032 | 0.001 | 0.0037 | 0.0007 | 0 | 0.0074 | -0.0171 | -0.0056 | -360.1281 | 17.5034 | -360.5866 | 17.8648 | -360.9281 | 18.1584 | -360.9374 | 17.4993 | -352.7829 | 18.7641 | -352.8414 | 16.8032
11:42 | 1352 | 21.521 | 194.7448 | 435.636 | 441.3662 | -21.7467 | -47.2697 | 1.2894 | -0.2492 | -7.6169 | -7.5967 | -3.3225 | -4.3979 | 2.1326 | -4.8063 | 0.5823 | 0.6331 | 0.9467 | 0.6923 | -131.0687 | -6.623 | -0.0073 | -1.9284 | -9.0981 | -7.9205 | -0.6546 |  | -3.5099 | -3.9365 | 4.0024 | 3.3667 | 3.3522 | 1.0192 | 10.6364 | 14.0809 | 14.6945 | 11.0071 | 0 | -0.003 | 0.0006 | 0.0036 | 0.001 | -0.0009 | -0.0008 | -0.015 | -0.0209 | -360.1742 | 17.4972 | -360.5558 | 17.8566 | -360.9127 | 18.1974 | -361.0328 | 17.5486 | -352.8229 | 18.7497 | -352.8414 | 16.8074
11:42 | 1353 | 21.5581 | 194.6503 | 435.5855 | 441.3009 | -21.732 | -47.377 | 1.2903 | -0.2571 | -7.6631 | -7.5943 | -3.3442 | -4.3927 | 2.1789 | -4.8316 | 0.5819 | 0.6354 | 0.9482 | 0.6923 | -131.0683 | -6.7652 | -0.0227 | -2.0319 | -9.1772 | -8.0108 | -0.6831 |  | -3.5365 | -3.9304 | 4.0037 | 3.3665 | 3.3487 | 1.0216 | 10.5962 | 14.0571 | 14.6835 | 10.9801 | -0.0003 | -0.0031 | 0.0003 | 0.0035 | -0.0001 | -0.0009 | 0.0011 | -0.0205 | -0.0119 | -360.2081 | 17.5075 | -360.5496 | 17.8525 | -360.8974 | 18.1461 | -360.9681 | 17.5445 | -352.8167 | 18.762 | -352.8075 | 16.7786
11:42 | 1354 | 21.5782 | 194.73 | 435.6165 | 441.335 | -21.6952 | -47.295 | 1.2886 | -0.2318 | -7.6406 | -7.5957 | -3.3368 | -4.3255 | 2.1909 | -4.8124 | 0.5821 | 0.6341 | 0.9467 | 0.6926 | -131.0328 | -6.6577 | -0.0591 | -1.8743 | -9.158 | -7.8894 | -0.5688 |  | -3.4463 | -3.8403 | 4.0035 | 3.3689 | 3.3507 | 1.0201 | 10.6099 | 14.0483 | 14.6546 | 10.9869 | -0.0004 | -0.0026 | 0.0007 | 0.0038 | 0.0007 | -0.0007 | -0.0052 | 0.0011 | -0.0198 | -360.165 | 17.5527 | -360.6327 | 17.8668 | -360.9251 | 18.1379 | -360.9374 | 17.5239 | -352.8567 | 18.8113 | -352.9121 | 16.8115
11:42 | 1355 | 21.5694 | 194.693 | 435.5853 | 441.256 | -21.531 | -47.2473 | 1.3621 | -0.1941 | -7.6006 | -7.5496 | -3.2435 | -4.3268 | 2.0896 | -4.7925 | 0.5817 | 0.6319 | 0.9483 | 0.6909 | -131.0765 | -6.6478 | -0.1259 | -1.8252 | -9.1218 | -7.8353 | -0.5556 |  | -3.4539 | -3.8911 | 4.0034 | 3.369 | 3.3518 | 1.0193 | 10.6066 | 14.0909 | 14.6553 | 10.9783 | -0.0001 | -0.0031 | 0.0001 | 0.0032 | -0.0001 | -0.0008 | 0.0193 | -0.0103 | 0.001 | -360.1773 | 17.526 | -360.6266 | 17.873 | -360.9189 | 18.1543 | -360.9343 | 17.5137 | -352.7952 | 18.7805 | -352.8629 | 16.8115
11:42 | 1356 | 21.5641 | 194.8327 | 435.606 | 441.2278 | -21.5795 | -47.2861 | 1.3708 | -0.2544 | -7.6962 | -7.5346 | -3.2891 | -4.3281 | 2.0314 | -4.8684 | 0.5828 | 0.6341 | 0.9479 | 0.6911 | -131.0425 | -6.6199 | -0.0823 | -1.829 | -9.2567 | -7.9089 | -0.648 |  | -3.4018 | -3.8213 | 4.0022 | 3.367 | 3.3519 | 1.0207 | 10.64 | 14.0957 | 14.6676 | 11.0226 | 0.0003 | -0.0031 | 0.0009 | 0.0039 | 0.0004 | -0.0008 | -0.0009 | -0.0079 | -0.0081 | -360.1958 | 17.5013 | -360.5496 | 17.8566 | -360.8974 | 18.1687 | -360.9743 | 17.5404 | -352.8414 | 18.7641 | -352.8198 | 16.7991
11:42 | 1357 | 21.5087 | 194.8481 | 435.6226 | 441.2617 | -21.6571 | -47.2197 | 1.3938 | -0.2944 | -7.6307 | -7.549 | -3.2256 | -4.1982 | 2.224 | -4.7532 | 0.5822 | 0.6387 | 0.9508 | 0.6926 | -131.0296 | -6.6042 | -0.0346 | -1.8832 | -9.2482 | -7.9105 | -0.6093 |  | -3.5275 | -3.871 | 4.0033 | 3.3671 | 3.3524 | 1.0214 | 10.6512 | 14.137 | 14.6797 | 11.055 | 0.0001 | -0.0027 | 0.001 | 0.004 | 0.0011 | -0.0002 | -0.0023 | -0.0016 | -0.0228 | -360.2542 | 17.526 | -360.5466 | 17.8319 | -360.8727 | 18.1604 | -360.9835 | 17.5629 | -352.8814 | 18.7846 | -352.829 | 16.7704
11:42 | 1358 | 21.4878 | 194.7576 | 435.6976 | 441.2153 | -21.6433 | -47.2447 | 1.3081 | -0.2875 | -7.6264 | -7.6099 | -3.3424 | -4.2921 | 2.184 | -4.7883 | 0.5832 | 0.6388 | 0.9513 | 0.6916 | -131.0926 | -6.6092 | -0.0847 | -1.9906 | -9.2186 | -7.8817 | -0.6191 |  | -3.4216 | -3.8284 | 4.0032 | 3.3674 | 3.3538 | 1.02 | 10.6307 | 14.1212 | 14.6819 | 11.0306 | -0.0007 | -0.003 | 0.0005 | 0.0037 | 0.0006 | -0.0005 | -0.0022 | 0.0033 | -0.0206 | -360.1835 | 17.526 | -360.565 | 17.836 | -360.8881 | 18.142 | -360.9527 | 17.5301 | -352.8198 | 18.7826 | -352.829 | 16.7827
11:42 | 1359 | 21.5256 | 194.7993 | 435.6861 | 441.1181 | -21.6085 | -47.3232 | 1.3461 | -0.2502 | -7.5712 | -7.559 | -3.3215 | -4.2058 | 2.2259 | -4.6886 | 0.5811 | 0.6346 | 0.9517 | 0.6908 | -131.1114 | -6.6086 | -0.0457 | -1.914 | -9.3246 | -7.9892 | -0.6448 |  | -3.3978 | -3.7867 | 4.0019 | 3.3707 | 3.3536 | 1.0205 | 10.6294 | 14.1147 | 14.7242 | 11.0226 | -0.0002 | -0.0028 | 0.0008 | 0.0038 | 0.0009 | -0.0006 | 0.0102 | -0.0009 | 0.003 | -360.1742 | 17.5137 | -360.6081 | 17.8791 | -360.9527 | 18.1625 | -361.0051 | 17.528 | -352.7798 | 18.7846 | -352.8783 | 16.8197
11:42 | 1360 | 21.5934 | 194.6799 | 435.6413 | 441.1753 | -21.6012 | -47.1989 | 1.4573 | -0.2847 | -7.5504 | -7.5746 | -3.319 | -4.184 | 2.2193 | -4.7716 | 0.5811 | 0.6329 | 0.9471 | 0.6904 | -131.0691 | -6.6383 | 0.0454 | -1.8731 | -9.3863 | -8.0199 | -0.6858 |  | -3.4123 | -3.8483 | 4.0035 | 3.3702 | 3.3524 | 1.0199 | 10.6134 | 14.075 | 14.705 | 10.9901 | -0.0004 | -0.0036 | 0.0004 | 0.0034 | 0.0003 | -0.0003 | 0.0203 | 0.001 | 0.0061 | -360.1711 | 17.5075 | -360.5373 | 17.8525 | -360.9312 | 18.1502 | -360.9435 | 17.5157 | -352.8167 | 18.762 | -352.8229 | 16.7868
11:42 | 1361 | 21.5871 | 194.7255 | 435.6957 | 441.1326 | -21.5137 | -47.1805 | 1.5247 | -0.3315 | -7.5945 | -7.5624 | -3.4105 | -4.2327 | 2.1849 | -4.7257 | 0.5818 | 0.6356 | 0.9493 | 0.6926 | -131.0435 | -6.7067 | 0.0549 | -1.7342 | -9.2338 | -7.8591 | -0.6741 |  | -3.4094 | -3.7839 | 4.0041 | 3.3657 | 3.3545 | 1.021 | 10.6089 | 14.0642 | 14.6685 | 10.975 | -0.0004 | -0.0033 | 0.0007 | 0.0034 | 0.0008 | -0.0009 | 0.0139 | -0.0144 | -0.0165 | -360.2019 | 17.5342 | -360.5681 | 17.8422 | -360.9004 | 18.1543 | -360.9989 | 17.5527 | -352.8691 | 18.7887 | -352.8629 | 16.7909
11:42 | 1362 | 21.6608 | 194.8042 | 435.609 | 441.0172 | -21.5167 | -47.1187 | 1.5003 | -0.2902 | -7.49 | -7.4743 | -3.2977 | -4.2553 | 2.1598 | -4.8121 | 0.5817 | 0.6357 | 0.9493 | 0.6918 | -131.0516 | -6.6447 | 0.0356 | -1.7476 | -9.185 | -7.9932 | -0.7171 |  | -3.3932 | -3.7718 | 4.0044 | 3.3672 | 3.354 | 1.0198 | 10.5913 | 14.0879 | 14.6496 | 10.9908 | -0.0002 | -0.0028 | 0.0011 | 0.004 | 0.0006 | -0.0005 | 0.0101 | -0.0197 | -0.0094 | -360.1742 | 17.5301 | -360.5989 | 17.8525 | -360.8881 | 18.1399 | -360.9374 | 17.528 | -352.8044 | 18.7744 | -352.8567 | 16.7848
11:42 | 1363 | 21.6832 | 194.8144 | 435.7264 | 441.0472 | -21.606 | -47.2002 | 1.4657 | -0.3166 | -7.4882 | -7.6221 | -3.338 | -4.2685 | 2.1632 | -4.726 | 0.5806 | 0.6336 | 0.9485 | 0.6927 | -131.0242 | -6.6725 | -0.046 | -1.9817 | -9.2386 | -7.9471 | -0.7576 |  | -3.405 | -3.7551 | 4.0041 | 3.3654 | 3.3527 | 1.021 | 10.6134 | 14.0864 | 14.6808 | 11.0136 | -0.0006 | -0.0026 | 0.0004 | 0.0039 | 0.0007 | -0.0008 | 0.0084 | -0.0098 | -0.0011 | -360.1773 | 17.5157 | -360.5743 | 17.8627 | -360.9158 | 18.1543 | -360.9835 | 17.5506 | -352.8414 | 18.7785 | -352.8506 | 16.8074
11:42 | 1364 | 21.7065 | 194.8341 | 435.7638 | 441.0052 | -21.583 | -47.228 | 1.3581 | -0.3609 | -7.5011 | -7.8042 | -3.3523 | -4.3144 | 2.1334 | -4.7627 | 0.5819 | 0.634 | 0.9536 | 0.6938 | -131.0539 | -6.5404 | -0.0652 | -1.9052 | -9.188 | -7.933 | -0.7043 |  | -3.4087 | -3.7434 | 4.0036 | 3.3655 | 3.3527 | 1.0202 | 10.6157 | 14.0831 | 14.6846 | 11.0269 | 0.0001 | -0.0031 | 0.0004 | 0.0042 | 0.0002 | -0.0006 | 0.0186 | -0.014 | 0.0018 | -360.165 | 17.5178 | -360.5773 | 17.8442 | -360.885 | 18.1563 | -360.9497 | 17.5321 | -352.8167 | 18.7703 | -352.8198 | 16.7848
11:42 | 1365 | 21.791 | 194.8591 | 435.7797 | 440.9963 | -21.608 | -47.2671 | 1.3571 | -0.287 | -7.4327 | -7.6664 | -3.2878 | -4.2536 | 2.192 | -4.7919 | 0.5815 | 0.6348 | 0.9487 | 0.6915 | -131.0228 | -6.4282 | -0.0023 | -1.9025 | -9.2653 | -7.9304 | -0.7133 |  | -3.3937 | -3.7323 | 4.0018 | 3.3687 | 3.352 | 1.0213 | 10.6305 | 14.1043 | 14.7024 | 11.0352 | 0.0002 | -0.003 | 0.0009 | 0.0035 | 0.0005 | -0.0005 | 0.0165 | -0.0177 | 0.0011 | -360.2081 | 17.5239 | -360.5589 | 17.8401 | -360.9004 | 18.1502 | -360.9712 | 17.5383 | -352.8506 | 18.7908 | -352.829 | 16.7889
11:42 | 1366 | 21.7139 | 194.7564 | 435.8578 | 440.8477 | -21.6739 | -47.3258 | 1.2289 | -0.3744 | -7.4691 | -7.582 | -3.2604 | -4.2696 | 2.1616 | -4.7434 | 0.5819 | 0.6333 | 0.9508 | 0.6928 | -130.9687 | -6.4627 | 0.0274 | -1.8169 | -9.2328 | -7.8826 | -0.7579 |  | -3.396 | -3.7518 | 4.003 | 3.3723 | 3.3512 | 1.0205 | 10.6618 | 14.1239 | 14.6752 | 11.0146 | -0.0002 | -0.0028 | 0.0005 | 0.0033 | 0.0006 | -0.0003 | 0.0007 | -0.0068 | -0.0068 | -360.1681 | 17.5219 | -360.5989 | 17.8442 | -360.8727 | 18.1522 | -360.9435 | 17.5363 | -352.7921 | 18.7723 | -352.8598 | 16.7971
11:42 | 1367 | 21.7071 | 194.7502 | 435.7275 | 440.7338 | -21.7284 | -47.4734 | 1.1965 | -0.2934 | -7.5112 | -7.5742 | -3.2149 | -4.209 | 2.2113 | -4.7217 | 0.5824 | 0.6337 | 0.9521 | 0.6945 | -130.9435 | -6.523 | -0.0251 | -1.7625 | -9.2234 | -7.9271 | -0.7152 |  | -3.3177 | -3.7916 | 4.0036 | 3.3685 | 3.3508 | 1.0205 | 10.6328 | 14.1126 | 14.683 | 11.0139 | -0.0002 | -0.0026 | 0.0007 | 0.0037 | 0.0006 | -0.0005 | 0.0029 | -0.0011 | -0.014 | -360.1865 | 17.5055 | -360.5743 | 17.8627 | -360.9127 | 18.1584 | -360.9681 | 17.5219 | -352.8075 | 18.7661 | -352.8567 | 16.8074
11:43 | 1368 | 21.6616 | 194.7821 | 435.7819 | 440.7288 | -21.7369 | -47.4156 | 1.2264 | -0.2986 | -7.4631 | -7.6927 | -3.2404 | -4.2347 | 2.161 | -4.7982 | 0.5819 | 0.6334 | 0.9531 | 0.6941 | -131.0247 | -6.5947 | -0.0632 | -1.739 | -9.2079 | -7.8741 | -0.6952 |  | -3.3687 | -3.7708 | 4.0029 | 3.3703 | 3.3549 | 1.0207 | 10.6422 | 14.0925 | 14.6945 | 11.0244 | -0.0001 | -0.0026 | 0.0004 | 0.0031 | 0.0006 | -0.001 | 0.013 | -0.0094 | 0.0126 | -360.2081 | 17.5178 | -360.565 | 17.8689 | -360.9312 | 18.1687 | -360.962 | 17.5239 | -352.8106 | 18.7744 | -352.8014 | 16.7971
11:43 | 1369 | 21.6785 | 194.8027 | 435.8661 | 440.7003 | -21.7022 | -47.4119 | 1.284 | -0.2773 | -7.4981 | -7.6233 | -3.2198 | -4.1685 | 2.2123 | -4.6845 | 0.5811 | 0.6353 | 0.9508 | 0.6941 | -131.1061 | -6.4397 | -0.0359 | -1.7552 | -9.2393 | -7.8856 | -0.6514 |  | -3.3658 | -3.8442 | 4.0032 | 3.3696 | 3.3517 | 1.0206 | 10.5996 | 14.084 | 14.6665 | 10.9826 | -0.0001 | -0.0034 | 0.0008 | 0.0034 | 0.0003 | -0.0005 | -0.0042 | -0.0111 | -0.0362 | -360.1588 | 17.5055 | -360.5435 | 17.8525 | -360.9035 | 18.1461 | -360.9527 | 17.5486 | -352.829 | 18.7579 | -352.8229 | 16.793
11:43 | 1370 | 21.6103 | 194.7687 | 435.7229 | 440.6609 | -21.626 | -47.3157 | 1.3254 | -0.1995 | -7.5423 | -7.6824 | -3.2108 | -4.1775 | 2.1447 | -4.6801 | 0.5827 | 0.6351 | 0.9499 | 0.6944 | -131.1592 | -6.4888 | 0.0167 | -1.9175 | -9.2208 | -7.7479 | -0.6368 |  | -3.3393 | -3.7558 | 4.0033 | 3.3693 | 3.3502 | 1.0206 | 10.595 | 14.0735 | 14.6437 | 10.9783 | 0 | -0.003 | 0.0011 | 0.0038 | 0.0009 | -0.001 | 0.015 | 0.0002 | 0.0076 | -360.2142 | 17.5486 | -360.605 | 17.8525 | -360.8789 | 18.1379 | -360.962 | 17.5424 | -352.8475 | 18.8031 | -352.8567 | 16.7786
11:43 | 1371 | 21.6181 | 194.725 | 435.7655 | 440.6114 | -21.5827 | -47.3212 | 1.3318 | -0.2965 | -7.4938 | -7.5405 | -3.2808 | -4.1149 | 2.2716 | -4.7592 | 0.583 | 0.6332 | 0.9486 | 0.6935 | -131.0784 | -6.5765 | 0.0518 | -1.7985 | -9.1343 | -7.7832 | -0.7026 |  | -3.3957 | -3.8844 | 4.0027 | 3.3709 | 3.3534 | 1.0216 | 10.6041 | 14.083 | 14.6662 | 10.9927 | 0.0001 | -0.0025 | 0.0006 | 0.0036 | 0.0006 | -0.0003 | -0.0089 | -0.0091 | -0.0147 | -360.1927 | 17.5363 | -360.5989 | 17.8668 | -360.885 | 18.1379 | -360.9343 | 17.528 | -352.8475 | 18.7887 | -352.8752 | 16.8156
11:43 | 1372 | 21.6813 | 194.7805 | 435.7171 | 440.5151 | -21.6997 | -47.3755 | 1.2698 | -0.2488 | -7.3383 | -7.5372 | -3.2253 | -4.0487 | 2.2864 | -4.6809 | 0.5828 | 0.6327 | 0.9496 | 0.6925 | -131.1468 | -6.5832 | -0.0477 | -1.6192 | -9.153 | -7.8421 | -0.6763 |  | -3.3366 | -3.8343 | 4.0029 | 3.3708 | 3.3558 | 1.0205 | 10.6215 | 14.0888 | 14.6778 | 10.9984 | -0.0003 | -0.0029 | 0.0008 | 0.0044 | 0.0009 | -0.0008 | 0.0057 | -0.0193 | -0.0062 | -360.1219 | 17.5137 | -360.5681 | 17.873 | -360.9251 | 18.1625 | -360.9712 | 17.526 | -352.789 | 18.7641 | -352.8475 | 16.8094
11:43 | 1373 | 21.6744 | 194.8107 | 435.787 | 440.5117 | -21.5842 | -47.4415 | 1.2776 | -0.2619 | -7.4456 | -7.6076 | -3.2114 | -4.0888 | 2.1973 | -4.7634 | 0.581 | 0.635 | 0.9495 | 0.6936 | -131.1171 | -6.5792 | -0.0019 | -1.6389 | -9.0844 | -7.8518 | -0.6178 |  | -3.3517 | -3.8368 | 4.004 | 3.3701 | 3.356 | 1.0199 | 10.6456 | 14.1019 | 14.7113 | 10.9984 | 0.0001 | -0.0028 | 0.0009 | 0.0036 | 0.0009 | -0.0004 | 0.0138 | -0.0104 | 0.0082 | -360.1773 | 17.5075 | -360.5312 | 17.8442 | -360.8881 | 18.1851 | -361.0204 | 17.5588 | -352.8537 | 18.76 | -352.8137 | 16.7868
11:43 | 1374 | 21.7057 | 194.8375 | 435.743 | 440.5246 | -21.6087 | -47.3462 | 1.3086 | -0.199 | -7.407 | -7.5694 | -3.1975 | -4.1936 | 2.1727 | -4.6358 | 0.5827 | 0.6344 | 0.9514 | 0.6933 | -131.0179 | -6.5376 | 0.0283 | -1.6552 | -9.148 | -7.8054 | -0.5238 |  | -3.4145 | -3.8518 | 4.0025 | 3.3692 | 3.3514 | 1.021 | 10.5924 | 14.1007 | 14.7157 | 11.0262 | 0 | -0.0031 | 0.0006 | 0.0036 | 0.0011 | 0 | 0.0156 | -0.0011 | -0.0019 | -360.2173 | 17.5178 | -360.5558 | 17.8401 | -360.8727 | 18.1645 | -360.9743 | 17.5486 | -352.8444 | 18.7723 | -352.8106 | 16.7766
11:43 | 1375 | 21.7002 | 194.8118 | 435.8884 | 440.5726 | -21.6638 | -47.3012 | 1.2695 | -0.1876 | -7.5175 | -7.4972 | -3.2503 | -4.1902 | 2.22 | -4.6842 | 0.5828 | 0.6346 | 0.9519 | 0.694 | -131.1184 | -6.5962 | -0.0102 | -1.6173 | -9.1079 | -7.8944 | -0.5277 |  | -3.4581 | -3.8258 | 4.0046 | 3.3708 | 3.3524 | 1.0217 | 10.6144 | 14.0879 | 14.6959 | 11.0024 | -0.0005 | -0.0028 | 0.0006 | 0.0034 | 0.0007 | -0.0007 | 0.0161 | -0.0062 | 0.0023 | -360.1742 | 17.5342 | -360.6081 | 17.8874 | -360.922 | 18.144 | -360.9404 | 17.5363 | -352.826 | 18.7846 | -352.8967 | 16.8176
11:43 | 1376 | 21.7108 | 194.7853 | 435.8573 | 440.4438 | -21.6216 | -47.2042 | 1.3707 | -0.2453 | -7.4884 | -7.3993 | -3.2267 | -4.1596 | 2.2541 | -4.6049 | 0.5836 | 0.6368 | 0.951 | 0.6928 | -131.0508 | -6.5392 | 0.0176 | -1.6813 | -9.0917 | -7.8557 | -0.5367 |  | -3.2991 | -3.7363 | 4.0029 | 3.3659 | 3.3502 | 1.0204 | 10.6249 | 14.1039 | 14.6935 | 11.0248 | -0.0005 | -0.0026 | 0.0009 | 0.0036 | 0.0002 | -0.0006 | -0.0031 | -0.0055 | -0.0167 | -360.1558 | 17.5034 | -360.6112 | 17.8853 | -360.9589 | 18.1604 | -360.9374 | 17.5116 | -352.7767 | 18.7579 | -352.8537 | 16.8197
11:43 | 1377 | 21.6503 | 194.7522 | 435.7322 | 440.4409 | -21.5264 | -47.1796 | 1.4328 | -0.2681 | -7.4674 | -7.5538 | -3.2558 | -4.1877 | 2.1964 | -4.6132 | 0.5811 | 0.6328 | 0.9465 | 0.692 | -130.956 | -6.4615 | 0.0566 | -1.7374 | -9.1204 | -7.8395 | -0.6198 |  | -3.3814 | -3.8243 | 4.0034 | 3.3662 | 3.3528 | 1.0214 | 10.6342 | 14.09 | 14.6965 | 11.0169 | -0.0003 | -0.0031 | 0.0007 | 0.0042 | 0.0006 | -0.0009 | 0.0075 | -0.0141 | -0.0071 | -360.1865 | 17.5075 | -360.5589 | 17.8874 | -360.9374 | 18.1522 | -360.9866 | 17.5363 | -352.8475 | 18.7703 | -352.8321 | 16.8012
11:43 | 1378 | 21.7287 | 194.7545 | 435.683 | 440.3787 | -21.6031 | -47.3552 | 1.3369 | -0.2847 | -7.5703 | -7.6732 | -3.2753 | -4.1711 | 2.1864 | -4.5526 | 0.5816 | 0.6316 | 0.9496 | 0.6916 | -130.9653 | -6.5112 | 0.0008 | -1.7194 | -9.0875 | -7.9124 | -0.5532 |  | -3.3099 | -3.7202 | 4.0016 | 3.3722 | 3.3539 | 1.0215 | 10.6238 | 14.0796 | 14.6574 | 10.9948 | 0 | -0.0033 | 0.0009 | 0.0038 | -0.0001 | -0.001 | -0.0114 | -0.0079 | -0.0027 | -360.2265 | 17.5219 | -360.5743 | 17.8545 | -360.842 | 18.1132 | -360.9558 | 17.5506 | -352.8567 | 18.7785 | -352.8321 | 16.7745
11:43 | 1379 | 21.7694 | 194.7691 | 435.7142 | 440.2948 | -21.6 | -47.2127 | 1.3636 | -0.258 | -7.6121 | -7.6501 | -3.2324 | -4.2395 | 2.1768 | -4.608 | 0.5814 | 0.6313 | 0.9498 | 0.6926 | -130.9681 | -6.5521 | -0.0077 | -1.7645 | -9.1042 | -7.9235 | -0.704 |  | -3.3269 | -3.7815 | 4.0025 | 3.3685 | 3.3521 | 1.0213 | 10.6468 | 14.1088 | 14.7 | 11.0345 | -0.0005 | -0.0034 | 0.0008 | 0.0042 | 0.0009 | -0.0007 | 0.0111 | -0.0066 | -0.0094 | -360.2111 | 17.5506 | -360.6266 | 17.8771 | -360.882 | 18.0968 | -360.9435 | 17.5363 | -352.866 | 18.8134 | -352.8906 | 16.7991
11:43 | 1380 | 21.8009 | 194.7446 | 435.7196 | 440.3083 | -21.6379 | -47.2178 | 1.2972 | -0.2146 | -7.5037 | -7.539 | -3.2371 | -4.1565 | 2.2453 | -4.6579 | 0.583 | 0.6297 | 0.9484 | 0.6923 | -130.9045 | -6.4633 | 0.0238 | -1.7184 | -9.0396 | -7.8779 | -0.6145 |  | -3.2978 | -3.6425 | 4.0031 | 3.3668 | 3.3493 | 1.0218 | 10.6319 | 14.0646 | 14.6833 | 11.0143 | -0.0004 | -0.0029 | 0.0002 | 0.0036 | 0.0003 | -0.0006 | 0.0106 | -0.0167 | -0.0061 | -360.165 | 17.5157 | -360.5804 | 17.8874 | -360.9158 | 18.1194 | -360.962 | 17.5219 | -352.8321 | 18.7887 | -352.8321 | 16.8032
11:43 | 1381 | 21.7884 | 194.7193 | 435.7019 | 440.3256 | -21.6177 | -47.2942 | 1.3043 | -0.1472 | -7.558 | -7.5116 | -3.2532 | -4.2567 | 2.1138 | -4.7247 | 0.5822 | 0.6325 | 0.9472 | 0.6935 | -130.8482 | -6.5307 | 0.0353 | -1.7424 | -9.1628 | -7.9625 | -0.5227 |  | -3.2701 | -3.682 | 4.0036 | 3.3682 | 3.3527 | 1.0226 | 10.6364 | 14.1042 | 14.7303 | 11.0125 | -0.0001 | -0.0029 | 0.0009 | 0.004 | 0.0006 | -0.0007 | -0.0023 | -0.0134 | -0.0083 | -360.1773 | 17.4993 | -360.5373 | 17.8668 | -360.9097 | 18.1461 | -360.9804 | 17.5342 | -352.8075 | 18.76 | -352.8014 | 16.7868
11:43 | 1382 | 21.8059 | 194.8174 | 435.6868 | 440.2614 | -21.6823 | -47.3494 | 1.2748 | -0.1244 | -7.4982 | -7.5881 | -3.2362 | -4.237 | 2.1563 | -4.6975 | 0.5811 | 0.6303 | 0.9473 | 0.6932 | -130.8743 | -6.5231 | -0.0109 | -1.7585 | -9.2355 | -7.9292 | -0.6176 |  | -3.2798 | -3.6908 | 4.0027 | 3.3719 | 3.3508 | 1.0209 | 10.6215 | 14.1003 | 14.7067 | 11.0273 | 0.0001 | -0.0034 | 0.0001 | 0.0029 | 0.0006 | -0.0005 | 0.0064 | -0.0121 | -0.0109 | -360.1804 | 17.5055 | -360.565 | 17.8545 | -360.9251 | 18.142 | -361.0174 | 17.5629 | -352.8537 | 18.76 | -352.8229 | 16.7827
11:43 | 1383 | 21.7911 | 194.7279 | 435.6138 | 440.1919 | -21.7543 | -47.2916 | 1.2864 | -0.1233 | -7.5086 | -7.5408 | -3.1752 | -4.2364 | 2.1278 | -4.6728 | 0.5821 | 0.634 | 0.9473 | 0.6935 | -130.8855 | -6.6225 | 0.0133 | -1.6789 | -9.1531 | -7.9363 | -0.5734 |  | -3.332 | -3.6832 | 4.0028 | 3.3677 | 3.3559 | 1.0219 | 10.6364 | 14.1098 | 14.6945 | 10.9897 | -0.0002 | -0.0029 | 0.0008 | 0.0035 | 0.0005 | -0.0006 | 0.0139 | 0.0095 | -0.0011 | -360.1681 | 17.5178 | -360.5743 | 17.8607 | -360.8758 | 18.1214 | -360.9989 | 17.5486 | -352.8198 | 18.7887 | -352.8537 | 16.7848
11:43 | 1384 | 21.7748 | 194.6769 | 435.7389 | 440.1852 | -21.6411 | -47.2298 | 1.2101 | -0.1379 | -7.4733 | -7.5791 | -3.2358 | -4.2184 | 2.1384 | -4.6433 | 0.5822 | 0.6332 | 0.9484 | 0.6937 | -130.9191 | -6.6242 | 0.0388 | -1.6517 | -9.1655 | -7.7898 | -0.5464 |  | -3.3586 | -3.81 | 4.0031 | 3.3661 | 3.3557 | 1.0218 | 10.6029 | 14.0821 | 14.6554 | 11.0428 | -0.0003 | -0.0029 | 0.0009 | 0.0034 | 0.001 | -0.0004 | 0.0077 | -0.003 | -0.0067 | -360.1988 | 17.5363 | -360.6173 | 17.8956 | -360.9651 | 18.1112 | -360.9097 | 17.5445 | -352.8167 | 18.7867 | -352.8721 | 16.8156
11:43 | 1385 | 21.778 | 194.6262 | 435.7137 | 440.1329 | -21.6785 | -47.2451 | 1.3349 | -0.1414 | -7.5103 | -7.5892 | -3.1076 | -4.1711 | 2.1891 | -4.6809 | 0.5815 | 0.6323 | 0.9493 | 0.6927 | -130.9781 | -6.5413 | 0.0269 | -1.7411 | -9.1208 | -7.9195 | -0.519 |  | -3.3078 | -3.7566 | 4.0012 | 3.3697 | 3.3517 | 1.0209 | 10.6133 | 14.0982 | 14.7119 | 11.0417 | -0.0001 | -0.0025 | 0.0009 | 0.0037 | 0.0005 | -0.0005 | 0.0081 | -0.0125 | -0.0112 | -360.1373 | 17.5198 | -360.5681 | 17.8689 | -360.9281 | 18.1255 | -360.9466 | 17.5404 | -352.8014 | 18.7805 | -352.8567 | 16.8032
11:43 | 1386 | 21.8103 | 194.7309 | 435.7104 | 440.0993 | -21.7086 | -47.3412 | 1.2072 | -0.1709 | -7.5697 | -7.5379 | -3.0918 | -4.1635 | 2.2036 | -4.6749 | 0.5798 | 0.6319 | 0.9484 | 0.6935 | -130.9594 | -6.6533 | 0.0509 | -1.6601 | -9.0859 | -7.8291 | -0.5038 |  | -3.3185 | -3.775 | 4.0026 | 3.3667 | 3.354 | 1.0219 | 10.625 | 14.0285 | 14.6451 | 10.9909 | -0.0005 | -0.0033 | 0.001 | 0.0042 | 0.0008 | -0.0009 | -0.0047 | -0.0108 | -0.0173 | -360.2019 | 17.5198 | -360.5527 | 17.8648 | -360.9158 | 18.1502 | -361.0235 | 17.5814 | -352.8414 | 18.7744 | -352.829 | 16.7909
11:43 | 1387 | 21.8064 | 194.6572 | 435.6255 | 440.1202 | -21.625 | -47.2394 | 1.304 | -0.1499 | -7.4748 | -7.5192 | -3.1516 | -4.1994 | 2.178 | -4.6197 | 0.58 | 0.6347 | 0.9513 | 0.6927 | -130.948 | -6.5292 | 0.1079 | -1.5605 | -9.006 | -7.7451 | -0.4472 |  | -3.3041 | -3.7969 | 4.0026 | 3.3646 | 3.3536 | 1.0214 | 10.6351 | 14.0975 | 14.7195 | 11.0453 | 0.0001 | -0.003 | 0.0006 | 0.0036 | 0.0005 | -0.0003 | 0.0038 | 0.0027 | -0.0115 | -360.2081 | 17.5137 | -360.5496 | 17.836 | -360.8574 | 18.105 | -360.9589 | 17.565 | -352.829 | 18.7723 | -352.8167 | 16.7786
11:43 | 1388 | 21.8463 | 194.6941 | 435.6128 | 440.0599 | -21.6795 | -47.238 | 1.346 | -0.2031 | -7.3842 | -7.5514 | -3.1467 | -4.1723 | 2.1374 | -4.6951 | 0.5818 | 0.6329 | 0.9505 | 0.6937 | -130.9224 | -6.4313 | 0.0659 | -1.5689 | -9.067 | -7.7532 | -0.5245 |  | -3.2923 | -3.7872 | 4.0021 | 3.3672 | 3.3521 | 1.0215 | 10.6099 | 14.0888 | 14.6952 | 10.9869 | -0.0002 | -0.0028 | -0.0001 | 0.0035 | 0.0007 | -0.0011 | 0.0061 | 0.0056 | -0.0178 | -360.2542 | 17.5301 | -360.5927 | 17.8791 | -360.9343 | 18.1317 | -360.9558 | 17.5609 | -352.8691 | 18.7887 | -352.8506 | 16.8032
11:43 | 1389 | 21.849 | 194.7077 | 435.6927 | 440.056 | -21.7299 | -47.3221 | 1.3216 | -0.2486 | -7.3569 | -7.5161 | -3.1498 | -4.2338 | 2.1447 | -4.6108 | 0.5826 | 0.6366 | 0.9489 | 0.6933 | -131.0375 | -6.405 | 0.1035 | -1.6107 | -8.9769 | -7.7918 | -0.5382 |  | -3.281 | -3.8303 | 4.0025 | 3.3676 | 3.3559 | 1.0219 | 10.6121 | 14.0856 | 14.6595 | 10.9883 | -0.0003 | -0.0027 | 0.0009 | 0.0041 | 0.0007 | -0.0001 | 0.0089 | -0.0153 | -0.0108 | -360.1281 | 17.5034 | -360.5804 | 17.8607 | -360.885 | 18.1194 | -360.9558 | 17.5404 | -352.7798 | 18.7559 | -352.826 | 16.7868
11:43 | 1390 | 21.8272 | 194.6103 | 435.537 | 440.0228 | -21.6974 | -47.247 | 1.3071 | -0.2036 | -7.3487 | -7.4619 | -3.1765 | -4.2664 | 2.1522 | -4.708 | 0.5827 | 0.6355 | 0.9503 | 0.6931 | -130.9404 | -6.4721 | 0.0567 | -1.6072 | -9.0163 | -7.8764 | -0.5079 |  | -3.3288 | -3.8737 | 4.0012 | 3.3662 | 3.3547 | 1.0204 | 10.6295 | 14.0914 | 14.7058 | 11.0172 | 0.0004 | -0.0026 | 0.0003 | 0.0035 | 0.0007 | -0.0006 | 0.0015 | -0.0041 | 0.0026 | -360.1804 | 17.5219 | -360.5527 | 17.8791 | -360.9466 | 18.1379 | -361.0112 | 17.5671 | -352.8229 | 18.7641 | -352.8321 | 16.8115
11:43 | 1391 | 21.8051 | 194.6425 | 435.5421 | 439.9623 | -21.6832 | -47.2235 | 1.3095 | -0.1682 | -7.4771 | -7.6623 | -3.2314 | -4.2385 | 2.1435 | -4.6545 | 0.5814 | 0.6328 | 0.9456 | 0.6935 | -130.8614 | -6.416 | 0.1318 | -1.6235 | -9.0632 | -7.8481 | -0.4394 |  | -3.4407 | -3.8431 | 4.0023 | 3.3681 | 3.3525 | 1.0223 | 10.6042 | 14.1002 | 14.6883 | 10.9873 | 0 | -0.0034 | 0.0007 | 0.0034 | 0.0003 | -0.0006 | 0.0081 | -0.002 | 0.0086 | -360.1742 | 17.5157 | -360.5835 | 17.8607 | -360.8666 | 18.1173 | -360.9466 | 17.5547 | -352.8229 | 18.7682 | -352.829 | 16.795
11:43 | 1392 | 21.7276 | 194.6727 | 435.6634 | 439.8451 | -21.7089 | -47.2952 | 1.3158 | -0.1606 | -7.3755 | -7.5374 | -3.147 | -4.1562 | 2.2593 | -4.5883 | 0.5824 | 0.6337 | 0.9497 | 0.6937 | -130.8787 | -6.3933 | 0.1723 | -1.7036 | -9.0756 | -7.8692 | -0.5277 |  | -3.3487 | -3.7469 | 4.0027 | 3.3655 | 3.3549 | 1.021 | 10.6144 | 14.0938 | 14.7317 | 11.0251 | 0.0002 | -0.0026 | 0.0011 | 0.0038 | 0.0004 | -0.0006 | 0.0181 | -0.0118 | -0.0144 | -360.1773 | 17.5219 | -360.5866 | 17.8689 | -360.8912 | 18.1337 | -360.9558 | 17.5527 | -352.8414 | 18.7805 | -352.8383 | 16.795
11:43 | 1393 | 21.815 | 194.7059 | 435.5761 | 439.8145 | -21.8012 | -47.3107 | 1.2674 | -0.1878 | -7.4341 | -7.5538 | -3.2724 | -4.19 | 2.159 | -4.6362 | 0.5817 | 0.635 | 0.9489 | 0.6944 | -131.0369 | -6.375 | 0.123 | -1.6553 | -9.1042 | -7.8448 | -0.4733 |  | -3.3647 | -3.7977 | 4.0026 | 3.3669 | 3.3535 | 1.0209 | 10.6446 | 14.1063 | 14.7194 | 11.0385 | -0.0006 | -0.0029 | 0.0004 | 0.003 | 0.0006 | -0.0006 | 0.0014 | -0.0216 | -0.032 | -360.1619 | 17.5157 | -360.5927 | 17.8648 | -360.8912 | 18.1276 | -360.9527 | 17.5629 | -352.7952 | 18.76 | -352.829 | 16.8012
11:43 | 1394 | 21.7545 | 194.6754 | 435.5942 | 439.651 | -21.7231 | -47.265 | 1.2784 | -0.2399 | -7.4673 | -7.6533 | -3.2593 | -4.1676 | 2.2883 | -4.6183 | 0.5835 | 0.6318 | 0.9487 | 0.6942 | -130.9457 | -6.4158 | 0.1556 | -1.6877 | -9.0999 | -7.8001 | -0.5439 |  | -3.4071 | -3.9047 | 4.0014 | 3.368 | 3.3553 | 1.0211 | 10.5845 | 14.0922 | 14.6461 | 10.9905 | -0.0006 | -0.003 | 0.001 | 0.0041 | 0.0003 | -0.0004 | 0.0027 | -0.0128 | 0.0166 | -360.205 | 17.5178 | -360.5527 | 17.8689 | -360.8789 | 18.1276 | -360.9527 | 17.5568 | -352.8137 | 18.7744 | -352.826 | 16.7889
11:43 | 1395 | 21.7142 | 194.6914 | 435.6196 | 439.5432 | -21.6948 | -47.2729 | 1.2292 | -0.2375 | -7.4257 | -7.5735 | -3.2561 | -4.2502 | 2.1762 | -4.7548 | 0.5822 | 0.6312 | 0.9472 | 0.6933 | -130.9388 | -6.3074 | 0.0926 | -1.6717 | -9.1086 | -7.7518 | -0.4761 |  | -3.3078 | -3.7764 | 4.0022 | 3.3671 | 3.351 | 1.023 | 10.6502 | 14.1125 | 14.7167 | 11.0431 | 0.0002 | -0.003 | 0.0005 | 0.0038 | 0.0008 | -0.0007 | 0.0195 | 0.0048 | -0.0095 | -360.2173 | 17.5363 | -360.5589 | 17.8668 | -360.8881 | 18.1276 | -360.9589 | 17.5773 | -352.8414 | 18.7682 | -352.8167 | 16.7848
11:43 | 1396 | 21.8398 | 194.6807 | 435.6309 | 439.367 | -21.7144 | -47.2354 | 1.2615 | -0.1909 | -7.3293 | -7.5753 | -3.1868 | -4.2219 | 2.2148 | -4.6334 | 0.5827 | 0.6316 | 0.9479 | 0.6927 | -130.9307 | -6.4181 | 0.0284 | -1.6477 | -9.0933 | -7.8263 | -0.5991 |  | -3.3652 | -3.7341 | 4.0026 | 3.365 | 3.3533 | 1.0216 | 10.6066 | 14.085 | 14.6426 | 11.0017 | -0.0002 | -0.0033 | 0.0001 | 0.0032 | 0.0001 | -0.0007 | 0.0038 | -0.0154 | 0.0054 | -360.1773 | 17.5301 | -360.5712 | 17.8627 | -360.882 | 18.1214 | -360.9527 | 17.5527 | -352.8167 | 18.7641 | -352.8506 | 16.7889
11:43 | 1397 | 21.8054 | 194.6314 | 435.7056 | 439.3434 | -21.7268 | -47.3173 | 1.2704 | -0.135 | -7.311 | -7.5899 | -3.2808 | -4.3009 | 2.1611 | -4.7011 | 0.5826 | 0.6302 | 0.9467 | 0.6936 | -130.9616 | -6.4 | 0.1156 | -1.6358 | -9.0755 | -7.8356 | -0.5031 |  | -3.2853 | -3.7601 | 4.0023 | 3.365 | 3.3496 | 1.0226 | 10.6272 | 14.0544 | 14.6915 | 11.0092 | -0.0004 | -0.0028 | 0.0007 | 0.0037 | 0.0011 | -0.0007 | 0.0141 | -0.0152 | -0.005 | -360.2019 | 17.5116 | -360.565 | 17.8709 | -360.9312 | 18.1502 | -360.9804 | 17.5568 | -352.8198 | 18.7579 | -352.829 | 16.8012
11:43 | 1398 | 21.8442 | 194.6998 | 435.6776 | 439.3288 | -21.6901 | -47.3565 | 1.302 | -0.1871 | -7.3939 | -7.5425 | -3.2536 | -4.2779 | 2.1676 | -4.6851 | 0.5823 | 0.6304 | 0.9487 | 0.6929 | -131.0023 | -6.4486 | 0.0154 | -1.6142 | -9.0641 | -7.7535 | -0.5032 |  | -3.2488 | -3.7776 | 4.0022 | 3.3646 | 3.3538 | 1.0218 | 10.6377 | 14.076 | 14.6938 | 11.0089 | -0.0006 | -0.003 | 0.0008 | 0.0037 | 0.0007 | -0.0004 | 0.0204 | -0.021 | 0.0171 | -360.1896 | 17.5034 | -360.5435 | 17.8545 | -360.882 | 18.1276 | -360.9804 | 17.5486 | -352.8106 | 18.7497 | -352.8198 | 16.7848
11:43 | 1399 | 21.9118 | 194.7622 | 435.609 | 439.4034 | -21.7102 | -47.2931 | 1.283 | -0.1226 | -7.3568 | -7.5419 | -3.2361 | -4.2606 | 2.1877 | -4.7137 | 0.5843 | 0.6303 | 0.949 | 0.6928 | -130.9895 | -6.4454 | 0.047 | -1.6056 | -9.0409 | -7.8625 | -0.4699 |  | -3.3157 | -3.7764 | 4.0039 | 3.3667 | 3.3543 | 1.0224 | 10.6017 | 14.1272 | 14.654 | 11.0071 | 0 | -0.0029 | 0.0007 | 0.0037 | 0.0006 | -0.0004 | 0.0059 | -0.004 | -0.0249 | -360.2265 | 17.5404 | -360.5835 | 17.8545 | -360.9312 | 18.1337 | -360.9681 | 17.5732 | -352.8752 | 18.7826 | -352.8383 | 16.7745
11:43 | 1400 | 21.8402 | 194.7076 | 435.6039 | 439.2896 | -21.6347 | -47.289 | 1.3431 | -0.1557 | -7.4385 | -7.5982 | -3.2693 | -4.3265 | 2.2092 | -4.5918 | 0.5827 | 0.6309 | 0.9479 | 0.6934 | -131.0129 | -6.3578 | 0.0795 | -1.5999 | -9.065 | -7.7588 | -0.499 |  | -3.3316 | -3.7427 | 4.0028 | 3.3652 | 3.3537 | 1.0226 | 10.6433 | 14.1055 | 14.698 | 11.0363 | 0 | -0.0032 | 0.0009 | 0.004 | 0.0005 | -0.0005 | 0.0088 | -0.0057 | -0.0105 | -360.1958 | 17.526 | -360.5773 | 17.8566 | -360.9004 | 18.105 | -360.9158 | 17.5363 | -352.8321 | 18.7805 | -352.8383 | 16.7868
11:43 | 1401 | 21.8568 | 194.7541 | 435.6945 | 439.288 | -21.6102 | -47.3461 | 1.3822 | -0.0433 | -7.3916 | -7.6493 | -3.2885 | -4.2494 | 2.2453 | -4.6387 | 0.5822 | 0.6327 | 0.946 | 0.6916 | -131.0003 | -6.3445 | 0.0946 | -1.4621 | -9.0068 | -7.8068 | -0.4953 |  | -3.2477 | -3.7117 | 4.004 | 3.3678 | 3.3522 | 1.0205 | 10.6526 | 14.1435 | 14.7347 | 11.0345 | -0.0004 | -0.003 | 0.0006 | 0.0038 | 0.0002 | -0.0006 | 0.0077 | -0.0106 | -0.0129 | -360.2081 | 17.5342 | -360.6081 | 17.8853 | -360.9189 | 18.1214 | -360.9712 | 17.5588 | -352.866 | 18.7744 | -352.8721 | 16.8053
11:43 | 1402 | 21.8142 | 194.7459 | 435.6364 | 439.2603 | -21.5808 | -47.299 | 1.3126 | -0.0767 | -7.4625 | -7.6261 | -3.3127 | -4.1519 | 2.3044 | -4.4625 | 0.5824 | 0.6325 | 0.9476 | 0.6928 | -130.9658 | -6.3106 | 0.1647 | -1.3568 | -8.9209 | -7.6622 | -0.4107 |  | -3.1764 | -3.6869 | 4.0029 | 3.3669 | 3.3539 | 1.0212 | 10.6399 | 14.096 | 14.6697 | 11.0103 | -0.0002 | -0.0027 | 0.0006 | 0.0037 | 0.0009 | -0.0009 | 0.0095 | 0 | -0.0094 | -360.2019 | 17.5034 | -360.5404 | 17.8504 | -360.8881 | 18.1358 | -360.9589 | 17.5445 | -352.8044 | 18.7456 | -352.8198 | 16.7807
11:43 | 1403 | 21.8787 | 194.7511 | 435.6975 | 439.2423 | -21.6042 | -47.2911 | 1.3921 | -0.0987 | -7.3204 | -7.5022 | -3.2443 | -4.207 | 2.3253 | -4.4974 | 0.5828 | 0.6349 | 0.9506 | 0.6926 | -130.9668 | -6.3977 | 0.1732 | -1.5717 | -8.9984 | -7.7275 | -0.5274 |  | -3.1834 | -3.7161 | 4.0035 | 3.3669 | 3.3508 | 1.0229 | 10.6375 | 14.1111 | 14.6854 | 11.0367 | -0.0006 | -0.0031 | 0.0005 | 0.0038 | 0.0005 | -0.0005 | 0.0145 | -0.0182 | -0.0159 | -360.2142 | 17.5137 | -360.5127 | 17.8504 | -360.9127 | 18.1399 | -360.9743 | 17.5917 | -352.8629 | 18.7559 | -352.8167 | 16.7704
11:43 | 1404 | 21.9225 | 194.7042 | 435.7757 | 439.1959 | -21.5402 | -47.2195 | 1.3923 | -0.0664 | -7.3586 | -7.6962 | -3.1958 | -4.2124 | 2.3034 | -4.504 | 0.5832 | 0.6323 | 0.9496 | 0.6944 | -131.0058 | -6.4789 | 0.1504 | -1.438 | -8.9405 | -7.6469 | -0.5595 |  | -3.2302 | -3.6561 | 4.004 | 3.3698 | 3.3572 | 1.0228 | 10.6227 | 14.084 | 14.707 | 11.0172 | 0 | -0.0032 | 0.0002 | 0.0036 | 0.0008 | -0.0008 | -0.0007 | -0.0142 | -0.0229 | -360.1927 | 17.5342 | -360.5681 | 17.8442 | -360.8604 | 18.1276 | -360.9958 | 17.5691 | -352.8537 | 18.7641 | -352.8414 | 16.756
11:43 | 1405 | 21.8542 | 194.655 | 435.7418 | 439.1774 | -21.6189 | -47.3302 | 1.3506 | -0.0931 | -7.3388 | -7.6332 | -3.134 | -4.1375 | 2.3396 | -4.5503 | 0.5828 | 0.6319 | 0.9481 | 0.6936 | -130.9111 | -6.4683 | 0.1799 | -1.3838 | -9.021 | -7.7364 | -0.4344 |  | -3.3316 | -3.7225 | 4.0044 | 3.3694 | 3.3526 | 1.0213 | 10.6144 | 14.0647 | 14.6496 | 10.9966 | 0 | -0.0029 | 0.0007 | 0.004 | 0.0006 | -0.0004 | 0.0084 | 0.005 | 0.0081 | -360.1619 | 17.5239 | -360.5989 | 17.8812 | -360.9343 | 18.0988 | -360.962 | 17.5527 | -352.8137 | 18.7661 | -352.8721 | 16.8032
11:43 | 1406 | 21.8741 | 194.7147 | 435.6484 | 439.1845 | -21.5931 | -47.2075 | 1.4545 | -0.1785 | -7.3412 | -7.6344 | -3.2275 | -4.2862 | 2.2764 | -4.6026 | 0.5821 | 0.6307 | 0.9447 | 0.6942 | -130.8479 | -6.3355 | 0.1917 | -1.3885 | -9.028 | -7.6249 | -0.4371 |  | -3.2961 | -3.7345 | 4.0027 | 3.3636 | 3.3525 | 1.0223 | 10.6342 | 14.0726 | 14.6965 | 11.0342 | -0.0004 | -0.0026 | 0.0007 | 0.0039 | 0.0007 | -0.0009 | 0.0089 | 0.0001 | -0.002 | -360.1773 | 17.5157 | -360.605 | 17.8956 | -360.9527 | 18.1481 | -360.9589 | 17.5301 | -352.7798 | 18.7661 | -352.8814 | 16.8094
11:43 | 1407 | 21.8022 | 194.6473 | 435.7238 | 439.1841 | -21.6687 | -47.1711 | 1.4409 | -0.1258 | -7.3843 | -7.6031 | -3.1599 | -4.2027 | 2.2691 | -4.6371 | 0.5823 | 0.6331 | 0.9445 | 0.6942 | -130.8337 | -6.3932 | 0.2125 | -1.5732 | -9.1232 | -7.7012 | -0.5479 |  | -3.3071 | -3.7249 | 4.004 | 3.366 | 3.3527 | 1.0231 | 10.5881 | 14.0434 | 14.625 | 10.983 | -0.0001 | -0.0027 | 0.0005 | 0.0033 | 0.0006 | -0.0001 | 0.0079 | 0.0011 | -0.009 | -360.1958 | 17.5096 | -360.5189 | 17.8545 | -360.9281 | 18.1296 | -360.9743 | 17.5506 | -352.7952 | 18.7538 | -352.8167 | 16.7786
11:43 | 1408 | 21.8477 | 194.679 | 435.6851 | 439.2706 | -21.6109 | -47.1078 | 1.425 | -0.1802 | -7.3957 | -7.5239 | -3.1796 | -4.2487 | 2.2314 | -4.5688 | 0.5815 | 0.6326 | 0.9492 | 0.6933 | -130.8407 | -6.305 | 0.2859 | -1.6526 | -9.0705 | -7.6657 | -0.4863 |  | -3.2605 | -3.7469 | 4.0024 | 3.3716 | 3.352 | 1.0233 | 10.6191 | 14.0751 | 14.6714 | 10.984 | 0.0002 | -0.003 | 0.0012 | 0.0038 | 0.0004 | -0.0009 | 0.0059 | -0.0054 | -0.0028 | -360.2296 | 17.5342 | -360.5927 | 17.8463 | -360.8789 | 18.1255 | -361.0143 | 17.5753 | -352.8506 | 18.7949 | -352.866 | 16.7642
11:43 | 1409 | 21.8702 | 194.649 | 435.7176 | 439.2348 | -21.5993 | -47.2207 | 1.4657 | -0.1353 | -7.3703 | -7.6676 | -3.2581 | -4.0735 | 2.2559 | -4.5681 | 0.5834 | 0.6349 | 0.949 | 0.6928 | -130.8882 | -6.3021 | 0.2797 | -1.8045 | -9.0827 | -7.6661 | -0.5229 |  | -3.2304 | -3.7435 | 4.0008 | 3.3703 | 3.3527 | 1.023 | 10.6341 | 14.0902 | 14.7102 | 11.0334 | -0.0001 | -0.003 | 0.0007 | 0.0036 | 0.0008 | -0.0003 | -0.0028 | -0.0085 | -0.006 | -360.1927 | 17.526 | -360.565 | 17.8545 | -360.8697 | 18.0988 | -360.9374 | 17.5506 | -352.8475 | 18.7744 | -352.8506 | 16.7745
11:43 | 1410 | 21.9344 | 194.7068 | 435.8374 | 439.2612 | -21.5797 | -47.1134 | 1.4367 | -0.1553 | -7.3778 | -7.701 | -3.2918 | -4.0936 | 2.3792 | -4.518 | 0.5833 | 0.6347 | 0.9478 | 0.6919 | -130.8654 | -6.3165 | 0.0669 | -1.8248 | -8.9671 | -7.6433 | -0.5535 |  | -3.2271 | -3.7339 | 4.002 | 3.3675 | 3.3512 | 1.023 | 10.6272 | 14.1006 | 14.703 | 10.9977 | -0.0005 | -0.0029 | 0.0006 | 0.0036 | 0.0004 | -0.0006 | 0.0017 | 0.0021 | -0.0152 | -360.1804 | 17.528 | -360.5958 | 17.8915 | -360.9466 | 18.1399 | -360.9651 | 17.5568 | -352.8014 | 18.7661 | -352.8537 | 16.8012
11:43 | 1411 | 21.9539 | 194.723 | 435.7423 | 439.231 | -21.5345 | -47.2421 | 1.4266 | -0.1657 | -7.4152 | -7.6161 | -3.2453 | -4.0844 | 2.2626 | -4.4683 | 0.5827 | 0.6341 | 0.9467 | 0.6926 | -130.7893 | -6.2487 | 0.1823 | -1.75 | -9.0198 | -7.666 | -0.5143 |  | -3.247 | -3.6236 | 4.0032 | 3.3669 | 3.3527 | 1.0222 | 10.6284 | 14.1074 | 14.7381 | 11.0165 | -0.0004 | -0.0024 | 0.0006 | 0.0039 | 0.0006 | -0.001 | 0.0173 | -0.0262 | 0.0133 | -360.1558 | 17.4972 | -360.5004 | 17.8401 | -360.8881 | 18.142 | -360.9743 | 17.5527 | -352.789 | 18.7395 | -352.789 | 16.7642
11:43 | 1412 | 21.9817 | 194.7344 | 435.8156 | 439.2301 | -21.5655 | -47.2626 | 1.4271 | -0.1268 | -7.3389 | -7.5227 | -3.2025 | -4.1313 | 2.2714 | -4.3951 | 0.5828 | 0.631 | 0.9459 | 0.6929 | -130.8288 | -6.2907 | 0.2106 | -1.5774 | -8.9532 | -7.7353 | -0.4475 |  | -3.1887 | -3.6406 | 4.0029 | 3.3691 | 3.3527 | 1.0229 | 10.6479 | 14.087 | 14.7371 | 11.0121 | -0.0002 | -0.0031 | 0.0004 | 0.0034 | 0.0003 | -0.0001 | -0.0086 | -0.0155 | -0.0105 | -360.2111 | 17.5157 | -360.5773 | 17.8689 | -360.9281 | 18.1461 | -361.0204 | 17.5835 | -352.8321 | 18.7559 | -352.826 | 16.7868
11:43 | 1413 | 21.9871 | 194.7041 | 435.7527 | 439.126 | -21.5951 | -47.2403 | 1.404 | -0.132 | -7.3348 | -7.459 | -3.189 | -4.26 | 2.3218 | -4.4035 | 0.5851 | 0.6299 | 0.9482 | 0.6915 | -130.8506 | -6.2702 | 0.2269 | -1.5989 | -8.9154 | -7.5724 | -0.4951 |  | -3.2355 | -3.5909 | 4.0023 | 3.3655 | 3.3559 | 1.0218 | 10.6123 | 14.1026 | 14.6679 | 11.0068 | -0.0003 | -0.0035 | 0.0002 | 0.0038 | 0.001 | -0.0008 | -0.001 | -0.0139 | -0.0053 | -360.2173 | 17.5321 | -360.5835 | 17.8504 | -360.8789 | 18.1132 | -360.9404 | 17.5445 | -352.8137 | 18.7703 | -352.829 | 16.7724
11:43 | 1414 | 21.8649 | 194.7605 | 435.7374 | 438.9885 | -21.5785 | -47.2625 | 1.4447 | -0.1298 | -7.4211 | -7.4385 | -3.2624 | -4.1742 | 2.2902 | -4.3553 | 0.5837 | 0.6326 | 0.951 | 0.6925 | -130.8543 | -6.3812 | 0.1871 | -1.6403 | -8.9319 | -7.4774 | -0.4711 |  | -3.2053 | -3.5201 | 4.003 | 3.3669 | 3.3527 | 1.0226 | 10.6387 | 14.0775 | 14.703 | 10.9919 | -0.0001 | -0.0028 | 0.0008 | 0.0035 | 0.0003 | -0.0004 | 0.0088 | -0.0057 | -0.0004 | -360.1711 | 17.5383 | -360.6081 | 17.9038 | -360.9404 | 18.1255 | -360.9374 | 17.5424 | -352.8475 | 18.7805 | -352.8783 | 16.8135
11:43 | 1415 | 21.878 | 194.7811 | 435.771 | 439.0356 | -21.51 | -47.2617 | 1.4297 | -0.1341 | -7.4263 | -7.3561 | -3.2963 | -4.1627 | 2.2831 | -4.314 | 0.5828 | 0.6307 | 0.948 | 0.692 | -130.8657 | -6.3076 | 0.1738 | -1.6382 | -9.0235 | -7.5954 | -0.5829 |  | -3.2359 | -3.5474 | 4.0029 | 3.3666 | 3.3542 | 1.0231 | 10.6364 | 14.0809 | 14.6945 | 11.0302 | -0.0003 | -0.0028 | 0.0009 | 0.0034 | 0.0011 | -0.0008 | -0.0001 | 0.0048 | -0.0017 | -360.1342 | 17.5198 | -360.6235 | 17.8771 | -360.9189 | 18.1317 | -360.9374 | 17.5342 | -352.7737 | 18.7661 | -352.8567 | 16.793
11:43 | 1416 | 21.9228 | 194.6992 | 435.7385 | 439.066 | -21.6032 | -47.34 | 1.3904 | -0.1783 | -7.4352 | -7.428 | -3.1967 | -4.118 | 2.284 | -4.4171 | 0.5834 | 0.6357 | 0.9511 | 0.6929 | -130.809 | -6.2769 | 0.1603 | -1.6964 | -9.0468 | -7.6422 | -0.5272 |  | -3.1591 | -3.5242 | 4.0019 | 3.3708 | 3.3549 | 1.0226 | 10.6191 | 14.0923 | 14.7108 | 11.0075 | -0.0002 | -0.003 | 0.0007 | 0.0038 | 0.0005 | -0.0006 | 0.0136 | -0.008 | -0.0083 | -360.1988 | 17.489 | -360.5435 | 17.8627 | -360.8912 | 18.1337 | -360.9835 | 17.5712 | -352.8321 | 18.7559 | -352.829 | 16.7786
11:43 | 1417 | 21.9227 | 194.7553 | 435.8475 | 438.9371 | -21.5437 | -47.28 | 1.4349 | -0.2297 | -7.4575 | -7.4108 | -3.319 | -4.0527 | 2.2866 | -4.3581 | 0.5831 | 0.6325 | 0.9467 | 0.692 | -130.8664 | -6.2079 | 0.2632 | -1.6128 | -8.983 | -7.6095 | -0.5575 |  | -3.1525 | -3.5455 | 4.0019 | 3.3679 | 3.3526 | 1.0232 | 10.6155 | 14.1297 | 14.6925 | 11.032 | 0.0001 | -0.0031 | 0.0009 | 0.0039 | 0.0007 | -0.0001 | 0.0054 | 0.008 | -0.0124 | -360.2111 | 17.5342 | -360.5743 | 17.8483 | -360.8758 | 18.1337 | -360.9897 | 17.5876 | -352.8629 | 18.7764 | -352.8506 | 16.754
11:43 | 1418 | 21.876 | 194.7162 | 435.8502 | 438.918 | -21.6216 | -47.4018 | 1.4207 | -0.1071 | -7.5 | -7.4453 | -3.3 | -4.2151 | 2.1853 | -4.4598 | 0.5836 | 0.6324 | 0.9489 | 0.6923 | -130.848 | -6.301 | 0.2083 | -1.6671 | -9.0057 | -7.5068 | -0.5848 |  | -3.1536 | -3.6157 | 4.0016 | 3.3654 | 3.3527 | 1.0238 | 10.6307 | 14.0867 | 14.6887 | 11.0533 | -0.0003 | -0.0033 | 0.0008 | 0.0039 | 0.0004 | -0.0007 | 0.0113 | -0.0064 | -0.0132 | -360.1958 | 17.528 | -360.5619 | 17.8504 | -360.8727 | 18.1132 | -360.9374 | 17.5547 | -352.8321 | 18.7744 | -352.8167 | 16.7683
11:43 | 1419 | 21.9528 | 194.7754 | 435.8457 | 438.9077 | -21.5326 | -47.4013 | 1.4709 | -0.0908 | -7.459 | -7.4273 | -3.2547 | -4.0665 | 2.2478 | -4.3926 | 0.5823 | 0.632 | 0.9448 | 0.6925 | -130.8399 | -6.2979 | 0.2441 | -1.5192 | -8.967 | -7.5175 | -0.4599 |  | -3.1456 | -3.5651 | 4.0013 | 3.3667 | 3.3535 | 1.0242 | 10.5915 | 14.0875 | 14.6927 | 11.0209 | -0.0005 | -0.003 | 0.0003 | 0.0035 | 0.0005 | -0.0004 | 0.0027 | -0.0121 | -0.0179 | -360.1681 | 17.5239 | -360.6235 | 17.8894 | -360.9374 | 18.1296 | -360.9681 | 17.5506 | -352.7921 | 18.7785 | -352.8629 | 16.8012
11:43 | 1420 | 21.9927 | 194.8114 | 435.82 | 438.9145 | -21.5171 | -47.3467 | 1.5498 | -0.1331 | -7.5002 | -7.4945 | -3.244 | -4.1192 | 2.2894 | -4.5019 | 0.5844 | 0.6322 | 0.9477 | 0.693 | -130.8582 | -6.2835 | 0.2054 | -1.5839 | -9.0387 | -7.6668 | -0.5039 |  | -3.0872 | -3.6189 | 4.0035 | 3.3641 | 3.3532 | 1.0233 | 10.6272 | 14.118 | 14.6857 | 11.0092 | -0.0008 | -0.0031 | 0.0005 | 0.0039 | 0.0012 | -0.0002 | 0.0158 | -0.0149 | 0.0055 | -360.125 | 17.4911 | -360.5558 | 17.8668 | -360.9281 | 18.1379 | -360.9589 | 17.5321 | -352.7798 | 18.7395 | -352.8321 | 16.7868
11:43 | 1421 | 21.9444 | 194.7528 | 435.7367 | 438.8817 | -21.4788 | -47.3752 | 1.5405 | -0.1063 | -7.5315 | -7.474 | -3.2695 | -4.1103 | 2.2541 | -4.4347 | 0.5841 | 0.6316 | 0.9498 | 0.6937 | -130.753 | -6.2872 | 0.2256 | -1.7336 | -9.1423 | -7.6191 | -0.5821 |  | -3.0899 | -3.621 | 4.0027 | 3.367 | 3.3536 | 1.0233 | 10.6111 | 14.1015 | 14.6792 | 11.0053 | -0.0001 | -0.003 | 0.0005 | 0.0044 | 0.0002 | -0.0006 | 0.0086 | -0.0024 | 0.0057 | -360.205 | 17.5178 | -360.5773 | 17.8791 | -360.9404 | 18.1399 | -360.9835 | 17.5712 | -352.8321 | 18.7559 | -352.8321 | 16.795
11:43 | 1422 | 21.9508 | 194.6713 | 435.604 | 438.8417 | -21.4922 | -47.2596 | 1.5627 | -0.0662 | -7.4388 | -7.3568 | -3.2683 | -4.1924 | 2.2412 | -4.3744 | 0.5825 | 0.6317 | 0.9494 | 0.6945 | -130.8171 | -6.2452 | 0.251 | -1.4778 | -9.0685 | -7.6157 | -0.5109 |  | -3.0998 | -3.4544 | 4.0036 | 3.3679 | 3.356 | 1.0233 | 10.6088 | 14.0934 | 14.6648 | 11.0262 | -0.0001 | -0.0036 | 0.0004 | 0.0037 | 0.0005 | -0.0011 | 0.0042 | -0.0118 | -0.0155 | -360.2327 | 17.5321 | -360.5835 | 17.836 | -360.8574 | 18.1255 | -360.9435 | 17.5568 | -352.8198 | 18.762 | -352.8567 | 16.7581
11:43 | 1423 | 22.0581 | 194.7433 | 435.8243 | 438.9417 | -21.491 | -47.3184 | 1.7073 | -0.1327 | -7.3981 | -7.3629 | -3.2214 | -4.0663 | 2.3234 | -4.4361 | 0.5821 | 0.6316 | 0.9442 | 0.6947 | -130.8651 | -6.2461 | 0.2115 | -1.5097 | -9.0451 | -7.7662 | -0.5564 |  | -3.1426 | -3.4479 | 4.0026 | 3.3655 | 3.3508 | 1.023 | 10.6295 | 14.103 | 14.7058 | 11.0518 | -0.0005 | -0.0029 | 0.0006 | 0.0035 | 0.0008 | -0.0001 | 0.0092 | -0.0078 | 0.0003 | -360.1958 | 17.5486 | -360.6235 | 17.8668 | -360.8881 | 18.1173 | -360.9527 | 17.5609 | -352.826 | 18.7867 | -352.8598 | 16.7889
11:43 | 1424 | 21.9732 | 194.7367 | 435.6432 | 438.9587 | -21.5476 | -47.3575 | 1.6296 | -0.0775 | -7.3817 | -7.2566 | -3.187 | -4.2042 | 2.3335 | -4.4054 | 0.583 | 0.6326 | 0.9483 | 0.6932 | -130.9612 | -6.3111 | 0.2499 | -1.4689 | -9.0362 | -7.6451 | -0.5968 |  | -3.072 | -3.4387 | 4.0031 | 3.3648 | 3.3536 | 1.0228 | 10.6364 | 14.1156 | 14.7524 | 11.036 | -0.0006 | -0.003 | 0.0009 | 0.0038 | 0.0007 | -0.001 | 0.0121 | -0.0033 | 0.0008 | -360.1619 | 17.5219 | -360.5958 | 17.8689 | -360.9035 | 18.1173 | -360.9466 | 17.5506 | -352.8044 | 18.7579 | -352.8567 | 16.7868
11:43 | 1425 | 21.9684 | 194.7669 | 435.6617 | 438.9755 | -21.429 | -47.3563 | 1.6437 | -0.1433 | -7.3842 | -7.2605 | -3.2084 | -4.2274 | 2.2537 | -4.407 | 0.5838 | 0.6312 | 0.9459 | 0.6938 | -130.9117 | -6.2689 | 0.3123 | -1.4222 | -9.1135 | -7.5743 | -0.4545 |  | -3.0912 | -3.496 | 4.0016 | 3.3643 | 3.353 | 1.0236 | 10.6063 | 14.0973 | 14.6547 | 11.011 | -0.0001 | -0.0029 | 0.0007 | 0.0033 | 0.0007 | -0.0003 | -0.0017 | -0.0078 | -0.021 | -360.1311 | 17.5034 | -360.5343 | 17.8586 | -360.9066 | 18.1543 | -360.9651 | 17.5383 | -352.7829 | 18.7497 | -352.8137 | 16.7848
11:43 | 1426 | 21.97 | 194.7367 | 435.6918 | 438.9224 | -21.4809 | -47.3672 | 1.6619 | -0.0338 | -7.3927 | -7.3204 | -3.1376 | -4.1794 | 2.2425 | -4.3372 | 0.5831 | 0.6307 | 0.9483 | 0.6927 | -130.9677 | -6.2623 | 0.33 | -1.564 | -9.1383 | -7.5665 | -0.5043 |  | -3.1338 | -3.4326 | 4.0006 | 3.3637 | 3.3521 | 1.0237 | 10.6248 | 14.0985 | 14.7371 | 11.0294 | 0.0001 | -0.003 | 0.0006 | 0.004 | 0.0005 | -0.0004 | 0.0198 | 0.0037 | 0.0065 | -360.2081 | 17.5034 | -360.5496 | 17.8607 | -360.922 | 18.142 | -361.0143 | 17.5773 | -352.8444 | 18.7456 | -352.826 | 16.7827
11:43 | 1427 | 21.95 | 194.8524 | 435.6747 | 439.0593 | -21.5668 | -47.4088 | 1.5916 | -0.1062 | -7.422 | -7.3477 | -3.3731 | -4.1088 | 2.2979 | -4.2722 | 0.5837 | 0.6339 | 0.9491 | 0.6916 | -130.9346 | -6.2671 | 0.3313 | -1.4253 | -9.0617 | -7.6306 | -0.4959 |  | -3.0602 | -3.404 | 4.0016 | 3.3677 | 3.3509 | 1.0239 | 10.6261 | 14.0934 | 14.6822 | 10.9974 | -0.0005 | -0.0031 | 0.0006 | 0.0037 | 0.0005 | -0.0008 | 0.0084 | -0.0063 | -0.0012 | -360.1435 | 17.5157 | -360.5558 | 17.8463 | -360.8727 | 18.0988 | -360.9681 | 17.5547 | -352.8167 | 18.7579 | -352.8475 | 16.7683
11:44 | 1428 | 21.9673 | 194.7082 | 435.7669 | 439.0568 | -21.6601 | -47.5347 | 1.5454 | -0.0343 | -7.4202 | -7.2892 | -3.2822 | -4.0601 | 2.2686 | -4.3765 | 0.5837 | 0.63 | 0.9482 | 0.6929 | -130.9408 | -6.3031 | 0.2526 | -1.4676 | -9.05 | -7.6161 | -0.4648 |  | -3.0394 | -3.4997 | 4.0027 | 3.3685 | 3.355 | 1.0241 | 10.6398 | 14.0961 | 14.7113 | 11.0273 | -0.0005 | -0.0024 | 0.0007 | 0.0043 | 0.0008 | -0.0002 | 0.0052 | -0.0109 | -0.0133 | -360.2142 | 17.5321 | -360.6019 | 17.8791 | -360.9312 | 18.0947 | -360.9312 | 17.5342 | -352.8229 | 18.7908 | -352.8814 | 16.7991
11:44 | 1429 | 21.919 | 194.8091 | 435.7494 | 439.1848 | -21.8208 | -47.5952 | 1.4375 | -0.0893 | -7.4526 | -7.3695 | -3.3295 | -4.0831 | 2.1885 | -4.4747 | 0.5845 | 0.633 | 0.948 | 0.6922 | -130.8895 | -6.2409 | 0.3021 | -1.4801 | -9.1065 | -7.7667 | -0.5012 |  | -3.0614 | -3.4346 | 4.002 | 3.3697 | 3.3531 | 1.0232 | 10.5891 | 14.0852 | 14.6737 | 11.001 | -0.0004 | -0.0029 | 0.0005 | 0.0041 | 0.0009 | -0.0009 | 0.0082 | -0.0009 | -0.0068 | -360.1404 | 17.5301 | -360.6235 | 17.875 | -360.9158 | 18.0865 | -360.9497 | 17.5301 | -352.7921 | 18.7744 | -352.8814 | 16.7971
11:44 | 1430 | 21.9801 | 194.7905 | 435.7004 | 439.1538 | -21.76 | -47.5347 | 1.5018 | -0.1014 | -7.3931 | -7.4118 | -3.3982 | -4.1297 | 2.2536 | -4.4707 | 0.585 | 0.6318 | 0.9475 | 0.6907 | -130.8897 | -6.2865 | 0.152 | -1.5003 | -9.0271 | -7.6085 | -0.5337 |  | -3.0748 | -3.358 | 4.0023 | 3.3694 | 3.3528 | 1.0248 | 10.6203 | 14.1109 | 14.6659 | 11.0201 | -0.0001 | -0.0033 | 0.0007 | 0.0037 | 0.0007 | -0.0001 | 0.0105 | -0.0067 | -0.0094 | -360.1804 | 17.4952 | -360.5435 | 17.8586 | -360.8758 | 18.1132 | -360.9497 | 17.5383 | -352.8229 | 18.7559 | -352.7921 | 16.7786
11:44 | 1431 | 21.985 | 194.7727 | 435.7884 | 439.2584 | -21.7216 | -47.372 | 1.4896 | -0.078 | -7.4156 | -7.3956 | -3.3263 | -4.1302 | 2.263 | -4.4382 | 0.5833 | 0.6328 | 0.9503 | 0.6929 | -130.9103 | -6.241 | 0.2127 | -1.5193 | -8.9934 | -7.6201 | -0.5307 |  | -3.0394 | -3.4036 | 4.0021 | 3.3661 | 3.3538 | 1.0238 | 10.6169 | 14.0553 | 14.7023 | 10.9995 | 0.0003 | -0.003 | 0.0005 | 0.004 | 0.0011 | -0.0008 | 0.0178 | 0.0013 | 0.0153 | -360.245 | 17.5116 | -360.5435 | 17.8483 | -360.9066 | 18.1029 | -361.0081 | 17.5917 | -352.8814 | 18.7661 | -352.7983 | 16.7724
11:44 | 1432 | 22.0141 | 194.8493 | 435.7681 | 439.2701 | -21.6605 | -47.3752 | 1.48 | -0.1061 | -7.4334 | -7.4179 | -3.3927 | -4.166 | 2.3691 | -4.321 | 0.5824 | 0.6309 | 0.9468 | 0.6926 | -130.8994 | -6.2006 | 0.3366 | -1.5246 | -9.0004 | -7.6507 | -0.5208 |  | -3.0348 | -3.3673 | 4.0002 | 3.3663 | 3.3491 | 1.0249 | 10.6066 | 14.0966 | 14.6842 | 11.0014 | -0.0006 | -0.0029 | 0.0008 | 0.0032 | 0.0001 | -0.0004 | 0.0276 | -0.0093 | 0.0076 | -360.1835 | 17.5137 | -360.5466 | 17.8319 | -360.8389 | 18.0886 | -360.9497 | 17.5568 | -352.8506 | 18.7682 | -352.8044 | 16.7601
11:44 | 1433 | 21.9038 | 194.8208 | 435.7255 | 439.3212 | -21.7022 | -47.4454 | 1.4716 | -0.0853 | -7.3959 | -7.3301 | -3.5384 | -4.0607 | 2.3614 | -4.3022 | 0.5828 | 0.6346 | 0.9458 | 0.6927 | -130.9621 | -6.1981 | 0.3064 | -1.5471 | -8.954 | -7.6446 | -0.5424 |  | -3.088 | -3.3667 | 4.0005 | 3.3679 | 3.3496 | 1.0246 | 10.6144 | 14.0996 | 14.6796 | 11.0136 | 0 | -0.0024 | 0.0002 | 0.003 | 0.0006 | -0.0008 | 0.0071 | -0.0112 | -0.0272 | -360.2111 | 17.5342 | -360.6112 | 17.8853 | -360.9343 | 18.0865 | -360.9897 | 17.5568 | -352.829 | 18.7744 | -352.8629 | 16.8012
11:44 | 1434 | 21.8741 | 194.7739 | 435.8211 | 439.3321 | -21.7525 | -47.2693 | 1.4834 | -0.0795 | -7.336 | -7.3388 | -3.5528 | -4.0609 | 2.3495 | -4.3356 | 0.5841 | 0.6367 | 0.9485 | 0.6953 | -130.9789 | -6.2264 | 0.3429 | -1.5446 | -8.993 | -7.6486 | -0.5519 |  | -3.0774 | -3.46 | 4.0028 | 3.368 | 3.3521 | 1.0244 | 10.6226 | 14.1073 | 14.6965 | 11.0111 | -0.0001 | -0.0029 | 0.0007 | 0.0034 | 0.0004 | -0.0007 | 0.0026 | 0.0038 | -0.0056 | -360.1065 | 17.4993 | -360.5835 | 17.8709 | -360.9435 | 18.0988 | -360.9251 | 17.5342 | -352.789 | 18.7395 | -352.8198 | 16.8074
11:44 | 1435 | 21.9552 | 194.7862 | 435.7579 | 439.3492 | -21.7405 | -47.3064 | 1.4068 | -0.0683 | -7.3456 | -7.4 | -3.5184 | -4.1593 | 2.3197 | -4.42 | 0.5841 | 0.637 | 0.9477 | 0.6937 | -130.9126 | -6.2952 | 0.3339 | -1.512 | -8.9933 | -7.5104 | -0.5368 |  | -2.9726 | -3.3047 | 4.0012 | 3.3672 | 3.352 | 1.0237 | 10.6306 | 14.0753 | 14.684 | 11.0298 | 0.0005 | -0.0024 | 0.0006 | 0.0037 | 0.0001 | -0.0008 | 0.016 | -0.0168 | -0.0156 | -360.2173 | 17.5075 | -360.5743 | 17.873 | -360.9589 | 18.1235 | -360.9712 | 17.565 | -352.829 | 18.76 | -352.866 | 16.795
11:44 | 1436 | 22.0198 | 194.7395 | 435.712 | 439.3427 | -21.656 | -47.3804 | 1.5065 | -0.0516 | -7.3038 | -7.2425 | -3.5132 | -4.2729 | 2.3005 | -4.377 | 0.5843 | 0.6341 | 0.9496 | 0.6942 | -130.8756 | -6.2295 | 0.416 | -1.4834 | -8.8855 | -7.5724 | -0.4923 |  | -3.0088 | -3.3774 | 4.0022 | 3.3712 | 3.352 | 1.0229 | 10.641 | 14.1262 | 14.701 | 11.0052 | -0.0002 | -0.003 | 0.0008 | 0.004 | 0.0005 | -0.0009 | 0.0111 | 0.0099 | 0.0046 | -360.1558 | 17.5157 | -360.5496 | 17.8319 | -360.8666 | 18.0742 | -360.962 | 17.5835 | -352.8167 | 18.7641 | -352.8106 | 16.7642
11:44 | 1437 | 21.9822 | 194.7795 | 435.7476 | 439.3336 | -21.6993 | -47.2836 | 1.5439 | -0.0819 | -7.3869 | -7.3471 | -3.5301 | -4.2 | 2.335 | -4.3917 | 0.584 | 0.6307 | 0.9464 | 0.6925 | -130.8147 | -6.1892 | 0.3533 | -1.5106 | -9.0062 | -7.564 | -0.5503 |  | -2.9462 | -3.2491 | 4.002 | 3.3653 | 3.3524 | 1.0232 | 10.6226 | 14.1132 | 14.7265 | 11.0454 | -0.0008 | -0.0029 | -0.0002 | 0.0037 | 0 | -0.0005 | -0.0097 | -0.0244 | -0.014 | -360.2512 | 17.5465 | -360.6019 | 17.8627 | -360.8758 | 18.0804 | -360.9435 | 17.5896 | -352.8752 | 18.799 | -352.8721 | 16.7848
11:44 | 1438 | 21.9755 | 194.7327 | 435.7625 | 439.3297 | -21.6619 | -47.3171 | 1.7099 | -0.0717 | -7.3504 | -7.3441 | -3.4652 | -4.2671 | 2.2641 | -4.4477 | 0.5847 | 0.636 | 0.9488 | 0.6938 | -130.7673 | -6.1299 | 0.3749 | -1.4654 | -8.8874 | -7.5378 | -0.5043 |  | -3.0185 | -3.3261 | 4.0018 | 3.3636 | 3.3506 | 1.0238 | 10.6122 | 14.0855 | 14.6874 | 11.0176 | -0.0002 | -0.0027 | 0.0006 | 0.004 | 0.0011 | -0.0008 | 0.0103 | -0.0003 | -0.0021 | -360.2081 | 17.5219 | -360.5958 | 17.8668 | -360.8974 | 18.0701 | -360.9497 | 17.5732 | -352.826 | 18.76 | -352.8629 | 16.7848
11:44 | 1439 | 22.0199 | 194.8579 | 435.8033 | 439.3203 | -21.6892 | -47.4019 | 1.5451 | -0.0937 | -7.3958 | -7.3019 | -3.4935 | -4.2285 | 2.3261 | -4.5853 | 0.583 | 0.6325 | 0.9473 | 0.6946 | -130.8102 | -6.1664 | 0.3925 | -1.497 | -8.9025 | -7.5852 | -0.5129 |  | -3.0383 | -3.3596 | 4.0033 | 3.3641 | 3.3533 | 1.0235 | 10.617 | 14.0839 | 14.7002 | 10.9945 | -0.0002 | -0.0035 | -0.0001 | 0.0029 | 0.0001 | -0.0008 | 0.0027 | 0.0063 | -0.0239 | -360.125 | 17.4972 | -360.5589 | 17.8607 | -360.9189 | 18.1112 | -360.9712 | 17.5629 | -352.8383 | 18.7415 | -352.8044 | 16.7868
11:44 | 1440 | 21.9725 | 194.7595 | 435.8529 | 439.3376 | -21.6348 | -47.295 | 1.5034 | -0.0824 | -7.4526 | -7.3511 | -3.5356 | -4.2517 | 2.3058 | -4.5428 | 0.5845 | 0.6315 | 0.9454 | 0.6941 | -130.891 | -6.2954 | 0.4199 | -1.3738 | -8.72 | -7.4778 | -0.4057 |  | -3.0413 | -3.4128 | 4.0016 | 3.3661 | 3.3499 | 1.0238 | 10.6215 | 14.1003 | 14.6778 | 10.9984 | -0.0003 | -0.0032 | 0.0002 | 0.0035 | 0.0008 | -0.0005 | -0.0017 | -0.001 | -0.014 | -360.1773 | 17.4972 | -360.5496 | 17.8504 | -360.9066 | 18.1173 | -361.0297 | 17.5917 | -352.829 | 18.7251 | -352.8075 | 16.7724
11:44 | 1441 | 21.9779 | 194.7656 | 435.8737 | 439.3706 | -21.6849 | -47.2671 | 1.5401 | -0.119 | -7.3403 | -7.2142 | -3.5085 | -4.2609 | 2.3606 | -4.5361 | 0.5827 | 0.6329 | 0.9487 | 0.6934 | -130.9081 | -6.2608 | 0.3132 | -1.4073 | -8.7687 | -7.4473 | -0.4302 |  | -2.9299 | -3.3566 | 4.0028 | 3.367 | 3.349 | 1.0244 | 10.6192 | 14.0864 | 14.6808 | 11.0194 | -0.0006 | -0.0032 | 0.0009 | 0.0033 | 0.0004 | -0.0008 | 0.0072 | -0.0122 | -0.007 | -360.165 | 17.5157 | -360.565 | 17.8381 | -360.8758 | 18.0804 | -360.9374 | 17.5753 | -352.8198 | 18.7559 | -352.8444 | 16.7766
11:44 | 1442 | 22.0688 | 194.7736 | 435.9196 | 439.5707 | -21.7119 | -47.2177 | 1.504 | -0.0397 | -7.362 | -7.1995 | -3.415 | -4.2314 | 2.3317 | -4.451 | 0.5834 | 0.6331 | 0.9506 | 0.6947 | -130.8813 | -6.2973 | 0.3385 | -1.3873 | -8.7898 | -7.4627 | -0.4084 |  | -3.0162 | -3.4742 | 4.0022 | 3.3644 | 3.3464 | 1.0238 | 10.5902 | 14.0865 | 14.6761 | 11.0248 | -0.0002 | -0.0027 | 0.0008 | 0.0039 | 0.0008 | -0.0001 | 0.0107 | -0.0161 | -0.0091 | -360.1958 | 17.526 | -360.6235 | 17.8997 | -360.9435 | 18.0906 | -360.9343 | 17.5629 | -352.8383 | 18.7661 | -352.8691 | 16.8135
11:44 | 1443 | 21.9881 | 194.8483 | 435.8427 | 439.5116 | -21.6819 | -47.333 | 1.5651 | -0.0503 | -7.3381 | -7.1498 | -3.3776 | -4.2571 | 2.293 | -4.4912 | 0.5839 | 0.6331 | 0.9506 | 0.6929 | -130.8699 | -6.1796 | 0.3877 | -1.4222 | -8.773 | -7.4601 | -0.4001 |  | -2.9779 | -3.4888 | 4.001 | 3.3683 | 3.3519 | 1.0234 | 10.6121 | 14.0972 | 14.7 | 11.0114 | 0.0002 | -0.0029 | 0.0009 | 0.0038 | 0.0007 | -0.0004 | 0.0033 | -0.0091 | -0.0269 | -360.165 | 17.5198 | -360.5989 | 17.8648 | -360.882 | 18.0947 | -360.9343 | 17.5486 | -352.7675 | 18.7436 | -352.8414 | 16.7848
11:44 | 1444 | 22.0497 | 194.8323 | 435.8573 | 439.6213 | -21.6885 | -47.2313 | 1.5512 | -0.1735 | -7.3062 | -7.2437 | -3.4014 | -4.1932 | 2.3032 | -4.5143 | 0.583 | 0.6332 | 0.9518 | 0.6928 | -130.8311 | -6.2634 | 0.408 | -1.4547 | -8.8021 | -7.5864 | -0.4249 |  | -3.0347 | -3.4317 | 4.0026 | 3.3654 | 3.3517 | 1.0234 | 10.6375 | 14.0997 | 14.6864 | 11.0132 | -0.0002 | -0.0034 | 0.0008 | 0.0037 | 0.0005 | -0.0002 | -0.0006 | -0.006 | -0.0148 | -360.2296 | 17.5157 | -360.5804 | 17.873 | -360.9127 | 18.1112 | -361.0143 | 17.6061 | -352.8506 | 18.7374 | -352.8198 | 16.8012
11:44 | 1445 | 22.0792 | 194.8664 | 435.8413 | 439.6638 | -21.7165 | -47.2371 | 1.5246 | -0.1681 | -7.3392 | -7.2911 | -3.4204 | -4.1408 | 2.2714 | -4.4926 | 0.5835 | 0.6308 | 0.9512 | 0.6943 | -130.8397 | -6.2605 | 0.3577 | -1.4104 | -8.8355 | -7.4981 | -0.4033 |  | -3.0079 | -3.4499 | 4.0005 | 3.3672 | 3.3502 | 1.0226 | 10.6433 | 14.1169 | 14.749 | 11.0367 | -0.0002 | -0.0027 | 0.0004 | 0.0036 | 0.0008 | -0.0009 | 0.0231 | -0.0138 | -0.0032 | -360.2111 | 17.5198 | -360.5681 | 17.8299 | -360.8635 | 18.0947 | -360.9743 | 17.5855 | -352.8567 | 18.7497 | -352.8106 | 16.756
11:44 | 1446 | 22.0979 | 194.8253 | 435.9391 | 439.7451 | -21.6587 | -47.1736 | 1.5721 | -0.1513 | -7.3763 | -7.1494 | -3.5248 | -4.2343 | 2.2446 | -4.5428 | 0.5844 | 0.6295 | 0.9502 | 0.6931 | -130.8107 | -6.1884 | 0.3376 | -1.3674 | -8.7773 | -7.4452 | -0.3873 |  | -2.9634 | -3.3977 | 4.0016 | 3.3687 | 3.3527 | 1.0243 | 10.6389 | 14.0888 | 14.6952 | 11.0273 | -0.0008 | -0.0032 | 0.0006 | 0.0041 | 0 | -0.0009 | 0.0122 | -0.0137 | -0.0125 | -360.2481 | 17.5301 | -360.5743 | 17.8607 | -360.8912 | 18.0906 | -360.9435 | 17.5773 | -352.8598 | 18.7579 | -352.8229 | 16.795
11:44 | 1447 | 22.1225 | 194.8616 | 435.9348 | 439.7134 | -21.7391 | -47.202 | 1.483 | -0.1062 | -7.3313 | -7.1547 | -3.4596 | -4.1538 | 2.3156 | -4.433 | 0.5833 | 0.6305 | 0.9528 | 0.6929 | -130.7979 | -6.1716 | 0.3021 | -1.3628 | -8.8237 | -7.6854 | -0.3707 |  | -2.996 | -3.4466 | 4.0006 | 3.3674 | 3.3503 | 1.024 | 10.626 | 14.1052 | 14.7248 | 10.985 | -0.0001 | -0.0028 | 0.0005 | 0.0035 | 0.001 | -0.0005 | 0.0062 | -0.0199 | -0.0129 | -360.1958 | 17.5013 | -360.605 | 17.8709 | -360.9404 | 18.1153 | -360.9497 | 17.5588 | -352.7829 | 18.7415 | -352.8598 | 16.8032
11:44 | 1448 | 22.0624 | 194.901 | 435.9144 | 439.661 | -21.604 | -47.1205 | 1.5957 | -0.0531 | -7.3019 | -7.2863 | -3.4483 | -4.1795 | 2.342 | -4.3356 | 0.583 | 0.6313 | 0.9504 | 0.694 | -130.8633 | -6.2544 | 0.3811 | -1.4402 | -8.7953 | -7.5232 | -0.3599 |  | -3.0876 | -3.3867 | 4.0004 | 3.3696 | 3.3518 | 1.0246 | 10.6422 | 14.0868 | 14.7303 | 11.0182 | 0.0001 | -0.0033 | 0.0009 | 0.0038 | 0.0003 | -0.0004 | 0.0119 | -0.0073 | -0.0115 | -360.1496 | 17.4911 | -360.5281 | 17.8566 | -360.9158 | 18.0947 | -360.9681 | 17.5794 | -352.789 | 18.723 | -352.8106 | 16.7848
11:44 | 1449 | 22.1461 | 194.805 | 435.9786 | 439.7425 | -21.6329 | -47.1837 | 1.6967 | -0.1052 | -7.3534 | -7.2376 | -3.439 | -4.1491 | 2.4085 | -4.4209 | 0.5829 | 0.6354 | 0.9488 | 0.6947 | -130.8841 | -6.2553 | 0.3508 | -1.4298 | -8.7805 | -7.7642 | -0.4099 |  | -3.0187 | -3.4373 | 4.0007 | 3.3664 | 3.349 | 1.0235 | 10.6076 | 14.0576 | 14.6935 | 10.9959 | -0.0001 | -0.0032 | 0.0011 | 0.0038 | 0.0007 | -0.001 | 0.0014 | -0.0135 | -0.0181 | -360.2142 | 17.5383 | -360.565 | 17.8545 | -360.9004 | 18.0988 | -360.9527 | 17.5917 | -352.8475 | 18.7641 | -352.8475 | 16.7745
11:44 | 1450 | 22.0768 | 194.8117 | 435.8101 | 439.8177 | -21.5683 | -47.257 | 1.7123 | -0.1663 | -7.4799 | -7.3287 | -3.4291 | -4.1039 | 2.4121 | -4.4622 | 0.5826 | 0.6319 | 0.9477 | 0.6936 | -130.8113 | -6.2176 | 0.3376 | -1.3666 | -8.6599 | -7.4474 | -0.3071 |  | -3.0368 | -3.4031 | 4.0017 | 3.3669 | 3.3527 | 1.0225 | 10.634 | 14.0846 | 14.6939 | 11.0388 | -0.0001 | -0.0024 | 0.0009 | 0.0037 | 0.0006 | -0.0002 | 0.005 | -0.0047 | -0.0204 | -360.125 | 17.5239 | -360.5835 | 17.8463 | -360.8666 | 18.066 | -360.9251 | 17.5609 | -352.8229 | 18.7559 | -352.8506 | 16.7971
11:44 | 1451 | 22.1365 | 194.9107 | 435.9066 | 439.8347 | -21.6365 | -47.2688 | 1.752 | -0.1521 | -7.4044 | -7.2902 | -3.3933 | -4.1554 | 2.4519 | -4.4168 | 0.5837 | 0.6343 | 0.9511 | 0.6953 | -130.9058 | -6.2516 | 0.3232 | -1.3448 | -8.6865 | -7.5008 | -0.3805 |  | -3.0486 | -3.3509 | 4.0002 | 3.3661 | 3.3548 | 1.0242 | 10.6307 | 14.104 | 14.6772 | 10.9897 | -0.0003 | -0.0026 | 0.0006 | 0.0039 | 0.0003 | -0.0007 | 0.0046 | -0.0161 | 0.0033 | -360.1865 | 17.5137 | -360.6112 | 17.8586 | -360.9251 | 18.1112 | -360.9651 | 17.5835 | -352.8506 | 18.7518 | -352.866 | 16.795
11:44 | 1452 | 22.1944 | 194.9014 | 435.9364 | 439.9114 | -21.6436 | -47.2069 | 1.689 | -0.2105 | -7.4407 | -7.2713 | -3.4545 | -4.1714 | 2.3427 | -4.4758 | 0.5835 | 0.633 | 0.9511 | 0.6958 | -130.9232 | -6.2225 | 0.3169 | -1.3453 | -8.7868 | -7.4809 | -0.4407 |  | -3.0455 | -3.2994 | 4.0009 | 3.3668 | 3.3496 | 1.0229 | 10.611 | 14.1018 | 14.6813 | 10.9988 | 0 | -0.0029 | 0.0006 | 0.0039 | 0.0009 | -0.0003 | 0.0084 | -0.0153 | -0.0082 | -360.1588 | 17.4993 | -360.5496 | 17.834 | -360.8789 | 18.0906 | -360.9589 | 17.5773 | -352.8044 | 18.7189 | -352.7829 | 16.7766
11:44 | 1453 | 22.0359 | 194.8743 | 435.8411 | 439.9069 | -21.6986 | -47.1913 | 1.7214 | -0.1166 | -7.4026 | -7.0898 | -3.4188 | -4.1269 | 2.3527 | -4.4451 | 0.583 | 0.6318 | 0.951 | 0.6938 | -130.8387 | -6.1481 | 0.4702 | -1.3646 | -8.8111 | -7.5717 | -0.4929 |  | -3.0641 | -3.3684 | 4.0024 | 3.3679 | 3.3479 | 1.0234 | 10.6411 | 14.1144 | 14.7163 | 11.0291 | 0.0002 | -0.003 | 0.0002 | 0.0035 | 0.0008 | -0.0001 | 0.003 | -0.0006 | -0.0202 | -360.1958 | 17.526 | -360.5589 | 17.8504 | -360.8881 | 18.1071 | -360.9866 | 17.5876 | -352.8537 | 18.762 | -352.8137 | 16.7786
11:44 | 1454 | 22.1238 | 194.8911 | 435.8323 | 439.8918 | -21.6289 | -47.2516 | 1.7251 | -0.1389 | -7.4444 | -7.2674 | -3.461 | -4.1834 | 2.3292 | -4.4207 | 0.5835 | 0.6283 | 0.9504 | 0.6931 | -130.8358 | -6.1262 | 0.3159 | -1.2844 | -8.7742 | -7.4885 | -0.4576 |  | -3.0432 | -3.443 | 4.0009 | 3.371 | 3.3482 | 1.0246 | 10.6008 | 14.0562 | 14.6263 | 10.9609 | -0.0002 | -0.0028 | 0.0006 | 0.0036 | 0.0003 | -0.0011 | -0.0105 | -0.0209 | -0.0227 | -360.1404 | 17.5034 | -360.5896 | 17.8627 | -360.882 | 18.0886 | -360.9558 | 17.5712 | -352.7952 | 18.7395 | -352.8444 | 16.7848
11:44 | 1455 | 22.1566 | 194.9032 | 435.8727 | 439.9079 | -21.6091 | -47.3121 | 1.6827 | -0.0856 | -7.3703 | -7.336 | -3.497 | -4.0787 | 2.4408 | -4.3898 | 0.5834 | 0.6294 | 0.9498 | 0.693 | -130.8655 | -6.195 | 0.397 | -1.4523 | -8.7646 | -7.4348 | -0.4374 |  | -3.1352 | -3.455 | 4.001 | 3.3676 | 3.3492 | 1.0246 | 10.6041 | 14.1063 | 14.6846 | 10.9923 | -0.0006 | -0.0028 | 0.0006 | 0.0038 | 0.0007 | 0 | 0.0056 | -0.0099 | -0.0122 | -360.1681 | 17.5219 | -360.5804 | 17.8689 | -360.922 | 18.1153 | -360.9589 | 17.5712 | -352.8106 | 18.7456 | -352.8629 | 16.7991
11:44 | 1456 | 22.09 | 194.8718 | 435.9073 | 440.0081 | -21.5947 | -47.1782 | 1.7947 | 0.0014 | -7.291 | -7.2842 | -3.428 | -4.102 | 2.406 | -4.4256 | 0.5838 | 0.6304 | 0.9458 | 0.6927 | -130.8446 | -6.1023 | 0.3994 | -1.5276 | -8.7259 | -7.4651 | -0.4709 |  | -3.0518 | -3.3302 | 4.0017 | 3.3656 | 3.3537 | 1.0233 | 10.5914 | 14.0876 | 14.6938 | 11.0205 | 0 | -0.0031 | 0.0005 | 0.0036 | 0.0009 | -0.0008 | -0.0008 | -0.0166 | -0.0173 | -360.1527 | 17.5055 | -360.565 | 17.8648 | -360.9343 | 18.0968 | -360.9774 | 17.5814 | -352.8014 | 18.7292 | -352.8106 | 16.795
11:44 | 1457 | 22.1027 | 194.9898 | 435.9355 | 440.0513 | -21.5864 | -47.143 | 1.8307 | 0.0005 | -7.3198 | -7.3093 | -3.3474 | -4.1466 | 2.3503 | -4.4204 | 0.5835 | 0.627 | 0.9504 | 0.6928 | -130.8966 | -6.0588 | 0.3449 | -1.5286 | -8.8693 | -7.5041 | -0.4677 |  | -2.9993 | -3.3467 | 4.0031 | 3.3656 | 3.3528 | 1.0241 | 10.6075 | 14.0867 | 14.6829 | 11.0071 | 0.0004 | -0.0027 | 0.0013 | 0.0043 | 0.0004 | -0.0003 | 0.0161 | -0.0074 | -0.0005 | -360.1865 | 17.5157 | -360.5619 | 17.8401 | -360.8666 | 18.0906 | -360.9651 | 17.5712 | -352.8198 | 18.7477 | -352.8414 | 16.7724
11:44 | 1458 | 22.0896 | 194.9399 | 435.9854 | 440.0797 | -21.5807 | -47.1408 | 1.7523 | -0.0784 | -7.337 | -7.3268 | -3.4312 | -4.1059 | 2.4889 | -4.2753 | 0.5835 | 0.6279 | 0.952 | 0.6937 | -130.8635 | -6.0634 | 0.3651 | -1.4594 | -8.8218 | -7.367 | -0.4046 |  | -3.081 | -3.3761 | 4.0025 | 3.3676 | 3.3522 | 1.0233 | 10.6572 | 14.1134 | 14.6928 | 11.0219 | -0.0003 | -0.0028 | 0.0009 | 0.0037 | 0.0009 | -0.0006 | 0.0184 | 0.0014 | 0.0132 | -360.2019 | 17.5342 | -360.5989 | 17.8648 | -360.9127 | 18.0886 | -360.9404 | 17.5835 | -352.8352 | 18.7579 | -352.8721 | 16.7909
11:44 | 1459 | 22.0842 | 194.8966 | 435.9612 | 440.0807 | -21.6105 | -47.1455 | 1.801 | -0.1156 | -7.2533 | -7.3365 | -3.477 | -4.1614 | 2.4404 | -4.2943 | 0.5836 | 0.6289 | 0.9475 | 0.6941 | -130.8578 | -6.1042 | 0.5461 | -1.4434 | -8.7395 | -7.4307 | -0.2579 |  | -3.0458 | -3.3489 | 4.0022 | 3.3676 | 3.3516 | 1.0235 | 10.6411 | 14.1144 | 14.7626 | 11.0522 | -0.0004 | -0.003 | 0.0001 | 0.0033 | 0.0004 | -0.0008 | -0.0023 | -0.0156 | -0.0325 | -360.1896 | 17.5116 | -360.5681 | 17.8483 | -360.882 | 18.0886 | -360.9404 | 17.5712 | -352.8014 | 18.7477 | -352.8506 | 16.7971
11:44 | 1460 | 22.1023 | 194.7121 | 435.7916 | 440.1233 | -21.6851 | -47.1453 | 1.6264 | -0.1748 | -7.2794 | -7.3301 | -3.4835 | -4.2154 | 2.3582 | -4.4335 | 0.5831 | 0.631 | 0.9488 | 0.6951 | -130.8446 | -6.0551 | 0.6064 | -1.4461 | -8.6635 | -7.4023 | -0.3373 |  | -2.9651 | -3.3245 | 4.0002 | 3.3655 | 3.3515 | 1.0243 | 10.6537 | 14.0927 | 14.714 | 11.0468 | 0 | -0.003 | 0.0006 | 0.0036 | 0.0004 | -0.0005 | -0.005 | -0.0194 | -0.0292 | -360.1835 | 17.5137 | -360.5773 | 17.8709 | -360.9251 | 18.1153 | -360.9497 | 17.5814 | -352.8137 | 18.7436 | -352.8167 | 16.7991
11:44 | 1461 | 22.1687 | 194.8625 | 435.8783 | 440.1336 | -21.6588 | -47.1199 | 1.664 | -0.2016 | -7.3124 | -7.3776 | -3.4897 | -4.1979 | 2.496 | -4.4245 | 0.5828 | 0.631 | 0.9485 | 0.6937 | -130.8084 | -6.019 | 0.4931 | -1.439 | -8.6344 | -7.4088 | -0.2933 |  | -2.9184 | -3.299 | 4.0005 | 3.3651 | 3.3514 | 1.0225 | 10.6504 | 14.1063 | 14.7194 | 11.0096 | -0.0004 | -0.0033 | 0.0004 | 0.0035 | 0.001 | -0.0007 | 0.002 | -0.01 | -0.0074 | -360.1435 | 17.5096 | -360.5558 | 17.8422 | -360.8727 | 18.0927 | -360.9589 | 17.5712 | -352.8044 | 18.7395 | -352.8321 | 16.7642
11:44 | 1462 | 22.2133 | 194.934 | 435.9037 | 440.2198 | -21.6937 | -47.1194 | 1.7053 | -0.1228 | -7.1864 | -7.2891 | -3.241 | -4.2364 | 2.5002 | -4.3749 | 0.5839 | 0.6274 | 0.947 | 0.6942 | -130.9153 | -6.0666 | 0.6014 | -1.3772 | -8.5807 | -7.3526 | -0.2575 |  | -2.9437 | -3.313 | 4.0008 | 3.3647 | 3.3534 | 1.0245 | 10.6089 | 14.0815 | 14.7033 | 11.0155 | -0.0002 | -0.0032 | 0.0004 | 0.0037 | 0.0003 | -0.0007 | 0.0074 | -0.0049 | -0.0223 | -360.2142 | 17.5198 | -360.5773 | 17.8648 | -360.8974 | 18.0947 | -360.962 | 17.5896 | -352.8321 | 18.762 | -352.8475 | 16.7848
11:44 | 1463 | 22.2242 | 194.8908 | 435.8804 | 440.3643 | -21.6905 | -47.2046 | 1.6693 | -0.1367 | -7.1995 | -7.3348 | -3.2713 | -4.1709 | 2.4178 | -4.4124 | 0.5834 | 0.63 | 0.9522 | 0.693 | -130.8472 | -6.1833 | 0.5061 | -1.3554 | -8.6328 | -7.3809 | -0.2289 |  | -2.9351 | -3.3013 | 4.0001 | 3.3669 | 3.3521 | 1.0237 | 10.6167 | 14.0902 | 14.7044 | 11.0103 | -0.0006 | -0.0029 | 0.0008 | 0.0042 | 0.0012 | -0.0008 | 0.0158 | 0.0002 | 0.0025 | -360.1742 | 17.5013 | -360.5743 | 17.8586 | -360.8697 | 18.0906 | -360.9558 | 17.5527 | -352.7983 | 18.7415 | -352.7983 | 16.7909
11:44 | 1464 | 22.2498 | 194.9187 | 435.9251 | 440.3346 | -21.6602 | -47.1611 | 1.5895 | -0.1288 | -7.1973 | -7.307 | -3.4028 | -4.0933 | 2.469 | -4.4255 | 0.5827 | 0.633 | 0.9484 | 0.6927 | -130.9869 | -6.2184 | 0.4219 | -1.1743 | -8.6502 | -7.3881 | -0.2589 |  | -2.8653 | -3.2681 | 4.0002 | 3.3632 | 3.3512 | 1.0251 | 10.6342 | 14.1015 | 14.7081 | 11.04 | -0.0004 | -0.0029 | 0.0005 | 0.0039 | 0.0003 | -0.0006 | 0.0177 | -0.0039 | 0.0041 | -360.205 | 17.5178 | -360.5866 | 17.8771 | -360.9281 | 18.1112 | -360.9835 | 17.5773 | -352.8229 | 18.7518 | -352.8629 | 16.8012
11:44 | 1465 | 22.2233 | 194.8376 | 435.9054 | 440.3417 | -21.5761 | -47.224 | 1.5546 | -0.0611 | -7.2068 | -7.1736 | -3.3522 | -4.1098 | 2.4039 | -4.4697 | 0.5835 | 0.6328 | 0.9491 | 0.6934 | -130.923 | -6.1333 | 0.5637 | -1.2487 | -8.7587 | -7.3987 | -0.2911 |  | -2.9055 | -3.257 | 4.0013 | 3.3645 | 3.3525 | 1.0259 | 10.6168 | 14.1017 | 14.686 | 11.0222 | 0 | -0.0036 | 0.0009 | 0.004 | 0.0006 | -0.0006 | -0.0029 | -0.0146 | -0.0154 | -360.1496 | 17.5055 | -360.5343 | 17.8381 | -360.8697 | 18.0886 | -360.9835 | 17.5753 | -352.7675 | 18.7477 | -352.8075 | 16.7704
11:44 | 1466 | 22.1403 | 194.8281 | 435.9657 | 440.4058 | -21.5886 | -47.1708 | 1.7318 | 0.0155 | -7.2855 | -7.2698 | -3.3678 | -4.0001 | 2.447 | -4.4062 | 0.582 | 0.6293 | 0.9489 | 0.6911 | -130.9275 | -6.1008 | 0.5202 | -1.2299 | -8.7191 | -7.3661 | -0.2452 |  | -2.928 | -3.2692 | 4.0014 | 3.3698 | 3.354 | 1.0271 | 10.6398 | 14.0788 | 14.7055 | 11.0446 | 0.0002 | -0.0029 | 0.0005 | 0.0033 | 0.0005 | -0.0001 | 0.0049 | -0.0125 | -0.016 | -360.2388 | 17.5137 | -360.5835 | 17.8545 | -360.8943 | 18.0968 | -360.9712 | 17.5773 | -352.8321 | 18.762 | -352.8414 | 16.7827
11:44 | 1467 | 22.3183 | 194.9589 | 435.9668 | 440.442 | -21.5981 | -47.2079 | 1.6947 | -0.01 | -7.2538 | -7.3224 | -3.347 | -3.96 | 2.3777 | -4.4188 | 0.5833 | 0.6321 | 0.9477 | 0.6923 | -130.9128 | -6.09 | 0.4771 | -1.2136 | -8.7202 | -7.3529 | -0.2407 |  | -2.9156 | -3.2755 | 4.0002 | 3.3658 | 3.354 | 1.0269 | 10.6457 | 14.1537 | 14.7555 | 11.0454 | -0.0006 | -0.0032 | 0.0004 | 0.0034 | 0.0004 | -0.0007 | 0.0086 | -0.013 | -0.0156 | -360.1865 | 17.5116 | -360.5773 | 17.8504 | -360.8758 | 18.0865 | -360.9558 | 17.5814 | -352.8167 | 18.7456 | -352.8567 | 16.7827
11:44 | 1468 | 22.2637 | 194.8351 | 435.9288 | 440.4672 | -21.6019 | -47.2027 | 1.61 | -0.0771 | -7.1976 | -7.3133 | -3.2938 | -4.1037 | 2.3469 | -4.4447 | 0.5842 | 0.6331 | 0.9538 | 0.6931 | -130.8348 | -5.9926 | 0.5169 | -1.3043 | -8.7293 | -7.4887 | -0.2371 |  | -2.994 | -3.2451 | 3.9997 | 3.3692 | 3.3506 | 1.0255 | 10.6179 | 14.0914 | 14.7 | 11.0403 | -0.0004 | -0.0029 | 0.0009 | 0.0038 | 0.0005 | -0.0005 | 0.0115 | -0.0194 | -0.0057 | -360.205 | 17.5178 | -360.5558 | 17.8566 | -360.922 | 18.105 | -360.9804 | 17.5671 | -352.8167 | 18.76 | -352.8383 | 16.7848
11:44 | 1469 | 22.2734 | 195.0193 | 436.0474 | 440.6032 | -21.6458 | -47.2898 | 1.6223 | -0.0526 | -7.2943 | -7.4188 | -3.345 | -4.0604 | 2.3522 | -4.4748 | 0.5831 | 0.6341 | 0.9457 | 0.6919 | -130.8559 | -6.0207 | 0.4735 | -1.3977 | -8.7649 | -7.3812 | -0.2851 |  | -2.9888 | -3.3148 | 4.002 | 3.368 | 3.3538 | 1.0262 | 10.6653 | 14.1332 | 14.7256 | 11.041 | -0.0001 | -0.0031 | 0.0003 | 0.0032 | 0.0008 | -0.0006 | -0.0024 | -0.0149 | -0.0323 | -360.1681 | 17.4972 | -360.5589 | 17.8586 | -360.9127 | 18.1153 | -360.9989 | 17.5876 | -352.789 | 18.7271 | -352.8352 | 16.7889
11:44 | 1470 | 22.1976 | 194.8724 | 435.8944 | 440.4581 | -21.6554 | -47.164 | 1.746 | -0.0323 | -7.2553 | -7.2957 | -3.2866 | -4.1486 | 2.4488 | -4.3606 | 0.5839 | 0.6345 | 0.9493 | 0.6936 | -130.8689 | -5.9646 | 0.4678 | -1.2502 | -8.6944 | -7.3776 | -0.2195 |  | -2.9603 | -3.2968 | 4.0012 | 3.3666 | 3.3485 | 1.0253 | 10.6088 | 14.0934 | 14.6938 | 11.0031 | -0.0001 | -0.0032 | 0.0007 | 0.0038 | 0.001 | -0.0006 | -0.0047 | -0.0092 | -0.0316 | -360.1742 | 17.5096 | -360.5681 | 17.8586 | -360.9097 | 18.0968 | -360.9466 | 17.5732 | -352.8014 | 18.7497 | -352.826 | 16.7868
11:44 | 1471 | 22.2344 | 194.9351 | 435.8431 | 440.57 | -21.5688 | -47.2207 | 1.763 | 0.0105 | -7.1773 | -7.316 | -3.2658 | -4.0966 | 2.388 | -4.3708 | 0.5843 | 0.6346 | 0.9501 | 0.6947 | -130.8225 | -5.9011 | 0.5639 | -1.1738 | -8.6495 | -7.4039 | -0.2351 |  | -2.9741 | -3.3304 | 4.0018 | 3.3646 | 3.355 | 1.0248 | 10.6202 | 14.0938 | 14.6622 | 11.002 | -0.0002 | -0.0028 | 0.0008 | 0.0043 | -0.0001 | -0.0006 | 0.0008 | -0.0041 | -0.0021 | -360.2111 | 17.5301 | -360.605 | 17.8586 | -360.9189 | 18.0968 | -360.9435 | 17.5855 | -352.8352 | 18.7538 | -352.8321 | 16.7889
11:44 | 1472 | 22.2196 | 194.8925 | 435.9515 | 440.4929 | -21.5782 | -47.1849 | 1.8048 | 0.0282 | -7.2629 | -7.359 | -3.3052 | -4.135 | 2.4246 | -4.3786 | 0.5852 | 0.6309 | 0.9519 | 0.694 | -130.8223 | -5.8882 | 0.5995 | -1.2183 | -8.6831 | -7.3168 | -0.1788 |  | -2.9359 | -3.3415 | 3.9997 | 3.366 | 3.3494 | 1.0253 | 10.6365 | 14.0576 | 14.6761 | 11.0132 | -0.0003 | -0.0027 | 0.0004 | 0.0039 | 0.0008 | -0.0009 | 0.0118 | -0.0036 | -0.0107 | -360.1311 | 17.5198 | -360.5773 | 17.8483 | -360.882 | 18.0783 | -360.9343 | 17.5568 | -352.7921 | 18.7579 | -352.8321 | 16.7909
11:44 | 1473 | 22.1937 | 194.9226 | 435.9557 | 440.6141 | -21.5648 | -47.1229 | 1.7522 | 0.0867 | -7.1881 | -7.2977 | -3.2374 | -4.1287 | 2.4321 | -4.3796 | 0.5849 | 0.6359 | 0.9503 | 0.6932 | -130.8992 | -5.9073 | 0.5868 | -1.3101 | -8.6842 | -7.4083 | -0.2382 |  | -2.833 | -3.3027 | 4.0023 | 3.3671 | 3.351 | 1.0257 | 10.641 | 14.1203 | 14.6884 | 11.0114 | -0.0001 | -0.0028 | 0.0009 | 0.0043 | 0 | -0.0004 | 0.009 | -0.0155 | -0.0116 | -360.1835 | 17.5301 | -360.5466 | 17.8566 | -360.9189 | 18.105 | -360.962 | 17.5691 | -352.8352 | 18.7456 | -352.8506 | 16.7991
11:44 | 1474 | 22.2892 | 194.938 | 435.9877 | 440.5466 | -21.5791 | -47.1316 | 1.7541 | 0.1615 | -7.187 | -7.2284 | -3.1856 | -4.0408 | 2.4033 | -4.3127 | 0.5846 | 0.6282 | 0.9545 | 0.6942 | -130.8821 | -5.8988 | 0.6839 | -1.2725 | -8.728 | -7.4995 | -0.3749 |  | -2.8473 | -3.2661 | 4.0009 | 3.3666 | 3.349 | 1.0253 | 10.6351 | 14.1034 | 14.7032 | 11.0507 | 0.0006 | -0.0028 | 0.0007 | 0.0039 | 0.0013 | -0.0005 | 0.0076 | -0.014 | -0.0147 | -360.1742 | 17.4931 | -360.5404 | 17.8237 | -360.8727 | 18.0886 | -360.9558 | 17.5855 | -352.7829 | 18.7251 | -352.8229 | 16.7745
11:44 | 1475 | 22.2646 | 195.0386 | 435.9538 | 440.5662 | -21.5679 | -47.0425 | 1.6285 | 0.1428 | -7.2651 | -7.2611 | -3.2294 | -4.1144 | 2.3783 | -4.4451 | 0.5841 | 0.6317 | 0.9543 | 0.6947 | -130.8126 | -5.8207 | 0.685 | -1.2542 | -8.6198 | -7.4619 | -0.3652 |  | -2.857 | -3.1835 | 4.0032 | 3.3674 | 3.35 | 1.0253 | 10.5984 | 14.0944 | 14.6825 | 10.9988 | -0.0004 | -0.0033 | -0.0002 | 0.0033 | 0.0007 | -0.0001 | 0.0004 | -0.0046 | -0.0211 | -360.2173 | 17.5321 | -360.5712 | 17.8278 | -360.8943 | 18.105 | -360.9804 | 17.5999 | -352.8414 | 18.7641 | -352.829 | 16.7766
11:44 | 1476 | 22.2991 | 195.0807 | 435.9837 | 440.5395 | -21.5476 | -47.0783 | 1.6618 | 0.1368 | -7.2471 | -7.2473 | -3.1279 | -4.0944 | 2.3602 | -4.4604 | 0.5842 | 0.6305 | 0.9534 | 0.694 | -130.8023 | -5.8792 | 0.6566 | -1.2048 | -8.5794 | -7.4453 | -0.2967 |  | -2.822 | -3.2143 | 4.0028 | 3.3655 | 3.3525 | 1.0262 | 10.6179 | 14.0856 | 14.7058 | 11.0345 | -0.0001 | -0.0023 | 0.0007 | 0.0036 | 0.0006 | -0.0008 | -0.0035 | -0.0148 | -0.0223 | -360.1835 | 17.5034 | -360.5804 | 17.8299 | -360.8635 | 18.0824 | -360.9189 | 17.5691 | -352.8137 | 18.7538 | -352.8229 | 16.7827
11:44 | 1477 | 22.2827 | 195.0861 | 436.0335 | 440.5795 | -21.5541 | -47.1319 | 1.6547 | 0.1136 | -7.2075 | -7.2407 | -3.0991 | -4.1115 | 2.4675 | -4.4108 | 0.5835 | 0.6306 | 0.9491 | 0.6924 | -130.8382 | -5.8162 | 0.5823 | -1.2317 | -8.5797 | -7.3348 | -0.3357 |  | -2.754 | -3.1532 | 4.0006 | 3.3643 | 3.3513 | 1.0256 | 10.6064 | 14.0969 | 14.6747 | 11.0295 | -0.0003 | -0.0028 | 0.0004 | 0.0033 | 0.0003 | -0.0008 | 0.0055 | -0.0097 | -0.0112 | -360.1896 | 17.5198 | -360.6081 | 17.8566 | -360.9312 | 18.1009 | -360.9681 | 17.5794 | -352.7983 | 18.7559 | -352.8937 | 16.8012
11:44 | 1478 | 22.3388 | 195.0907 | 436.0235 | 440.5693 | -21.3669 | -46.9298 | 1.8765 | 0.0498 | -7.2592 | -7.1503 | -3.1872 | -4.163 | 2.4393 | -4.4497 | 0.5848 | 0.6322 | 0.9501 | 0.694 | -130.7645 | -5.8058 | 0.5811 | -1.2581 | -8.5119 | -7.3155 | -0.2218 |  | -2.7871 | -3.1894 | 4.0002 | 3.3632 | 3.3497 | 1.0237 | 10.6065 | 14.0737 | 14.6795 | 10.9952 | 0.0002 | -0.0028 | 0.0005 | 0.0036 | 0.0006 | -0.0006 | -0.0034 | -0.018 | -0.0293 | -360.1188 | 17.4829 | -360.5373 | 17.8401 | -360.9035 | 18.0865 | -360.9527 | 17.5486 | -352.7614 | 18.721 | -352.8198 | 16.793
11:44 | 1479 | 22.2349 | 195.0401 | 436.0488 | 440.5876 | -21.3458 | -46.9406 | 1.8458 | 0.1359 | -7.2657 | -7.2002 | -3.1817 | -4.0956 | 2.4041 | -4.3865 | 0.5838 | 0.6312 | 0.9513 | 0.6928 | -130.8548 | -5.8615 | 0.5094 | -1.3152 | -8.5255 | -7.437 | -0.3383 |  | -2.8297 | -3.2225 | 4.0012 | 3.3653 | 3.3509 | 1.0249 | 10.6249 | 14.0923 | 14.7108 | 11.019 | 0 | -0.0033 | 0.0014 | 0.0046 | 0.0008 | -0.0012 | 0.0069 | -0.0148 | 0.0072 | -360.1865 | 17.5178 | -360.5804 | 17.8463 | -360.9374 | 18.0845 | -360.9743 | 17.5917 | -352.8137 | 18.7415 | -352.8321 | 16.8074
11:44 | 1480 | 22.2587 | 195.0093 | 436.043 | 440.5439 | -21.3443 | -46.9528 | 1.9145 | 0.1541 | -7.2386 | -7.2503 | -3.2305 | -4.0138 | 2.4109 | -4.4194 | 0.5856 | 0.6325 | 0.948 | 0.693 | -130.8324 | -5.8422 | 0.5752 | -1.4038 | -8.4856 | -7.3008 | -0.1798 |  | -2.8993 | -3.3242 | 4.0017 | 3.3665 | 3.3533 | 1.0248 | 10.6284 | 14.1074 | 14.7091 | 11.028 | -0.0004 | -0.0029 | 0.0002 | 0.0037 | 0.0002 | -0.0004 | 0.01 | -0.0132 | -0.0041 | -360.205 | 17.5178 | -360.5743 | 17.7991 | -360.845 | 18.068 | -360.9558 | 17.5671 | -352.8106 | 18.7538 | -352.826 | 16.7683
11:44 | 1481 | 22.2402 | 194.915 | 435.9663 | 440.5622 | -21.3714 | -46.9012 | 1.8539 | 0.1559 | -7.2544 | -7.2257 | -3.1324 | -4.0776 | 2.4163 | -4.5365 | 0.5853 | 0.6327 | 0.9495 | 0.6944 | -130.8359 | -5.8355 | 0.57 | -1.2434 | -8.4812 | -7.2431 | -0.2367 |  | -2.8817 | -3.2694 | 4.0017 | 3.3644 | 3.3503 | 1.0251 | 10.6421 | 14.1043 | 14.7314 | 11.0236 | -0.0003 | -0.0028 | 0.0009 | 0.004 | 0.0012 | -0.0005 | 0.0142 | -0.0032 | -0.012 | -360.2358 | 17.5363 | -360.5927 | 17.8607 | -360.9189 | 18.0598 | -360.9466 | 17.5835 | -352.8598 | 18.7682 | -352.8998 | 16.8053
11:44 | 1482 | 22.2523 | 194.9402 | 435.9629 | 440.5082 | -21.3499 | -46.8812 | 1.9389 | 0.1561 | -7.2296 | -7.2365 | -3.1159 | -4.0907 | 2.3919 | -4.44 | 0.5837 | 0.6296 | 0.9504 | 0.6933 | -130.8011 | -5.931 | 0.5393 | -1.2572 | -8.3955 | -7.2423 | -0.2164 |  | -2.8967 | -3.3804 | 4.0012 | 3.3678 | 3.3541 | 1.0245 | 10.6237 | 14.0913 | 14.7047 | 11.0118 | -0.0002 | -0.0032 | 0.0011 | 0.004 | 0.0001 | -0.0007 | 0.0202 | 0.0085 | -0.0178 | -360.1619 | 17.5013 | -360.5589 | 17.8381 | -360.9097 | 18.0721 | -360.9743 | 17.5629 | -352.7429 | 18.7312 | -352.8414 | 16.7827
11:44 | 1483 | 22.2274 | 194.97 | 435.945 | 440.543 | -21.4525 | -46.8735 | 1.8035 | 0.1387 | -7.2144 | -7.2818 | -3.1301 | -4.0594 | 2.4078 | -4.3601 | 0.5852 | 0.6295 | 0.9479 | 0.6931 | -130.8369 | -5.9265 | 0.5921 | -1.2922 | -8.3278 | -7.2435 | -0.1905 |  | -2.8807 | -3.3081 | 4.0015 | 3.3705 | 3.3559 | 1.0267 | 10.6307 | 14.0982 | 14.7235 | 11.0533 | 0.0001 | -0.0032 | 0.0007 | 0.003 | 0.0009 | -0.0006 | 0.0042 | -0.0076 | -0.0188 | -360.2265 | 17.4993 | -360.5466 | 17.836 | -360.922 | 18.1029 | -360.9897 | 17.5958 | -352.8537 | 18.7395 | -352.7921 | 16.7909
11:44 | 1484 | 22.2508 | 194.9017 | 436.0053 | 440.5478 | -21.4458 | -46.8953 | 1.7964 | 0.1915 | -7.259 | -7.194 | -3.1058 | -4.1512 | 2.3437 | -4.4125 | 0.5845 | 0.6317 | 0.9474 | 0.6954 | -130.8028 | -5.9511 | 0.5986 | -1.3691 | -8.345 | -7.2368 | -0.2041 |  | -2.9357 | -3.3529 | 4.0009 | 3.3677 | 3.3527 | 1.0255 | 10.6066 | 14.0851 | 14.6726 | 10.9956 | -0.0001 | -0.0032 | 0.0006 | 0.0037 | 0 | -0.0005 | 0.0089 | 0.0005 | -0.0064 | -360.1681 | 17.4972 | -360.5373 | 17.8052 | -360.8297 | 18.0845 | -360.9927 | 17.5835 | -352.8198 | 18.7271 | -352.786 | 16.7622
11:44 | 1485 | 22.2748 | 194.9644 | 436.0384 | 440.6685 | -21.4165 | -46.8111 | 1.783 | 0.1243 | -7.2538 | -7.2464 | -3.1316 | -4.1666 | 2.4417 | -4.3267 | 0.5845 | 0.6273 | 0.9474 | 0.6941 | -130.882 | -5.9005 | 0.5891 | -1.3247 | -8.4062 | -7.3343 | -0.2554 |  | -2.8607 | -3.2559 | 4.0011 | 3.3669 | 3.3554 | 1.0258 | 10.5858 | 14.0758 | 14.657 | 10.9924 | -0.0007 | -0.003 | 0.0002 | 0.0033 | 0.0004 | -0.0009 | -0.0003 | -0.0029 | -0.0217 | -360.1865 | 17.5321 | -360.6143 | 17.8278 | -360.9312 | 18.0742 | -360.9374 | 17.5958 | -352.8321 | 18.7641 | -352.8444 | 16.7889
11:44 | 1486 | 22.2895 | 194.9376 | 435.8819 | 440.6546 | -21.4533 | -46.8407 | 1.7346 | 0.1398 | -7.2436 | -7.274 | -3.1359 | -4.2093 | 2.4648 | -4.3794 | 0.5837 | 0.6271 | 0.9476 | 0.6928 | -130.8259 | -5.898 | 0.5796 | -1.4162 | -8.4184 | -7.2302 | -0.2659 |  | -2.8652 | -3.3144 | 4.0015 | 3.3673 | 3.3547 | 1.0263 | 10.6191 | 14.0867 | 14.7003 | 10.9955 | -0.0001 | -0.0026 | 0.0005 | 0.004 | 0.0005 | -0.0008 | 0.0017 | -0.0093 | -0.0133 | -360.1219 | 17.4952 | -360.5527 | 17.836 | -360.9374 | 18.066 | -360.9312 | 17.5588 | -352.7306 | 18.7271 | -352.8567 | 16.8074
11:44 | 1487 | 22.2218 | 194.9305 | 435.9503 | 440.6655 | -21.482 | -46.958 | 1.7315 | 0.1108 | -7.2664 | -7.2445 | -3.127 | -4.1654 | 2.43 | -4.369 | 0.5834 | 0.6288 | 0.9484 | 0.6942 | -130.753 | -5.916 | 0.6331 | -1.2955 | -8.3616 | -7.1788 | -0.1779 |  | -2.8534 | -3.3964 | 4.0009 | 3.3661 | 3.3539 | 1.0259 | 10.6123 | 14.0968 | 14.6737 | 11.0125 | -0.0002 | -0.0031 | 0.0009 | 0.0042 | 0.0003 | -0.0006 | 0.0252 | -0.0083 | 0.0056 | -360.1681 | 17.5075 | -360.5681 | 17.8319 | -360.9589 | 18.105 | -360.962 | 17.5794 | -352.8014 | 18.7436 | -352.8414 | 16.8156
11:45 | 1488 | 22.2693 | 194.9774 | 436.0148 | 440.6662 | -21.5708 | -46.9377 | 1.6381 | 0.095 | -7.2284 | -7.2774 | -3.1634 | -4.2171 | 2.4041 | -4.4413 | 0.5835 | 0.6274 | 0.9475 | 0.6944 | -130.8619 | -5.8376 | 0.6799 | -1.196 | -8.4924 | -7.2181 | -0.1458 |  | -2.8127 | -3.288 | 4.0004 | 3.3672 | 3.3531 | 1.0257 | 10.6075 | 14.0751 | 14.6656 | 11.0013 | -0.0003 | -0.003 | 0.0005 | 0.0035 | 0.001 | -0.0003 | 0.0119 | 0.0024 | -0.0075 | -360.1742 | 17.4993 | -360.5066 | 17.7847 | -360.8543 | 18.066 | -360.9651 | 17.5855 | -352.8044 | 18.7292 | -352.8106 | 16.7663
11:45 | 1489 | 22.3074 | 195.0304 | 436.0214 | 440.6549 | -21.5363 | -46.9777 | 1.6646 | 0.1071 | -7.2653 | -7.3641 | -3.0969 | -4.1259 | 2.5004 | -4.3755 | 0.5854 | 0.6311 | 0.9468 | 0.6944 | -130.7674 | -5.7732 | 0.6584 | -1.1324 | -8.4478 | -7.1241 | -0.1035 |  | -2.8628 | -3.2813 | 4.0015 | 3.3664 | 3.3527 | 1.0268 | 10.6249 | 14.1214 | 14.6945 | 11.0475 | -0.0008 | -0.0033 | 0.0006 | 0.0038 | 0.0009 | -0.0001 | 0.0074 | 0.0002 | 0.0021 | -360.205 | 17.5342 | -360.5804 | 17.795 | -360.8635 | 18.0639 | -360.9651 | 17.604 | -352.8721 | 18.7764 | -352.8814 | 16.7909
11:45 | 1490 | 22.2267 | 194.9178 | 435.903 | 440.6342 | -21.5428 | -47.0606 | 1.6935 | 0.135 | -7.1866 | -7.361 | -3.0502 | -4.1986 | 2.4161 | -4.4222 | 0.5845 | 0.6317 | 0.9502 | 0.6962 | -130.831 | -5.8465 | 0.6493 | -1.2656 | -8.4034 | -7.247 | -0.1795 |  | -2.8201 | -3.2845 | 4.0014 | 3.3667 | 3.3559 | 1.0262 | 10.642 | 14.1219 | 14.7219 | 11.0518 | -0.0001 | -0.0026 | 0.0009 | 0.0038 | 0.0009 | -0.0003 | 0.0223 | -0.0039 | -0.0325 | -360.1927 | 17.5116 | -360.5681 | 17.8032 | -360.9004 | 18.0557 | -360.9127 | 17.5876 | -352.8106 | 18.7497 | -352.8414 | 16.7909
11:45 | 1491 | 22.3006 | 194.9343 | 436.018 | 440.7142 | -21.5329 | -47.0361 | 1.6841 | 0.1518 | -7.2099 | -7.3832 | -3.1079 | -4.099 | 2.4592 | -4.3021 | 0.585 | 0.6317 | 0.9484 | 0.6946 | -130.8123 | -5.7778 | 0.6711 | -1.2611 | -8.5036 | -7.1973 | -0.1738 |  | -2.8157 | -3.2963 | 3.9996 | 3.3669 | 3.3503 | 1.0246 | 10.6363 | 14.1216 | 14.7314 | 11.0179 | 0.0001 | -0.003 | 0.0003 | 0.0036 | 0.0004 | -0.0004 | 0.0011 | -0.0041 | 0.0003 | -360.1435 | 17.4952 | -360.5558 | 17.8073 | -360.9281 | 18.1112 | -360.9497 | 17.5732 | -352.7983 | 18.7395 | -352.826 | 16.8053
11:45 | 1492 | 22.185 | 194.9475 | 435.9699 | 440.6891 | -21.5872 | -47.0958 | 1.7187 | 0.1537 | -7.2087 | -7.3743 | -3.1216 | -4.0419 | 2.5136 | -4.3617 | 0.5856 | 0.6323 | 0.9431 | 0.6954 | -130.7258 | -5.7186 | 0.6379 | -1.1698 | -8.4489 | -7.1971 | -0.1135 |  | -2.8297 | -3.315 | 3.9992 | 3.3661 | 3.3539 | 1.0271 | 10.6296 | 14.0911 | 14.6863 | 11.0237 | -0.0001 | -0.0035 | 0.0005 | 0.0037 | 0.0003 | -0.0012 | 0.0002 | -0.0028 | 0.0048 | -360.1835 | 17.4808 | -360.5127 | 17.7888 | -360.9066 | 18.1173 | -361.0143 | 17.5999 | -352.789 | 18.7251 | -352.7829 | 16.7724
11:45 | 1493 | 22.2033 | 194.8926 | 435.9798 | 440.7256 | -21.5587 | -46.9638 | 1.7464 | 0.1762 | -7.1938 | -7.3528 | -3.1493 | -4.0193 | 2.5522 | -4.3191 | 0.5848 | 0.6349 | 0.948 | 0.6952 | -130.8531 | -5.8494 | 0.5059 | -1.188 | -8.537 | -7.2155 | -0.1292 |  | -2.795 | -3.304 | 4.0008 | 3.3678 | 3.3542 | 1.0243 | 10.6041 | 14.0889 | 14.6846 | 11.0154 | -0.0002 | -0.0025 | 0.0008 | 0.0036 | 0.0002 | -0.0007 | 0.0093 | -0.0007 | -0.0048 | -360.1773 | 17.487 | -360.5343 | 17.7888 | -360.845 | 18.0763 | -360.9743 | 17.5937 | -352.829 | 18.7312 | -352.829 | 16.7786
11:45 | 1494 | 22.2114 | 194.9194 | 436.1001 | 440.6939 | -21.5692 | -46.9722 | 1.7829 | 0.1539 | -7.1515 | -7.3631 | -3.0863 | -4.1355 | 2.4479 | -4.4942 | 0.5855 | 0.6364 | 0.9487 | 0.6964 | -130.8411 | -5.8578 | 0.5592 | -1.2881 | -8.5482 | -7.18 | -0.2333 |  | -2.8053 | -3.3763 | 3.9995 | 3.3678 | 3.3527 | 1.0246 | 10.6179 | 14.1028 | 14.6989 | 11.0118 | -0.0007 | -0.0029 | 0.0006 | 0.0033 | 0.0003 | -0.0013 | 0.0038 | 0.0005 | 0.0005 | -360.2327 | 17.5383 | -360.5927 | 17.8134 | -360.9404 | 18.0639 | -360.9158 | 17.5732 | -352.8198 | 18.7559 | -352.866 | 16.8094
11:45 | 1495 | 22.2574 | 194.9579 | 436.0068 | 440.7032 | -21.5924 | -47.1253 | 1.7995 | 0.1595 | -7.0374 | -7.3774 | -3.02 | -4.2243 | 2.4444 | -4.421 | 0.584 | 0.6334 | 0.9512 | 0.6922 | -130.7463 | -5.8229 | 0.5508 | -1.267 | -8.5731 | -7.2383 | -0.1484 |  | -2.8051 | -3.3453 | 4.0016 | 3.3681 | 3.3529 | 1.0266 | 10.604 | 14.0544 | 14.6857 | 11.0208 | 0.0001 | -0.0029 | 0.0012 | 0.0046 | 0.0004 | -0.0004 | 0.0186 | 0.0006 | 0.0035 | -360.1527 | 17.4931 | -360.5589 | 17.8032 | -360.9404 | 18.068 | -360.922 | 17.5486 | -352.7706 | 18.723 | -352.8598 | 16.8094
11:45 | 1496 | 22.2705 | 194.8844 | 436.0556 | 440.7417 | -21.6117 | -47.1418 | 1.779 | 0.1436 | -7.1112 | -7.4308 | -3.024 | -4.281 | 2.4471 | -4.4544 | 0.5856 | 0.6336 | 0.9526 | 0.6956 | -130.7043 | -5.7488 | 0.6694 | -1.138 | -8.4819 | -7.2062 | -0.1044 |  | -2.8218 | -3.3912 | 4.0007 | 3.3674 | 3.3523 | 1.026 | 10.6156 | 14.0833 | 14.6915 | 10.9977 | 0.0003 | -0.0032 | 0.0007 | 0.004 | 0.0007 | -0.0003 | 0.0112 | -0.0156 | 0.0059 | -360.2111 | 17.4972 | -360.5219 | 17.7909 | -360.922 | 18.1071 | -360.9804 | 17.5917 | -352.8106 | 18.7333 | -352.8444 | 16.8032
11:45 | 1497 | 22.2505 | 194.9764 | 436.1098 | 440.7398 | -21.5956 | -47.0819 | 1.7522 | 0.1896 | -7.1484 | -7.4349 | -3.1103 | -4.2249 | 2.4174 | -4.3151 | 0.585 | 0.6313 | 0.9528 | 0.6948 | -130.7803 | -5.7987 | 0.6439 | -1.138 | -8.4131 | -7.1126 | -0.075 |  | -2.702 | -3.3417 | 3.9994 | 3.3634 | 3.3495 | 1.0251 | 10.6225 | 14.0844 | 14.6928 | 11.0276 | 0.0001 | -0.0026 | 0.0005 | 0.0036 | 0.0007 | -0.0008 | 0.0032 | -0.0002 | -0.0011 | -360.2111 | 17.489 | -360.4881 | 17.7518 | -360.8481 | 18.0537 | -360.9497 | 17.6061 | -352.8598 | 18.7251 | -352.8075 | 16.7663
11:45 | 1498 | 22.2936 | 195.0283 | 436.0513 | 440.8386 | -21.5854 | -47.1065 | 1.7561 | 0.1569 | -7.0582 | -7.405 | -3.0967 | -4.1853 | 2.4333 | -4.3261 | 0.5853 | 0.6326 | 0.9511 | 0.6947 | -130.8611 | -5.8873 | 0.708 | -1.1271 | -8.5474 | -7.2706 | -0.1253 |  | -2.7606 | -3.4 | 3.9997 | 3.364 | 3.352 | 1.0262 | 10.6341 | 14.096 | 14.7276 | 11.0219 | -0.0004 | -0.0024 | 0.0009 | 0.0041 | 0.0005 | -0.0001 | 0.0134 | -0.0021 | 0.003 | -360.2419 | 17.5383 | -360.565 | 17.7765 | -360.8912 | 18.0763 | -360.9712 | 17.602 | -352.8691 | 18.76 | -352.8321 | 16.795
11:45 | 1499 | 22.3554 | 195.0916 | 435.9973 | 440.7934 | -21.5513 | -47.0892 | 1.737 | 0.1997 | -6.958 | -7.2539 | -3.0213 | -4.2007 | 2.503 | -4.3558 | 0.5851 | 0.6336 | 0.9512 | 0.6948 | -130.8564 | -5.7551 | 0.5564 | -1.1702 | -8.5577 | -7.2394 | -0.2136 |  | -2.7061 | -3.3631 | 4 | 3.365 | 3.3549 | 1.0258 | 10.6123 | 14.1026 | 14.6621 | 11.0299 | -0.0004 | -0.003 | 0.0004 | 0.0035 | 0.0007 | -0.0009 | 0.0009 | -0.0091 | -0.0031 | -360.1373 | 17.487 | -360.5681 | 17.795 | -360.9189 | 18.0742 | -360.9374 | 17.5609 | -352.7829 | 18.7271 | -352.8506 | 16.8094
11:45 | 1500 | 22.3509 | 195.0201 | 436.0426 | 440.882 | -21.5276 | -47.1153 | 1.6825 | 0.221 | -7.0562 | -7.3197 | -3.0336 | -4.2543 | 2.4556 | -4.3945 | 0.5852 | 0.6352 | 0.9502 | 0.6945 | -130.8671 | -5.9144 | 0.5638 | -1.1884 | -8.5164 | -7.189 | -0.1595 |  | -2.7992 | -3.3544 | 3.9999 | 3.3652 | 3.3504 | 1.0261 | 10.6156 | 14.0717 | 14.703 | 10.9919 | 0.0006 | -0.0024 | 0.0007 | 0.004 | 0.0002 | 0 | 0.0009 | -0.0126 | -0.0315 | -360.1588 | 17.4726 | -360.5158 | 17.8052 | -360.9343 | 18.1071 | -361.0174 | 17.5876 | -352.7921 | 18.7148 | -352.829 | 16.8115
11:45 | 1501 | 22.1842 | 194.9596 | 436.0683 | 440.9452 | -21.5645 | -47.2028 | 1.7179 | 0.1974 | -7.0368 | -7.1613 | -3.0059 | -4.254 | 2.4995 | -4.3501 | 0.5835 | 0.6354 | 0.9462 | 0.6936 | -130.8082 | -5.8409 | 0.5955 | -1.2272 | -8.5145 | -7.2241 | -0.2025 |  | -2.8844 | -3.3021 | 3.9999 | 3.3609 | 3.3518 | 1.0279 | 10.6169 | 14.0783 | 14.6665 | 10.9768 | -0.0001 | -0.0032 | 0.0006 | 0.0034 | 0.0004 | -0.0012 | 0.0071 | -0.0055 | -0.0121 | -360.2081 | 17.4829 | -360.5281 | 17.7888 | -360.9127 | 18.0865 | -361.002 | 17.5978 | -352.8106 | 18.7251 | -352.7767 | 16.7971
11:45 | 1502 | 22.2396 | 194.9384 | 436.0962 | 440.9184 | -21.4517 | -47.1092 | 1.7796 | 0.158 | -7.1179 | -7.366 | -3.0526 | -4.2098 | 2.5003 | -4.3438 | 0.5845 | 0.6352 | 0.9479 | 0.694 | -130.7388 | -5.8205 | 0.5319 | -1.2208 | -8.5133 | -7.1645 | -0.0886 |  | -2.8021 | -3.2999 | 4.001 | 3.3646 | 3.3516 | 1.0276 | 10.6202 | 14.1227 | 14.6796 | 11.0251 | -0.0003 | -0.0028 | 0.0009 | 0.0038 | 0.0007 | -0.0005 | -0.0011 | 0.0019 | -0.0239 | -360.2111 | 17.5219 | -360.5496 | 17.7765 | -360.8697 | 18.0619 | -360.962 | 17.5855 | -352.8506 | 18.76 | -352.8444 | 16.795
11:45 | 1503 | 22.3492 | 194.9188 | 436.0016 | 440.9153 | -21.336 | -47.0586 | 1.7867 | 0.1889 | -7.108 | -7.3308 | -3.1 | -4.2156 | 2.4545 | -4.3569 | 0.5852 | 0.6359 | 0.9521 | 0.6949 | -130.8107 | -5.7699 | 0.728 | -1.2383 | -8.4656 | -7.2298 | -0.0859 |  | -2.7639 | -3.2218 | 4.0014 | 3.3676 | 3.3535 | 1.0274 | 10.6248 | 14.0753 | 14.6782 | 10.9894 | -0.0003 | -0.0027 | 0.0008 | 0.0039 | 0.0009 | -0.0004 | -0.0054 | -0.0063 | -0.0102 | -360.1835 | 17.5342 | -360.6081 | 17.8134 | -360.922 | 18.0701 | -360.922 | 17.5753 | -352.8506 | 18.76 | -352.8752 | 16.8197
11:45 | 1504 | 22.3388 | 194.9448 | 436.0234 | 440.8967 | -21.4466 | -47.1528 | 1.828 | 0.116 | -7.1334 | -7.3657 | -3.0365 | -4.1796 | 2.5659 | -4.2826 | 0.5853 | 0.6351 | 0.9521 | 0.6942 | -130.7686 | -5.8264 | 0.7299 | -1.2314 | -8.4392 | -7.2147 | -0.0662 |  | -2.7625 | -3.3035 | 4.0002 | 3.3671 | 3.3524 | 1.0276 | 10.6226 | 14.0957 | 14.7255 | 11.0284 | -0.0004 | -0.0032 | 0.0006 | 0.0034 | 0.0007 | -0.001 | 0.0035 | 0.0045 | -0.0275 | -360.1496 | 17.4849 | -360.5312 | 17.795 | -360.8758 | 18.068 | -360.9466 | 17.5753 | -352.7767 | 18.7251 | -352.826 | 16.8053
11:45 | 1505 | 22.3553 | 194.9624 | 435.978 | 440.9002 | -21.5393 | -47.1527 | 1.8553 | 0.1198 | -7.1614 | -7.3774 | -3.0827 | -4.1353 | 2.5015 | -4.3256 | 0.5846 | 0.6335 | 0.9518 | 0.6933 | -130.8123 | -5.896 | 0.6541 | -1.1143 | -8.3778 | -7.23 | -0.0522 |  | -2.7415 | -3.2499 | 3.9998 | 3.3696 | 3.3504 | 1.0259 | 10.6076 | 14.0806 | 14.6577 | 11.0309 | 0.0001 | -0.0033 | 0.0009 | 0.0041 | 0.0007 | -0.0002 | -0.0032 | -0.0138 | -0.0045 | -360.2204 | 17.4952 | -360.5004 | 17.7785 | -360.922 | 18.1009 | -361.0297 | 17.6184 | -352.8567 | 18.7312 | -352.8167 | 16.7909
11:45 | 1506 | 22.3437 | 194.9954 | 435.9307 | 440.8814 | -21.4709 | -47.1853 | 1.8551 | 0.1641 | -7.1318 | -7.3571 | -3.013 | -4.1423 | 2.495 | -4.3598 | 0.5848 | 0.6346 | 0.9513 | 0.6942 | -130.7319 | -5.8743 | 0.6591 | -1.1365 | -8.3727 | -7.212 | 0.0059 |  | -2.8258 | -3.346 | 4.0007 | 3.3663 | 3.3501 | 1.0265 | 10.6353 | 14.1086 | 14.7221 | 11.058 | -0.0003 | -0.0027 | 0.0008 | 0.0039 | 0.001 | -0.0008 | 0.0203 | -0.0068 | 0.0021 | -360.1773 | 17.4931 | -360.485 | 17.758 | -360.8912 | 18.0804 | -360.9774 | 17.602 | -352.8537 | 18.7312 | -352.7952 | 16.7601
11:45 | 1507 | 22.3216 | 195.0326 | 436.025 | 441.0077 | -21.4495 | -47.1384 | 1.7999 | 0.1621 | -7.0968 | -7.2997 | -3.0832 | -4.1501 | 2.4892 | -4.3455 | 0.5841 | 0.6327 | 0.9467 | 0.693 | -130.7302 | -5.8335 | 0.7246 | -1.142 | -8.469 | -7.1904 | -0.0787 |  | -2.7543 | -3.2235 | 4.0008 | 3.3669 | 3.3523 | 1.0269 | 10.6191 | 14.0865 | 14.6877 | 11.0306 | -0.0005 | -0.0024 | 0.0003 | 0.0036 | 0.0003 | -0.0006 | 0.0114 | -0.0043 | -0.0077 | -360.2081 | 17.5137 | -360.5527 | 17.7909 | -360.9004 | 18.0701 | -360.9589 | 17.5712 | -352.8229 | 18.7559 | -352.8444 | 16.8074
11:45 | 1508 | 22.3412 | 194.9334 | 436.0008 | 440.9541 | -21.4642 | -47.213 | 1.8322 | 0.1736 | -7.0682 | -7.4187 | -3.0828 | -4.1076 | 2.5036 | -4.2999 | 0.5838 | 0.6322 | 0.9479 | 0.6946 | -130.6826 | -5.7673 | 0.7403 | -1.0421 | -8.3954 | -7.1499 | -0.0004 |  | -2.8244 | -3.2614 | 3.9994 | 3.3673 | 3.3517 | 1.0254 | 10.6399 | 14.1076 | 14.7044 | 10.9988 | -0.0001 | -0.0031 | 0.0009 | 0.0041 | 0.001 | -0.0006 | 0.0079 | 0.008 | 0.0052 | -360.1219 | 17.5055 | -360.6112 | 17.8258 | -360.9651 | 18.0886 | -360.9435 | 17.565 | -352.8075 | 18.7374 | -352.8752 | 16.8299
11:45 | 1509 | 22.3308 | 194.9124 | 435.9525 | 440.9391 | -21.4971 | -47.2852 | 1.7658 | 0.1658 | -7.1628 | -7.4291 | -3.0364 | -4.14 | 2.5382 | -4.3172 | 0.5857 | 0.6348 | 0.9505 | 0.6956 | -130.7259 | -5.7473 | 0.7416 | -1.042 | -8.3997 | -6.9966 | -0.0047 |  | -2.8131 | -3.3461 | 4 | 3.364 | 3.3551 | 1.0262 | 10.5994 | 14.0785 | 14.6976 | 11.0396 | -0.0002 | -0.0032 | 0.0008 | 0.0032 | 0.0004 | -0.0004 | 0.0176 | 0.0004 | -0.0142 | -360.1311 | 17.487 | -360.5281 | 17.7909 | -360.9097 | 18.0824 | -360.9527 | 17.565 | -352.7614 | 18.7251 | -352.8198 | 16.8032
11:45 | 1510 | 22.3158 | 195.0524 | 436.0797 | 441.0749 | -21.566 | -47.3027 | 1.7433 | 0.1245 | -7.1586 | -7.256 | -3.0753 | -4.0345 | 2.4985 | -4.274 | 0.5843 | 0.6333 | 0.9524 | 0.6948 | -130.6827 | -5.7728 | 0.6582 | -1.1173 | -8.4361 | -7.0842 | -0.0839 |  | -2.813 | -3.2963 | 4.0017 | 3.3671 | 3.3528 | 1.0271 | 10.6261 | 14.0529 | 14.6938 | 11.0031 | -0.0003 | -0.0035 | 0.0006 | 0.0033 | 0.0007 | -0.0007 | 0.0124 | -0.0166 | -0.0281 | -360.1835 | 17.5055 | -360.5373 | 17.7765 | -360.8758 | 18.0742 | -360.9866 | 17.6102 | -352.8814 | 18.7353 | -352.8167 | 16.7786
11:45 | 1511 | 22.3361 | 194.9955 | 435.9646 | 440.9775 | -21.5777 | -47.3773 | 1.7151 | 0.1471 | -7.0593 | -7.3138 | -2.9776 | -4.0434 | 2.5007 | -4.3085 | 0.5846 | 0.6327 | 0.9482 | 0.6934 | -130.6878 | -5.7293 | 0.646 | -1.0902 | -8.3838 | -7.1712 | -0.0391 |  | -2.7724 | -3.3495 | 3.9991 | 3.3655 | 3.3545 | 1.0264 | 10.5926 | 14.0772 | 14.6894 | 11.0215 | -0.0005 | -0.0028 | 0.0004 | 0.0035 | 0.0006 | -0.0005 | 0.0034 | -0.0052 | -0.0021 | -360.2296 | 17.526 | -360.565 | 17.7703 | -360.885 | 18.0721 | -360.9589 | 17.6184 | -352.8629 | 18.7661 | -352.8414 | 16.7807
11:45 | 1512 | 22.366 | 195.0022 | 436.048 | 441.0742 | -21.5345 | -47.2581 | 1.7833 | 0.1919 | -6.9888 | -7.2991 | -2.9851 | -4.0437 | 2.5605 | -4.2921 | 0.5859 | 0.6313 | 0.9471 | 0.6945 | -130.7308 | -5.7193 | 0.732 | -1.0624 | -8.2851 | -7.0675 | -0.0229 |  | -2.811 | -3.302 | 4.0001 | 3.368 | 3.3526 | 1.0271 | 10.6271 | 14.1123 | 14.7215 | 11.0204 | -0.0002 | -0.0023 | 0.0001 | 0.0037 | 0.0008 | -0.0004 | 0.0148 | -0.0033 | -0.0212 | -360.1588 | 17.5034 | -360.5466 | 17.7744 | -360.9097 | 18.068 | -360.9251 | 17.5773 | -352.826 | 18.7292 | -352.8137 | 16.7909
11:45 | 1513 | 22.3802 | 194.9463 | 435.9185 | 441.0522 | -21.4926 | -47.3336 | 1.7515 | 0.1731 | -7.05 | -7.1978 | -2.9378 | -4.0664 | 2.5271 | -4.2464 | 0.5835 | 0.6304 | 0.9449 | 0.6932 | -130.7389 | -5.8031 | 0.615 | -1.0209 | -8.2249 | -7.0407 | 0.016 |  | -2.6957 | -3.2555 | 3.9993 | 3.3674 | 3.3525 | 1.0267 | 10.6353 | 14.0855 | 14.6932 | 11.0349 | 0.0001 | -0.0031 | 0.0005 | 0.0039 | 0.0007 | -0.0006 | 0.0052 | 0.0026 | -0.006 | -360.1681 | 17.4747 | -360.5589 | 17.8217 | -360.9497 | 18.1091 | -360.9897 | 17.5753 | -352.7952 | 18.7292 | -352.8414 | 16.8176
11:45 | 1514 | 22.3953 | 195.0496 | 435.9949 | 441.0302 | -21.4992 | -47.2117 | 1.7765 | 0.1768 | -7.0472 | -7.1472 | -2.9312 | -4.009 | 2.5679 | -4.2307 | 0.5842 | 0.6322 | 0.946 | 0.6938 | -130.8254 | -5.8271 | 0.5871 | -1.1083 | -8.3253 | -7.0888 | -0.0595 |  | -2.7618 | -3.3113 | 3.9997 | 3.3677 | 3.3524 | 1.027 | 10.6617 | 14.1184 | 14.7294 | 11.0717 | -0.0001 | -0.0031 | 0.0007 | 0.0041 | 0.0004 | -0.0005 | 0.0042 | -0.003 | -0.0195 | -360.1711 | 17.4685 | -360.5281 | 17.7991 | -360.9251 | 18.0968 | -360.9589 | 17.5794 | -352.7829 | 18.7107 | -352.786 | 16.7909
11:45 | 1515 | 22.3305 | 194.9992 | 435.8935 | 440.9777 | -21.4913 | -47.289 | 1.7836 | 0.0921 | -7.0134 | -7.3728 | -2.9661 | -4.0886 | 2.5586 | -4.2634 | 0.5841 | 0.6318 | 0.948 | 0.6933 | -130.805 | -5.8762 | 0.6675 | -1.0641 | -8.2922 | -6.9785 | -0.1136 |  | -2.7486 | -3.3504 | 4.0001 | 3.3688 | 3.3473 | 1.0265 | 10.6399 | 14.1365 | 14.687 | 11.0219 | -0.0004 | -0.0027 | 0.0005 | 0.0039 | 0.0007 | -0.0007 | 0.0126 | -0.0022 | -0.0092 | -360.2204 | 17.5055 | -360.5373 | 17.7806 | -360.882 | 18.068 | -360.9712 | 17.5917 | -352.8537 | 18.7456 | -352.8414 | 16.7827
11:45 | 1516 | 22.3957 | 195.0252 | 436.0748 | 441.1591 | -21.4758 | -47.3144 | 1.8173 | 0.0725 | -7.0882 | -7.2862 | -3.0188 | -4.1013 | 2.5909 | -4.2345 | 0.5839 | 0.6315 | 0.9489 | 0.6939 | -130.8158 | -5.7616 | 0.5757 | -1.0367 | -8.3521 | -7.1152 | -0.059 |  | -2.7552 | -3.3411 | 4.0013 | 3.3661 | 3.3529 | 1.0271 | 10.6582 | 14.1323 | 14.7205 | 11.0218 | -0.0001 | -0.0024 | 0.0009 | 0.0042 | 0.0006 | -0.0001 | 0.0086 | 0.0011 | -0.0055 | -360.1988 | 17.5342 | -360.605 | 17.7991 | -360.8758 | 18.066 | -360.9281 | 17.5794 | -352.8321 | 18.7723 | -352.8752 | 16.7991
11:45 | 1517 | 22.3418 | 194.9352 | 435.9933 | 441.2022 | -21.4482 | -47.2563 | 1.8144 | 0.1344 | -7.0482 | -7.3585 | -2.9583 | -4.1019 | 2.6132 | -4.2514 | 0.5845 | 0.6312 | 0.95 | 0.694 | -130.8788 | -5.8237 | 0.5233 | -1.1205 | -8.3877 | -7.1088 | -0.1144 |  | -2.7612 | -3.3815 | 3.9996 | 3.3648 | 3.3509 | 1.0274 | 10.6064 | 14.1086 | 14.6874 | 11.0233 | 0.0004 | -0.0028 | 0.001 | 0.0037 | 0.0006 | -0.001 | 0.0231 | 0.0009 | 0.0026 | -360.165 | 17.5013 | -360.5435 | 17.8011 | -360.9066 | 18.0516 | -360.8943 | 17.5753 | -352.8014 | 18.7395 | -352.8414 | 16.8032
11:45 | 1518 | 22.3968 | 195.0321 | 436.0144 | 441.1397 | -21.5129 | -47.3025 | 1.831 | 0.1632 | -7.0593 | -7.4171 | -2.9972 | -4.1479 | 2.6035 | -4.2902 | 0.5828 | 0.6339 | 0.9511 | 0.6945 | -130.6692 | -5.7396 | 0.6359 | -1.1119 | -8.4326 | -7.0915 | -0.1037 |  | -2.733 | -3.4045 | 4.002 | 3.3703 | 3.3513 | 1.0273 | 10.5927 | 14.0712 | 14.6525 | 10.9703 | -0.0002 | -0.0034 | 0.0003 | 0.0033 | 0.0003 | -0.0007 | 0.0082 | 0.0017 | 0.0155 | -360.1742 | 17.4829 | -360.5312 | 17.7929 | -360.9127 | 18.1112 | -360.9897 | 17.5937 | -352.8506 | 18.7353 | -352.8075 | 16.7991
11:45 | 1519 | 22.5068 | 195.0952 | 436.1484 | 441.299 | -21.5783 | -47.3609 | 1.7558 | 0.2148 | -7.0656 | -7.2042 | -2.9635 | -4.1521 | 2.5567 | -4.237 | 0.5853 | 0.6321 | 0.9503 | 0.6946 | -130.7459 | -5.7336 | 0.6446 | -1.2074 | -8.3884 | -7.1137 | -0.025 |  | -2.7927 | -3.4917 | 4.0016 | 3.3659 | 3.3487 | 1.0266 | 10.6018 | 14.0692 | 14.6993 | 11.0132 | 0 | -0.0027 | 0.0007 | 0.0038 | 0.0011 | -0.0006 | 0.0116 | -0.0198 | -0.0158 | -360.1927 | 17.4849 | -360.5189 | 17.7621 | -360.8697 | 18.0968 | -361.0297 | 17.604 | -352.8198 | 18.7271 | -352.7552 | 16.7724
11:45 | 1520 | 22.4857 | 195.0636 | 436.0638 | 441.2492 | -21.5113 | -47.3211 | 1.8099 | 0.2034 | -7.1978 | -7.1542 | -2.9727 | -4.12 | 2.6096 | -4.2724 | 0.5847 | 0.6362 | 0.9494 | 0.6943 | -130.7154 | -5.7758 | 0.6704 | -1.194 | -8.3541 | -7.145 | -0.0672 |  | -2.7335 | -3.4029 | 4.001 | 3.364 | 3.3482 | 1.0277 | 10.5949 | 14.0563 | 14.6621 | 10.9837 | -0.0006 | -0.0029 | 0.0012 | 0.0041 | 0.0005 | -0.0007 | 0.0122 | -0.0061 | 0.0045 | -360.205 | 17.4931 | -360.5466 | 17.7929 | -360.8697 | 18.0701 | -360.9866 | 17.5958 | -352.8383 | 18.7456 | -352.8167 | 16.793
11:45 | 1521 | 22.4362 | 195.0564 | 436.0391 | 441.2849 | -21.4842 | -47.2411 | 1.8671 | 0.2981 | -7.1159 | -7.1523 | -2.8916 | -4.123 | 2.6243 | -4.2632 | 0.585 | 0.6335 | 0.9495 | 0.6936 | -130.7686 | -5.8092 | 0.7143 | -1.1238 | -8.3647 | -7.039 | 0.0371 |  | -2.7459 | -3.3901 | 4.0014 | 3.3637 | 3.3521 | 1.0269 | 10.6087 | 14.0819 | 14.6601 | 11.0028 | 0.0001 | -0.0022 | 0.0004 | 0.0038 | 0.0006 | -0.0005 | 0.0019 | 0.0084 | -0.011 | -360.2327 | 17.5239 | -360.6019 | 17.8217 | -360.9681 | 18.0721 | -360.9281 | 17.5732 | -352.8198 | 18.76 | -352.8967 | 16.8279
11:45 | 1522 | 22.4786 | 195.1234 | 436.133 | 441.3024 | -21.4838 | -47.2154 | 1.8414 | 0.2558 | -7.1085 | -7.2309 | -2.9527 | -4.0872 | 2.65 | -4.2909 | 0.5843 | 0.6338 | 0.9495 | 0.6952 | -130.7454 | -5.8799 | 0.8371 | -1.1466 | -8.451 | -7.1091 | 0.0144 |  | -2.7503 | -3.3402 | 4.0008 | 3.3649 | 3.3508 | 1.0273 | 10.6342 | 14.1017 | 14.7149 | 11.0222 | 0.0002 | -0.0034 | 0.0006 | 0.0041 | 0.0005 | -0.001 | 0.0051 | 0.0048 | -0.016 | -360.1465 | 17.4829 | -360.5496 | 17.797 | -360.922 | 18.0701 | -360.9281 | 17.5506 | -352.7675 | 18.7395 | -352.8444 | 16.8217
11:45 | 1523 | 22.4651 | 195.0503 | 436.1162 | 441.3057 | -21.443 | -47.2431 | 1.8472 | 0.259 | -7.0089 | -7.2243 | -2.9037 | -4.1448 | 2.5886 | -4.3174 | 0.5845 | 0.6333 | 0.9482 | 0.6946 | -130.7677 | -5.7433 | 0.8409 | -1.1433 | -8.4438 | -7.0516 | 0.0106 |  | -2.7044 | -3.3386 | 4.0005 | 3.3649 | 3.3538 | 1.0283 | 10.6513 | 14.1657 | 14.7355 | 11.0616 | -0.0002 | -0.0028 | 0.0006 | 0.0038 | 0.0005 | 0 | 0.0178 | -0.0105 | -0.0138 | -360.1773 | 17.4849 | -360.5373 | 17.7806 | -360.9097 | 18.0988 | -361.0051 | 17.604 | -352.8229 | 18.7395 | -352.8229 | 16.7909
11:45 | 1524 | 22.5067 | 195.0554 | 436.1311 | 441.2954 | -21.4719 | -47.2613 | 1.8193 | 0.2613 | -7.0029 | -7.2632 | -2.9655 | -4.1728 | 2.5629 | -4.3244 | 0.5852 | 0.6331 | 0.9509 | 0.6947 | -130.7484 | -5.8404 | 0.7187 | -1.1922 | -8.4761 | -7.0928 | -0.0836 |  | -2.7657 | -3.3495 | 4.0009 | 3.3665 | 3.352 | 1.0274 | 10.6305 | 14.1159 | 14.714 | 11.0525 | -0.0002 | -0.0025 | 0.0002 | 0.0035 | 0.0011 | -0.0007 | -0.0006 | -0.0003 | -0.0157 | -360.2204 | 17.4931 | -360.5158 | 17.7375 | -360.8666 | 18.0475 | -360.9435 | 17.602 | -352.8352 | 18.7456 | -352.7798 | 16.7601
11:45 | 1525 | 22.3785 | 195.0465 | 436.0598 | 441.276 | -21.484 | -47.2272 | 1.882 | 0.2008 | -7.0808 | -7.2878 | -2.9362 | -4.2078 | 2.5779 | -4.3231 | 0.5851 | 0.6356 | 0.9495 | 0.693 | -130.8147 | -5.8032 | 0.7754 | -1.2218 | -8.4342 | -7.0638 | 0.0209 |  | -2.6904 | -3.3071 | 4.0003 | 3.3627 | 3.3534 | 1.0278 | 10.6238 | 14.1141 | 14.7084 | 11.0068 | -0.0007 | -0.0032 | 0.0004 | 0.0034 | 0.0003 | -0.0005 | 0.0179 | -0.0015 | -0.0069 | -360.2173 | 17.5157 | -360.5435 | 17.758 | -360.8574 | 18.0742 | -360.9651 | 17.5958 | -352.8721 | 18.7641 | -352.8444 | 16.7848
11:45 | 1526 | 22.3936 | 195.0947 | 436.027 | 441.3128 | -21.624 | -47.2856 | 1.8537 | 0.2082 | -7.0285 | -7.2362 | -3.0152 | -4.1584 | 2.5809 | -4.2302 | 0.5851 | 0.6345 | 0.9515 | 0.6939 | -130.7391 | -5.7528 | 0.7585 | -1.2582 | -8.4649 | -7.097 | 0.0102 |  | -2.7376 | -3.3729 | 4.0007 | 3.3673 | 3.3537 | 1.0266 | 10.611 | 14.0785 | 14.686 | 11.0107 | 0.0003 | -0.003 | 0.0007 | 0.0036 | 0.0007 | -0.001 | 0.0165 | -0.0075 | -0.0285 | -360.1835 | 17.5013 | -360.5496 | 17.7683 | -360.9127 | 18.068 | -360.9158 | 17.5629 | -352.7521 | 18.7333 | -352.8506 | 16.7991
11:45 | 1527 | 22.4962 | 195.1326 | 436.0709 | 441.363 | -21.4416 | -47.2525 | 1.8082 | 0.2721 | -7.0668 | -7.3097 | -2.9451 | -4.2002 | 2.582 | -4.2341 | 0.5853 | 0.6357 | 0.9513 | 0.696 | -130.7264 | -5.8232 | 0.8364 | -1.2702 | -8.4742 | -7.0349 | -0.0309 |  | -2.7117 | -3.3712 | 4.0007 | 3.3683 | 3.3523 | 1.0278 | 10.595 | 14.0676 | 14.6369 | 11.0017 | -0.0003 | -0.0034 | 0.0002 | 0.0034 | 0.0004 | -0.0008 | 0.0039 | -0.0194 | -0.015 | -360.1496 | 17.4808 | -360.5435 | 17.7826 | -360.9404 | 18.1071 | -361.0051 | 17.5917 | -352.7706 | 18.7251 | -352.8352 | 16.8135
11:45 | 1528 | 22.5395 | 195.0845 | 436.01 | 441.3378 | -21.4744 | -47.2512 | 1.887 | 0.303 | -7.0773 | -7.2974 | -2.9972 | -4.1472 | 2.5775 | -4.2739 | 0.5851 | 0.6369 | 0.9486 | 0.6956 | -130.6931 | -5.8486 | 0.7691 | -1.1302 | -8.4726 | -7.124 | -0.0229 |  | -2.7743 | -3.3396 | 4 | 3.3613 | 3.3549 | 1.0267 | 10.626 | 14.0821 | 14.7133 | 11.0197 | -0.0004 | -0.003 | 0.0008 | 0.0038 | 0.0006 | -0.0008 | 0.0033 | -0.0011 | -0.0122 | -360.1527 | 17.4829 | -360.5066 | 17.7683 | -360.9281 | 18.0988 | -360.9681 | 17.5794 | -352.7798 | 18.7148 | -352.7921 | 16.7909
11:45 | 1529 | 22.4919 | 195.2426 | 436.1662 | 441.4789 | -21.373 | -47.0554 | 2.0618 | 0.2556 | -7.013 | -7.202 | -2.9804 | -4.2055 | 2.5032 | -4.2109 | 0.5846 | 0.6308 | 0.9516 | 0.6956 | -130.6299 | -5.7226 | 0.8625 | -1.1126 | -8.3759 | -7.0564 | -0.0095 |  | -2.7024 | -3.3125 | 4.0004 | 3.3673 | 3.3543 | 1.0274 | 10.5983 | 14.1005 | 14.6904 | 11.0154 | -0.0004 | -0.0027 | 0.0005 | 0.0037 | 0.0008 | -0.0006 | 0.0356 | -0.0078 | 0.0029 | -360.2358 | 17.5055 | -360.5558 | 17.7498 | -360.8881 | 18.068 | -360.9589 | 17.5958 | -352.8321 | 18.7477 | -352.8229 | 16.7909
11:45 | 1530 | 22.5275 | 195.1829 | 436.2047 | 441.5069 | -21.2812 | -46.8809 | 2.0611 | 0.294 | -7.0224 | -7.0657 | -2.8835 | -4.2803 | 2.5566 | -4.2098 | 0.5852 | 0.6333 | 0.9484 | 0.6955 | -130.6627 | -5.7153 | 0.7323 | -1.157 | -8.4062 | -7.018 | -0.0278 |  | -2.6876 | -3.2457 | 3.9997 | 3.3647 | 3.3501 | 1.028 | 10.6329 | 14.1006 | 14.7088 | 11.0208 | -0.0003 | -0.0034 | 0.0006 | 0.0039 | 0.0005 | -0.0004 | 0.0094 | -0.0064 | -0.0136 | -360.2327 | 17.5198 | -360.5866 | 17.7662 | -360.9066 | 18.0639 | -360.9251 | 17.5794 | -352.8014 | 18.7661 | -352.866 | 16.793
11:45 | 1531 | 22.4916 | 195.1225 | 436.2463 | 441.5418 | -21.2822 | -46.9135 | 2.0459 | 0.2735 | -6.9975 | -7.1484 | -2.8825 | -4.3508 | 2.5102 | -4.1684 | 0.5844 | 0.6324 | 0.9492 | 0.6932 | -130.7616 | -5.8004 | 0.8143 | -1.1373 | -8.3617 | -6.9841 | 0.0828 |  | -2.7281 | -3.28 | 4.0005 | 3.3672 | 3.3549 | 1.0267 | 10.6536 | 14.1102 | 14.715 | 11.0233 | 0.0003 | -0.003 | 0.001 | 0.0041 | 0.0006 | -0.0004 | 0.0096 | -0.009 | -0.012 | -360.165 | 17.5055 | -360.5773 | 17.7724 | -360.9127 | 18.0701 | -360.9127 | 17.5794 | -352.8044 | 18.7477 | -352.8598 | 16.8094
11:45 | 1532 | 22.455 | 195.1434 | 436.1711 | 441.543 | -21.3003 | -46.9304 | 2.0845 | 0.2205 | -6.9964 | -7.1633 | -2.8267 | -4.2684 | 2.6246 | -4.2077 | 0.5844 | 0.6336 | 0.9509 | 0.6943 | -130.6956 | -5.7118 | 0.8901 | -1.1243 | -8.3457 | -7.0034 | 0.0418 |  | -2.7284 | -3.298 | 3.9993 | 3.3649 | 3.3514 | 1.0267 | 10.6469 | 14.1086 | 14.7279 | 11.0464 | -0.0005 | -0.0036 | 0.0005 | 0.0034 | 0.0004 | -0.0005 | 0.0023 | -0.0009 | -0.0187 | -360.2019 | 17.4849 | -360.5219 | 17.7765 | -360.9189 | 18.1112 | -360.9989 | 17.5876 | -352.7737 | 18.7353 | -352.8137 | 16.8053
11:45 | 1533 | 22.5126 | 195.1589 | 436.225 | 441.511 | -21.3012 | -46.8685 | 2.1568 | 0.351 | -7.0112 | -7.1881 | -2.8318 | -4.2413 | 2.5325 | -4.2014 | 0.5833 | 0.6346 | 0.9498 | 0.694 | -130.6915 | -5.7178 | 0.9004 | -1.1377 | -8.3678 | -6.9765 | 0.0313 |  | -2.7032 | -3.2929 | 4 | 3.3654 | 3.352 | 1.0271 | 10.6134 | 14.1097 | 14.705 | 11.0017 | -0.0004 | -0.0027 | 0.0002 | 0.0034 | 0.0007 | -0.0005 | -0.0037 | -0.0136 | -0.0151 | -360.1435 | 17.4685 | -360.4973 | 17.7354 | -360.8974 | 18.1112 | -361.002 | 17.5978 | -352.826 | 18.721 | -352.7952 | 16.7786
11:45 | 1534 | 22.5303 | 195.1143 | 436.2175 | 441.5138 | -21.2907 | -46.9563 | 2.0516 | 0.395 | -6.9357 | -7.1586 | -2.8703 | -4.2495 | 2.5664 | -4.2273 | 0.5835 | 0.6359 | 0.9506 | 0.696 | -130.7069 | -5.8 | 0.85 | -1.1093 | -8.3337 | -7.0469 | 0.0005 |  | -2.7315 | -3.2832 | 3.9999 | 3.364 | 3.3535 | 1.0271 | 10.6169 | 14.0957 | 14.6792 | 11.0226 | -0.0001 | -0.0028 | 0.0005 | 0.0028 | 0.0003 | -0.0005 | -0.0011 | -0.0079 | -0.0242 | -360.1958 | 17.4952 | -360.5466 | 17.7621 | -360.882 | 18.0988 | -361.0512 | 17.5978 | -352.8198 | 18.7395 | -352.8106 | 16.7848
11:45 | 1535 | 22.4398 | 195.1487 | 436.0991 | 441.4782 | -21.2955 | -47.0006 | 2.0541 | 0.4196 | -6.8523 | -7.1725 | -2.8077 | -4.1749 | 2.5736 | -4.2565 | 0.5841 | 0.6335 | 0.9498 | 0.6954 | -130.7302 | -5.8011 | 0.8102 | -1.0618 | -8.4041 | -7.0489 | 0.0217 |  | -2.7062 | -3.3263 | 3.9984 | 3.3619 | 3.3527 | 1.0261 | 10.6088 | 14.0586 | 14.6985 | 11.0151 | 0.0001 | -0.0034 | 0.0007 | 0.0035 | 0.0008 | -0.0008 | 0.0137 | -0.0188 | -0.0036 | -360.1927 | 17.5013 | -360.525 | 17.7559 | -360.8881 | 18.0639 | -360.8881 | 17.5712 | -352.7644 | 18.7395 | -352.8444 | 16.7827
11:45 | 1536 | 22.4792 | 195.1171 | 436.0921 | 441.6215 | -21.4071 | -46.9476 | 2.0138 | 0.3159 | -6.9637 | -7.1758 | -2.8528 | -4.3245 | 2.5559 | -4.2299 | 0.5858 | 0.6311 | 0.951 | 0.6945 | -130.735 | -5.8748 | 0.7962 | -1.0371 | -8.3437 | -7.0146 | 0.0455 |  | -2.7457 | -3.2268 | 3.9988 | 3.3649 | 3.3548 | 1.0263 | 10.5995 | 14.0668 | 14.6618 | 11.0169 | 0.0003 | -0.0029 | 0.001 | 0.004 | 0.0002 | -0.0004 | 0.0192 | 0.0064 | 0.0061 | -360.1527 | 17.4972 | -360.5896 | 17.7991 | -360.9312 | 18.0865 | -360.9097 | 17.5691 | -352.826 | 18.7436 | -352.8598 | 16.8197
11:45 | 1537 | 22.4849 | 195.1419 | 436.007 | 441.6241 | -21.3786 | -46.939 | 2.1025 | 0.2897 | -6.9392 | -7.1275 | -2.8684 | -4.3324 | 2.6024 | -4.2282 | 0.5845 | 0.6313 | 0.9502 | 0.6956 | -130.7274 | -5.7406 | 0.8151 | -0.9923 | -8.3566 | -7.0657 | 0.03 |  | -2.6927 | -3.2171 | 3.9999 | 3.3678 | 3.3515 | 1.0261 | 10.6398 | 14.1194 | 14.7413 | 11.0384 | -0.0002 | -0.0026 | 0.0006 | 0.0044 | 0.0008 | -0.0007 | -0.0053 | -0.0207 | -0.0002 | -360.1496 | 17.4911 | -360.5527 | 17.7642 | -360.8881 | 18.0988 | -360.9251 | 17.5527 | -352.786 | 18.7333 | -352.8321 | 16.8012
11:45 | 1538 | 22.5348 | 195.1771 | 436.1932 | 441.6889 | -21.3232 | -46.9779 | 2.0562 | 0.233 | -7.0473 | -7.1117 | -2.852 | -4.2846 | 2.6288 | -4.2155 | 0.5845 | 0.6341 | 0.9475 | 0.6948 | -130.7345 | -5.8384 | 0.7946 | -1.0832 | -8.4261 | -6.997 | 0.0138 |  | -2.6707 | -3.3102 | 3.9979 | 3.3664 | 3.3517 | 1.0266 | 10.6606 | 14.1286 | 14.7327 | 11.0363 | -0.0001 | -0.0024 | 0.0006 | 0.0038 | 0.0008 | -0.0004 | 0.0173 | -0.0088 | 0.0076 | -360.245 | 17.489 | -360.5466 | 17.7683 | -360.8974 | 18.0968 | -360.9712 | 17.5835 | -352.8444 | 18.721 | -352.8075 | 16.795
11:45 | 1539 | 22.5199 | 195.1782 | 436.0973 | 441.6716 | -21.332 | -46.9178 | 2.0563 | 0.3678 | -6.8815 | -7.1725 | -2.8046 | -4.292 | 2.6223 | -4.2044 | 0.5849 | 0.63 | 0.9487 | 0.694 | -130.653 | -5.7445 | 0.7737 | -1.127 | -8.3542 | -6.9764 | -0.0047 |  | -2.7221 | -3.3789 | 3.9992 | 3.3667 | 3.3517 | 1.0272 | 10.6548 | 14.1056 | 14.6817 | 11.0186 | 0.0002 | -0.0029 | 0.0005 | 0.0038 | 0.0008 | 0.0001 | 0.0005 | -0.0186 | 0.0047 | -360.1958 | 17.5013 | -360.5558 | 17.7539 | -360.8666 | 18.0721 | -360.9804 | 17.5896 | -352.8691 | 18.7477 | -352.8167 | 16.7766
11:45 | 1540 | 22.5375 | 195.1949 | 436.114 | 441.6639 | -21.2656 | -47.0168 | 2.0366 | 0.3343 | -6.9347 | -7.1159 | -2.8054 | -4.3211 | 2.6495 | -4.2126 | 0.5849 | 0.6347 | 0.9507 | 0.694 | -130.685 | -5.7839 | 0.8441 | -1.1566 | -8.3554 | -7.0251 | -0.0028 |  | -2.5535 | -3.2486 | 3.9989 | 3.3685 | 3.3562 | 1.0275 | 10.6434 | 14.1226 | 14.719 | 11.0197 | 0 | -0.0029 | 0.0003 | 0.0037 | 0.0005 | -0.001 | 0 | -0.0123 | -0.0081 | -360.205 | 17.5055 | -360.5527 | 17.7724 | -360.8912 | 18.0804 | -360.9374 | 17.5855 | -352.8475 | 18.7436 | -352.8352 | 16.7807
11:45 | 1541 | 22.5348 | 195.1489 | 436.1112 | 441.746 | -21.3104 | -46.9734 | 2.0571 | 0.3324 | -6.8668 | -7.0292 | -2.7705 | -4.3811 | 2.6107 | -4.1947 | 0.584 | 0.633 | 0.9503 | 0.6948 | -130.6908 | -5.7712 | 0.8323 | -1.1354 | -8.3342 | -7.0408 | 0.0119 |  | -2.6824 | -3.2891 | 3.9993 | 3.3663 | 3.3533 | 1.026 | 10.5823 | 14.0722 | 14.6413 | 10.966 | -0.0005 | -0.0031 | 0.0008 | 0.0034 | 0.0002 | -0.0005 | 0.0035 | -0.0056 | -0.0066 | -360.125 | 17.489 | -360.5496 | 17.7888 | -360.9097 | 18.0906 | -360.9497 | 17.565 | -352.7921 | 18.7353 | -352.8475 | 16.8094
11:45 | 1542 | 22.4899 | 195.1045 | 436.1981 | 441.7703 | -21.3163 | -46.9692 | 1.9634 | 0.3524 | -6.9224 | -7.1045 | -2.8479 | -4.207 | 2.7034 | -4.187 | 0.5841 | 0.6313 | 0.9503 | 0.6956 | -130.6633 | -5.8212 | 0.9004 | -1.1822 | -8.3203 | -6.9716 | -0.0686 |  | -2.6858 | -3.2339 | 3.9985 | 3.3639 | 3.3523 | 1.0267 | 10.5995 | 14.09 | 14.6792 | 11.0053 | -0.0005 | -0.0028 | 0.0007 | 0.0039 | 0.0008 | -0.0007 | 0.0031 | -0.0078 | 0.0093 | -360.1619 | 17.4788 | -360.5127 | 17.7642 | -360.9035 | 18.1112 | -360.9343 | 17.5712 | -352.7921 | 18.723 | -352.7921 | 16.7766
11:45 | 1543 | 22.459 | 195.1599 | 436.0453 | 441.7102 | -21.4688 | -47.0199 | 1.9579 | 0.394 | -6.8548 | -7.0985 | -2.8303 | -4.2516 | 2.7391 | -4.2041 | 0.5849 | 0.63 | 0.9483 | 0.6953 | -130.7342 | -5.7577 | 0.8746 | -1.1238 | -8.3533 | -6.9823 | 0.029 |  | -2.6175 | -3.2294 | 3.9992 | 3.3642 | 3.3484 | 1.0275 | 10.5974 | 14.0525 | 14.598 | 10.9523 | 0.0003 | -0.0025 | 0.0008 | 0.0034 | 0.0003 | -0.0004 | 0.0008 | -0.0248 | -0.0065 | -360.1742 | 17.4829 | -360.5527 | 17.7785 | -360.9281 | 18.0824 | -360.9958 | 17.5958 | -352.8137 | 18.7395 | -352.829 | 16.7991
11:45 | 1544 | 22.4172 | 195.192 | 435.9975 | 441.68 | -21.4315 | -47.1124 | 1.9569 | 0.3832 | -6.8789 | -7.0969 | -2.8376 | -4.2536 | 2.7434 | -4.1828 | 0.5853 | 0.6324 | 0.9509 | 0.6933 | -130.7323 | -5.7484 | 0.7739 | -1.1438 | -8.4569 | -7.0971 | 0.0096 |  | -2.5935 | -3.1991 | 3.9985 | 3.362 | 3.3517 | 1.0277 | 10.6169 | 14.0784 | 14.6502 | 10.9937 | 0 | -0.0033 | 0.0012 | 0.0039 | 0.001 | -0.0007 | 0.0156 | 0.0078 | -0.0039 | -360.1742 | 17.5075 | -360.5558 | 17.758 | -360.8666 | 18.066 | -360.9497 | 17.5671 | -352.8198 | 18.7518 | -352.8014 | 16.7663
11:45 | 1545 | 22.503 | 195.201 | 436.0572 | 441.8189 | -21.4846 | -47.1272 | 1.9537 | 0.3864 | -6.8326 | -7.1028 | -2.799 | -4.2219 | 2.7066 | -4.1544 | 0.5856 | 0.6323 | 0.9457 | 0.6956 | -130.7432 | -5.8496 | 0.7955 | -1.2309 | -8.5249 | -7.0916 | -0.0405 |  | -2.6564 | -3.2556 | 3.9984 | 3.3642 | 3.351 | 1.0285 | 10.6261 | 14.0704 | 14.6659 | 11.0143 | 0 | -0.003 | 0.0005 | 0.0036 | 0.0007 | -0.0004 | 0.0182 | -0.005 | -0.0094 | -360.2481 | 17.5198 | -360.5773 | 17.8052 | -360.9251 | 18.0906 | -360.9497 | 17.5855 | -352.8383 | 18.762 | -352.866 | 16.8135
11:45 | 1546 | 22.4281 | 195.1238 | 436.1206 | 441.7682 | -21.4048 | -47.1112 | 1.9335 | 0.3622 | -6.9136 | -7.0745 | -2.7345 | -4.2771 | 2.7599 | -4.1791 | 0.5844 | 0.6316 | 0.946 | 0.6936 | -130.7077 | -5.8706 | 0.7455 | -1.2737 | -8.3656 | -7.0642 | 0.0597 |  | -2.4982 | -3.1515 | 3.9997 | 3.3656 | 3.3501 | 1.0284 | 10.6422 | 14.0984 | 14.7014 | 11.0182 | -0.0004 | -0.0026 | 0.0004 | 0.0038 | 0.0008 | -0.0003 | 0.0054 | -0.0122 | -0.0123 | -360.1342 | 17.4911 | -360.5558 | 17.7703 | -360.8635 | 18.0804 | -360.9189 | 17.5609 | -352.786 | 18.7436 | -352.8167 | 16.793
11:45 | 1547 | 22.4849 | 195.0686 | 436.1921 | 441.8209 | -21.4646 | -47.0782 | 1.9159 | 0.4115 | -6.8168 | -7.0312 | -2.6959 | -4.2543 | 2.6943 | -4.1527 | 0.5845 | 0.6335 | 0.9509 | 0.6947 | -130.72 | -5.8042 | 0.7888 | -1.15 | -8.3456 | -6.9564 | -0.0181 |  | -2.5616 | -3.1533 | 4 | 3.3693 | 3.3543 | 1.0284 | 10.6386 | 14.1471 | 14.7225 | 11.0374 | -0.0006 | -0.0029 | 0.0006 | 0.0036 | 0.0008 | -0.0004 | 0.0071 | 0.0045 | -0.0084 | -360.2204 | 17.5116 | -360.5589 | 17.7806 | -360.9035 | 18.105 | -360.9804 | 17.5876 | -352.8229 | 18.7497 | -352.829 | 16.793
11:46 | 1548 | 22.5222 | 195.1195 | 436.2285 | 441.7753 | -21.5114 | -47.2221 | 1.884 | 0.4381 | -6.8361 | -7.0486 | -2.6945 | -4.1907 | 2.691 | -4.2329 | 0.5849 | 0.6343 | 0.9505 | 0.6965 | -130.6652 | -5.737 | 0.85 | -1.0899 | -8.3641 | -6.904 | 0.0436 |  | -2.5372 | -3.1343 | 3.9999 | 3.3633 | 3.3469 | 1.0288 | 10.6422 | 14.1272 | 14.735 | 11.036 | 0.0001 | -0.003 | 0.0002 | 0.0036 | 0.0003 | -0.0005 | 0.0209 | -0.0063 | -0.0087 | -360.1742 | 17.489 | -360.5281 | 17.7744 | -360.8697 | 18.066 | -360.9343 | 17.5794 | -352.8137 | 18.7436 | -352.8075 | 16.8032
11:46 | 1549 | 22.609 | 195.1758 | 436.2243 | 441.7918 | -21.388 | -47.0168 | 1.8662 | 0.4605 | -6.8121 | -7.0296 | -2.7516 | -4.1965 | 2.7186 | -4.1471 | 0.585 | 0.6308 | 0.9487 | 0.6944 | -130.644 | -5.7703 | 0.7978 | -1.1155 | -8.4607 | -7.0725 | -0.0476 |  | -2.5036 | -3.2119 | 3.9988 | 3.3667 | 3.3532 | 1.0267 | 10.648 | 14.1329 | 14.735 | 11.0186 | -0.0002 | -0.0032 | 0.0009 | 0.0038 | 0.0009 | -0.0007 | 0.0098 | -0.0173 | -0.0095 | -360.1804 | 17.4952 | -360.5527 | 17.7683 | -360.8697 | 18.0927 | -360.9774 | 17.5691 | -352.746 | 18.7395 | -352.8352 | 16.7971
11:46 | 1550 | 22.5501 | 195.1017 | 436.2369 | 441.7674 | -21.4581 | -47.0534 | 1.9488 | 0.4492 | -6.8848 | -7.1163 | -2.7894 | -4.1759 | 2.6916 | -4.1533 | 0.5833 | 0.6324 | 0.948 | 0.6944 | -130.6227 | -5.7437 | 0.8295 | -1.0789 | -8.3784 | -7.0907 | -0.0208 |  | -2.5396 | -3.0805 | 3.9992 | 3.3683 | 3.3532 | 1.0276 | 10.6029 | 14.0877 | 14.718 | 11.0028 | -0.0006 | -0.0032 | 0.0011 | 0.0038 | 0.0006 | -0.0004 | 0.0014 | -0.0101 | -0.0134 | -360.2173 | 17.5034 | -360.5619 | 17.7867 | -360.9251 | 18.0968 | -360.962 | 17.5917 | -352.826 | 18.7518 | -352.8567 | 16.8156
11:46 | 1551 | 22.5956 | 195.1285 | 436.1585 | 441.8044 | -21.4479 | -47.0598 | 2.0166 | 0.4726 | -6.9128 | -7.0763 | -2.7436 | -4.164 | 2.6744 | -4.1342 | 0.5857 | 0.6353 | 0.9506 | 0.6951 | -130.5995 | -5.7692 | 0.8326 | -1.117 | -8.3972 | -7.1637 | -0.0511 |  | -2.5782 | -3.1456 | 3.9988 | 3.3656 | 3.3537 | 1.0275 | 10.6123 | 14.0505 | 14.6853 | 10.9952 | -0.0008 | -0.0033 | 0.0005 | 0.0033 | 0.0007 | -0.001 | 0.0027 | -0.0123 | -0.0282 | -360.1588 | 17.4767 | -360.5343 | 17.7744 | -360.8604 | 18.0845 | -360.9681 | 17.5712 | -352.746 | 18.7271 | -352.8044 | 16.7909
11:46 | 1552 | 22.5817 | 195.1842 | 436.1124 | 441.8552 | -21.434 | -47.0786 | 1.9617 | 0.3564 | -6.9584 | -7.0734 | -2.8116 | -4.169 | 2.5533 | -4.1945 | 0.5848 | 0.6324 | 0.948 | 0.6945 | -130.6579 | -5.8474 | 0.8413 | -1.095 | -8.3273 | -7.0821 | -0.0476 |  | -2.563 | -3.1841 | 4.0005 | 3.3658 | 3.3552 | 1.0287 | 10.5995 | 14.0553 | 14.6618 | 11.0111 | 0.0001 | -0.0028 | 0.001 | 0.0042 | 0.0006 | -0.0003 | 0.0204 | -0.0064 | -0.018 | -360.2081 | 17.5055 | -360.5619 | 17.7847 | -360.9189 | 18.1132 | -360.9681 | 17.5835 | -352.8567 | 18.7538 | -352.8414 | 16.8094
11:46 | 1553 | 22.5751 | 195.2288 | 436.1624 | 441.8147 | -21.397 | -47.1905 | 1.979 | 0.2868 | -6.9194 | -7.0304 | -2.8012 | -4.2272 | 2.6233 | -4.2613 | 0.5845 | 0.6343 | 0.9483 | 0.6949 | -130.713 | -5.8516 | 0.9048 | -1.0935 | -8.28 | -7.0638 | -0.039 |  | -2.5596 | -3.2171 | 3.9998 | 3.3646 | 3.3569 | 1.0296 | 10.6434 | 14.0935 | 14.6601 | 10.9854 | 0 | -0.0032 | 0.0005 | 0.0035 | 0.001 | -0.0007 | 0.001 | -0.0085 | -0.0146 | -360.1835 | 17.4808 | -360.5558 | 17.7703 | -360.8635 | 18.0701 | -360.9189 | 17.5712 | -352.7737 | 18.7312 | -352.8167 | 16.8032
11:46 | 1554 | 22.6587 | 195.2188 | 436.2344 | 441.777 | -21.4251 | -47.198 | 1.974 | 0.2944 | -6.9196 | -6.9568 | -2.7594 | -4.1936 | 2.6681 | -4.1496 | 0.5848 | 0.6321 | 0.9495 | 0.6958 | -130.6623 | -5.8068 | 0.8156 | -1.0673 | -8.3287 | -7.0436 | -0.1439 |  | -2.5606 | -3.2285 | 3.9988 | 3.3662 | 3.3526 | 1.0288 | 10.6006 | 14.0913 | 14.6816 | 11.0291 | -0.0003 | -0.0032 | 0.0003 | 0.0035 | 0.001 | -0.0004 | 0.0013 | -0.0127 | -0.0159 | -360.2235 | 17.5157 | -360.6081 | 17.797 | -360.9251 | 18.1071 | -360.9774 | 17.5753 | -352.826 | 18.76 | -352.8598 | 16.8299
11:46 | 1555 | 22.5563 | 195.1858 | 436.1683 | 441.7872 | -21.433 | -47.0736 | 1.955 | 0.3696 | -6.8653 | -6.9096 | -2.7342 | -4.1054 | 2.7012 | -4.1348 | 0.5858 | 0.6337 | 0.9499 | 0.6955 | -130.7141 | -5.7153 | 0.7331 | -1.19 | -8.3656 | -7.0744 | -0.0598 |  | -2.5778 | -3.2599 | 3.9978 | 3.3649 | 3.3493 | 1.0271 | 10.6363 | 14.0985 | 14.6793 | 11.0063 | -0.0004 | -0.0024 | 0.0008 | 0.0039 | 0.0008 | -0.0005 | -0.0003 | -0.0089 | -0.0289 | -360.1465 | 17.4849 | -360.5466 | 17.7642 | -360.9035 | 18.0824 | -360.9281 | 17.5629 | -352.7583 | 18.7271 | -352.8198 | 16.8074
11:46 | 1556 | 22.6102 | 195.2823 | 436.2648 | 441.8236 | -21.4217 | -47.1437 | 1.9263 | 0.4403 | -6.867 | -7.0124 | -2.7285 | -4.0501 | 2.7402 | -4.1136 | 0.5844 | 0.6343 | 0.95 | 0.6951 | -130.6788 | -5.7412 | 0.7432 | -1.0313 | -8.2961 | -6.9827 | -0.0153 |  | -2.4951 | -3.2038 | 3.9974 | 3.3657 | 3.3527 | 1.0274 | 10.6411 | 14.0913 | 14.7105 | 11.0118 | 0 | -0.0029 | 0.0002 | 0.0032 | 0.0007 | -0.0003 | 0.0137 | -0.0071 | -0.0171 | -360.1865 | 17.5034 | -360.5804 | 17.7826 | -360.885 | 18.105 | -360.9958 | 17.604 | -352.8198 | 18.7333 | -352.8383 | 16.8115
11:46 | 1557 | 22.5906 | 195.2223 | 436.2326 | 441.8766 | -21.3649 | -47.1749 | 1.965 | 0.3548 | -6.9332 | -6.9814 | -2.7181 | -4.1077 | 2.6878 | -4.1004 | 0.5831 | 0.6321 | 0.9516 | 0.6951 | -130.7895 | -5.7792 | 0.7708 | -1.1216 | -8.3531 | -7.0169 | -0.0913 |  | -2.4775 | -3.1515 | 3.9968 | 3.3663 | 3.3484 | 1.0277 | 10.6019 | 14.098 | 14.6866 | 11.0136 | 0.0001 | -0.0029 | 0.0008 | 0.0038 | 0.0006 | -0.0007 | 0.0058 | 0.0019 | -0.0123 | -360.2204 | 17.5013 | -360.5281 | 17.758 | -360.8512 | 18.0701 | -360.9343 | 17.5794 | -352.8075 | 18.7436 | -352.8229 | 16.795
11:46 | 1558 | 22.6421 | 195.2537 | 436.1994 | 441.8271 | -21.3378 | -47.1353 | 2.0173 | 0.3731 | -6.8583 | -6.977 | -2.8015 | -4.1562 | 2.717 | -4.1378 | 0.5848 | 0.6336 | 0.95 | 0.6954 | -130.688 | -5.7647 | 0.7152 | -1.021 | -8.2718 | -6.9591 | -0.0234 |  | -2.5578 | -3.2447 | 3.9986 | 3.366 | 3.3485 | 1.0275 | 10.6226 | 14.0901 | 14.6918 | 11.0396 | -0.0001 | -0.0029 | 0.0012 | 0.004 | 0.0007 | -0.0009 | 0.0194 | 0.0013 | -0.004 | -360.2296 | 17.5034 | -360.5681 | 17.7724 | -360.8912 | 18.0804 | -360.962 | 17.5876 | -352.8506 | 18.7579 | -352.789 | 16.7991
11:46 | 1559 | 22.5982 | 195.2605 | 436.1318 | 441.8154 | -21.3049 | -47.0073 | 2.0299 | 0.4408 | -6.8439 | -7.035 | -2.7585 | -4.1762 | 2.6814 | -4.1682 | 0.5846 | 0.6348 | 0.9493 | 0.6956 | -130.6359 | -5.8011 | 0.7028 | -1.099 | -8.2651 | -6.9182 | 0.019 |  | -2.4412 | -3.2709 | 3.9967 | 3.3631 | 3.353 | 1.0261 | 10.6087 | 14.1052 | 14.6959 | 11.0255 | -0.0003 | -0.0028 | 0.0008 | 0.0035 | 0.0005 | -0.0002 | -0.0016 | -0.009 | -0.0245 | -360.1496 | 17.4952 | -360.5804 | 17.7867 | -360.8789 | 18.0927 | -360.9435 | 17.5588 | -352.7737 | 18.7497 | -352.8444 | 16.8238
11:46 | 1560 | 22.6353 | 195.2271 | 436.172 | 441.8338 | -21.2636 | -47.0227 | 2.0449 | 0.3852 | -6.851 | -7.0038 | -2.7837 | -4.0776 | 2.7846 | -4.0773 | 0.5846 | 0.6337 | 0.9483 | 0.6953 | -130.6978 | -5.8065 | 0.7317 | -1.0936 | -8.2856 | -6.9631 | 0.0546 |  | -2.4327 | -3.1928 | 3.9975 | 3.3685 | 3.3497 | 1.0267 | 10.6156 | 14.0717 | 14.6799 | 11.0208 | -0.0001 | -0.0025 | 0.0008 | 0.0037 | 0.0006 | -0.0013 | 0.0071 | -0.0063 | -0.0083 | -360.1558 | 17.4767 | -360.5281 | 17.7744 | -360.9312 | 18.1071 | -360.9835 | 17.5712 | -352.7952 | 18.7271 | -352.7767 | 16.7909
11:46 | 1561 | 22.6519 | 195.2608 | 436.03 | 441.8728 | -21.3117 | -47.0329 | 1.9953 | 0.4263 | -6.8541 | -6.9279 | -2.7893 | -3.982 | 2.7721 | -4.0378 | 0.585 | 0.6325 | 0.9516 | 0.6942 | -130.7611 | -5.8234 | 0.8101 | -1.0928 | -8.2138 | -6.9989 | 0.0087 |  | -2.5138 | -3.2254 | 3.9998 | 3.3662 | 3.3525 | 1.0285 | 10.626 | 14.1226 | 14.6901 | 11.0255 | -0.0001 | -0.0032 | 0.0007 | 0.004 | 0.0004 | -0.0003 | 0.0056 | -0.0124 | -0.0082 | -360.1804 | 17.4808 | -360.5312 | 17.7724 | -360.9066 | 18.0988 | -361.0143 | 17.6061 | -352.8352 | 18.7333 | -352.829 | 16.8094
11:46 | 1562 | 22.7407 | 195.386 | 436.1294 | 441.9109 | -21.2362 | -46.9393 | 2.0705 | 0.3926 | -6.8283 | -6.9677 | -2.7014 | -3.984 | 2.7481 | -4.0482 | 0.5855 | 0.6339 | 0.9497 | 0.6951 | -130.6839 | -5.8067 | 0.9318 | -1.1207 | -8.2746 | -6.9141 | -0.0261 |  | -2.4982 | -3.2992 | 3.9992 | 3.369 | 3.3524 | 1.0275 | 10.6284 | 14.1132 | 14.7034 | 11.0165 | 0.0008 | -0.0028 | 0.0005 | 0.0037 | 0.0009 | -0.0009 | 0.0116 | -0.0093 | -0.0016 | -360.2173 | 17.5034 | -360.5558 | 17.7559 | -360.8543 | 18.0578 | -360.9343 | 17.5712 | -352.7521 | 18.7538 | -352.8106 | 16.7889
11:46 | 1563 | 22.674 | 195.2935 | 436.165 | 441.9279 | -21.2513 | -46.9449 | 2.0816 | 0.463 | -6.8196 | -6.8449 | -2.7669 | -4.0359 | 2.637 | -4.1039 | 0.5855 | 0.6313 | 0.9483 | 0.6961 | -130.6912 | -5.74 | 0.8754 | -0.8924 | -8.212 | -6.9993 | -0.0147 |  | -2.4581 | -3.2026 | 3.9978 | 3.3661 | 3.3513 | 1.0276 | 10.6411 | 14.0682 | 14.6932 | 10.9887 | -0.0002 | -0.0027 | 0.0005 | 0.0039 | 0.0004 | -0.0004 | 0.0081 | -0.0163 | -0.0031 | -360.165 | 17.5055 | -360.6173 | 17.8155 | -360.9466 | 18.0804 | -360.9743 | 17.5773 | -352.8137 | 18.7518 | -352.8721 | 16.832
11:46 | 1564 | 22.6963 | 195.2157 | 436.2967 | 441.9436 | -21.3024 | -46.9614 | 2.1215 | 0.464 | -6.7838 | -6.8023 | -2.6706 | -4.0603 | 2.6296 | -4.0866 | 0.5853 | 0.6311 | 0.952 | 0.6955 | -130.6472 | -5.6251 | 0.8793 | -0.9342 | -8.2352 | -6.9451 | 0.0108 |  | -2.5047 | -3.2756 | 3.9994 | 3.365 | 3.3504 | 1.0281 | 10.6168 | 14.0554 | 14.686 | 10.9818 | -0.0003 | -0.0026 | 0.0005 | 0.0037 | 0.0004 | -0.0007 | -0.0078 | -0.0009 | -0.0251 | -360.1373 | 17.4911 | -360.5435 | 17.7826 | -360.9035 | 18.0906 | -360.9312 | 17.5486 | -352.7737 | 18.7333 | -352.8167 | 16.8156
11:46 | 1565 | 22.7301 | 195.2347 | 436.1729 | 441.9196 | -21.3594 | -46.9367 | 2.1006 | 0.4285 | -6.8893 | -7.0179 | -2.6929 | -4.0815 | 2.6871 | -4.1555 | 0.5853 | 0.6311 | 0.9503 | 0.6957 | -130.6374 | -5.6917 | 0.7643 | -0.9345 | -8.2136 | -7.0116 | 0.0105 |  | -2.5636 | -3.2744 | 3.9983 | 3.3662 | 3.3493 | 1.0281 | 10.6377 | 14.0876 | 14.7343 | 11.032 | -0.0001 | -0.0033 | 0.0003 | 0.0037 | 0.0002 | -0.0009 | -0.0037 | -0.0133 | -0.0105 | -360.2296 | 17.487 | -360.5466 | 17.7724 | -360.9004 | 18.0988 | -361.0051 | 17.5937 | -352.8014 | 18.7395 | -352.8137 | 16.795
11:46 | 1566 | 22.7041 | 195.212 | 436.0772 | 442.0155 | -21.3026 | -46.9008 | 2.1884 | 0.4189 | -6.8532 | -6.9121 | -2.7312 | -4.0147 | 2.7873 | -4.1384 | 0.5845 | 0.6321 | 0.949 | 0.6938 | -130.675 | -5.7155 | 0.8178 | -1.0143 | -8.2376 | -6.9993 | -0.0396 |  | -2.5354 | -3.1977 | 3.9987 | 3.3675 | 3.3509 | 1.0281 | 10.641 | 14.103 | 14.7174 | 11.0114 | -0.0001 | -0.0032 | 0.0012 | 0.004 | 0.0004 | 0 | 0.0172 | 0.0004 | 0.0078 | -360.2265 | 17.5116 | -360.5835 | 17.7724 | -360.8358 | 18.0763 | -360.9712 | 17.5855 | -352.866 | 18.7661 | -352.8414 | 16.8053
11:46 | 1567 | 22.7172 | 195.2076 | 436.1491 | 442.0131 | -21.2401 | -46.8745 | 2.1492 | 0.4482 | -6.8365 | -6.928 | -2.777 | -4.0334 | 2.7841 | -4.0865 | 0.5847 | 0.6336 | 0.9539 | 0.6953 | -130.6885 | -5.7087 | 0.7513 | -0.9004 | -8.2813 | -7.0055 | 0.0412 |  | -2.4761 | -3.1068 | 3.9998 | 3.3662 | 3.3552 | 1.0272 | 10.6019 | 14.1095 | 14.6924 | 11.0252 | -0.0005 | -0.0032 | 0.0007 | 0.0033 | 0.0006 | -0.0009 | 0.0021 | -0.0065 | -0.0152 | -360.1988 | 17.4993 | -360.5373 | 17.7703 | -360.882 | 18.0598 | -360.9158 | 17.5691 | -352.789 | 18.7456 | -352.8137 | 16.7971
11:46 | 1568 | 22.746 | 195.2598 | 436.3374 | 442.0281 | -21.2491 | -46.763 | 2.1888 | 0.4531 | -6.8579 | -6.9619 | -2.7753 | -4.0524 | 2.7406 | -4.0291 | 0.5853 | 0.6289 | 0.9523 | 0.6952 | -130.695 | -5.704 | 0.8194 | -0.8998 | -8.1605 | -6.9585 | 0.0528 |  | -2.4512 | -3.2103 | 3.9986 | 3.3643 | 3.3542 | 1.0284 | 10.6193 | 14.063 | 14.6614 | 10.9913 | -0.0005 | -0.0031 | 0.0007 | 0.0033 | 0.0007 | -0.0004 | 0.0065 | -0.002 | 0.0048 | -360.1496 | 17.5013 | -360.5773 | 17.8032 | -360.9558 | 18.1132 | -360.9681 | 17.5753 | -352.7921 | 18.7518 | -352.8629 | 16.8299
11:46 | 1569 | 22.6828 | 195.264 | 436.2188 | 442.0511 | -21.1985 | -46.9064 | 2.1412 | 0.4782 | -6.8177 | -6.9281 | -2.7995 | -4.0574 | 2.7532 | -3.9371 | 0.5858 | 0.6328 | 0.9511 | 0.696 | -130.5775 | -5.5709 | 0.8165 | -0.9648 | -8.0879 | -6.9526 | 0.0691 |  | -2.4906 | -3.2445 | 4.0006 | 3.3644 | 3.3516 | 1.0282 | 10.6445 | 14.095 | 14.6867 | 11.0377 | 0 | -0.0028 | 0.0007 | 0.0036 | 0.0007 | -0.0011 | 0.0117 | -0.0057 | -0.0068 | -360.1711 | 17.4644 | -360.4912 | 17.7498 | -360.8727 | 18.1112 | -360.9897 | 17.5814 | -352.8075 | 18.721 | -352.7798 | 16.793
11:46 | 1570 | 22.6916 | 195.2161 | 436.2141 | 441.9587 | -21.2433 | -46.8938 | 2.1664 | 0.4759 | -6.8644 | -6.9791 | -2.7671 | -4.0836 | 2.7586 | -4.0731 | 0.5858 | 0.6333 | 0.9532 | 0.697 | -130.6436 | -5.5973 | 0.8025 | -0.8748 | -8.1096 | -6.8302 | 0.1025 |  | -2.496 | -3.169 | 3.9993 | 3.3666 | 3.3551 | 1.0289 | 10.6516 | 14.1129 | 14.7186 | 11.0346 | 0 | -0.0035 | -0.0001 | 0.0035 | 0.0004 | -0.0007 | 0.0013 | -0.0082 | -0.0068 | -360.1896 | 17.489 | -360.5466 | 17.758 | -360.8666 | 18.0988 | -361.0112 | 17.5937 | -352.8137 | 18.7436 | -352.7952 | 16.7827
11:46 | 1571 | 22.7401 | 195.3079 | 436.1972 | 442.0798 | -21.2736 | -46.9903 | 2.1535 | 0.5134 | -6.7951 | -6.9641 | -2.8122 | -4.008 | 2.7694 | -3.9765 | 0.5844 | 0.6313 | 0.9502 | 0.6974 | -130.7226 | -5.6476 | 0.7881 | -0.9799 | -8.2339 | -6.832 | 0.0406 |  | -2.4265 | -3.1742 | 4.0005 | 3.3642 | 3.3527 | 1.0271 | 10.6225 | 14.1018 | 14.7044 | 11.0276 | -0.0002 | -0.0033 | 0.0005 | 0.0039 | 0.0008 | -0.0007 | 0.0053 | -0.017 | -0.0243 | -360.205 | 17.5096 | -360.5958 | 17.795 | -360.9189 | 18.0824 | -360.9343 | 17.5691 | -352.8321 | 18.7661 | -352.8598 | 16.8258
11:46 | 1572 | 22.7517 | 195.2473 | 436.2642 | 442.0744 | -21.2927 | -47.1094 | 2.0162 | 0.4095 | -6.8033 | -6.9804 | -2.8565 | -3.9357 | 2.8861 | -3.9706 | 0.5846 | 0.6288 | 0.9495 | 0.6977 | -130.6185 | -5.6391 | 0.7633 | -0.7677 | -8.2256 | -6.8166 | 0.0903 |  | -2.4993 | -3.0819 | 4.0008 | 3.3637 | 3.3494 | 1.029 | 10.6513 | 14.1427 | 14.7076 | 11.0149 | -0.0005 | -0.0026 | 0.0008 | 0.004 | 0.0007 | -0.0001 | -0.0089 | -0.0114 | 0.0107 | -360.1342 | 17.4664 | -360.5435 | 17.7847 | -360.9066 | 18.0906 | -360.9343 | 17.5404 | -352.7337 | 18.7189 | -352.8137 | 16.8197
11:46 | 1573 | 22.7004 | 195.3555 | 436.2065 | 442.0629 | -21.3171 | -46.9652 | 2.1194 | 0.444 | -6.8674 | -6.958 | -2.8342 | -3.918 | 2.9816 | -3.9372 | 0.5828 | 0.6304 | 0.9501 | 0.6965 | -130.6593 | -5.6477 | 0.8397 | -0.8848 | -8.2442 | -6.7885 | 0.059 |  | -2.5358 | -3.2261 | 3.9992 | 3.3666 | 3.3516 | 1.0302 | 10.6446 | 14.1409 | 14.702 | 11.0212 | -0.0008 | -0.003 | 0.0004 | 0.0037 | 0.0003 | -0.0005 | 0.0087 | -0.0189 | -0.004 | -360.1804 | 17.4952 | -360.5589 | 17.7806 | -360.9466 | 18.1235 | -360.9774 | 17.5876 | -352.7921 | 18.7374 | -352.8321 | 16.8217
11:46 | 1574 | 22.6981 | 195.3293 | 436.2761 | 442.0663 | -21.2711 | -47.0341 | 2.1405 | 0.4391 | -6.8882 | -6.9768 | -2.7919 | -3.9122 | 2.9676 | -3.9898 | 0.5849 | 0.6342 | 0.9466 | 0.6961 | -130.7512 | -5.6933 | 0.8044 | -0.9217 | -8.2568 | -6.7903 | 0.0757 |  | -2.4837 | -3.2327 | 3.9989 | 3.3647 | 3.3488 | 1.0285 | 10.6466 | 14.1034 | 14.7205 | 11.0334 | 0 | -0.0028 | 0.0013 | 0.0042 | 0.0009 | -0.0003 | -0.0025 | -0.0084 | 0.0052 | -360.1865 | 17.4829 | -360.5066 | 17.7395 | -360.8604 | 18.0639 | -360.9404 | 17.5855 | -352.7983 | 18.7374 | -352.8106 | 16.7848
11:46 | 1575 | 22.7216 | 195.3474 | 436.2269 | 442.125 | -21.232 | -46.9055 | 2.1748 | 0.5533 | -6.8921 | -6.9764 | -2.7461 | -3.9166 | 2.9219 | -3.9341 | 0.5848 | 0.6331 | 0.948 | 0.6968 | -130.751 | -5.7012 | 0.8062 | -0.9442 | -8.2082 | -6.8399 | 0.168 |  | -2.5522 | -3.1851 | 4 | 3.3613 | 3.3499 | 1.0286 | 10.6076 | 14.0922 | 14.6693 | 10.979 | 0 | -0.0033 | 0.0009 | 0.0036 | 0.0003 | -0.0007 | 0.0063 | -0.0102 | -0.0179 | -360.1988 | 17.526 | -360.6143 | 17.7765 | -360.9097 | 18.0721 | -360.9097 | 17.5691 | -352.8475 | 18.7826 | -352.8721 | 16.8135
11:46 | 1576 | 22.8384 | 195.3248 | 436.2598 | 442.125 | -21.2124 | -46.959 | 2.1247 | 0.5376 | -6.8003 | -7.0683 | -2.6769 | -3.978 | 2.885 | -4.1611 | 0.5837 | 0.634 | 0.9497 | 0.6991 | -130.6797 | -5.5905 | 0.8696 | -0.9009 | -8.3119 | -6.776 | 0.1571 |  | -2.476 | -3.1704 | 3.9996 | 3.3686 | 3.3497 | 1.0295 | 10.6019 | 14.1095 | 14.6693 | 11.0078 | -0.0003 | -0.0029 | 0.0007 | 0.004 | 0.0007 | -0.0009 | 0.0174 | -0.0112 | -0.0043 | -360.1742 | 17.489 | -360.5681 | 17.7765 | -360.9004 | 18.0639 | -360.9343 | 17.5609 | -352.8044 | 18.7456 | -352.8537 | 16.8258
11:46 | 1577 | 22.745 | 195.2325 | 436.2753 | 442.0574 | -21.175 | -46.94 | 2.0782 | 0.4797 | -6.8118 | -7.0505 | -2.7986 | -4.001 | 2.8345 | -4.0995 | 0.5838 | 0.6304 | 0.9513 | 0.6974 | -130.7249 | -5.6272 | 0.8329 | -0.8249 | -8.2286 | -6.8231 | 0.1802 |  | -2.5668 | -3.2431 | 3.999 | 3.3652 | 3.3504 | 1.0294 | 10.6052 | 14.0787 | 14.6523 | 11.0103 | 0 | -0.0025 | 0.0006 | 0.0036 | 0.0004 | -0.0002 | 0.0092 | -0.0179 | -0.018 | -360.1681 | 17.4623 | -360.5066 | 17.7457 | -360.9066 | 18.1009 | -360.9743 | 17.5712 | -352.7737 | 18.7251 | -352.7706 | 16.7889
11:46 | 1578 | 22.7745 | 195.2697 | 436.236 | 442.1281 | -21.158 | -46.9531 | 2.147 | 0.5594 | -6.794 | -7.0288 | -2.7146 | -4.0247 | 2.8074 | -4.1822 | 0.585 | 0.6327 | 0.9472 | 0.6983 | -130.7242 | -5.5691 | 0.9082 | -0.9042 | -8.1711 | -6.7063 | 0.2214 |  | -2.5259 | -3.2109 | 3.9994 | 3.3647 | 3.3481 | 1.031 | 10.6389 | 14.1177 | 14.7067 | 11.0331 | -0.0003 | -0.0031 | 0.0003 | 0.0034 | 0.0006 | -0.001 | -0.0038 | -0.0018 | -0.0138 | -360.2081 | 17.4952 | -360.5373 | 17.7293 | -360.882 | 18.0988 | -361.0051 | 17.6102 | -352.8567 | 18.7641 | -352.8167 | 16.7889
11:46 | 1579 | 22.8104 | 196.2441 | 436.2261 | 442.0634 | -21.2309 | -47.0015 | 2.1373 | 0.4852 | -6.7733 | -6.9838 | -2.7065 | -3.9801 | 2.8022 | -4.1621 | 0.5847 | 0.6306 | 0.9501 | 0.6981 | -130.7582 | -5.5443 | 0.8217 | -0.752 | -8.1711 | -6.7015 | 0.2244 |  | -2.5195 | -3.2672 | 3.9985 | 3.364 | 3.3488 | 1.0305 | 10.6376 | 14.111 | 14.6843 | 10.985 | 0.0005 | -0.003 | 0.0009 | 0.0041 | 0.0006 | -0.0001 | 0.0274 | -0.0031 | 0.0045 | -360.1681 | 17.4952 | -360.5312 | 17.7272 | -360.842 | 18.0845 | -360.9343 | 17.5794 | -352.789 | 18.7456 | -352.7952 | 16.7827
11:46 | 1580 | 22.8076 | 198.545 | 436.2504 | 442.103 | -21.3256 | -46.9537 | 2.0449 | 0.4647 | -6.7426 | -7.0249 | -2.7871 | -3.9753 | 2.8432 | -4.0202 | 0.5845 | 0.6318 | 0.9507 | 0.6992 | -130.7626 | -5.6208 | 0.763 | -0.7389 | -8.1614 | -6.7165 | 0.2129 |  | -2.439 | -3.178 | 3.9978 | 3.3652 | 3.3521 | 1.0306 | 10.6456 | 14.1193 | 14.717 | 11.033 | -0.0001 | -0.0029 | 0.0009 | 0.004 | 0.0008 | -0.0006 | 0.0073 | 0.0059 | -0.0196 | -360.1742 | 17.5096 | -360.6112 | 17.8032 | -360.9651 | 18.1173 | -360.9558 | 17.5773 | -352.8229 | 18.7538 | -352.8875 | 16.8443
11:46 | 1581 | 22.8125 | 197.8495 | 436.3548 | 442.1943 | -21.2137 | -47.0081 | 2.154 | 0.5234 | -6.796 | -7.0976 | -2.6926 | -3.9532 | 2.9221 | -4.0318 | 0.5852 | 0.6342 | 0.9523 | 0.697 | -130.7151 | -5.5958 | 0.8963 | -0.7038 | -8.106 | -6.629 | 0.2596 |  | -2.4722 | -3.249 | 3.9989 | 3.3627 | 3.3496 | 1.0288 | 10.6537 | 14.1159 | 14.6908 | 11.0352 | -0.0004 | -0.0024 | 0.0009 | 0.0039 | 0.0007 | -0.0004 | 0.0138 | -0.0155 | -0.023 | -360.0973 | 17.4541 | -360.525 | 17.7642 | -360.8974 | 18.1317 | -360.9589 | 17.565 | -352.7275 | 18.7004 | -352.786 | 16.8197
11:46 | 1582 | 22.8384 | 197.3247 | 436.1917 | 442.1054 | -21.3118 | -46.9576 | 2.17 | 0.4748 | -6.8563 | -7.0662 | -2.7626 | -3.8832 | 2.8991 | -4.0242 | 0.5851 | 0.6307 | 0.951 | 0.6968 | -130.7108 | -5.5632 | 0.9237 | -0.6869 | -8.1155 | -6.6898 | 0.274 |  | -2.4273 | -3.219 | 3.9995 | 3.3636 | 3.3502 | 1.0298 | 10.6422 | 14.0753 | 14.6898 | 10.9951 | -0.0004 | -0.0027 | 0.0006 | 0.0036 | 0.0008 | -0.0005 | 0.0251 | 0.0017 | 0.0012 | -360.205 | 17.4808 | -360.5404 | 17.7703 | -360.9281 | 18.1358 | -360.9958 | 17.5999 | -352.8383 | 18.7436 | -352.8075 | 16.8074
11:46 | 1583 | 22.8093 | 196.8518 | 436.1958 | 442.1129 | -21.3327 | -46.9741 | 2.1272 | 0.4561 | -6.8347 | -6.9931 | -2.7957 | -3.911 | 2.8782 | -4.0243 | 0.584 | 0.6324 | 0.9518 | 0.6985 | -130.7494 | -5.5139 | 0.9242 | -0.6935 | -8.1169 | -6.6523 | 0.2684 |  | -2.4155 | -3.1534 | 3.9985 | 3.3653 | 3.3502 | 1.0297 | 10.6353 | 14.1144 | 14.7047 | 11.0464 | 0.0003 | -0.0028 | 0.0008 | 0.0037 | 0.0004 | -0.0011 | 0.0002 | -0.0167 | -0.0136 | -360.1958 | 17.5075 | -360.5527 | 17.7498 | -360.8512 | 18.0886 | -360.922 | 17.5835 | -352.8198 | 18.762 | -352.829 | 16.7991
11:46 | 1584 | 22.8707 | 195.8828 | 436.2666 | 442.1686 | -21.219 | -46.948 | 2.2077 | 0.4107 | -6.8088 | -6.9115 | -2.7759 | -3.9767 | 2.9274 | -3.9621 | 0.5831 | 0.6291 | 0.9517 | 0.6981 | -130.7341 | -5.5914 | 0.8603 | -0.7637 | -8.0669 | -6.7353 | 0.2196 |  | -2.3924 | -3.1828 | 3.9987 | 3.3616 | 3.3493 | 1.0298 | 10.603 | 14.076 | 14.6822 | 10.9743 | -0.0002 | -0.0032 | 0.001 | 0.0037 | 0.0007 | -0.0003 | -0.0035 | -0.0006 | -0.0339 | -360.1742 | 17.5116 | -360.5989 | 17.7847 | -360.9127 | 18.0968 | -360.9004 | 17.5609 | -352.7798 | 18.76 | -352.8783 | 16.8197
11:46 | 1585 | 22.83 | 195.5442 | 436.2506 | 442.1424 | -21.2236 | -47.0478 | 2.1379 | 0.5162 | -6.8515 | -7.0198 | -2.7389 | -4.0105 | 2.919 | -4.0039 | 0.5853 | 0.6312 | 0.9535 | 0.6975 | -130.6641 | -5.5448 | 0.9045 | -0.7045 | -8.0742 | -6.7535 | 0.2518 |  | -2.4117 | -3.1623 | 3.9988 | 3.3661 | 3.3482 | 1.0299 | 10.595 | 14.0677 | 14.6784 | 10.9956 | -0.0005 | -0.003 | 0.0009 | 0.004 | 0.0005 | -0.0015 | 0.0116 | -0.019 | -0.0086 | -360.1742 | 17.4849 | -360.565 | 17.7744 | -360.9251 | 18.1296 | -360.9497 | 17.5691 | -352.7767 | 18.7477 | -352.8475 | 16.8299
11:46 | 1586 | 22.8858 | 195.5188 | 436.2719 | 442.2054 | -21.2657 | -47.0833 | 2.0896 | 0.4539 | -6.8854 | -6.9493 | -2.7616 | -4.051 | 2.8801 | -4.0659 | 0.585 | 0.6328 | 0.9513 | 0.6982 | -130.61 | -5.5486 | 0.8503 | -0.8393 | -8.0688 | -6.7446 | 0.2475 |  | -2.3673 | -3.2145 | 3.9995 | 3.3633 | 3.3545 | 1.0299 | 10.6007 | 14.0621 | 14.6563 | 10.9952 | -0.0001 | -0.0019 | 0.0005 | 0.0038 | 0.0003 | -0.0004 | 0.0035 | -0.0198 | -0.0102 | -360.1865 | 17.4767 | -360.4973 | 17.7518 | -360.8758 | 18.1112 | -360.9681 | 17.5773 | -352.8198 | 18.7189 | -352.7798 | 16.7807
11:46 | 1587 | 22.8221 | 195.2084 | 436.2411 | 442.1751 | -21.3195 | -47.137 | 2.1564 | 0.4921 | -6.8316 | -6.98 | -2.7496 | -4.0552 | 2.8437 | -4.0606 | 0.5843 | 0.6333 | 0.951 | 0.6983 | -130.589 | -5.5028 | 0.9157 | -0.9274 | -8.103 | -6.8047 | 0.2493 |  | -2.4896 | -3.2086 | 3.9998 | 3.3618 | 3.3501 | 1.0292 | 10.6238 | 14.1143 | 14.6747 | 11.0295 | -0.0002 | -0.0031 | 0.001 | 0.0042 | 0.0009 | -0.0011 | 0.012 | -0.0079 | -0.0061 | -360.2573 | 17.5034 | -360.5712 | 17.7539 | -360.8758 | 18.1132 | -360.9835 | 17.5937 | -352.8752 | 18.7559 | -352.829 | 16.7971
11:46 | 1588 | 22.9065 | 195.0158 | 436.3238 | 442.2602 | -21.266 | -47.1737 | 2.2072 | 0.4949 | -6.8886 | -6.9989 | -2.7682 | -4.0156 | 2.9465 | -4.021 | 0.5853 | 0.6317 | 0.9495 | 0.6977 | -130.6425 | -5.4729 | 0.9581 | -1.0196 | -8.1161 | -6.9168 | 0.2075 |  | -2.4087 | -3.0908 | 3.9998 | 3.3641 | 3.354 | 1.0289 | 10.6399 | 14.0612 | 14.6686 | 11.0165 | 0.0001 | -0.003 | 0.0004 | 0.0036 | 0.0009 | -0.0001 | 0.0165 | -0.0036 | -0.0122 | -360.1342 | 17.487 | -360.5558 | 17.7683 | -360.8666 | 18.0865 | -360.9158 | 17.5363 | -352.7767 | 18.7353 | -352.8198 | 16.8012
11:46 | 1589 | 22.8687 | 195.057 | 436.3428 | 442.2342 | -21.2647 | -47.1401 | 2.1134 | 0.5371 | -6.8598 | -6.9671 | -2.7786 | -4.0068 | 2.9728 | -3.9958 | 0.584 | 0.633 | 0.9522 | 0.6974 | -130.7108 | -5.5063 | 0.9701 | -0.9825 | -8.1017 | -6.7997 | 0.1884 |  | -2.4158 | -3.1336 | 3.9998 | 3.3669 | 3.3495 | 1.0277 | 10.6283 | 14.1076 | 14.716 | 10.9988 | -0.0004 | -0.0028 | -0.0003 | 0.0038 | 0.0012 | 0 | 0.0156 | -0.0018 | -0.0084 | -360.1681 | 17.487 | -360.5866 | 17.8011 | -360.9343 | 18.1502 | -360.9712 | 17.5547 | -352.7798 | 18.7395 | -352.8475 | 16.8402
11:46 | 1590 | 22.9508 | 195.0465 | 436.3834 | 442.1771 | -21.3036 | -47.2 | 2.126 | 0.5399 | -6.8056 | -6.9285 | -2.6591 | -3.9822 | 2.9414 | -4.0293 | 0.5834 | 0.6341 | 0.9512 | 0.6986 | -130.6072 | -5.4601 | 0.9621 | -0.9394 | -8.0469 | -6.6518 | 0.3052 |  | -2.4289 | -3.1094 | 3.9989 | 3.3652 | 3.3519 | 1.0283 | 10.6342 | 14.0842 | 14.7081 | 11.0169 | -0.0007 | -0.0029 | 0.0004 | 0.0035 | 0.0006 | -0.0005 | 0.0014 | -0.0077 | -0.0307 | -360.1588 | 17.45 | -360.5066 | 17.7744 | -360.9097 | 18.1276 | -360.9527 | 17.5568 | -352.7921 | 18.7271 | -352.7521 | 16.8176
11:46 | 1591 | 22.9466 | 195.1112 | 436.3924 | 442.2508 | -21.388 | -47.3318 | 2.122 | 0.5814 | -6.8228 | -7.004 | -2.6592 | -3.9866 | 2.9033 | -4.0833 | 0.5844 | 0.6349 | 0.9496 | 0.6962 | -130.6661 | -5.386 | 1.0016 | -0.9046 | -8.0151 | -6.6869 | 0.2617 |  | -2.457 | -3.1268 | 3.9992 | 3.3638 | 3.3493 | 1.0277 | 10.6712 | 14.0809 | 14.7292 | 11.036 | 0 | -0.0028 | 0.0007 | 0.0035 | 0.0001 | -0.0004 | 0.0114 | 0.0018 | -0.0139 | -360.1927 | 17.5055 | -360.5466 | 17.7662 | -360.8758 | 18.1296 | -360.9589 | 17.5712 | -352.8321 | 18.7579 | -352.8321 | 16.7991
11:46 | 1592 | 22.8511 | 195.0794 | 436.2834 | 442.2542 | -21.3268 | -47.3647 | 2.1262 | 0.5567 | -6.8276 | -7.0402 | -2.802 | -4.0507 | 2.8803 | -4.0692 | 0.5843 | 0.6348 | 0.949 | 0.697 | -130.6125 | -5.4726 | 0.9294 | -0.9393 | -8.0694 | -6.7061 | 0.2934 |  | -2.3888 | -3.0175 | 3.9996 | 3.363 | 3.3515 | 1.0289 | 10.6446 | 14.1236 | 14.7136 | 11.0038 | -0.0002 | -0.0032 | 0.0008 | 0.0035 | 0.0005 | -0.0008 | 0.0015 | -0.0061 | -0.0156 | -360.2019 | 17.5116 | -360.5896 | 17.7826 | -360.9127 | 18.1091 | -360.9004 | 17.5506 | -352.826 | 18.7785 | -352.8537 | 16.8115
11:46 | 1593 | 22.8851 | 195.1237 | 436.3335 | 442.2212 | -21.3664 | -47.4237 | 2.1353 | 0.5699 | -6.8154 | -7.099 | -2.723 | -3.9814 | 2.9292 | -3.9394 | 0.584 | 0.6325 | 0.9521 | 0.6973 | -130.6293 | -5.4722 | 0.9495 | -0.9829 | -8.0829 | -6.775 | 0.2521 |  | -2.3847 | -3.0117 | 3.9985 | 3.3641 | 3.3496 | 1.0284 | 10.6469 | 14.0854 | 14.7037 | 10.989 | -0.0004 | -0.0029 | 0.0005 | 0.0037 | 0.0004 | -0.0004 | 0.0145 | -0.0019 | -0.0011 | -360.1804 | 17.4849 | -360.5558 | 17.7703 | -360.8943 | 18.105 | -360.9374 | 17.5445 | -352.789 | 18.7477 | -352.8229 | 16.8094
11:46 | 1594 | 22.939 | 195.1581 | 436.4024 | 442.2372 | -21.3336 | -47.2984 | 2.2377 | 0.5642 | -6.7651 | -7.0174 | -2.6986 | -4.0138 | 2.9475 | -4.0002 | 0.5842 | 0.6312 | 0.9517 | 0.6978 | -130.7003 | -5.4568 | 0.9595 | -0.9608 | -8.1193 | -6.7762 | 0.2714 |  | -2.3358 | -3.0398 | 3.9977 | 3.3659 | 3.3515 | 1.0273 | 10.6319 | 14.0762 | 14.7006 | 11.0201 | -0.0003 | -0.0028 | 0.0006 | 0.004 | 0.0005 | -0.0011 | 0.014 | -0.0013 | -0.002 | -360.2235 | 17.4849 | -360.5312 | 17.7785 | -360.9004 | 18.1502 | -360.9712 | 17.5609 | -352.8444 | 18.76 | -352.8383 | 16.8217
11:46 | 1595 | 23.0005 | 195.1232 | 436.3742 | 442.3105 | -21.2649 | -47.2136 | 2.2568 | 0.5891 | -6.7881 | -6.9957 | -2.6732 | -3.9816 | 2.9929 | -3.9384 | 0.5852 | 0.6358 | 0.9525 | 0.6973 | -130.6616 | -5.4882 | 0.9422 | -0.96 | -8.0774 | -6.8125 | 0.2201 |  | -2.3134 | -3.0352 | 3.9987 | 3.3644 | 3.3512 | 1.0284 | 10.6411 | 14.0855 | 14.6932 | 11.0002 | -0.0004 | -0.0027 | 0.0006 | 0.0041 | 0.0005 | -0.0005 | 0.0062 | -0.0213 | 0.0004 | -360.165 | 17.4726 | -360.5219 | 17.7477 | -360.8512 | 18.0947 | -360.9343 | 17.5671 | -352.7952 | 18.7477 | -352.7767 | 16.7889
11:46 | 1596 | 22.9317 | 195.0263 | 436.3724 | 442.3115 | -21.2021 | -47.1793 | 2.3828 | 0.5543 | -6.7417 | -6.9741 | -2.708 | -4.0181 | 2.9824 | -3.986 | 0.5849 | 0.6325 | 0.9507 | 0.6972 | -130.6745 | -5.5534 | 0.9882 | -0.9036 | -8.0429 | -6.7531 | 0.2949 |  | -2.3443 | -2.9717 | 3.9992 | 3.3681 | 3.3545 | 1.0292 | 10.6352 | 14.1145 | 14.7231 | 11.0403 | -0.0001 | -0.0036 | 0.0003 | 0.0038 | 0.001 | -0.0005 | 0.016 | -0.0147 | 0.0106 | -360.2265 | 17.5075 | -360.5496 | 17.7724 | -360.9066 | 18.1276 | -360.9651 | 17.5712 | -352.829 | 18.7723 | -352.8321 | 16.8135
11:46 | 1597 | 22.9228 | 195.0817 | 436.4055 | 442.3089 | -21.0345 | -47.1511 | 2.404 | 0.5212 | -6.7181 | -6.9946 | -2.6201 | -4.1465 | 3.0041 | -4.1272 | 0.5864 | 0.636 | 0.9501 | 0.699 | -130.7401 | -5.5831 | 0.9715 | -0.9627 | -8.0696 | -6.7772 | 0.2831 |  | -2.3486 | -3.0184 | 3.9982 | 3.3669 | 3.3506 | 1.0281 | 10.6548 | 14.117 | 14.7154 | 11.0247 | 0 | -0.003 | 0.0006 | 0.0036 | 0.0009 | 0 | -0.0015 | -0.0002 | -0.0255 | -360.1435 | 17.4767 | -360.5158 | 17.7785 | -360.8574 | 18.1173 | -360.9343 | 17.5404 | -352.7644 | 18.7436 | -352.8229 | 16.8258
11:46 | 1598 | 22.8679 | 195.0714 | 436.3401 | 442.2878 | -21.0387 | -47.1829 | 2.3832 | 0.5525 | -6.597 | -6.9652 | -2.7075 | -4.0543 | 2.9754 | -4.0187 | 0.5859 | 0.6351 | 0.9527 | 0.7001 | -130.694 | -5.5711 | 0.8829 | -0.883 | -8.0113 | -6.6903 | 0.2935 |  | -2.3946 | -3.1237 | 3.9991 | 3.364 | 3.3527 | 1.029 | 10.6642 | 14.103 | 14.7174 | 11.0114 | -0.0005 | -0.0027 | 0.0006 | 0.0038 | 0.0007 | -0.0003 | 0.0123 | -0.0015 | -0.0089 | -360.1681 | 17.4952 | -360.5558 | 17.7847 | -360.922 | 18.1379 | -360.9835 | 17.5588 | -352.8014 | 18.7538 | -352.8321 | 16.8197
11:46 | 1599 | 22.9094 | 195.1285 | 436.391 | 442.3668 | -21.1035 | -47.192 | 2.3276 | 0.5993 | -6.681 | -6.8726 | -2.702 | -4.007 | 2.9841 | -3.9802 | 0.5848 | 0.6339 | 0.9537 | 0.6992 | -130.6291 | -5.5684 | 1.0188 | -0.7325 | -8.0527 | -6.6569 | 0.3143 |  | -2.352 | -3.0887 | 3.9999 | 3.3664 | 3.3501 | 1.0269 | 10.6295 | 14.0682 | 14.6758 | 11.0002 | -0.0001 | -0.0023 | 0.0012 | 0.0036 | 0.0002 | -0.0005 | 0.0147 | -0.013 | 0.0079 | -360.1896 | 17.4788 | -360.5373 | 17.7847 | -360.8727 | 18.1091 | -360.922 | 17.5671 | -352.786 | 18.7497 | -352.8075 | 16.8299
11:46 | 1600 | 22.8759 | 195.0562 | 436.3899 | 442.282 | -21.0341 | -47.1645 | 2.3145 | 0.5864 | -6.7207 | -6.9049 | -2.7249 | -4.0351 | 3.0006 | -3.9213 | 0.5849 | 0.6317 | 0.9531 | 0.6981 | -130.7215 | -5.6142 | 1.0716 | -0.7502 | -7.999 | -6.6296 | 0.3805 |  | -2.3376 | -3.0113 | 4.0006 | 3.3653 | 3.3542 | 1.0294 | 10.6202 | 14.0821 | 14.7133 | 11.0255 | 0.0003 | -0.0029 | 0.001 | 0.0038 | 0.0005 | -0.0006 | 0.007 | -0.0094 | -0.0254 | -360.1804 | 17.5055 | -360.5404 | 17.7847 | -360.8912 | 18.1235 | -360.9651 | 17.5588 | -352.786 | 18.7682 | -352.8137 | 16.8156
11:46 | 1601 | 22.8978 | 195.0727 | 436.4105 | 442.3116 | -21.1129 | -47.1171 | 2.3324 | 0.6044 | -6.7705 | -6.8336 | -2.7323 | -4.0359 | 2.9678 | -3.9629 | 0.5835 | 0.6338 | 0.9517 | 0.6986 | -130.7009 | -5.4784 | 1.0789 | -0.8924 | -8.0204 | -6.6904 | 0.3086 |  | -2.3812 | -3.1168 | 3.999 | 3.3676 | 3.3531 | 1.027 | 10.5961 | 14.0978 | 14.7029 | 11.0082 | 0 | -0.0034 | 0.0006 | 0.0038 | 0.0007 | -0.0009 | 0.0133 | 0.0112 | -0.0198 | -360.1835 | 17.487 | -360.5496 | 17.7826 | -360.885 | 18.1255 | -360.9251 | 17.5506 | -352.786 | 18.7641 | -352.826 | 16.8299
11:46 | 1602 | 22.9354 | 195.1253 | 436.4316 | 442.3208 | -20.9913 | -47.1241 | 2.3035 | 0.5316 | -6.7134 | -6.9305 | -2.7793 | -4.0723 | 2.9728 | -3.9693 | 0.5851 | 0.6311 | 0.9521 | 0.6985 | -130.7548 | -5.6428 | 1.0108 | -0.8644 | -8.0001 | -6.6261 | 0.373 |  | -2.3119 | -3.0383 | 4.0003 | 3.3688 | 3.3561 | 1.0292 | 10.6329 | 14.0833 | 14.6915 | 11.0323 | -0.0002 | -0.003 | 0.0005 | 0.0032 | 0.0005 | -0.0002 | 0.0227 | -0.0057 | -0.0039 | -360.1465 | 17.487 | -360.5496 | 17.7703 | -360.8727 | 18.1153 | -360.9681 | 17.5527 | -352.7737 | 18.7415 | -352.8137 | 16.8156
11:46 | 1603 | 22.9248 | 195.1154 | 436.3517 | 442.3183 | -20.9726 | -47.059 | 2.3961 | 0.6552 | -6.6952 | -6.8903 | -2.7861 | -4.0005 | 2.9933 | -3.8474 | 0.5848 | 0.6318 | 0.9524 | 0.699 | -130.6917 | -5.4376 | 1.142 | -0.9255 | -7.9654 | -6.7057 | 0.3016 |  | -2.3248 | -3.0547 | 3.9985 | 3.3664 | 3.3579 | 1.0293 | 10.6261 | 14.0818 | 14.6938 | 10.98 | 0 | -0.0025 | 0.0001 | 0.0037 | 0.001 | -0.0009 | 0.0024 | -0.0047 | -0.0255 | -360.165 | 17.4993 | -360.5712 | 17.7888 | -360.885 | 18.1337 | -360.9558 | 17.5629 | -352.8414 | 18.7703 | -352.8383 | 16.832
11:46 | 1604 | 22.9063 | 195.0757 | 436.3833 | 442.3327 | -20.9994 | -46.9829 | 2.4384 | 0.5602 | -6.6354 | -6.785 | -2.7694 | -4.0432 | 3.02 | -3.8648 | 0.5848 | 0.631 | 0.9552 | 0.6971 | -130.6746 | -5.5354 | 1.086 | -0.9004 | -7.9943 | -6.7115 | 0.2414 |  | -2.3461 | -3.0844 | 3.9995 | 3.3659 | 3.3539 | 1.029 | 10.6272 | 14.0948 | 14.7088 | 11.0497 | 0.0001 | -0.0029 | 0.0006 | 0.0038 | 0.0005 | -0.0003 | -0.003 | -0.0055 | -0.0081 | -360.1896 | 17.4849 | -360.5558 | 17.7683 | -360.885 | 18.0906 | -360.922 | 17.5588 | -352.8014 | 18.7395 | -352.8229 | 16.8156
11:46 | 1605 | 22.9457 | 195.1743 | 436.4539 | 442.3003 | -21.0018 | -46.9789 | 2.4066 | 0.6696 | -6.6516 | -6.821 | -2.7423 | -4.1092 | 3.0394 | -3.8927 | 0.5843 | 0.6325 | 0.9538 | 0.6969 | -130.7227 | -5.4889 | 0.9761 | -0.9478 | -7.9479 | -6.71 | 0.2283 |  | -2.3421 | -3.1271 | 3.9992 | 3.3658 | 3.3538 | 1.0296 | 10.6352 | 14.103 | 14.6942 | 11.0229 | 0.0005 | -0.0026 | 0.0006 | 0.0034 | 0.0008 | -0.0008 | 0.014 | -0.0145 | -0.0081 | -360.1927 | 17.5096 | -360.5681 | 17.795 | -360.9035 | 18.1379 | -360.9404 | 17.5547 | -352.8198 | 18.7805 | -352.8321 | 16.834
11:46 | 1606 | 23.0029 | 195.0841 | 436.4711 | 442.374 | -20.9907 | -47.0746 | 2.3477 | 0.6074 | -6.6543 | -6.8309 | -2.8117 | -4.1377 | 3.0869 | -3.995 | 0.5845 | 0.6328 | 0.9534 | 0.6979 | -130.6997 | -5.5628 | 0.9325 | -0.8037 | -7.9327 | -6.6251 | 0.2391 |  | -2.3217 | -3.053 | 3.9988 | 3.3664 | 3.3549 | 1.0306 | 10.6065 | 14.0968 | 14.6853 | 11.0299 | -0.0002 | -0.0032 | 0.0003 | 0.0035 | 0.0001 | -0.0006 | 0.004 | -0.0074 | -0.0193 | -360.1773 | 17.4541 | -360.5158 | 17.7703 | -360.8758 | 18.1132 | -360.9281 | 17.5465 | -352.7429 | 18.7353 | -352.7829 | 16.8094
11:46 | 1607 | 23.0652 | 195.1193 | 436.4796 | 442.4085 | -20.9962 | -47.0764 | 2.3503 | 0.6228 | -6.6725 | -6.8855 | -2.7154 | -4.0498 | 3.0404 | -3.9536 | 0.585 | 0.6358 | 0.9532 | 0.6988 | -130.737 | -5.4827 | 0.9781 | -0.6698 | -7.9432 | -6.6201 | 0.3391 |  | -2.378 | -3.044 | 4 | 3.3658 | 3.3531 | 1.03 | 10.6167 | 14.0844 | 14.6986 | 10.9814 | -0.0004 | -0.0026 | 0.001 | 0.0038 | 0.0003 | -0.0008 | 0.0008 | -0.0108 | -0.0105 | -360.2142 | 17.489 | -360.5589 | 17.7867 | -360.9035 | 18.1317 | -361.0051 | 17.5794 | -352.8075 | 18.7497 | -352.8137 | 16.8197
11:47 | 1608 | 23.0733 | 195.1641 | 436.4147 | 442.4013 | -21.0863 | -47.0853 | 2.3835 | 0.5979 | -6.6241 | -6.8404 | -2.7158 | -3.9952 | 3.125 | -3.8639 | 0.5837 | 0.6329 | 0.9519 | 0.6994 | -130.7517 | -5.6366 | 0.9644 | -0.8735 | -7.907 | -6.6081 | 0.3311 |  | -2.2797 | -3.0265 | 3.9999 | 3.3636 | 3.3548 | 1.0297 | 10.6492 | 14.0935 | 14.7122 | 11.0374 | -0.0002 | -0.0028 | 0.0003 | 0.0035 | 0.0004 | -0.0007 | 0.0126 | -0.0035 | -0.0213 | -360.1742 | 17.4808 | -360.5343 | 17.7683 | -360.8666 | 18.105 | -360.9343 | 17.5465 | -352.8014 | 18.7661 | -352.8075 | 16.8176
11:47 | 1609 | 23.0074 | 195.062 | 436.4932 | 442.4281 | -21.103 | -47.0617 | 2.4046 | 0.5789 | -6.6312 | -6.7366 | -2.6896 | -3.9712 | 3.1247 | -3.8543 | 0.5829 | 0.6324 | 0.9517 | 0.6977 | -130.7662 | -5.5132 | 1.0063 | -0.8685 | -8.0069 | -6.6536 | 0.2837 |  | -2.3437 | -3.0901 | 3.9997 | 3.3639 | 3.3546 | 1.0315 | 10.6481 | 14.0806 | 14.6808 | 11.0136 | -0.0003 | -0.0033 | 0.0007 | 0.0037 | 0.0007 | -0.0007 | 0.0084 | -0.0113 | -0.0236 | -360.1742 | 17.5034 | -360.6081 | 17.7991 | -360.9004 | 18.1091 | -360.9312 | 17.5527 | -352.8075 | 18.7723 | -352.8475 | 16.8402
11:47 | 1610 | 22.9547 | 195.0547 | 436.5907 | 442.4796 | -21.0221 | -46.9155 | 2.4397 | 0.5544 | -6.6331 | -6.7152 | -2.7258 | -4.0619 | 2.9986 | -3.9157 | 0.5839 | 0.6346 | 0.9503 | 0.6969 | -130.6727 | -5.4816 | 1.0686 | -0.7766 | -7.9704 | -6.5035 | 0.3568 |  | -2.3034 | -3.0869 | 3.9991 | 3.3639 | 3.3523 | 1.0297 | 10.6156 | 14.0948 | 14.6857 | 10.9919 | 0.0001 | -0.0032 | 0.001 | 0.0039 | 0.001 | -0.0006 | 0.0014 | -0.0024 | 0.0021 | -360.1773 | 17.487 | -360.5527 | 17.7888 | -360.8943 | 18.1071 | -360.9066 | 17.526 | -352.7952 | 18.76 | -352.8475 | 16.8402
11:47 | 1611 | 22.9739 | 195.0005 | 436.5526 | 442.4173 | -21.0926 | -47.0022 | 2.4587 | 0.6207 | -6.5822 | -6.7848 | -2.6476 | -4.0244 | 3.0433 | -3.974 | 0.5845 | 0.6334 | 0.9496 | 0.6972 | -130.6778 | -5.3778 | 0.9907 | -0.8215 | -8.0006 | -6.4842 | 0.3689 |  | -2.4184 | -3.1437 | 3.9989 | 3.3649 | 3.3546 | 1.0299 | 10.6182 | 14.0964 | 14.6821 | 11.0195 | -0.0006 | -0.0031 | -0.0001 | 0.0032 | -0.0001 | -0.0006 | 0.022 | -0.0059 | -0.0148 | -360.1927 | 17.4767 | -360.5558 | 17.7744 | -360.9035 | 18.1337 | -360.9558 | 17.5527 | -352.7952 | 18.7456 | -352.7829 | 16.8279
11:47 | 1612 | 23.0055 | 195.1287 | 436.4776 | 442.3484 | -21.1279 | -47.0703 | 2.4023 | 0.5822 | -6.6489 | -6.8175 | -2.6881 | -3.9586 | 3.1155 | -3.8907 | 0.5847 | 0.6354 | 0.9523 | 0.6982 | -130.6292 | -5.3877 | 1.1436 | -0.8337 | -7.9468 | -6.5447 | 0.3337 |  | -2.3089 | -3.0881 | 4.0003 | 3.3646 | 3.3546 | 1.0302 | 10.6353 | 14.0855 | 14.7105 | 11.0291 | -0.0002 | -0.0026 | 0.0007 | 0.004 | 0.0008 | -0.0007 | 0.027 | -0.0133 | 0.0042 | -360.245 | 17.489 | -360.5312 | 17.7621 | -360.842 | 18.1091 | -360.9774 | 17.5753 | -352.826 | 18.7456 | -352.8167 | 16.8156
11:47 | 1613 | 22.9908 | 195.1629 | 436.4501 | 442.3694 | -21.1057 | -47.019 | 2.4705 | 0.6655 | -6.5681 | -6.8443 | -2.6146 | -3.9938 | 3.0563 | -3.8622 | 0.5846 | 0.6324 | 0.9529 | 0.6987 | -130.7896 | -5.4195 | 1.0913 | -0.8711 | -8.0164 | -6.5703 | 0.3096 |  | -2.3679 | -2.9444 | 3.9998 | 3.3646 | 3.3512 | 1.0308 | 10.6041 | 14.083 | 14.7125 | 10.9696 | -0.0002 | -0.0033 | 0.0002 | 0.0033 | 0.0005 | -0.0003 | 0.005 | -0.0077 | -0.0061 | -360.2419 | 17.5055 | -360.5373 | 17.758 | -360.8635 | 18.1029 | -360.9374 | 17.5588 | -352.8383 | 18.7744 | -352.7829 | 16.8032
11:47 | 1614 | 23.071 | 195.1089 | 436.4267 | 442.4163 | -21.0593 | -46.9334 | 2.6141 | 0.6379 | -6.5617 | -6.761 | -2.6666 | -3.937 | 3.025 | -3.8174 | 0.5856 | 0.6326 | 0.9499 | 0.6982 | -130.7281 | -5.4303 | 1.0523 | -0.8916 | -8.1205 | -6.6196 | 0.254 |  | -2.3695 | -3.0958 | 4 | 3.3599 | 3.3488 | 1.0303 | 10.648 | 14.1272 | 14.7177 | 11.0244 | 0.0001 | -0.0031 | 0.0004 | 0.0037 | 0.0004 | -0.0007 | 0.0251 | -0.014 | 0.0144 | -360.1711 | 17.489 | -360.5773 | 17.795 | -360.9066 | 18.1194 | -360.9497 | 17.5506 | -352.789 | 18.7641 | -352.8444 | 16.8464
11:47 | 1615 | 22.9969 | 195.0861 | 436.4096 | 442.3441 | -21.2527 | -47.1409 | 2.4819 | 0.6643 | -6.5482 | -6.6385 | -2.5937 | -3.9681 | 3.0416 | -3.8496 | 0.5846 | 0.6333 | 0.9541 | 0.6967 | -130.7649 | -5.338 | 1.0102 | -0.811 | -7.9848 | -6.5254 | 0.3573 |  | -2.4008 | -3.0915 | 4.0019 | 3.3638 | 3.3521 | 1.0299 | 10.6594 | 14.1219 | 14.7277 | 11.0344 | 0.0001 | -0.0025 | 0.0014 | 0.0042 | 0.0004 | -0.0005 | 0.0045 | -0.0083 | -0.0052 | -360.1527 | 17.4664 | -360.5127 | 17.7683 | -360.9127 | 18.1317 | -360.9589 | 17.5424 | -352.7706 | 18.7292 | -352.7737 | 16.8135
11:47 | 1616 | 23.037 | 195.1219 | 436.4184 | 442.3256 | -21.1926 | -47.1168 | 2.3997 | 0.6655 | -6.611 | -6.6512 | -2.6084 | -3.9713 | 3.0331 | -3.8765 | 0.5867 | 0.6334 | 0.9539 | 0.6978 | -130.7604 | -5.4858 | 0.9303 | -0.9572 | -7.8894 | -6.57 | 0.2919 |  | -2.3445 | -3.0173 | 4.0006 | 3.3628 | 3.3514 | 1.0284 | 10.6942 | 14.1332 | 14.7487 | 11.0352 | -0.0006 | -0.0029 | 0.0008 | 0.0033 | 0.0001 | -0.0006 | 0.0127 | -0.023 | 0.0016 | -360.1865 | 17.489 | -360.5527 | 17.7929 | -360.8974 | 18.1296 | -360.9897 | 17.5773 | -352.7829 | 18.7415 | -352.8106 | 16.8238
11:47 | 1617 | 23.0488 | 195.1415 | 436.4024 | 442.4132 | -21.1699 | -47.1019 | 2.3887 | 0.6108 | -6.6838 | -6.7072 | -2.658 | -3.8655 | 3.0954 | -3.8859 | 0.5855 | 0.6339 | 0.949 | 0.6981 | -130.7612 | -5.4186 | 1.0607 | -0.9185 | -8.0046 | -6.6843 | 0.2827 |  | -2.2851 | -2.9796 | 4.0009 | 3.3656 | 3.3497 | 1.0288 | 10.6457 | 14.1191 | 14.7218 | 11.0276 | 0 | -0.0026 | 0.0006 | 0.0043 | 0.0008 | -0.0006 | 0.0111 | -0.0061 | -0.016 | -360.1773 | 17.4911 | -360.5466 | 17.7703 | -360.882 | 18.0968 | -360.9127 | 17.5383 | -352.7829 | 18.7477 | -352.8167 | 16.8094
11:47 | 1618 | 23.0948 | 195.1464 | 436.4348 | 442.4237 | -21.221 | -47.2062 | 2.3452 | 0.656 | -6.6072 | -6.6834 | -2.5481 | -3.9023 | 3.0471 | -3.9383 | 0.5858 | 0.6376 | 0.9498 | 0.6981 | -130.7517 | -5.3816 | 1.0211 | -0.8595 | -7.9608 | -6.658 | 0.2761 |  | -2.235 | -2.9545 | 4.0001 | 3.3656 | 3.3517 | 1.0303 | 10.6722 | 14.1228 | 14.7501 | 11.0767 | 0.0002 | -0.003 | 0.0007 | 0.0036 | 0.0005 | -0.0006 | 0.0153 | -0.0131 | -0.0038 | -360.1958 | 17.5116 | -360.5989 | 17.8093 | -360.9466 | 18.1194 | -360.9281 | 17.5506 | -352.7983 | 18.7559 | -352.8752 | 16.8587
11:47 | 1619 | 23.0613 | 195.1711 | 436.5713 | 442.4945 | -21.151 | -47.0843 | 2.4319 | 0.6432 | -6.657 | -6.6777 | -2.5802 | -3.9204 | 3.0589 | -3.8669 | 0.5856 | 0.6309 | 0.9506 | 0.697 | -130.7391 | -5.3974 | 1.0961 | -0.8099 | -7.982 | -6.6092 | 0.2719 |  | -2.3118 | -3.0662 | 4.0018 | 3.3642 | 3.3562 | 1.0308 | 10.6376 | 14.1168 | 14.7075 | 11.0486 | -0.0002 | -0.0033 | 0.0002 | 0.0033 | 0.0013 | -0.0006 | 0.0024 | -0.0122 | -0.0119 | -360.1558 | 17.4747 | -360.5096 | 17.7703 | -360.8543 | 18.1153 | -360.9251 | 17.5404 | -352.7644 | 18.7395 | -352.786 | 16.8217
11:47 | 1620 | 23.059 | 195.1776 | 436.4858 | 442.4589 | -21.1089 | -46.9568 | 2.4142 | 0.624 | -6.6805 | -6.7106 | -2.6785 | -3.8888 | 3.1035 | -3.8364 | 0.5851 | 0.6318 | 0.9509 | 0.6988 | -130.7494 | -5.3197 | 1.1224 | -0.8039 | -7.9492 | -6.5878 | 0.2584 |  | -2.2608 | -2.9598 | 4.001 | 3.3649 | 3.3556 | 1.0293 | 10.603 | 14.0413 | 14.6243 | 11.0031 | -0.0003 | -0.0029 | 0.0005 | 0.0038 | 0.0006 | -0.0005 | 0.0092 | -0.0006 | 0.0033 | -360.2173 | 17.5096 | -360.5589 | 17.7888 | -360.8789 | 18.1235 | -361.002 | 17.5835 | -352.8229 | 18.7682 | -352.829 | 16.8217
11:47 | 1621 | 23.0271 | 195.2665 | 436.5652 | 442.5468 | -21.1581 | -47.0325 | 2.4716 | 0.7302 | -6.5944 | -6.6254 | -2.4879 | -3.8113 | 3.1228 | -3.9364 | 0.5854 | 0.6323 | 0.9485 | 0.6982 | -130.7239 | -5.3396 | 1.1773 | -0.9619 | -8.0114 | -6.6462 | 0.2632 |  | -2.2627 | -3.0165 | 4.0003 | 3.3621 | 3.353 | 1.0292 | 10.6214 | 14.089 | 14.6683 | 11.0035 | -0.0001 | -0.0026 | 0.0008 | 0.0039 | 0.001 | -0.0008 | -0.0012 | -0.0181 | -0.0155 | -360.2019 | 17.4911 | -360.525 | 17.7601 | -360.8512 | 18.0865 | -360.922 | 17.5568 | -352.8167 | 18.7641 | -352.8229 | 16.7991
11:47 | 1622 | 23.1146 | 195.3065 | 436.624 | 442.5493 | -21.2442 | -46.9937 | 2.376 | 0.6814 | -6.6381 | -6.7199 | -2.5617 | -3.8692 | 3.0886 | -3.8964 | 0.5857 | 0.6321 | 0.9532 | 0.699 | -130.737 | -5.3771 | 1.0966 | -0.921 | -7.9603 | -6.6548 | 0.3271 |  | -2.226 | -2.8619 | 3.9995 | 3.3617 | 3.3542 | 1.0289 | 10.6261 | 14.0876 | 14.688 | 11.0147 | 0.0002 | -0.003 | 0.0003 | 0.0039 | 0.0004 | 0.0002 | 0.0111 | -0.0008 | 0.0022 | -360.1988 | 17.5055 | -360.5743 | 17.7991 | -360.9404 | 18.1255 | -360.962 | 17.5588 | -352.786 | 18.7682 | -352.8321 | 16.8381
11:47 | 1623 | 23.139 | 195.2321 | 436.537 | 442.5338 | -21.2422 | -47.1608 | 2.4049 | 0.7311 | -6.6244 | -6.6866 | -2.6264 | -3.9061 | 3.1303 | -3.9691 | 0.5888 | 0.6359 | 0.9528 | 0.6987 | -130.7247 | -5.4651 | 1.0678 | -0.9807 | -7.956 | -6.6267 | 0.2562 |  | -2.2822 | -2.9783 | 3.9992 | 3.3651 | 3.3526 | 1.0294 | 10.6329 | 14.1122 | 14.6915 | 11.0092 | 0.0001 | -0.003 | 0.0008 | 0.0041 | 0.0011 | -0.0007 | 0.0084 | 0.0019 | -0.0081 | -360.1096 | 17.4541 | -360.5312 | 17.7703 | -360.8758 | 18.144 | -360.9404 | 17.5363 | -352.7614 | 18.7312 | -352.7706 | 16.8238
11:47 | 1624 | 23.0758 | 195.1452 | 436.634 | 442.5058 | -21.2681 | -47.0272 | 2.3763 | 0.7621 | -6.6124 | -6.7746 | -2.5522 | -3.9068 | 3.1403 | -3.8908 | 0.5857 | 0.635 | 0.9525 | 0.6978 | -130.7038 | -5.4775 | 1.0879 | -0.978 | -7.8778 | -6.6535 | 0.3073 |  | -2.3278 | -3.052 | 4.001 | 3.3672 | 3.351 | 1.03 | 10.6456 | 14.0963 | 14.7181 | 11.0384 | -0.0001 | -0.0026 | 0.0011 | 0.0039 | 0.0007 | -0.0003 | 0.0191 | -0.017 | -0.0086 | -360.1835 | 17.4931 | -360.565 | 17.7909 | -360.8881 | 18.142 | -360.9866 | 17.5773 | -352.8106 | 18.7497 | -352.789 | 16.8197
11:47 | 1625 | 23.0629 | 195.0947 | 436.394 | 442.5263 | -21.2448 | -47.0193 | 2.4334 | 0.7076 | -6.6862 | -6.6985 | -2.536 | -3.9428 | 3.1412 | -3.9932 | 0.5871 | 0.6376 | 0.9551 | 0.6992 | -130.681 | -5.3791 | 1.0944 | -0.8417 | -7.9546 | -6.5835 | 0.2453 |  | -2.3447 | -3.0151 | 3.9997 | 3.3661 | 3.3548 | 1.03 | 10.6295 | 14.0971 | 14.6874 | 11.0176 | -0.0004 | -0.0027 | 0.0002 | 0.0035 | 0.0011 | -0.0001 | 0.0166 | -0.0043 | 0.0067 | -360.2081 | 17.4952 | -360.5281 | 17.7703 | -360.8758 | 18.0968 | -360.922 | 17.5588 | -352.7829 | 18.7579 | -352.826 | 16.8176
11:47 | 1626 | 23.0989 | 195.0595 | 436.4383 | 442.497 | -21.2029 | -47.0712 | 2.5471 | 0.7081 | -6.6439 | -6.7502 | -2.6446 | -3.8745 | 3.1219 | -3.9188 | 0.5862 | 0.631 | 0.9493 | 0.6978 | -130.719 | -5.4144 | 1.0984 | -0.7977 | -8.0336 | -6.7142 | 0.3224 |  | -2.2472 | -2.9141 | 3.9987 | 3.3656 | 3.3552 | 1.0291 | 10.6319 | 14.1107 | 14.7054 | 10.9974 | -0.0002 | -0.0027 | 0.0002 | 0.0035 | 0.0002 | -0.0012 | 0.005 | -0.0157 | 0.003 | -360.1958 | 17.5013 | -360.5804 | 17.7991 | -360.9158 | 18.1194 | -360.8974 | 17.5445 | -352.8137 | 18.7579 | -352.8506 | 16.8505
11:47 | 1627 | 23.1119 | 195.1456 | 436.4749 | 442.5478 | -21.093 | -47.1092 | 2.4901 | 0.8013 | -6.6544 | -6.7156 | -2.5433 | -3.9253 | 3.1173 | -3.8326 | 0.5855 | 0.631 | 0.95 | 0.6977 | -130.7312 | -5.3866 | 1.1174 | -0.7522 | -7.9933 | -6.5863 | 0.3065 |  | -2.1949 | -2.9204 | 3.9997 | 3.3625 | 3.3517 | 1.0308 | 10.67 | 14.1144 | 14.6874 | 11.0464 | 0 | -0.0033 | 0.0002 | 0.0031 | 0.0005 | -0.0004 | -0.0052 | -0.0043 | -0.0157 | -360.1281 | 17.487 | -360.5681 | 17.7724 | -360.882 | 18.1194 | -360.9004 | 17.5342 | -352.7952 | 18.7518 | -352.8198 | 16.8381
11:47 | 1628 | 23.0766 | 195.1191 | 436.4701 | 442.5901 | -21.0407 | -47.0989 | 2.5285 | 0.7514 | -6.615 | -6.7672 | -2.5623 | -3.8671 | 3.1008 | -3.7971 | 0.5848 | 0.6268 | 0.9491 | 0.7004 | -130.7786 | -5.36 | 1.0737 | -0.7253 | -8.0146 | -6.5817 | 0.3432 |  | -2.2334 | -2.9091 | 3.9988 | 3.361 | 3.3537 | 1.03 | 10.6493 | 14.0876 | 14.688 | 11.0262 | 0 | -0.003 | 0.0006 | 0.0041 | 0.0007 | -0.0009 | 0.0059 | -0.0156 | 0.003 | -360.2419 | 17.4808 | -360.5496 | 17.7703 | -360.8912 | 18.1296 | -360.9743 | 17.5629 | -352.7952 | 18.7374 | -352.7737 | 16.8135
11:47 | 1629 | 23.114 | 195.1365 | 436.5112 | 442.5814 | -21.103 | -47.0921 | 2.4983 | 0.7073 | -6.6042 | -6.766 | -2.4756 | -3.9012 | 3.1503 | -3.8518 | 0.5859 | 0.6337 | 0.953 | 0.6989 | -130.6375 | -5.2686 | 1.1359 | -0.761 | -7.9557 | -6.6314 | 0.3084 |  | -2.1753 | -2.8996 | 3.9994 | 3.3664 | 3.3542 | 1.0315 | 10.6342 | 14.0842 | 14.656 | 10.9937 | -0.0004 | -0.0028 | 0.0007 | 0.004 | 0.0002 | -0.0004 | 0.0073 | -0.0084 | -0.0027 | -360.2081 | 17.4952 | -360.5343 | 17.7703 | -360.8635 | 18.1153 | -360.9743 | 17.5671 | -352.8352 | 18.7764 | -352.8167 | 16.8115
11:47 | 1630 | 23.1899 | 195.1015 | 436.5304 | 442.5397 | -21.0728 | -47.0864 | 2.4065 | 0.7445 | -6.4923 | -6.6878 | -2.4908 | -3.9056 | 3.1814 | -3.7804 | 0.586 | 0.6359 | 0.9551 | 0.7004 | -130.6513 | -5.3416 | 1.2136 | -0.8294 | -7.9891 | -6.6887 | 0.3283 |  | -2.2502 | -2.9684 | 4.0009 | 3.3654 | 3.3553 | 1.0311 | 10.6122 | 14.0969 | 14.6979 | 11.0237 | -0.0002 | -0.0032 | 0.0004 | 0.0037 | 0.001 | -0.0007 | -0.0049 | 0.0011 | -0.0339 | -360.1527 | 17.4808 | -360.5619 | 17.7724 | -360.8481 | 18.1132 | -360.9374 | 17.5486 | -352.8106 | 18.762 | -352.829 | 16.7991
11:47 | 1631 | 23.1751 | 195.1311 | 436.454 | 442.5629 | -21.1312 | -47.0524 | 2.4866 | 0.7202 | -6.4764 | -6.6175 | -2.495 | -3.8815 | 3.1732 | -3.7843 | 0.5871 | 0.6342 | 0.9497 | 0.6988 | -130.8248 | -5.4621 | 1.1361 | -0.838 | -7.888 | -6.6626 | 0.2838 |  | -2.2691 | -2.9375 | 3.9991 | 3.365 | 3.3526 | 1.0292 | 10.6134 | 14.098 | 14.6982 | 11.0309 | -0.0001 | -0.0032 | 0.0007 | 0.0035 | 0.0001 | -0.0009 | 0.0041 | -0.0107 | -0.0301 | -360.1558 | 17.4849 | -360.5743 | 17.795 | -360.9066 | 18.1584 | -360.9404 | 17.5588 | -352.8137 | 18.7661 | -352.8567 | 16.8443
11:47 | 1632 | 23.1123 | 195.1439 | 436.4755 | 442.5411 | -21.0683 | -47.0425 | 2.4624 | 0.6405 | -6.4282 | -6.7089 | -2.5128 | -4.0135 | 3.2165 | -3.8283 | 0.5864 | 0.6342 | 0.9538 | 0.6994 | -130.649 | -5.4108 | 1.1686 | -0.9142 | -7.932 | -6.6151 | 0.2196 |  | -2.2504 | -3.0208 | 3.9994 | 3.3644 | 3.3523 | 1.029 | 10.6249 | 14.1156 | 14.6772 | 10.9955 | -0.0001 | -0.003 | 0.001 | 0.0037 | 0.0008 | -0.0006 | 0.0106 | -0.0019 | 0.0061 | -360.1619 | 17.4603 | -360.5004 | 17.7642 | -360.882 | 18.1625 | -360.9404 | 17.5342 | -352.7398 | 18.7415 | -352.7583 | 16.8032
11:47 | 1633 | 23.0927 | 195.0405 | 436.5024 | 442.4921 | -21.0537 | -46.9931 | 2.5 | 0.7033 | -6.4905 | -6.7214 | -2.5235 | -3.955 | 3.1659 | -3.7633 | 0.5863 | 0.6347 | 0.9508 | 0.6997 | -130.657 | -5.5304 | 0.9956 | -0.9466 | -7.9249 | -6.5515 | 0.3378 |  | -2.2075 | -2.926 | 3.9994 | 3.3652 | 3.3546 | 1.0305 | 10.6469 | 14.1143 | 14.7268 | 11.0353 | -0.0006 | -0.003 | 0.0002 | 0.0032 | 0.0007 | -0.0006 | -0.0037 | 0.0013 | -0.0111 | -360.1742 | 17.4829 | -360.5527 | 17.7888 | -360.9189 | 18.1584 | -360.9989 | 17.5855 | -352.8106 | 18.7415 | -352.8321 | 16.8176
11:47 | 1634 | 23.1155 | 195.035 | 436.5589 | 442.5574 | -21.037 | -47.0517 | 2.5017 | 0.647 | -6.4873 | -6.6617 | -2.5542 | -3.9242 | 3.1488 | -3.7851 | 0.5869 | 0.6347 | 0.9535 | 0.6982 | -130.717 | -5.5522 | 1.029 | -1.0583 | -7.8736 | -6.6448 | 0.3243 |  | -2.1945 | -3.0086 | 3.9998 | 3.3629 | 3.3538 | 1.031 | 10.626 | 14.0994 | 14.6901 | 11.0024 | 0 | -0.0025 | 0.0009 | 0.0037 | 0.0004 | -0.0006 | 0.0072 | -0.0129 | -0.0068 | -360.1988 | 17.487 | -360.5373 | 17.7765 | -360.8297 | 18.1276 | -360.9158 | 17.5424 | -352.786 | 18.7682 | -352.8198 | 16.8094
11:47 | 1635 | 23.2037 | 195.0954 | 436.6295 | 442.5517 | -21.047 | -47.066 | 2.4788 | 0.6971 | -6.4859 | -6.7753 | -2.5531 | -3.9166 | 3.0912 | -3.7445 | 0.586 | 0.6332 | 0.9539 | 0.6991 | -130.6514 | -5.4574 | 1.1922 | -1.0218 | -7.7874 | -6.6026 | 0.3763 |  | -2.1585 | -3.0149 | 4.0004 | 3.3662 | 3.3556 | 1.0308 | 10.6561 | 14.1237 | 14.732 | 10.9919 | -0.0002 | -0.0033 | 0.0003 | 0.0033 | 0.0009 | -0.0005 | 0.009 | -0.0109 | -0.013 | -360.1835 | 17.4972 | -360.6173 | 17.8155 | -360.9281 | 18.1502 | -360.9466 | 17.5383 | -352.8044 | 18.7538 | -352.8598 | 16.8566
11:47 | 1636 | 23.2837 | 195.2148 | 436.6668 | 442.6855 | -21.1675 | -47.1366 | 2.4509 | 0.6637 | -6.4749 | -6.8009 | -2.6374 | -4.0188 | 3.1198 | -3.7738 | 0.585 | 0.6327 | 0.9534 | 0.6986 | -130.7005 | -5.4466 | 1.1227 | -1.0233 | -7.8505 | -6.6107 | 0.3849 |  | -2.1179 | -2.9762 | 4.0006 | 3.3662 | 3.3499 | 1.0296 | 10.6008 | 14.0676 | 14.66 | 10.9786 | -0.0001 | -0.0031 | 0.0005 | 0.0037 | 0.0002 | -0.0006 | 0.0044 | -0.0116 | -0.0008 | -360.1835 | 17.4767 | -360.5404 | 17.7785 | -360.8666 | 18.1584 | -360.8974 | 17.5157 | -352.7583 | 18.7415 | -352.8106 | 16.8381
11:47 | 1637 | 23.1705 | 195.1132 | 436.4024 | 442.519 | -21.1176 | -47.1258 | 2.4728 | 0.6745 | -6.5113 | -6.7226 | -2.6524 | -3.9382 | 3.1841 | -3.738 | 0.5855 | 0.6324 | 0.9508 | 0.7009 | -130.7288 | -5.5664 | 1.0687 | -0.9824 | -7.7655 | -6.6198 | 0.3538 |  | -2.2285 | -2.9806 | 3.9995 | 3.3656 | 3.3549 | 1.0312 | 10.6537 | 14.1099 | 14.6782 | 11.0125 | -0.0005 | -0.0032 | 0.0009 | 0.004 | 0.0007 | -0.0007 | 0.0068 | 0.0076 | -0.0135 | -360.1958 | 17.4849 | -360.5527 | 17.7847 | -360.8912 | 18.1666 | -360.9743 | 17.565 | -352.8167 | 18.762 | -352.826 | 16.8176
11:47 | 1638 | 23.1034 | 195.0488 | 436.5046 | 442.5144 | -21.1051 | -47.1535 | 2.4683 | 0.7157 | -6.455 | -6.5827 | -2.6161 | -3.9294 | 3.2046 | -3.7673 | 0.5865 | 0.6312 | 0.9527 | 0.7001 | -130.6977 | -5.4472 | 1.0837 | -1.0842 | -7.8389 | -6.6151 | 0.2492 |  | -2.1834 | -2.9611 | 3.9996 | 3.3648 | 3.3521 | 1.0301 | 10.6328 | 14.1182 | 14.7341 | 11.0374 | -0.0005 | -0.0027 | 0.0007 | 0.0037 | 0.0006 | -0.0003 | 0.0077 | -0.012 | -0.004 | -360.2327 | 17.4993 | -360.5496 | 17.7539 | -360.845 | 18.1194 | -360.9097 | 17.5465 | -352.8229 | 18.7579 | -352.8106 | 16.8032
11:47 | 1639 | 23.1982 | 195.1371 | 436.5161 | 442.5332 | -21.0105 | -47.1956 | 2.5225 | 0.7013 | -6.5693 | -6.607 | -2.6782 | -4.0239 | 3.2611 | -3.8014 | 0.5864 | 0.6328 | 0.9527 | 0.7013 | -130.6677 | -5.4635 | 1.1473 | -1.0988 | -7.8379 | -6.5546 | 0.2143 |  | -2.1899 | -2.934 | 3.9994 | 3.3629 | 3.352 | 1.0298 | 10.6596 | 14.1329 | 14.7235 | 11.036 | -0.0001 | -0.003 | 0.0008 | 0.0041 | 0.0004 | -0.0011 | 0.0076 | -0.0132 | 0.0061 | -360.1681 | 17.5034 | -360.5681 | 17.8052 | -360.8943 | 18.1461 | -360.9527 | 17.5363 | -352.826 | 18.7682 | -352.8506 | 16.8361
11:47 | 1640 | 23.1527 | 195.0576 | 436.4688 | 442.536 | -20.918 | -47.1932 | 2.4588 | 0.7479 | -6.4971 | -6.596 | -2.5733 | -3.9071 | 3.2022 | -3.7543 | 0.5873 | 0.6339 | 0.9564 | 0.7001 | -130.7119 | -5.454 | 1.1615 | -1.0416 | -7.8118 | -6.5677 | 0.2719 |  | -2.0894 | -2.9419 | 3.9995 | 3.3648 | 3.3517 | 1.0293 | 10.6583 | 14.1322 | 14.7137 | 11.028 | 0.0001 | -0.003 | 0.0006 | 0.0036 | 0.0003 | -0.0005 | 0.0055 | -0.0055 | -0.0182 | -360.1527 | 17.4603 | -360.5096 | 17.7806 | -360.882 | 18.1687 | -360.9589 | 17.5137 | -352.7798 | 18.7333 | -352.7583 | 16.8217
11:47 | 1641 | 23.161 | 195.1148 | 436.539 | 442.4929 | -20.8944 | -47.0652 | 2.5345 | 0.7116 | -6.5126 | -6.5207 | -2.5341 | -3.9257 | 3.2159 | -3.6907 | 0.586 | 0.6313 | 0.9541 | 0.6998 | -130.8092 | -5.5013 | 1.2285 | -0.9476 | -7.7224 | -6.4402 | 0.3039 |  | -2.1914 | -2.9142 | 3.9994 | 3.3672 | 3.3533 | 1.03 | 10.6572 | 14.1249 | 14.7391 | 11.0392 | -0.0003 | -0.0027 | 0.0001 | 0.0034 | 0.0004 | -0.001 | 0.0124 | 0.0061 | -0.0048 | -360.1835 | 17.4808 | -360.5435 | 17.7785 | -360.9035 | 18.183 | -361.0204 | 17.565 | -352.8198 | 18.7436 | -352.7737 | 16.8156
11:47 | 1642 | 23.1892 | 195.0891 | 436.4482 | 442.5514 | -20.9009 | -47.1515 | 2.5586 | 0.6746 | -6.4734 | -6.6241 | -2.5454 | -4.0305 | 3.1787 | -3.7666 | 0.585 | 0.6297 | 0.9541 | 0.6998 | -130.7113 | -5.5236 | 1.1355 | -0.7456 | -7.7163 | -6.4753 | 0.3512 |  | -2.1514 | -2.9458 | 3.9988 | 3.3656 | 3.3555 | 1.0292 | 10.6342 | 14.0843 | 14.7091 | 11.0107 | -0.0007 | -0.0028 | 0.0008 | 0.0038 | 0.0009 | -0.0003 | -0.0031 | 0.0002 | -0.0113 | -360.2142 | 17.4829 | -360.5404 | 17.7642 | -360.842 | 18.1173 | -360.9066 | 17.5363 | -352.786 | 18.7497 | -352.8229 | 16.8135
11:47 | 1643 | 23.1882 | 195.1527 | 436.5937 | 442.5572 | -20.9703 | -47.0837 | 2.5017 | 0.7604 | -6.4308 | -6.5874 | -2.5413 | -4.1018 | 3.1473 | -3.8065 | 0.588 | 0.6351 | 0.9495 | 0.7008 | -130.6912 | -5.441 | 1.1847 | -0.6948 | -7.6541 | -6.5617 | 0.3714 |  | -2.1918 | -2.9445 | 4.0004 | 3.3644 | 3.3502 | 1.0317 | 10.6455 | 14.1022 | 14.7076 | 11.0323 | -0.0002 | -0.0024 | 0.0009 | 0.0041 | 0.0014 | -0.0005 | 0.0054 | -0.0161 | -0.021 | -360.1681 | 17.5075 | -360.5989 | 17.8175 | -360.9343 | 18.1481 | -360.9127 | 17.5096 | -352.7767 | 18.7908 | -352.8629 | 16.8546
11:47 | 1644 | 23.244 | 195.0906 | 436.5777 | 442.5481 | -21.0146 | -47.1888 | 2.5204 | 0.7897 | -6.5416 | -6.6515 | -2.5798 | -4.0318 | 3.1483 | -3.7509 | 0.5859 | 0.6316 | 0.95 | 0.6996 | -130.691 | -5.4373 | 1.2647 | -0.76 | -7.6145 | -6.5142 | 0.4166 |  | -2.169 | -2.9237 | 4.0018 | 3.3687 | 3.3534 | 1.0325 | 10.6401 | 14.0667 | 14.6607 | 11.0172 | 0.0002 | -0.0031 | 0.0005 | 0.0034 | 0.0007 | -0.0007 | 0.0202 | -0.0095 | -0.023 | -360.1496 | 17.4705 | -360.5558 | 17.7888 | -360.8912 | 18.1522 | -360.9066 | 17.4849 | -352.7521 | 18.7497 | -352.8229 | 16.832
11:47 | 1645 | 23.2899 | 195.0669 | 436.5645 | 442.5822 | -20.9488 | -47.054 | 2.5406 | 0.8176 | -6.5038 | -6.6074 | -2.5632 | -4.054 | 3.1897 | -3.8528 | 0.5862 | 0.6301 | 0.9549 | 0.6998 | -130.7875 | -5.3516 | 1.1929 | -0.7916 | -7.6582 | -6.4692 | 0.3642 |  | -2.1531 | -2.8395 | 4.001 | 3.3688 | 3.3526 | 1.0307 | 10.6214 | 14.1064 | 14.6567 | 11.0208 | 0.0002 | -0.0032 | 0.0014 | 0.0042 | 0.0007 | -0.0005 | 0.0138 | 0.0003 | -0.0089 | -360.2142 | 17.4829 | -360.5404 | 17.7765 | -360.8697 | 18.1892 | -360.9958 | 17.5404 | -352.8475 | 18.7641 | -352.786 | 16.8012
11:47 | 1646 | 23.3161 | 195.1165 | 436.5591 | 442.6502 | -21.0163 | -47.137 | 2.5624 | 0.8589 | -6.4956 | -6.6619 | -2.5394 | -4.0012 | 3.1552 | -3.763 | 0.5858 | 0.6328 | 0.9536 | 0.701 | -130.815 | -5.4226 | 1.1999 | -0.848 | -7.7848 | -6.4862 | 0.3493 |  | -2.1693 | -2.9077 | 4.0013 | 3.365 | 3.3514 | 1.0307 | 10.6387 | 14.0775 | 14.7146 | 11.0266 | 0.0002 | -0.0026 | 0.0006 | 0.0036 | 0.0012 | -0.0007 | 0.0105 | -0.0094 | 0.001 | -360.2327 | 17.4993 | -360.5435 | 17.7477 | -360.8512 | 18.1379 | -360.9343 | 17.5301 | -352.8106 | 18.7682 | -352.7983 | 16.8094
11:47 | 1647 | 23.2049 | 195.1008 | 436.5117 | 442.6517 | -21.0125 | -47.1169 | 2.5296 | 0.854 | -6.4957 | -6.6641 | -2.5728 | -3.9689 | 3.199 | -3.7444 | 0.5855 | 0.6304 | 0.955 | 0.7014 | -130.7829 | -5.2863 | 1.2138 | -0.7995 | -7.7635 | -6.5194 | 0.3666 |  | -2.1173 | -2.8599 | 4.0029 | 3.3657 | 3.3507 | 1.0301 | 10.6134 | 14.0923 | 14.6587 | 10.9786 | -0.0004 | -0.0029 | 0.0006 | 0.0037 | 0.0004 | 0.0001 | 0.0082 | -0.0054 | -0.0081 | -360.2419 | 17.5075 | -360.605 | 17.7826 | -360.9035 | 18.1604 | -360.9312 | 17.5219 | -352.8198 | 18.7867 | -352.8444 | 16.8258
11:47 | 1648 | 23.2195 | 195.1432 | 436.4719 | 442.6485 | -21.1196 | -47.1304 | 2.4332 | 0.8113 | -6.5496 | -6.4916 | -2.5454 | -4.0121 | 3.1269 | -3.7489 | 0.5856 | 0.6301 | 0.9534 | 0.6997 | -130.8008 | -5.3453 | 1.1916 | -0.8536 | -7.7535 | -6.548 | 0.3597 |  | -2.1021 | -2.9135 | 4.0035 | 3.3676 | 3.3536 | 1.0311 | 10.611 | 14.0787 | 14.6755 | 10.993 | -0.0001 | -0.0028 | 0.0005 | 0.0037 | 0.0009 | -0.0009 | 0.0179 | -0.0068 | -0.0145 | -360.1496 | 17.4726 | -360.5219 | 17.7826 | -360.9004 | 18.1728 | -360.9589 | 17.5034 | -352.7644 | 18.7415 | -352.7952 | 16.8258
11:47 | 1649 | 23.3833 | 195.2271 | 436.6813 | 442.7221 | -21.0824 | -47.1178 | 2.5067 | 0.7838 | -6.5603 | -6.7274 | -2.5704 | -3.9441 | 3.1869 | -3.828 | 0.5861 | 0.6334 | 0.9522 | 0.6995 | -130.8019 | -5.3959 | 1.1589 | -0.8169 | -7.6698 | -6.5563 | 0.3337 |  | -2.2217 | -2.9101 | 4.0026 | 3.3649 | 3.3536 | 1.0317 | 10.6504 | 14.1467 | 14.7078 | 11.0212 | -0.0002 | -0.003 | 0.0007 | 0.0035 | 0.0007 | -0.0002 | 0.0179 | -0.0149 | 0.0048 | -360.205 | 17.4623 | -360.5404 | 17.7683 | -360.8943 | 18.1994 | -361.0204 | 17.5301 | -352.7737 | 18.7436 | -352.7644 | 16.8135
11:47 | 1650 | 23.4278 | 195.2638 | 436.5538 | 442.7249 | -20.9975 | -47.0762 | 2.4948 | 0.7691 | -6.4922 | -6.6226 | -2.5382 | -3.9139 | 3.1987 | -3.7326 | 0.5855 | 0.6327 | 0.9544 | 0.6984 | -130.7886 | -5.4025 | 1.1488 | -0.8411 | -7.7317 | -6.5049 | 0.3812 |  | -2.1693 | -2.9368 | 4.0014 | 3.3666 | 3.3524 | 1.0312 | 10.6191 | 14.1097 | 14.6993 | 11.019 | 0.0003 | -0.0025 | 0.0009 | 0.0042 | 0.0012 | -0.0005 | 0.0036 | 0.0052 | -0.0077 | -360.1773 | 17.4685 | -360.5219 | 17.758 | -360.8543 | 18.1645 | -360.9497 | 17.526 | -352.8198 | 18.76 | -352.7829 | 16.8176
11:47 | 1651 | 23.2752 | 195.1072 | 436.5927 | 442.6408 | -21.0377 | -47.1801 | 2.5075 | 0.7504 | -6.4262 | -6.5105 | -2.6592 | -4.043 | 3.1996 | -3.843 | 0.5855 | 0.6295 | 0.9544 | 0.701 | -130.8022 | -5.3743 | 1.239 | -0.9016 | -7.7791 | -6.5096 | 0.3953 |  | -2.2041 | -2.9165 | 4.0021 | 3.367 | 3.3506 | 1.0317 | 10.6539 | 14.0865 | 14.6761 | 11.019 | -0.0005 | -0.0029 | 0.0002 | 0.0035 | 0.0004 | -0.0007 | -0.0093 | -0.0022 | -0.0196 | -360.2388 | 17.5055 | -360.5804 | 17.7724 | -360.9004 | 18.1461 | -360.8974 | 17.5178 | -352.7829 | 18.7805 | -352.8537 | 16.8217
11:47 | 1652 | 23.3307 | 195.1969 | 436.5628 | 442.6959 | -20.9319 | -47.1214 | 2.5256 | 0.814 | -6.3963 | -6.5395 | -2.5036 | -3.9295 | 3.2521 | -3.7417 | 0.5859 | 0.6308 | 0.9531 | 0.7006 | -130.7329 | -5.3671 | 1.2404 | -0.806 | -7.8282 | -6.4381 | 0.3993 |  | -2.2146 | -3.0108 | 4.0016 | 3.3692 | 3.352 | 1.0319 | 10.625 | 14.0922 | 14.6982 | 11.0021 | -0.0003 | -0.0032 | 0.0006 | 0.0038 | 0.0008 | -0.0005 | 0.0007 | -0.0126 | -0.0154 | -360.1619 | 17.487 | -360.5804 | 17.8032 | -360.9127 | 18.1687 | -360.9066 | 17.4972 | -352.7644 | 18.7723 | -352.8783 | 16.8648
11:47 | 1653 | 23.2254 | 195.12 | 436.6784 | 442.6594 | -20.9406 | -47.0572 | 2.625 | 0.846 | -6.4123 | -6.5193 | -2.3872 | -3.9666 | 3.1891 | -3.8183 | 0.5871 | 0.6355 | 0.956 | 0.7024 | -130.7227 | -5.3514 | 1.193 | -0.7523 | -7.8394 | -6.4498 | 0.4141 |  | -2.1882 | -2.8631 | 4.0018 | 3.3671 | 3.3531 | 1.0318 | 10.6422 | 14.1215 | 14.7245 | 11.0182 | 0.0003 | -0.0031 | 0.0013 | 0.004 | 0.0006 | -0.0012 | 0.0055 | -0.0142 | -0.0247 | -360.1496 | 17.4685 | -360.5189 | 17.7621 | -360.885 | 18.1687 | -360.9281 | 17.4993 | -352.7337 | 18.7518 | -352.7767 | 16.8279
11:47 | 1654 | 23.2649 | 195.263 | 436.6051 | 442.7403 | -20.9897 | -47.0489 | 2.5953 | 0.7812 | -6.4117 | -6.4347 | -2.4394 | -3.9378 | 3.183 | -3.8038 | 0.5859 | 0.6309 | 0.9499 | 0.7009 | -130.7928 | -5.3812 | 1.065 | -0.6744 | -7.7868 | -6.3962 | 0.4017 |  | -2.1207 | -2.9107 | 4.0005 | 3.3659 | 3.3512 | 1.0317 | 10.6377 | 14.076 | 14.6764 | 11.0205 | -0.0005 | -0.0035 | 0.0006 | 0.0033 | 0.0004 | -0.0006 | -0.0069 | -0.0078 | -0.0074 | -360.1865 | 17.4911 | -360.5281 | 17.7601 | -360.8635 | 18.1748 | -360.9989 | 17.5445 | -352.8598 | 18.7723 | -352.8137 | 16.8115
11:47 | 1655 | 23.275 | 195.2574 | 436.4873 | 442.7166 | -21.0535 | -47.0613 | 2.5566 | 0.8396 | -6.4204 | -6.5126 | -2.3978 | -3.976 | 3.152 | -3.6354 | 0.5858 | 0.6304 | 0.9531 | 0.6992 | -130.7898 | -5.4107 | 1.1108 | -0.6783 | -7.7386 | -6.53 | 0.4389 |  | -2.0883 | -2.9883 | 4.0011 | 3.367 | 3.3545 | 1.0317 | 10.648 | 14.1272 | 14.6945 | 11.0013 | -0.0003 | -0.0028 | 0.0008 | 0.0041 | 0.001 | -0.0006 | -0.0073 | 0.0021 | -0.0041 | -360.2265 | 17.4972 | -360.5281 | 17.7457 | -360.8358 | 18.1358 | -360.9127 | 17.5157 | -352.8014 | 18.7703 | -352.8075 | 16.7991
11:47 | 1656 | 23.3307 | 195.3017 | 436.5952 | 442.7326 | -21.0148 | -47.0073 | 2.6393 | 0.8018 | -6.4179 | -6.4296 | -2.5176 | -3.9043 | 3.2622 | -3.6581 | 0.5867 | 0.6306 | 0.949 | 0.6993 | -130.8184 | -5.4603 | 1.176 | -0.6419 | -7.7022 | -6.4549 | 0.4436 |  | -2.1914 | -2.9688 | 4.0014 | 3.3645 | 3.3521 | 1.0328 | 10.6376 | 14.0936 | 14.6901 | 11.0313 | -0.0002 | -0.003 | 0.0006 | 0.0039 | 0.0003 | -0.0003 | 0.0234 | -0.006 | -0.0147 | -360.1619 | 17.489 | -360.5866 | 17.7888 | -360.9127 | 18.1707 | -360.9435 | 17.5321 | -352.7952 | 18.7805 | -352.8383 | 16.8402
11:47 | 1657 | 23.2961 | 195.3271 | 436.5627 | 442.7281 | -20.8424 | -47.0492 | 2.6976 | 0.824 | -6.4909 | -6.5491 | -2.4797 | -4.0062 | 3.2459 | -3.6814 | 0.5853 | 0.6307 | 0.9509 | 0.6997 | -130.7997 | -5.3938 | 1.1325 | -0.6861 | -7.7281 | -6.4585 | 0.3797 |  | -2.1494 | -2.9875 | 4.0003 | 3.365 | 3.3488 | 1.0314 | 10.6375 | 14.14 | 14.7259 | 11.0598 | 0.0001 | -0.0029 | 0.0003 | 0.0034 | 0.0006 | -0.0006 | -0.0039 | -0.0098 | -0.0078 | -360.1127 | 17.4603 | -360.5127 | 17.7621 | -360.8912 | 18.183 | -360.9497 | 17.4972 | -352.7614 | 18.7395 | -352.789 | 16.8217
11:47 | 1658 | 23.2937 | 195.2519 | 436.5288 | 442.6779 | -20.9367 | -46.8981 | 2.6923 | 0.7692 | -6.3777 | -6.5111 | -2.4488 | -3.9933 | 3.3072 | -3.7174 | 0.5872 | 0.6332 | 0.9527 | 0.7003 | -130.8447 | -5.3768 | 1.0939 | -0.6995 | -7.741 | -6.3939 | 0.4187 |  | -2.1479 | -3.0117 | 4.0015 | 3.3642 | 3.353 | 1.0315 | 10.6513 | 14.1426 | 14.7355 | 11.0558 | -0.0001 | -0.0031 | 0.0009 | 0.0039 | 0.0005 | -0.0003 | 0.0002 | 0.0004 | -0.0134 | -360.1804 | 17.4623 | -360.5589 | 17.7703 | -360.9281 | 18.1851 | -360.9558 | 17.5383 | -352.8137 | 18.7559 | -352.8106 | 16.8258
11:47 | 1659 | 23.3353 | 195.2955 | 436.6106 | 442.7093 | -20.9465 | -46.8018 | 2.7177 | 0.8186 | -6.3664 | -6.5621 | -2.4331 | -4.0026 | 3.2245 | -3.7421 | 0.5853 | 0.6307 | 0.9531 | 0.6996 | -130.9285 | -5.5129 | 1.1446 | -0.6372 | -7.7006 | -6.5479 | 0.4751 |  | -2.061 | -2.9674 | 3.9997 | 3.364 | 3.3488 | 1.0313 | 10.6481 | 14.1095 | 14.7214 | 11.0136 | -0.0009 | -0.0031 | 0.0006 | 0.0035 | 0.0011 | -0.0008 | -0.001 | -0.0066 | 0.0052 | -360.1988 | 17.4972 | -360.5558 | 17.7518 | -360.845 | 18.1461 | -360.9158 | 17.5178 | -352.7921 | 18.7682 | -352.7829 | 16.8074
11:47 | 1660 | 23.3203 | 195.2951 | 436.5304 | 442.6198 | -20.8669 | -46.8239 | 2.8254 | 0.8082 | -6.407 | -6.6329 | -2.4973 | -3.9197 | 3.2989 | -3.6104 | 0.5864 | 0.6281 | 0.9501 | 0.6996 | -130.8544 | -5.5401 | 1.137 | -0.744 | -7.7876 | -6.5057 | 0.4358 |  | -2.1878 | -2.9118 | 4.0007 | 3.3634 | 3.3503 | 1.0309 | 10.6699 | 14.1262 | 14.7184 | 11.0457 | -0.0002 | -0.0025 | 0.0009 | 0.0037 | 0.0007 | -0.0003 | 0.0141 | -0.0012 | -0.001 | -360.2358 | 17.5034 | -360.6235 | 17.7991 | -360.922 | 18.1584 | -360.9343 | 17.5137 | -352.8321 | 18.7846 | -352.8537 | 16.8443
11:47 | 1661 | 23.4152 | 195.3834 | 436.6325 | 442.7112 | -20.8687 | -46.9286 | 2.7454 | 0.8325 | -6.3857 | -6.5294 | -2.5064 | -3.9503 | 3.2792 | -3.6184 | 0.5867 | 0.6311 | 0.9506 | 0.6998 | -130.8552 | -5.5523 | 1.0913 | -0.7565 | -7.7644 | -6.4955 | 0.4043 |  | -2.0848 | -2.8632 | 3.9997 | 3.366 | 3.3537 | 1.0333 | 10.6584 | 14.1144 | 14.7221 | 11.058 | -0.0007 | -0.0035 | 0.0007 | 0.0039 | 0.0012 | -0.0005 | 0.0095 | -0.0184 | -0.0118 | -360.1742 | 17.4788 | -360.5619 | 17.7642 | -360.842 | 18.1481 | -360.9127 | 17.4993 | -352.746 | 18.76 | -352.8075 | 16.8197
11:47 | 1662 | 23.3327 | 195.3051 | 436.5455 | 442.6619 | -20.8805 | -46.9583 | 2.6 | 0.8586 | -6.3409 | -6.6301 | -2.441 | -3.9425 | 3.2631 | -3.6207 | 0.5874 | 0.6311 | 0.9536 | 0.7005 | -130.8173 | -5.478 | 1.1982 | -0.715 | -7.8193 | -6.4705 | 0.3558 |  | -2.0374 | -2.9248 | 4.0005 | 3.3626 | 3.3513 | 1.0311 | 10.6354 | 14.0854 | 14.6747 | 11.0006 | 0.0001 | -0.0031 | 0.0002 | 0.0034 | 0.0006 | -0.0007 | 0.0118 | -0.0153 | -0.0092 | -360.1927 | 17.4829 | -360.5466 | 17.7765 | -360.9251 | 18.1851 | -360.9927 | 17.5404 | -352.7983 | 18.7641 | -352.8167 | 16.832
11:47 | 1663 | 23.3876 | 195.3821 | 436.5668 | 442.6334 | -20.8278 | -46.9803 | 2.6557 | 0.8007 | -6.5123 | -6.7028 | -2.4741 | -3.9546 | 3.3066 | -3.6071 | 0.5846 | 0.6318 | 0.9525 | 0.7004 | -130.8089 | -5.4234 | 1.2021 | -0.6668 | -7.7777 | -6.4069 | 0.3748 |  | -2.0163 | -2.912 | 4.0015 | 3.3649 | 3.3523 | 1.032 | 10.6457 | 14.1076 | 14.7044 | 11.0334 | 0 | -0.0028 | 0.0005 | 0.004 | 0.0007 | -0.0003 | 0.017 | -0.0041 | -0.0185 | -360.2111 | 17.4644 | -360.5219 | 17.7498 | -360.8358 | 18.1399 | -360.9497 | 17.528 | -352.7829 | 18.7518 | -352.8075 | 16.8032
11:47 | 1664 | 23.4157 | 195.3234 | 436.6522 | 442.7084 | -20.845 | -46.9346 | 2.6252 | 0.8148 | -6.4391 | -6.644 | -2.4836 | -3.9569 | 3.2978 | -3.5896 | 0.5878 | 0.6334 | 0.9525 | 0.7017 | -130.829 | -5.5135 | 1.1887 | -0.7832 | -7.7496 | -6.5105 | 0.3506 |  | -2.1359 | -2.9114 | 4.002 | 3.3633 | 3.352 | 1.0329 | 10.6688 | 14.1076 | 14.687 | 11.0392 | -0.0005 | -0.0028 | 0.0004 | 0.0041 | 0.0009 | -0.0008 | -0.0025 | -0.0036 | -0.0106 | -360.2111 | 17.5013 | -360.5312 | 17.758 | -360.882 | 18.1748 | -360.9404 | 17.5178 | -352.8167 | 18.7723 | -352.8014 | 16.8094
11:47 | 1665 | 23.3871 | 195.3435 | 436.6075 | 442.7881 | -20.9128 | -46.9243 | 2.7241 | 0.8246 | -6.3627 | -6.5878 | -2.4412 | -3.9464 | 3.2547 | -3.5456 | 0.5849 | 0.6297 | 0.9558 | 0.701 | -130.7836 | -5.4396 | 1.1194 | -0.7328 | -7.7507 | -6.4511 | 0.3719 |  | -2.0535 | -2.9117 | 4.0022 | 3.3677 | 3.3524 | 1.0316 | 10.6317 | 14.1228 | 14.698 | 11.0478 | -0.0001 | -0.0028 | 0.0006 | 0.0038 | 0.0004 | -0.0004 | -0.0015 | -0.0117 | -0.0226 | -360.1404 | 17.4767 | -360.5589 | 17.7785 | -360.882 | 18.1543 | -360.9312 | 17.5157 | -352.7706 | 18.7579 | -352.8014 | 16.834
11:47 | 1666 | 23.4636 | 195.3246 | 436.6591 | 442.7715 | -20.8576 | -46.9634 | 2.7807 | 0.7713 | -6.4041 | -6.6664 | -2.3843 | -3.8716 | 3.3276 | -3.6619 | 0.5857 | 0.6371 | 0.9541 | 0.7011 | -130.8082 | -5.4105 | 1.1088 | -0.8885 | -7.6881 | -6.5083 | 0.411 |  | -2.052 | -2.8687 | 4.0011 | 3.366 | 3.3499 | 1.0311 | 10.6411 | 14.1202 | 14.6932 | 11.0118 | 0 | -0.0033 | 0.0005 | 0.0037 | 0.001 | -0.0008 | -0.0067 | -0.0079 | -0.0091 | -360.1558 | 17.4705 | -360.5343 | 17.7642 | -360.882 | 18.183 | -360.9527 | 17.5034 | -352.7521 | 18.76 | -352.7798 | 16.8135
11:47 | 1667 | 23.4122 | 195.2383 | 436.6785 | 442.755 | -20.8843 | -47.0692 | 2.7121 | 0.7533 | -6.4039 | -6.7231 | -2.5201 | -3.8691 | 3.2974 | -3.5899 | 0.5856 | 0.6329 | 0.951 | 0.7025 | -130.8142 | -5.4746 | 1.1217 | -0.823 | -7.7203 | -6.5693 | 0.3436 |  | -2.0853 | -2.8763 | 4.0009 | 3.3668 | 3.3527 | 1.0323 | 10.6607 | 14.088 | 14.6912 | 11.0251 | 0 | -0.0027 | 0.0006 | 0.0034 | 0.0004 | -0.0003 | 0.0133 | -0.0065 | -0.0172 | -360.1927 | 17.4747 | -360.5466 | 17.7806 | -360.8881 | 18.1584 | -360.9343 | 17.526 | -352.786 | 18.7579 | -352.8167 | 16.834
11:48 | 1668 | 23.462 | 195.3088 | 436.6446 | 442.8634 | -20.8883 | -47.0039 | 2.7476 | 0.6814 | -6.4575 | -6.7271 | -2.4862 | -3.8875 | 3.2602 | -3.6136 | 0.5856 | 0.6317 | 0.9521 | 0.7012 | -130.7892 | -5.4895 | 1.1481 | -0.8063 | -7.7202 | -6.5025 | 0.3531 |  | -2.109 | -3.0067 | 4.0018 | 3.3678 | 3.3497 | 1.0332 | 10.6214 | 14.1005 | 14.6673 | 11.0385 | -0.0004 | -0.0028 | 0.0005 | 0.0031 | 0.0009 | -0.0009 | 0.025 | -0.0101 | -0.0046 | -360.1988 | 17.4911 | -360.5589 | 17.758 | -360.8789 | 18.1584 | -360.9004 | 17.5178 | -352.7706 | 18.7661 | -352.829 | 16.8115
11:48 | 1669 | 23.3554 | 195.2673 | 436.5201 | 442.8093 | -20.8956 | -46.9711 | 2.7283 | 0.6578 | -6.4491 | -6.6603 | -2.5084 | -3.8423 | 3.2157 | -3.6099 | 0.5859 | 0.6326 | 0.9527 | 0.7007 | -130.8145 | -5.489 | 1.2049 | -0.8849 | -7.6394 | -6.4554 | 0.4268 |  | -2.0829 | -2.9603 | 4.0024 | 3.3646 | 3.3506 | 1.0313 | 10.6504 | 14.0947 | 14.6788 | 11.0269 | -0.0003 | -0.0024 | 0.0005 | 0.0035 | 0.001 | -0.0006 | 0.0156 | 0.0077 | -0.0171 | -360.1835 | 17.4849 | -360.5712 | 17.7765 | -360.8758 | 18.1707 | -360.9435 | 17.5075 | -352.8075 | 18.7867 | -352.8106 | 16.834
11:48 | 1670 | 23.4184 | 195.2641 | 436.5602 | 442.7437 | -20.8483 | -46.8808 | 2.7182 | 0.7101 | -6.3917 | -6.651 | -2.5043 | -3.8703 | 3.2822 | -3.584 | 0.5866 | 0.6308 | 0.9572 | 0.7012 | -130.8642 | -5.5494 | 1.2172 | -0.8284 | -7.7084 | -6.4247 | 0.4735 |  | -2.1551 | -2.9687 | 4.0021 | 3.3657 | 3.3518 | 1.032 | 10.6294 | 14.0858 | 14.6837 | 11.0341 | 0 | -0.0029 | 0.0004 | 0.0038 | 0.0008 | -0.0005 | 0.0154 | -0.004 | -0.0079 | -360.1558 | 17.4685 | -360.5466 | 17.7744 | -360.8727 | 18.1604 | -360.9681 | 17.5116 | -352.7644 | 18.7703 | -352.8321 | 16.8176
11:48 | 1671 | 23.3381 | 195.2023 | 436.5196 | 442.7145 | -20.8277 | -46.9521 | 2.7273 | 0.7606 | -6.3851 | -6.5231 | -2.4933 | -3.8404 | 3.2806 | -3.619 | 0.5856 | 0.6291 | 0.9507 | 0.7017 | -130.8973 | -5.5283 | 1.1122 | -0.8675 | -7.711 | -6.4505 | 0.4439 |  | -2.1593 | -2.9756 | 4.0022 | 3.3645 | 3.3514 | 1.0312 | 10.6285 | 14.0897 | 14.6886 | 11.0234 | -0.0004 | -0.0033 | 0.0003 | 0.0035 | 0.0007 | -0.001 | 0.0104 | -0.0141 | -0.0235 | -360.165 | 17.4808 | -360.5435 | 17.7621 | -360.882 | 18.1748 | -360.9466 | 17.5198 | -352.7952 | 18.7723 | -352.8014 | 16.832
11:48 | 1672 | 23.4424 | 195.231 | 436.4756 | 442.805 | -20.8397 | -46.9773 | 2.8202 | 0.8158 | -6.3193 | -6.46 | -2.4646 | -3.9073 | 3.3127 | -3.609 | 0.5871 | 0.634 | 0.9508 | 0.7004 | -130.8543 | -5.5158 | 1.2825 | -0.8327 | -7.7332 | -6.4735 | 0.4204 |  | -2.0777 | -2.953 | 4.0032 | 3.3649 | 3.3533 | 1.0301 | 10.6307 | 14.0982 | 14.6829 | 11.0302 | 0.0001 | -0.002 | 0.0005 | 0.0036 | 0.0004 | -0.0004 | 0.0182 | -0.0052 | 0.0107 | -360.165 | 17.4747 | -360.5312 | 17.7621 | -360.8697 | 18.1543 | -360.9343 | 17.5239 | -352.7706 | 18.7641 | -352.8106 | 16.8238
11:48 | 1673 | 23.472 | 195.2838 | 436.5892 | 442.8353 | -20.8922 | -47.0022 | 2.7814 | 0.8058 | -6.3489 | -6.3937 | -2.3845 | -3.8823 | 3.337 | -3.5821 | 0.5854 | 0.6308 | 0.9511 | 0.7005 | -130.8497 | -5.4863 | 1.2444 | -0.8529 | -7.716 | -6.4762 | 0.3856 |  | -2.018 | -2.9625 | 4.0015 | 3.3605 | 3.3497 | 1.0317 | 10.6387 | 14.1181 | 14.7157 | 11.0146 | -0.0003 | -0.0027 | 0.001 | 0.0039 | 0.0012 | -0.0005 | 0.0087 | 0.0012 | -0.008 | -360.2081 | 17.4911 | -360.5558 | 17.7601 | -360.8912 | 18.183 | -360.9404 | 17.5157 | -352.7952 | 18.7723 | -352.8414 | 16.8197
11:48 | 1674 | 23.5062 | 195.3415 | 436.7274 | 442.9206 | -20.8859 | -47.0843 | 2.7583 | 0.8409 | -6.3751 | -6.6008 | -2.4391 | -3.9422 | 3.3752 | -3.5283 | 0.5863 | 0.6309 | 0.9527 | 0.7002 | -130.7606 | -5.4158 | 1.2973 | -0.7419 | -7.7215 | -6.4525 | 0.4301 |  | -2.1563 | -3.0348 | 4.0023 | 3.3659 | 3.3526 | 1.0324 | 10.6665 | 14.1283 | 14.748 | 11.0197 | -0.0001 | -0.0033 | 0.001 | 0.0042 | 0.0002 | -0.0005 | 0.005 | -0.0021 | -0.0213 | -360.1681 | 17.4767 | -360.5343 | 17.7703 | -360.8604 | 18.1707 | -360.9527 | 17.5116 | -352.8044 | 18.7497 | -352.7798 | 16.8299
11:48 | 1675 | 23.5402 | 195.3163 | 436.6446 | 442.875 | -20.8212 | -47.0492 | 2.7526 | 0.8207 | -6.3444 | -6.5169 | -2.421 | -3.8881 | 3.2617 | -3.4753 | 0.5863 | 0.6299 | 0.9499 | 0.7008 | -130.8108 | -5.4761 | 1.2218 | -0.7778 | -7.742 | -6.4061 | 0.3678 |  | -2.1457 | -2.9721 | 4.0012 | 3.364 | 3.3476 | 1.033 | 10.6469 | 14.0854 | 14.6863 | 11.0122 | -0.0003 | -0.0033 | 0.0006 | 0.0037 | 0.0012 | -0.0008 | 0.0012 | -0.0101 | -0.0153 | -360.1865 | 17.4829 | -360.5373 | 17.7724 | -360.8635 | 18.1687 | -360.9466 | 17.5239 | -352.7921 | 18.7661 | -352.8106 | 16.8156
11:48 | 1676 | 23.6477 | 195.3969 | 436.644 | 442.919 | -20.8889 | -47.0597 | 2.7685 | 0.8277 | -6.3846 | -6.4887 | -2.4437 | -3.9263 | 3.2794 | -3.4809 | 0.5861 | 0.6288 | 0.9517 | 0.7017 | -130.8153 | -5.4416 | 1.2049 | -0.711 | -7.7313 | -6.4181 | 0.4152 |  | -2.1768 | -2.9687 | 4.0033 | 3.3653 | 3.3526 | 1.0321 | 10.6573 | 14.119 | 14.7034 | 11.028 | -0.0004 | -0.003 | 0.0005 | 0.0032 | 0.0004 | -0.0009 | 0.0049 | -0.0037 | -0.0123 | -360.1804 | 17.4849 | -360.5158 | 17.7744 | -360.885 | 18.1481 | -360.9312 | 17.5239 | -352.7921 | 18.7641 | -352.789 | 16.8197
11:48 | 1677 | 23.4658 | 195.2766 | 436.657 | 442.9459 | -20.8456 | -47.0847 | 2.7374 | 0.8104 | -6.4241 | -6.481 | -2.4247 | -3.9587 | 3.3689 | -3.5175 | 0.5854 | 0.6289 | 0.9498 | 0.7014 | -130.8092 | -5.4251 | 1.2779 | -0.7385 | -7.7174 | -6.4241 | 0.3764 |  | -2.1322 | -2.9687 | 4.0025 | 3.3663 | 3.3522 | 1.0327 | 10.6297 | 14.0734 | 14.6542 | 10.9786 | -0.0004 | -0.003 | 0.0007 | 0.0035 | 0.0004 | -0.001 | 0.0011 | -0.0022 | -0.0099 | -360.1865 | 17.4829 | -360.5712 | 17.7826 | -360.882 | 18.1645 | -360.9312 | 17.5157 | -352.789 | 18.7805 | -352.8321 | 16.834
11:48 | 1678 | 23.5358 | 195.2901 | 436.7311 | 442.99 | -20.8148 | -47.0506 | 2.7464 | 0.8077 | -6.4113 | -6.4797 | -2.5188 | -3.8982 | 3.4059 | -3.4241 | 0.5869 | 0.6326 | 0.9511 | 0.701 | -130.8386 | -5.5361 | 1.225 | -0.7862 | -7.719 | -6.4281 | 0.4323 |  | -2.1716 | -3.053 | 4.0023 | 3.3658 | 3.3504 | 1.0321 | 10.6469 | 14.0971 | 14.6932 | 10.9887 | -0.0005 | -0.0033 | 0.001 | 0.0036 | 0.0008 | -0.0006 | 0.0143 | 0.0011 | -0.0007 | -360.2081 | 17.4849 | -360.5496 | 17.7847 | -360.8943 | 18.1666 | -360.9281 | 17.5055 | -352.7798 | 18.76 | -352.7737 | 16.8176
11:48 | 1679 | 23.5498 | 195.3839 | 436.6694 | 443.0329 | -20.8553 | -47.0389 | 2.7255 | 0.804 | -6.3436 | -6.393 | -2.509 | -3.8977 | 3.3906 | -3.419 | 0.5861 | 0.6319 | 0.9518 | 0.7003 | -130.7481 | -5.5091 | 1.362 | -0.7894 | -7.7617 | -6.333 | 0.4517 |  | -2.1883 | -2.9293 | 4.0035 | 3.3634 | 3.355 | 1.0331 | 10.6422 | 14.104 | 14.7119 | 11.0244 | -0.0001 | -0.0031 | 0.0005 | 0.0037 | 0.0007 | -0.0006 | 0.0215 | -0.0083 | -0.0021 | -360.1681 | 17.4767 | -360.5558 | 17.8032 | -360.8758 | 18.1789 | -360.9712 | 17.528 | -352.7706 | 18.7703 | -352.8198 | 16.8381
11:48 | 1680 | 23.5015 | 195.3143 | 436.6895 | 442.976 | -20.8138 | -47.0989 | 2.7391 | 0.8994 | -6.2561 | -6.4019 | -2.4532 | -3.8501 | 3.3627 | -3.4756 | 0.5862 | 0.6287 | 0.9503 | 0.7006 | -130.7476 | -5.5623 | 1.3289 | -0.8309 | -7.8443 | -6.414 | 0.3104 |  | -2.1156 | -2.9156 | 4.0029 | 3.3643 | 3.3516 | 1.0308 | 10.6353 | 14.1028 | 14.7163 | 11.0349 | -0.0005 | -0.0033 | 0.0004 | 0.0039 | 0.0007 | -0.0007 | 0.0093 | -0.0051 | -0.0112 | -360.1988 | 17.489 | -360.5127 | 17.7642 | -360.8727 | 18.1543 | -360.9435 | 17.5198 | -352.7737 | 18.7579 | -352.7829 | 16.7971
11:48 | 1681 | 23.4843 | 195.3089 | 436.6232 | 442.8673 | -20.9078 | -47.1366 | 2.7017 | 0.8809 | -6.2965 | -6.4325 | -2.4528 | -3.9025 | 3.3641 | -3.4401 | 0.5869 | 0.6309 | 0.9504 | 0.7 | -130.7324 | -5.4935 | 1.4074 | -0.7606 | -7.8603 | -6.4215 | 0.3804 |  | -2.0861 | -2.9047 | 4.0019 | 3.3652 | 3.3559 | 1.0329 | 10.6468 | 14.1203 | 14.7058 | 11.0172 | -0.0006 | -0.0028 | 0.0007 | 0.0037 | 0.0006 | -0.0003 | 0.012 | -0.0115 | -0.0193 | -360.2019 | 17.4829 | -360.5681 | 17.795 | -360.8881 | 18.1748 | -360.9558 | 17.5301 | -352.8137 | 18.7703 | -352.8414 | 16.832
11:48 | 1682 | 23.5454 | 195.309 | 436.5629 | 442.8258 | -20.9835 | -47.1497 | 2.6162 | 0.9337 | -6.256 | -6.5108 | -2.484 | -3.9171 | 3.3098 | -3.4974 | 0.5866 | 0.6313 | 0.9507 | 0.7009 | -130.8841 | -5.5423 | 1.3593 | -0.7476 | -7.8293 | -6.3853 | 0.3645 |  | -2.1316 | -2.8791 | 4.0024 | 3.3653 | 3.3526 | 1.033 | 10.6608 | 14.0992 | 14.7227 | 11.0205 | -0.0008 | -0.0034 | 0.0005 | 0.0036 | 0.0011 | -0.0003 | 0.0122 | -0.0021 | -0.005 | -360.1496 | 17.4767 | -360.5466 | 17.7642 | -360.8666 | 18.183 | -360.922 | 17.4972 | -352.7552 | 18.7538 | -352.7706 | 16.8176
11:48 | 1683 | 23.4655 | 195.2785 | 436.595 | 442.8778 | -21.042 | -47.0466 | 2.5592 | 0.9297 | -6.2749 | -6.4661 | -2.4977 | -3.953 | 3.3381 | -3.4953 | 0.5865 | 0.6301 | 0.9511 | 0.7013 | -130.8194 | -5.4752 | 1.2784 | -0.7272 | -7.7719 | -6.278 | 0.4577 |  | -2.0791 | -2.8934 | 4.0027 | 3.3638 | 3.3528 | 1.0317 | 10.6261 | 14.1051 | 14.6601 | 11.0028 | 0.0001 | -0.0031 | 0.0006 | 0.0034 | 0.0005 | -0.0001 | 0.0094 | -0.0054 | 0.0074 | -360.1096 | 17.4726 | -360.5466 | 17.8052 | -360.9035 | 18.1789 | -361.0143 | 17.5363 | -352.8075 | 18.762 | -352.8321 | 16.8299
11:48 | 1684 | 23.5019 | 195.3134 | 436.6247 | 442.8734 | -21.0612 | -47.0256 | 2.5425 | 0.9262 | -6.2899 | -6.4666 | -2.3735 | -3.9734 | 3.3298 | -3.519 | 0.587 | 0.6261 | 0.95 | 0.7012 | -130.9044 | -5.5336 | 1.2702 | -0.7404 | -7.8072 | -6.3069 | 0.402 |  | -2.0483 | -2.81 | 4.0022 | 3.3645 | 3.3524 | 1.0334 | 10.663 | 14.1019 | 14.7286 | 10.9868 | 0.0001 | -0.0029 | 0.0006 | 0.0036 | 0.0005 | -0.0009 | 0.0004 | 0.0039 | -0.0043 | -360.165 | 17.4829 | -360.5189 | 17.7662 | -360.842 | 18.1687 | -360.9404 | 17.5178 | -352.7921 | 18.7744 | -352.789 | 16.8094
11:48 | 1685 | 23.5199 | 195.3116 | 436.6382 | 442.9087 | -21.0225 | -47.1127 | 2.6423 | 0.9838 | -6.2384 | -6.4254 | -2.4868 | -4.0281 | 3.371 | -3.5456 | 0.5864 | 0.6285 | 0.9545 | 0.6991 | -130.8353 | -5.4633 | 1.3107 | -0.6842 | -7.8452 | -6.293 | 0.3898 |  | -2.0115 | -2.9084 | 4.0035 | 3.3657 | 3.3557 | 1.0336 | 10.6551 | 14.0992 | 14.6764 | 11.0089 | -0.0006 | -0.003 | 0.0005 | 0.0035 | 0.0005 | -0.0007 | 0.0073 | -0.002 | 0.015 | -360.1619 | 17.4849 | -360.5989 | 17.7888 | -360.8574 | 18.1666 | -360.9251 | 17.5096 | -352.7952 | 18.7908 | -352.8352 | 16.8381
11:48 | 1686 | 23.4561 | 195.2825 | 436.6451 | 442.9456 | -20.9844 | -47.198 | 2.6554 | 0.9533 | -6.2791 | -6.6609 | -2.6119 | -4.0387 | 3.4456 | -3.5283 | 0.5865 | 0.6295 | 0.948 | 0.7001 | -130.8253 | -5.4781 | 1.249 | -0.7758 | -7.7921 | -6.2891 | 0.36 |  | -1.9392 | -2.9043 | 4.0031 | 3.363 | 3.3538 | 1.032 | 10.6676 | 14.1182 | 14.682 | 11.02 | -0.0002 | -0.0023 | 0.0007 | 0.0038 | 0.0007 | -0.0008 | 0.0138 | -0.0121 | 0.0085 | -360.2111 | 17.487 | -360.5589 | 17.7806 | -360.885 | 18.1748 | -360.9466 | 17.5075 | -352.7798 | 18.7723 | -352.826 | 16.8279
11:48 | 1687 | 23.4241 | 195.2843 | 436.6537 | 442.9495 | -20.9632 | -47.2637 | 2.7726 | 0.8725 | -6.2527 | -6.4889 | -2.54 | -3.8949 | 3.4783 | -3.4934 | 0.5867 | 0.6275 | 0.9521 | 0.6995 | -130.8837 | -5.6025 | 1.367 | -0.7754 | -7.8051 | -6.259 | 0.5039 |  | -1.9916 | -2.8117 | 4.002 | 3.3655 | 3.3535 | 1.034 | 10.6712 | 14.0982 | 14.6829 | 11.0533 | 0.0001 | -0.0029 | 0.0006 | 0.0038 | 0.0009 | -0.0004 | 0.0135 | -0.0093 | 0.0058 | -360.1711 | 17.4685 | -360.525 | 17.7744 | -360.8574 | 18.1871 | -360.9558 | 17.5301 | -352.7798 | 18.7518 | -352.789 | 16.8094
11:48 | 1688 | 23.5577 | 195.2783 | 436.7703 | 442.9268 | -20.9682 | -47.0936 | 2.715 | 0.9587 | -6.1625 | -6.4785 | -2.4515 | -3.9232 | 3.446 | -3.5384 | 0.5854 | 0.6259 | 0.9501 | 0.7009 | -130.8435 | -5.5295 | 1.3285 | -0.7436 | -7.7005 | -6.1934 | 0.4915 |  | -1.9702 | -2.8261 | 4.0014 | 3.3655 | 3.3513 | 1.0326 | 10.6374 | 14.1288 | 14.728 | 11.0475 | 0.0002 | -0.0031 | 0.0009 | 0.0042 | 0.0006 | -0.0002 | -0.0068 | -0.0003 | -0.0184 | -360.2265 | 17.4952 | -360.5312 | 17.7642 | -360.885 | 18.1687 | -360.9558 | 17.5239 | -352.8198 | 18.7805 | -352.786 | 16.793
11:48 | 1689 | 23.5513 | 195.2888 | 436.7037 | 442.9944 | -20.9944 | -47.1646 | 2.7007 | 0.9033 | -6.169 | -6.5143 | -2.4989 | -3.8864 | 3.4129 | -3.5021 | 0.5851 | 0.6293 | 0.9475 | 0.7002 | -130.9043 | -5.545 | 1.2988 | -0.7089 | -7.6672 | -6.144 | 0.4387 |  | -1.9902 | -2.8003 | 4.0015 | 3.3662 | 3.3491 | 1.0335 | 10.6572 | 14.0904 | 14.7344 | 11.0215 | 0.0001 | -0.0026 | 0.0009 | 0.0041 | 0.0009 | -0.0006 | 0.0107 | -0.0128 | -0.0151 | -360.1681 | 17.4808 | -360.565 | 17.7929 | -360.885 | 18.1748 | -360.9281 | 17.5034 | -352.7798 | 18.7785 | -352.8167 | 16.8299
11:48 | 1690 | 23.5455 | 195.2809 | 436.7494 | 442.9797 | -20.9078 | -47.1407 | 2.8009 | 0.8594 | -6.0915 | -6.4906 | -2.5091 | -4.0132 | 3.322 | -3.5922 | 0.5885 | 0.6284 | 0.9492 | 0.7002 | -130.839 | -5.5564 | 1.2815 | -0.6471 | -7.6019 | -6.1345 | 0.529 |  | -1.934 | -2.8099 | 4.0031 | 3.3681 | 3.3521 | 1.033 | 10.655 | 14.1109 | 14.718 | 11.0548 | -0.0006 | -0.0027 | 0.0001 | 0.0036 | 0.0008 | -0.0001 | 0.0009 | 0 | -0.0036 | -360.1096 | 17.4705 | -360.5435 | 17.7991 | -360.9127 | 18.2036 | -360.9681 | 17.4931 | -352.7521 | 18.76 | -352.8229 | 16.8279
11:48 | 1691 | 23.455 | 195.3316 | 436.7509 | 442.9388 | -20.9552 | -47.1806 | 2.6844 | 0.8985 | -6.1576 | -6.5535 | -2.5361 | -3.917 | 3.3962 | -3.5118 | 0.5873 | 0.6297 | 0.9515 | 0.7011 | -130.7635 | -5.4639 | 1.3546 | -0.6088 | -7.6392 | -6.0587 | 0.4736 |  | -1.9376 | -2.99 | 4.003 | 3.3676 | 3.3532 | 1.0343 | 10.6503 | 14.1064 | 14.7088 | 11.0381 | 0.0003 | -0.0026 | 0.0006 | 0.0038 | 0.0008 | -0.0007 | 0.0085 | -0.0182 | -0.021 | -360.1311 | 17.4541 | -360.5096 | 17.7724 | -360.8789 | 18.183 | -360.9374 | 17.5198 | -352.7767 | 18.7395 | -352.7798 | 16.8258
11:48 | 1692 | 23.5106 | 195.3563 | 436.7129 | 443.0094 | -20.9447 | -47.1727 | 2.7551 | 0.9064 | -6.1554 | -6.4682 | -2.4649 | -3.9263 | 3.3755 | -3.5684 | 0.5861 | 0.6265 | 0.9485 | 0.7013 | -130.7724 | -5.5724 | 1.3656 | -0.6112 | -7.5794 | -6.1948 | 0.3884 |  | -2.0545 | -2.9866 | 4.0036 | 3.3649 | 3.3505 | 1.0323 | 10.6331 | 14.0888 | 14.7009 | 11.0215 | 0.0001 | -0.0032 | 0.0003 | 0.0032 | 0.0006 | -0.0005 | -0.0017 | -0.0098 | -0.0123 | -360.2235 | 17.5013 | -360.5619 | 17.7826 | -360.842 | 18.1851 | -360.9435 | 17.528 | -352.8414 | 18.7887 | -352.7983 | 16.8135
11:48 | 1693 | 23.4426 | 195.3088 | 436.7758 | 443.0352 | -20.9979 | -47.1279 | 2.5836 | 0.8848 | -6.1645 | -6.4513 | -2.5053 | -3.9281 | 3.3645 | -3.5544 | 0.5866 | 0.6277 | 0.9481 | 0.7006 | -130.7268 | -5.4818 | 1.3042 | -0.5317 | -7.6074 | -6.1407 | 0.4424 |  | -1.993 | -2.9088 | 4.0032 | 3.3626 | 3.3499 | 1.0337 | 10.6319 | 14.0934 | 14.688 | 11.0262 | -0.0001 | -0.0028 | 0.0005 | 0.0039 | 0.001 | -0.0007 | 0.0081 | -0.0058 | -0.0007 | -360.1896 | 17.4931 | -360.5435 | 17.7806 | -360.8881 | 18.1563 | -360.8697 | 17.4829 | -352.8014 | 18.7805 | -352.8229 | 16.8238
11:48 | 1694 | 23.3959 | 195.3987 | 436.7277 | 442.9059 | -20.945 | -47.0999 | 2.7385 | 0.8785 | -6.2443 | -6.5887 | -2.5118 | -3.9457 | 3.4215 | -3.4296 | 0.5863 | 0.6299 | 0.9517 | 0.7013 | -130.8326 | -5.5162 | 1.2931 | -0.6537 | -7.7182 | -6.2161 | 0.4337 |  | -1.9995 | -2.9164 | 4.0022 | 3.3654 | 3.353 | 1.0335 | 10.64 | 14.0784 | 14.6734 | 10.9995 | -0.0003 | -0.0027 | 0.0012 | 0.0042 | 0.0003 | -0.0006 | 0.012 | -0.012 | -0.0051 | -360.1681 | 17.4931 | -360.5681 | 17.8032 | -360.885 | 18.1871 | -360.9527 | 17.5116 | -352.7829 | 18.7805 | -352.8414 | 16.834
11:48 | 1695 | 23.4451 | 195.4466 | 436.7652 | 442.9595 | -21.0126 | -47.1012 | 2.6859 | 0.8791 | -6.1924 | -6.4521 | -2.5012 | -4.0383 | 3.4493 | -3.4589 | 0.5868 | 0.6313 | 0.9488 | 0.6992 | -130.7527 | -5.5278 | 1.2703 | -0.5879 | -7.7266 | -6.2412 | 0.3884 |  | -2.0297 | -2.8633 | 4.0035 | 3.3635 | 3.3547 | 1.0328 | 10.6584 | 14.1435 | 14.7347 | 11.0287 | -0.0014 | -0.0027 | 0.0005 | 0.0038 | 0.0005 | -0.001 | 0.0111 | -0.0063 | 0.0089 | -360.1865 | 17.4418 | -360.4912 | 17.7683 | -360.8604 | 18.1728 | -360.9589 | 17.5219 | -352.7952 | 18.7477 | -352.7521 | 16.8032
11:48 | 1696 | 23.4923 | 195.4908 | 436.8881 | 442.9799 | -20.832 | -47.0148 | 2.8176 | 0.8694 | -6.1685 | -6.7156 | -2.4975 | -3.8548 | 3.4618 | -3.4678 | 0.5866 | 0.629 | 0.9497 | 0.7006 | -130.811 | -5.5597 | 1.2749 | -0.5967 | -7.6801 | -6.2518 | 0.4202 |  | -2.0258 | -2.8784 | 4.0027 | 3.3623 | 3.3538 | 1.0324 | 10.6653 | 14.1274 | 14.714 | 11.0236 | -0.0001 | -0.0032 | 0.0009 | 0.0045 | 0.001 | -0.0003 | 0.0086 | -0.0184 | 0.0027 | -360.2604 | 17.5075 | -360.5312 | 17.7724 | -360.8758 | 18.1769 | -360.962 | 17.5363 | -352.8506 | 18.799 | -352.789 | 16.8053
11:48 | 1697 | 23.4463 | 195.4521 | 436.705 | 442.9754 | -20.8228 | -47.0345 | 2.9236 | 0.9703 | -6.1495 | -6.4904 | -2.3894 | -3.9527 | 3.4672 | -3.5207 | 0.5873 | 0.6311 | 0.9488 | 0.7018 | -130.8056 | -5.5302 | 1.2775 | -0.6211 | -7.5736 | -6.1604 | 0.5156 |  | -2.035 | -2.8632 | 4.0027 | 3.3655 | 3.3548 | 1.0319 | 10.6631 | 14.1074 | 14.7207 | 10.9934 | -0.0003 | -0.0035 | 0.0006 | 0.0038 | 0.0004 | -0.0006 | -0.0084 | -0.002 | 0.0057 | -360.1896 | 17.4849 | -360.5404 | 17.8052 | -360.8881 | 18.144 | -360.9035 | 17.4993 | -352.7614 | 18.7764 | -352.8014 | 16.8217
11:48 | 1698 | 23.4275 | 195.4244 | 436.7676 | 443.0032 | -20.8817 | -47.196 | 2.7236 | 0.942 | -6.1697 | -6.5069 | -2.4188 | -3.9611 | 3.423 | -3.614 | 0.5876 | 0.6335 | 0.951 | 0.7 | -130.7881 | -5.5841 | 1.2279 | -0.7095 | -7.6654 | -6.1817 | 0.5099 |  | -2.0238 | -2.9417 | 4.0016 | 3.3644 | 3.3493 | 1.0324 | 10.6537 | 14.1332 | 14.7487 | 11.0641 | 0.0001 | -0.0026 | 0.0004 | 0.0035 | 0.0011 | -0.0004 | 0.0024 | -0.0066 | -0.028 | -360.1435 | 17.4644 | -360.5404 | 17.8093 | -360.9343 | 18.1953 | -360.9681 | 17.5096 | -352.746 | 18.7518 | -352.8198 | 16.8361
11:48 | 1699 | 23.4574 | 195.3934 | 436.6912 | 443.0141 | -20.8918 | -47.2634 | 2.8014 | 0.9224 | -6.1813 | -6.4622 | -2.4261 | -3.9714 | 3.4533 | -3.5442 | 0.5881 | 0.6325 | 0.9486 | 0.7014 | -130.7986 | -5.6061 | 1.2627 | -0.6437 | -7.5892 | -6.1871 | 0.5932 |  | -1.9936 | -2.9861 | 4.0019 | 3.3649 | 3.3528 | 1.0332 | 10.6367 | 14.1093 | 14.6845 | 11.0202 | -0.0005 | -0.0029 | 0.0005 | 0.0035 | 0 | -0.0008 | 0.0087 | 0.0048 | -0.0047 | -360.1681 | 17.4541 | -360.5066 | 17.7867 | -360.9127 | 18.1933 | -360.9404 | 17.5116 | -352.7614 | 18.7456 | -352.7921 | 16.8074
11:48 | 1700 | 23.4863 | 195.4627 | 436.7045 | 443.0342 | -20.9152 | -47.2477 | 2.7627 | 0.8964 | -6.2138 | -6.5838 | -2.4629 | -3.8877 | 3.4642 | -3.4819 | 0.5873 | 0.6304 | 0.9503 | 0.7001 | -130.77 | -5.5515 | 1.271 | -0.6388 | -7.5404 | -6.208 | 0.5144 |  | -1.906 | -2.7884 | 4.0019 | 3.3671 | 3.3512 | 1.0329 | 10.6307 | 14.0865 | 14.6703 | 11.0017 | -0.0001 | -0.003 | 0.0012 | 0.0036 | 0.0012 | -0.0006 | -0.0052 | -0.0043 | -0.0316 | -360.1835 | 17.4931 | -360.5219 | 17.7703 | -360.8543 | 18.1604 | -360.9527 | 17.5178 | -352.8106 | 18.7846 | -352.8106 | 16.8012
11:48 | 1701 | 23.6 | 195.4912 | 436.8557 | 443.094 | -20.9229 | -47.1785 | 2.7345 | 0.8803 | -6.1497 | -6.601 | -2.503 | -3.9057 | 3.4567 | -3.4055 | 0.5878 | 0.6293 | 0.9492 | 0.7005 | -130.703 | -5.5112 | 1.1639 | -0.5502 | -7.5329 | -6.265 | 0.5638 |  | -1.9332 | -2.8753 | 4.0017 | 3.3653 | 3.3544 | 1.0331 | 10.6538 | 14.0982 | 14.7003 | 11.036 | -0.0001 | -0.003 | 0.0008 | 0.0035 | 0.0004 | -0.0007 | 0.0078 | -0.0066 | -0.0215 | -360.1958 | 17.5157 | -360.6143 | 17.8011 | -360.9158 | 18.1666 | -360.8758 | 17.5034 | -352.8137 | 18.7969 | -352.866 | 16.8279
11:48 | 1702 | 23.6492 | 195.5062 | 436.8485 | 443.1653 | -20.9412 | -47.195 | 2.7586 | 1.016 | -6.1273 | -6.5175 | -2.4864 | -3.8493 | 3.5623 | -3.447 | 0.587 | 0.6305 | 0.9518 | 0.7007 | -130.7255 | -5.4584 | 1.1585 | -0.5766 | -7.5881 | -6.245 | 0.5524 |  | -2.0069 | -2.8199 | 4.0022 | 3.3651 | 3.3531 | 1.0325 | 10.6227 | 14.0898 | 14.7013 | 11.0057 | -0.0008 | -0.0036 | 0.0009 | 0.0038 | 0.0006 | -0.0008 | 0.0017 | 0.0033 | 0.0086 | -360.1527 | 17.4705 | -360.5343 | 17.7826 | -360.8912 | 18.1748 | -360.9035 | 17.4972 | -352.7675 | 18.76 | -352.7952 | 16.8217
11:48 | 1703 | 23.552 | 195.4554 | 436.7356 | 443.0627 | -20.9537 | -47.1844 | 2.9272 | 0.9332 | -6.1063 | -6.5028 | -2.5126 | -3.7862 | 3.4747 | -3.3854 | 0.5872 | 0.6331 | 0.9529 | 0.7006 | -130.7478 | -5.543 | 1.0938 | -0.5814 | -7.6448 | -6.2351 | 0.6089 |  | -1.9393 | -2.8307 | 4.0015 | 3.364 | 3.3556 | 1.0325 | 10.6583 | 14.1206 | 14.7484 | 11.0453 | -0.0002 | -0.0027 | 0.0005 | 0.0042 | 0.0005 | -0.0003 | 0.0161 | -0.0091 | -0.0086 | -360.2204 | 17.4644 | -360.5004 | 17.7785 | -360.9004 | 18.2097 | -361.002 | 17.528 | -352.8137 | 18.7559 | -352.7767 | 16.8032
11:48 | 1704 | 23.5783 | 195.3601 | 436.7498 | 443.0061 | -20.887 | -47.2681 | 2.8273 | 0.8536 | -6.1082 | -6.5354 | -2.4568 | -3.7986 | 3.4553 | -3.4231 | 0.587 | 0.6335 | 0.9545 | 0.7005 | -130.7466 | -5.5122 | 1.195 | -0.623 | -7.6781 | -6.1848 | 0.5385 |  | -1.9005 | -2.8377 | 4.0018 | 3.3673 | 3.3549 | 1.0322 | 10.6516 | 14.1073 | 14.6965 | 11.0111 | -0.0005 | -0.0033 | 0.0002 | 0.0036 | 0.0004 | -0.0007 | 0.0093 | 0.007 | 0.0023 | -360.1927 | 17.4664 | -360.5035 | 17.7436 | -360.8543 | 18.1645 | -360.9404 | 17.5198 | -352.8075 | 18.7661 | -352.8014 | 16.7786
11:48 | 1705 | 23.571 | 195.3781 | 436.7734 | 442.8831 | -20.9533 | -47.2502 | 2.7967 | 0.8898 | -6.0384 | -6.4247 | -2.4074 | -3.7669 | 3.5155 | -3.4491 | 0.5869 | 0.6334 | 0.9522 | 0.7025 | -130.7665 | -5.4823 | 1.2145 | -0.6033 | -7.6435 | -6.2846 | 0.5604 |  | -1.8896 | -2.8553 | 4.0015 | 3.3629 | 3.3535 | 1.0331 | 10.634 | 14.1251 | 14.7113 | 11.0446 | 0.0003 | -0.0032 | 0.0007 | 0.0037 | 0.0012 | 0 | 0.0006 | -0.0074 | -0.0185 | -360.1896 | 17.5034 | -360.5927 | 17.795 | -360.885 | 18.1789 | -360.9312 | 17.5055 | -352.7829 | 18.7908 | -352.8229 | 16.8135
11:48 | 1706 | 23.5354 | 195.3885 | 436.6855 | 442.9423 | -20.9745 | -47.3538 | 2.8214 | 0.9695 | -6.0334 | -6.5308 | -2.4628 | -3.8011 | 3.5285 | -3.3962 | 0.5871 | 0.6312 | 0.9502 | 0.7009 | -130.8561 | -5.5343 | 1.1186 | -0.6509 | -7.6511 | -6.2512 | 0.5342 |  | -1.9015 | -2.9013 | 4.0021 | 3.3664 | 3.3557 | 1.0328 | 10.6479 | 14.1274 | 14.7256 | 11.0525 | -0.0001 | -0.0032 | 0.0002 | 0.0037 | 0.0005 | -0.0004 | 0.015 | 0.0069 | -0.02 | -360.1188 | 17.4521 | -360.5189 | 17.7991 | -360.922 | 18.1769 | -360.8974 | 17.4767 | -352.7706 | 18.7518 | -352.7952 | 16.8402
11:48 | 1707 | 23.4973 | 195.3067 | 436.7728 | 442.9734 | -20.9945 | -47.2606 | 2.8279 | 0.8254 | -6.0687 | -6.4484 | -2.4575 | -3.7631 | 3.6005 | -3.3882 | 0.5881 | 0.6316 | 0.9482 | 0.7012 | -130.8284 | -5.5343 | 1.1358 | -0.5789 | -7.6127 | -6.1515 | 0.5198 |  | -1.9773 | -2.8886 | 4.0029 | 3.3646 | 3.3523 | 1.0341 | 10.6735 | 14.1063 | 14.6962 | 11.0154 | -0.0005 | -0.0027 | 0.001 | 0.0038 | 0.0004 | -0.001 | 0.0039 | -0.0075 | -0.0052 | -360.1711 | 17.4726 | -360.5404 | 17.797 | -360.9374 | 18.1994 | -360.9558 | 17.5096 | -352.7706 | 18.7579 | -352.7983 | 16.8258
11:48 | 1708 | 23.5375 | 195.4536 | 436.7809 | 443.0603 | -20.9835 | -47.2121 | 2.8282 | 0.7365 | -6.2621 | -6.4403 | -2.58 | -3.7661 | 3.4564 | -3.5262 | 0.5877 | 0.6308 | 0.9473 | 0.6999 | -130.8386 | -5.5046 | 1.0997 | -0.6232 | -7.6098 | -6.2636 | 0.5274 |  | -1.9186 | -2.8104 | 4.001 | 3.3618 | 3.351 | 1.0339 | 10.6341 | 14.1018 | 14.6639 | 10.9988 | 0.0002 | -0.0027 | 0.0013 | 0.0037 | 0.0004 | -0.0002 | 0.0045 | 0.0035 | -0.0065 | -360.1619 | 17.4644 | -360.4942 | 17.7559 | -360.8266 | 18.1728 | -360.9774 | 17.5178 | -352.7798 | 18.7703 | -352.7429 | 16.7909
11:48 | 1709 | 23.6391 | 195.3392 | 436.7778 | 443.0201 | -20.9774 | -47.112 | 2.7528 | 0.8959 | -6.1688 | -6.5746 | -2.4459 | -3.8186 | 3.4486 | -3.489 | 0.5877 | 0.6323 | 0.951 | 0.7023 | -130.8455 | -5.5342 | 1.1393 | -0.7365 | -7.6099 | -6.2513 | 0.5427 |  | -1.9369 | -2.7936 | 4.0021 | 3.3663 | 3.3554 | 1.0338 | 10.6308 | 14.0748 | 14.6808 | 11.0136 | -0.0002 | -0.0031 | 0.0006 | 0.0037 | 0.0005 | -0.0009 | 0.0152 | -0.0066 | -0.0153 | -360.245 | 17.5198 | -360.5804 | 17.7888 | -360.8912 | 18.1604 | -360.9189 | 17.5301 | -352.8198 | 18.8072 | -352.8567 | 16.8176
11:48 | 1710 | 23.57 | 195.3502 | 436.7896 | 443.0651 | -20.8548 | -47.0936 | 2.8331 | 0.9174 | -6.1873 | -6.4458 | -2.5163 | -3.8742 | 3.4291 | -3.5203 | 0.587 | 0.6323 | 0.9488 | 0.7029 | -130.8657 | -5.4968 | 1.0658 | -0.834 | -7.6041 | -6.2384 | 0.4565 |  | -1.9385 | -2.7824 | 4.0024 | 3.3638 | 3.3567 | 1.0349 | 10.6639 | 14.1093 | 14.71 | 11.0388 | 0.0003 | -0.0028 | 0.0013 | 0.0041 | 0.0005 | -0.0001 | 0.0019 | -0.0102 | 0.0023 | -360.1681 | 17.4747 | -360.5466 | 17.7785 | -360.8697 | 18.1481 | -360.882 | 17.4952 | -352.789 | 18.7723 | -352.8229 | 16.8135
11:48 | 1711 | 23.601 | 195.2988 | 436.8127 | 443.0475 | -20.9128 | -47.2002 | 2.7807 | 0.8856 | -6.1543 | -6.3321 | -2.4244 | -3.7768 | 3.5317 | -3.354 | 0.5885 | 0.6309 | 0.9505 | 0.7027 | -130.8843 | -5.5696 | 1.0172 | -0.7298 | -7.6408 | -6.1985 | 0.5187 |  | -1.9555 | -2.8811 | 4.001 | 3.3682 | 3.3517 | 1.0331 | 10.6364 | 14.0926 | 14.7014 | 11.0125 | -0.0001 | -0.0026 | 0.0004 | 0.0039 | 0.0009 | -0.0009 | 0.0088 | -0.0174 | -0.0038 | -360.1619 | 17.4767 | -360.5373 | 17.7991 | -360.9035 | 18.2097 | -360.962 | 17.5198 | -352.7952 | 18.7682 | -352.8014 | 16.834
11:48 | 1712 | 23.6268 | 195.3039 | 436.7535 | 443.0717 | -20.9675 | -47.2547 | 2.6921 | 0.9233 | -6.1444 | -6.4426 | -2.4386 | -3.8002 | 3.4518 | -3.4139 | 0.5882 | 0.6345 | 0.9534 | 0.7015 | -130.8991 | -5.5453 | 1.2695 | -0.628 | -7.6737 | -6.1668 | 0.5293 |  | -1.8895 | -2.8841 | 4.0026 | 3.3654 | 3.3517 | 1.0339 | 10.6423 | 14.1039 | 14.7166 | 11.019 | -0.0004 | -0.0025 | 0 | 0.0036 | 0.0007 | -0.0007 | -0.0084 | 0.0017 | -0.0243 | -360.1496 | 17.4418 | -360.4604 | 17.7601 | -360.8543 | 18.1953 | -360.9589 | 17.5137 | -352.7983 | 18.7436 | -352.7614 | 16.795
11:48 | 1713 | 23.583 | 195.3615 | 436.7118 | 443.0575 | -20.9576 | -47.1612 | 2.7751 | 0.9199 | -6.15 | -6.3809 | -2.4301 | -3.812 | 3.4682 | -3.493 | 0.5869 | 0.6334 | 0.9463 | 0.6991 | -130.8666 | -5.495 | 1.3168 | -0.5668 | -7.5756 | -6.1868 | 0.5724 |  | -1.876 | -2.8255 | 4.0019 | 3.3632 | 3.3492 | 1.0335 | 10.663 | 14.1251 | 14.7228 | 11.0388 | -0.0003 | -0.0029 | 0.0005 | 0.0041 | 0.0007 | -0.0002 | 0.0086 | -0.0034 | -0.0016 | -360.2081 | 17.4808 | -360.5373 | 17.7765 | -360.8543 | 18.1892 | -360.9897 | 17.5363 | -352.8229 | 18.7744 | -352.8167 | 16.8135
11:48 | 1714 | 23.6172 | 195.2674 | 436.7737 | 443.0191 | -20.9541 | -47.1542 | 2.7658 | 0.9183 | -6.1294 | -6.4632 | -2.3192 | -3.8074 | 3.5279 | -3.3792 | 0.5872 | 0.6313 | 0.9478 | 0.7014 | -130.8764 | -5.5029 | 1.1898 | -0.6293 | -7.6089 | -6.1848 | 0.5569 |  | -1.8365 | -2.77 | 4.0003 | 3.364 | 3.3515 | 1.034 | 10.6296 | 14.1373 | 14.6968 | 11.001 | -0.0002 | -0.0035 | -0.0002 | 0.0031 | 0.0002 | -0.0009 | 0.0048 | -0.0099 | -0.0159 | -360.1465 | 17.4788 | -360.5466 | 17.7765 | -360.8727 | 18.1543 | -360.9035 | 17.4849 | -352.7829 | 18.7682 | -352.7737 | 16.8176
11:48 | 1715 | 23.6155 | 195.2965 | 436.7961 | 442.9721 | -20.9514 | -47.0141 | 2.8953 | 0.8434 | -6.2019 | -6.4848 | -2.474 | -3.8026 | 3.5425 | -3.3781 | 0.5887 | 0.6333 | 0.9497 | 0.7017 | -130.85 | -5.5619 | 1.2719 | -0.6296 | -7.6414 | -6.2387 | 0.6305 |  | -1.959 | -2.9014 | 4.0015 | 3.3662 | 3.3531 | 1.0341 | 10.6389 | 14.083 | 14.6894 | 11.01 | 0.0003 | -0.0026 | 0.0007 | 0.0039 | 0.0006 | -0.0003 | 0.0098 | -0.0053 | -0.0219 | -360.1311 | 17.489 | -360.5866 | 17.8217 | -360.9251 | 18.183 | -360.9404 | 17.4972 | -352.7675 | 18.7805 | -352.829 | 16.8566
11:48 | 1716 | 23.5964 | 195.3272 | 436.893 | 443.0277 | -20.945 | -47.0448 | 2.8368 | 0.8819 | -6.1814 | -6.5749 | -2.5084 | -3.7243 | 3.5436 | -3.4009 | 0.5891 | 0.6328 | 0.9491 | 0.702 | -130.8112 | -5.5928 | 1.1584 | -0.6065 | -7.6072 | -6.2515 | 0.646 |  | -1.8996 | -2.8296 | 3.9993 | 3.3631 | 3.3513 | 1.0329 | 10.6458 | 14.0957 | 14.7081 | 11.0053 | -0.0005 | -0.0028 | 0.001 | 0.0037 | 0.0007 | -0.0008 | 0.0129 | -0.01 | -0.0119 | -360.1465 | 17.4685 | -360.525 | 17.7642 | -360.8727 | 18.1871 | -360.9097 | 17.4829 | -352.7521 | 18.7579 | -352.7644 | 16.8053
11:48 | 1717 | 23.6246 | 195.3174 | 436.7703 | 443.0754 | -20.9526 | -47.0473 | 2.8947 | 0.9155 | -6.129 | -6.5796 | -2.3809 | -3.6902 | 3.5806 | -3.2982 | 0.5876 | 0.6287 | 0.9505 | 0.7018 | -130.8407 | -5.4766 | 1.2519 | -0.6269 | -7.6526 | -6.1726 | 0.5748 |  | -1.8604 | -2.8385 | 4.0029 | 3.3657 | 3.3518 | 1.0338 | 10.6366 | 14.1037 | 14.6751 | 11.0078 | -0.0004 | -0.0028 | 0.0012 | 0.0038 | 0.0004 | -0.0002 | 0.0002 | -0.0037 | 0.0041 | -360.205 | 17.4685 | -360.5281 | 17.7826 | -360.8697 | 18.1912 | -360.9897 | 17.5383 | -352.8014 | 18.7703 | -352.8106 | 16.8176
11:48 | 1718 | 23.7151 | 195.3963 | 436.9542 | 443.0988 | -20.8857 | -47.0729 | 2.8941 | 0.9383 | -6.0728 | -6.5516 | -2.384 | -3.6751 | 3.5556 | -3.2818 | 0.5881 | 0.6313 | 0.9499 | 0.7034 | -130.7684 | -5.5084 | 1.257 | -0.5595 | -7.6434 | -6.1816 | 0.5321 |  | -1.8792 | -2.8234 | 4.0013 | 3.3641 | 3.3489 | 1.0329 | 10.6548 | 14.0997 | 14.698 | 11.0305 | 0.0003 | -0.003 | 0.0015 | 0.0043 | 0.0006 | -0.001 | -0.0061 | 0.0026 | -0.0024 | -360.1835 | 17.4788 | -360.5189 | 17.7539 | -360.8327 | 18.1543 | -360.9374 | 17.5198 | -352.8137 | 18.7682 | -352.7706 | 16.793
11:48 | 1719 | 23.8411 | 195.3657 | 436.9424 | 443.1642 | -20.8442 | -47.1524 | 2.8503 | 0.9591 | -6.0544 | -6.4159 | -2.4488 | -3.7382 | 3.5221 | -3.3468 | 0.5873 | 0.6298 | 0.9498 | 0.7022 | -130.7728 | -5.5664 | 1.2364 | -0.5467 | -7.5641 | -6.1322 | 0.5651 |  | -1.8549 | -2.7615 | 4.0028 | 3.367 | 3.3502 | 1.033 | 10.6699 | 14.1262 | 14.701 | 11.0399 | -0.0003 | -0.003 | 0.0006 | 0.0035 | 0.0003 | -0.0007 | 0.0058 | -0.0061 | -0.0088 | -360.2173 | 17.4829 | -360.5589 | 17.8052 | -360.922 | 18.181 | -360.9527 | 17.5239 | -352.789 | 18.7846 | -352.8229 | 16.8361
11:48 | 1720 | 23.6883 | 195.3245 | 436.9059 | 443.1178 | -20.8717 | -47.0571 | 2.8608 | 0.8814 | -6.1023 | -6.4829 | -2.4181 | -3.6917 | 3.6479 | -3.324 | 0.5869 | 0.6305 | 0.9525 | 0.7038 | -130.7845 | -5.5155 | 1.2279 | -0.6388 | -7.5275 | -6.1131 | 0.6011 |  | -1.9238 | -2.8601 | 4.003 | 3.3648 | 3.3519 | 1.0342 | 10.6284 | 14.119 | 14.7034 | 11.028 | -0.0002 | -0.0028 | 0.0003 | 0.0036 | 0.0011 | -0.0006 | -0.0026 | -0.0074 | 0.0014 | -360.1188 | 17.4541 | -360.5466 | 17.7806 | -360.8604 | 18.1871 | -360.9158 | 17.489 | -352.7337 | 18.762 | -352.8106 | 16.8156
11:48 | 1721 | 23.7098 | 195.3509 | 436.8909 | 443.1068 | -20.85 | -46.9542 | 2.9222 | 0.9632 | -6.205 | -6.5079 | -2.4351 | -3.8408 | 3.5575 | -3.3113 | 0.5876 | 0.6328 | 0.9517 | 0.702 | -130.8316 | -5.6466 | 1.1842 | -0.6378 | -7.6074 | -6.1033 | 0.5773 |  | -1.9406 | -2.8435 | 4.0013 | 3.368 | 3.3531 | 1.0331 | 10.6583 | 14.132 | 14.7068 | 11.011 | -0.0006 | -0.0028 | 0.0008 | 0.0041 | 0.001 | -0.0003 | 0.0018 | -0.0084 | 0.0111 | -360.1865 | 17.4767 | -360.5281 | 17.797 | -360.9312 | 18.1953 | -360.9897 | 17.528 | -352.7921 | 18.7682 | -352.8137 | 16.8217
11:48 | 1722 | 23.6981 | 195.3276 | 436.9015 | 443.1603 | -20.8062 | -46.9981 | 2.915 | 0.9225 | -6.1241 | -6.5357 | -2.3225 | -3.7583 | 3.5818 | -3.3418 | 0.5876 | 0.6272 | 0.9513 | 0.7009 | -130.8405 | -5.4942 | 1.2996 | -0.6485 | -7.5694 | -6.1272 | 0.6102 |  | -1.926 | -2.8325 | 4.0019 | 3.3689 | 3.35 | 1.0338 | 10.6642 | 14.1203 | 14.7116 | 11.0287 | 0.0002 | -0.0027 | 0.0005 | 0.0036 | 0.0005 | -0.0008 | 0.0108 | -0.0088 | 0.0012 | -360.1773 | 17.4562 | -360.5189 | 17.7662 | -360.8297 | 18.1502 | -360.9404 | 17.5075 | -352.7521 | 18.762 | -352.7767 | 16.8135
11:48 | 1723 | 23.7017 | 195.2425 | 436.8277 | 443.1131 | -20.8294 | -46.8919 | 3.0188 | 0.8995 | -6.124 | -6.4984 | -2.1792 | -3.686 | 3.6047 | -3.2893 | 0.5871 | 0.6322 | 0.9526 | 0.701 | -130.8132 | -5.4858 | 1.2666 | -0.5183 | -7.55 | -6.1562 | 0.6068 |  | -1.8839 | -2.7947 | 4.0033 | 3.3697 | 3.3549 | 1.0331 | 10.648 | 14.081 | 14.6898 | 11.0182 | -0.0002 | -0.0035 | 0.0007 | 0.0037 | 0.0011 | -0.0004 | -0.0017 | -0.0105 | 0.001 | -360.2111 | 17.5034 | -360.5835 | 17.7991 | -360.9035 | 18.1871 | -360.9435 | 17.5219 | -352.8075 | 18.7867 | -352.8506 | 16.8238
11:48 | 1724 | 23.7628 | 195.3761 | 436.8457 | 443.1658 | -20.8774 | -47.0161 | 2.876 | 0.8675 | -6.1677 | -6.4077 | -2.1297 | -3.6685 | 3.5359 | -3.2706 | 0.5871 | 0.6307 | 0.9499 | 0.7012 | -130.8006 | -5.5262 | 1.167 | -0.5907 | -7.5709 | -6.0724 | 0.6085 |  | -1.9415 | -2.8501 | 4.0023 | 3.3669 | 3.3532 | 1.0335 | 10.6493 | 14.0702 | 14.6764 | 11.0089 | -0.0003 | -0.003 | 0.0009 | 0.0037 | 0.0006 | -0.0004 | 0.0155 | 0.0013 | 0.0025 | -360.1342 | 17.4685 | -360.5343 | 17.797 | -360.8358 | 18.1604 | -360.9251 | 17.4972 | -352.7767 | 18.7579 | -352.8014 | 16.8094
11:48 | 1725 | 23.8117 | 195.3453 | 436.9561 | 443.2295 | -20.7115 | -46.9436 | 2.9629 | 0.8629 | -6.0935 | -6.4826 | -2.1212 | -3.7036 | 3.6253 | -3.2589 | 0.5864 | 0.6321 | 0.95 | 0.702 | -130.8431 | -5.53 | 1.1685 | -0.6334 | -7.5357 | -6.1623 | 0.6161 |  | -2.0527 | -2.845 | 4.0013 | 3.3655 | 3.3527 | 1.0332 | 10.6308 | 14.0864 | 14.6924 | 11.0309 | -0.0008 | -0.0033 | 0.0003 | 0.0032 | 0.0009 | -0.0007 | 0.0051 | -0.0114 | -0.0128 | -360.1865 | 17.4911 | -360.5435 | 17.8011 | -360.8943 | 18.1974 | -360.9681 | 17.5198 | -352.7952 | 18.7785 | -352.8198 | 16.8156
11:48 | 1726 | 23.8476 | 195.446 | 436.9742 | 443.1527 | -20.7683 | -46.8674 | 2.9218 | 0.8982 | -6.1205 | -6.4793 | -2.204 | -3.6815 | 3.5623 | -3.301 | 0.587 | 0.6302 | 0.949 | 0.7012 | -130.8371 | -5.5407 | 1.2114 | -0.6356 | -7.5949 | -6.2582 | 0.6316 |  | -1.9628 | -2.8046 | 4.0009 | 3.3664 | 3.3539 | 1.0332 | 10.6317 | 14.1169 | 14.6854 | 11.0078 | -0.0002 | -0.003 | 0.001 | 0.0041 | 0.0009 | 0.0003 | 0.0082 | -0.005 | -0.0059 | -360.1865 | 17.4705 | -360.5035 | 17.7929 | -360.882 | 18.1625 | -360.9251 | 17.5096 | -352.7737 | 18.7579 | -352.7706 | 16.8135
11:48 | 1727 | 23.7626 | 195.4054 | 436.9266 | 443.073 | -20.9853 | -47.0692 | 2.89 | 1.0171 | -6.0097 | -6.4241 | -2.0923 | -3.7357 | 3.6528 | -3.2841 | 0.5881 | 0.6307 | 0.9538 | 0.7019 | -130.8531 | -5.5278 | 1.1201 | -0.5162 | -7.6429 | -6.1833 | 0.5972 |  | -2.0049 | -2.7912 | 4.0009 | 3.3631 | 3.3496 | 1.0331 | 10.6734 | 14.1181 | 14.6983 | 11.0377 | 0.0002 | -0.0028 | 0.0006 | 0.0036 | 0.0009 | -0.0008 | 0.0066 | -0.0069 | -0.0037 | -360.1958 | 17.4911 | -360.5589 | 17.8134 | -360.8912 | 18.183 | -360.9558 | 17.5178 | -352.786 | 18.7805 | -352.826 | 16.8176
11:49 | 1728 | 23.8516 | 195.417 | 436.9107 | 443.1345 | -20.8896 | -47.0797 | 2.9255 | 0.986 | -6.0763 | -6.3951 | -2.1431 | -3.637 | 3.6374 | -3.3035 | 0.5881 | 0.6306 | 0.9528 | 0.7001 | -130.7727 | -5.4823 | 1.0439 | -0.5277 | -7.595 | -6.2004 | 0.5104 |  | -1.9765 | -2.8291 | 4.0026 | 3.3641 | 3.352 | 1.0352 | 10.6723 | 14.1285 | 14.6969 | 11.0136 | -0.0004 | -0.0032 | 0.0002 | 0.0034 | 0.0008 | 0.0001 | 0.0055 | -0.0081 | -0.0157 | -360.1496 | 17.4726 | -360.5219 | 17.7929 | -360.8635 | 18.181 | -360.9066 | 17.4931 | -352.7767 | 18.7703 | -352.7952 | 16.8135
11:49 | 1729 | 23.7915 | 195.4149 | 436.7556 | 443.1003 | -20.7487 | -46.8522 | 3.0405 | 0.9737 | -6.0826 | -6.5065 | -2.2474 | -3.7354 | 3.5921 | -3.2746 | 0.5864 | 0.6298 | 0.9526 | 0.7016 | -130.6688 | -5.6084 | 1.0242 | -0.6272 | -7.6064 | -6.1507 | 0.57 |  | -1.8636 | -2.7241 | 4.004 | 3.367 | 3.3514 | 1.0334 | 10.6849 | 14.1242 | 14.7467 | 11.037 | -0.0002 | -0.0023 | 0.0006 | 0.004 | 0.0006 | -0.0009 | -0.0023 | -0.0214 | -0.016 | -360.1865 | 17.4747 | -360.5558 | 17.8258 | -360.9189 | 18.1974 | -360.9897 | 17.5404 | -352.7798 | 18.7682 | -352.8075 | 16.8279
11:49 | 1730 | 23.7695 | 195.3921 | 436.8112 | 443.0691 | -20.884 | -46.828 | 2.9645 | 0.9057 | -6.0085 | -6.3649 | -2.2229 | -3.7344 | 3.5483 | -3.2633 | 0.5888 | 0.6306 | 0.9539 | 0.7022 | -130.7269 | -5.6214 | 1.0508 | -0.4208 | -7.5567 | -6.0451 | 0.6313 |  | -1.9431 | -2.8115 | 4.0029 | 3.3662 | 3.3573 | 1.0363 | 10.6653 | 14.1331 | 14.7187 | 11.0471 | -0.0002 | -0.0028 | 0.0009 | 0.004 | 0.0007 | -0.0003 | 0.0105 | -0.0168 | -0.0122 | -360.1588 | 17.4726 | -360.5127 | 17.7909 | -360.8543 | 18.1687 | -360.9374 | 17.5096 | -352.7644 | 18.7538 | -352.7921 | 16.8115
11:49 | 1731 | 23.7153 | 195.406 | 436.7324 | 443.1003 | -20.8361 | -46.824 | 3.0034 | 0.9756 | -6.0122 | -6.3913 | -2.2367 | -3.71 | 3.6062 | -3.2201 | 0.5891 | 0.6305 | 0.9509 | 0.7038 | -130.7682 | -5.5739 | 1.0471 | -0.4048 | -7.568 | -6.1444 | 0.6794 |  | -1.9683 | -2.9127 | 4.0029 | 3.3638 | 3.3522 | 1.0349 | 10.6458 | 14.1073 | 14.6907 | 11.0226 | -0.0001 | -0.0031 | 0.0005 | 0.0039 | 0.0004 | -0.0007 | 0.0012 | -0.0181 | -0.0201 | -360.1927 | 17.5055 | -360.5712 | 17.8032 | -360.885 | 18.1851 | -360.9589 | 17.5239 | -352.829 | 18.7928 | -352.7952 | 16.8115
11:49 | 1732 | 23.8674 | 195.447 | 436.9035 | 443.0825 | -20.877 | -46.9614 | 2.9414 | 1.0293 | -5.9148 | -6.2688 | -2.3025 | -3.6667 | 3.6121 | -3.281 | 0.589 | 0.629 | 0.9526 | 0.7023 | -130.7273 | -5.5545 | 1.0757 | -0.3755 | -7.5463 | -6.0787 | 0.67 |  | -1.9474 | -2.8449 | 4.0022 | 3.3675 | 3.3536 | 1.0335 | 10.6168 | 14.0785 | 14.6918 | 11.028 | 0.0001 | -0.0029 | 0.001 | 0.0042 | 0.0004 | -0.001 | 0.014 | -0.0175 | 0.0025 | -360.1527 | 17.4829 | -360.5219 | 17.7847 | -360.8574 | 18.1502 | -360.8635 | 17.4931 | -352.7737 | 18.7826 | -352.8106 | 16.8032
11:49 | 1733 | 23.9421 | 195.3683 | 436.8621 | 443.0918 | -20.879 | -46.9087 | 2.8927 | 1.0083 | -5.9119 | -6.3856 | -2.3119 | -3.6139 | 3.6803 | -3.1927 | 0.5888 | 0.6299 | 0.9512 | 0.7015 | -130.6925 | -5.4866 | 1.0737 | -0.3563 | -7.4995 | -6.1154 | 0.6949 |  | -1.9062 | -2.887 | 4.0015 | 3.3662 | 3.3529 | 1.034 | 10.625 | 14.0922 | 14.7156 | 11.0483 | -0.0003 | -0.0028 | 0.0005 | 0.0032 | 0.0006 | -0.0006 | -0.0014 | -0.0085 | -0.0335 | -360.2235 | 17.4993 | -360.5743 | 17.8319 | -360.8881 | 18.1645 | -360.8974 | 17.5116 | -352.789 | 18.7908 | -352.8414 | 16.834
11:49 | 1734 | 23.8754 | 195.3527 | 436.8819 | 443.068 | -20.9089 | -47.0148 | 3.024 | 0.9795 | -5.9584 | -6.3716 | -2.3147 | -3.63 | 3.7079 | -3.206 | 0.5866 | 0.6325 | 0.9504 | 0.7028 | -130.7999 | -5.552 | 0.9918 | -0.3226 | -7.4197 | -6.039 | 0.7423 |  | -1.9449 | -2.8791 | 4.003 | 3.3664 | 3.3545 | 1.0353 | 10.6214 | 14.0947 | 14.702 | 10.9865 | 0 | -0.0027 | 0.0006 | 0.0033 | 0.0009 | -0.001 | 0.013 | -0.0006 | -0.0133 | -360.1404 | 17.4644 | -360.5158 | 17.8073 | -360.8789 | 18.1687 | -360.9251 | 17.4952 | -352.746 | 18.762 | -352.7921 | 16.8115
11:49 | 1735 | 23.8816 | 195.3489 | 436.8489 | 443.089 | -20.9203 | -46.9708 | 3.003 | 1.0412 | -5.9767 | -6.3566 | -2.2803 | -3.6651 | 3.6718 | -3.1771 | 0.5879 | 0.6297 | 0.952 | 0.7014 | -130.7653 | -5.5221 | 1.0282 | -0.5319 | -7.4363 | -6.0177 | 0.7328 |  | -1.911 | -2.8206 | 4.0028 | 3.3659 | 3.3546 | 1.0363 | 10.6296 | 14.091 | 14.691 | 10.9952 | -0.0001 | -0.003 | 0.001 | 0.0034 | 0.0007 | -0.0005 | 0.0114 | -0.0022 | -0.0134 | -360.1896 | 17.4705 | -360.4912 | 17.7867 | -360.8912 | 18.181 | -360.9651 | 17.5404 | -352.789 | 18.762 | -352.7706 | 16.8074
11:49 | 1736 | 23.864 | 195.3605 | 436.8188 | 443.0718 | -20.8969 | -46.8635 | 3.0454 | 1.0416 | -5.9299 | -6.3049 | -2.3112 | -3.6683 | 3.6651 | -3.1453 | 0.5882 | 0.6321 | 0.951 | 0.7022 | -130.724 | -5.5961 | 1.0686 | -0.6046 | -7.5302 | -6.0925 | 0.6811 |  | -1.8787 | -2.8096 | 4.0026 | 3.3625 | 3.3539 | 1.0341 | 10.6526 | 14.1145 | 14.7289 | 11.0229 | 0.0003 | -0.0027 | 0.0001 | 0.0031 | 0.0007 | -0.0008 | 0.0142 | 0.0046 | -0.0025 | -360.2081 | 17.4726 | -360.5219 | 17.7765 | -360.8235 | 18.1666 | -360.9712 | 17.5301 | -352.7921 | 18.762 | -352.7737 | 16.7827
11:49 | 1737 | 23.7963 | 195.3219 | 436.8223 | 443.0504 | -20.7905 | -46.7439 | 3.1624 | 1.0606 | -5.8748 | -6.2584 | -2.264 | -3.636 | 3.5581 | -3.198 | 0.588 | 0.6311 | 0.9522 | 0.7017 | -130.6995 | -5.637 | 1.012 | -0.7009 | -7.4616 | -6.1264 | 0.5852 |  | -1.9187 | -2.7588 | 4.0032 | 3.3667 | 3.359 | 1.0342 | 10.6411 | 14.1144 | 14.7163 | 11.0464 | -0.0002 | -0.0027 | 0.0008 | 0.0041 | 0.0003 | -0.0004 | 0.0274 | -0.0203 | -0.0179 | -360.2111 | 17.4972 | -360.5404 | 17.8114 | -360.8758 | 18.1502 | -360.9127 | 17.5157 | -352.7952 | 18.7805 | -352.826 | 16.8238
11:49 | 1738 | 23.8569 | 195.4498 | 436.8878 | 443.0236 | -20.7292 | -46.6602 | 3.201 | 1.0246 | -5.9486 | -6.2672 | -2.337 | -3.6598 | 3.6065 | -3.2044 | 0.589 | 0.6303 | 0.9534 | 0.7029 | -130.7458 | -5.5191 | 1.0346 | -0.6456 | -7.4428 | -6.1317 | 0.6635 |  | -1.856 | -2.8494 | 4.0005 | 3.3689 | 3.3583 | 1.034 | 10.6619 | 14.1064 | 14.6973 | 11.0208 | -0.0005 | -0.0026 | 0.0007 | 0.0037 | 0.001 | -0.0005 | 0.0045 | -0.0251 | -0.0092 | -360.1865 | 17.4726 | -360.5466 | 17.8217 | -360.9374 | 18.1666 | -360.9066 | 17.4993 | -352.7306 | 18.7579 | -352.8106 | 16.834
11:49 | 1739 | 23.8859 | 195.6224 | 436.8798 | 443.0691 | -20.7472 | -46.6762 | 3.1116 | 1.0665 | -5.9874 | -6.2669 | -2.2708 | -3.6871 | 3.6279 | -3.2218 | 0.5874 | 0.6287 | 0.9566 | 0.7014 | -130.7489 | -5.5115 | 1.0437 | -0.6699 | -7.5245 | -6.1519 | 0.6178 |  | -1.8899 | -2.8278 | 4.0014 | 3.3634 | 3.3528 | 1.0334 | 10.6307 | 14.1329 | 14.6945 | 11.0302 | -0.0001 | -0.0029 | 0.0009 | 0.0041 | 0.0004 | -0.0004 | 0.0021 | 0.0052 | -0.0157 | -360.1435 | 17.4664 | -360.5343 | 17.8155 | -360.9004 | 18.1748 | -360.9251 | 17.4993 | -352.7213 | 18.76 | -352.8014 | 16.8217
11:49 | 1740 | 23.8449 | 195.5057 | 436.774 | 443.0266 | -20.7671 | -46.7174 | 3.2595 | 1.0368 | -6.0884 | -6.2086 | -2.2864 | -3.6911 | 3.6484 | -3.0962 | 0.5883 | 0.6283 | 0.9521 | 0.702 | -130.6902 | -5.4864 | 1.0466 | -0.6223 | -7.5453 | -6.1731 | 0.554 |  | -1.9469 | -2.9002 | 4.0019 | 3.3644 | 3.3557 | 1.0347 | 10.6469 | 14.1258 | 14.721 | 11.0179 | 0.0001 | -0.0034 | 0.0005 | 0.0034 | 0.0006 | -0.0004 | 0.0289 | -0.0044 | 0.001 | -360.1988 | 17.4849 | -360.5312 | 17.8011 | -360.8697 | 18.1707 | -360.9804 | 17.5424 | -352.8198 | 18.7703 | -352.7644 | 16.7971
11:49 | 1741 | 23.8554 | 195.6205 | 436.772 | 443.2083 | -20.6944 | -46.8053 | 3.2188 | 1.0185 | -6.1225 | -6.2468 | -2.2082 | -3.7122 | 3.675 | -3.1808 | 0.5879 | 0.6312 | 0.9555 | 0.7022 | -130.681 | -5.4727 | 1.0753 | -0.5869 | -7.5755 | -6.1431 | 0.5736 |  | -1.9016 | -2.9055 | 4.0019 | 3.3646 | 3.3526 | 1.0353 | 10.6514 | 14.1135 | 14.717 | 11.0446 | -0.0001 | -0.0031 | 0.0008 | 0.0031 | 0.0009 | -0.0006 | -0.0031 | 0.001 | -0.0107 | -360.2388 | 17.4952 | -360.5281 | 17.7847 | -360.802 | 18.1337 | -360.9097 | 17.5321 | -352.8106 | 18.7867 | -352.7737 | 16.7971
11:49 | 1742 | 23.9039 | 195.6299 | 436.8623 | 443.3018 | -20.6669 | -46.7421 | 3.2614 | 0.9761 | -6.2181 | -6.1985 | -2.177 | -3.7483 | 3.6396 | -3.1737 | 0.5864 | 0.6286 | 0.9523 | 0.7013 | -130.7216 | -5.4987 | 1.0577 | -0.5606 | -7.565 | -6.1932 | 0.5806 |  | -1.938 | -2.9611 | 4.0008 | 3.3649 | 3.3549 | 1.0338 | 10.6227 | 14.1129 | 14.7013 | 11.0346 | -0.0007 | -0.003 | 0.0003 | 0.0034 | 0.0002 | -0.001 | 0.0015 | -0.0084 | -0.019 | -360.1896 | 17.5075 | -360.5835 | 17.8134 | -360.9035 | 18.1543 | -360.9189 | 17.5363 | -352.826 | 18.799 | -352.8198 | 16.8197
11:49 | 1743 | 23.9075 | 195.5415 | 436.8196 | 443.1699 | -20.676 | -46.7692 | 3.2537 | 0.9707 | -6.161 | -6.4118 | -2.2404 | -3.7844 | 3.6499 | -3.2943 | 0.5891 | 0.6314 | 0.9533 | 0.7019 | -130.7591 | -5.6097 | 1.0657 | -0.7063 | -7.5527 | -6.1476 | 0.5305 |  | -1.8342 | -2.8529 | 4.0011 | 3.3615 | 3.3557 | 1.0344 | 10.6527 | 14.1144 | 14.7337 | 10.9944 | -0.0003 | -0.0026 | 0.0007 | 0.0036 | 0.0009 | -0.0009 | 0.0231 | -0.0056 | 0.0131 | -360.1311 | 17.4541 | -360.4819 | 17.7909 | -360.8943 | 18.1851 | -360.9466 | 17.5075 | -352.7337 | 18.7395 | -352.7614 | 16.8197
11:49 | 1744 | 23.9318 | 195.5815 | 436.841 | 443.1894 | -20.7435 | -46.6884 | 3.3049 | 1.0304 | -6.0965 | -6.3017 | -2.1945 | -3.7569 | 3.688 | -3.1782 | 0.5895 | 0.6326 | 0.9529 | 0.7036 | -130.7825 | -5.4737 | 1.1033 | -0.6391 | -7.5019 | -6.1063 | 0.5722 |  | -1.802 | -2.8281 | 4.002 | 3.3645 | 3.3487 | 1.0337 | 10.6549 | 14.1168 | 14.6901 | 11.0544 | 0.0001 | -0.0031 | 0.0007 | 0.0037 | 0.0008 | -0.0004 | 0.0022 | -0.0015 | -0.0089 | -360.1865 | 17.4582 | -360.5096 | 17.8011 | -360.9066 | 18.1953 | -360.9927 | 17.5486 | -352.7952 | 18.7497 | -352.7829 | 16.8197
11:49 | 1745 | 24.0097 | 195.5905 | 436.9203 | 443.2366 | -20.7174 | -46.7711 | 3.1748 | 1.06 | -6.0569 | -6.1728 | -2.1715 | -3.669 | 3.6859 | -3.24 | 0.5886 | 0.6317 | 0.9545 | 0.7024 | -130.7887 | -5.5449 | 1.1167 | -0.587 | -7.5123 | -6.0213 | 0.6422 |  | -1.8559 | -2.85 | 4.001 | 3.3638 | 3.3488 | 1.0338 | 10.6561 | 14.1295 | 14.7378 | 11.0092 | -0.0002 | -0.0034 | 0.0011 | 0.0042 | 0.0009 | -0.0007 | 0.0174 | -0.0112 | -0.0154 | -360.1681 | 17.4808 | -360.5373 | 17.7806 | -360.8604 | 18.1584 | -360.922 | 17.5239 | -352.7644 | 18.7682 | -352.8014 | 16.8012
11:49 | 1746 | 24.0197 | 195.4665 | 436.8745 | 443.2577 | -20.7489 | -46.8577 | 3.3001 | 1.079 | -6.1041 | -6.2689 | -2.1912 | -3.6608 | 3.6639 | -3.1042 | 0.5886 | 0.6336 | 0.954 | 0.7027 | -130.8025 | -5.4518 | 1.1138 | -0.479 | -7.5115 | -5.9148 | 0.6646 |  | -1.8026 | -2.6876 | 4.0023 | 3.3661 | 3.3567 | 1.0346 | 10.6744 | 14.1427 | 14.7307 | 11.0438 | -0.0001 | -0.0024 | 0.0008 | 0.0042 | 0.0009 | 0 | 0.0121 | 0.0063 | -0.0177 | -360.1896 | 17.4952 | -360.5896 | 17.8073 | -360.9158 | 18.1522 | -360.8789 | 17.5137 | -352.7983 | 18.7846 | -352.8352 | 16.8361
11:49 | 1747 | 24.0112 | 195.5632 | 436.9104 | 443.2357 | -20.7291 | -46.9448 | 3.2816 | 1.0797 | -6.1047 | -6.2545 | -2.2339 | -3.6945 | 3.7194 | -3.1499 | 0.5876 | 0.6337 | 0.9546 | 0.7019 | -130.8007 | -5.4229 | 1.0889 | -0.4195 | -7.5017 | -6.0186 | 0.6275 |  | -1.7891 | -2.7642 | 4.0008 | 3.3646 | 3.3525 | 1.0349 | 10.6573 | 14.1479 | 14.7149 | 11.0511 | -0.0011 | -0.0033 | 0.0007 | 0.0038 | 0.0005 | -0.0007 | 0.0157 | 0.0041 | -0.0076 | -360.2173 | 17.4931 | -360.5773 | 17.8217 | -360.9004 | 18.1502 | -360.9312 | 17.528 | -352.746 | 18.7682 | -352.8352 | 16.8197
11:49 | 1748 | 23.97 | 195.5499 | 436.8663 | 443.2016 | -20.7154 | -46.8665 | 3.2439 | 1.2308 | -6.0365 | -6.1523 | -2.1558 | -3.6644 | 3.666 | -3.2495 | 0.5884 | 0.6337 | 0.9531 | 0.7014 | -130.7333 | -5.3853 | 1.1118 | -0.566 | -7.4201 | -5.9937 | 0.5474 |  | -1.8363 | -2.828 | 4.0027 | 3.3635 | 3.3525 | 1.0357 | 10.6527 | 14.1143 | 14.6979 | 11.0064 | -0.0002 | -0.0031 | 0.0006 | 0.0036 | 0.0005 | -0.0003 | 0.018 | -0.0053 | 0.0081 | -360.2173 | 17.4582 | -360.4789 | 17.7826 | -360.882 | 18.1666 | -360.9281 | 17.5321 | -352.7552 | 18.7436 | -352.7737 | 16.7991
11:49 | 1749 | 23.9334 | 195.5115 | 436.9835 | 443.3035 | -20.7976 | -46.9795 | 3.1534 | 1.1744 | -6.0116 | -6.1962 | -2.2116 | -3.7666 | 3.646 | -3.1632 | 0.5888 | 0.6324 | 0.9549 | 0.7001 | -130.8186 | -5.4461 | 1.0669 | -0.4227 | -7.3549 | -5.9039 | 0.6696 |  | -1.8664 | -2.852 | 4.0008 | 3.3638 | 3.3496 | 1.033 | 10.6376 | 14.1109 | 14.7064 | 11.0259 | 0.0003 | -0.0031 | 0.0005 | 0.0033 | 0.0003 | -0.0009 | 0.0096 | -0.009 | -0.0085 | -360.1958 | 17.4808 | -360.5281 | 17.7888 | -360.8543 | 18.1789 | -360.9866 | 17.5547 | -352.8044 | 18.7661 | -352.7921 | 16.793
11:49 | 1750 | 23.8873 | 195.5013 | 436.8141 | 443.2334 | -20.7182 | -46.8898 | 3.1412 | 1.1465 | -5.9747 | -6.2876 | -2.2164 | -3.7789 | 3.6596 | -3.192 | 0.5884 | 0.6322 | 0.9553 | 0.7022 | -130.8203 | -5.3481 | 1.0581 | -0.4318 | -7.4116 | -5.9331 | 0.7616 |  | -1.8853 | -2.9145 | 4.0009 | 3.3631 | 3.3509 | 1.0347 | 10.6273 | 14.1119 | 14.6952 | 10.9984 | -0.0004 | -0.003 | 0.0009 | 0.0035 | 0.0005 | -0.0009 | 0.013 | -0.0134 | -0.0136 | -360.1927 | 17.4829 | -360.5127 | 17.7867 | -360.8697 | 18.1625 | -360.9158 | 17.5096 | -352.7675 | 18.7682 | -352.7983 | 16.7827
11:49 | 1751 | 23.966 | 195.585 | 436.9015 | 443.2456 | -20.8564 | -46.9661 | 3.0126 | 1.0802 | -5.893 | -6.2886 | -2.1848 | -3.7169 | 3.6588 | -3.0892 | 0.5886 | 0.6296 | 0.9572 | 0.7002 | -130.8362 | -5.4334 | 0.9569 | -0.4072 | -7.3636 | -5.9392 | 0.6925 |  | -1.8796 | -2.793 | 4.0016 | 3.3642 | 3.3486 | 1.0356 | 10.6019 | 14.1037 | 14.6288 | 10.9847 | -0.0002 | -0.0025 | 0.0008 | 0.0038 | 0.0005 | -0.0003 | 0.0184 | -0.0087 | -0.0017 | -360.1711 | 17.4767 | -360.5527 | 17.8299 | -360.9158 | 18.1707 | -360.9466 | 17.5342 | -352.7552 | 18.76 | -352.826 | 16.8176
11:49 | 1752 | 23.9984 | 195.6165 | 436.959 | 443.3541 | -20.9087 | -47.1018 | 2.9574 | 1.1433 | -5.917 | -6.2536 | -2.1845 | -3.7459 | 3.6054 | -3.0802 | 0.5874 | 0.6314 | 0.9513 | 0.7008 | -130.7675 | -5.3503 | 1.0377 | -0.5638 | -7.4132 | -5.9206 | 0.701 |  | -1.8908 | -2.8239 | 4.0032 | 3.3674 | 3.356 | 1.0362 | 10.6538 | 14.1098 | 14.6772 | 11.0244 | -0.0002 | -0.0031 | 0.0004 | 0.0036 | 0.0009 | -0.0005 | 0.006 | -0.0146 | -0.0189 | -360.1773 | 17.4829 | -360.5404 | 17.797 | -360.8727 | 18.1687 | -360.9312 | 17.526 | -352.7706 | 18.7703 | -352.8014 | 16.7909
11:49 | 1753 | 23.9635 | 195.5935 | 437.0157 | 443.2591 | -20.8681 | -46.9542 | 2.9902 | 1.0333 | -6.0249 | -6.1782 | -2.2309 | -3.6892 | 3.7465 | -3.0851 | 0.588 | 0.6298 | 0.956 | 0.7016 | -130.7883 | -5.3305 | 1.0812 | -0.6473 | -7.3478 | -6.0417 | 0.6545 |  | -1.7748 | -2.846 | 4.0016 | 3.366 | 3.3508 | 1.0322 | 10.6618 | 14.1297 | 14.7099 | 11.0204 | 0.0002 | -0.0027 | 0.0006 | 0.0042 | 0.0005 | -0.0002 | 0.0034 | -0.0204 | -0.0185 | -360.165 | 17.4644 | -360.5189 | 17.7847 | -360.8481 | 18.1522 | -360.9066 | 17.5219 | -352.7675 | 18.7518 | -352.7952 | 16.7889
11:49 | 1754 | 24.0665 | 195.533 | 436.8748 | 443.3168 | -20.7947 | -46.8925 | 3.0107 | 1.1423 | -5.9238 | -6.1679 | -2.1598 | -3.6541 | 3.7393 | -3.1074 | 0.5868 | 0.6312 | 0.9542 | 0.701 | -130.7267 | -5.3732 | 1.0866 | -0.4954 | -7.2915 | -5.9143 | 0.7195 |  | -1.76 | -2.7783 | 4.0023 | 3.3684 | 3.3509 | 1.0345 | 10.6607 | 14.1285 | 14.7027 | 11.0309 | -0.0001 | -0.0029 | 0.0004 | 0.0039 | 0.0006 | -0.0007 | 0.0166 | -0.0006 | 0.0185 | -360.2081 | 17.489 | -360.5712 | 17.8114 | -360.8327 | 18.1645 | -360.9127 | 17.5301 | -352.786 | 18.7887 | -352.8444 | 16.8012
11:49 | 1755 | 24.0339 | 195.4512 | 436.8835 | 443.2476 | -20.828 | -46.9289 | 3.068 | 1.0485 | -5.9384 | -6.1099 | -2.153 | -3.7145 | 3.7884 | -3.0766 | 0.5872 | 0.6311 | 0.9508 | 0.703 | -130.7387 | -5.3892 | 1.1613 | -0.5329 | -7.3576 | -5.9643 | 0.6786 |  | -1.8093 | -2.8142 | 4.0014 | 3.363 | 3.3517 | 1.0337 | 10.6747 | 14.1189 | 14.7197 | 11.0342 | -0.0003 | -0.0025 | 0.0006 | 0.0038 | 0 | -0.0006 | 0.0055 | -0.0095 | 0.0135 | -360.1527 | 17.4664 | -360.5096 | 17.7909 | -360.8635 | 18.1625 | -360.9004 | 17.5116 | -352.7306 | 18.7559 | -352.7706 | 16.7889
11:49 | 1756 | 24.0698 | 195.5685 | 436.7769 | 443.3205 | -20.8308 | -47.0353 | 3.0376 | 1.0314 | -5.9333 | -6.2682 | -2.1923 | -3.7287 | 3.8317 | -3.0284 | 0.5898 | 0.6317 | 0.9514 | 0.7013 | -130.7097 | -5.3983 | 1.1571 | -0.492 | -7.2815 | -5.9281 | 0.7135 |  | -1.835 | -2.8356 | 4.0024 | 3.3636 | 3.3494 | 1.0345 | 10.6572 | 14.1307 | 14.7334 | 11.0276 | -0.0003 | -0.0028 | 0.0004 | 0.0037 | 0.0008 | -0.0006 | 0.0125 | -0.0036 | -0.0095 | -360.1558 | 17.4747 | -360.5127 | 17.8011 | -360.8789 | 18.183 | -360.9774 | 17.5465 | -352.7706 | 18.762 | -352.8106 | 16.8012
11:49 | 1757 | 24.0535 | 195.4977 | 436.9481 | 443.3197 | -20.8381 | -47.029 | 3.0706 | 1.0452 | -5.8543 | -6.1177 | -2.3027 | -3.7534 | 3.7973 | -3.1069 | 0.5891 | 0.6326 | 0.9538 | 0.7024 | -130.7171 | -5.3526 | 1.0512 | -0.5165 | -7.3145 | -6.0092 | 0.7108 |  | -1.8154 | -2.8862 | 4.003 | 3.3621 | 3.3546 | 1.0348 | 10.6285 | 14.0725 | 14.6839 | 10.9768 | 0.0001 | -0.0032 | 0.0005 | 0.0034 | 0.0007 | -0.0004 | 0.0034 | -0.0084 | -0.002 | -360.165 | 17.4664 | -360.5035 | 17.7785 | -360.8358 | 18.1728 | -360.9281 | 17.5219 | -352.7583 | 18.7456 | -352.786 | 16.7766
11:49 | 1758 | 24.1361 | 195.5799 | 437.0452 | 443.3298 | -20.8119 | -47.0048 | 3.069 | 1.0347 | -5.8379 | -6.2188 | -2.2346 | -3.8077 | 3.7171 | -3.2262 | 0.5878 | 0.6328 | 0.9496 | 0.7011 | -130.6891 | -5.3674 | 1.1227 | -0.5224 | -7.3648 | -5.965 | 0.7583 |  | -1.8299 | -2.8291 | 4.0018 | 3.361 | 3.3524 | 1.0353 | 10.6088 | 14.0876 | 14.6417 | 10.9916 | 0.0006 | -0.0029 | 0.0005 | 0.0038 | 0.0005 | -0.0007 | 0.0065 | -0.0017 | -0.0073 | -360.2142 | 17.5013 | -360.5343 | 17.8073 | -360.8881 | 18.1625 | -360.9374 | 17.5301 | -352.7706 | 18.7887 | -352.8075 | 16.8053
11:49 | 1759 | 24.0451 | 195.5289 | 437.0247 | 443.3292 | -20.6896 | -46.9079 | 3.1261 | 1.0887 | -5.832 | -6.2292 | -2.2527 | -3.7665 | 3.7733 | -3.1661 | 0.5887 | 0.6339 | 0.9545 | 0.7019 | -130.7292 | -5.3822 | 1.0836 | -0.5397 | -7.3495 | -5.9359 | 0.721 |  | -1.7823 | -2.7663 | 4.0032 | 3.3653 | 3.3538 | 1.0355 | 10.6099 | 14.0772 | 14.672 | 11.0042 | -0.0003 | -0.0029 | 0.0009 | 0.0033 | 0.0008 | -0.001 | 0.0192 | -0.0118 | -0.0172 | -360.1681 | 17.4726 | -360.5804 | 17.8278 | -360.9158 | 18.1604 | -360.8881 | 17.5075 | -352.7244 | 18.76 | -352.7983 | 16.8197
11:49 | 1760 | 24.0608 | 195.461 | 437.0423 | 443.3227 | -20.65 | -46.903 | 3.2365 | 1.0262 | -5.8213 | -6.1631 | -2.2354 | -3.7076 | 3.8085 | -3.0928 | 0.5885 | 0.6333 | 0.9553 | 0.7021 | -130.8968 | -5.4972 | 1.0449 | -0.5447 | -7.3865 | -5.9976 | 0.6968 |  | -1.8193 | -2.717 | 4.0012 | 3.3611 | 3.349 | 1.0338 | 10.6388 | 14.1294 | 14.6962 | 11.0327 | -0.0005 | -0.0029 | 0.0007 | 0.0034 | 0.0003 | -0.0005 | 0.0011 | -0.0124 | -0.0206 | -360.1496 | 17.4705 | -360.525 | 17.797 | -360.8974 | 18.181 | -360.9312 | 17.5116 | -352.7521 | 18.7477 | -352.8014 | 16.8135
11:49 | 1761 | 24.1153 | 195.5916 | 437.014 | 443.28 | -20.6246 | -46.8353 | 3.1599 | 1.0262 | -5.8828 | -6.2089 | -2.1782 | -3.6368 | 3.8172 | -3.1069 | 0.588 | 0.6318 | 0.9532 | 0.7005 | -130.8514 | -5.446 | 1.2146 | -0.476 | -7.342 | -6.093 | 0.6431 |  | -1.8273 | -2.77 | 4.0006 | 3.3646 | 3.3536 | 1.0342 | 10.6457 | 14.0901 | 14.6918 | 10.9876 | 0 | -0.0032 | 0.0012 | 0.0046 | 0.001 | -0.0004 | 0.0045 | -0.0147 | -0.0212 | -360.1804 | 17.4747 | -360.525 | 17.7826 | -360.8512 | 18.1707 | -360.9558 | 17.5363 | -352.7983 | 18.7538 | -352.7737 | 16.7807
11:49 | 1762 | 24.1113 | 195.5964 | 437.0588 | 443.3855 | -20.6666 | -46.8958 | 3.2324 | 1.0924 | -5.7828 | -6.1129 | -2.3654 | -3.6245 | 3.7924 | -3.1616 | 0.5879 | 0.6311 | 0.9532 | 0.6996 | -130.8865 | -5.4424 | 1.0075 | -0.532 | -7.3382 | -6.0362 | 0.5582 |  | -1.8938 | -2.6885 | 4.0011 | 3.3639 | 3.3518 | 1.0326 | 10.6492 | 14.1282 | 14.689 | 11.0432 | -0.0001 | -0.0032 | 0.0003 | 0.0036 | 0.0002 | -0.0004 | 0.0118 | -0.0087 | -0.0178 | -360.2081 | 17.5055 | -360.5527 | 17.7888 | -360.8512 | 18.1379 | -360.9004 | 17.5301 | -352.826 | 18.7846 | -352.8383 | 16.795
11:49 | 1763 | 24.1292 | 195.5078 | 437.0345 | 443.3514 | -20.656 | -46.8515 | 3.2337 | 1.1829 | -5.7089 | -6.141 | -2.3742 | -3.632 | 3.822 | -3.1124 | 0.5885 | 0.633 | 0.9545 | 0.7018 | -130.8054 | -5.4624 | 1.2006 | -0.5644 | -7.3437 | -6.05 | 0.6127 |  | -1.8304 | -2.7119 | 4.0021 | 3.3634 | 3.3513 | 1.0339 | 10.6389 | 14.1235 | 14.6952 | 11.0158 | -0.0004 | -0.0029 | 0.0006 | 0.0036 | 0.0007 | -0.0006 | 0.0246 | 0.0033 | 0.0161 | -360.1742 | 17.4829 | -360.5466 | 17.8093 | -360.8974 | 18.1543 | -360.8881 | 17.5157 | -352.7583 | 18.7682 | -352.8198 | 16.8094
11:49 | 1764 | 24.1601 | 195.5318 | 437.1209 | 443.3817 | -20.6612 | -46.8212 | 3.2188 | 1.1445 | -5.7252 | -6.1233 | -2.3322 | -3.6375 | 3.9238 | -3.0577 | 0.5884 | 0.6337 | 0.9541 | 0.7019 | -130.8257 | -5.5154 | 1.2777 | -0.619 | -7.4388 | -6.2351 | 0.5965 |  | -1.8606 | -2.695 | 4.0014 | 3.3645 | 3.3518 | 1.0358 | 10.6353 | 14.1202 | 14.6932 | 11.0407 | -0.0005 | -0.0029 | 0.0003 | 0.0038 | 0.0007 | -0.0001 | 0.003 | -0.0018 | -0.0258 | -360.1311 | 17.4541 | -360.4973 | 17.8032 | -360.8666 | 18.1892 | -360.9404 | 17.5178 | -352.7921 | 18.7415 | -352.7767 | 16.8053
11:49 | 1765 | 24.0995 | 195.5361 | 437.1059 | 443.3177 | -20.4951 | -46.7297 | 3.1781 | 1.1439 | -5.7547 | -6.1119 | -2.3101 | -3.6415 | 3.8239 | -3.0956 | 0.5885 | 0.6335 | 0.9533 | 0.7023 | -130.7875 | -5.4823 | 1.266 | -0.4765 | -7.4456 | -6.0463 | 0.6195 |  | -1.8175 | -2.7627 | 4.0015 | 3.3637 | 3.3517 | 1.0343 | 10.6549 | 14.0994 | 14.6901 | 11.037 | -0.0001 | -0.0028 | 0.001 | 0.0041 | 0.0005 | -0.001 | 0.0101 | -0.0124 | 0.0112 | -360.2142 | 17.4664 | -360.5066 | 17.7909 | -360.8758 | 18.1789 | -360.9527 | 17.5486 | -352.7767 | 18.7456 | -352.7675 | 16.7642
11:49 | 1766 | 24.0953 | 195.5172 | 437.0359 | 443.3015 | -20.5914 | -46.7695 | 3.2066 | 1.1679 | -5.6906 | -6.0259 | -2.2957 | -3.6417 | 3.8386 | -3.0787 | 0.5869 | 0.6319 | 0.9515 | 0.7004 | -130.833 | -5.5928 | 1.1094 | -0.5511 | -7.5057 | -6.0806 | 0.5867 |  | -1.8322 | -2.7513 | 4.0021 | 3.3633 | 3.3507 | 1.0335 | 10.6457 | 14.1363 | 14.7265 | 11.0165 | 0 | -0.0034 | 0.0009 | 0.0036 | 0.0004 | -0.0006 | 0.0061 | 0.0015 | -0.0095 | -360.165 | 17.4788 | -360.5343 | 17.797 | -360.845 | 18.1666 | -360.9343 | 17.5301 | -352.8044 | 18.762 | -352.8044 | 16.8032
11:49 | 1767 | 24.1372 | 195.6246 | 437.1592 | 443.4083 | -20.667 | -46.9133 | 3.0966 | 1.1325 | -5.7375 | -6.0149 | -2.2202 | -3.6886 | 3.8261 | -3.097 | 0.588 | 0.6323 | 0.9544 | 0.7005 | -130.8275 | -5.5157 | 1.1169 | -0.5053 | -7.3771 | -6.0485 | 0.6166 |  | -1.8434 | -2.7237 | 4.002 | 3.3611 | 3.3514 | 1.0339 | 10.6539 | 14.1153 | 14.6924 | 11.0136 | -0.0004 | -0.0031 | 0.0007 | 0.0038 | 0.0006 | -0.0008 | 0.0253 | -0.0038 | -0.0183 | -360.1742 | 17.4993 | -360.5681 | 17.834 | -360.9374 | 18.1584 | -360.882 | 17.4993 | -352.7706 | 18.7703 | -352.8321 | 16.8238
11:49 | 1768 | 24.1238 | 195.6117 | 436.9401 | 443.405 | -20.6868 | -46.9062 | 3.0603 | 1.1482 | -5.7837 | -5.9992 | -2.2808 | -3.7291 | 3.7769 | -3.0188 | 0.5875 | 0.6347 | 0.9563 | 0.7023 | -130.8244 | -5.475 | 1.1486 | -0.5411 | -7.3898 | -6.0934 | 0.6124 |  | -1.8433 | -2.7825 | 4.0017 | 3.3662 | 3.3502 | 1.0345 | 10.6837 | 14.1405 | 14.7406 | 11.0529 | -0.0006 | -0.0028 | 0.0003 | 0.0035 | 0.0006 | -0.0006 | 0.0317 | -0.0141 | -0.0044 | -360.1065 | 17.4664 | -360.5466 | 17.8278 | -360.9035 | 18.1789 | -360.9127 | 17.5034 | -352.7767 | 18.7559 | -352.8198 | 16.8217
11:49 | 1769 | 24.1689 | 195.5298 | 437.0686 | 443.3807 | -20.7714 | -46.9697 | 3.023 | 1.1247 | -5.8525 | -6.0384 | -2.337 | -3.6819 | 3.8371 | -3.0885 | 0.5878 | 0.6341 | 0.9544 | 0.7018 | -130.8451 | -5.563 | 1.0978 | -0.5645 | -7.4591 | -6.0831 | 0.6026 |  | -1.8526 | -2.8624 | 4.003 | 3.3635 | 3.3491 | 1.0348 | 10.641 | 14.1088 | 14.7116 | 11.0576 | -0.0002 | -0.0029 | 0.0002 | 0.0039 | 0.0006 | -0.0007 | 0.0059 | -0.0092 | -0.007 | -360.165 | 17.4808 | -360.5312 | 17.7929 | -360.8666 | 18.1912 | -360.9712 | 17.5342 | -352.786 | 18.7538 | -352.8014 | 16.793
11:49 | 1770 | 24.2064 | 195.5507 | 437.1385 | 443.4031 | -20.6794 | -46.9078 | 3.1694 | 1.2624 | -5.7612 | -5.9736 | -2.2785 | -3.6013 | 3.854 | -3.0697 | 0.5876 | 0.6299 | 0.9476 | 0.7019 | -130.8561 | -5.5882 | 1.1136 | -0.5873 | -7.3012 | -6.1942 | 0.6674 |  | -1.8863 | -2.7903 | 4.0027 | 3.3621 | 3.346 | 1.0343 | 10.6525 | 14.1089 | 14.6953 | 11.0399 | 0.0003 | -0.0029 | 0.0006 | 0.0037 | 0.0013 | -0.0006 | 0.0138 | -0.0083 | -0.015 | -360.2235 | 17.4993 | -360.5435 | 17.7744 | -360.8266 | 18.1481 | -360.9127 | 17.5383 | -352.8075 | 18.7723 | -352.8167 | 16.7827
11:49 | 1771 | 24.1963 | 195.5884 | 437.1774 | 443.4222 | -20.6895 | -46.8706 | 3.1578 | 1.1421 | -5.7822 | -6.0407 | -2.2525 | -3.6776 | 3.8417 | -3.0134 | 0.5884 | 0.6327 | 0.9519 | 0.7027 | -130.8519 | -5.603 | 1.0951 | -0.5437 | -7.3276 | -5.9843 | 0.6991 |  | -1.8492 | -2.8373 | 4.0025 | 3.3619 | 3.3504 | 1.0339 | 10.6446 | 14.1408 | 14.7009 | 11.0042 | -0.0002 | -0.0034 | 0.0001 | 0.0035 | 0.0002 | -0.0002 | 0.0114 | -0.0032 | 0.0092 | -360.2358 | 17.5075 | -360.5527 | 17.7991 | -360.8635 | 18.1625 | -360.9251 | 17.528 | -352.8137 | 18.7887 | -352.7983 | 16.795
11:49 | 1772 | 24.2914 | 195.5304 | 437.073 | 443.3814 | -20.676 | -46.7979 | 3.1651 | 1.1669 | -5.702 | -6.0115 | -2.3269 | -3.6782 | 3.8591 | -3.0413 | 0.5873 | 0.6335 | 0.952 | 0.702 | -130.8051 | -5.5232 | 1.0885 | -0.4846 | -7.3757 | -6.0184 | 0.666 |  | -1.7624 | -2.7905 | 4.0026 | 3.3636 | 3.3481 | 1.0343 | 10.6145 | 14.1051 | 14.7064 | 11.0201 | -0.0005 | -0.0027 | 0.0004 | 0.0037 | 0.0008 | -0.0009 | 0.0122 | -0.0131 | -0.0106 | -360.1465 | 17.4644 | -360.5281 | 17.8114 | -360.8574 | 18.1645 | -360.8974 | 17.5075 | -352.7614 | 18.7477 | -352.8167 | 16.8135
11:49 | 1773 | 24.3006 | 195.5369 | 437.0859 | 443.375 | -20.7308 | -46.927 | 3.2101 | 1.1673 | -5.669 | -6.0617 | -2.3406 | -3.6576 | 3.7707 | -3.0598 | 0.5869 | 0.6343 | 0.9547 | 0.7022 | -130.8619 | -5.6179 | 1.0793 | -0.5225 | -7.4235 | -6.0052 | 0.705 |  | -1.7827 | -2.7844 | 4.001 | 3.3649 | 3.35 | 1.0341 | 10.6583 | 14.0858 | 14.7242 | 11.0457 | -0.0001 | -0.0026 | 0.0011 | 0.004 | 0.0008 | 0 | 0.0041 | -0.0013 | -0.016 | -360.1435 | 17.4623 | -360.5127 | 17.797 | -360.9004 | 18.2056 | -360.962 | 17.5321 | -352.7583 | 18.7395 | -352.7798 | 16.7909
11:49 | 1774 | 24.2718 | 195.6186 | 437.1389 | 443.5067 | -20.6269 | -46.9301 | 3.1393 | 1.1836 | -5.6907 | -6.1414 | -2.2766 | -3.6441 | 3.7666 | -3.1247 | 0.5864 | 0.6333 | 0.95 | 0.7013 | -130.8469 | -5.5847 | 1.0542 | -0.5098 | -7.5383 | -6.0441 | 0.6914 |  | -1.746 | -2.7993 | 4.0021 | 3.3666 | 3.3502 | 1.0338 | 10.6399 | 14.0902 | 14.716 | 11.0276 | 0 | -0.0029 | 0.001 | 0.0037 | 0.0009 | -0.0006 | 0.0158 | 0.0076 | -0.0064 | -360.1804 | 17.45 | -360.4881 | 17.7888 | -360.8574 | 18.1687 | -360.9435 | 17.526 | -352.7737 | 18.7374 | -352.746 | 16.7909
11:49 | 1775 | 24.2628 | 195.6235 | 437.1393 | 443.5308 | -20.6399 | -47.0216 | 3.1546 | 1.216 | -5.5863 | -6.0649 | -2.2466 | -3.5561 | 3.8501 | -3.0229 | 0.5878 | 0.6284 | 0.9527 | 0.7025 | -130.9316 | -5.6561 | 1.0167 | -0.4524 | -7.5336 | -6.0506 | 0.6825 |  | -1.7829 | -2.7067 | 4.0019 | 3.3646 | 3.3488 | 1.0346 | 10.6527 | 14.1144 | 14.6642 | 11.0349 | 0.0003 | -0.0031 | 0.0006 | 0.0038 | 0.0005 | -0.0006 | -0.0055 | -0.0099 | -0.014 | -360.2173 | 17.5096 | -360.5619 | 17.8073 | -360.8881 | 18.1748 | -360.922 | 17.5424 | -352.8075 | 18.7846 | -352.8321 | 16.793
11:49 | 1776 | 24.192 | 195.6389 | 437.1033 | 443.5068 | -20.7103 | -46.98 | 3.2419 | 1.2649 | -5.6351 | -6.0898 | -2.2541 | -3.5578 | 3.8874 | -3.0371 | 0.5887 | 0.632 | 0.9586 | 0.7036 | -130.8375 | -5.6073 | 1.0768 | -0.4404 | -7.5188 | -6.0144 | 0.7284 |  | -1.7122 | -2.7015 | 4.0016 | 3.3648 | 3.3481 | 1.0338 | 10.6225 | 14.1249 | 14.716 | 10.9988 | -0.0003 | -0.0029 | 0.0006 | 0.0034 | 0.0004 | -0.0009 | 0.003 | -0.0055 | -0.0084 | -360.1804 | 17.4911 | -360.5681 | 17.8134 | -360.8881 | 18.1461 | -360.8881 | 17.5055 | -352.7706 | 18.7703 | -352.8198 | 16.8074
11:49 | 1777 | 24.1796 | 195.5278 | 437.0831 | 443.4164 | -20.7145 | -46.8753 | 3.2246 | 1.2628 | -5.6333 | -6.0102 | -2.1986 | -3.5231 | 3.8653 | -3.0065 | 0.5878 | 0.6302 | 0.9522 | 0.7018 | -130.9604 | -5.5634 | 1.0581 | -0.4813 | -7.5239 | -5.9933 | 0.6447 |  | -1.8304 | -2.7241 | 4.0017 | 3.361 | 3.3477 | 1.034 | 10.6629 | 14.1252 | 14.7413 | 11.0558 | 0.0002 | -0.0024 | 0.0004 | 0.0037 | 0.0005 | -0.001 | -0.0004 | 0 | -0.0212 | -360.1373 | 17.4931 | -360.6019 | 17.834 | -360.9158 | 18.1707 | -360.9343 | 17.5178 | -352.7583 | 18.7867 | -352.8414 | 16.8094
11:49 | 1778 | 24.22 | 195.5667 | 437.0502 | 443.4079 | -20.6673 | -46.8914 | 3.308 | 1.2569 | -5.6346 | -6.022 | -2.1639 | -3.5637 | 3.829 | -3.0269 | 0.5876 | 0.6304 | 0.9524 | 0.7021 | -130.8253 | -5.5513 | 1.0681 | -0.5669 | -7.4911 | -5.9576 | 0.6149 |  | -1.7748 | -2.9014 | 4.0026 | 3.3692 | 3.35 | 1.0355 | 10.61 | 14.1002 | 14.6767 | 11.0162 | -0.0003 | -0.003 | 0.0003 | 0.0039 | 0.0002 | -0.0005 | 0.005 | -0.0179 | -0.0059 | -360.1558 | 17.4521 | -360.4758 | 17.795 | -360.8543 | 18.1789 | -360.9343 | 17.5137 | -352.7583 | 18.7415 | -352.7244 | 16.793
11:49 | 1779 | 24.3053 | 195.5599 | 437.126 | 443.4234 | -20.5812 | -46.8635 | 3.3394 | 1.1923 | -5.6872 | -6.1369 | -2.2523 | -3.7217 | 3.7759 | -3.0291 | 0.5868 | 0.6318 | 0.9536 | 0.7017 | -130.817 | -5.593 | 1.0762 | -0.5125 | -7.3889 | -5.8812 | 0.7214 |  | -1.7456 | -2.8151 | 4.002 | 3.3631 | 3.3469 | 1.0347 | 10.6607 | 14.1343 | 14.7375 | 11.0367 | 0.0004 | -0.0028 | 0.0007 | 0.0037 | 0.001 | -0.0006 | 0.0128 | -0.0075 | -0.0094 | -360.205 | 17.4788 | -360.5189 | 17.7867 | -360.8604 | 18.1912 | -360.9804 | 17.5506 | -352.8137 | 18.7661 | -352.7767 | 16.7848
11:49 | 1780 | 24.2286 | 195.5584 | 436.9816 | 443.3495 | -20.6042 | -46.9104 | 3.3977 | 1.1634 | -5.7246 | -6.1056 | -2.3252 | -3.6626 | 3.8286 | -3.0102 | 0.5869 | 0.6336 | 0.951 | 0.7015 | -130.85 | -5.5859 | 1.1499 | -0.4859 | -7.33 | -5.8179 | 0.7097 |  | -1.8067 | -2.8482 | 4.0013 | 3.3642 | 3.3472 | 1.0354 | 10.6585 | 14.12 | 14.6805 | 11.0122 | -0.0002 | -0.0029 | 0.0005 | 0.0039 | 0.0003 | -0.0004 | 0.0126 | -0.0035 | 0.0016 | -360.1927 | 17.4767 | -360.5066 | 17.797 | -360.8327 | 18.1604 | -360.9404 | 17.5321 | -352.789 | 18.7661 | -352.789 | 16.7766
11:49 | 1781 | 24.2643 | 195.6202 | 437.0187 | 443.4019 | -20.6918 | -46.9894 | 3.3296 | 1.1531 | -5.724 | -6.1934 | -2.2206 | -3.597 | 3.9114 | -2.8998 | 0.5881 | 0.6324 | 0.9524 | 0.7022 | -130.7508 | -5.5163 | 1.1995 | -0.6177 | -7.3942 | -5.9519 | 0.6507 |  | -1.7127 | -2.8265 | 4.0008 | 3.3655 | 3.3496 | 1.0338 | 10.6376 | 14.1166 | 14.7527 | 11.0201 | -0.0007 | -0.003 | 0.0011 | 0.0039 | 0.0009 | -0.0007 | 0.001 | 0.0052 | -0.026 | -360.165 | 17.487 | -360.5927 | 17.8504 | -360.9158 | 18.1687 | -360.9281 | 17.5239 | -352.7737 | 18.7744 | -352.8229 | 16.8279
11:49 | 1782 | 24.2934 | 195.6382 | 437.1448 | 443.4755 | -20.6589 | -46.9843 | 3.2609 | 1.1732 | -5.7071 | -6.0621 | -2.3087 | -3.7314 | 3.859 | -2.9691 | 0.5894 | 0.6316 | 0.9515 | 0.7019 | -130.8155 | -5.5162 | 1.17 | -0.5518 | -7.461 | -5.9101 | 0.6876 |  | -1.7626 | -2.8561 | 4.0002 | 3.3632 | 3.3453 | 1.0343 | 10.67 | 14.1145 | 14.7116 | 11.0287 | -0.0003 | -0.0028 | 0.0006 | 0.0039 | 0.0005 | -0.0005 | 0.0006 | -0.0137 | -0.0092 | -360.1527 | 17.4623 | -360.5343 | 17.8258 | -360.9312 | 18.1687 | -360.9158 | 17.5055 | -352.7244 | 18.7477 | -352.7952 | 16.8074
11:49 | 1783 | 24.279 | 195.6698 | 437.1503 | 443.5046 | -20.7696 | -46.9759 | 3.2532 | 1.2062 | -5.7436 | -6.1592 | -2.3517 | -3.6592 | 3.801 | -2.9338 | 0.5873 | 0.6301 | 0.9518 | 0.7029 | -130.7371 | -5.4665 | 1.0904 | -0.507 | -7.4448 | -5.8806 | 0.7538 |  | -1.735 | -2.7935 | 4.0014 | 3.3628 | 3.3493 | 1.0345 | 10.6193 | 14.1035 | 14.6729 | 10.9855 | -0.0001 | -0.0033 | 0.0006 | 0.0034 | 0.0007 | -0.0009 | -0.0008 | -0.0081 | -0.02 | -360.1527 | 17.4726 | -360.5435 | 17.8258 | -360.9035 | 18.1645 | -360.9466 | 17.5198 | -352.789 | 18.7641 | -352.789 | 16.8074
11:49 | 1784 | 24.3116 | 195.5071 | 437.0457 | 443.4109 | -20.7116 | -47.0439 | 3.2008 | 1.2461 | -5.7035 | -6.1662 | -2.2809 | -3.6652 | 3.8122 | -2.979 | 0.5866 | 0.6308 | 0.9518 | 0.7024 | -130.7965 | -5.5534 | 1.114 | -0.4593 | -7.4115 | -5.8615 | 0.7708 |  | -1.7559 | -2.7718 | 4.0017 | 3.3651 | 3.3522 | 1.0342 | 10.6213 | 14.1239 | 14.6752 | 11.0146 | 0.0002 | -0.003 | 0.0008 | 0.0035 | 0.001 | -0.0001 | 0.0072 | -0.0101 | -0.0264 | -360.1773 | 17.4788 | -360.5158 | 17.7847 | -360.8389 | 18.1276 | -360.9312 | 17.5219 | -352.7521 | 18.7579 | -352.7798 | 16.7724
11:49 | 1785 | 24.2748 | 195.5677 | 437.0904 | 443.484 | -20.7428 | -47.0136 | 3.2281 | 1.2622 | -5.6706 | -6.1043 | -2.3008 | -3.6638 | 3.8562 | -2.9946 | 0.588 | 0.6301 | 0.9475 | 0.7006 | -130.7352 | -5.4701 | 1.1653 | -0.4065 | -7.4207 | -5.968 | 0.7143 |  | -1.7422 | -2.7552 | 4.0018 | 3.3646 | 3.3516 | 1.0358 | 10.6216 | 14.1174 | 14.6873 | 11.0108 | -0.0007 | -0.0032 | 0.0003 | 0.0032 | 0.0004 | -0.0009 | 0.0061 | -0.0089 | -0.0066 | -360.2173 | 17.5013 | -360.5773 | 17.8093 | -360.8574 | 18.1214 | -360.9189 | 17.5342 | -352.8537 | 18.7887 | -352.8106 | 16.793
11:49 | 1786 | 24.3264 | 195.5349 | 437.0702 | 443.4339 | -20.7299 | -46.8506 | 3.3036 | 1.2861 | -5.7436 | -6.1845 | -2.3452 | -3.7123 | 3.8806 | -2.9775 | 0.5866 | 0.6306 | 0.9522 | 0.7023 | -130.8016 | -5.5303 | 1.0999 | -0.358 | -7.3047 | -5.9018 | 0.7726 |  | -1.7795 | -2.7809 | 4.001 | 3.3604 | 3.3512 | 1.0345 | 10.6134 | 14.0806 | 14.6808 | 11.0021 | -0.0002 | -0.0028 | 0.0006 | 0.0037 | 0.0006 | -0.0009 | 0.0017 | -0.0005 | -0.0147 | -360.1619 | 17.4808 | -360.5619 | 17.8217 | -360.885 | 18.1276 | -360.9189 | 17.526 | -352.7983 | 18.7661 | -352.8167 | 16.8032
11:49 | 1787 | 24.279 | 195.5428 | 437.0946 | 443.4675 | -20.5501 | -46.7843 | 3.3873 | 1.3312 | -5.6623 | -6.1523 | -2.2677 | -3.7809 | 3.8013 | -3.1696 | 0.5876 | 0.6347 | 0.953 | 0.7021 | -130.7715 | -5.539 | 1.1481 | -0.4771 | -7.3547 | -5.9392 | 0.779 |  | -1.8316 | -2.7863 | 4.0036 | 3.3638 | 3.3479 | 1.0352 | 10.6351 | 14.1322 | 14.7137 | 11.0626 | 0 | -0.0028 | 0.0005 | 0.0038 | 0.0005 | -0.0005 | -0.0062 | -0.0103 | -0.0158 | -360.1896 | 17.4664 | -360.5496 | 17.8175 | -360.8697 | 18.1604 | -360.9312 | 17.5157 | -352.7706 | 18.7682 | -352.8167 | 16.8032
11:50 | 1788 | 24.2919 | 195.5525 | 437.0427 | 443.4172 | -20.5634 | -46.8541 | 3.3851 | 1.286 | -5.6553 | -6.1884 | -2.2527 | -3.6927 | 3.8143 | -3.0921 | 0.5884 | 0.6334 | 0.9544 | 0.7039 | -130.8013 | -5.4656 | 1.1891 | -0.4507 | -7.2301 | -5.8733 | 0.7505 |  | -1.7975 | -2.7723 | 4.0022 | 3.3689 | 3.3508 | 1.0358 | 10.6643 | 14.1315 | 14.6968 | 11.0183 | -0.0005 | -0.0035 | 0.0001 | 0.0036 | 0.0005 | -0.0008 | -0.0079 | -0.017 | -0.0113 | -360.1896 | 17.4459 | -360.5066 | 17.8134 | -360.8789 | 18.1584 | -360.9435 | 17.5404 | -352.7767 | 18.7436 | -352.749 | 16.7909
11:50 | 1789 | 24.2759 | 195.6289 | 437.0195 | 443.3633 | -20.6166 | -46.7988 | 3.3301 | 1.2868 | -5.6104 | -6.2238 | -2.2929 | -3.6648 | 3.8677 | -3.0017 | 0.5888 | 0.6342 | 0.9523 | 0.7034 | -130.8706 | -5.5362 | 1.0935 | -0.4635 | -7.3356 | -6.0451 | 0.724 |  | -1.7234 | -2.8077 | 4.0018 | 3.3699 | 3.3481 | 1.0353 | 10.6732 | 14.1243 | 14.7304 | 11.0308 | -0.0001 | -0.0027 | 0.0014 | 0.0048 | 0.0007 | -0.0001 | 0.0162 | -0.0085 | -0.0099 | -360.1558 | 17.4541 | -360.5004 | 17.8134 | -360.845 | 18.1337 | -360.9527 | 17.5424 | -352.7829 | 18.7436 | -352.7921 | 16.795
11:50 | 1790 | 24.2574 | 195.6013 | 437.0362 | 443.3451 | -20.6931 | -46.8527 | 3.4027 | 1.2513 | -5.6009 | -6.2005 | -2.2445 | -3.7088 | 3.8437 | -2.9874 | 0.5894 | 0.6297 | 0.9502 | 0.7016 | -130.8301 | -5.4481 | 1.042 | -0.5073 | -7.2828 | -6.0702 | 0.7315 |  | -1.6772 | -2.7987 | 4.0032 | 3.3689 | 3.352 | 1.0356 | 10.678 | 14.1343 | 14.7143 | 11.0367 | -0.0009 | -0.003 | 0.0009 | 0.0036 | 0.0007 | -0.0009 | -0.0101 | -0.023 | -0.0273 | -360.2358 | 17.4952 | -360.5435 | 17.8155 | -360.8758 | 18.1296 | -360.9035 | 17.5383 | -352.7952 | 18.7867 | -352.8014 | 16.7848
11:50 | 1791 | 24.2752 | 195.5156 | 437.0006 | 443.3962 | -20.7036 | -46.8495 | 3.4668 | 1.1465 | -5.6042 | -6.1746 | -2.2336 | -3.7112 | 3.8222 | -3.0467 | 0.5881 | 0.6312 | 0.9536 | 0.7028 | -130.8198 | -5.4868 | 1.1697 | -0.5977 | -7.2728 | -6.1067 | 0.6702 |  | -1.7014 | -2.8923 | 4.0022 | 3.3632 | 3.3498 | 1.0354 | 10.6618 | 14.1471 | 14.6936 | 11.0374 | 0 | -0.0026 | 0.0004 | 0.0035 | 0.0007 | -0.0001 | 0.0032 | -0.0095 | -0.0099 | -360.1681 | 17.487 | -360.5619 | 17.8381 | -360.8912 | 18.1235 | -360.8974 | 17.528 | -352.786 | 18.7723 | -352.8352 | 16.8135
11:50 | 1792 | 24.2247 | 195.4906 | 437.0932 | 443.3395 | -20.6373 | -46.8216 | 3.464 | 1.1282 | -5.6505 | -6.2655 | -2.3253 | -3.5513 | 3.9264 | -2.9101 | 0.5877 | 0.6283 | 0.9517 | 0.7035 | -130.8694 | -5.5123 | 1.1942 | -0.5641 | -7.3324 | -6.1564 | 0.6616 |  | -1.5947 | -2.8834 | 4.001 | 3.3633 | 3.3497 | 1.0351 | 10.6237 | 14.1261 | 14.7 | 11.0229 | 0.0001 | -0.0031 | 0.001 | 0.0038 | 0.0011 | -0.0008 | 0 | 0.0045 | -0.0089 | -360.1558 | 17.489 | -360.5743 | 17.834 | -360.885 | 18.1317 | -360.9312 | 17.5321 | -352.7552 | 18.7723 | -352.829 | 16.8032
11:50 | 1793 | 24.2423 | 195.4883 | 437.076 | 443.331 | -20.6363 | -46.8539 | 3.4784 | 1.1349 | -5.6848 | -6.174 | -2.34 | -3.6118 | 3.9052 | -2.9268 | 0.587 | 0.6277 | 0.9509 | 0.703 | -130.7841 | -5.4267 | 1.239 | -0.5343 | -7.2844 | -5.9755 | 0.7271 |  | -1.717 | -2.9005 | 4.0028 | 3.3638 | 3.35 | 1.0338 | 10.6539 | 14.1037 | 14.6751 | 11.0136 | -0.0001 | -0.0029 | 0 | 0.0031 | 0.0008 | -0.0003 | 0.0112 | -0.0094 | -0.0125 | -360.1435 | 17.4623 | -360.5066 | 17.8155 | -360.8604 | 18.1502 | -360.9404 | 17.5609 | -352.7737 | 18.7497 | -352.8106 | 16.7971
11:50 | 1794 | 24.4002 | 195.5776 | 437.0995 | 443.3716 | -20.655 | -46.8835 | 3.4779 | 1.2225 | -5.4869 | -6.0947 | -2.2592 | -3.5984 | 3.9688 | -2.8903 | 0.5855 | 0.6313 | 0.9509 | 0.7017 | -130.8103 | -5.339 | 1.295 | -0.3276 | -7.2674 | -5.9109 | 0.6979 |  | -1.6747 | -2.8825 | 4.0025 | 3.3616 | 3.3478 | 1.0347 | 10.6122 | 14.0911 | 14.6458 | 11.0064 | -0.0002 | -0.0025 | 0.0009 | 0.004 | 0.001 | -0.0006 | 0.0101 | -0.0208 | -0.0166 | -360.1865 | 17.4664 | -360.5189 | 17.7888 | -360.8604 | 18.1276 | -360.9251 | 17.5691 | -352.789 | 18.7456 | -352.7675 | 16.7766
11:50 | 1795 | 24.285 | 195.6734 | 437.1949 | 443.4214 | -20.6551 | -46.888 | 3.3896 | 1.1424 | -5.575 | -6.1423 | -2.314 | -3.5849 | 3.8971 | -2.8555 | 0.5868 | 0.6299 | 0.9512 | 0.7037 | -130.8878 | -5.3838 | 1.2274 | -0.3453 | -7.2077 | -5.9512 | 0.7448 |  | -1.6422 | -2.8706 | 4.002 | 3.3653 | 3.3477 | 1.0361 | 10.6307 | 14.0865 | 14.6414 | 10.9901 | -0.0003 | -0.0029 | 0.0011 | 0.0041 | 0.0008 | -0.0006 | -0.005 | -0.0055 | -0.0239 | -360.1988 | 17.5034 | -360.5066 | 17.7909 | -360.8543 | 18.1461 | -360.9312 | 17.5609 | -352.826 | 18.7703 | -352.8014 | 16.7868
11:50 | 1796 | 24.269 | 195.6465 | 437.1705 | 443.4352 | -20.6158 | -46.9364 | 3.4697 | 1.2203 | -5.4944 | -6.1072 | -2.3476 | -3.5765 | 3.7974 | -2.903 | 0.5874 | 0.6312 | 0.9514 | 0.7027 | -130.8773 | -5.3802 | 1.2018 | -0.3728 | -7.2529 | -6.0576 | 0.7595 |  | -1.6996 | -2.89 | 4.0028 | 3.3632 | 3.348 | 1.0351 | 10.6341 | 14.1076 | 14.6755 | 10.993 | 0.0003 | -0.0027 | 0.0006 | 0.0038 | 0.0007 | 0.0003 | 0.0098 | -0.0047 | -0.0005 | -360.1742 | 17.4767 | -360.5219 | 17.8196 | -360.8758 | 18.1276 | -360.885 | 17.5445 | -352.7706 | 18.7538 | -352.8044 | 16.8053
11:50 | 1797 | 24.3322 | 195.6781 | 437.0373 | 443.3772 | -20.6906 | -47.0549 | 3.3071 | 1.2569 | -5.5671 | -6.0326 | -2.3425 | -3.6324 | 3.8738 | -2.8308 | 0.5874 | 0.6321 | 0.9524 | 0.7029 | -130.8446 | -5.3386 | 1.1941 | -0.5095 | -7.2296 | -6.0472 | 0.6729 |  | -1.7111 | -2.8365 | 4.002 | 3.3611 | 3.3479 | 1.0363 | 10.6329 | 14.118 | 14.6973 | 11.0092 | 0.0001 | -0.003 | 0.001 | 0.0044 | 0.0006 | -0.0009 | 0.0092 | -0.0042 | 0 | -360.1219 | 17.4623 | -360.5435 | 17.8299 | -360.9127 | 18.1563 | -360.9343 | 17.5363 | -352.7521 | 18.7518 | -352.8321 | 16.8135
11:50 | 1798 | 24.2498 | 195.7506 | 437.0653 | 443.4762 | -20.6972 | -46.9955 | 3.3549 | 1.273 | -5.5387 | -6.123 | -2.3422 | -3.7204 | 3.9145 | -2.8941 | 0.5871 | 0.633 | 0.9543 | 0.7017 | -130.8625 | -5.3733 | 1.1334 | -0.5797 | -7.2602 | -6.0076 | 0.6244 |  | -1.6584 | -2.8727 | 4.0014 | 3.3611 | 3.3491 | 1.036 | 10.6398 | 14.1251 | 14.6939 | 11.0215 | -0.0003 | -0.0026 | 0.0005 | 0.0037 | 0 | -0.0001 | -0.0036 | -0.0116 | -0.0306 | -360.1465 | 17.4582 | -360.5127 | 17.8155 | -360.8974 | 18.1481 | -360.922 | 17.5342 | -352.7429 | 18.7169 | -352.7521 | 16.795
11:50 | 1799 | 24.3931 | 195.6494 | 437.0915 | 443.5044 | -20.7267 | -47.0138 | 3.3635 | 1.2985 | -5.5585 | -6.1049 | -2.3546 | -3.6697 | 3.9069 | -2.923 | 0.5883 | 0.6297 | 0.9498 | 0.7025 | -130.8119 | -5.3616 | 1.1608 | -0.4597 | -7.2528 | -5.9745 | 0.6331 |  | -1.6742 | -2.8676 | 4.0007 | 3.3656 | 3.3505 | 1.0364 | 10.6469 | 14.1144 | 14.7105 | 11.0522 | -0.0006 | -0.0025 | 0.0001 | 0.0033 | 0.001 | -0.0007 | 0.0212 | -0.0102 | 0.004 | -360.1988 | 17.4788 | -360.5219 | 17.8032 | -360.8789 | 18.1481 | -360.9681 | 17.565 | -352.8044 | 18.7538 | -352.8106 | 16.793
11:50 | 1800 | 24.3399 | 195.5784 | 437.0343 | 443.4992 | -20.7235 | -47.0241 | 3.2613 | 1.3146 | -5.5607 | -6.0642 | -2.3228 | -3.6209 | 3.9207 | -2.9479 | 0.587 | 0.6279 | 0.9501 | 0.7031 | -130.8279 | -5.3932 | 1.1402 | -0.2843 | -7.2574 | -5.8912 | 0.7926 |  | -1.723 | -2.8156 | 4.0021 | 3.3626 | 3.3483 | 1.0352 | 10.6389 | 14.0944 | 14.6883 | 10.993 | -0.0003 | -0.0031 | 0.0005 | 0.0035 | 0.0003 | -0.0009 | -0.0018 | -0.0092 | -0.0009 | -360.2296 | 17.489 | -360.5496 | 17.797 | -360.8666 | 18.1071 | -360.8943 | 17.5321 | -352.7921 | 18.7682 | -352.7952 | 16.7745
11:50 | 1801 | 24.3616 | 195.5703 | 437.0275 | 443.5636 | -20.6667 | -47.1012 | 3.3275 | 1.3933 | -5.5553 | -5.9349 | -2.2923 | -3.6522 | 3.8454 | -3.0515 | 0.5889 | 0.6328 | 0.9524 | 0.7026 | -130.8554 | -5.4625 | 1.1106 | -0.3831 | -7.2296 | -5.9942 | 0.8305 |  | -1.6793 | -2.8309 | 4.0018 | 3.3641 | 3.3509 | 1.0354 | 10.6562 | 14.1178 | 14.6962 | 11.0212 | 0.0003 | -0.003 | 0.0004 | 0.0034 | 0.0007 | -0.0007 | 0.0075 | -0.0124 | -0.0249 | -360.2142 | 17.4829 | -360.5835 | 17.8237 | -360.8758 | 18.1214 | -360.8974 | 17.5486 | -352.8167 | 18.7579 | -352.8167 | 16.8012
11:50 | 1802 | 24.4195 | 195.6014 | 436.997 | 443.6086 | -20.7588 | -47.0616 | 3.3044 | 1.3542 | -5.6118 | -5.9301 | -2.3214 | -3.6281 | 3.8683 | -2.9641 | 0.5883 | 0.6289 | 0.9504 | 0.7013 | -130.814 | -5.3672 | 1.2384 | -0.4373 | -7.2675 | -6.0012 | 0.8083 |  | -1.683 | -2.7554 | 4.0017 | 3.3621 | 3.3494 | 1.037 | 10.6205 | 14.0584 | 14.6396 | 11.0097 | -0.0004 | -0.0033 | 0.0006 | 0.0036 | 0.0007 | -0.0005 | 0.0137 | -0.0017 | 0.0117 | -360.1804 | 17.4705 | -360.5466 | 17.8217 | -360.885 | 18.1502 | -360.962 | 17.5404 | -352.7644 | 18.7395 | -352.8075 | 16.7827
11:50 | 1803 | 24.3924 | 195.4964 | 436.9907 | 443.4542 | -20.742 | -47.0588 | 3.2821 | 1.2936 | -5.5882 | -5.9701 | -2.2764 | -3.6529 | 3.9282 | -2.9212 | 0.5879 | 0.6278 | 0.9518 | 0.7022 | -130.7943 | -5.4242 | 1.1961 | -0.4275 | -7.2337 | -5.9593 | 0.7502 |  | -1.7169 | -2.7157 | 4.0016 | 3.3667 | 3.351 | 1.0359 | 10.633 | 14.0889 | 14.702 | 11.0212 | -0.0006 | -0.0028 | 0.001 | 0.0042 | 0.0004 | -0.0006 | 0.0043 | -0.0226 | -0.0183 | -360.1742 | 17.448 | -360.4912 | 17.795 | -360.8666 | 18.1502 | -360.9589 | 17.5609 | -352.8044 | 18.7456 | -352.746 | 16.7766
11:50 | 1804 | 24.4321 | 195.6895 | 437.0425 | 443.4809 | -20.766 | -47.0786 | 3.3711 | 1.3527 | -5.577 | -5.838 | -2.3247 | -3.6721 | 3.9019 | -2.9138 | 0.5882 | 0.6297 | 0.9517 | 0.7016 | -130.7726 | -5.509 | 1.2899 | -0.3645 | -7.2477 | -5.9688 | 0.7405 |  | -1.6269 | -2.7391 | 4.0004 | 3.3647 | 3.3501 | 1.0352 | 10.6677 | 14.1063 | 14.7078 | 11.0269 | 0 | -0.0028 | 0.0005 | 0.0036 | 0.001 | -0.0003 | -0.0075 | -0.0189 | -0.0097 | -360.1619 | 17.4644 | -360.5189 | 17.8175 | -360.8481 | 18.1502 | -360.9927 | 17.5629 | -352.7583 | 18.7538 | -352.7829 | 16.7704
11:50 | 1805 | 24.4707 | 195.617 | 437.0468 | 443.5636 | -20.7299 | -47.0334 | 3.3297 | 1.3097 | -5.5458 | -6.1056 | -2.3337 | -3.7301 | 3.8411 | -3.0263 | 0.5877 | 0.6303 | 0.9471 | 0.7011 | -130.8744 | -5.5122 | 1.1706 | -0.3681 | -7.3483 | -5.9659 | 0.7022 |  | -1.6431 | -2.7306 | 4.0018 | 3.3648 | 3.35 | 1.0372 | 10.6527 | 14.1375 | 14.7221 | 11.0349 | 0 | -0.003 | 0.0008 | 0.0039 | 0.0003 | -0.0004 | 0.0038 | -0.0106 | -0.012 | -360.1496 | 17.4726 | -360.525 | 17.8093 | -360.8266 | 18.1132 | -360.8943 | 17.5383 | -352.7767 | 18.762 | -352.7952 | 16.7766
11:50 | 1806 | 24.4718 | 195.6581 | 437.0112 | 443.578 | -20.7558 | -47.0179 | 3.3755 | 1.356 | -5.615 | -6.0733 | -2.2835 | -3.715 | 3.8995 | -2.9274 | 0.5882 | 0.6308 | 0.9508 | 0.7014 | -130.8641 | -5.4737 | 1.3062 | -0.3685 | -7.3299 | -5.904 | 0.705 |  | -1.689 | -2.6784 | 4.0029 | 3.3672 | 3.3542 | 1.0354 | 10.6619 | 14.1237 | 14.7204 | 11.0555 | -0.0001 | -0.0028 | 0.0008 | 0.004 | 0.001 | -0.0003 | 0.0068 | -0.0095 | -0.0114 | -360.1558 | 17.4911 | -360.5896 | 17.8566 | -360.9281 | 18.1317 | -360.922 | 17.5465 | -352.789 | 18.7682 | -352.829 | 16.8156
11:50 | 1807 | 24.451 | 195.6912 | 437.1353 | 443.6018 | -20.7067 | -46.9391 | 3.3974 | 1.33 | -5.6134 | -6.0441 | -2.2965 | -3.7084 | 3.9058 | -2.9027 | 0.5875 | 0.6305 | 0.955 | 0.7023 | -130.7923 | -5.3986 | 1.1979 | -0.324 | -7.3646 | -5.867 | 0.7739 |  | -1.7097 | -2.6595 | 4.0018 | 3.3654 | 3.3527 | 1.0349 | 10.6446 | 14.1408 | 14.6894 | 11.0042 | -0.0007 | -0.0028 | 0.0003 | 0.0032 | 0.0003 | -0.0006 | 0.0168 | -0.0189 | -0.0009 | -360.1404 | 17.4685 | -360.5527 | 17.8175 | -360.885 | 18.1337 | -360.882 | 17.5178 | -352.746 | 18.7477 | -352.8198 | 16.7909
11:50 | 1808 | 24.5229 | 195.7298 | 437.1423 | 443.6901 | -20.7344 | -47.0093 | 3.4494 | 1.3426 | -5.5974 | -6.0717 | -2.2735 | -3.607 | 3.9044 | -2.8136 | 0.5869 | 0.63 | 0.9525 | 0.7021 | -130.8565 | -5.4979 | 1.2932 | -0.2871 | -7.2586 | -5.8693 | 0.7499 |  | -1.6418 | -2.6783 | 4.0024 | 3.3637 | 3.3484 | 1.036 | 10.6215 | 14.1177 | 14.7009 | 10.9984 | -0.0005 | -0.0026 | 0.0005 | 0.0037 | 0.0007 | -0.0009 | 0.0161 | -0.0032 | -0.0033 | -360.1835 | 17.4603 | -360.525 | 17.8258 | -360.882 | 18.1502 | -360.9774 | 17.5629 | -352.7737 | 18.7477 | -352.8106 | 16.7909
11:50 | 1809 | 24.5257 | 195.7229 | 437.18 | 443.7871 | -20.7873 | -46.9353 | 3.4331 | 1.2913 | -5.5344 | -5.9928 | -2.2429 | -3.5933 | 3.8521 | -2.8873 | 0.5882 | 0.6311 | 0.9487 | 0.7029 | -130.892 | -5.4965 | 1.225 | -0.3448 | -7.2328 | -5.8473 | 0.7993 |  | -1.638 | -2.7501 | 4.0008 | 3.3651 | 3.3522 | 1.0361 | 10.6515 | 14.1018 | 14.6928 | 11.0565 | -0.0001 | -0.0033 | 0.0005 | 0.0037 | 0.0007 | -0.0003 | 0.0135 | -0.0112 | -0.0054 | -360.1558 | 17.4562 | -360.485 | 17.7826 | -360.805 | 18.1132 | -360.922 | 17.565 | -352.7829 | 18.7436 | -352.7675 | 16.756
11:50 | 1810 | 24.5078 | 195.6204 | 437.2279 | 443.7415 | -20.7159 | -46.9556 | 3.4207 | 1.3473 | -5.5887 | -5.9394 | -2.2642 | -3.6345 | 3.9312 | -2.8665 | 0.5877 | 0.6315 | 0.9485 | 0.7041 | -130.8977 | -5.6161 | 1.2416 | -0.3882 | -7.2426 | -5.8664 | 0.7875 |  | -1.5949 | -2.6772 | 4.0032 | 3.3655 | 3.3506 | 1.0377 | 10.6193 | 14.0978 | 14.674 | 11.014 | -0.0003 | -0.0036 | 0.0003 | 0.0036 | 0.0008 | -0.001 | -0.0072 | -0.0051 | -0.0239 | -360.2204 | 17.4952 | -360.5619 | 17.8134 | -360.8604 | 18.144 | -360.962 | 17.5691 | -352.8044 | 18.7744 | -352.7767 | 16.7807
11:50 | 1811 | 24.4893 | 195.6948 | 437.1735 | 443.6182 | -20.7452 | -46.9128 | 3.4593 | 1.3517 | -5.5691 | -6.0541 | -2.2134 | -3.6746 | 3.885 | -2.935 | 0.5877 | 0.633 | 0.9521 | 0.7031 | -130.8461 | -5.4573 | 1.2364 | -0.3779 | -7.2805 | -5.8959 | 0.7798 |  | -1.59 | -2.7311 | 4.0034 | 3.3645 | 3.3507 | 1.0369 | 10.6307 | 14.104 | 14.7119 | 11.0129 | -0.0007 | -0.0033 | 0.001 | 0.0041 | 0.0006 | -0.0005 | 0.016 | -0.0105 | -0.0018 | -360.1496 | 17.4767 | -360.5496 | 17.8175 | -360.8974 | 18.1255 | -360.8697 | 17.528 | -352.7737 | 18.7477 | -352.826 | 16.7909
11:50 | 1812 | 24.4912 | 195.6054 | 437.1674 | 443.5949 | -20.7007 | -47.017 | 3.4461 | 1.3271 | -5.5331 | -6.0785 | -2.2552 | -3.6466 | 3.9308 | -2.8546 | 0.588 | 0.6346 | 0.952 | 0.7024 | -130.9489 | -5.6031 | 1.1899 | -0.3416 | -7.2842 | -5.955 | 0.674 |  | -1.6475 | -2.7546 | 4.0024 | 3.363 | 3.3523 | 1.0358 | 10.6767 | 14.1277 | 14.7508 | 11.0633 | -0.0001 | -0.0027 | 0.0006 | 0.0033 | 0.0006 | -0.0004 | -0.0004 | -0.004 | -0.0286 | -360.1527 | 17.4582 | -360.5281 | 17.8381 | -360.9066 | 18.1584 | -360.9404 | 17.5445 | -352.7244 | 18.7374 | -352.8075 | 16.8094
11:50 | 1813 | 24.531 | 195.5863 | 437.1895 | 443.6409 | -20.7938 | -47.1412 | 3.3485 | 1.3979 | -5.5144 | -6.1033 | -2.2284 | -3.5705 | 3.9865 | -2.8118 | 0.5889 | 0.6306 | 0.9485 | 0.7032 | -130.9193 | -5.5679 | 1.2166 | -0.3016 | -7.2345 | -5.8648 | 0.7774 |  | -1.6326 | -2.7738 | 4.0036 | 3.3644 | 3.3491 | 1.0372 | 10.6537 | 14.1101 | 14.7198 | 11.0294 | -0.0001 | -0.003 | 0.0005 | 0.0036 | 0.0006 | -0.0007 | 0.0089 | -0.0095 | -0.0103 | -360.1619 | 17.4562 | -360.5158 | 17.8258 | -360.9097 | 18.1563 | -360.9497 | 17.5486 | -352.7675 | 18.7374 | -352.7644 | 16.7848
11:50 | 1814 | 24.4734 | 195.5909 | 437.2095 | 443.577 | -20.7115 | -47.0915 | 3.2348 | 1.358 | -5.5996 | -5.9731 | -2.2598 | -3.6517 | 3.9564 | -2.8533 | 0.589 | 0.6324 | 0.9494 | 0.7029 | -130.9447 | -5.5227 | 1.2231 | -0.3235 | -7.2201 | -5.8683 | 0.8082 |  | -1.5887 | -2.5477 | 4.003 | 3.3627 | 3.3477 | 1.037 | 10.6918 | 14.1252 | 14.7413 | 11.0558 | 0.0001 | -0.0032 | 0.0005 | 0.004 | 0.0003 | -0.0002 | 0.0054 | -0.0191 | -0.0214 | -360.1896 | 17.4849 | -360.5219 | 17.8073 | -360.8358 | 18.1235 | -360.9035 | 17.5486 | -352.786 | 18.7661 | -352.8075 | 16.7704
11:50 | 1815 | 24.4883 | 195.7311 | 437.2513 | 443.5624 | -20.7538 | -47.1316 | 3.2515 | 1.337 | -5.5861 | -6.0655 | -2.2511 | -3.5721 | 4.009 | -2.8086 | 0.589 | 0.6298 | 0.951 | 0.7031 | -131.0434 | -5.57 | 1.1908 | -0.3586 | -7.2627 | -5.9448 | 0.7722 |  | -1.705 | -2.5858 | 4.0027 | 3.3641 | 3.3486 | 1.0352 | 10.6803 | 14.1308 | 14.7113 | 11.0388 | -0.0001 | -0.0027 | 0.0002 | 0.0033 | 0.0007 | -0.0008 | 0.0254 | -0.0066 | 0.0029 | -360.2111 | 17.5137 | -360.6019 | 17.8299 | -360.9004 | 18.1091 | -360.9127 | 17.5506 | -352.8198 | 18.7805 | -352.8506 | 16.7889
11:50 | 1816 | 24.4433 | 195.6139 | 437.1464 | 443.5717 | -20.7321 | -47.0875 | 3.178 | 1.3175 | -5.5744 | -6.0529 | -2.2172 | -3.6819 | 3.9881 | -2.8351 | 0.5871 | 0.6312 | 0.9508 | 0.7019 | -130.9773 | -5.4805 | 1.2147 | -0.4617 | -7.1998 | -5.8927 | 0.8804 |  | -1.5958 | -2.5969 | 4.0038 | 3.3638 | 3.3505 | 1.0384 | 10.6077 | 14.0978 | 14.7261 | 11.0024 | -0.0006 | -0.0032 | 0.0005 | 0.0034 | -0.0001 | -0.0009 | 0.004 | -0.003 | -0.006 | -360.1773 | 17.4644 | -360.5281 | 17.8258 | -360.8758 | 18.1214 | -360.8912 | 17.5342 | -352.7706 | 18.7415 | -352.8198 | 16.7868
11:50 | 1817 | 24.4458 | 195.5763 | 437.2747 | 443.5006 | -20.6668 | -47.1101 | 3.2354 | 1.2832 | -5.5875 | -6.0805 | -2.2743 | -3.5611 | 3.9286 | -2.8203 | 0.5869 | 0.6296 | 0.952 | 0.7035 | -130.9394 | -5.4523 | 1.2223 | -0.3698 | -7.2841 | -5.8765 | 0.7865 |  | -1.6083 | -2.5599 | 4.0034 | 3.3637 | 3.3506 | 1.0372 | 10.6295 | 14.0913 | 14.7047 | 11.0291 | -0.0005 | -0.003 | 0.0006 | 0.0035 | 0.0015 | -0.0005 | 0.022 | -0.0238 | -0.0015 | -360.1804 | 17.4623 | -360.5066 | 17.8196 | -360.9035 | 18.1645 | -360.9712 | 17.5753 | -352.8044 | 18.7395 | -352.7429 | 16.7868
11:50 | 1818 | 24.46 | 195.7522 | 437.198 | 443.6382 | -20.759 | -47.0923 | 3.1171 | 1.2289 | -5.6425 | -6.0581 | -2.3347 | -3.6089 | 3.9753 | -2.7612 | 0.5876 | 0.6324 | 0.952 | 0.7034 | -130.8976 | -5.4957 | 1.2853 | -0.3109 | -7.2481 | -5.9133 | 0.7415 |  | -1.5961 | -2.5664 | 4.0039 | 3.3657 | 3.3542 | 1.0377 | 10.6226 | 14.0901 | 14.6628 | 11.0049 | 0.0004 | -0.003 | 0.0009 | 0.0037 | 0.0005 | -0.0005 | 0.0106 | -0.0119 | -0.0171 | -360.2019 | 17.4644 | -360.4666 | 17.7765 | -360.8143 | 18.1255 | -360.9404 | 17.5732 | -352.786 | 18.7292 | -352.7552 | 16.756
11:50 | 1819 | 24.5855 | 195.672 | 437.2732 | 443.6859 | -20.6798 | -47.0462 | 3.2491 | 1.334 | -5.5412 | -6.145 | -2.1656 | -3.5453 | 3.8908 | -2.9231 | 0.5886 | 0.6312 | 0.9513 | 0.703 | -130.976 | -5.5655 | 1.262 | -0.3505 | -7.1524 | -5.8518 | 0.8058 |  | -1.5878 | -2.6648 | 4.0031 | 3.3661 | 3.3538 | 1.0367 | 10.5961 | 14.0516 | 14.6624 | 10.9678 | 0 | -0.0032 | 0.0004 | 0.0039 | 0.0006 | -0.0005 | 0.0005 | 0.0018 | -0.0051 | -360.2327 | 17.4911 | -360.5896 | 17.8217 | -360.8604 | 18.1235 | -360.9127 | 17.5547 | -352.7798 | 18.7682 | -352.8106 | 16.7848
11:50 | 1820 | 24.5661 | 195.7105 | 437.3338 | 443.658 | -20.7285 | -46.9898 | 3.3368 | 1.3684 | -5.6368 | -6.1556 | -2.2233 | -3.4415 | 3.9798 | -2.8008 | 0.5887 | 0.6288 | 0.9495 | 0.7026 | -130.9686 | -5.5541 | 1.2329 | -0.4049 | -7.2314 | -5.893 | 0.8629 |  | -1.5746 | -2.5708 | 4.0029 | 3.3633 | 3.3502 | 1.0362 | 10.6421 | 14.1043 | 14.685 | 11.0063 | -0.0001 | -0.0023 | 0.0004 | 0.0033 | 0.0005 | -0.0006 | 0.0031 | -0.0093 | -0.0101 | -360.1281 | 17.4582 | -360.5312 | 17.836 | -360.922 | 18.1255 | -360.9097 | 17.5198 | -352.7213 | 18.7333 | -352.7583 | 16.8032
11:50 | 1821 | 24.5009 | 195.6965 | 437.3357 | 443.6897 | -20.6918 | -47.0651 | 3.3362 | 1.4131 | -5.5068 | -5.9854 | -2.1837 | -3.5266 | 4.0142 | -2.8941 | 0.5875 | 0.6265 | 0.9516 | 0.7028 | -131.0089 | -5.587 | 1.2087 | -0.4024 | -7.2535 | -5.8305 | 0.859 |  | -1.6188 | -2.8311 | 4.0024 | 3.3646 | 3.35 | 1.0363 | 10.6515 | 14.1248 | 14.7265 | 11.0049 | -0.0001 | -0.0027 | 0.0004 | 0.0037 | 0.0004 | -0.0004 | 0.0146 | 0.0017 | -0.0035 | -360.125 | 17.4644 | -360.5281 | 17.8237 | -360.9127 | 18.1584 | -360.922 | 17.5321 | -352.7706 | 18.7477 | -352.789 | 16.8115
11:50 | 1822 | 24.4331 | 195.6266 | 437.2245 | 443.581 | -20.6773 | -47.0265 | 3.3065 | 1.3579 | -5.5499 | -6.0253 | -2.2012 | -3.4161 | 4.0181 | -2.7392 | 0.589 | 0.633 | 0.9526 | 0.7031 | -130.9859 | -5.6057 | 1.3566 | -0.383 | -7.2963 | -5.8748 | 0.7438 |  | -1.6785 | -2.8215 | 4.0024 | 3.3643 | 3.3537 | 1.0364 | 10.6688 | 14.1308 | 14.7228 | 11.0388 | 0.0005 | -0.0025 | 0.0008 | 0.0042 | 0.0009 | -0.0005 | 0.0021 | -0.004 | 0.0093 | -360.1804 | 17.4705 | -360.5404 | 17.797 | -360.8481 | 18.1358 | -360.9251 | 17.5671 | -352.786 | 18.7518 | -352.7675 | 16.7786
11:50 | 1823 | 24.4206 | 195.7552 | 437.2855 | 443.6169 | -20.658 | -47.0621 | 3.2726 | 1.3622 | -5.6321 | -6.0283 | -2.1926 | -3.5341 | 3.9278 | -2.8521 | 0.5893 | 0.6316 | 0.954 | 0.7052 | -130.9922 | -5.6239 | 1.2717 | -0.3382 | -7.2293 | -5.851 | 0.8004 |  | -1.6601 | -2.757 | 4.0027 | 3.3652 | 3.3508 | 1.0372 | 10.6549 | 14.1226 | 14.7248 | 11.0197 | -0.0002 | -0.0033 | 0.0007 | 0.004 | 0.0005 | -0.0004 | -0.0011 | 0.0004 | -0.0125 | -360.1958 | 17.5013 | -360.5558 | 17.8011 | -360.8327 | 18.1071 | -360.8912 | 17.5609 | -352.8198 | 18.7703 | -352.8167 | 16.7848
11:50 | 1824 | 24.436 | 195.6299 | 437.2285 | 443.5278 | -20.6683 | -47.1318 | 3.3389 | 1.3766 | -5.5341 | -6.0115 | -2.1714 | -3.5138 | 3.9979 | -2.8488 | 0.5879 | 0.6351 | 0.9531 | 0.7041 | -131.0397 | -5.5728 | 1.1894 | -0.266 | -7.2661 | -5.7777 | 0.8075 |  | -1.6333 | -2.8456 | 4.0017 | 3.3642 | 3.3492 | 1.0363 | 10.6515 | 14.1017 | 14.7149 | 11.0165 | -0.0005 | -0.0028 | 0.0009 | 0.0038 | 0.0007 | -0.0009 | 0.0049 | -0.017 | -0.0138 | -360.2142 | 17.4911 | -360.5773 | 17.8381 | -360.8943 | 18.1276 | -360.9127 | 17.5527 | -352.8014 | 18.762 | -352.7983 | 16.7909
11:50 | 1825 | 24.5039 | 195.6329 | 437.3693 | 443.624 | -20.5745 | -47.0744 | 3.4252 | 1.4203 | -5.4913 | -6.0083 | -2.1812 | -3.4604 | 4.0316 | -2.8011 | 0.5881 | 0.6354 | 0.9529 | 0.7032 | -131.0168 | -5.536 | 1.2701 | -0.2858 | -7.2172 | -5.8596 | 0.7841 |  | -1.6194 | -2.8035 | 4.0023 | 3.3628 | 3.3477 | 1.0376 | 10.6318 | 14.0879 | 14.6785 | 11.037 | -0.0004 | -0.0026 | 0.0006 | 0.0033 | 0.0007 | -0.0006 | 0.0031 | -0.0144 | -0.0206 | -360.1311 | 17.448 | -360.5189 | 17.8134 | -360.8543 | 18.1461 | -360.9374 | 17.5363 | -352.7521 | 18.7312 | -352.7552 | 16.7868
11:50 | 1826 | 24.5708 | 195.7163 | 437.2273 | 443.6078 | -20.6623 | -46.992 | 3.3476 | 1.4331 | -5.5388 | -5.97 | -2.1815 | -3.4613 | 3.9948 | -2.8605 | 0.5882 | 0.6315 | 0.9534 | 0.7043 | -130.9624 | -5.5267 | 1.2249 | -0.3069 | -7.1962 | -5.8823 | 0.8643 |  | -1.5863 | -2.7724 | 4.0023 | 3.367 | 3.3506 | 1.0368 | 10.6332 | 14.1058 | 14.6815 | 10.9819 | -0.0003 | -0.0032 | 0.0004 | 0.0034 | 0.0006 | -0.0011 | 0.021 | 0.0033 | 0.0073 | -360.1558 | 17.4562 | -360.5189 | 17.8114 | -360.8758 | 18.1604 | -360.9712 | 17.5691 | -352.789 | 18.7395 | -352.746 | 16.7745
11:50 | 1827 | 24.4995 | 195.7078 | 437.2346 | 443.5719 | -20.7033 | -47.0407 | 3.3396 | 1.4004 | -5.4529 | -6.006 | -2.1567 | -3.5789 | 3.9432 | -2.8925 | 0.5879 | 0.6284 | 0.9521 | 0.7023 | -130.9307 | -5.5856 | 1.2864 | -0.3607 | -7.2694 | -5.8433 | 0.8638 |  | -1.617 | -2.8079 | 4.0012 | 3.3666 | 3.3499 | 1.037 | 10.6272 | 14.118 | 14.6915 | 11.015 | 0 | -0.0031 | 0.0006 | 0.0039 | 0.0009 | -0.0003 | 0.007 | -0.0132 | -0.0139 | -360.165 | 17.4644 | -360.525 | 17.7991 | -360.8358 | 18.1317 | -360.9374 | 17.5588 | -352.7767 | 18.7497 | -352.7921 | 16.7807
11:50 | 1828 | 24.5066 | 195.6682 | 437.3139 | 443.688 | -20.6809 | -46.9986 | 3.3888 | 1.4198 | -5.4793 | -5.8433 | -2.1523 | -3.6206 | 4.0061 | -2.8683 | 0.5872 | 0.6314 | 0.9525 | 0.7028 | -130.9469 | -5.7079 | 1.3137 | -0.3039 | -7.1589 | -5.7613 | 0.9759 |  | -1.6394 | -2.7285 | 4.0019 | 3.3663 | 3.3531 | 1.0363 | 10.6458 | 14.0898 | 14.6723 | 10.9999 | -0.0004 | -0.0031 | 0.0003 | 0.0035 | 0.0008 | -0.0007 | 0.0042 | -0.0151 | -0.0141 | -360.205 | 17.5116 | -360.5835 | 17.8381 | -360.9281 | 18.1276 | -360.8789 | 17.5506 | -352.7983 | 18.7785 | -352.826 | 16.8094
11:50 | 1829 | 24.6159 | 195.7466 | 437.3668 | 443.6993 | -20.672 | -47.0378 | 3.3502 | 1.357 | -5.5369 | -5.93 | -2.195 | -3.59 | 4.0254 | -2.8393 | 0.5871 | 0.6345 | 0.9511 | 0.7034 | -131.0231 | -5.6759 | 1.1926 | -0.2609 | -7.2114 | -5.735 | 0.9587 |  | -1.6678 | -2.7566 | 4.0021 | 3.3658 | 3.3519 | 1.0365 | 10.663 | 14.1018 | 14.7102 | 11.045 | -0.0004 | -0.0027 | 0.0006 | 0.0035 | 0.0007 | -0.0002 | 0.0247 | 0.0001 | 0.0042 | -360.1404 | 17.4644 | -360.5558 | 17.8155 | -360.8789 | 18.144 | -360.8974 | 17.5055 | -352.746 | 18.7559 | -352.8014 | 16.8053
11:50 | 1830 | 24.6158 | 195.7057 | 437.365 | 443.7319 | -20.6801 | -47.0418 | 3.3938 | 1.3943 | -5.5408 | -5.871 | -2.1968 | -3.5853 | 4.0125 | -2.8207 | 0.5874 | 0.6297 | 0.9509 | 0.7038 | -130.895 | -5.5927 | 1.2614 | -0.3192 | -7.138 | -5.8693 | 0.9067 |  | -1.6733 | -2.6667 | 4.0012 | 3.3624 | 3.3514 | 1.0363 | 10.626 | 14.1052 | 14.719 | 11.0313 | 0 | -0.0029 | 0.0005 | 0.0037 | 0.0005 | -0.0006 | 0.0066 | -0.0079 | -0.0131 | -360.165 | 17.4705 | -360.5404 | 17.8175 | -360.8881 | 18.1625 | -360.9404 | 17.5629 | -352.7921 | 18.7456 | -352.786 | 16.7848
11:50 | 1831 | 24.5993 | 195.6486 | 437.312 | 443.7401 | -20.6863 | -47.0183 | 3.3367 | 1.442 | -5.5611 | -5.863 | -2.1616 | -3.5085 | 4.012 | -2.8219 | 0.5865 | 0.6277 | 0.9497 | 0.7041 | -130.9833 | -5.6824 | 1.184 | -0.4291 | -7.2619 | -5.9283 | 0.8983 |  | -1.6693 | -2.7951 | 4.0029 | 3.3623 | 3.3477 | 1.0365 | 10.6678 | 14.1292 | 14.7472 | 11.0389 | -0.0001 | -0.0036 | 0.001 | 0.0039 | 0.0004 | -0.0006 | 0.0062 | -0.0037 | -0.0205 | -360.1711 | 17.4685 | -360.5066 | 17.7909 | -360.805 | 18.1132 | -360.9527 | 17.5691 | -352.7798 | 18.7415 | -352.7829 | 16.7683
11:50 | 1832 | 24.5988 | 195.6858 | 437.2927 | 443.618 | -20.7101 | -46.9915 | 3.4055 | 1.4211 | -5.4914 | -5.6567 | -2.0689 | -3.6293 | 3.9327 | -2.9953 | 0.5879 | 0.6289 | 0.9481 | 0.7043 | -130.9647 | -5.5772 | 1.1786 | -0.4317 | -7.2518 | -5.9063 | 0.8954 |  | -1.5938 | -2.7335 | 4.0004 | 3.3626 | 3.3503 | 1.0375 | 10.6537 | 14.1043 | 14.7198 | 11.0063 | -0.0001 | -0.0029 | 0.0011 | 0.0043 | 0.0004 | -0.0004 | 0.0159 | -0.0031 | 0.0072 | -360.2727 | 17.4993 | -360.5404 | 17.8114 | -360.8666 | 18.1276 | -360.9312 | 17.5629 | -352.826 | 18.7723 | -352.8075 | 16.7786
11:50 | 1833 | 24.6866 | 195.6714 | 437.3804 | 443.6436 | -20.6978 | -46.9249 | 3.4468 | 1.4735 | -5.424 | -5.8075 | -2.1392 | -3.4857 | 3.9674 | -2.8399 | 0.5886 | 0.6299 | 0.9528 | 0.7062 | -130.9803 | -5.6692 | 1.2021 | -0.3876 | -7.2253 | -5.796 | 0.9354 |  | -1.6292 | -2.6562 | 4.0022 | 3.3621 | 3.3486 | 1.0377 | 10.6539 | 14.1444 | 14.705 | 11.0421 | -0.0008 | -0.0031 | 0.0007 | 0.0033 | 0.0009 | -0.0012 | -0.005 | -0.0091 | -0.0173 | -360.125 | 17.4562 | -360.5312 | 17.8258 | -360.8543 | 18.1173 | -360.9127 | 17.5178 | -352.7183 | 18.7436 | -352.8075 | 16.7971
11:50 | 1834 | 24.6597 | 195.6708 | 437.42 | 443.634 | -20.6361 | -46.9262 | 3.5387 | 1.4524 | -5.394 | -5.6754 | -2.1209 | -3.5319 | 3.9258 | -2.842 | 0.5871 | 0.6307 | 0.9508 | 0.7034 | -130.9888 | -5.7448 | 1.1766 | -0.4091 | -7.3442 | -5.8518 | 0.9521 |  | -1.5918 | -2.6366 | 4.0032 | 3.3628 | 3.3537 | 1.0378 | 10.6641 | 14.1436 | 14.6895 | 11.0283 | -0.0006 | -0.0029 | 0.0007 | 0.0034 | 0.0005 | -0.0001 | 0.0199 | -0.0141 | 0.0012 | -360.1927 | 17.4603 | -360.5189 | 17.8237 | -360.9343 | 18.1522 | -360.9589 | 17.5547 | -352.7767 | 18.7333 | -352.789 | 16.8053
11:50 | 1835 | 24.6507 | 195.6315 | 437.3535 | 443.6483 | -20.5741 | -46.8012 | 3.5423 | 1.4771 | -5.4509 | -5.7843 | -2.1036 | -3.4878 | 3.9811 | -2.785 | 0.5875 | 0.6312 | 0.9499 | 0.7037 | -130.9432 | -5.6439 | 1.2023 | -0.3686 | -7.2575 | -5.8193 | 0.9914 |  | -1.5664 | -2.6882 | 4.0021 | 3.3618 | 3.3509 | 1.0376 | 10.618 | 14.0854 | 14.6863 | 10.9775 | 0.0001 | -0.0034 | 0.0004 | 0.0035 | 0.0004 | -0.0011 | -0.0019 | -0.0194 | -0.001 | -360.1773 | 17.4603 | -360.5066 | 17.7909 | -360.8297 | 18.0988 | -360.9404 | 17.5465 | -352.7552 | 18.7292 | -352.7706 | 16.7827
11:50 | 1836 | 24.5543 | 195.6712 | 437.3569 | 443.6655 | -20.5582 | -46.8308 | 3.4531 | 1.4654 | -5.4565 | -5.7962 | -2.1384 | -3.5232 | 3.9449 | -2.8242 | 0.5878 | 0.6321 | 0.955 | 0.7037 | -130.9792 | -5.7061 | 1.1615 | -0.3279 | -7.2867 | -5.8981 | 0.9808 |  | -1.5596 | -2.6076 | 4.0025 | 3.3644 | 3.3481 | 1.0368 | 10.663 | 14.1365 | 14.7681 | 11.045 | 0.0001 | -0.003 | 0.0004 | 0.0034 | 0.0004 | -0.0002 | -0.0021 | -0.0114 | -0.0265 | -360.2019 | 17.5096 | -360.5681 | 17.8196 | -360.8943 | 18.1029 | -360.8974 | 17.5465 | -352.8229 | 18.7867 | -352.8352 | 16.8012
11:50 | 1837 | 24.6148 | 195.6683 | 437.3778 | 443.7333 | -20.5612 | -46.8442 | 3.4398 | 1.4979 | -5.4493 | -5.7375 | -2.1455 | -3.5587 | 3.983 | -2.7728 | 0.5877 | 0.6335 | 0.9538 | 0.7031 | -130.9331 | -5.7724 | 1.2449 | -0.3249 | -7.2452 | -5.7247 | 1.0498 |  | -1.5208 | -2.6498 | 4.003 | 3.3673 | 3.3491 | 1.0366 | 10.6213 | 14.1181 | 14.7041 | 11.0435 | -0.0002 | -0.0028 | 0.0006 | 0.0037 | 0.0011 | -0.0005 | 0.0122 | 0.0013 | 0.0064 | -360.1404 | 17.4767 | -360.5681 | 17.8155 | -360.842 | 18.0927 | -360.885 | 17.526 | -352.7213 | 18.7456 | -352.7829 | 16.795
11:50 | 1838 | 24.5879 | 195.6861 | 437.3379 | 443.6869 | -20.5294 | -46.9876 | 3.5153 | 1.4824 | -5.4966 | -5.7076 | -2.1259 | -3.5006 | 4.0795 | -2.7796 | 0.5886 | 0.6338 | 0.9557 | 0.7051 | -130.9713 | -5.7334 | 1.1996 | -0.2468 | -7.205 | -5.7933 | 0.9702 |  | -1.5349 | -2.7236 | 4.0035 | 3.3643 | 3.3479 | 1.037 | 10.6561 | 14.1353 | 14.7204 | 11.0439 | -0.0003 | -0.0026 | 0.0008 | 0.0039 | 0.0005 | -0.0003 | 0.0041 | -0.0102 | -0.0054 | -360.1742 | 17.4664 | -360.5281 | 17.8073 | -360.882 | 18.1276 | -360.962 | 17.5547 | -352.8075 | 18.7456 | -352.7983 | 16.7971
11:50 | 1839 | 24.6294 | 195.7457 | 437.4262 | 443.7722 | -20.5373 | -46.8964 | 3.4399 | 1.4496 | -5.4737 | -5.7014 | -2.1417 | -3.4502 | 4.0841 | -2.7181 | 0.5877 | 0.6324 | 0.9515 | 0.7023 | -130.9473 | -5.6552 | 1.1978 | -0.2236 | -7.1782 | -5.783 | 1.0249 |  | -1.561 | -2.6843 | 4.0039 | 3.3669 | 3.3495 | 1.0379 | 10.6444 | 14.1182 | 14.6936 | 11.0258 | -0.0001 | -0.0026 | 0.0009 | 0.0042 | 0.0011 | 0 | 0.0085 | -0.0063 | -0.0195 | -360.1988 | 17.4562 | -360.5127 | 17.7826 | -360.8174 | 18.0927 | -360.9251 | 17.5794 | -352.7737 | 18.7374 | -352.7675 | 16.7622
11:50 | 1840 | 24.5711 | 195.6604 | 437.4779 | 443.7074 | -20.5096 | -46.9569 | 3.5391 | 1.5459 | -5.4298 | -5.7106 | -2.1397 | -3.4297 | 4.0589 | -2.715 | 0.5873 | 0.6333 | 0.9507 | 0.7028 | -130.9521 | -5.6889 | 1.1493 | -0.2233 | -7.1875 | -5.7073 | 0.9767 |  | -1.5312 | -2.5831 | 4.0027 | 3.3634 | 3.3518 | 1.0363 | 10.647 | 14.1083 | 14.6968 | 11.001 | 0.0001 | -0.0032 | 0.0003 | 0.0035 | 0.0007 | -0.0008 | 0.0114 | -0.013 | -0.0073 | -360.205 | 17.5034 | -360.5158 | 17.797 | -360.8604 | 18.1132 | -360.9281 | 17.5712 | -352.7983 | 18.762 | -352.786 | 16.7724
11:50 | 1841 | 24.67 | 195.7012 | 437.4093 | 443.786 | -20.4809 | -47.0181 | 3.6278 | 1.5398 | -5.4186 | -5.7095 | -2.1577 | -3.4804 | 3.9816 | -2.744 | 0.5881 | 0.6311 | 0.9526 | 0.7042 | -131.0077 | -5.7353 | 1.1611 | -0.2829 | -7.1877 | -5.6595 | 0.9216 |  | -1.5973 | -2.6506 | 4.0035 | 3.3652 | 3.3494 | 1.0366 | 10.6169 | 14.0956 | 14.6839 | 11.0288 | -0.0001 | -0.0027 | 0.0004 | 0.0038 | 0.0002 | -0.0005 | 0.0114 | 0.0009 | -0.0163 | -360.1835 | 17.4726 | -360.5435 | 17.834 | -360.885 | 18.0865 | -360.9035 | 17.5609 | -352.749 | 18.7374 | -352.7737 | 16.7971
11:50 | 1842 | 24.62 | 195.6704 | 437.4739 | 443.7429 | -20.5734 | -47.0099 | 3.6529 | 1.5469 | -5.3926 | -5.6694 | -2.1056 | -3.4482 | 4.0654 | -2.741 | 0.5891 | 0.6328 | 0.9526 | 0.7048 | -131.0226 | -5.6715 | 1.2203 | -0.2652 | -7.1446 | -5.8204 | 1.0131 |  | -1.497 | -2.5921 | 4.0028 | 3.3638 | 3.3512 | 1.0369 | 10.6422 | 14.1214 | 14.6598 | 11.0129 | -0.0004 | -0.0027 | 0.0005 | 0.0032 | 0.001 | -0.0006 | 0.0011 | -0.0091 | -0.0113 | -360.1496 | 17.4582 | -360.5373 | 17.8278 | -360.9004 | 18.1235 | -360.9404 | 17.5527 | -352.749 | 18.7395 | -352.7952 | 16.8074
11:50 | 1843 | 24.6768 | 195.7667 | 437.4942 | 443.7399 | -20.5837 | -47.0744 | 3.6595 | 1.4744 | -5.4767 | -5.7647 | -2.1661 | -3.463 | 4.1397 | -2.7372 | 0.5883 | 0.6298 | 0.9475 | 0.7053 | -131.0519 | -5.6554 | 1.144 | -0.2985 | -7.208 | -5.8025 | 0.9075 |  | -1.5455 | -2.6662 | 4.004 | 3.367 | 3.3516 | 1.0364 | 10.6273 | 14.0944 | 14.6999 | 10.9988 | -0.0004 | -0.0032 | 0.0003 | 0.0034 | 0.0002 | -0.0008 | 0.0192 | -0.0054 | 0.0101 | -360.1927 | 17.4685 | -360.5281 | 17.8175 | -360.9004 | 18.1091 | -360.9035 | 17.5794 | -352.7675 | 18.7374 | -352.7737 | 16.793
11:50 | 1844 | 24.6148 | 195.6647 | 437.283 | 443.6427 | -20.6736 | -47.1359 | 3.4871 | 1.4199 | -5.4258 | -5.7695 | -2.1237 | -3.5311 | 4.0226 | -2.8344 | 0.5889 | 0.6294 | 0.9495 | 0.705 | -130.9874 | -5.5832 | 1.2978 | -0.383 | -7.2385 | -5.8798 | 0.8813 |  | -1.5247 | -2.6989 | 4.0028 | 3.3682 | 3.3459 | 1.0369 | 10.6283 | 14.1135 | 14.6997 | 10.981 | 0.0004 | -0.0026 | 0.0009 | 0.004 | 0.0008 | -0.0008 | 0.0076 | -0.0086 | -0.0176 | -360.1804 | 17.4788 | -360.5404 | 17.797 | -360.8297 | 18.1071 | -360.9158 | 17.5671 | -352.7829 | 18.7703 | -352.7675 | 16.7704
11:50 | 1845 | 24.6156 | 195.6563 | 437.3459 | 443.7141 | -20.7358 | -47.1806 | 3.5033 | 1.4219 | -5.4826 | -5.7223 | -2.1788 | -3.575 | 4.027 | -2.7608 | 0.5885 | 0.6314 | 0.9507 | 0.704 | -130.9785 | -5.5614 | 1.2141 | -0.3014 | -7.1522 | -5.8355 | 0.9485 |  | -1.5333 | -2.6046 | 4.0029 | 3.3677 | 3.3498 | 1.037 | 10.6446 | 14.1294 | 14.6962 | 11.0038 | -0.0001 | -0.0032 | 0.0003 | 0.0036 | 0.0002 | -0.0006 | 0.0264 | -0.0124 | -0.0054 | -360.2081 | 17.4931 | -360.5712 | 17.8463 | -360.8943 | 18.0968 | -360.9066 | 17.5814 | -352.8075 | 18.7538 | -352.8075 | 16.8053
11:50 | 1846 | 24.6612 | 195.5896 | 437.3928 | 443.7135 | -20.6808 | -47.1032 | 3.4618 | 1.3888 | -5.5277 | -5.8063 | -2.1609 | -3.506 | 4.0686 | -2.6421 | 0.5889 | 0.6318 | 0.9503 | 0.7034 | -131.0543 | -5.7252 | 1.2314 | -0.3975 | -7.149 | -5.8132 | 0.9529 |  | -1.5216 | -2.6289 | 4.0038 | 3.3658 | 3.3538 | 1.0377 | 10.6422 | 14.1214 | 14.7292 | 11.0129 | -0.0005 | -0.0028 | 0.0007 | 0.0041 | 0.0007 | -0.0007 | 0.0008 | -0.0209 | -0.0092 | -360.1219 | 17.4582 | -360.5373 | 17.8134 | -360.8543 | 18.1091 | -360.9066 | 17.5588 | -352.7275 | 18.7271 | -352.7644 | 16.7848
11:50 | 1847 | 24.7576 | 195.7748 | 437.3707 | 443.8106 | -20.6373 | -47.0623 | 3.5749 | 1.4162 | -5.5073 | -5.6376 | -2.0633 | -3.4589 | 4.153 | -2.5964 | 0.5881 | 0.6322 | 0.9516 | 0.7054 | -131.049 | -5.6594 | 1.1864 | -0.3751 | -7.1674 | -5.7956 | 0.973 |  | -1.6327 | -2.6429 | 4.0025 | 3.3658 | 3.3527 | 1.0375 | 10.6756 | 14.115 | 14.7205 | 11.0623 | -0.0003 | -0.0029 | 0.0006 | 0.0038 | 0.001 | -0.0003 | 0.023 | 0.0056 | 0.0018 | -360.2481 | 17.4644 | -360.525 | 17.8217 | -360.9097 | 18.1235 | -360.9712 | 17.5978 | -352.8137 | 18.7374 | -352.7706 | 16.7889
11:51 | 1848 | 24.6723 | 195.7422 | 437.4114 | 443.8161 | -20.6733 | -47.1366 | 3.4785 | 1.3497 | -5.4632 | -5.8187 | -2.1343 | -3.419 | 4.1098 | -2.7329 | 0.5897 | 0.6286 | 0.9483 | 0.7047 | -131.0871 | -5.5813 | 1.2254 | -0.31 | -7.2308 | -5.9215 | 0.8753 |  | -1.4617 | -2.623 | 4.0041 | 3.3677 | 3.3499 | 1.037 | 10.6387 | 14.1411 | 14.7146 | 11.0381 | -0.0002 | -0.0033 | 0.0002 | 0.0036 | 0.0006 | -0.0007 | 0.0121 | -0.0113 | -0.0056 | -360.165 | 17.4521 | -360.5219 | 17.7909 | -360.8174 | 18.1112 | -360.922 | 17.5671 | -352.7829 | 18.7395 | -352.7675 | 16.7683
11:51 | 1849 | 24.6786 | 195.6577 | 437.4227 | 443.8306 | -20.6441 | -47.0656 | 3.6446 | 1.4127 | -5.4142 | -5.9121 | -2.1129 | -3.5002 | 4.1167 | -2.7217 | 0.5893 | 0.6335 | 0.9554 | 0.7039 | -131.069 | -5.5654 | 1.2587 | -0.2609 | -7.1479 | -5.742 | 0.9295 |  | -1.5261 | -2.6852 | 4.0034 | 3.3634 | 3.3475 | 1.0366 | 10.6366 | 14.0806 | 14.6808 | 11.0078 | 0 | -0.0032 | 0.0009 | 0.0037 | 0.0009 | -0.0008 | 0.0131 | 0.0042 | -0.015 | -360.2019 | 17.4726 | -360.5681 | 17.8422 | -360.8974 | 18.1029 | -360.9189 | 17.5753 | -352.7737 | 18.7518 | -352.826 | 16.795
11:51 | 1850 | 24.6191 | 195.7063 | 437.4052 | 443.7819 | -20.5434 | -46.9705 | 3.5891 | 1.4425 | -5.4252 | -5.8648 | -2.1535 | -3.4799 | 4.1523 | -2.6789 | 0.589 | 0.6308 | 0.9532 | 0.7036 | -131.0986 | -5.5781 | 1.2096 | -0.2387 | -7.1691 | -5.7178 | 0.9631 |  | -1.4896 | -2.65 | 4.0036 | 3.3634 | 3.3483 | 1.0356 | 10.6619 | 14.1178 | 14.7309 | 11.0212 | -0.0006 | -0.003 | 0.0004 | 0.0033 | 0.0006 | -0.0004 | 0.0044 | -0.0084 | -0.0106 | -360.1435 | 17.4623 | -360.5619 | 17.8278 | -360.8974 | 18.105 | -360.9343 | 17.5486 | -352.7367 | 18.723 | -352.7952 | 16.7991
11:51 | 1851 | 24.7131 | 195.6899 | 437.4494 | 443.8355 | -20.554 | -46.9592 | 3.642 | 1.4313 | -5.4569 | -5.9255 | -2.1168 | -3.4745 | 4.1264 | -2.6825 | 0.5888 | 0.6293 | 0.9523 | 0.705 | -131.1026 | -5.5233 | 1.2695 | -0.3159 | -7.2506 | -5.8659 | 0.8735 |  | -1.4993 | -2.6583 | 4.0045 | 3.3681 | 3.3492 | 1.0371 | 10.6308 | 14.0921 | 14.7029 | 10.9909 | -0.0007 | -0.0029 | 0.0005 | 0.0035 | 0.0006 | -0.0009 | -0.0001 | -0.0091 | -0.0253 | -360.1773 | 17.4644 | -360.5189 | 17.8114 | -360.8758 | 18.1173 | -360.9312 | 17.5629 | -352.7706 | 18.7374 | -352.7952 | 16.793
11:51 | 1852 | 24.7466 | 195.7695 | 437.4219 | 443.841 | -20.6256 | -46.9061 | 3.5982 | 1.4769 | -5.4017 | -5.7537 | -1.9348 | -3.5032 | 4.1671 | -2.6745 | 0.5891 | 0.6326 | 0.9515 | 0.7028 | -131.0709 | -5.6702 | 1.1966 | -0.2549 | -7.2663 | -5.7565 | 1.0489 |  | -1.6362 | -2.6411 | 4.0063 | 3.3644 | 3.3523 | 1.0375 | 10.6122 | 14.1144 | 14.67 | 11.0118 | -0.0001 | -0.0034 | 0.0011 | 0.0039 | 0.0006 | -0.0002 | 0.0081 | -0.0068 | -0.0122 | -360.1927 | 17.4726 | -360.5404 | 17.8134 | -360.8481 | 18.1029 | -360.9589 | 17.5876 | -352.7737 | 18.7271 | -352.789 | 16.7889
11:51 | 1853 | 24.7015 | 195.7327 | 437.4518 | 443.8091 | -20.6583 | -47.022 | 3.5521 | 1.5133 | -5.411 | -5.7468 | -2.0376 | -3.4218 | 4.1516 | -2.6539 | 0.5884 | 0.6305 | 0.9521 | 0.7031 | -131.067 | -5.5431 | 1.2753 | -0.2452 | -7.2153 | -5.7776 | 0.9737 |  | -1.5669 | -2.5439 | 4.0045 | 3.3647 | 3.3495 | 1.0371 | 10.6457 | 14.1191 | 14.6813 | 11.0334 | 0 | -0.0032 | 0.0007 | 0.004 | 0.0011 | -0.0006 | 0.0143 | 0 | -0.0113 | -360.2173 | 17.4829 | -360.525 | 17.7867 | -360.8574 | 18.0865 | -360.9035 | 17.565 | -352.7829 | 18.7456 | -352.7829 | 16.7786
11:51 | 1854 | 24.738 | 195.7754 | 437.5123 | 443.8081 | -20.6218 | -47.0784 | 3.6917 | 1.4238 | -5.3717 | -5.7899 | -1.9984 | -3.4515 | 4.0831 | -2.6866 | 0.588 | 0.6318 | 0.9486 | 0.7034 | -131.0445 | -5.5418 | 1.2609 | -0.329 | -7.1089 | -5.778 | 0.9528 |  | -1.5193 | -2.6112 | 4.0051 | 3.3601 | 3.3513 | 1.0358 | 10.6481 | 14.127 | 14.734 | 11.0363 | -0.0007 | -0.0035 | 0.0006 | 0.0041 | 0.0005 | -0.0004 | -0.0002 | -0.0026 | -0.0227 | -360.1958 | 17.4829 | -360.5281 | 17.8299 | -360.8974 | 18.1091 | -360.9281 | 17.5753 | -352.7798 | 18.7518 | -352.789 | 16.8074
11:51 | 1855 | 24.7404 | 195.7424 | 437.3798 | 443.8077 | -20.6057 | -47.0514 | 3.6345 | 1.4516 | -5.4021 | -5.9226 | -2.0777 | -3.4749 | 4.1064 | -2.7365 | 0.5896 | 0.6339 | 0.956 | 0.7028 | -131.0096 | -5.5303 | 1.231 | -0.1742 | -7.0708 | -5.7664 | 0.9761 |  | -1.5678 | -2.6418 | 4.0043 | 3.3607 | 3.3526 | 1.0352 | 10.6386 | 14.1242 | 14.7236 | 11.0659 | -0.0002 | -0.0026 | 0.0007 | 0.0041 | 0.0009 | -0.0005 | 0.0253 | -0.0138 | 0.0073 | -360.1311 | 17.4582 | -360.4973 | 17.8011 | -360.845 | 18.1194 | -360.9066 | 17.5465 | -352.7983 | 18.7292 | -352.7706 | 16.7848
11:51 | 1856 | 24.8158 | 195.7925 | 437.4825 | 443.8119 | -20.7167 | -47.1655 | 3.5752 | 1.4795 | -5.4726 | -5.8263 | -2.0961 | -3.5107 | 4.0893 | -2.697 | 0.5902 | 0.6309 | 0.953 | 0.7039 | -131.1336 | -5.6844 | 1.1349 | -0.1763 | -7.0772 | -5.8235 | 0.9643 |  | -1.478 | -2.6141 | 4.0051 | 3.3617 | 3.3495 | 1.0348 | 10.6826 | 14.1563 | 14.7545 | 11.0352 | 0 | -0.0026 | 0.0006 | 0.0037 | 0.0003 | -0.0005 | 0.0011 | -0.0001 | -0.0059 | -360.1681 | 17.4562 | -360.5219 | 17.8237 | -360.882 | 18.1132 | -360.9435 | 17.5876 | -352.7798 | 18.7395 | -352.7952 | 16.7971
11:51 | 1857 | 24.718 | 195.7663 | 437.4094 | 443.8313 | -20.6599 | -47.2143 | 3.6366 | 1.5557 | -5.4778 | -5.7384 | -2.0392 | -3.4008 | 4.0965 | -2.6396 | 0.5899 | 0.6306 | 0.9521 | 0.7032 | -131.0144 | -5.5004 | 1.3362 | -0.1609 | -7.1151 | -5.7411 | 1.0102 |  | -1.4736 | -2.5718 | 4.0055 | 3.3639 | 3.3519 | 1.0365 | 10.6146 | 14.0934 | 14.7111 | 11.0262 | 0.0002 | -0.0032 | 0.0008 | 0.0036 | 0.0008 | -0.0008 | -0.0008 | -0.0111 | -0.0135 | -360.2204 | 17.487 | -360.5189 | 17.7929 | -360.845 | 18.0947 | -360.8943 | 17.5629 | -352.749 | 18.7538 | -352.7767 | 16.7745
11:51 | 1858 | 24.7334 | 195.7208 | 437.4482 | 443.8936 | -20.561 | -47.232 | 3.6061 | 1.4796 | -5.5382 | -5.8122 | -2.0432 | -3.4813 | 4.1196 | -2.6271 | 0.5904 | 0.6331 | 0.9534 | 0.7033 | -131.0916 | -5.5402 | 1.2706 | -0.1519 | -7.0703 | -5.7418 | 1.0113 |  | -1.4488 | -2.5162 | 4.0061 | 3.3638 | 3.3516 | 1.0367 | 10.6641 | 14.1262 | 14.7068 | 11.0283 | 0.0001 | -0.003 | 0.0009 | 0.0033 | 0.0006 | -0.0011 | 0.0145 | -0.0095 | -0.0061 | -360.1865 | 17.4788 | -360.5435 | 17.8114 | -360.885 | 18.0927 | -360.8912 | 17.565 | -352.7737 | 18.7518 | -352.7829 | 16.8032
11:51 | 1859 | 24.7106 | 195.6582 | 437.3091 | 443.784 | -20.5939 | -47.3019 | 3.5567 | 1.436 | -5.4866 | -5.8077 | -2.029 | -3.377 | 4.1727 | -2.5926 | 0.59 | 0.6333 | 0.9519 | 0.7036 | -131.156 | -5.6026 | 1.2342 | -0.1864 | -7.1546 | -5.741 | 0.9943 |  | -1.5218 | -2.6856 | 4.0069 | 3.3605 | 3.3512 | 1.0381 | 10.6562 | 14.1061 | 14.7125 | 11.0331 | -0.0007 | -0.0028 | 0.0005 | 0.0035 | 0.0001 | -0.0007 | 0.0031 | -0.0094 | -0.0128 | -360.1835 | 17.4705 | -360.5681 | 17.8134 | -360.8697 | 18.1194 | -360.9404 | 17.5609 | -352.7767 | 18.7395 | -352.7798 | 16.793
11:51 | 1860 | 24.7745 | 195.7716 | 437.2938 | 443.9159 | -20.5824 | -47.0958 | 3.6532 | 1.4757 | -5.4004 | -5.8172 | -2.0472 | -3.4378 | 4.1504 | -2.6442 | 0.5908 | 0.6341 | 0.9534 | 0.7036 | -131.0756 | -5.5325 | 1.2798 | -0.3397 | -7.292 | -5.8109 | 0.9036 |  | -1.4838 | -2.6129 | 4.0039 | 3.3636 | 3.3517 | 1.0371 | 10.6388 | 14.0773 | 14.7078 | 11.0038 | -0.0004 | -0.0029 | 0.0012 | 0.004 | 0.0011 | -0.0009 | 0.0067 | -0.0139 | -0.0003 | -360.1711 | 17.45 | -360.4789 | 17.797 | -360.8512 | 18.0947 | -360.9127 | 17.5753 | -352.7614 | 18.721 | -352.7429 | 16.7807
11:51 | 1861 | 24.8348 | 195.79 | 437.3114 | 443.8696 | -20.5196 | -47.0043 | 3.7785 | 1.5459 | -5.3318 | -5.7818 | -1.9751 | -3.4588 | 4.232 | -2.7071 | 0.5888 | 0.6338 | 0.9536 | 0.7028 | -131.0834 | -5.4609 | 1.2206 | -0.219 | -7.2874 | -5.7931 | 0.9051 |  | -1.5046 | -2.6654 | 4.0063 | 3.3637 | 3.3512 | 1.0365 | 10.6398 | 14.1251 | 14.6765 | 11.0157 | 0.0003 | -0.0028 | 0.0007 | 0.0039 | 0.0005 | -0.0003 | 0.0168 | 0.0003 | 0.0036 | -360.2111 | 17.4829 | -360.5527 | 17.8032 | -360.8697 | 18.1132 | -360.9558 | 17.5855 | -352.8044 | 18.762 | -352.8044 | 16.7766
11:51 | 1862 | 24.9046 | 195.9089 | 437.3593 | 443.9334 | -20.5098 | -46.9661 | 3.7903 | 1.5601 | -5.4264 | -5.9176 | -1.9375 | -3.4698 | 4.1329 | -2.7322 | 0.5905 | 0.6336 | 0.9518 | 0.7035 | -131.1655 | -5.4829 | 1.254 | -0.3475 | -7.2786 | -5.8489 | 0.9301 |  | -1.4699 | -2.6697 | 4.0052 | 3.3642 | 3.3513 | 1.0366 | 10.6342 | 14.1015 | 14.7197 | 11.0342 | 0.0001 | -0.003 | 0.0005 | 0.004 | 0.0009 | -0.0007 | 0.0145 | -0.0062 | 0.0024 | -360.1988 | 17.4767 | -360.5466 | 17.8114 | -360.8727 | 18.0886 | -360.8912 | 17.5609 | -352.7644 | 18.7292 | -352.7829 | 16.7827
11:51 | 1863 | 24.8319 | 195.8512 | 437.3657 | 443.8592 | -20.5898 | -47.0278 | 3.7433 | 1.5604 | -5.3071 | -5.8837 | -1.9542 | -3.4829 | 4.1365 | -2.667 | 0.5893 | 0.6329 | 0.9515 | 0.7027 | -131.0306 | -5.5307 | 1.2056 | -0.3581 | -7.3621 | -5.8376 | 0.8638 |  | -1.549 | -2.6512 | 4.0059 | 3.3646 | 3.3529 | 1.0381 | 10.6445 | 14.1065 | 14.6983 | 11.032 | 0.0001 | -0.0024 | 0.0007 | 0.0043 | 0.0006 | -0.0001 | 0.02 | -0.0068 | 0.0071 | -360.1281 | 17.4685 | -360.5558 | 17.8093 | -360.8912 | 18.1112 | -360.9158 | 17.5629 | -352.749 | 18.7415 | -352.8075 | 16.8074
11:51 | 1864 | 24.9132 | 195.7989 | 437.4988 | 443.9379 | -20.6526 | -47.059 | 3.6182 | 1.5172 | -5.4445 | -5.9084 | -1.9865 | -3.4222 | 4.1928 | -2.584 | 0.5896 | 0.6358 | 0.9551 | 0.7039 | -131.0533 | -5.5566 | 1.2579 | -0.2878 | -7.3979 | -5.8197 | 0.8935 |  | -1.5418 | -2.6693 | 4.005 | 3.362 | 3.3522 | 1.0371 | 10.648 | 14.1331 | 14.7361 | 11.0298 | -0.0004 | -0.0028 | 0.0006 | 0.0038 | 0.0011 | -0.0003 | -0.0039 | -0.0142 | -0.0215 | -360.1988 | 17.4644 | -360.5035 | 17.8093 | -360.9127 | 18.1194 | -360.9343 | 17.5691 | -352.786 | 18.7333 | -352.7767 | 16.7909
11:51 | 1865 | 24.9219 | 195.8073 | 437.557 | 443.9612 | -20.6034 | -47.1122 | 3.6626 | 1.5542 | -5.391 | -5.8962 | -1.976 | -3.3982 | 4.2257 | -2.635 | 0.5906 | 0.6333 | 0.9521 | 0.7033 | -131.0895 | -5.6691 | 1.2468 | -0.5296 | -7.3063 | -5.908 | 0.8945 |  | -1.4741 | -2.6584 | 4.0062 | 3.3659 | 3.353 | 1.0368 | 10.6111 | 14.1073 | 14.6676 | 11.0226 | 0.0001 | -0.0025 | 0.0007 | 0.0039 | 0.0008 | -0.0005 | 0.0202 | -0.0136 | 0.015 | -360.1773 | 17.4788 | -360.525 | 17.7847 | -360.8174 | 18.0824 | -360.922 | 17.5609 | -352.7275 | 18.7353 | -352.7767 | 16.7745
11:51 | 1866 | 24.8943 | 195.8486 | 437.4504 | 443.9751 | -20.5483 | -47.0264 | 3.7014 | 1.5512 | -5.3694 | -5.834 | -1.9415 | -3.4392 | 4.2151 | -2.6891 | 0.589 | 0.6333 | 0.951 | 0.7058 | -131.0077 | -5.6883 | 1.3251 | -0.4728 | -7.245 | -5.7656 | 0.9042 |  | -1.4948 | -2.5922 | 4.0062 | 3.3644 | 3.3507 | 1.0363 | 10.6042 | 14.0713 | 14.6478 | 10.9988 | 0.0002 | -0.003 | 0.0009 | 0.0037 | 0.0007 | -0.0006 | 0.0124 | 0.0015 | -0.0002 | -360.1927 | 17.4788 | -360.5743 | 17.8134 | -360.885 | 18.1029 | -360.9312 | 17.5794 | -352.8075 | 18.7518 | -352.8198 | 16.8032
11:51 | 1867 | 24.9266 | 195.7594 | 437.4698 | 443.9974 | -20.5669 | -47.0284 | 3.7244 | 1.6166 | -5.2985 | -5.7898 | -1.949 | -3.4818 | 4.2132 | -2.6546 | 0.5894 | 0.6325 | 0.9523 | 0.7048 | -131.0098 | -5.5406 | 1.2843 | -0.4308 | -7.1494 | -5.8188 | 0.9778 |  | -1.4669 | -2.6392 | 4.0058 | 3.3608 | 3.3492 | 1.0376 | 10.6401 | 14.1303 | 14.7128 | 11.0288 | -0.0006 | -0.003 | 0.0009 | 0.0039 | 0.0007 | -0.0008 | -0.0019 | -0.0185 | -0.0281 | -360.1558 | 17.4767 | -360.5404 | 17.7991 | -360.8758 | 18.1214 | -360.9312 | 17.5609 | -352.7398 | 18.7312 | -352.7798 | 16.7868
11:51 | 1868 | 24.8839 | 195.8414 | 437.4716 | 443.9236 | -20.559 | -47.0461 | 3.7475 | 1.4955 | -5.2856 | -5.8703 | -1.9711 | -3.387 | 4.2002 | -2.675 | 0.5893 | 0.6314 | 0.95 | 0.7042 | -131.0035 | -5.6704 | 1.259 | -0.4755 | -7.1382 | -5.7823 | 0.953 |  | -1.4871 | -2.573 | 4.0066 | 3.3621 | 3.3484 | 1.0351 | 10.6168 | 14.1132 | 14.7034 | 11.0338 | -0.0004 | -0.0025 | 0.0011 | 0.004 | 0.0005 | -0.0008 | -0.0048 | 0.0012 | -0.0314 | -360.1804 | 17.45 | -360.5066 | 17.7888 | -360.8604 | 18.1194 | -360.9497 | 17.5773 | -352.786 | 18.7189 | -352.7644 | 16.7827
11:51 | 1869 | 24.911 | 195.888 | 437.5175 | 443.9253 | -20.5964 | -47.0616 | 3.7475 | 1.5791 | -5.3622 | -5.7846 | -1.9367 | -3.363 | 4.1565 | -2.6634 | 0.5882 | 0.6323 | 0.9508 | 0.7047 | -131.0837 | -5.67 | 1.2984 | -0.4649 | -7.0322 | -5.6663 | 1.0356 |  | -1.4776 | -2.586 | 4.0071 | 3.3644 | 3.3546 | 1.0372 | 10.6666 | 14.0935 | 14.6833 | 10.997 | 0.0001 | -0.0031 | 0.001 | 0.004 | 0.0008 | -0.0009 | 0.0294 | -0.0034 | 0.0195 | -360.1588 | 17.4952 | -360.5589 | 17.8032 | -360.882 | 18.1235 | -360.9589 | 17.5753 | -352.7644 | 18.7538 | -352.7921 | 16.7848
11:51 | 1870 | 24.8792 | 195.7767 | 437.5847 | 443.8481 | -20.6147 | -47.084 | 3.7248 | 1.5468 | -5.273 | -5.761 | -1.9069 | -3.3634 | 4.1349 | -2.7725 | 0.5884 | 0.6368 | 0.9529 | 0.7055 | -131.0269 | -5.5979 | 1.1991 | -0.4731 | -7.0551 | -5.7423 | 0.9811 |  | -1.482 | -2.5981 | 4.0046 | 3.364 | 3.3521 | 1.0358 | 10.6756 | 14.1554 | 14.7726 | 11.0623 | 0.0002 | -0.0031 | 0.0006 | 0.0042 | 0.0006 | 0 | -0.0038 | -0.0061 | -0.0226 | -360.1619 | 17.4623 | -360.525 | 17.8155 | -360.8789 | 18.0742 | -360.8912 | 17.5506 | -352.7429 | 18.7271 | -352.8167 | 16.7971
11:51 | 1871 | 24.9563 | 195.7423 | 437.5405 | 443.9107 | -20.5473 | -47.026 | 3.8303 | 1.593 | -5.3216 | -5.7636 | -1.9323 | -3.4317 | 4.1676 | -2.6012 | 0.5897 | 0.6356 | 0.9554 | 0.705 | -130.9801 | -5.5382 | 1.1941 | -0.4854 | -7.0217 | -5.7189 | 0.9912 |  | -1.4256 | -2.6055 | 4.0046 | 3.3632 | 3.3508 | 1.0352 | 10.6446 | 14.1177 | 14.7125 | 11.0331 | 0.0001 | -0.0033 | 0.0005 | 0.0039 | 0.0008 | -0.0012 | 0.0079 | -0.0123 | -0.0096 | -360.165 | 17.4788 | -360.5589 | 17.8093 | -360.9097 | 18.1337 | -360.9312 | 17.5465 | -352.7952 | 18.7497 | -352.8075 | 16.7991
11:51 | 1872 | 24.8471 | 195.777 | 437.5157 | 443.9358 | -20.562 | -47.0042 | 3.8047 | 1.6153 | -5.2346 | -5.7259 | -1.8741 | -3.4073 | 4.1442 | -2.6348 | 0.5901 | 0.6331 | 0.9523 | 0.7038 | -131.0386 | -5.6857 | 1.2057 | -0.6385 | -7.0828 | -5.8202 | 0.949 |  | -1.3615 | -2.5375 | 4.0048 | 3.3665 | 3.3508 | 1.0353 | 10.648 | 14.1387 | 14.7177 | 11.0129 | -0.0006 | -0.0027 | 0.0002 | 0.0033 | 0.0004 | -0.0003 | 0.0064 | 0.0023 | -0.005 | -360.1927 | 17.4685 | -360.525 | 17.7991 | -360.8266 | 18.1194 | -360.962 | 17.5753 | -352.7552 | 18.7374 | -352.7583 | 16.7766
11:51 | 1873 | 24.8468 | 195.7078 | 437.4357 | 443.9175 | -20.5756 | -47.1048 | 3.7584 | 1.6476 | -5.1034 | -5.7361 | -1.8288 | -3.447 | 4.1239 | -2.7098 | 0.5904 | 0.6339 | 0.9547 | 0.7053 | -131.0958 | -5.7376 | 1.1009 | -0.4745 | -7.0982 | -5.8028 | 0.9753 |  | -1.3902 | -2.508 | 4.0051 | 3.3605 | 3.3533 | 1.0362 | 10.6387 | 14.1123 | 14.7041 | 11.0146 | -0.0004 | -0.0025 | 0.0008 | 0.0036 | 0.0006 | -0.0009 | 0.0134 | 0.0043 | -0.0014 | -360.2081 | 17.487 | -360.5281 | 17.7888 | -360.8235 | 18.0947 | -360.9004 | 17.5609 | -352.8075 | 18.762 | -352.7952 | 16.7766
11:51 | 1874 | 25.0009 | 195.9166 | 437.5214 | 443.9586 | -20.4948 | -46.9028 | 3.8403 | 1.6498 | -5.208 | -5.6852 | -1.9462 | -3.4739 | 4.2272 | -2.6421 | 0.5893 | 0.6322 | 0.9559 | 0.7036 | -131.0279 | -5.6747 | 1.2199 | -0.4193 | -6.9158 | -5.7927 | 1.0306 |  | -1.3249 | -2.5251 | 4.0051 | 3.362 | 3.3527 | 1.0364 | 10.6376 | 14.1282 | 14.6948 | 11.0028 | -0.0003 | -0.0035 | 0.0006 | 0.0036 | 0 | -0.0007 | 0.0037 | -0.0012 | -0.0184 | -360.2081 | 17.487 | -360.5589 | 17.8217 | -360.9127 | 18.1153 | -360.9527 | 17.5568 | -352.7706 | 18.7374 | -352.8014 | 16.8053
11:51 | 1875 | 24.9485 | 195.8906 | 437.5285 | 443.9369 | -20.4552 | -46.866 | 3.8863 | 1.5693 | -5.2851 | -5.7298 | -1.8866 | -3.553 | 4.1288 | -2.6811 | 0.5896 | 0.6355 | 0.9552 | 0.7038 | -130.987 | -5.7521 | 1.154 | -0.3676 | -6.9761 | -5.6906 | 1.0559 |  | -1.4509 | -2.6064 | 4.0055 | 3.3658 | 3.353 | 1.0359 | 10.6515 | 14.1018 | 14.716 | 11.0161 | -0.0001 | -0.0031 | 0.0008 | 0.0039 | 0.0006 | -0.0006 | 0.0262 | -0.0129 | 0.0092 | -360.1435 | 17.4459 | -360.4635 | 17.7826 | -360.8543 | 18.1255 | -360.9374 | 17.5527 | -352.7552 | 18.7087 | -352.7121 | 16.7807
11:51 | 1876 | 25.0069 | 195.8875 | 437.5028 | 444.0069 | -20.4036 | -46.9321 | 3.868 | 1.6459 | -5.2662 | -5.6765 | -1.9608 | -3.5077 | 4.1221 | -2.5976 | 0.5884 | 0.6313 | 0.9542 | 0.7043 | -131.0394 | -5.7217 | 1.098 | -0.4851 | -7.092 | -5.8061 | 1.0142 |  | -1.4453 | -2.5313 | 4.0068 | 3.3606 | 3.3502 | 1.0361 | 10.6458 | 14.1246 | 14.6849 | 11.0169 | -0.0006 | -0.0032 | 0.0014 | 0.0041 | 0.0008 | -0.0008 | -0.0026 | -0.0156 | -0.0204 | -360.2142 | 17.4829 | -360.5435 | 17.797 | -360.8574 | 18.1091 | -360.9712 | 17.5855 | -352.7921 | 18.7477 | -352.8014 | 16.7889
11:51 | 1877 | 25.0985 | 195.7974 | 437.5708 | 444.0096 | -20.3885 | -46.9798 | 3.9865 | 1.5997 | -5.1685 | -5.7356 | -1.957 | -3.542 | 4.1628 | -2.5956 | 0.5893 | 0.6346 | 0.9547 | 0.7055 | -131.0668 | -5.7572 | 1.2081 | -0.3697 | -7.0834 | -5.7599 | 1.0493 |  | -1.4013 | -2.5034 | 4.0053 | 3.3651 | 3.3534 | 1.0371 | 10.6676 | 14.1356 | 14.7515 | 11.0547 | -0.0003 | -0.0027 | 0.0009 | 0.0039 | 0.0002 | -0.0006 | 0.0021 | -0.0099 | -0.0151 | -360.1835 | 17.4767 | -360.5312 | 17.8073 | -360.9004 | 18.066 | -360.8881 | 17.5506 | -352.749 | 18.7374 | -352.789 | 16.8053
11:51 | 1878 | 24.9963 | 195.8659 | 437.5267 | 444.0283 | -20.383 | -46.9228 | 3.9399 | 1.6503 | -5.0996 | -5.6956 | -1.868 | -3.5481 | 4.2267 | -2.5261 | 0.5892 | 0.631 | 0.9496 | 0.7034 | -131.1065 | -5.8031 | 1.2345 | -0.2643 | -7.1334 | -5.6214 | 1.0002 |  | -1.4324 | -2.5578 | 4.0065 | 3.3639 | 3.3499 | 1.0371 | 10.6733 | 14.124 | 14.7341 | 11.0431 | -0.0001 | -0.0029 | 0 | 0.0038 | 0.0009 | -0.0005 | 0.0208 | -0.013 | 0.0119 | -360.1527 | 17.4644 | -360.5466 | 17.8093 | -360.922 | 18.1153 | -360.9281 | 17.5506 | -352.746 | 18.7395 | -352.8075 | 16.8115
11:51 | 1879 | 24.9245 | 195.7584 | 437.4428 | 444.0271 | -20.3475 | -46.9449 | 3.9157 | 1.6201 | -5.1432 | -5.6933 | -1.873 | -3.5007 | 4.1997 | -2.5738 | 0.5881 | 0.6281 | 0.9531 | 0.703 | -131.0871 | -5.7039 | 1.2851 | -0.2537 | -7.1208 | -5.6632 | 1.0411 |  | -1.4179 | -2.5953 | 4.005 | 3.361 | 3.3479 | 1.0359 | 10.6723 | 14.1283 | 14.7364 | 11.0024 | 0.0001 | -0.0032 | 0.0004 | 0.0036 | 0 | -0.0007 | 0.0179 | -0.0038 | 0.0088 | -360.1927 | 17.4705 | -360.5127 | 17.7601 | -360.8235 | 18.0824 | -360.9374 | 17.5876 | -352.7675 | 18.7271 | -352.7583 | 16.7704
11:51 | 1880 | 24.9141 | 195.8211 | 437.5248 | 443.9064 | -20.3647 | -46.8948 | 3.7869 | 1.6952 | -5.135 | -5.5896 | -1.9571 | -3.4757 | 4.1765 | -2.5912 | 0.5894 | 0.6333 | 0.9586 | 0.7029 | -130.9756 | -5.5992 | 1.2835 | -0.2372 | -7.1253 | -5.6982 | 1.0651 |  | -1.4274 | -2.5455 | 4.0058 | 3.3625 | 3.355 | 1.0365 | 10.656 | 14.1414 | 14.7225 | 11.0316 | 0 | -0.0026 | 0.0002 | 0.0038 | 0.001 | -0.0005 | 0.0096 | -0.0104 | -0.0085 | -360.2019 | 17.5034 | -360.5773 | 17.7683 | -360.842 | 18.0824 | -360.8789 | 17.5773 | -352.7952 | 18.7723 | -352.8321 | 16.7848
11:51 | 1881 | 24.9353 | 195.8196 | 437.5521 | 443.8859 | -20.3311 | -46.9557 | 3.8496 | 1.6128 | -5.1081 | -5.6488 | -1.8855 | -3.5038 | 4.166 | -2.572 | 0.5897 | 0.6311 | 0.9545 | 0.7049 | -131.0296 | -5.6841 | 1.2924 | -0.343 | -7.1236 | -5.7875 | 0.961 |  | -1.4358 | -2.4917 | 4.005 | 3.3607 | 3.3532 | 1.0362 | 10.6619 | 14.1294 | 14.7367 | 11.0443 | -0.0003 | -0.0028 | 0.0006 | 0.0036 | 0 | -0.0004 | -0.0027 | -0.0101 | -0.0151 | -360.1835 | 17.4685 | -360.5527 | 17.795 | -360.8974 | 18.1091 | -360.9127 | 17.5588 | -352.7552 | 18.7251 | -352.7983 | 16.8074
11:51 | 1882 | 24.9713 | 195.7486 | 437.4978 | 444.0149 | -20.319 | -46.8853 | 3.7801 | 1.5062 | -5.1756 | -5.7863 | -1.9515 | -3.3902 | 4.2151 | -2.5787 | 0.5885 | 0.6302 | 0.9549 | 0.7065 | -131.0899 | -5.6835 | 1.2709 | -0.3986 | -7.1266 | -5.7003 | 1.1235 |  | -1.4027 | -2.544 | 4.0064 | 3.3613 | 3.3507 | 1.0366 | 10.634 | 14.1079 | 14.6892 | 11.0327 | 0.0004 | -0.0025 | 0.0016 | 0.0042 | 0.0012 | -0.0006 | 0.013 | -0.0137 | -0.0151 | -360.1588 | 17.4521 | -360.4666 | 17.7375 | -360.8604 | 18.1296 | -360.962 | 17.5773 | -352.7798 | 18.7066 | -352.746 | 16.7766
11:51 | 1883 | 24.9874 | 195.7712 | 437.4003 | 443.9613 | -20.2935 | -46.8448 | 3.8762 | 1.6073 | -5.1396 | -5.8041 | -2.0035 | -3.4781 | 4.1859 | -2.521 | 0.5899 | 0.6344 | 0.9542 | 0.7062 | -131.1204 | -5.8159 | 1.344 | -0.4351 | -7.1041 | -5.8147 | 1.0452 |  | -1.4121 | -2.5785 | 4.0072 | 3.3642 | 3.3551 | 1.0359 | 10.6087 | 14.1166 | 14.6717 | 11.0201 | 0.0002 | -0.003 | 0.0008 | 0.0038 | 0.0007 | -0.0005 | 0.0128 | -0.0158 | -0.0086 | -360.1835 | 17.487 | -360.525 | 17.7662 | -360.842 | 18.0968 | -360.9497 | 17.5937 | -352.8106 | 18.7312 | -352.7644 | 16.7786
11:51 | 1884 | 24.928 | 195.703 | 437.4951 | 443.9365 | -20.3132 | -47.0424 | 4.0312 | 1.6109 | -5.1884 | -5.7401 | -1.9619 | -3.4368 | 4.1232 | -2.6621 | 0.5897 | 0.6283 | 0.9542 | 0.7069 | -131.1604 | -5.8601 | 1.3634 | -0.5578 | -7.2027 | -5.7866 | 0.9568 |  | -1.4542 | -2.5583 | 4.007 | 3.3631 | 3.3534 | 1.0365 | 10.6296 | 14.1026 | 14.7258 | 11.0068 | 0.0002 | -0.0026 | 0.0008 | 0.0035 | 0.0005 | -0.0008 | 0.0147 | -0.0061 | 0.0029 | -360.1219 | 17.4582 | -360.5466 | 17.797 | -360.9158 | 18.0824 | -360.845 | 17.5342 | -352.6998 | 18.7128 | -352.8137 | 16.8238
11:51 | 1885 | 24.9465 | 195.7716 | 437.6016 | 444.102 | -20.3393 | -46.9571 | 3.873 | 1.5724 | -5.22 | -5.7364 | -2.0324 | -3.5184 | 4.1737 | -2.603 | 0.5895 | 0.6274 | 0.9527 | 0.7069 | -131.2221 | -5.8311 | 1.3171 | -0.6202 | -7.1996 | -5.7443 | 1.0728 |  | -1.4223 | -2.5532 | 4.0079 | 3.3636 | 3.3527 | 1.0361 | 10.641 | 14.1203 | 14.6942 | 11.0345 | -0.0005 | -0.0026 | 0.0003 | 0.0035 | 0.0007 | -0.0007 | 0.0035 | -0.0077 | -0.0224 | -360.1558 | 17.4685 | -360.5466 | 17.795 | -360.9343 | 18.1194 | -360.9374 | 17.565 | -352.7244 | 18.7169 | -352.7737 | 16.8156
11:51 | 1886 | 25.0271 | 195.8476 | 437.7108 | 444.1216 | -20.3586 | -47.0199 | 3.8382 | 1.6272 | -5.1994 | -5.7949 | -1.9949 | -3.4249 | 4.3151 | -2.5445 | 0.5896 | 0.6307 | 0.9545 | 0.7066 | -131.2207 | -5.8005 | 1.2911 | -0.5329 | -7.0668 | -5.8031 | 1.0911 |  | -1.5005 | -2.5792 | 4.0069 | 3.3671 | 3.3526 | 1.0363 | 10.6505 | 14.1233 | 14.6999 | 10.9988 | -0.0005 | -0.003 | -0.0002 | 0.0031 | 0.0003 | -0.0005 | 0.0094 | -0.0099 | -0.0243 | -360.2142 | 17.4664 | -360.5035 | 17.7395 | -360.8235 | 18.0886 | -360.9158 | 17.5753 | -352.7614 | 18.723 | -352.7644 | 16.7745
11:51 | 1887 | 25.0191 | 195.8327 | 437.6585 | 444.0723 | -20.253 | -46.9839 | 3.8919 | 1.6073 | -5.1762 | -5.7703 | -2.0341 | -3.5355 | 4.305 | -2.4539 | 0.5895 | 0.6311 | 0.9539 | 0.7065 | -131.2254 | -5.7763 | 1.3539 | -0.4084 | -6.9832 | -5.6616 | 1.1726 |  | -1.4578 | -2.5889 | 4.0072 | 3.3653 | 3.3537 | 1.0371 | 10.6387 | 14.118 | 14.6799 | 11.0266 | 0.0005 | -0.0028 | 0.0008 | 0.0041 | 0.0012 | -0.0002 | 0.0001 | -0.0037 | -0.0076 | -360.2265 | 17.5013 | -360.5681 | 17.7785 | -360.842 | 18.068 | -360.9158 | 17.5712 | -352.8014 | 18.762 | -352.8537 | 16.8012
11:51 | 1888 | 25.0501 | 195.8158 | 437.6323 | 444.0386 | -20.2867 | -47.0165 | 3.9186 | 1.5963 | -5.2662 | -5.7801 | -2.0057 | -3.5375 | 4.2428 | -2.5105 | 0.5894 | 0.6296 | 0.9541 | 0.706 | -131.142 | -5.7782 | 1.3221 | -0.4125 | -7.041 | -5.7337 | 1.1091 |  | -1.4441 | -2.509 | 4.007 | 3.3635 | 3.3511 | 1.036 | 10.64 | 14.0957 | 14.7197 | 11.0169 | 0.0001 | -0.0031 | 0.0004 | 0.0039 | 0.0003 | -0.0005 | 0.0095 | -0.0081 | -0.0048 | -360.1558 | 17.4644 | -360.5127 | 17.7909 | -360.9035 | 18.1009 | -360.9097 | 17.5527 | -352.749 | 18.7128 | -352.7921 | 16.8156
11:51 | 1889 | 25.0482 | 195.7947 | 437.6878 | 444.0385 | -20.4098 | -47.0777 | 3.8571 | 1.5412 | -5.2326 | -5.726 | -2.0379 | -3.5 | 4.2886 | -2.5174 | 0.589 | 0.6287 | 0.9506 | 0.7048 | -131.1262 | -5.8395 | 1.2251 | -0.2471 | -7.1012 | -5.707 | 1.0528 |  | -1.4651 | -2.4557 | 4.0086 | 3.3647 | 3.3529 | 1.037 | 10.6631 | 14.1017 | 14.6628 | 11.0165 | -0.0004 | -0.0028 | 0.0005 | 0.0036 | 0.0006 | -0.0006 | 0.0111 | 0.0001 | 0.0025 | -360.1281 | 17.4377 | -360.4512 | 17.7518 | -360.8512 | 18.1173 | -360.9558 | 17.5794 | -352.7706 | 18.6963 | -352.6906 | 16.7766
11:51 | 1890 | 25.081 | 195.8742 | 437.639 | 444.0574 | -20.3385 | -47.0025 | 3.9923 | 1.5519 | -5.2441 | -5.6692 | -2.0417 | -3.4453 | 4.2576 | -2.4985 | 0.5889 | 0.6303 | 0.9535 | 0.7057 | -131.099 | -5.8838 | 1.2443 | -0.2377 | -7.081 | -5.6995 | 1.0682 |  | -1.3444 | -2.4527 | 4.0076 | 3.3638 | 3.3515 | 1.0354 | 10.6491 | 14.1227 | 14.6796 | 11.0424 | -0.0001 | -0.0026 | 0.0011 | 0.0039 | 0.0003 | -0.0004 | 0.0038 | 0.0014 | -0.0031 | -360.1865 | 17.4911 | -360.5158 | 17.7744 | -360.8574 | 18.1009 | -360.9681 | 17.5917 | -352.7921 | 18.7271 | -352.7767 | 16.7971
11:51 | 1891 | 25.0764 | 195.8038 | 437.5888 | 444.0354 | -20.3935 | -47.0115 | 3.909 | 1.4854 | -5.3223 | -5.6567 | -2.0232 | -3.5026 | 4.2437 | -2.456 | 0.5886 | 0.6309 | 0.9528 | 0.7071 | -131.1477 | -5.7703 | 1.3039 | -0.1767 | -7.0603 | -5.5953 | 1.137 |  | -1.3689 | -2.4515 | 4.0085 | 3.3607 | 3.3533 | 1.0359 | 10.6642 | 14.1492 | 14.7347 | 11.0461 | -0.0002 | -0.0031 | 0.0006 | 0.0038 | 0.0007 | -0.0007 | 0.011 | -0.0063 | 0.013 | -360.1496 | 17.4664 | -360.5589 | 17.8011 | -360.8974 | 18.0742 | -360.8789 | 17.5424 | -352.7121 | 18.7189 | -352.8044 | 16.8135
11:51 | 1892 | 25.1052 | 195.8738 | 437.5701 | 444.0785 | -20.348 | -46.8627 | 3.982 | 1.6206 | -5.256 | -5.5363 | -1.9572 | -3.4871 | 4.193 | -2.525 | 0.5892 | 0.6293 | 0.9515 | 0.7057 | -131.0644 | -5.8196 | 1.3383 | -0.2648 | -7.1257 | -5.6827 | 1.0415 |  | -1.4312 | -2.5459 | 4.0079 | 3.3631 | 3.3533 | 1.0367 | 10.6191 | 14.0981 | 14.6877 | 11.0075 | 0.0002 | -0.0029 | 0.0008 | 0.0037 | 0.0007 | -0.0007 | -0.0075 | -0.0097 | -0.03 | -360.1927 | 17.4685 | -360.525 | 17.795 | -360.922 | 18.1255 | -360.922 | 17.5671 | -352.7583 | 18.7169 | -352.7798 | 16.832
11:51 | 1893 | 25.1094 | 195.85 | 437.617 | 444.0513 | -20.3647 | -46.9154 | 3.947 | 1.6521 | -5.2132 | -5.6543 | -1.9615 | -3.4087 | 4.2599 | -2.4843 | 0.5893 | 0.6247 | 0.9514 | 0.7073 | -131.0147 | -5.8624 | 1.2902 | -0.2052 | -7.1398 | -5.7228 | 1.0945 |  | -1.4316 | -2.5781 | 4.0077 | 3.3604 | 3.3496 | 1.036 | 10.6861 | 14.1541 | 14.7644 | 11.0789 | -0.0001 | -0.0029 | 0.0007 | 0.0037 | 0.0004 | -0.0012 | 0.0052 | -0.0017 | -0.003 | -360.1711 | 17.4726 | -360.5096 | 17.758 | -360.8266 | 18.0845 | -360.9466 | 17.5896 | -352.7644 | 18.7251 | -352.7552 | 16.7848
11:51 | 1894 | 25.1591 | 195.9949 | 437.6362 | 444.1088 | -20.3313 | -46.8482 | 3.9704 | 1.6448 | -5.2092 | -5.696 | -1.8655 | -3.4278 | 4.2975 | -2.5226 | 0.5901 | 0.6291 | 0.9544 | 0.7055 | -131.0162 | -5.8838 | 1.2759 | -0.1601 | -7.1552 | -5.6534 | 1.1358 |  | -1.5219 | -2.6308 | 4.0078 | 3.3639 | 3.3544 | 1.0345 | 10.663 | 14.154 | 14.7344 | 11.0735 | -0.0004 | -0.0029 | 0.0003 | 0.0035 | 0.0009 | -0.0004 | 0.0037 | -0.0151 | -0.0015 | -360.2019 | 17.4788 | -360.5281 | 17.7867 | -360.8604 | 18.0639 | -360.8789 | 17.5732 | -352.7921 | 18.7477 | -352.8229 | 16.8156
11:51 | 1895 | 25.1415 | 195.9033 | 437.5308 | 444.0729 | -20.2964 | -46.8651 | 4.049 | 1.6026 | -5.2839 | -5.7528 | -1.9876 | -3.4077 | 4.2558 | -2.489 | 0.5888 | 0.6296 | 0.9535 | 0.7072 | -130.9588 | -5.7935 | 1.3459 | -0.219 | -7.1307 | -5.6498 | 1.171 |  | -1.4962 | -2.6393 | 4.0068 | 3.361 | 3.3484 | 1.0349 | 10.67 | 14.1435 | 14.6884 | 11.0461 | -0.0002 | -0.0031 | 0.0006 | 0.0042 | 0.0007 | -0.0003 | 0.0062 | -0.0156 | 0.0034 | -360.1619 | 17.4562 | -360.5219 | 17.7847 | -360.8912 | 18.1132 | -360.9589 | 17.5609 | -352.7183 | 18.7148 | -352.7798 | 16.8053
11:51 | 1896 | 25.2007 | 195.8625 | 437.5261 | 444.0242 | -20.2979 | -46.8181 | 4.0955 | 1.5818 | -5.3133 | -5.7304 | -1.9709 | -3.4357 | 4.2381 | -2.5557 | 0.5884 | 0.6307 | 0.9542 | 0.7076 | -131.031 | -5.9202 | 1.2738 | -0.1569 | -6.9997 | -5.66 | 1.1011 |  | -1.4754 | -2.6042 | 4.0069 | 3.362 | 3.3512 | 1.036 | 10.6688 | 14.1482 | 14.717 | 11.0562 | -0.0001 | -0.0031 | 0.0007 | 0.0044 | 0.0008 | -0.0008 | 0.0267 | -0.0015 | 0.003 | -360.1865 | 17.4562 | -360.4819 | 17.7498 | -360.8297 | 18.1071 | -360.9589 | 17.5855 | -352.7644 | 18.7066 | -352.7121 | 16.7683
11:51 | 1897 | 25.2195 | 195.7669 | 437.5761 | 444.1185 | -20.3153 | -46.8058 | 4.1154 | 1.5732 | -5.3225 | -5.6171 | -1.9652 | -3.355 | 4.33 | -2.5088 | 0.5897 | 0.6295 | 0.9562 | 0.7076 | -130.9478 | -5.8826 | 1.328 | -0.1269 | -6.9993 | -5.6461 | 1.1414 |  | -1.4283 | -2.5171 | 4.0074 | 3.3612 | 3.3516 | 1.0363 | 10.6457 | 14.0901 | 14.6802 | 11.0222 | -0.0001 | -0.0033 | 0.0007 | 0.0036 | 0.0005 | 0 | 0.0139 | -0.0078 | -0.0001 | -360.1773 | 17.4911 | -360.5773 | 17.8032 | -360.8881 | 18.0886 | -360.9189 | 17.5773 | -352.786 | 18.7456 | -352.8167 | 16.8217
11:51 | 1898 | 25.1624 | 195.7764 | 437.6056 | 444.0502 | -20.3207 | -46.9706 | 4.0267 | 1.619 | -5.2979 | -5.6749 | -1.9717 | -3.4009 | 4.3377 | -2.4091 | 0.5897 | 0.6296 | 0.9525 | 0.7057 | -130.9168 | -5.7907 | 1.3801 | -0.2049 | -6.9801 | -5.6407 | 1.1187 |  | -1.4994 | -2.5547 | 4.0075 | 3.3607 | 3.3483 | 1.0348 | 10.6596 | 14.1155 | 14.7166 | 11.0075 | -0.0007 | -0.003 | 0.0013 | 0.0038 | 0.0009 | -0.0007 | -0.0023 | 0.0076 | -0.0112 | -360.1435 | 17.4541 | -360.5189 | 17.7826 | -360.9035 | 18.1009 | -360.9035 | 17.5609 | -352.7337 | 18.6922 | -352.7644 | 16.8094
11:51 | 1899 | 25.1734 | 195.7829 | 437.6856 | 444.0816 | -20.3501 | -46.777 | 4.0112 | 1.6723 | -5.2907 | -5.7892 | -1.915 | -3.3222 | 4.2838 | -2.4672 | 0.5894 | 0.6288 | 0.9493 | 0.7052 | -130.9088 | -5.8084 | 1.314 | -0.2834 | -7.085 | -5.7644 | 1.0349 |  | -1.4134 | -2.5258 | 4.0084 | 3.3614 | 3.3516 | 1.0356 | 10.671 | 14.1334 | 14.7498 | 11.0522 | 0.0002 | -0.0025 | 0.0011 | 0.0039 | 0.0008 | -0.0003 | 0.0036 | -0.0106 | -0.0026 | -360.1742 | 17.4747 | -360.5189 | 17.758 | -360.8297 | 18.0947 | -360.9127 | 17.5753 | -352.7583 | 18.7333 | -352.7675 | 16.7848
11:51 | 1900 | 25.2065 | 195.7878 | 437.6777 | 444.1089 | -20.3516 | -46.8308 | 4.0188 | 1.6968 | -5.2413 | -5.6788 | -1.9136 | -3.3454 | 4.3379 | -2.4436 | 0.589 | 0.6289 | 0.9578 | 0.705 | -130.9106 | -5.8517 | 1.3266 | -0.301 | -6.997 | -5.6521 | 1.097 |  | -1.3998 | -2.456 | 4.0089 | 3.3609 | 3.352 | 1.0354 | 10.6481 | 14.127 | 14.7224 | 11.0363 | -0.0001 | -0.0032 | 0.0009 | 0.0038 | 0.0005 | -0.0009 | 0.0045 | 0.0057 | -0.019 | -360.1804 | 17.4849 | -360.5373 | 17.7888 | -360.8789 | 18.0947 | -360.9312 | 17.5835 | -352.7614 | 18.7415 | -352.8106 | 16.8176
11:51 | 1901 | 25.1649 | 195.7788 | 437.709 | 444.1491 | -20.279 | -46.8893 | 4.0077 | 1.6545 | -5.2159 | -5.6283 | -1.9206 | -3.2692 | 4.4102 | -2.3848 | 0.5895 | 0.6314 | 0.9552 | 0.7054 | -130.8962 | -5.8621 | 1.278 | -0.2563 | -7.0519 | -5.7804 | 1.0307 |  | -1.4496 | -2.5203 | 4.0083 | 3.3629 | 3.3536 | 1.0359 | 10.6653 | 14.1389 | 14.6898 | 11.0587 | 0.0001 | -0.0031 | 0.001 | 0.004 | 0.0011 | -0.0005 | 0.0155 | -0.0123 | 0.0016 | -360.1773 | 17.4377 | -360.5096 | 17.7724 | -360.845 | 18.0988 | -360.9189 | 17.565 | -352.7367 | 18.7169 | -352.7398 | 16.8094
11:51 | 1902 | 25.1861 | 195.8306 | 437.6496 | 444.1504 | -20.302 | -46.8566 | 3.938 | 1.7339 | -5.1807 | -5.6766 | -1.8456 | -3.3824 | 4.2952 | -2.3887 | 0.5888 | 0.6312 | 0.9579 | 0.7064 | -130.8568 | -5.8766 | 1.3794 | -0.351 | -7.0203 | -5.632 | 0.9992 |  | -1.4322 | -2.539 | 4.0073 | 3.357 | 3.3488 | 1.0361 | 10.6549 | 14.111 | 14.7075 | 11.0082 | -0.0003 | -0.0029 | 0.0004 | 0.0038 | 0.0007 | -0.0005 | 0.0192 | -0.0041 | 0.0008 | -360.1835 | 17.4911 | -360.5373 | 17.7662 | -360.885 | 18.1071 | -360.9466 | 17.5896 | -352.7675 | 18.7312 | -352.7767 | 16.7909
11:51 | 1903 | 25.1776 | 195.8105 | 437.6101 | 444.1252 | -20.2878 | -46.8864 | 4.0416 | 1.6897 | -5.2421 | -5.7215 | -1.9069 | -3.2895 | 4.3986 | -2.3084 | 0.59 | 0.6339 | 0.956 | 0.7062 | -130.9237 | -5.9523 | 1.3957 | -0.1813 | -7.0673 | -5.8785 | 1.0767 |  | -1.4654 | -2.517 | 4.0082 | 3.3597 | 3.3467 | 1.0349 | 10.6491 | 14.1227 | 14.6969 | 11.0193 | -0.0001 | -0.0026 | 0.0006 | 0.004 | 0.0008 | -0.0007 | 0.0223 | 0.0037 | 0.0041 | -360.2173 | 17.4541 | -360.5127 | 17.7662 | -360.8327 | 18.0845 | -360.9004 | 17.5609 | -352.749 | 18.7087 | -352.7675 | 16.8094
11:51 | 1904 | 25.1425 | 195.9816 | 437.7393 | 444.1724 | -20.3734 | -46.872 | 3.9255 | 1.6897 | -5.2101 | -5.6505 | -1.9092 | -3.3778 | 4.3923 | -2.2966 | 0.5898 | 0.6304 | 0.9556 | 0.706 | -130.8697 | -5.8941 | 1.2712 | -0.2294 | -6.9728 | -5.6523 | 1.0994 |  | -1.3911 | -2.5197 | 4.0096 | 3.3628 | 3.3519 | 1.0361 | 10.6434 | 14.1226 | 14.7075 | 10.9908 | 0.0005 | -0.0029 | 0.0005 | 0.0036 | 0.0004 | -0.0007 | 0.0077 | -0.0026 | 0.0051 | -360.2235 | 17.4767 | -360.5404 | 17.7847 | -360.8881 | 18.1112 | -360.9281 | 17.5773 | -352.7614 | 18.7107 | -352.8044 | 16.834
11:51 | 1905 | 25.1037 | 195.8764 | 437.7119 | 444.1547 | -20.3927 | -46.8844 | 3.929 | 1.7391 | -5.1849 | -5.7172 | -1.8921 | -3.4072 | 4.318 | -2.3576 | 0.59 | 0.628 | 0.9516 | 0.7054 | -130.8102 | -5.8096 | 1.3123 | -0.1769 | -6.9856 | -5.7007 | 1.1779 |  | -1.4319 | -2.4648 | 4.0096 | 3.3615 | 3.3513 | 1.0344 | 10.6654 | 14.0981 | 14.7224 | 11.0248 | -0.0003 | -0.0033 | 0.0006 | 0.0037 | 0.0007 | -0.0007 | 0.0074 | -0.0081 | -0.0262 | -360.2019 | 17.4623 | -360.5219 | 17.758 | -360.8574 | 18.0886 | -360.9127 | 17.5629 | -352.7275 | 18.7107 | -352.749 | 16.8074
11:51 | 1906 | 25.1981 | 195.9341 | 437.772 | 444.2711 | -20.407 | -47.0388 | 3.9581 | 1.6873 | -5.2555 | -5.7018 | -1.8957 | -3.3128 | 4.3314 | -2.3529 | 0.59 | 0.6275 | 0.9539 | 0.7052 | -130.8456 | -5.8552 | 1.3363 | -0.2692 | -6.9832 | -5.6826 | 1.1597 |  | -1.4266 | -2.5502 | 4.0107 | 3.363 | 3.3499 | 1.0351 | 10.6469 | 14.126 | 14.6816 | 11.0176 | 0.0002 | -0.0027 | 0.0008 | 0.0036 | 0.0003 | -0.0003 | 0.0191 | -0.0037 | -0.0277 | -360.1835 | 17.4582 | -360.5343 | 17.7662 | -360.8389 | 18.0947 | -360.922 | 17.5732 | -352.7275 | 18.7148 | -352.7675 | 16.8032
11:51 | 1907 | 25.2176 | 195.9518 | 437.753 | 444.1485 | -20.3823 | -47.0496 | 3.9655 | 1.7949 | -5.1784 | -5.6621 | -1.8473 | -3.2737 | 4.364 | -2.3646 | 0.5887 | 0.6303 | 0.953 | 0.7066 | -130.8798 | -5.9012 | 1.3709 | -0.2034 | -6.9677 | -5.7455 | 1.0928 |  | -1.391 | -2.6722 | 4.0091 | 3.3618 | 3.3527 | 1.0342 | 10.6401 | 14.1129 | 14.6897 | 11.0288 | -0.0001 | -0.0029 | 0.0006 | 0.0031 | 0.0003 | -0.0012 | -0.006 | -0.0002 | -0.0288 | -360.1681 | 17.4726 | -360.5558 | 17.7826 | -360.8512 | 18.1009 | -360.9374 | 17.5753 | -352.7367 | 18.7312 | -352.8106 | 16.8156
11:52 | 1908 | 25.1789 | 195.9012 | 437.7093 | 444.191 | -20.3891 | -46.9522 | 4.0262 | 1.7505 | -5.1945 | -5.6611 | -1.9095 | -3.3943 | 4.3494 | -2.419 | 0.5905 | 0.6333 | 0.9569 | 0.7063 | -130.936 | -5.8652 | 1.3684 | -0.1983 | -7.0054 | -5.7209 | 1.1666 |  | -1.3878 | -2.6773 | 4.0089 | 3.3628 | 3.3549 | 1.035 | 10.6549 | 14.111 | 14.6901 | 11.0082 | -0.0007 | -0.0023 | 0.0004 | 0.0034 | -0.0001 | -0.0007 | 0.0107 | -0.023 | -0.0101 | -360.1465 | 17.4582 | -360.5189 | 17.7621 | -360.845 | 18.0824 | -360.9035 | 17.5691 | -352.7275 | 18.7251 | -352.7583 | 16.8115
11:52 | 1909 | 25.2721 | 196.0438 | 437.6502 | 444.2344 | -20.3656 | -46.8712 | 4.0348 | 1.7299 | -5.1437 | -5.5933 | -1.816 | -3.3084 | 4.3407 | -2.378 | 0.5882 | 0.6316 | 0.9584 | 0.7049 | -130.9177 | -5.8183 | 1.2449 | -0.2867 | -7.087 | -5.6872 | 1.0986 |  | -1.354 | -2.7333 | 4.0083 | 3.3645 | 3.3562 | 1.0356 | 10.6401 | 14.1245 | 14.7128 | 11.0346 | 0 | -0.0032 | 0.0004 | 0.0035 | 0.0014 | -0.0006 | 0.009 | -0.016 | 0.0038 | -360.2081 | 17.4767 | -360.5373 | 17.7744 | -360.8727 | 18.0968 | -360.9312 | 17.5917 | -352.7798 | 18.7312 | -352.7737 | 16.8074
11:52 | 1910 | 25.2988 | 196.0554 | 437.7796 | 444.1698 | -20.32 | -47.0346 | 4.0421 | 1.6863 | -5.0441 | -5.6267 | -1.8672 | -3.3262 | 4.3342 | -2.3338 | 0.5894 | 0.6336 | 0.9559 | 0.707 | -130.8903 | -5.841 | 1.167 | -0.2087 | -6.9515 | -5.7175 | 1.1741 |  | -1.4061 | -2.678 | 4.0095 | 3.3614 | 3.3534 | 1.0351 | 10.6354 | 14.1143 | 14.6863 | 11.0237 | -0.0005 | -0.0029 | 0.0006 | 0.0038 | 0.0006 | -0.0002 | 0.0297 | 0.0061 | -0.0033 | -360.1711 | 17.4521 | -360.5158 | 17.7724 | -360.845 | 18.0865 | -360.882 | 17.5588 | -352.7429 | 18.723 | -352.7337 | 16.8156
11:52 | 1911 | 25.2967 | 195.9259 | 437.6776 | 444.1753 | -20.3374 | -47.0076 | 4.0986 | 1.5705 | -5.0853 | -5.6724 | -1.934 | -3.2604 | 4.4045 | -2.3767 | 0.5899 | 0.6308 | 0.9526 | 0.7053 | -130.9324 | -5.8758 | 1.2569 | -0.2166 | -6.9576 | -5.6844 | 1.0918 |  | -1.3899 | -2.663 | 4.008 | 3.365 | 3.3534 | 1.0338 | 10.6619 | 14.1178 | 14.6962 | 10.9923 | -0.0003 | -0.0027 | 0.0008 | 0.0041 | 0.0005 | -0.0005 | 0.0022 | -0.0084 | 0.002 | -360.1188 | 17.4623 | -360.5219 | 17.7744 | -360.8666 | 18.1173 | -360.9281 | 17.5794 | -352.749 | 18.7087 | -352.8044 | 16.834
11:52 | 1912 | 25.2568 | 196.0621 | 437.7549 | 444.1964 | -20.2982 | -47.0639 | 4.0835 | 1.6384 | -5.0964 | -5.6371 | -1.9257 | -3.3017 | 4.3802 | -2.3607 | 0.5902 | 0.6305 | 0.9534 | 0.7063 | -130.9493 | -5.8917 | 1.402 | -0.2247 | -6.9508 | -5.7106 | 1.0791 |  | -1.3758 | -2.6793 | 4.0077 | 3.3614 | 3.3508 | 1.0336 | 10.6388 | 14.1409 | 14.7251 | 11.0269 | -0.0006 | -0.003 | 0.0006 | 0.004 | 0.0008 | -0.0006 | 0.0066 | -0.0132 | 0.0084 | -360.1773 | 17.4603 | -360.5004 | 17.7642 | -360.8481 | 18.0906 | -360.9097 | 17.5671 | -352.7429 | 18.7128 | -352.7306 | 16.8197
11:52 | 1913 | 25.2218 | 196.0077 | 437.7214 | 444.2406 | -20.3443 | -47.0678 | 4.0021 | 1.6417 | -5.0798 | -5.6602 | -1.9403 | -3.412 | 4.39 | -2.3812 | 0.5888 | 0.6286 | 0.9546 | 0.7068 | -130.9396 | -5.955 | 1.4341 | -0.2073 | -6.9437 | -5.7447 | 1.0503 |  | -1.3372 | -2.6529 | 4.0089 | 3.3572 | 3.3534 | 1.0348 | 10.6837 | 14.123 | 14.728 | 11.059 | 0.0003 | -0.0032 | 0.0006 | 0.0036 | 0.0007 | 0.0001 | 0.01 | -0.0111 | -0.0158 | -360.1804 | 17.4808 | -360.5404 | 17.7724 | -360.8543 | 18.0845 | -360.9097 | 17.5671 | -352.8044 | 18.7395 | -352.7706 | 16.8217
11:52 | 1914 | 25.3203 | 195.9985 | 437.7656 | 444.2657 | -20.3805 | -46.9989 | 4.0379 | 1.6534 | -5.1367 | -5.6865 | -1.9403 | -3.2493 | 4.4691 | -2.3329 | 0.5901 | 0.6294 | 0.9548 | 0.7065 | -130.9358 | -6.0387 | 1.405 | -0.1152 | -6.9443 | -5.7792 | 1.2223 |  | -1.3564 | -2.6058 | 4.01 | 3.3627 | 3.3558 | 1.035 | 10.6725 | 14.1048 | 14.6812 | 11.0324 | -0.0003 | -0.0036 | 0.0008 | 0.0035 | 0.0004 | -0.0009 | 0 | -0.0006 | -0.0121 | -360.1711 | 17.4747 | -360.5527 | 17.7765 | -360.8697 | 18.0927 | -360.9097 | 17.5712 | -352.7121 | 18.7251 | -352.7829 | 16.8238
11:52 | 1915 | 25.3036 | 195.9566 | 437.6805 | 444.2178 | -20.4594 | -46.988 | 3.9703 | 1.6789 | -5.0894 | -5.6149 | -1.8874 | -3.27 | 4.377 | -2.2449 | 0.5897 | 0.6286 | 0.9567 | 0.7077 | -130.9783 | -6.0627 | 1.3543 | -0.2867 | -6.9499 | -5.7424 | 1.163 |  | -1.2608 | -2.5528 | 4.01 | 3.3648 | 3.3547 | 1.0358 | 10.6722 | 14.1344 | 14.7443 | 11.0247 | -0.0002 | -0.0026 | 0.0008 | 0.0035 | 0.0004 | -0.0002 | 0.0136 | 0.0073 | 0.0114 | -360.1865 | 17.4521 | -360.4973 | 17.7662 | -360.8543 | 18.0865 | -360.9127 | 17.5855 | -352.7337 | 18.723 | -352.7644 | 16.8176
11:52 | 1916 | 25.3185 | 195.9256 | 437.7652 | 444.2539 | -20.5115 | -47.0752 | 3.9258 | 1.6062 | -5.0926 | -5.6025 | -1.9006 | -3.4185 | 4.4153 | -2.3433 | 0.5889 | 0.6293 | 0.9592 | 0.7075 | -130.8955 | -5.9549 | 1.3651 | -0.4606 | -6.9242 | -5.7683 | 1.1577 |  | -1.3193 | -2.6551 | 4.0084 | 3.3625 | 3.3523 | 1.0345 | 10.6676 | 14.147 | 14.7215 | 11.0262 | 0.0001 | -0.0026 | 0.001 | 0.0034 | 0.0007 | -0.0012 | 0.0014 | -0.0075 | -0.0243 | -360.2173 | 17.4747 | -360.5219 | 17.758 | -360.8481 | 18.0927 | -360.9251 | 17.5896 | -352.7521 | 18.7066 | -352.7675 | 16.8094
11:52 | 1917 | 25.3159 | 195.9791 | 437.815 | 444.2658 | -20.4495 | -47.0915 | 3.9068 | 1.6011 | -5.0768 | -5.704 | -1.8626 | -3.3884 | 4.3855 | -2.3304 | 0.5904 | 0.6303 | 0.9548 | 0.7085 | -130.9016 | -6.0484 | 1.4269 | -0.419 | -6.9877 | -5.7246 | 1.0996 |  | -1.3159 | -2.6354 | 4.0094 | 3.3647 | 3.3529 | 1.0341 | 10.6584 | 14.1607 | 14.7337 | 11.0233 | -0.0001 | -0.0032 | 0.0013 | 0.004 | 0.0003 | -0.0004 | 0.0049 | -0.0063 | -0.0219 | -360.2111 | 17.4664 | -360.5127 | 17.7806 | -360.8297 | 18.0886 | -360.9066 | 17.5712 | -352.7798 | 18.7251 | -352.7583 | 16.8279
11:52 | 1918 | 25.3507 | 195.9742 | 437.7841 | 444.2611 | -20.4064 | -46.9932 | 3.9201 | 1.6208 | -4.9921 | -5.5376 | -1.9393 | -3.3705 | 4.4234 | -2.3186 | 0.5904 | 0.6295 | 0.9555 | 0.7077 | -130.9058 | -6.0216 | 1.4249 | -0.4663 | -7.0203 | -5.7471 | 1.0952 |  | -1.3609 | -2.6764 | 4.0106 | 3.3651 | 3.3537 | 1.0349 | 10.6767 | 14.1451 | 14.7393 | 11.0576 | -0.0002 | -0.003 | 0.0005 | 0.0037 | 0.0011 | -0.0008 | 0.0102 | -0.01 | -0.0101 | -360.1465 | 17.4521 | -360.5712 | 17.7806 | -360.8635 | 18.1009 | -360.9343 | 17.5773 | -352.7398 | 18.6984 | -352.7614 | 16.8217
11:52 | 1919 | 25.366 | 195.9948 | 437.7914 | 444.335 | -20.3819 | -47.0117 | 3.9552 | 1.7613 | -5.0406 | -5.5728 | -1.8929 | -3.348 | 4.4296 | -2.2568 | 0.5889 | 0.6316 | 0.9555 | 0.7078 | -130.9138 | -6.1205 | 1.4047 | -0.4217 | -7.1384 | -5.7084 | 1.0065 |  | -1.3834 | -2.5759 | 4.0132 | 3.3655 | 3.354 | 1.0359 | 10.656 | 14.1297 | 14.7157 | 11.0204 | -0.0004 | -0.0034 | 0.0007 | 0.004 | 0.0011 | -0.0002 | -0.003 | -0.0189 | -0.0097 | -360.1465 | 17.4439 | -360.4912 | 17.7683 | -360.8574 | 18.0906 | -360.9281 | 17.5712 | -352.7767 | 18.7004 | -352.7244 | 16.8299
11:52 | 1920 | 25.3964 | 195.9105 | 437.7666 | 444.338 | -20.4664 | -47.1324 | 3.8749 | 1.7332 | -5.0098 | -5.536 | -1.9066 | -3.3953 | 4.3766 | -2.3634 | 0.5899 | 0.6346 | 0.9577 | 0.7089 | -130.9038 | -6.0745 | 1.3902 | -0.4511 | -7.0868 | -5.7128 | 1.0603 |  | -1.3203 | -2.6039 | 4.0123 | 3.3639 | 3.3547 | 1.0362 | 10.6468 | 14.1145 | 14.7116 | 11.0172 | -0.0009 | -0.0028 | 0.0007 | 0.0043 | 0.0006 | -0.0002 | 0.0076 | -0.0016 | 0.0151 | -360.2173 | 17.4747 | -360.5404 | 17.7765 | -360.8543 | 18.0824 | -360.9374 | 17.5855 | -352.746 | 18.7395 | -352.7921 | 16.8115
11:52 | 1921 | 25.3549 | 195.954 | 437.8308 | 444.2186 | -20.474 | -47.1671 | 3.8859 | 1.746 | -5.0943 | -5.5957 | -1.8634 | -3.3174 | 4.4246 | -2.1905 | 0.59 | 0.6338 | 0.9575 | 0.71 | -130.9516 | -6.0473 | 1.3966 | -0.4636 | -7.0983 | -5.7322 | 0.9545 |  | -1.2825 | -2.6478 | 4.0139 | 3.3624 | 3.3534 | 1.0364 | 10.6619 | 14.1411 | 14.6973 | 11.0266 | 0 | -0.0028 | 0.0008 | 0.0036 | 0.0012 | -0.0004 | -0.0053 | -0.009 | -0.0175 | -360.1619 | 17.4664 | -360.5435 | 17.7806 | -360.842 | 18.066 | -360.8974 | 17.5568 | -352.709 | 18.7189 | -352.7583 | 16.8361
11:52 | 1922 | 25.3402 | 196.0161 | 437.8121 | 444.3337 | -20.3034 | -47.0352 | 4.0358 | 1.7022 | -5.1018 | -5.5771 | -1.8992 | -3.2182 | 4.3691 | -2.1528 | 0.5893 | 0.6311 | 0.9546 | 0.7087 | -130.9465 | -5.972 | 1.321 | -0.5686 | -7.0797 | -5.7813 | 0.9662 |  | -1.2643 | -2.5875 | 4.0126 | 3.3608 | 3.3545 | 1.0349 | 10.6585 | 14.1316 | 14.7037 | 11.0237 | 0.0002 | -0.0034 | 0.0006 | 0.0039 | -0.0002 | -0.0004 | -0.0007 | 0.0113 | -0.0139 | -360.1711 | 17.4685 | -360.5527 | 17.7826 | -360.8727 | 18.1255 | -360.962 | 17.5732 | -352.746 | 18.7128 | -352.7767 | 16.8279
11:52 | 1923 | 25.3217 | 195.8585 | 437.8982 | 444.2239 | -20.3378 | -46.9448 | 4.0227 | 1.7032 | -5.1612 | -5.6419 | -1.9627 | -3.3574 | 4.3657 | -2.1819 | 0.5899 | 0.6301 | 0.9525 | 0.7088 | -130.9359 | -6.0666 | 1.3316 | -0.5143 | -7.0287 | -5.7366 | 0.9866 |  | -1.2803 | -2.6099 | 4.0124 | 3.3631 | 3.3541 | 1.0345 | 10.6329 | 14.089 | 14.6857 | 10.9919 | 0.0003 | -0.0031 | 0.0013 | 0.004 | 0.0003 | -0.0005 | -0.0018 | -0.0049 | -0.0013 | -360.1927 | 17.448 | -360.4819 | 17.7539 | -360.8174 | 18.0721 | -360.9251 | 17.5896 | -352.7429 | 18.7004 | -352.749 | 16.8115
11:52 | 1924 | 25.3909 | 195.9848 | 437.9179 | 444.2842 | -20.2493 | -46.9446 | 4.1401 | 1.7469 | -5.1891 | -5.6121 | -1.9499 | -3.3467 | 4.4223 | -2.243 | 0.5893 | 0.632 | 0.9561 | 0.7094 | -130.8923 | -5.9883 | 1.3822 | -0.3371 | -7.031 | -5.6612 | 1.0848 |  | -1.3324 | -2.5246 | 4.0147 | 3.3641 | 3.3538 | 1.0352 | 10.6689 | 14.1132 | 14.6918 | 10.9991 | -0.0002 | -0.0028 | 0.0008 | 0.0038 | 0.0003 | -0.0007 | 0.0027 | -0.0038 | -0.01 | -360.2111 | 17.487 | -360.5373 | 17.7806 | -360.882 | 18.1029 | -360.9281 | 17.5773 | -352.7829 | 18.7312 | -352.7737 | 16.8176
11:52 | 1925 | 25.3565 | 196.0107 | 437.9778 | 444.3062 | -20.3222 | -47.0133 | 4.0784 | 1.6814 | -5.1726 | -5.5996 | -1.9376 | -3.3688 | 4.3966 | -2.2234 | 0.5887 | 0.6287 | 0.9547 | 0.7088 | -130.9042 | -5.9956 | 1.3537 | -0.179 | -6.9896 | -5.6284 | 1.1424 |  | -1.3833 | -2.5964 | 4.0147 | 3.3619 | 3.3552 | 1.0355 | 10.6745 | 14.1308 | 14.7402 | 11.0446 | 0.0001 | -0.0024 | 0.0011 | 0.004 | 0.0011 | -0.0007 | -0.0044 | 0.0009 | -0.0198 | -360.1281 | 17.4562 | -360.5219 | 17.7785 | -360.8543 | 18.1029 | -360.885 | 17.565 | -352.7183 | 18.6984 | -352.7675 | 16.8176
11:52 | 1926 | 25.3269 | 195.9594 | 437.8352 | 444.2947 | -20.2464 | -46.8956 | 4.0528 | 1.7578 | -5.0439 | -5.5178 | -1.8634 | -3.4295 | 4.3751 | -2.2984 | 0.5898 | 0.6297 | 0.9564 | 0.7082 | -130.9939 | -5.9955 | 1.2444 | -0.223 | -7.0095 | -5.6949 | 1.0154 |  | -1.3689 | -2.593 | 4.0132 | 3.3613 | 3.3504 | 1.0349 | 10.6491 | 14.1227 | 14.7317 | 11.0136 | 0.0001 | -0.003 | 0.0009 | 0.0039 | 0.0004 | -0.0006 | 0.0046 | -0.0092 | -0.0217 | -360.1496 | 17.4644 | -360.525 | 17.7847 | -360.8912 | 18.1214 | -360.922 | 17.5896 | -352.7275 | 18.7128 | -352.7429 | 16.8279
11:52 | 1927 | 25.3309 | 195.8949 | 437.9061 | 444.2693 | -20.2905 | -46.9988 | 4.1123 | 1.758 | -5.1094 | -5.6852 | -1.9391 | -3.4893 | 4.3932 | -2.2697 | 0.5894 | 0.6299 | 0.9547 | 0.7098 | -130.8801 | -5.946 | 1.3624 | -0.2415 | -7.0288 | -5.7057 | 1.0782 |  | -1.376 | -2.5804 | 4.0133 | 3.3642 | 3.3497 | 1.0349 | 10.6758 | 14.126 | 14.7568 | 11.0233 | 0.0002 | -0.0026 | 0.0006 | 0.004 | 0.0008 | -0.0008 | 0.0191 | -0.0007 | -0.0074 | -360.1988 | 17.4664 | -360.5189 | 17.7642 | -360.8235 | 18.0804 | -360.9312 | 17.5732 | -352.7337 | 18.7128 | -352.7552 | 16.8176
11:52 | 1928 | 25.3523 | 195.8882 | 437.8829 | 444.3248 | -20.3723 | -47.097 | 4.022 | 1.7939 | -5.079 | -5.6892 | -1.8203 | -3.4616 | 4.3727 | -2.2632 | 0.589 | 0.6304 | 0.9588 | 0.7084 | -130.9364 | -5.9227 | 1.257 | -0.3377 | -7.0394 | -5.7439 | 1.0952 |  | -1.3673 | -2.5795 | 4.0122 | 3.3657 | 3.3499 | 1.0357 | 10.678 | 14.1402 | 14.7269 | 11.0536 | -0.0007 | -0.0026 | 0.0006 | 0.0039 | 0.0001 | -0.0002 | 0.0062 | -0.0175 | -0.0291 | -360.1681 | 17.4685 | -360.525 | 17.7744 | -360.8512 | 18.0906 | -360.9004 | 17.5732 | -352.7398 | 18.7189 | -352.7552 | 16.8258
11:52 | 1929 | 25.4403 | 195.9347 | 437.8592 | 444.2194 | -20.3399 | -47.1512 | 3.9433 | 1.7854 | -5.1386 | -5.7159 | -1.8416 | -3.3986 | 4.46 | -2.2642 | 0.5884 | 0.6317 | 0.9582 | 0.7087 | -130.8608 | -5.9312 | 1.4819 | -0.3518 | -7.0277 | -5.6112 | 1.0986 |  | -1.366 | -2.6391 | 4.0134 | 3.3639 | 3.3519 | 1.0374 | 10.6411 | 14.1258 | 14.6979 | 11.0179 | 0 | -0.003 | 0.0006 | 0.0033 | 0.0006 | -0.0007 | -0.0056 | -0.0139 | -0.0348 | -360.1958 | 17.4623 | -360.5219 | 17.7621 | -360.8543 | 18.1071 | -360.9035 | 17.5629 | -352.7306 | 18.7169 | -352.7644 | 16.8217
11:52 | 1930 | 25.4359 | 196.0262 | 437.8433 | 444.2789 | -20.3867 | -46.9655 | 4.027 | 1.8017 | -5.1663 | -5.6678 | -1.8293 | -3.3798 | 4.4362 | -2.2735 | 0.5883 | 0.6284 | 0.955 | 0.7088 | -130.9461 | -5.8497 | 1.3671 | -0.503 | -7.0203 | -5.6691 | 1.1026 |  | -1.3582 | -2.7508 | 4.0124 | 3.365 | 3.3498 | 1.0365 | 10.6446 | 14.1236 | 14.7194 | 10.9923 | 0.0005 | -0.0029 | 0.0004 | 0.0037 | 0.0004 | -0.0004 | 0.0023 | -0.0097 | -0.0055 | -360.2019 | 17.4582 | -360.4942 | 17.7457 | -360.8358 | 18.0865 | -360.9497 | 17.5814 | -352.7337 | 18.7087 | -352.7644 | 16.8279
11:52 | 1931 | 25.5216 | 195.9722 | 437.9625 | 444.2645 | -20.3512 | -47.0989 | 3.998 | 1.8484 | -5.0609 | -5.6103 | -1.8577 | -3.3717 | 4.4074 | -2.2826 | 0.5894 | 0.6302 | 0.9596 | 0.7091 | -130.9469 | -5.8454 | 1.4145 | -0.5234 | -6.9667 | -5.7426 | 1.0642 |  | -1.2773 | -2.5824 | 4.0142 | 3.3653 | 3.3513 | 1.036 | 10.6308 | 14.0922 | 14.7156 | 10.9847 | -0.0002 | -0.0033 | 0.0011 | 0.0037 | 0.0006 | -0.0005 | 0.0047 | -0.0137 | 0.0018 | -360.1619 | 17.4788 | -360.525 | 17.7436 | -360.8666 | 18.1112 | -360.9066 | 17.5753 | -352.7306 | 18.7148 | -352.7706 | 16.8279
11:52 | 1932 | 25.5305 | 195.9854 | 437.9416 | 444.3677 | -20.3523 | -47.0148 | 4.0078 | 1.9203 | -5.0732 | -5.5905 | -1.8485 | -3.3837 | 4.4724 | -2.3272 | 0.5887 | 0.6285 | 0.9555 | 0.708 | -130.89 | -5.7777 | 1.3998 | -0.4916 | -6.898 | -5.6998 | 1.1148 |  | -1.3206 | -2.6381 | 4.0132 | 3.3648 | 3.3493 | 1.0366 | 10.6285 | 14.1012 | 14.6944 | 11.0061 | -0.0003 | -0.0029 | 0.0009 | 0.0035 | 0.0006 | -0.0013 | 0.0214 | -0.0136 | -0.0137 | -360.1588 | 17.4459 | -360.4973 | 17.7457 | -360.8266 | 18.0865 | -360.8943 | 17.5629 | -352.7121 | 18.6984 | -352.7614 | 16.8197
11:52 | 1933 | 25.4892 | 195.9792 | 437.9296 | 444.303 | -20.4207 | -47.1626 | 4.0409 | 1.852 | -5.108 | -5.6239 | -1.9416 | -3.3542 | 4.4628 | -2.2766 | 0.5908 | 0.6289 | 0.9566 | 0.7083 | -130.9354 | -5.8639 | 1.3772 | -0.3 | -6.8914 | -5.6671 | 1.0973 |  | -1.3024 | -2.6536 | 4.0136 | 3.3632 | 3.3502 | 1.036 | 10.6607 | 14.1399 | 14.7248 | 11.0197 | -0.0008 | -0.0025 | 0.001 | 0.0041 | 0 | -0.0005 | 0.0163 | -0.0133 | -0.0012 | -360.1619 | 17.4705 | -360.5158 | 17.7457 | -360.8697 | 18.105 | -360.9189 | 17.5794 | -352.7614 | 18.7107 | -352.749 | 16.8217
11:52 | 1934 | 25.4595 | 195.9872 | 437.9162 | 444.2145 | -20.3846 | -47.081 | 3.9668 | 1.8749 | -5.123 | -5.5278 | -1.913 | -3.4261 | 4.409 | -2.2698 | 0.5898 | 0.6279 | 0.9551 | 0.709 | -130.8658 | -5.8925 | 1.3378 | -0.2571 | -6.9667 | -5.6761 | 1.0332 |  | -1.292 | -2.4682 | 4.0141 | 3.3624 | 3.3523 | 1.0357 | 10.6677 | 14.1295 | 14.7436 | 11.0497 | 0.0001 | -0.003 | 0.0005 | 0.0036 | 0.0009 | -0.0009 | -0.0014 | -0.0081 | -0.0116 | -360.165 | 17.4521 | -360.4881 | 17.7395 | -360.8512 | 18.0824 | -360.882 | 17.5629 | -352.6937 | 18.7045 | -352.7367 | 16.8156
11:52 | 1935 | 25.3969 | 195.9536 | 437.8573 | 444.2182 | -20.4184 | -47.0884 | 4.0143 | 1.8949 | -5.1585 | -5.5739 | -1.8649 | -3.4079 | 4.4452 | -2.2433 | 0.5894 | 0.6278 | 0.9562 | 0.7081 | -130.9552 | -5.8418 | 1.3282 | -0.5356 | -6.9332 | -5.6985 | 0.977 |  | -1.2763 | -2.4259 | 4.0143 | 3.3665 | 3.3501 | 1.0351 | 10.6653 | 14.1331 | 14.7477 | 11.0298 | 0.0006 | -0.0032 | 0.0003 | 0.0037 | 0.0004 | -0.0004 | -0.0049 | -0.0203 | -0.023 | -360.2235 | 17.4623 | -360.5373 | 17.7539 | -360.882 | 18.1194 | -360.9097 | 17.5732 | -352.7767 | 18.7292 | -352.7552 | 16.834
11:52 | 1936 | 25.4934 | 195.9384 | 437.8498 | 444.1991 | -20.343 | -47.0917 | 4.0822 | 1.8408 | -5.196 | -5.4469 | -1.8077 | -3.4992 | 4.3862 | -2.3134 | 0.5886 | 0.6317 | 0.9541 | 0.7075 | -130.826 | -5.8152 | 1.3645 | -0.3268 | -7.0169 | -5.642 | 0.9924 |  | -1.2641 | -2.4146 | 4.0138 | 3.3593 | 3.3484 | 1.0365 | 10.6642 | 14.1491 | 14.7105 | 11.0291 | -0.0004 | -0.0032 | 0.0006 | 0.004 | 0.0005 | -0.0006 | -0.0043 | -0.009 | -0.0151 | -360.1527 | 17.448 | -360.5066 | 17.7252 | -360.8174 | 18.1091 | -360.9343 | 17.5712 | -352.6998 | 18.7066 | -352.7521 | 16.8135
11:52 | 1937 | 25.4566 | 195.9101 | 437.9219 | 444.1314 | -20.5532 | -47.1437 | 4.0341 | 1.8063 | -5.1239 | -5.4866 | -1.7582 | -3.4156 | 4.446 | -2.3274 | 0.5896 | 0.6328 | 0.9558 | 0.7108 | -130.8746 | -5.8468 | 1.3651 | -0.3492 | -6.9502 | -5.6423 | 1.0078 |  | -1.3298 | -2.469 | 4.0127 | 3.3613 | 3.3508 | 1.0364 | 10.6354 | 14.1258 | 14.7153 | 11.041 | -0.0003 | -0.0029 | 0.0005 | 0.0033 | 0.0004 | -0.0004 | 0.004 | -0.0099 | -0.0204 | -360.2204 | 17.4788 | -360.565 | 17.7477 | -360.8512 | 18.0988 | -360.9189 | 17.5937 | -352.7921 | 18.7333 | -352.7921 | 16.8238
11:52 | 1938 | 25.4898 | 195.8686 | 437.8506 | 444.2196 | -20.5256 | -47.1725 | 4.0387 | 1.8716 | -5.1759 | -5.5998 | -1.7726 | -3.4952 | 4.4575 | -2.2628 | 0.5896 | 0.6338 | 0.954 | 0.7092 | -130.8657 | -5.8542 | 1.3715 | -0.5316 | -6.9703 | -5.7458 | 1.028 |  | -1.4047 | -2.6137 | 4.015 | 3.3598 | 3.3508 | 1.036 | 10.6526 | 14.1088 | 14.6884 | 11.0229 | -0.0006 | -0.003 | 0.0006 | 0.0039 | 0.0011 | -0.0002 | 0.0164 | -0.0042 | -0.0105 | -360.1281 | 17.4521 | -360.5158 | 17.7375 | -360.8204 | 18.0927 | -360.8912 | 17.565 | -352.6783 | 18.7128 | -352.7583 | 16.8217
11:52 | 1939 | 25.5309 | 195.994 | 437.8747 | 444.282 | -20.509 | -47.1795 | 4.0199 | 1.8712 | -5.1527 | -5.6127 | -1.7544 | -3.4503 | 4.5626 | -2.2349 | 0.5898 | 0.632 | 0.9563 | 0.7093 | -130.9261 | -5.8489 | 1.2996 | -0.3923 | -7.0039 | -5.6478 | 1.0163 |  | -1.2995 | -2.6126 | 4.0128 | 3.3622 | 3.3521 | 1.0359 | 10.6724 | 14.1166 | 14.6948 | 11.0259 | 0.0004 | -0.0033 | 0.0012 | 0.0038 | 0.0003 | -0.001 | -0.0004 | -0.0056 | -0.0278 | -360.1835 | 17.4623 | -360.5219 | 17.7518 | -360.8666 | 18.1317 | -360.9251 | 17.5753 | -352.749 | 18.7128 | -352.7583 | 16.8361
11:52 | 1940 | 25.4398 | 195.9189 | 437.8521 | 444.2141 | -20.5022 | -47.1112 | 3.9908 | 1.8796 | -5.1386 | -5.6548 | -1.6617 | -3.42 | 4.5311 | -2.2454 | 0.5902 | 0.6316 | 0.9562 | 0.7095 | -130.8093 | -5.8381 | 1.363 | -0.5099 | -6.9288 | -5.7336 | 0.991 |  | -1.3506 | -2.6718 | 4.0136 | 3.3611 | 3.3542 | 1.0358 | 10.6861 | 14.1483 | 14.7181 | 11.0616 | 0.0002 | -0.0033 | 0.0011 | 0.0037 | 0.0008 | -0.0002 | 0.0095 | -0.0056 | -0.004 | -360.1281 | 17.4295 | -360.4573 | 17.7149 | -360.8174 | 18.1194 | -360.9343 | 17.5712 | -352.706 | 18.684 | -352.7183 | 16.7991
11:52 | 1941 | 25.441 | 195.9556 | 437.9134 | 444.2621 | -20.4769 | -47.0363 | 4.0471 | 1.7425 | -5.1042 | -5.6556 | -1.6557 | -3.4702 | 4.5538 | -2.1701 | 0.5903 | 0.6281 | 0.954 | 0.7106 | -130.8341 | -5.8628 | 1.4412 | -0.5082 | -6.9109 | -5.732 | 1.0594 |  | -1.288 | -2.6054 | 4.0128 | 3.3631 | 3.3511 | 1.0374 | 10.6342 | 14.1015 | 14.7023 | 11.0342 | -0.0004 | -0.0028 | 0.0003 | 0.0031 | 0.0005 | -0.001 | 0.0145 | -0.0146 | -0.0164 | -360.1927 | 17.4788 | -360.5373 | 17.7416 | -360.8604 | 18.1194 | -360.9435 | 17.5773 | -352.7706 | 18.7415 | -352.7829 | 16.8217
11:52 | 1942 | 25.3896 | 195.8076 | 437.8402 | 444.1835 | -20.429 | -47.0694 | 3.9956 | 1.8568 | -5.003 | -5.5467 | -1.6336 | -3.4576 | 4.5518 | -2.1487 | 0.59 | 0.6331 | 0.9557 | 0.7093 | -130.9448 | -5.8756 | 1.3248 | -0.4991 | -6.9586 | -5.6807 | 0.9959 |  | -1.3877 | -2.6415 | 4.0122 | 3.3618 | 3.3514 | 1.0375 | 10.6896 | 14.1285 | 14.749 | 11.0251 | -0.0002 | -0.0025 | 0.0009 | 0.0035 | 0.0002 | -0.0003 | 0.0098 | -0.0001 | 0.0087 | -360.1404 | 17.4439 | -360.5281 | 17.7559 | -360.8697 | 18.0947 | -360.8789 | 17.5363 | -352.6967 | 18.6984 | -352.7583 | 16.8402
11:52 | 1943 | 25.5281 | 195.9332 | 437.8126 | 444.3059 | -20.4363 | -47.0371 | 4.0037 | 1.7127 | -5.0507 | -5.7089 | -1.8081 | -3.3736 | 4.5815 | -2.1515 | 0.5905 | 0.6343 | 0.9555 | 0.709 | -131.0085 | -5.9714 | 1.292 | -0.4293 | -6.9352 | -5.6058 | 0.9503 |  | -1.4021 | -2.6527 | 4.0135 | 3.363 | 3.35 | 1.036 | 10.6365 | 14.0981 | 14.7224 | 11.0017 | -0.0001 | -0.003 | 0.0001 | 0.0036 | 0.001 | -0.001 | 0.0145 | -0.0064 | -0.0054 | -360.165 | 17.4603 | -360.5158 | 17.7601 | -360.9189 | 18.142 | -360.9312 | 17.5527 | -352.749 | 18.7128 | -352.7583 | 16.8464
11:52 | 1944 | 25.5009 | 195.9281 | 437.847 | 444.2513 | -20.4625 | -47.045 | 3.9846 | 1.7899 | -5.101 | -5.6682 | -1.6696 | -3.3504 | 4.5518 | -2.1969 | 0.5909 | 0.6295 | 0.9571 | 0.7079 | -130.9858 | -5.9533 | 1.2627 | -0.5432 | -6.8967 | -5.6872 | 1.0313 |  | -1.3823 | -2.6317 | 4.013 | 3.3652 | 3.3535 | 1.0371 | 10.6342 | 14.1132 | 14.7091 | 11.0222 | 0.0002 | -0.0031 | 0.0006 | 0.0038 | 0.0006 | -0.0001 | 0.003 | -0.0001 | -0.0235 | -360.2081 | 17.4541 | -360.4942 | 17.7128 | -360.802 | 18.0947 | -360.9374 | 17.5691 | -352.749 | 18.7066 | -352.7552 | 16.7909
11:52 | 1945 | 25.5545 | 195.934 | 437.8219 | 444.2801 | -20.4264 | -47.0839 | 4.0295 | 1.8499 | -5.0476 | -5.7024 | -1.7803 | -3.3964 | 4.5735 | -2.2109 | 0.589 | 0.6299 | 0.9566 | 0.7103 | -130.9599 | -5.8785 | 1.3266 | -0.4529 | -6.9765 | -5.6318 | 1.0753 |  | -1.3272 | -2.5339 | 4.0128 | 3.3637 | 3.3524 | 1.0361 | 10.6272 | 14.118 | 14.6799 | 11.0266 | 0.0001 | -0.0028 | 0.001 | 0.004 | 0.0013 | -0.0002 | 0.0176 | 0.0035 | -0.0117 | -360.1896 | 17.4993 | -360.5866 | 17.758 | -360.8666 | 18.0763 | -360.8943 | 17.5629 | -352.8014 | 18.7518 | -352.8106 | 16.834
11:52 | 1946 | 25.5496 | 195.8475 | 437.7819 | 444.2269 | -20.4564 | -47.1457 | 3.9802 | 1.8245 | -5.0934 | -5.6207 | -1.7315 | -3.34 | 4.5934 | -2.2093 | 0.5907 | 0.6291 | 0.9556 | 0.7077 | -130.8632 | -5.8276 | 1.3424 | -0.2344 | -6.9598 | -5.598 | 1.0655 |  | -1.2572 | -2.5882 | 4.0121 | 3.3668 | 3.3513 | 1.0356 | 10.641 | 14.1261 | 14.7116 | 11.0172 | -0.0002 | -0.0026 | 0.0004 | 0.0037 | 0 | -0.0005 | -0.0035 | -0.0103 | -0.0125 | -360.0911 | 17.4459 | -360.5127 | 17.7498 | -360.8666 | 18.0947 | -360.9035 | 17.5424 | -352.6813 | 18.6963 | -352.7337 | 16.8197
11:52 | 1947 | 25.4852 | 195.9257 | 437.758 | 444.2809 | -20.4199 | -47.1251 | 4.009 | 1.8403 | -4.9925 | -5.781 | -1.7819 | -3.3855 | 4.5516 | -2.2119 | 0.5903 | 0.6297 | 0.9558 | 0.7097 | -130.8344 | -5.7064 | 1.3898 | -0.2516 | -6.9719 | -5.6636 | 1.0292 |  | -1.2537 | -2.5481 | 4.0134 | 3.3633 | 3.3556 | 1.0368 | 10.663 | 14.1076 | 14.7102 | 11.0219 | -0.0001 | -0.0025 | 0.0006 | 0.0038 | 0.0006 | -0.0005 | 0.0275 | -0.0024 | 0.0123 | -360.2081 | 17.4521 | -360.4912 | 17.7231 | -360.8389 | 18.1296 | -360.962 | 17.5958 | -352.7921 | 18.7128 | -352.7306 | 16.795
11:52 | 1948 | 25.5354 | 195.9881 | 437.8244 | 444.2427 | -20.2467 | -47.012 | 4.168 | 1.8287 | -4.9978 | -5.7133 | -1.7418 | -3.3911 | 4.5252 | -2.231 | 0.5895 | 0.6319 | 0.9576 | 0.7109 | -130.9337 | -5.9825 | 1.222 | -0.3083 | -6.9305 | -5.6621 | 1.0358 |  | -1.3685 | -2.5444 | 4.0142 | 3.3654 | 3.3526 | 1.036 | 10.6827 | 14.1331 | 14.7419 | 11.0529 | 0.0003 | -0.0032 | 0.0008 | 0.0035 | 0.0006 | -0.0005 | 0.0206 | -0.0034 | 0.0082 | -360.2081 | 17.4705 | -360.5096 | 17.7108 | -360.802 | 18.0824 | -360.882 | 17.5712 | -352.7767 | 18.723 | -352.7521 | 16.7909
11:52 | 1949 | 25.4628 | 196.002 | 437.8803 | 444.2742 | -20.219 | -47.0059 | 4.2708 | 1.8342 | -4.9902 | -5.5402 | -1.7224 | -3.3776 | 4.5299 | -2.2045 | 0.5892 | 0.6299 | 0.9584 | 0.709 | -130.8712 | -5.8254 | 1.3098 | -0.4153 | -6.9545 | -5.5961 | 0.9843 |  | -1.2862 | -2.4913 | 4.0147 | 3.3652 | 3.353 | 1.0363 | 10.6596 | 14.1387 | 14.7177 | 11.0129 | 0 | -0.003 | 0.0003 | 0.0034 | 0.0002 | -0.0009 | 0.0025 | -0.0059 | -0.0053 | -360.1558 | 17.4603 | -360.5804 | 17.7867 | -360.922 | 18.1235 | -360.9343 | 17.5424 | -352.7213 | 18.7271 | -352.8106 | 16.8484
11:52 | 1950 | 25.4962 | 196.0331 | 437.808 | 444.3903 | -20.2265 | -46.9956 | 4.293 | 1.8295 | -4.9158 | -5.4277 | -1.7733 | -3.3523 | 4.579 | -2.2653 | 0.5895 | 0.6272 | 0.9609 | 0.7098 | -130.8551 | -5.8382 | 1.3483 | -0.4241 | -6.9994 | -5.6351 | 0.987 |  | -1.3828 | -2.5413 | 4.0144 | 3.3648 | 3.3526 | 1.0363 | 10.6803 | 14.1308 | 14.7402 | 10.9984 | -0.0004 | -0.0029 | 0.0007 | 0.0034 | 0.0008 | -0.0007 | -0.003 | -0.0155 | -0.0098 | -360.1588 | 17.4254 | -360.4881 | 17.7334 | -360.8697 | 18.1276 | -360.9404 | 17.5588 | -352.6967 | 18.6861 | -352.706 | 16.8115
11:52 | 1951 | 25.3542 | 196.0415 | 437.8889 | 444.34 | -20.2336 | -46.9479 | 4.3058 | 1.8833 | -5.0175 | -5.4169 | -1.7288 | -3.3409 | 4.5247 | -2.2528 | 0.5898 | 0.6336 | 0.9602 | 0.7094 | -130.9376 | -5.9136 | 1.3195 | -0.3416 | -6.9878 | -5.6065 | 1.0429 |  | -1.4276 | -2.5566 | 4.0138 | 3.3647 | 3.3499 | 1.0374 | 10.663 | 14.1366 | 14.7228 | 11.0446 | 0 | -0.0025 | 0.0007 | 0.0036 | 0.0005 | -0.0005 | 0.0036 | -0.0179 | -0.0215 | -360.2573 | 17.4829 | -360.5619 | 17.7395 | -360.8481 | 18.105 | -360.9343 | 17.5876 | -352.7983 | 18.7374 | -352.8014 | 16.8176
11:52 | 1952 | 25.4106 | 196.0445 | 437.856 | 444.2656 | -20.1929 | -47.0314 | 4.2613 | 1.8478 | -5.0425 | -5.4624 | -1.7583 | -3.3711 | 4.5215 | -2.2572 | 0.5905 | 0.6285 | 0.9567 | 0.7089 | -130.8121 | -5.9148 | 1.2631 | -0.4025 | -6.9581 | -5.5832 | 1.0703 |  | -1.3721 | -2.6441 | 4.0154 | 3.3626 | 3.351 | 1.0362 | 10.6389 | 14.1177 | 14.6662 | 10.9927 | 0.0004 | -0.003 | 0.0007 | 0.0039 | 0.0007 | -0.0009 | 0.0025 | -0.0055 | -0.0052 | -360.165 | 17.4829 | -360.5712 | 17.758 | -360.8574 | 18.0783 | -360.8389 | 17.5301 | -352.7367 | 18.7292 | -352.7952 | 16.834
11:52 | 1953 | 25.4926 | 195.9477 | 437.825 | 444.3401 | -20.2693 | -46.9828 | 4.2911 | 1.851 | -5.0752 | -5.6129 | -1.7526 | -3.325 | 4.5515 | -2.1948 | 0.5904 | 0.6305 | 0.9563 | 0.7097 | -130.8494 | -5.8145 | 1.2301 | -0.4969 | -7.046 | -5.6797 | 1.041 |  | -1.3118 | -2.5228 | 4.013 | 3.3639 | 3.3506 | 1.0366 | 10.6435 | 14.1223 | 14.7111 | 11.032 | -0.0002 | -0.0033 | 0.001 | 0.0039 | 0.0004 | -0.0001 | 0.0096 | 0.0013 | -0.0046 | -360.1711 | 17.4623 | -360.5435 | 17.7724 | -360.8912 | 18.1194 | -360.9466 | 17.5629 | -352.7244 | 18.721 | -352.786 | 16.8546
11:52 | 1954 | 25.5635 | 195.9581 | 437.7625 | 444.3735 | -20.2214 | -46.952 | 4.218 | 1.8367 | -5.1407 | -5.5103 | -1.7947 | -3.3068 | 4.5918 | -2.1384 | 0.5892 | 0.6345 | 0.9565 | 0.7103 | -130.8825 | -5.9446 | 1.1755 | -0.4748 | -6.9583 | -5.6184 | 1.1241 |  | -1.3656 | -2.5257 | 4.0136 | 3.3605 | 3.3512 | 1.0353 | 10.6123 | 14.1082 | 14.69 | 11.0071 | -0.0004 | -0.003 | 0.0002 | 0.0034 | 0.0007 | -0.0009 | 0.0055 | 0.0015 | -0.032 | -360.1865 | 17.4439 | -360.4696 | 17.7108 | -360.7897 | 18.1029 | -360.9097 | 17.5814 | -352.7952 | 18.6984 | -352.6998 | 16.8012
11:52 | 1955 | 25.5744 | 195.9253 | 437.8148 | 444.3126 | -20.236 | -46.989 | 4.3448 | 1.8523 | -5.0997 | -5.5149 | -1.8195 | -3.3401 | 4.5737 | -2.0831 | 0.5895 | 0.634 | 0.9566 | 0.7093 | -130.8965 | -5.9159 | 1.2871 | -0.5004 | -7.0221 | -5.5648 | 1.0957 |  | -1.3234 | -2.6037 | 4.0128 | 3.3616 | 3.3527 | 1.0355 | 10.6204 | 14.1107 | 14.688 | 11.0205 | -0.0002 | -0.0029 | 0.0009 | 0.0042 | 0.0004 | -0.0001 | 0.0099 | -0.024 | -0.0211 | -360.245 | 17.5013 | -360.5619 | 17.7416 | -360.8666 | 18.1029 | -360.9035 | 17.5835 | -352.789 | 18.7436 | -352.8106 | 16.8381
11:52 | 1956 | 25.5257 | 196.0301 | 437.85 | 444.275 | -20.2256 | -46.994 | 4.3278 | 1.9029 | -5.1211 | -5.4346 | -1.7318 | -3.2032 | 4.6557 | -2.0912 | 0.5906 | 0.63 | 0.9579 | 0.7097 | -130.918 | -5.9515 | 1.3129 | -0.5537 | -6.9756 | -5.6581 | 1.0905 |  | -1.2716 | -2.5447 | 4.0132 | 3.3599 | 3.351 | 1.0356 | 10.6734 | 14.1297 | 14.7273 | 11.0204 | 0 | -0.003 | 0.0006 | 0.0038 | 0.0003 | -0.0007 | 0.0128 | -0.008 | 0.0021 | -360.1004 | 17.4315 | -360.5066 | 17.7621 | -360.8758 | 18.1173 | -360.8943 | 17.5321 | -352.6752 | 18.7087 | -352.7552 | 16.8484
11:52 | 1957 | 25.5034 | 195.9283 | 437.8611 | 444.2834 | -20.2508 | -46.9449 | 4.3648 | 1.9387 | -5.0145 | -5.4455 | -1.7092 | -3.1816 | 4.6219 | -2.0501 | 0.5912 | 0.631 | 0.9534 | 0.7108 | -130.9069 | -5.9126 | 1.428 | -0.4831 | -6.9873 | -5.7172 | 1.0767 |  | -1.2732 | -2.6262 | 4.0137 | 3.3582 | 3.3484 | 1.0345 | 10.647 | 14.1313 | 14.7189 | 11.0071 | -0.0003 | -0.0034 | 0.0005 | 0.0034 | 0.0007 | -0.0004 | 0.0112 | -0.0136 | -0.0113 | -360.1835 | 17.4336 | -360.5004 | 17.7518 | -360.8789 | 18.142 | -360.9527 | 17.5855 | -352.7367 | 18.6963 | -352.746 | 16.8361
11:52 | 1958 | 25.4969 | 195.9689 | 437.8608 | 444.3062 | -20.3639 | -46.9711 | 4.2587 | 1.9631 | -4.9668 | -5.4919 | -1.7286 | -3.2182 | 4.6129 | -2.0262 | 0.5893 | 0.6317 | 0.9554 | 0.7086 | -130.8764 | -5.9394 | 1.4088 | -0.3822 | -7.0098 | -5.6948 | 1.1091 |  | -1.3104 | -2.6407 | 4.0129 | 3.3628 | 3.3478 | 1.0358 | 10.6839 | 14.1283 | 14.7306 | 11.0428 | 0 | -0.0029 | 0.0005 | 0.0036 | 0.0003 | -0.0004 | 0.0108 | -0.012 | -0.0261 | -360.1927 | 17.4705 | -360.5189 | 17.7436 | -360.8081 | 18.0947 | -360.9158 | 17.5547 | -352.7798 | 18.7292 | -352.7644 | 16.8217
11:52 | 1959 | 25.4662 | 195.9326 | 437.8238 | 444.2975 | -20.339 | -46.9917 | 4.3061 | 1.8813 | -4.9211 | -5.5213 | -1.8307 | -3.3601 | 4.5662 | -2.1116 | 0.5905 | 0.6269 | 0.9558 | 0.7079 | -130.9366 | -5.9643 | 1.3878 | -0.4538 | -7.0539 | -5.6521 | 1.0482 |  | -1.369 | -2.506 | 4.0135 | 3.3625 | 3.3498 | 1.0347 | 10.6607 | 14.14 | 14.7375 | 11.0309 | -0.0004 | -0.0026 | 0.0005 | 0.0036 | 0.0006 | -0.0009 | 0.0178 | -0.0074 | -0.0013 | -360.1711 | 17.4829 | -360.5896 | 17.7909 | -360.9097 | 18.1029 | -360.8789 | 17.5486 | -352.7398 | 18.7395 | -352.829 | 16.8628
11:52 | 1960 | 25.6074 | 195.9421 | 437.8742 | 444.2772 | -20.3759 | -46.9484 | 4.3053 | 1.9901 | -4.9605 | -5.6078 | -1.7752 | -3.347 | 4.5864 | -2.154 | 0.5897 | 0.6298 | 0.9565 | 0.7093 | -130.8981 | -5.9868 | 1.4055 | -0.3861 | -6.9983 | -5.5501 | 1.094 |  | -1.3451 | -2.5544 | 4.0131 | 3.3636 | 3.349 | 1.0368 | 10.6596 | 14.1097 | 14.7166 | 11.0479 | -0.0003 | -0.0031 | 0.0002 | 0.0034 | 0.0006 | -0.0004 | -0.0012 | -0.0163 | -0.0123 | -360.1588 | 17.4582 | -360.5066 | 17.7518 | -360.8543 | 18.1235 | -360.9343 | 17.5547 | -352.7029 | 18.7087 | -352.7275 | 16.832
11:52 | 1961 | 25.7341 | 195.9776 | 437.9001 | 444.347 | -20.401 | -46.9594 | 4.1759 | 1.9069 | -4.9991 | -5.5933 | -1.7422 | -3.267 | 4.5836 | -2.1904 | 0.59 | 0.6297 | 0.9547 | 0.7087 | -130.9595 | -5.9218 | 1.2768 | -0.4021 | -7.0142 | -5.5783 | 1.1425 |  | -1.285 | -2.684 | 4.0144 | 3.3646 | 3.3522 | 1.0352 | 10.6629 | 14.1196 | 14.7365 | 11.0149 | 0.0004 | -0.003 | 0.0012 | 0.0041 | 0.0006 | -0.0006 | 0.0078 | -0.0021 | -0.0218 | -360.1958 | 17.4726 | -360.525 | 17.7354 | -360.8174 | 18.0947 | -360.9343 | 17.5773 | -352.7675 | 18.7189 | -352.786 | 16.8238
11:52 | 1962 | 25.6059 | 196.0002 | 437.805 | 444.3094 | -20.3473 | -47.0044 | 4.1949 | 1.8766 | -4.9486 | -5.6299 | -1.6965 | -3.3059 | 4.6122 | -2.0894 | 0.5907 | 0.6272 | 0.9559 | 0.7086 | -130.9359 | -5.9176 | 1.3024 | -0.3691 | -6.989 | -5.4583 | 1.1858 |  | -1.264 | -2.561 | 4.0139 | 3.364 | 3.3494 | 1.034 | 10.6654 | 14.1617 | 14.7282 | 11.0537 | -0.0006 | -0.0034 | 0.0003 | 0.0037 | -0.0002 | -0.0009 | 0.0094 | 0.0004 | 0.006 | -360.205 | 17.4623 | -360.525 | 17.7765 | -360.8727 | 18.0906 | -360.8943 | 17.5588 | -352.7367 | 18.7312 | -352.7706 | 16.834
11:52 | 1963 | 25.6337 | 195.8642 | 437.8589 | 444.3734 | -20.2503 | -46.9647 | 4.2184 | 1.9053 | -4.8891 | -5.3952 | -1.6539 | -3.2505 | 4.6017 | -2.1102 | 0.5914 | 0.6277 | 0.9544 | 0.7101 | -130.879 | -5.8895 | 1.4022 | -0.4583 | -6.9949 | -5.4962 | 1.022 |  | -1.2821 | -2.5263 | 4.0132 | 3.3615 | 3.3505 | 1.0346 | 10.6572 | 14.1424 | 14.6997 | 11.0157 | -0.0001 | -0.0027 | 0.001 | 0.0039 | 0.0011 | -0.0005 | 0.0139 | -0.0026 | -0.0053 | -360.165 | 17.4582 | -360.4942 | 17.7642 | -360.8604 | 18.1255 | -360.9404 | 17.5486 | -352.7183 | 18.7148 | -352.7644 | 16.834
11:52 | 1964 | 25.5471 | 195.9727 | 437.8887 | 444.2824 | -20.3225 | -46.9726 | 4.1821 | 1.8765 | -4.9215 | -5.6106 | -1.7077 | -3.2472 | 4.6483 | -2.0556 | 0.5928 | 0.6286 | 0.9552 | 0.7099 | -130.9539 | -5.9353 | 1.4016 | -0.4647 | -6.9605 | -5.5681 | 1.1455 |  | -1.2627 | -2.4567 | 4.0141 | 3.3622 | 3.349 | 1.0349 | 10.619 | 14.1331 | 14.6956 | 11.0067 | -0.0001 | -0.0028 | 0.0004 | 0.0035 | 0.0006 | -0.0003 | 0.0086 | -0.016 | -0.0121 | -360.165 | 17.45 | -360.5312 | 17.7539 | -360.8297 | 18.1132 | -360.9127 | 17.5732 | -352.7552 | 18.7107 | -352.7429 | 16.832
11:52 | 1965 | 25.6007 | 196.0231 | 438.0164 | 444.3458 | -20.4104 | -47.1359 | 4.0381 | 1.9068 | -4.9281 | -5.6248 | -1.6382 | -3.2554 | 4.6802 | -2.0877 | 0.5911 | 0.629 | 0.9561 | 0.71 | -130.974 | -5.8859 | 1.353 | -0.5219 | -7.0142 | -5.6129 | 1.0863 |  | -1.1913 | -2.4782 | 4.0158 | 3.3633 | 3.3494 | 1.0361 | 10.6596 | 14.1328 | 14.7398 | 11.0363 | -0.0001 | -0.0033 | 0 | 0.0031 | 0.0003 | -0.001 | 0.0033 | -0.0047 | -0.0146 | -360.1773 | 17.4726 | -360.5219 | 17.7765 | -360.8604 | 18.0988 | -360.9035 | 17.565 | -352.7614 | 18.7292 | -352.7737 | 16.8525
11:52 | 1966 | 25.5773 | 195.9411 | 437.8841 | 444.3505 | -20.4185 | -47.1269 | 4.1487 | 1.8389 | -4.9719 | -5.6527 | -1.7133 | -3.2892 | 4.7451 | -2.0098 | 0.5907 | 0.6272 | 0.9557 | 0.7105 | -131.0047 | -5.9383 | 1.256 | -0.528 | -7.0722 | -5.5653 | 1.0879 |  | -1.2266 | -2.5125 | 4.0147 | 3.3627 | 3.351 | 1.0361 | 10.6249 | 14.0982 | 14.6945 | 11.0186 | 0.0003 | -0.003 | 0.0011 | 0.0041 | 0.0011 | -0.0003 | 0.009 | -0.0169 | -0.018 | -360.1835 | 17.4582 | -360.5158 | 17.7416 | -360.8512 | 18.1112 | -360.8727 | 17.5527 | -352.7152 | 18.7066 | -352.7706 | 16.832
11:52 | 1967 | 25.6566 | 195.9809 | 437.8404 | 444.3527 | -20.2974 | -47.0402 | 4.2007 | 1.8809 | -4.9306 | -5.4867 | -1.6405 | -3.2608 | 4.7102 | -2.1224 | 0.59 | 0.6306 | 0.9569 | 0.7098 | -130.9534 | -5.8439 | 1.3076 | -0.543 | -7.1225 | -5.6587 | 1.0609 |  | -1.2201 | -2.4529 | 4.0138 | 3.3616 | 3.3516 | 1.0357 | 10.6214 | 14.1178 | 14.6731 | 10.9923 | -0.0003 | -0.0029 | 0.0008 | 0.0036 | 0.0004 | -0.0006 | 0.0114 | -0.0114 | 0.001 | -360.1927 | 17.4603 | -360.5127 | 17.7559 | -360.8358 | 18.1173 | -360.9097 | 17.5609 | -352.7706 | 18.721 | -352.7798 | 16.8381
11:53 | 1968 | 25.6127 | 196.015 | 437.8108 | 444.3238 | -20.2999 | -47.0658 | 4.3113 | 1.841 | -4.858 | -5.6991 | -1.6724 | -3.263 | 4.6642 | -2.0585 | 0.5909 | 0.629 | 0.9537 | 0.7099 | -130.9183 | -5.8688 | 1.3058 | -0.5504 | -7.0468 | -5.626 | 1.0217 |  | -1.2224 | -2.5701 | 4.0148 | 3.3667 | 3.3548 | 1.0365 | 10.6468 | 14.1319 | 14.6826 | 11.0345 | -0.0002 | -0.0026 | 0.0007 | 0.0039 | 0.0008 | -0.0005 | 0.0085 | -0.0099 | -0.0245 | -360.2204 | 17.4664 | -360.5466 | 17.758 | -360.8758 | 18.0988 | -360.9251 | 17.5588 | -352.7121 | 18.7395 | -352.7614 | 16.832
11:53 | 1969 | 25.6402 | 196.0046 | 437.9385 | 444.3198 | -20.2153 | -47.0642 | 4.3572 | 1.9548 | -4.8068 | -5.5591 | -1.5581 | -3.2637 | 4.6747 | -2.0629 | 0.5901 | 0.6285 | 0.9573 | 0.7105 | -131.0093 | -5.9004 | 1.2984 | -0.3399 | -7.0601 | -5.591 | 0.9986 |  | -1.3236 | -2.6208 | 4.0151 | 3.364 | 3.3517 | 1.0362 | 10.6445 | 14.1006 | 14.6915 | 11.015 | 0 | -0.003 | 0.001 | 0.0045 | 0.0006 | -0.0002 | 0.0091 | -0.0012 | 0.0074 | -360.1435 | 17.4439 | -360.5312 | 17.7642 | -360.8389 | 18.105 | -360.9251 | 17.5568 | -352.7367 | 18.7169 | -352.7706 | 16.8484
11:53 | 1970 | 25.5712 | 195.8915 | 437.941 | 444.3655 | -20.3642 | -47.1445 | 4.2395 | 1.9744 | -4.7623 | -5.444 | -1.5676 | -3.2576 | 4.7652 | -2.0176 | 0.5903 | 0.6331 | 0.9548 | 0.7094 | -130.9804 | -6.0488 | 1.2967 | -0.4016 | -7.0814 | -5.6332 | 1.0287 |  | -1.2942 | -2.5746 | 4.0147 | 3.3657 | 3.3501 | 1.0363 | 10.6723 | 14.1283 | 14.7248 | 11.0082 | 0.0001 | -0.0019 | 0.0001 | 0.0044 | 0.0011 | -0.0006 | 0.0135 | -0.0011 | 0.0075 | -360.2142 | 17.4726 | -360.5219 | 17.7313 | -360.8604 | 18.1173 | -360.9251 | 17.5753 | -352.7614 | 18.7292 | -352.746 | 16.8094
11:53 | 1971 | 25.5743 | 195.8827 | 437.9211 | 444.3104 | -20.3523 | -47.0524 | 4.1114 | 1.9579 | -4.814 | -5.4644 | -1.644 | -3.2443 | 4.7329 | -2.0499 | 0.5903 | 0.6299 | 0.9531 | 0.708 | -130.9385 | -5.8805 | 1.3622 | -0.4623 | -7.132 | -5.7313 | 0.9512 |  | -1.1825 | -2.5269 | 4.014 | 3.3606 | 3.3495 | 1.0354 | 10.6699 | 14.1494 | 14.7184 | 11.0283 | 0.0001 | -0.0029 | 0.0006 | 0.0037 | 0.0001 | -0.0006 | -0.0046 | -0.004 | -0.0039 | -360.1804 | 17.4562 | -360.5404 | 17.7498 | -360.8389 | 18.0947 | -360.8912 | 17.5547 | -352.746 | 18.7251 | -352.7521 | 16.834
11:53 | 1972 | 25.623 | 195.9007 | 437.834 | 444.2717 | -20.327 | -47.1299 | 4.1698 | 1.899 | -4.8576 | -5.5202 | -1.6116 | -3.2311 | 4.7614 | -1.9572 | 0.5904 | 0.6308 | 0.9535 | 0.709 | -131.0168 | -5.9678 | 1.2988 | -0.3133 | -7.0127 | -5.5636 | 1.0636 |  | -1.2855 | -2.5278 | 4.0139 | 3.3638 | 3.3543 | 1.0354 | 10.655 | 14.1398 | 14.718 | 11.0316 | -0.0002 | -0.0028 | 0.0007 | 0.0035 | 0.0003 | -0.0012 | 0.0137 | -0.0148 | -0.0218 | -360.1835 | 17.4664 | -360.5558 | 17.7703 | -360.8974 | 18.1235 | -360.9466 | 17.5547 | -352.7398 | 18.723 | -352.8075 | 16.8525
11:53 | 1973 | 25.5531 | 195.8983 | 437.9187 | 444.2681 | -20.3527 | -47.0541 | 4.2587 | 1.9307 | -4.8622 | -5.4193 | -1.6348 | -3.3443 | 4.7675 | -2.0262 | 0.5912 | 0.6293 | 0.9545 | 0.7091 | -131.0063 | -5.9546 | 1.1715 | -0.2834 | -7.0749 | -5.6176 | 0.9964 |  | -1.2941 | -2.5088 | 4.0132 | 3.3658 | 3.3479 | 1.0369 | 10.6583 | 14.1378 | 14.73 | 11.0457 | 0.0001 | -0.0027 | 0.0005 | 0.0035 | 0.0009 | -0.0002 | 0.0316 | -0.0125 | 0.0115 | -360.1496 | 17.4172 | -360.4696 | 17.7416 | -360.882 | 18.1173 | -360.9281 | 17.5465 | -352.7337 | 18.6922 | -352.7244 | 16.832
11:53 | 1974 | 25.6706 | 195.9326 | 437.8178 | 444.3749 | -20.2909 | -47.0408 | 4.2489 | 1.9363 | -4.8204 | -5.4791 | -1.5697 | -3.2468 | 4.7779 | -1.9962 | 0.5905 | 0.6303 | 0.9544 | 0.7084 | -130.9418 | -5.8704 | 1.2546 | -0.3035 | -7.0296 | -5.6094 | 1.0031 |  | -1.2791 | -2.5061 | 4.0145 | 3.3663 | 3.3502 | 1.0356 | 10.677 | 14.1097 | 14.7108 | 11.0075 | 0.0001 | -0.0033 | 0.0007 | 0.0035 | 0.0008 | -0.001 | 0.0125 | 0.0005 | -0.007 | -360.2081 | 17.487 | -360.5404 | 17.7436 | -360.8512 | 18.1091 | -360.9004 | 17.5773 | -352.7921 | 18.7497 | -352.7644 | 16.8279
11:53 | 1975 | 25.6772 | 196.0081 | 437.842 | 444.2722 | -20.2536 | -46.9527 | 4.2482 | 1.966 | -4.8098 | -5.4298 | -1.6064 | -3.2629 | 4.7557 | -2.0902 | 0.591 | 0.6339 | 0.9574 | 0.7092 | -130.8491 | -6.0433 | 1.2235 | -0.3216 | -7.06 | -5.6479 | 0.9948 |  | -1.2244 | -2.4584 | 4.0154 | 3.3658 | 3.3498 | 1.0381 | 10.6562 | 14.1177 | 14.7067 | 11.0158 | -0.0002 | -0.0029 | 0.0007 | 0.0034 | 0.0007 | -0.0005 | 0.0071 | -0.0041 | -0.0155 | -360.1435 | 17.4562 | -360.5743 | 17.7559 | -360.8666 | 18.0865 | -360.8512 | 17.5198 | -352.6967 | 18.7271 | -352.8475 | 16.8607
11:53 | 1976 | 25.637 | 195.9898 | 437.7707 | 444.3577 | -20.1468 | -46.8555 | 4.4088 | 1.8404 | -4.8018 | -5.4742 | -1.6599 | -3.3586 | 4.8039 | -1.9523 | 0.5904 | 0.6326 | 0.9537 | 0.7095 | -130.91 | -5.9631 | 1.321 | -0.2679 | -7.0965 | -5.7159 | 1.0324 |  | -1.3118 | -2.5059 | 4.0152 | 3.3626 | 3.3488 | 1.0366 | 10.6341 | 14.1134 | 14.716 | 11.0508 | -0.0004 | -0.0028 | 0.0005 | 0.0037 | 0.0007 | -0.0003 | -0.0024 | -0.0121 | -0.0074 | -360.1773 | 17.4562 | -360.5066 | 17.7518 | -360.8635 | 18.1317 | -360.9651 | 17.5814 | -352.746 | 18.7066 | -352.749 | 16.8361
11:53 | 1977 | 25.5994 | 195.967 | 437.7115 | 444.3288 | -20.2084 | -46.8607 | 4.399 | 1.983 | -4.7946 | -5.4724 | -1.5615 | -3.3794 | 4.8037 | -2.0269 | 0.5904 | 0.6358 | 0.9528 | 0.7091 | -131.0084 | -5.9839 | 1.3527 | -0.2904 | -7.0735 | -5.6433 | 1.0362 |  | -1.2365 | -2.471 | 4.0147 | 3.3658 | 3.3504 | 1.0377 | 10.6572 | 14.1307 | 14.6986 | 11.0219 | -0.0004 | -0.0028 | 0.0008 | 0.0043 | 0.0007 | -0.0007 | -0.0047 | -0.014 | -0.005 | -360.1773 | 17.4664 | -360.4819 | 17.7087 | -360.7897 | 18.0763 | -360.9035 | 17.5712 | -352.7983 | 18.7333 | -352.7429 | 16.8074
11:53 | 1978 | 25.7428 | 195.9518 | 437.7953 | 444.3892 | -20.2005 | -46.8752 | 4.3936 | 1.9049 | -4.8073 | -5.4696 | -1.6181 | -3.3299 | 4.7734 | -1.9887 | 0.5913 | 0.6314 | 0.9545 | 0.7094 | -130.9998 | -5.9651 | 1.2604 | -0.272 | -7.0298 | -5.6687 | 1.0392 |  | -1.2642 | -2.4513 | 4.0151 | 3.3643 | 3.3521 | 1.0371 | 10.6769 | 14.1215 | 14.7361 | 11.0356 | 0 | -0.0031 | 0.0001 | 0.0036 | 0.0006 | 0 | 0.0078 | -0.0062 | -0.0169 | -360.2081 | 17.4788 | -360.5496 | 17.7477 | -360.8789 | 18.1132 | -360.9035 | 17.5588 | -352.7583 | 18.7415 | -352.7829 | 16.8464
11:53 | 1979 | 25.676 | 195.9675 | 437.7636 | 444.3652 | -20.2395 | -46.8875 | 4.3475 | 1.9097 | -4.8041 | -5.4643 | -1.5895 | -3.3218 | 4.7212 | -1.9728 | 0.5912 | 0.6334 | 0.9533 | 0.7088 | -131.0545 | -5.9978 | 1.2541 | -0.1513 | -7.0043 | -5.6197 | 1.0225 |  | -1.2437 | -2.3787 | 4.0144 | 3.3645 | 3.3514 | 1.0369 | 10.6561 | 14.1526 | 14.7262 | 11.0323 | -0.0003 | -0.0033 | 0.0008 | 0.0041 | 0.0012 | -0.0004 | 0.0042 | -0.0027 | 0.0048 | -360.125 | 17.411 | -360.4696 | 17.7334 | -360.8574 | 18.1379 | -360.9527 | 17.5445 | -352.706 | 18.6861 | -352.7213 | 16.8299
11:53 | 1980 | 25.6951 | 195.9175 | 437.8335 | 444.3466 | -20.2364 | -46.9264 | 4.3851 | 2.0011 | -4.7474 | -5.4008 | -1.5625 | -3.3227 | 4.7372 | -1.9767 | 0.5908 | 0.6317 | 0.9492 | 0.7083 | -131.0048 | -6.0429 | 1.2709 | -0.1591 | -6.9992 | -5.619 | 1.1029 |  | -1.2297 | -2.4082 | 4.0135 | 3.3653 | 3.3509 | 1.0358 | 10.6446 | 14.1294 | 14.6962 | 11.0269 | -0.0004 | -0.0029 | 0.0007 | 0.0039 | 0.0001 | -0.0002 | 0.0014 | 0.001 | -0.0083 | -360.1988 | 17.45 | -360.4819 | 17.7252 | -360.8204 | 18.1235 | -360.9527 | 17.5814 | -352.7675 | 18.7169 | -352.7521 | 16.8238
11:53 | 1981 | 25.7843 | 196.0508 | 437.9857 | 444.3758 | -20.2991 | -46.9197 | 4.3571 | 1.9488 | -4.7896 | -5.5136 | -1.6486 | -3.4186 | 4.716 | -1.9699 | 0.5918 | 0.631 | 0.9508 | 0.7084 | -131.0254 | -6.1231 | 1.3087 | -0.213 | -7.0071 | -5.6077 | 1.0434 |  | -1.2453 | -2.4297 | 4.0134 | 3.3573 | 3.3495 | 1.0362 | 10.6329 | 14.1123 | 14.7041 | 11.0377 | -0.0003 | -0.0031 | 0.0007 | 0.0033 | 0.0011 | -0.0005 | 0.0191 | -0.0246 | -0.0218 | -360.2173 | 17.4849 | -360.5712 | 17.7498 | -360.8697 | 18.0865 | -360.8604 | 17.5486 | -352.7644 | 18.7374 | -352.8075 | 16.8402
11:53 | 1982 | 25.824 | 196.0185 | 437.9738 | 444.3386 | -20.3366 | -47.0329 | 4.3578 | 1.9342 | -4.8075 | -5.4738 | -1.6342 | -3.4024 | 4.7703 | -1.978 | 0.5905 | 0.6314 | 0.9533 | 0.7083 | -130.9905 | -6.0411 | 1.315 | -0.1809 | -6.981 | -5.5696 | 1.1505 |  | -1.2451 | -2.3634 | 4.0143 | 3.3642 | 3.3524 | 1.0373 | 10.663 | 14.1424 | 14.7344 | 11.0562 | 0.0002 | -0.003 | 0.0008 | 0.0038 | 0.0008 | -0.0003 | 0.004 | -0.0046 | -0.0078 | -360.1373 | 17.4541 | -360.5343 | 17.7601 | -360.9035 | 18.1132 | -360.8912 | 17.5404 | -352.7213 | 18.7148 | -352.7983 | 16.8689
11:53 | 1983 | 25.7978 | 196.0266 | 437.9303 | 444.3906 | -20.2845 | -47.0525 | 4.3119 | 2.0394 | -4.6678 | -5.3688 | -1.5789 | -3.2585 | 4.7501 | -2.0394 | 0.5898 | 0.6323 | 0.9516 | 0.7083 | -130.9902 | -6.0644 | 1.3165 | -0.1176 | -6.92 | -5.4398 | 1.2223 |  | -1.2946 | -2.4132 | 4.0127 | 3.3625 | 3.3506 | 1.0361 | 10.663 | 14.1423 | 14.7044 | 11.0334 | -0.0002 | -0.0036 | 0.0009 | 0.0039 | 0.0007 | -0.0007 | 0.0031 | -0.0144 | -0.0117 | -360.2019 | 17.4582 | -360.4696 | 17.7067 | -360.8635 | 18.1173 | -360.9404 | 17.5814 | -352.7614 | 18.7087 | -352.7367 | 16.8135
11:53 | 1984 | 25.8535 | 195.9868 | 437.9774 | 444.3958 | -20.2295 | -47.0019 | 4.2718 | 2.0673 | -4.6276 | -5.387 | -1.5318 | -3.2229 | 4.8076 | -2.0314 | 0.5916 | 0.6329 | 0.952 | 0.7076 | -131.0747 | -6.1001 | 1.2123 | -0.119 | -6.8939 | -5.5459 | 1.1707 |  | -1.3254 | -2.44 | 4.0134 | 3.3644 | 3.3508 | 1.0352 | 10.6376 | 14.134 | 14.7238 | 11.0028 | -0.0003 | -0.0029 | 0.0009 | 0.0038 | 0.0005 | -0.001 | 0.0105 | -0.0099 | -0.0192 | -360.2142 | 17.4767 | -360.5343 | 17.7108 | -360.7927 | 18.0824 | -360.9066 | 17.5609 | -352.8044 | 18.7436 | -352.7675 | 16.8217
11:53 | 1985 | 25.8586 | 195.9498 | 437.9129 | 444.4376 | -20.2374 | -47.028 | 4.2947 | 2.0553 | -4.7783 | -5.5004 | -1.5663 | -3.2373 | 4.8078 | -1.9879 | 0.5908 | 0.6316 | 0.9477 | 0.7082 | -131.0673 | -6.1023 | 1.2135 | -0.1962 | -6.9365 | -5.7164 | 1.1487 |  | -1.1965 | -2.475 | 4.0143 | 3.3636 | 3.3501 | 1.0358 | 10.6549 | 14.1458 | 14.7085 | 11.0193 | -0.0002 | -0.0028 | 0.0006 | 0.0037 | 0.0005 | -0.0003 | 0.0013 | -0.014 | -0.0046 | -360.2081 | 17.4705 | -360.5496 | 17.7621 | -360.8974 | 18.1132 | -360.922 | 17.5547 | -352.7398 | 18.7292 | -352.7798 | 16.8505
11:53 | 1986 | 25.8313 | 195.9526 | 437.8025 | 444.3553 | -20.271 | -47.0726 | 4.2924 | 2.0198 | -4.7656 | -5.5512 | -1.5722 | -3.2823 | 4.7939 | -1.97 | 0.5925 | 0.6315 | 0.9523 | 0.7083 | -131.0645 | -6.099 | 1.2243 | -0.1473 | -6.8444 | -5.5454 | 1.2341 |  | -1.2555 | -2.3636 | 4.0126 | 3.3637 | 3.347 | 1.0357 | 10.6699 | 14.1494 | 14.7184 | 11.0341 | 0 | -0.0028 | 0.0005 | 0.0039 | 0.0008 | -0.0007 | 0.0095 | -0.006 | -0.0111 | -360.1096 | 17.4336 | -360.4512 | 17.7169 | -360.8512 | 18.1481 | -360.9497 | 17.5629 | -352.7183 | 18.7025 | -352.7152 | 16.8217
11:53 | 1987 | 25.8618 | 196.0034 | 437.9385 | 444.3639 | -20.2929 | -47.0802 | 4.2268 | 2.0418 | -4.7925 | -5.4522 | -1.6262 | -3.2598 | 4.7699 | -1.911 | 0.5921 | 0.6305 | 0.9522 | 0.7077 | -131.0457 | -6.0916 | 1.2122 | -0.1708 | -6.8626 | -5.5813 | 1.1381 |  | -1.252 | -2.5274 | 4.0134 | 3.3655 | 3.3491 | 1.0362 | 10.6595 | 14.1042 | 14.6898 | 11.024 | 0.0003 | -0.0031 | 0.0006 | 0.0037 | 0.0006 | -0.0003 | 0.0247 | -0.0062 | -0.0124 | -360.1742 | 17.4582 | -360.5158 | 17.719 | -360.8327 | 18.144 | -360.9743 | 17.5876 | -352.7644 | 18.721 | -352.7737 | 16.8197
11:53 | 1988 | 25.8466 | 195.9553 | 437.85 | 444.3143 | -20.3807 | -47.064 | 4.2146 | 1.9792 | -4.8132 | -5.5672 | -1.6185 | -3.2932 | 4.8962 | -1.9616 | 0.5908 | 0.6299 | 0.9494 | 0.7076 | -131.0908 | -6.0922 | 1.2829 | -0.0676 | -6.849 | -5.7133 | 1.1935 |  | -1.2638 | -2.4219 | 4.0132 | 3.3671 | 3.3509 | 1.0383 | 10.6179 | 14.1202 | 14.6932 | 11.0349 | -0.0002 | -0.0029 | 0.0006 | 0.0043 | 0.0013 | -0.0003 | 0.0154 | -0.0038 | -0.0126 | -360.1465 | 17.4685 | -360.5466 | 17.7313 | -360.842 | 18.1091 | -360.8574 | 17.5445 | -352.7398 | 18.7251 | -352.7798 | 16.8361
11:53 | 1989 | 25.8386 | 196.0115 | 437.825 | 444.3527 | -20.3624 | -47.0622 | 4.2708 | 2.0073 | -4.7209 | -5.5949 | -1.5703 | -3.2813 | 4.8392 | -1.8976 | 0.5906 | 0.6291 | 0.954 | 0.7068 | -131.0398 | -6.1091 | 1.3474 | -0.1123 | -6.9355 | -5.5718 | 1.2128 |  | -1.2198 | -2.4322 | 4.0136 | 3.3666 | 3.353 | 1.0359 | 10.6735 | 14.1237 | 14.7088 | 11.015 | -0.0004 | -0.0026 | 0.0009 | 0.0036 | 0.0003 | -0.0005 | 0.0075 | -0.0076 | -0.0042 | -360.1342 | 17.4603 | -360.565 | 17.7498 | -360.9158 | 18.1625 | -360.9343 | 17.5404 | -352.7121 | 18.723 | -352.7798 | 16.8484
11:53 | 1990 | 25.8457 | 195.9511 | 437.9118 | 444.308 | -20.3205 | -47.1559 | 4.3258 | 1.997 | -4.7512 | -5.5131 | -1.5679 | -3.4442 | 4.8501 | -1.9657 | 0.5909 | 0.6306 | 0.9566 | 0.7085 | -131.1366 | -6.1117 | 1.2734 | -0.1212 | -6.9216 | -5.5565 | 1.2118 |  | -1.1756 | -2.4267 | 4.0153 | 3.3659 | 3.3445 | 1.0366 | 10.6562 | 14.1352 | 14.7078 | 11.0212 | -0.0001 | -0.0028 | 0.0009 | 0.0037 | 0.0007 | -0.001 | -0.0036 | 0.0093 | -0.0353 | -360.1681 | 17.4562 | -360.4819 | 17.7046 | -360.8143 | 18.1276 | -360.9312 | 17.5732 | -352.7121 | 18.7189 | -352.7275 | 16.8053
11:53 | 1991 | 25.843 | 195.9193 | 437.939 | 444.2954 | -20.3025 | -47.0617 | 4.3705 | 2.1228 | -4.7437 | -5.5211 | -1.5715 | -3.3341 | 4.7801 | -1.9181 | 0.592 | 0.6314 | 0.9564 | 0.7079 | -131.0893 | -6.0803 | 1.2576 | -0.1566 | -7.0232 | -5.7665 | 1.1154 |  | -1.1992 | -2.4354 | 4.0134 | 3.3624 | 3.3501 | 1.0372 | 10.6504 | 14.1236 | 14.6731 | 11.0327 | 0 | -0.0034 | 0.0006 | 0.0034 | 0.001 | 0 | 0.0118 | -0.0069 | -0.0069 | -360.2142 | 17.5116 | -360.5527 | 17.7252 | -360.8604 | 18.1317 | -360.9004 | 17.5609 | -352.8044 | 18.762 | -352.8044 | 16.8238
11:53 | 1992 | 25.9043 | 195.9379 | 437.9601 | 444.3024 | -20.1408 | -46.8869 | 4.3722 | 2.1419 | -4.7298 | -5.506 | -1.5293 | -3.3841 | 4.8458 | -1.9207 | 0.5905 | 0.6322 | 0.9547 | 0.7086 | -131.0769 | -6.043 | 1.2203 | -0.1037 | -6.9217 | -5.616 | 1.1576 |  | -1.2437 | -2.4921 | 4.0142 | 3.361 | 3.3485 | 1.0374 | 10.6389 | 14.1002 | 14.6594 | 11.0046 | 0.0002 | -0.003 | 0.0002 | 0.0031 | 0.0005 | -0.0009 | 0.0039 | -0.0032 | -0.0173 | -360.1681 | 17.4459 | -360.525 | 17.719 | -360.8604 | 18.1276 | -360.9066 | 17.5445 | -352.7429 | 18.723 | -352.7675 | 16.8381
11:53 | 1993 | 25.8582 | 195.9328 | 438.044 | 444.3783 | -20.1546 | -46.8708 | 4.4508 | 2.1219 | -4.7196 | -5.4935 | -1.5455 | -3.4222 | 4.8944 | -1.9116 | 0.5908 | 0.6307 | 0.9555 | 0.7083 | -131.0123 | -5.9908 | 1.3154 | -0.1221 | -6.888 | -5.6369 | 1.192 |  | -1.1846 | -2.5553 | 4.0146 | 3.3621 | 3.3463 | 1.0378 | 10.6584 | 14.1492 | 14.7521 | 11.0287 | -0.0005 | -0.0028 | 0.0004 | 0.0034 | 0.001 | -0.0004 | 0.0019 | -0.0172 | 0.0006 | -360.205 | 17.4562 | -360.485 | 17.719 | -360.8697 | 18.1563 | -360.9343 | 17.5486 | -352.7767 | 18.7087 | -352.7337 | 16.8197
11:53 | 1994 | 25.8871 | 195.9525 | 437.983 | 444.393 | -20.1788 | -46.9543 | 4.3929 | 2.1449 | -4.7183 | -5.5279 | -1.5558 | -3.3428 | 4.9214 | -1.8429 | 0.5923 | 0.63 | 0.9539 | 0.7092 | -131.0551 | -5.9659 | 1.4043 | -0.0761 | -6.9127 | -5.609 | 1.1047 |  | -1.2796 | -2.5151 | 4.0138 | 3.3624 | 3.3498 | 1.0394 | 10.6583 | 14.1264 | 14.7368 | 11.028 | 0 | -0.0025 | 0.0003 | 0.0035 | 0.0007 | -0.0001 | 0.0002 | -0.0187 | -0.0258 | -360.1588 | 17.4644 | -360.525 | 17.6964 | -360.8204 | 18.1276 | -360.9035 | 17.5363 | -352.749 | 18.721 | -352.7552 | 16.8135
11:53 | 1995 | 25.912 | 195.9354 | 437.9754 | 444.4061 | -20.2123 | -46.944 | 4.3973 | 2.1002 | -4.6741 | -5.5117 | -1.5192 | -3.423 | 4.9264 | -1.8115 | 0.5902 | 0.6294 | 0.9549 | 0.7089 | -131.0429 | -5.9905 | 1.3853 | -0.1634 | -6.9217 | -5.6277 | 1.1315 |  | -1.1765 | -2.4682 | 4.014 | 3.3649 | 3.3448 | 1.0373 | 10.6653 | 14.1389 | 14.7129 | 11.0182 | -0.0001 | -0.003 | 0.0003 | 0.0036 | 0.0011 | -0.0004 | 0.0105 | -0.0101 | 0.0016 | -360.205 | 17.4664 | -360.5404 | 17.7395 | -360.8881 | 18.1481 | -360.9251 | 17.5486 | -352.7429 | 18.7292 | -352.7583 | 16.832
11:53 | 1996 | 25.9075 | 195.9522 | 437.8734 | 444.3181 | -20.1551 | -46.8737 | 4.4328 | 2.0611 | -4.7551 | -5.5396 | -1.5979 | -3.2836 | 4.9449 | -1.9323 | 0.5914 | 0.6281 | 0.9552 | 0.7081 | -131.0275 | -5.8433 | 1.3509 | -0.1851 | -6.8786 | -5.5764 | 1.1465 |  | -1.3243 | -2.6309 | 4.0133 | 3.3681 | 3.3497 | 1.0369 | 10.6619 | 14.1353 | 14.7551 | 11.0208 | -0.0002 | -0.0034 | 0.0007 | 0.0038 | 0.0005 | -0.0002 | 0.0034 | -0.0107 | -0.0065 | -360.1958 | 17.4603 | -360.5004 | 17.7087 | -360.845 | 18.1358 | -360.8943 | 17.5321 | -352.7367 | 18.721 | -352.7644 | 16.834
11:53 | 1997 | 25.9986 | 196.0082 | 437.9344 | 444.3718 | -20.2155 | -46.8366 | 4.4791 | 2.1938 | -4.698 | -5.441 | -1.5921 | -3.4263 | 4.8762 | -1.9058 | 0.5908 | 0.6288 | 0.9533 | 0.7081 | -131 | -5.9056 | 1.3499 | -0.2546 | -6.9137 | -5.6644 | 1.1373 |  | -1.3058 | -2.5072 | 4.0139 | 3.3653 | 3.3502 | 1.0364 | 10.6757 | 14.1378 | 14.7474 | 11.0341 | -0.0002 | -0.0027 | 0.0007 | 0.0036 | 0.001 | -0.0007 | -0.0071 | -0.0014 | -0.0222 | -360.2142 | 17.4747 | -360.525 | 17.7313 | -360.8881 | 18.1563 | -360.9281 | 17.5527 | -352.7583 | 18.7292 | -352.7706 | 16.8402
11:53 | 1998 | 25.9483 | 195.9728 | 437.8931 | 444.3795 | -20.1499 | -46.8399 | 4.444 | 2.1226 | -4.7054 | -5.367 | -1.5504 | -3.4204 | 4.8456 | -1.9311 | 0.5904 | 0.6272 | 0.9534 | 0.7076 | -130.9951 | -5.836 | 1.4185 | -0.254 | -6.8749 | -5.6241 | 1.1101 |  | -1.2697 | -2.5153 | 4.0138 | 3.3632 | 3.346 | 1.0368 | 10.6377 | 14.0992 | 14.6938 | 11.0147 | -0.0004 | -0.0029 | 0.0011 | 0.0043 | -0.0001 | -0.0007 | -0.0006 | -0.0062 | -0.0189 | -360.1281 | 17.4644 | -360.5035 | 17.7005 | -360.8174 | 18.1379 | -360.9004 | 17.5239 | -352.6906 | 18.7292 | -352.789 | 16.8299
11:53 | 1999 | 25.8996 | 195.9847 | 437.9857 | 444.4268 | -20.109 | -46.7725 | 4.4472 | 2.0208 | -4.6861 | -5.3456 | -1.5693 | -3.3825 | 4.8595 | -1.9776 | 0.5907 | 0.6318 | 0.9574 | 0.7096 | -130.9422 | -5.8847 | 1.4681 | -0.2295 | -6.8088 | -5.5685 | 1.1382 |  | -1.2327 | -2.4876 | 4.0138 | 3.3647 | 3.347 | 1.0377 | 10.6376 | 14.0994 | 14.7017 | 10.9908 | -0.0001 | -0.0029 | 0.0008 | 0.0035 | 0.0009 | -0.0012 | 0.0137 | -0.0211 | -0.0015 | -360.2173 | 17.4664 | -360.5404 | 17.7354 | -360.8758 | 18.144 | -360.9374 | 17.5486 | -352.749 | 18.7312 | -352.786 | 16.8443
11:53 | 2000 | 25.9721 | 195.978 | 437.9991 | 444.4161 | -20.1949 | -46.8765 | 4.4094 | 2.121 | -4.6726 | -5.4723 | -1.5617 | -3.4019 | 4.8929 | -1.8688 | 0.5914 | 0.632 | 0.9527 | 0.7104 | -131.03 | -5.8892 | 1.4521 | -0.3745 | -6.8366 | -5.5857 | 1.1409 |  | -1.2853 | -2.5332 | 4.0145 | 3.3618 | 3.3495 | 1.039 | 10.6423 | 14.1327 | 14.7156 | 11.0136 | -0.0001 | -0.0034 | 0.0006 | 0.0038 | 0.0005 | -0.0006 | -0.0022 | -0.0054 | -0.0043 | -360.1958 | 17.4541 | -360.4789 | 17.6923 | -360.8266 | 18.1296 | -360.9004 | 17.5445 | -352.7644 | 18.723 | -352.7398 | 16.8012
11:53 | 2001 | 25.9694 | 195.9111 | 437.9601 | 444.4817 | -20.147 | -47.1259 | 4.3354 | 2.0885 | -4.5999 | -5.4316 | -1.4907 | -3.2969 | 4.8758 | -1.841 | 0.591 | 0.6306 | 0.9514 | 0.7076 | -131.1009 | -5.936 | 1.432 | -0.356 | -6.9182 | -5.6227 | 1.143 |  | -1.2295 | -2.4653 | 4.0133 | 3.3608 | 3.349 | 1.0367 | 10.6284 | 14.0901 | 14.7034 | 10.9876 | 0 | -0.003 | 0.0008 | 0.0036 | 0.001 | -0.0005 | -0.0003 | -0.008 | -0.0319 | -360.1927 | 17.4623 | -360.5189 | 17.7272 | -360.8389 | 18.1379 | -360.9158 | 17.5506 | -352.7706 | 18.7374 | -352.789 | 16.834
11:53 | 2002 | 25.9242 | 195.9191 | 437.9878 | 444.4278 | -20.1276 | -47.0283 | 4.387 | 2.1559 | -4.5749 | -5.3858 | -1.5265 | -3.3274 | 4.77 | -1.942 | 0.5884 | 0.6327 | 0.9513 | 0.7077 | -131.0959 | -5.9036 | 1.4092 | -0.3073 | -6.9066 | -5.6333 | 1.1425 |  | -1.1598 | -2.5075 | 4.0146 | 3.3657 | 3.3467 | 1.0379 | 10.6723 | 14.1285 | 14.6796 | 11.0309 | -0.0002 | -0.0027 | 0.001 | 0.0039 | 0.0006 | -0.0006 | 0.0012 | -0.0113 | -0.0196 | -360.1435 | 17.4521 | -360.5466 | 17.7498 | -360.8481 | 18.1337 | -360.9281 | 17.5301 | -352.7121 | 18.7292 | -352.7798 | 16.8279
11:53 | 2003 | 25.8947 | 195.8994 | 437.9791 | 444.4225 | -20.2241 | -47.085 | 4.3047 | 2.2154 | -4.582 | -5.3906 | -1.5129 | -3.341 | 4.7834 | -1.9333 | 0.5904 | 0.6334 | 0.9529 | 0.7075 | -131.1378 | -5.9348 | 1.4384 | -0.3682 | -6.8938 | -5.5611 | 1.1386 |  | -1.234 | -2.5103 | 4.0141 | 3.3597 | 3.3497 | 1.0368 | 10.6654 | 14.1444 | 14.734 | 11.0132 | -0.0006 | -0.0033 | 0.0006 | 0.0038 | 0.0002 | -0.0004 | 0.0068 | -0.0117 | -0.0043 | -360.1804 | 17.4336 | -360.4942 | 17.7498 | -360.885 | 18.1502 | -360.9527 | 17.5239 | -352.749 | 18.7271 | -352.7213 | 16.8423
11:53 | 2004 | 25.8629 | 195.892 | 438.0102 | 444.3317 | -20.1915 | -47.01 | 4.4844 | 2.2117 | -4.5919 | -5.3972 | -1.4702 | -3.4689 | 4.8671 | -1.92 | 0.5904 | 0.6327 | 0.9535 | 0.7079 | -131.0734 | -5.9253 | 1.4779 | -0.3887 | -6.9388 | -5.486 | 1.1943 |  | -1.2566 | -2.5129 | 4.0148 | 3.3647 | 3.3488 | 1.0383 | 10.6998 | 14.1278 | 14.7287 | 11.0456 | 0.0004 | -0.003 | 0.001 | 0.0045 | 0.0015 | -0.0002 | 0.0006 | -0.0137 | -0.0049 | -360.1804 | 17.448 | -360.5158 | 17.721 | -360.8574 | 18.1481 | -360.9435 | 17.5506 | -352.7614 | 18.7271 | -352.7337 | 16.8381
11:53 | 2005 | 25.9002 | 195.9819 | 437.9707 | 444.3722 | -20.215 | -47.0612 | 4.5093 | 2.2203 | -4.6223 | -5.3863 | -1.5106 | -3.326 | 4.87 | -1.9037 | 0.5902 | 0.6342 | 0.9536 | 0.7101 | -131.0754 | -6.0023 | 1.3735 | -0.3642 | -6.9301 | -5.5497 | 1.1775 |  | -1.2333 | -2.4687 | 4.0128 | 3.3621 | 3.3469 | 1.0375 | 10.685 | 14.1644 | 14.7504 | 11.0551 | -0.0004 | -0.0033 | 0.0004 | 0.0034 | 0.0004 | -0.0003 | 0.0099 | 0.0042 | -0.0195 | -360.2142 | 17.4829 | -360.5435 | 17.7313 | -360.8512 | 18.1132 | -360.8512 | 17.528 | -352.7767 | 18.7641 | -352.7921 | 16.834
11:53 | 2006 | 25.8997 | 195.9973 | 438.0847 | 444.4547 | -20.0773 | -46.95 | 4.5043 | 2.1769 | -4.5997 | -5.358 | -1.4359 | -3.3478 | 4.9143 | -1.8678 | 0.5917 | 0.6341 | 0.9539 | 0.7092 | -131.1353 | -6.0222 | 1.3361 | -0.2027 | -6.9544 | -5.4873 | 1.1341 |  | -1.1726 | -2.4672 | 4.0154 | 3.363 | 3.3509 | 1.0369 | 10.6539 | 14.1212 | 14.6935 | 11.0306 | -0.0004 | -0.0026 | 0.0003 | 0.0034 | 0.0012 | -0.0006 | 0.0098 | -0.0017 | -0.0168 | -360.1835 | 17.489 | -360.5835 | 17.7457 | -360.9127 | 18.1296 | -360.8912 | 17.5342 | -352.7398 | 18.7477 | -352.8352 | 16.8525
11:53 | 2007 | 25.9124 | 195.9971 | 437.9468 | 444.393 | -20.1445 | -47.0437 | 4.4733 | 2.1313 | -4.5881 | -5.2978 | -1.4508 | -3.2289 | 5.0077 | -1.8148 | 0.5911 | 0.6293 | 0.9532 | 0.7098 | -131.0688 | -5.8459 | 1.3751 | -0.2274 | -6.9543 | -5.5582 | 1.1296 |  | -1.2123 | -2.5453 | 4.0124 | 3.3643 | 3.3485 | 1.0364 | 10.6468 | 14.1261 | 14.7231 | 11.0114 | -0.0002 | -0.0027 | 0.0007 | 0.0038 | 0 | -0.0009 | 0.0238 | 0.008 | 0.0111 | -360.165 | 17.4254 | -360.4635 | 17.7149 | -360.845 | 18.142 | -360.9251 | 17.5363 | -352.7152 | 18.7128 | -352.7183 | 16.8197
11:53 | 2008 | 25.971 | 196.0752 | 438.0693 | 444.3886 | -20.1165 | -46.9181 | 4.5498 | 2.0659 | -4.639 | -5.3603 | -1.4963 | -3.2716 | 4.9309 | -1.8055 | 0.5906 | 0.6284 | 0.9543 | 0.7101 | -130.9442 | -5.8279 | 1.4434 | -0.2332 | -6.9915 | -5.4609 | 1.1344 |  | -1.0743 | -2.4856 | 4.0135 | 3.3638 | 3.3477 | 1.0367 | 10.6273 | 14.1235 | 14.6836 | 11.01 | 0.0001 | -0.0033 | 0.0005 | 0.0032 | 0.001 | -0.0004 | 0.0051 | -0.0111 | -0.0185 | -360.2388 | 17.4829 | -360.5189 | 17.7005 | -360.8297 | 18.1461 | -360.9527 | 17.5814 | -352.8075 | 18.7579 | -352.7767 | 16.8135
11:53 | 2009 | 25.9694 | 196.0112 | 438.0232 | 444.3708 | -20.0558 | -47.0572 | 4.528 | 2.1304 | -4.667 | -5.3788 | -1.46 | -3.2647 | 4.9651 | -1.911 | 0.5908 | 0.6308 | 0.9524 | 0.7108 | -131.0183 | -5.9018 | 1.4597 | -0.2611 | -6.8593 | -5.4909 | 1.2067 |  | -1.1855 | -2.3533 | 4.0137 | 3.3664 | 3.3482 | 1.0388 | 10.6343 | 14.1072 | 14.6723 | 11.0115 | 0 | -0.0034 | 0.0005 | 0.0036 | 0.0006 | -0.0005 | 0.01 | -0.0141 | -0.0194 | -360.1835 | 17.4603 | -360.5127 | 17.7128 | -360.8204 | 18.1194 | -360.882 | 17.528 | -352.7644 | 18.7518 | -352.7737 | 16.834
11:53 | 2010 | 25.9526 | 195.9941 | 437.9188 | 444.3436 | -20.0494 | -46.8889 | 4.5841 | 2.1317 | -4.6693 | -5.326 | -1.5092 | -3.1857 | 4.9789 | -1.9351 | 0.592 | 0.633 | 0.9576 | 0.7101 | -131.0407 | -5.8468 | 1.3829 | -0.2578 | -6.8977 | -5.4975 | 1.1948 |  | -1.2278 | -2.3464 | 4.0136 | 3.3665 | 3.351 | 1.039 | 10.6618 | 14.1239 | 14.6983 | 11.032 | -0.0003 | -0.0027 | 0.0008 | 0.0043 | 0.0007 | -0.0007 | -0.0024 | -0.0123 | -0.012 | -360.1711 | 17.4521 | -360.5343 | 17.7724 | -360.9343 | 18.1584 | -360.9343 | 17.5239 | -352.6967 | 18.7333 | -352.7829 | 16.8607
11:53 | 2011 | 25.9201 | 195.9726 | 437.913 | 444.2761 | -20.0676 | -46.8869 | 4.454 | 2.1488 | -4.6033 | -5.2346 | -1.4687 | -3.2686 | 4.9265 | -1.9115 | 0.5915 | 0.6301 | 0.9545 | 0.7108 | -131.071 | -5.8563 | 1.4186 | -0.225 | -6.9368 | -5.5446 | 1.2026 |  | -1.1978 | -2.3699 | 4.0137 | 3.3643 | 3.3483 | 1.0376 | 10.6838 | 14.14 | 14.7027 | 11.0309 | -0.0002 | -0.0024 | 0.0004 | 0.0037 | 0.0007 | 0 | 0.0054 | -0.0046 | -0.0132 | -360.1311 | 17.4233 | -360.4604 | 17.721 | -360.8481 | 18.1481 | -360.9466 | 17.5301 | -352.7337 | 18.7128 | -352.6967 | 16.8258
11:53 | 2012 | 25.9719 | 195.911 | 438.0885 | 444.3443 | -20.1255 | -46.9017 | 4.6233 | 2.1001 | -4.6849 | -5.3801 | -1.4519 | -3.2625 | 4.9537 | -1.9782 | 0.5912 | 0.6306 | 0.9541 | 0.7099 | -131.0401 | -5.8916 | 1.4111 | -0.2953 | -6.9749 | -5.5199 | 1.2532 |  | -1.1148 | -2.3362 | 4.0142 | 3.3609 | 3.3464 | 1.0358 | 10.6597 | 14.1095 | 14.623 | 11.0021 | 0 | -0.003 | 0.0005 | 0.0041 | 0.0006 | -0.0006 | 0.0132 | 0.0071 | -0.0027 | -360.2573 | 17.4829 | -360.5435 | 17.7067 | -360.8389 | 18.1296 | -360.9312 | 17.5547 | -352.7675 | 18.76 | -352.7921 | 16.8238
11:53 | 2013 | 25.9856 | 196.098 | 438.0783 | 444.3482 | -20.194 | -46.9508 | 4.7218 | 2.0287 | -4.6888 | -5.4084 | -1.4387 | -3.2963 | 4.9315 | -1.9619 | 0.5902 | 0.6304 | 0.9551 | 0.7098 | -131.0331 | -5.9128 | 1.4266 | -0.3306 | -6.8153 | -5.4101 | 1.3245 |  | -1.1469 | -2.3495 | 4.0131 | 3.3613 | 3.3475 | 1.0361 | 10.6618 | 14.1065 | 14.733 | 11.0262 | 0.0002 | -0.0028 | 0.0006 | 0.0036 | 0.0007 | -0.0004 | 0.0041 | -0.0157 | -0.0057 | -360.1896 | 17.4685 | -360.5496 | 17.7231 | -360.8697 | 18.1153 | -360.8481 | 17.5034 | -352.7121 | 18.7559 | -352.8044 | 16.8546
11:53 | 2014 | 25.9568 | 195.911 | 438.0569 | 444.3172 | -20.1082 | -46.9768 | 4.7273 | 2.0585 | -4.7338 | -5.3431 | -1.4359 | -3.2804 | 4.9137 | -1.7892 | 0.5916 | 0.6328 | 0.9562 | 0.7109 | -131.0516 | -6.0142 | 1.3835 | -0.2523 | -6.8308 | -5.5584 | 1.2255 |  | -1.1341 | -2.3946 | 4.014 | 3.363 | 3.3497 | 1.0367 | 10.6608 | 14.1282 | 14.689 | 11.0316 | -0.0002 | -0.0031 | 0.0001 | 0.0031 | 0 | -0.0006 | 0 | -0.0026 | -0.0194 | -360.165 | 17.4582 | -360.5404 | 17.7313 | -360.9004 | 18.1543 | -360.922 | 17.5219 | -352.6875 | 18.7456 | -352.7644 | 16.8464
11:53 | 2015 | 25.9389 | 195.9627 | 438.0027 | 444.4042 | -20.119 | -46.8733 | 4.7832 | 2.1384 | -4.6927 | -5.2744 | -1.4402 | -3.1696 | 5.0345 | -1.7767 | 0.5905 | 0.6317 | 0.9526 | 0.7093 | -131.0393 | -5.9053 | 1.383 | -0.1093 | -6.8435 | -5.5365 | 1.1837 |  | -1.0825 | -2.3931 | 4.0136 | 3.364 | 3.3463 | 1.0376 | 10.5997 | 14.0952 | 14.6865 | 10.9664 | -0.0007 | -0.0031 | 0.0002 | 0.0035 | 0.0005 | -0.0012 | -0.0019 | -0.0007 | -0.014 | -360.1773 | 17.4336 | -360.4635 | 17.7005 | -360.8327 | 18.144 | -360.9281 | 17.5547 | -352.7644 | 18.7374 | -352.7152 | 16.8258
11:53 | 2016 | 26.0178 | 196.0092 | 438.1629 | 444.3916 | -20.0942 | -46.9338 | 4.65 | 2.0759 | -4.7263 | -5.3581 | -1.5112 | -3.1742 | 5.0138 | -1.7941 | 0.5921 | 0.6297 | 0.9525 | 0.7101 | -130.9974 | -5.9891 | 1.419 | -0.0631 | -6.8288 | -5.5267 | 1.2341 |  | -1.1209 | -2.412 | 4.0135 | 3.3632 | 3.3496 | 1.0378 | 10.6711 | 14.1157 | 14.6782 | 11.0298 | 0.0002 | -0.0024 | 0.0004 | 0.0032 | 0.0005 | -0.0004 | -0.0024 | -0.0095 | -0.0058 | -360.2327 | 17.487 | -360.525 | 17.7046 | -360.8174 | 18.1296 | -360.9066 | 17.5691 | -352.8075 | 18.7661 | -352.7737 | 16.8053
11:53 | 2017 | 26.1557 | 196.0375 | 438.0174 | 444.4761 | -20.0973 | -46.9756 | 4.5776 | 2.0843 | -4.773 | -5.4346 | -1.5413 | -3.198 | 5.0063 | -1.7769 | 0.5903 | 0.6306 | 0.9537 | 0.7099 | -131.0295 | -5.8661 | 1.4231 | -0.0813 | -6.7873 | -5.449 | 1.2682 |  | -1.1672 | -2.4291 | 4.0128 | 3.3631 | 3.3487 | 1.0392 | 10.6482 | 14.1093 | 14.7019 | 11.0028 | -0.0003 | -0.0031 | 0.0003 | 0.0033 | 0.0001 | -0.0015 | -0.0001 | -0.0094 | -0.0301 | -360.1527 | 17.4603 | -360.5189 | 17.7313 | -360.845 | 18.1153 | -360.8974 | 17.5219 | -352.7337 | 18.7477 | -352.7767 | 16.8381
11:53 | 2018 | 26.039 | 195.9516 | 438.0501 | 444.4123 | -20.2038 | -47.0107 | 4.6246 | 2.1095 | -4.733 | -5.2349 | -1.5427 | -3.0691 | 5.0778 | -1.6406 | 0.5907 | 0.6286 | 0.9547 | 0.7113 | -131.1555 | -5.855 | 1.3939 | -0.2787 | -6.8456 | -5.4867 | 1.2061 |  | -1.2001 | -2.548 | 4.0126 | 3.3655 | 3.3491 | 1.0387 | 10.6549 | 14.1343 | 14.6969 | 11.0136 | 0.0001 | -0.0028 | 0.0009 | 0.0039 | 0.0002 | -0.0003 | -0.0002 | -0.0097 | -0.0207 | -360.1219 | 17.4439 | -360.485 | 17.7293 | -360.9035 | 18.1707 | -360.9651 | 17.5301 | -352.7306 | 18.7271 | -352.7706 | 16.8423
11:53 | 2019 | 26.0336 | 196.0307 | 437.9773 | 444.4328 | -20.182 | -47.058 | 4.5916 | 2.1982 | -4.7197 | -5.3933 | -1.5504 | -3.1237 | 5.0305 | -1.8507 | 0.5917 | 0.6296 | 0.9536 | 0.7099 | -131.0635 | -5.7982 | 1.4974 | -0.312 | -6.8132 | -5.5578 | 1.1572 |  | -1.2953 | -2.4687 | 4.013 | 3.3658 | 3.3488 | 1.0376 | 10.6698 | 14.1381 | 14.7379 | 11.0334 | -0.0002 | -0.0025 | 0.0005 | 0.0038 | 0.001 | -0.0005 | 0.0148 | -0.0087 | -0.0006 | -360.165 | 17.4295 | -360.4942 | 17.7046 | -360.8174 | 18.1481 | -360.9404 | 17.5404 | -352.7398 | 18.723 | -352.7244 | 16.834
11:53 | 2020 | 26.0016 | 195.9734 | 437.9584 | 444.4521 | -20.2089 | -46.9922 | 4.5091 | 2.1606 | -4.6768 | -5.359 | -1.59 | -3.1133 | 4.9838 | -1.7002 | 0.5898 | 0.6297 | 0.9543 | 0.7085 | -131.1113 | -5.8123 | 1.4037 | -0.2687 | -6.8755 | -5.4767 | 1.1099 |  | -1.1485 | -2.5067 | 4.0123 | 3.3647 | 3.3494 | 1.0365 | 10.6804 | 14.1538 | 14.7565 | 11.0334 | -0.0006 | -0.0027 | 0 | 0.0033 | 0.0005 | -0.001 | 0.0206 | -0.0084 | -0.0096 | -360.2081 | 17.4808 | -360.5496 | 17.7169 | -360.845 | 18.1296 | -360.9189 | 17.5424 | -352.789 | 18.7764 | -352.749 | 16.8238
11:53 | 2021 | 26.0218 | 195.9356 | 437.8824 | 444.4717 | -20.2717 | -47.0605 | 4.5383 | 2.1774 | -4.5968 | -5.2958 | -1.5891 | -3.1215 | 5.0548 | -1.7613 | 0.5917 | 0.6303 | 0.9568 | 0.7105 | -131.0655 | -5.9447 | 1.4246 | -0.2406 | -6.8825 | -5.602 | 1.1449 |  | -1.1755 | -2.5986 | 4.0136 | 3.3665 | 3.3482 | 1.0372 | 10.6514 | 14.1366 | 14.717 | 11.0562 | 0.0002 | -0.0032 | 0.0005 | 0.0036 | 0.0012 | -0.0002 | 0.0075 | -0.0064 | -0.0173 | -360.1342 | 17.4685 | -360.5589 | 17.7354 | -360.8666 | 18.1132 | -360.8543 | 17.5096 | -352.7367 | 18.7538 | -352.7983 | 16.8525
11:53 | 2022 | 26.1197 | 195.9467 | 437.9686 | 444.4758 | -20.2835 | -47.076 | 4.4785 | 2.1277 | -4.5732 | -5.4423 | -1.5799 | -3.1802 | 5.0521 | -1.6886 | 0.5914 | 0.6317 | 0.9578 | 0.7089 | -131.0232 | -5.8141 | 1.4157 | -0.2718 | -6.7779 | -5.5158 | 1.1162 |  | -1.182 | -2.408 | 4.0131 | 3.3634 | 3.351 | 1.0361 | 10.6746 | 14.1538 | 14.716 | 11.0334 | -0.0002 | -0.0033 | 0.0008 | 0.0038 | 0.0009 | -0.0004 | 0.008 | -0.0051 | 0.0022 | -360.1711 | 17.4664 | -360.5312 | 17.7334 | -360.8727 | 18.1481 | -360.9281 | 17.5321 | -352.7737 | 18.7579 | -352.749 | 16.8381
11:53 | 2023 | 26.1313 | 195.9525 | 438.1225 | 444.5228 | -20.3339 | -47.1532 | 4.4135 | 2.072 | -4.6267 | -5.4061 | -1.5235 | -3.0754 | 5.0955 | -1.6565 | 0.591 | 0.6299 | 0.9542 | 0.7108 | -131.0201 | -5.8476 | 1.3518 | -0.1791 | -6.7116 | -5.4034 | 1.1648 |  | -1.1645 | -2.5135 | 4.0123 | 3.3634 | 3.3482 | 1.0387 | 10.6228 | 14.1301 | 14.7002 | 11.0234 | -0.0007 | -0.003 | 0.0005 | 0.0036 | 0.0003 | -0.0006 | 0.001 | -0.0045 | -0.0125 | -360.1711 | 17.4459 | -360.4819 | 17.6944 | -360.7927 | 18.1235 | -360.9004 | 17.565 | -352.7675 | 18.7292 | -352.7275 | 16.8197
11:53 | 2024 | 26.1382 | 195.9357 | 438.1301 | 444.5308 | -20.2698 | -47.1037 | 4.3817 | 2.1908 | -4.6397 | -5.4148 | -1.5606 | -3.1041 | 5.0388 | -1.8243 | 0.5914 | 0.6304 | 0.9552 | 0.7097 | -131.0391 | -5.7698 | 1.4616 | -0.1165 | -6.7461 | -5.405 | 1.1869 |  | -1.1339 | -2.4212 | 4.0124 | 3.3613 | 3.3479 | 1.0383 | 10.6549 | 14.0994 | 14.7133 | 11.0139 | -0.0004 | -0.0029 | 0.001 | 0.0038 | 0.001 | -0.0008 | -0.0021 | -0.0144 | 0.0018 | -360.2358 | 17.4911 | -360.5127 | 17.7108 | -360.845 | 18.1379 | -360.9374 | 17.5568 | -352.786 | 18.7661 | -352.7767 | 16.8238
11:53 | 2025 | 26.1571 | 195.9743 | 438.0568 | 444.5697 | -20.1865 | -47.0238 | 4.4791 | 2.1867 | -4.6865 | -5.3354 | -1.5304 | -3.0398 | 5.1597 | -1.6902 | 0.5923 | 0.635 | 0.9605 | 0.7099 | -131.0243 | -5.8021 | 1.4682 | -0.1667 | -6.7887 | -5.402 | 1.1999 |  | -1.1826 | -2.4794 | 4.0115 | 3.3633 | 3.3469 | 1.0376 | 10.6297 | 14.0907 | 14.6889 | 11.0133 | -0.0004 | -0.0032 | 0.0006 | 0.0036 | 0.0002 | -0.0007 | 0.0068 | -0.0111 | 0.0033 | -360.1158 | 17.448 | -360.5219 | 17.719 | -360.8389 | 18.1379 | -360.8912 | 17.5157 | -352.7275 | 18.7333 | -352.7706 | 16.8443
11:53 | 2026 | 26.0878 | 195.9625 | 438.0313 | 444.4433 | -20.1344 | -46.8101 | 4.5886 | 2.1587 | -4.7406 | -5.3059 | -1.5684 | -3.0673 | 5.1119 | -1.6506 | 0.592 | 0.6315 | 0.9551 | 0.7089 | -131.1331 | -5.87 | 1.4768 | -0.2155 | -6.9174 | -5.4819 | 1.1712 |  | -1.2321 | -2.5526 | 4.0129 | 3.3612 | 3.3458 | 1.0378 | 10.6572 | 14.1251 | 14.7286 | 11.0157 | -0.0001 | -0.0035 | 0.0014 | 0.0045 | 0.0009 | -0.0007 | 0.0244 | -0.012 | 0.0126 | -360.1404 | 17.4562 | -360.5189 | 17.7293 | -360.8943 | 18.1728 | -360.9343 | 17.5383 | -352.7367 | 18.7271 | -352.746 | 16.8505
11:53 | 2027 | 26.0817 | 195.8947 | 438.01 | 444.4954 | -20.1123 | -46.9271 | 4.6556 | 2.2254 | -4.7297 | -5.3047 | -1.5183 | -3.1245 | 5.0308 | -1.7032 | 0.592 | 0.6302 | 0.9579 | 0.7086 | -131.1036 | -5.8544 | 1.4478 | -0.1374 | -6.8476 | -5.4866 | 1.1814 |  | -1.2189 | -2.5229 | 4.0129 | 3.3607 | 3.349 | 1.038 | 10.6779 | 14.1461 | 14.7338 | 11.0532 | -0.0002 | -0.0028 | 0.0007 | 0.0037 | 0.001 | -0.0001 | -0.0041 | -0.0036 | -0.0159 | -360.1311 | 17.4377 | -360.4881 | 17.7067 | -360.805 | 18.1214 | -360.9066 | 17.5486 | -352.7213 | 18.7271 | -352.7337 | 16.8176
11:54 | 2028 | 26.123 | 195.9135 | 437.9706 | 444.4124 | -20.1026 | -46.9756 | 4.6455 | 2.1283 | -4.7494 | -5.2656 | -1.5448 | -3.1011 | 4.9854 | -1.7248 | 0.5907 | 0.6315 | 0.9562 | 0.7101 | -131.0867 | -5.8277 | 1.4075 | -0.1608 | -6.8181 | -5.4123 | 1.2387 |  | -1.1316 | -2.417 | 4.0136 | 3.3652 | 3.3479 | 1.039 | 10.6503 | 14.1412 | 14.7273 | 11.0724 | -0.0002 | -0.0023 | 0.0001 | 0.0038 | 0.0007 | -0.0005 | 0.0163 | 0.002 | 0.0057 | -360.2111 | 17.4993 | -360.5804 | 17.7539 | -360.882 | 18.1379 | -360.9004 | 17.5404 | -352.7521 | 18.7661 | -352.7952 | 16.8402
11:54 | 2029 | 26.1429 | 195.9405 | 438.0877 | 444.495 | -20.0997 | -46.8814 | 4.6357 | 2.1502 | -4.6312 | -5.2243 | -1.4725 | -3.0592 | 5.0508 | -1.7436 | 0.5923 | 0.6304 | 0.9554 | 0.7113 | -131.0743 | -5.8719 | 1.3667 | -0.175 | -6.7183 | -5.3712 | 1.1773 |  | -1.1501 | -2.4211 | 4.0124 | 3.3634 | 3.3488 | 1.0378 | 10.6688 | 14.1482 | 14.7402 | 11.0504 | -0.0001 | -0.0032 | 0.0008 | 0.0039 | 0.0008 | -0.0003 | -0.0083 | -0.0047 | -0.0306 | -360.1373 | 17.4521 | -360.5189 | 17.7375 | -360.8358 | 18.1276 | -360.8974 | 17.5096 | -352.6937 | 18.7415 | -352.7614 | 16.8279
11:54 | 2030 | 26.0996 | 195.9314 | 438.0019 | 444.4405 | -20.055 | -46.8783 | 4.7209 | 2.1158 | -4.6599 | -5.2603 | -1.4866 | -3.0558 | 4.999 | -1.8117 | 0.5921 | 0.6302 | 0.9568 | 0.7089 | -131.0302 | -5.8506 | 1.466 | -0.2524 | -6.6957 | -5.3656 | 1.1923 |  | -1.113 | -2.3506 | 4.0135 | 3.3598 | 3.3481 | 1.0385 | 10.6792 | 14.1701 | 14.7215 | 11.0377 | 0.0002 | -0.0029 | 0.0003 | 0.0033 | 0.0006 | -0.0008 | -0.0014 | -0.0022 | -0.0109 | -360.1804 | 17.4562 | -360.5035 | 17.7375 | -360.8543 | 18.144 | -360.9312 | 17.5527 | -352.7583 | 18.7456 | -352.749 | 16.8299
11:54 | 2031 | 26.1743 | 195.8879 | 438.043 | 444.4697 | -20.0385 | -46.9141 | 4.6356 | 2.1945 | -4.5473 | -5.2587 | -1.4229 | -3.0666 | 5.0481 | -1.7819 | 0.5908 | 0.6268 | 0.9566 | 0.7085 | -130.9997 | -5.8097 | 1.6175 | -0.1515 | -6.7933 | -5.3874 | 1.1436 |  | -1.1214 | -2.4059 | 4.0147 | 3.3675 | 3.3485 | 1.0391 | 10.6596 | 14.0808 | 14.6993 | 11.0306 | -0.0002 | -0.0031 | 0.0006 | 0.0036 | 0.0009 | -0.0008 | 0.0076 | -0.0061 | -0.01 | -360.1927 | 17.4664 | -360.485 | 17.7046 | -360.8174 | 18.1255 | -360.885 | 17.5363 | -352.7675 | 18.7661 | -352.7429 | 16.8053
11:54 | 2032 | 26.1816 | 195.9619 | 438.014 | 444.5037 | -20.034 | -46.904 | 4.6416 | 2.1817 | -4.614 | -5.211 | -1.408 | -3.1303 | 5.0761 | -1.7269 | 0.592 | 0.6305 | 0.9562 | 0.7087 | -131.0916 | -5.9061 | 1.5097 | -0.2121 | -6.834 | -5.4191 | 1.1811 |  | -1.0853 | -2.5337 | 4.0148 | 3.3646 | 3.3498 | 1.0392 | 10.6525 | 14.132 | 14.701 | 11.0168 | -0.0001 | -0.0026 | 0.001 | 0.0037 | 0.0005 | -0.0007 | 0.0021 | -0.0108 | -0.0174 | -360.1373 | 17.4644 | -360.525 | 17.7457 | -360.8727 | 18.142 | -360.9189 | 17.5301 | -352.7367 | 18.7559 | -352.786 | 16.8423
11:54 | 2033 | 26.169 | 196.0021 | 438.1259 | 444.5645 | -20.0749 | -46.8646 | 4.6628 | 2.1977 | -4.5249 | -5.301 | -1.4464 | -3.1308 | 5.0819 | -1.7265 | 0.5924 | 0.6333 | 0.956 | 0.7099 | -131.1048 | -5.8126 | 1.5486 | -0.2378 | -6.8165 | -5.4151 | 1.1378 |  | -1.1866 | -2.5149 | 4.0145 | 3.3616 | 3.3474 | 1.0385 | 10.6191 | 14.0981 | 14.6761 | 10.9728 | 0 | -0.0027 | 0.0007 | 0.0036 | 0.0006 | -0.0007 | 0.0183 | -0.0041 | 0.0056 | -360.165 | 17.4439 | -360.4881 | 17.7108 | -360.8727 | 18.1584 | -360.9312 | 17.5383 | -352.7367 | 18.7497 | -352.7367 | 16.8094
11:54 | 2034 | 26.2263 | 196.0321 | 438.0422 | 444.5017 | -20.1087 | -46.8682 | 4.6423 | 2.2989 | -4.3782 | -5.1447 | -1.3633 | -3.1789 | 4.9999 | -1.7591 | 0.5918 | 0.6318 | 0.954 | 0.7096 | -131.098 | -5.7418 | 1.5501 | -0.1279 | -6.7398 | -5.3659 | 1.2013 |  | -1.1276 | -2.5312 | 4.0145 | 3.3653 | 3.3496 | 1.0392 | 10.6295 | 14.1028 | 14.7105 | 10.9829 | 0 | -0.003 | 0.0011 | 0.0041 | 0.0004 | -0.0005 | 0.003 | -0.0124 | -0.0051 | -360.1896 | 17.4541 | -360.5035 | 17.721 | -360.8327 | 18.1214 | -360.9189 | 17.5465 | -352.7183 | 18.7682 | -352.7521 | 16.8197
11:54 | 2035 | 26.2238 | 196.0582 | 438.1185 | 444.4662 | -20.0527 | -46.8522 | 4.5963 | 2.3417 | -4.4007 | -5.034 | -1.2991 | -3.1587 | 5.0391 | -1.7185 | 0.5921 | 0.6306 | 0.9557 | 0.7094 | -131.0618 | -5.798 | 1.5283 | -0.2268 | -6.7703 | -5.4666 | 1.1453 |  | -1.1368 | -2.5196 | 4.0147 | 3.3644 | 3.3483 | 1.0395 | 10.678 | 14.1402 | 14.7269 | 11.0189 | 0.0006 | -0.0028 | 0.0007 | 0.0038 | 0.0008 | -0.0008 | 0.0132 | 0.0056 | -0.0002 | -360.1742 | 17.4685 | -360.5281 | 17.7395 | -360.8881 | 18.1502 | -360.8912 | 17.5404 | -352.7429 | 18.7682 | -352.8014 | 16.8258
11:54 | 2036 | 26.2283 | 196.1334 | 438.062 | 444.4187 | -19.9931 | -46.9283 | 4.6353 | 2.1913 | -4.5123 | -5.1042 | -1.4343 | -3.0892 | 5.0401 | -1.6766 | 0.5906 | 0.6321 | 0.9504 | 0.7085 | -130.9839 | -5.8502 | 1.4335 | -0.2408 | -6.8423 | -5.5635 | 1.0796 |  | -1.1249 | -2.5145 | 4.0125 | 3.3627 | 3.3468 | 1.0384 | 10.685 | 14.1526 | 14.732 | 11.0266 | -0.0004 | -0.003 | 0.0005 | 0.0037 | 0.0008 | 0.0003 | -0.0064 | 0.0061 | -0.0254 | -360.1281 | 17.4521 | -360.4942 | 17.7087 | -360.842 | 18.1461 | -360.9066 | 17.5342 | -352.709 | 18.7497 | -352.7306 | 16.8074
11:54 | 2037 | 26.1875 | 196.1003 | 438.0765 | 444.5239 | -20.0535 | -46.9697 | 4.6362 | 2.2334 | -4.5308 | -5.0816 | -1.4167 | -3.1133 | 5.0739 | -1.6604 | 0.592 | 0.6326 | 0.9546 | 0.7102 | -131.0211 | -5.8881 | 1.4215 | -0.2097 | -6.9022 | -5.4949 | 1.0773 |  | -1.1508 | -2.5743 | 4.0143 | 3.3645 | 3.3471 | 1.0386 | 10.6469 | 14.12 | 14.6979 | 11.0064 | -0.0006 | -0.0026 | 0.0004 | 0.0039 | 0.0009 | -0.0008 | 0.0042 | -0.0043 | -0.0204 | -360.2081 | 17.4705 | -360.5189 | 17.721 | -360.8543 | 18.1543 | -360.9281 | 17.5588 | -352.7552 | 18.7703 | -352.8167 | 16.8217
11:54 | 2038 | 26.2641 | 196.1274 | 438.1438 | 444.562 | -20.1113 | -46.9918 | 4.7245 | 2.2187 | -4.5557 | -5.2239 | -1.4572 | -3.1015 | 5.1168 | -1.7121 | 0.5926 | 0.6322 | 0.9578 | 0.7104 | -131.0969 | -5.8925 | 1.4316 | -0.1429 | -6.8913 | -5.4411 | 1.1436 |  | -1.1758 | -2.5924 | 4.0146 | 3.3662 | 3.3463 | 1.0395 | 10.6977 | 14.1423 | 14.7623 | 11.0276 | 0.0002 | -0.0033 | 0.0006 | 0.0034 | 0.0009 | -0.0003 | 0.0037 | -0.0148 | -0.0085 | -360.165 | 17.4418 | -360.4973 | 17.7087 | -360.8204 | 18.1461 | -360.8727 | 17.5363 | -352.7429 | 18.7436 | -352.7244 | 16.8176
11:54 | 2039 | 26.2556 | 196.1076 | 438.1644 | 444.4957 | -20.1802 | -46.9148 | 4.7056 | 2.274 | -4.5998 | -5.2022 | -1.5321 | -3.1119 | 5.0623 | -1.6825 | 0.5929 | 0.6334 | 0.9558 | 0.7114 | -131.0912 | -5.8437 | 1.4625 | -0.1806 | -6.8606 | -5.3975 | 1.2183 |  | -1.1569 | -2.612 | 4.0148 | 3.3624 | 3.3449 | 1.0369 | 10.662 | 14.1119 | 14.7125 | 11.0389 | 0 | -0.0028 | 0.0004 | 0.0034 | 0.0009 | -0.0005 | -0.0067 | -0.0225 | -0.0051 | -360.1588 | 17.4726 | -360.5219 | 17.7272 | -360.8758 | 18.1871 | -360.9466 | 17.5486 | -352.789 | 18.7641 | -352.7829 | 16.834
11:54 | 2040 | 26.2976 | 196.1901 | 438.0684 | 444.5206 | -20.1047 | -46.9552 | 4.7477 | 2.308 | -4.5557 | -5.1598 | -1.4109 | -3.1477 | 4.9702 | -1.6367 | 0.5931 | 0.6316 | 0.9539 | 0.7109 | -131.182 | -5.8346 | 1.4604 | -0.3059 | -6.9397 | -5.4821 | 1.1618 |  | -1.1506 | -2.4634 | 4.0141 | 3.3655 | 3.345 | 1.0378 | 10.6399 | 14.1074 | 14.6918 | 11.0338 | -0.0002 | -0.0029 | 0.0013 | 0.004 | 0.0008 | -0.0011 | 0.0099 | -0.0045 | -0.0106 | -360.1619 | 17.4418 | -360.4942 | 17.719 | -360.8512 | 18.1543 | -360.9158 | 17.5321 | -352.7029 | 18.7395 | -352.7429 | 16.8279
11:54 | 2041 | 26.2734 | 196.1102 | 438.0213 | 444.4406 | -20.172 | -47.093 | 4.6909 | 2.1975 | -4.5873 | -5.2487 | -1.4757 | -3.1252 | 5.0348 | -1.6217 | 0.591 | 0.6305 | 0.9524 | 0.7094 | -131.1737 | -5.8422 | 1.5399 | -0.2565 | -6.9094 | -5.5232 | 1.094 |  | -1.1261 | -2.4788 | 4.0158 | 3.364 | 3.3496 | 1.0392 | 10.6712 | 14.1328 | 14.7108 | 11.0363 | -0.0005 | -0.0027 | 0.0008 | 0.004 | 0.0005 | -0.0005 | 0.0012 | 0.0034 | -0.0089 | -360.1835 | 17.4664 | -360.5127 | 17.719 | -360.8727 | 18.1707 | -360.9127 | 17.5445 | -352.6998 | 18.7579 | -352.7767 | 16.8381
11:54 | 2042 | 26.2215 | 196.184 | 438.1249 | 444.473 | -20.17 | -47.0557 | 4.703 | 2.2112 | -4.5683 | -5.1456 | -1.5144 | -3.0139 | 5.0124 | -1.6426 | 0.5921 | 0.6337 | 0.9563 | 0.711 | -131.1755 | -5.9194 | 1.5313 | -0.3451 | -6.8528 | -5.4338 | 1.1277 |  | -1.0499 | -2.4823 | 4.0141 | 3.363 | 3.3488 | 1.0378 | 10.6642 | 14.0971 | 14.6989 | 11.0464 | 0 | -0.003 | 0.0007 | 0.0037 | 0.0005 | -0.0013 | -0.0015 | -0.0105 | -0.0178 | -360.1619 | 17.4521 | -360.5066 | 17.7149 | -360.845 | 18.1625 | -360.9435 | 17.5198 | -352.709 | 18.7374 | -352.7367 | 16.8156
11:54 | 2043 | 26.2913 | 196.1312 | 438.115 | 444.5175 | -20.0645 | -46.9485 | 4.6982 | 2.2608 | -4.6035 | -5.1371 | -1.478 | -3.0489 | 4.9796 | -1.7205 | 0.5927 | 0.6349 | 0.9554 | 0.7099 | -131.1392 | -5.8285 | 1.4468 | -0.4302 | -6.8701 | -5.388 | 1.1011 |  | -1.1045 | -2.5354 | 4.0162 | 3.3647 | 3.3457 | 1.0369 | 10.6655 | 14.1384 | 14.704 | 10.9963 | -0.0003 | -0.0037 | 0.0002 | 0.0037 | 0.0001 | -0.0005 | -0.0002 | -0.0112 | -0.0304 | -360.1958 | 17.4562 | -360.5219 | 17.719 | -360.8358 | 18.1563 | -360.8912 | 17.5342 | -352.7614 | 18.7559 | -352.7706 | 16.8176
11:54 | 2044 | 26.3663 | 196.2024 | 438.1915 | 444.5576 | -20.0354 | -47.0196 | 4.6883 | 2.1205 | -4.5709 | -5.1035 | -1.409 | -3.0581 | 5.0225 | -1.6928 | 0.5911 | 0.6298 | 0.9565 | 0.7101 | -131.0949 | -5.8167 | 1.5366 | -0.3518 | -6.8743 | -5.4138 | 1.1297 |  | -1.0283 | -2.5044 | 4.0146 | 3.3629 | 3.3481 | 1.0376 | 10.6931 | 14.1608 | 14.7405 | 11.0345 | -0.0003 | -0.0031 | 0.0004 | 0.0039 | 0.0012 | -0.0009 | -0.0052 | -0.014 | -0.0176 | -360.1558 | 17.4562 | -360.5404 | 17.719 | -360.845 | 18.1625 | -360.8943 | 17.5055 | -352.7275 | 18.7723 | -352.7398 | 16.8156
11:54 | 2045 | 26.3498 | 196.0874 | 438.2054 | 444.6163 | -20.0349 | -47.0129 | 4.6828 | 2.173 | -4.5281 | -5.0451 | -1.3591 | -3.098 | 5.0392 | -1.7341 | 0.5916 | 0.6346 | 0.9572 | 0.7102 | -131.1377 | -5.8898 | 1.456 | -0.2727 | -6.915 | -5.5236 | 1.2012 |  | -1.0104 | -2.4879 | 4.0166 | 3.3633 | 3.3484 | 1.0385 | 10.6585 | 14.0969 | 14.6979 | 10.989 | -0.0007 | -0.003 | 0.0004 | 0.0037 | 0.0006 | -0.0001 | -0.0015 | -0.0174 | -0.023 | -360.165 | 17.4521 | -360.4881 | 17.7231 | -360.8481 | 18.1604 | -360.9374 | 17.5219 | -352.7429 | 18.7477 | -352.7798 | 16.8217
11:54 | 2046 | 26.2791 | 196.1519 | 438.2199 | 444.5833 | -20.0795 | -46.9347 | 4.6275 | 2.1572 | -4.4989 | -5.0938 | -1.3781 | -3.1248 | 5.0031 | -1.6258 | 0.5918 | 0.6332 | 0.9596 | 0.7101 | -131.1579 | -5.8255 | 1.4956 | -0.1238 | -6.8116 | -5.4616 | 1.2376 |  | -1.0252 | -2.5245 | 4.0147 | 3.3624 | 3.3477 | 1.0369 | 10.6873 | 14.1145 | 14.7347 | 11.0287 | -0.0004 | -0.0027 | 0.0005 | 0.0037 | 0.0008 | -0.0004 | 0.0143 | -0.018 | -0.0187 | -360.2081 | 17.4705 | -360.5281 | 17.7252 | -360.8697 | 18.1604 | -360.9066 | 17.5342 | -352.7614 | 18.762 | -352.7644 | 16.8238
11:54 | 2047 | 26.2643 | 196.1121 | 438.0251 | 444.4552 | -20.0958 | -46.9425 | 4.6496 | 2.1766 | -4.4687 | -5.1624 | -1.4448 | -3.1036 | 5.0059 | -1.6383 | 0.5921 | 0.631 | 0.9574 | 0.7105 | -131.1496 | -5.8988 | 1.5173 | -0.1731 | -6.7254 | -5.4429 | 1.2034 |  | -1.1076 | -2.5156 | 4.0141 | 3.3611 | 3.3498 | 1.039 | 10.6607 | 14.1283 | 14.6959 | 11.0428 | 0.0001 | -0.0031 | 0.0005 | 0.0035 | 0.0008 | -0.0006 | 0.0113 | -0.009 | 0.0012 | -360.1404 | 17.448 | -360.5127 | 17.7108 | -360.8143 | 18.1728 | -360.885 | 17.5013 | -352.709 | 18.7477 | -352.7614 | 16.8279
11:54 | 2048 | 26.3112 | 196.0852 | 438.0822 | 444.506 | -20.1721 | -47.1278 | 4.5464 | 2.2148 | -4.3866 | -5.069 | -1.4091 | -3.1115 | 4.983 | -1.7158 | 0.5917 | 0.6326 | 0.9575 | 0.711 | -131.1378 | -5.9564 | 1.4615 | -0.2115 | -6.8619 | -5.4716 | 1.1913 |  | -1.0856 | -2.4849 | 4.0149 | 3.3625 | 3.3454 | 1.0384 | 10.6654 | 14.1039 | 14.7166 | 11.0306 | -0.0007 | -0.0036 | 0.0009 | 0.0035 | 0.0004 | -0.0009 | 0.001 | 0.009 | -0.016 | -360.1588 | 17.4459 | -360.5035 | 17.721 | -360.8697 | 18.181 | -360.9466 | 17.5363 | -352.7213 | 18.7415 | -352.7583 | 16.8258
11:54 | 2049 | 26.2013 | 196.0156 | 438.094 | 444.4543 | -20.1196 | -46.9824 | 4.5301 | 2.2853 | -4.3668 | -5.0702 | -1.4492 | -3.1435 | 5.0231 | -1.6899 | 0.591 | 0.6321 | 0.9562 | 0.7114 | -131.1915 | -5.932 | 1.4692 | -0.1401 | -6.7943 | -5.4102 | 1.2134 |  | -1.0962 | -2.4947 | 4.0162 | 3.3616 | 3.3463 | 1.0384 | 10.6712 | 14.1445 | 14.7119 | 11.0071 | -0.0003 | -0.0027 | 0.0009 | 0.0035 | 0.001 | -0.0005 | 0.0111 | -0.0018 | -0.0079 | -360.1804 | 17.4521 | -360.4973 | 17.7026 | -360.8358 | 18.1563 | -360.8943 | 17.5157 | -352.746 | 18.7497 | -352.7521 | 16.8464
11:54 | 2050 | 26.2547 | 196.0982 | 438.1387 | 444.5858 | -20.1808 | -47.0186 | 4.5018 | 2.2755 | -4.3947 | -5.1786 | -1.4683 | -3.1694 | 4.9557 | -1.6878 | 0.5909 | 0.6309 | 0.9518 | 0.7113 | -131.184 | -5.9165 | 1.4511 | -0.2696 | -6.8077 | -5.4387 | 1.1832 |  | -1.0307 | -2.4972 | 4.0169 | 3.3635 | 3.3501 | 1.0396 | 10.6792 | 14.1297 | 14.7215 | 11.032 | -0.0005 | -0.0032 | 0.0011 | 0.0038 | 0.0003 | -0.0007 | -0.0084 | -0.0074 | -0.0115 | -360.2111 | 17.4726 | -360.5681 | 17.7436 | -360.8881 | 18.1604 | -360.9097 | 17.5055 | -352.7121 | 18.7682 | -352.786 | 16.8546
11:54 | 2051 | 26.2463 | 196.1173 | 438.1517 | 444.5896 | -20.0659 | -47.0817 | 4.4643 | 2.219 | -4.4863 | -5.1065 | -1.5491 | -3.138 | 5.0241 | -1.661 | 0.5921 | 0.6318 | 0.9551 | 0.7122 | -131.0902 | -5.9634 | 1.4998 | -0.3114 | -6.8704 | -5.4718 | 1.2521 |  | -0.9782 | -2.4595 | 4.0169 | 3.3624 | 3.3474 | 1.0373 | 10.6584 | 14.1492 | 14.7116 | 11.0518 | 0.0001 | -0.0031 | 0.0006 | 0.0039 | 0.0012 | -0.0003 | 0.0242 | -0.0039 | -0.0119 | -360.1465 | 17.45 | -360.5066 | 17.7149 | -360.8574 | 18.1687 | -360.9066 | 17.5075 | -352.7121 | 18.7415 | -352.7521 | 16.8484
11:54 | 2052 | 26.3595 | 196.0809 | 438.107 | 444.5483 | -19.992 | -46.9308 | 4.5648 | 2.2772 | -4.3999 | -5.1904 | -1.5025 | -3.1048 | 5.0706 | -1.6735 | 0.5925 | 0.6322 | 0.9557 | 0.7117 | -131.1419 | -5.924 | 1.465 | -0.2949 | -6.7918 | -5.4419 | 1.2696 |  | -0.9522 | -2.3858 | 4.016 | 3.3636 | 3.3495 | 1.0388 | 10.6988 | 14.1264 | 14.7484 | 11.0569 | 0.0002 | -0.0031 | 0.0001 | 0.0035 | 0.0002 | -0.0005 | 0.0114 | -0.0052 | -0.0125 | -360.2296 | 17.4747 | -360.5066 | 17.721 | -360.845 | 18.1687 | -360.9158 | 17.526 | -352.7583 | 18.7764 | -352.7737 | 16.8012
11:54 | 2053 | 26.4035 | 196.1061 | 438.1566 | 444.5326 | -19.9922 | -46.9367 | 4.6281 | 2.2613 | -4.3276 | -5.0057 | -1.5015 | -3.0689 | 5.1432 | -1.606 | 0.5918 | 0.6288 | 0.9527 | 0.7098 | -131.1877 | -5.9782 | 1.3757 | -0.2225 | -6.7804 | -5.3845 | 1.2388 |  | -1.0385 | -2.3878 | 4.0141 | 3.3638 | 3.3484 | 1.0377 | 10.6643 | 14.1143 | 14.7268 | 11.041 | 0.0001 | -0.003 | 0.0006 | 0.0041 | 0.0008 | -0.0008 | 0.0123 | -0.0231 | -0.0118 | -360.1865 | 17.4603 | -360.5281 | 17.719 | -360.8204 | 18.142 | -360.8666 | 17.5116 | -352.7521 | 18.7518 | -352.7767 | 16.832
11:54 | 2054 | 26.4136 | 196.1133 | 438.2946 | 444.6055 | -19.9789 | -47.0341 | 4.635 | 2.2685 | -4.4079 | -5.0414 | -1.5529 | -3.0688 | 5.1392 | -1.532 | 0.5912 | 0.6289 | 0.9552 | 0.7106 | -131.2334 | -5.989 | 1.4831 | -0.2182 | -6.6983 | -5.423 | 1.2229 |  | -1.0218 | -2.4837 | 4.0153 | 3.3624 | 3.3483 | 1.0382 | 10.6721 | 14.1866 | 14.728 | 11.0417 | -0.0002 | -0.0023 | 0.0005 | 0.004 | 0.0004 | -0.0003 | 0.0244 | -0.01 | 0.0015 | -360.1496 | 17.448 | -360.5158 | 17.7272 | -360.8697 | 18.1933 | -360.9158 | 17.5055 | -352.7121 | 18.7395 | -352.7398 | 16.8279
11:54 | 2055 | 26.4101 | 196.1304 | 438.264 | 444.5994 | -20.007 | -47.1065 | 4.6551 | 2.2975 | -4.4171 | -5.0845 | -1.5175 | -3.0848 | 5.054 | -1.5591 | 0.592 | 0.6298 | 0.9557 | 0.7124 | -131.1895 | -6.0332 | 1.4194 | -0.2381 | -6.6566 | -5.3084 | 1.2639 |  | -1.0032 | -2.3816 | 4.016 | 3.3663 | 3.3475 | 1.0377 | 10.6781 | 14.1455 | 14.7238 | 11.0201 | -0.0002 | -0.0033 | 0.0008 | 0.0038 | 0.0009 | -0.0007 | -0.002 | -0.0012 | 0.0058 | -360.1527 | 17.448 | -360.4789 | 17.6964 | -360.7989 | 18.1748 | -360.9312 | 17.5219 | -352.7429 | 18.7518 | -352.7183 | 16.8197
11:54 | 2056 | 26.3993 | 196.0429 | 438.2463 | 444.5855 | -19.9703 | -46.947 | 4.8687 | 2.1838 | -4.393 | -5.0727 | -1.4866 | -3.0868 | 5.0917 | -1.5765 | 0.5911 | 0.631 | 0.9511 | 0.7108 | -131.1474 | -6.0971 | 1.3394 | -0.3339 | -6.7968 | -5.4326 | 1.1726 |  | -0.989 | -2.5517 | 4.0144 | 3.3615 | 3.3479 | 1.0381 | 10.6538 | 14.1387 | 14.7177 | 11.0417 | 0 | -0.0028 | 0.002 | 0.0044 | 0.0005 | -0.0005 | 0.0039 | -0.0132 | 0.0185 | -360.1896 | 17.4664 | -360.5281 | 17.7252 | -360.8327 | 18.1543 | -360.9004 | 17.5178 | -352.7521 | 18.7723 | -352.7767 | 16.8135
11:54 | 2057 | 26.5238 | 196.0571 | 438.2731 | 444.5724 | -19.9252 | -46.9001 | 4.8003 | 2.2168 | -4.4302 | -5.0954 | -1.5297 | -3.1031 | 5.0993 | -1.5009 | 0.5922 | 0.6312 | 0.9576 | 0.7118 | -131.2025 | -6.0454 | 1.3698 | -0.274 | -6.6961 | -5.4228 | 1.2629 |  | -1.0615 | -2.463 | 4.0151 | 3.361 | 3.3498 | 1.0378 | 10.6631 | 14.1306 | 14.686 | 11.0165 | -0.0003 | -0.0029 | 0.0007 | 0.0033 | 0.0012 | -0.0006 | 0.0095 | -0.0128 | -0.0082 | -360.1158 | 17.4439 | -360.525 | 17.7375 | -360.9035 | 18.1892 | -360.9127 | 17.5096 | -352.7121 | 18.7559 | -352.7798 | 16.8587
11:54 | 2058 | 26.4996 | 196.1697 | 438.1927 | 444.5981 | -19.8973 | -46.9106 | 4.913 | 2.2213 | -4.4598 | -5.1344 | -1.4158 | -3.2178 | 5.059 | -1.5565 | 0.5926 | 0.6324 | 0.9542 | 0.7109 | -131.1522 | -5.979 | 1.4104 | -0.2812 | -6.6844 | -5.3761 | 1.2866 |  | -0.9625 | -2.426 | 4.0158 | 3.3608 | 3.3495 | 1.0384 | 10.6691 | 14.1011 | 14.7281 | 11.0007 | -0.0008 | -0.0029 | 0.0005 | 0.0034 | 0.0003 | -0.001 | 0.0129 | -0.0163 | -0.0167 | -360.1527 | 17.4356 | -360.4912 | 17.7046 | -360.8204 | 18.1645 | -360.9097 | 17.5178 | -352.6844 | 18.7271 | -352.7213 | 16.8217
11:54 | 2059 | 26.5071 | 196.1105 | 438.2383 | 444.6234 | -19.973 | -46.8243 | 4.9112 | 2.2155 | -4.4844 | -5.1861 | -1.3834 | -3.2496 | 5.1082 | -1.5029 | 0.5926 | 0.6351 | 0.9515 | 0.7116 | -131.1332 | -5.9823 | 1.4681 | -0.2104 | -6.6834 | -5.4458 | 1.2556 |  | -1.0047 | -2.4567 | 4.0148 | 3.3593 | 3.3505 | 1.0379 | 10.6688 | 14.1191 | 14.6755 | 11.0045 | 0.0004 | -0.0024 | 0.0007 | 0.0047 | 0.0007 | -0.0003 | -0.0035 | -0.0056 | 0.0024 | -360.2481 | 17.4808 | -360.5435 | 17.7231 | -360.8512 | 18.1707 | -360.8881 | 17.5342 | -352.7829 | 18.7785 | -352.7798 | 16.834
11:54 | 2060 | 26.4868 | 196.0745 | 438.2257 | 444.6089 | -19.9755 | -46.8805 | 4.8592 | 2.2592 | -4.4879 | -5.1518 | -1.3942 | -3.2212 | 5.1395 | -1.5603 | 0.5935 | 0.633 | 0.9581 | 0.7112 | -131.1767 | -6.005 | 1.461 | -0.2453 | -6.7408 | -5.4738 | 1.2195 |  | -1.0137 | -2.4086 | 4.0145 | 3.36 | 3.3482 | 1.039 | 10.677 | 14.127 | 14.734 | 11.0132 | 0.0001 | -0.0035 | 0.0004 | 0.0036 | 0.0009 | -0.0008 | 0.0071 | -0.0244 | -0.0166 | -360.1158 | 17.4582 | -360.525 | 17.7169 | -360.8358 | 18.1481 | -360.882 | 17.4911 | -352.7121 | 18.7497 | -352.7952 | 16.8443
11:54 | 2061 | 26.4349 | 196.0699 | 438.2695 | 444.6009 | -19.9663 | -46.8529 | 4.9185 | 2.2768 | -4.5652 | -5.2856 | -1.409 | -3.3045 | 5.1127 | -1.6243 | 0.5934 | 0.6308 | 0.9531 | 0.712 | -131.1629 | -5.9416 | 1.4471 | -0.2246 | -6.7435 | -5.4348 | 1.2777 |  | -1.0375 | -2.4717 | 4.0146 | 3.3592 | 3.3481 | 1.0377 | 10.6654 | 14.1272 | 14.7524 | 11.0302 | 0.0004 | -0.0029 | 0.0006 | 0.0041 | 0.0002 | -0.0002 | 0.0065 | -0.0128 | -0.0219 | -360.2111 | 17.4459 | -360.5066 | 17.7169 | -360.8789 | 18.1994 | -360.9804 | 17.528 | -352.749 | 18.7477 | -352.746 | 16.8361
11:54 | 2062 | 26.4639 | 196.0918 | 438.2647 | 444.6264 | -19.9953 | -46.8322 | 4.9405 | 2.249 | -4.552 | -5.1856 | -1.4362 | -3.3303 | 5.0181 | -1.6159 | 0.5932 | 0.6312 | 0.9523 | 0.7109 | -131.1123 | -5.9573 | 1.4963 | -0.2637 | -6.8269 | -5.3887 | 1.186 |  | -1.0665 | -2.3008 | 4.0152 | 3.3608 | 3.348 | 1.0366 | 10.671 | 14.1448 | 14.7314 | 11.0525 | -0.0001 | -0.0025 | 0.0006 | 0.0035 | 0.001 | -0.0008 | 0.0127 | -0.0137 | -0.0082 | -360.2204 | 17.45 | -360.4942 | 17.68 | -360.7804 | 18.1461 | -360.8943 | 17.526 | -352.7552 | 18.7579 | -352.7121 | 16.795
11:54 | 2063 | 26.5702 | 196.1171 | 438.3069 | 444.6345 | -19.9371 | -46.9242 | 4.916 | 2.1596 | -4.566 | -5.2784 | -1.4639 | -3.2239 | 5.1583 | -1.5055 | 0.591 | 0.6308 | 0.9515 | 0.7098 | -131.0309 | -6.0306 | 1.578 | -0.1967 | -6.8278 | -5.485 | 1.2185 |  | -1.0583 | -2.3404 | 4.0155 | 3.36 | 3.3451 | 1.0378 | 10.6724 | 14.1512 | 14.7401 | 11.0205 | -0.0007 | -0.003 | 0.0006 | 0.0034 | 0.0002 | -0.0005 | 0.0097 | -0.0111 | -0.0064 | -360.1865 | 17.4767 | -360.5466 | 17.7416 | -360.8881 | 18.1604 | -360.9066 | 17.5342 | -352.7275 | 18.762 | -352.7737 | 16.8525
11:54 | 2064 | 26.5427 | 196.1259 | 438.304 | 444.5795 | -19.9351 | -46.9148 | 5.0534 | 2.2333 | -4.5651 | -5.211 | -1.3846 | -3.2653 | 5.2242 | -1.5729 | 0.5923 | 0.6316 | 0.9546 | 0.7098 | -131.1236 | -6.0175 | 1.472 | -0.1763 | -6.741 | -5.3662 | 1.2459 |  | -1.0108 | -2.3256 | 4.0142 | 3.3616 | 3.3468 | 1.0373 | 10.6665 | 14.1285 | 14.7433 | 11.0367 | -0.0001 | -0.0031 | 0.0005 | 0.0038 | 0.0007 | -0.0007 | -0.0027 | -0.0058 | -0.0111 | -360.1435 | 17.4315 | -360.4696 | 17.7026 | -360.8512 | 18.1912 | -360.9281 | 17.5075 | -352.6998 | 18.7292 | -352.6937 | 16.8381
11:54 | 2065 | 26.4858 | 196.1521 | 438.2605 | 444.5782 | -19.9475 | -47.0017 | 4.9551 | 2.2827 | -4.5121 | -5.235 | -1.4154 | -3.143 | 5.2795 | -1.5517 | 0.5924 | 0.6323 | 0.956 | 0.7112 | -131.2107 | -6.0947 | 1.4059 | -0.3231 | -6.7635 | -5.4987 | 1.2107 |  | -1.0189 | -2.2633 | 4.0144 | 3.3629 | 3.3479 | 1.0369 | 10.7023 | 14.1528 | 14.7388 | 11.0551 | 0.0001 | -0.0031 | 0.0005 | 0.0035 | 0.0003 | -0.0009 | 0.0174 | -0.0116 | -0.0061 | -360.1711 | 17.4521 | -360.5035 | 17.6985 | -360.8389 | 18.1851 | -360.9681 | 17.5404 | -352.7521 | 18.7477 | -352.749 | 16.8156
11:54 | 2066 | 26.4934 | 196.0999 | 438.1776 | 444.5769 | -19.952 | -46.9019 | 5.0065 | 2.3749 | -4.4546 | -5.2116 | -1.3714 | -3.133 | 5.1623 | -1.5312 | 0.5935 | 0.6317 | 0.953 | 0.7101 | -131.1255 | -6.1188 | 1.4281 | -0.2678 | -6.7895 | -5.3514 | 1.2872 |  | -1.0154 | -2.3586 | 4.0164 | 3.3618 | 3.3463 | 1.0393 | 10.6804 | 14.1479 | 14.7207 | 11.0222 | -0.0002 | -0.0029 | 0.0005 | 0.0033 | 0.0009 | -0.0007 | 0.0021 | -0.0173 | -0.0084 | -360.1527 | 17.4603 | -360.5127 | 17.7252 | -360.8574 | 18.144 | -360.8481 | 17.5034 | -352.746 | 18.7518 | -352.7583 | 16.8607
11:54 | 2067 | 26.5179 | 196.1094 | 438.3205 | 444.6094 | -19.9888 | -46.9042 | 4.9841 | 2.3406 | -4.4727 | -5.159 | -1.3814 | -3.1524 | 5.2457 | -1.5914 | 0.5926 | 0.6303 | 0.9563 | 0.7113 | -131.2137 | -6.004 | 1.4282 | -0.2978 | -6.7745 | -5.4941 | 1.3285 |  | -1.0543 | -2.3651 | 4.0146 | 3.3629 | 3.3469 | 1.0379 | 10.655 | 14.1224 | 14.689 | 11.0316 | -0.0007 | -0.003 | 0.0003 | 0.0036 | 0.0007 | -0.0009 | 0.0091 | -0.0017 | 0.0061 | -360.1404 | 17.4541 | -360.525 | 17.7375 | -360.9127 | 18.1892 | -360.9189 | 17.5075 | -352.7183 | 18.7374 | -352.746 | 16.8546
11:54 | 2068 | 26.5783 | 196.1621 | 438.2862 | 444.7256 | -19.9466 | -46.8779 | 4.9447 | 2.3416 | -4.4649 | -5.1452 | -1.3251 | -3.2019 | 5.0266 | -1.612 | 0.592 | 0.6337 | 0.9561 | 0.7115 | -131.2175 | -6.0237 | 1.3231 | -0.4102 | -6.8117 | -5.4201 | 1.32 |  | -1.0041 | -2.3622 | 4.014 | 3.3614 | 3.3466 | 1.0378 | 10.6886 | 14.1097 | 14.6993 | 11.0075 | 0.0001 | -0.0027 | 0.0004 | 0.0038 | 0.0007 | -0.0001 | 0.0027 | -0.0176 | -0.004 | -360.2019 | 17.4603 | -360.4696 | 17.6902 | -360.8143 | 18.1666 | -360.9466 | 17.5445 | -352.7337 | 18.7456 | -352.746 | 16.8176
11:54 | 2069 | 26.5616 | 196.13 | 438.3667 | 444.5845 | -20.0481 | -46.8979 | 4.8941 | 2.2223 | -4.4366 | -5.183 | -1.4311 | -3.221 | 5.1046 | -1.67 | 0.5926 | 0.6336 | 0.9528 | 0.7118 | -131.1534 | -6.0435 | 1.4513 | -0.2889 | -6.8072 | -5.4464 | 1.3401 |  | -0.981 | -2.4093 | 4.0138 | 3.3632 | 3.3488 | 1.0381 | 10.7012 | 14.1226 | 14.7248 | 11.0082 | 0 | -0.0035 | 0.0011 | 0.0044 | 0.0012 | -0.0004 | 0.0105 | -0.0069 | -0.0087 | -360.2419 | 17.4911 | -360.5743 | 17.7354 | -360.8758 | 18.142 | -360.8789 | 17.5075 | -352.7737 | 18.7887 | -352.8106 | 16.8443
11:54 | 2070 | 26.4879 | 196.1069 | 438.2847 | 444.5213 | -20.0215 | -46.8646 | 4.9602 | 2.2695 | -4.375 | -5.0921 | -1.3789 | -3.165 | 5.0933 | -1.5825 | 0.5927 | 0.6312 | 0.9531 | 0.7113 | -131.1623 | -5.9501 | 1.4879 | -0.0908 | -6.8276 | -5.415 | 1.3259 |  | -1.071 | -2.395 | 4.013 | 3.3617 | 3.3452 | 1.0369 | 10.6804 | 14.1481 | 14.7218 | 11.0334 | -0.0004 | -0.0033 | 0.0004 | 0.004 | 0.0007 | -0.0001 | 0.0052 | 0.0022 | -0.0225 | -360.0973 | 17.4377 | -360.5158 | 17.7272 | -360.8666 | 18.1769 | -360.9035 | 17.5055 | -352.6813 | 18.7353 | -352.746 | 16.8443
11:54 | 2071 | 26.5211 | 196.0483 | 438.2693 | 444.5768 | -20.0563 | -46.8741 | 4.8866 | 2.2116 | -4.3215 | -5.0778 | -1.3956 | -3.077 | 5.1726 | -1.5217 | 0.5918 | 0.6294 | 0.9537 | 0.7107 | -131.1264 | -5.903 | 1.5675 | -0.1909 | -6.8494 | -5.4342 | 1.2373 |  | -0.9491 | -2.3603 | 4.0136 | 3.3626 | 3.3433 | 1.0376 | 10.6988 | 14.1552 | 14.7184 | 11.0457 | -0.0002 | -0.0027 | 0.0005 | 0.0035 | 0.0013 | -0.0001 | 0.0191 | -0.0131 | 0.0052 | -360.2265 | 17.4521 | -360.5035 | 17.6964 | -360.8481 | 18.181 | -360.9435 | 17.5486 | -352.8229 | 18.76 | -352.7306 | 16.8074
11:54 | 2072 | 26.5153 | 196.1769 | 438.2116 | 444.4944 | -19.907 | -46.803 | 4.9554 | 2.1917 | -4.3903 | -5.0325 | -1.2844 | -3.0873 | 5.1946 | -1.5202 | 0.5929 | 0.6315 | 0.9516 | 0.7109 | -131.2224 | -6.036 | 1.4877 | -0.1461 | -6.8743 | -5.6412 | 1.2785 |  | -1.0126 | -2.3874 | 4.0133 | 3.3606 | 3.3477 | 1.0364 | 10.6817 | 14.1488 | 14.6968 | 11.0241 | -0.0007 | -0.0032 | 0.001 | 0.0038 | 0.0003 | -0.0005 | 0.0062 | -0.0177 | -0.0167 | -360.1804 | 17.4562 | -360.5189 | 17.7128 | -360.8204 | 18.1666 | -360.8912 | 17.5075 | -352.7675 | 18.7703 | -352.7706 | 16.8299
11:54 | 2073 | 26.5279 | 196.2109 | 438.1099 | 444.5245 | -19.9638 | -46.8592 | 4.9326 | 2.1455 | -4.3594 | -5.0117 | -1.3036 | -3.0164 | 5.1157 | -1.4031 | 0.5916 | 0.6338 | 0.9531 | 0.7111 | -131.134 | -6.0622 | 1.4347 | -0.1653 | -6.9082 | -5.5428 | 1.1655 |  | -1.0364 | -2.3678 | 4.0133 | 3.3626 | 3.3503 | 1.0381 | 10.7011 | 14.1344 | 14.7559 | 11.0478 | 0.0003 | -0.003 | 0.0007 | 0.0035 | 0.0007 | -0.0008 | 0.0063 | 0.0061 | -0.0135 | -360.1465 | 17.4397 | -360.5281 | 17.7457 | -360.8912 | 18.2015 | -360.9558 | 17.4993 | -352.7121 | 18.7374 | -352.7521 | 16.8423
11:54 | 2074 | 26.5311 | 196.2068 | 438.2208 | 444.511 | -20.0219 | -46.8449 | 4.9316 | 2.1896 | -4.3221 | -4.9982 | -1.348 | -3.0281 | 5.1091 | -1.3447 | 0.5923 | 0.6312 | 0.9527 | 0.7097 | -131.222 | -6.0875 | 1.4454 | -0.2639 | -6.8834 | -5.5091 | 1.2616 |  | -1.0252 | -2.3358 | 4.0154 | 3.3636 | 3.3513 | 1.038 | 10.6827 | 14.162 | 14.7245 | 11.0356 | -0.0001 | -0.0033 | 0.0009 | 0.0037 | 0.0007 | -0.0004 | -0.0043 | 0.0055 | -0.0147 | -360.1619 | 17.4172 | -360.4789 | 17.719 | -360.8174 | 18.183 | -360.9558 | 17.5157 | -352.7521 | 18.7271 | -352.706 | 16.8279
11:54 | 2075 | 26.6306 | 196.1815 | 438.2588 | 444.5228 | -20.0633 | -46.8145 | 4.8602 | 2.2379 | -4.2572 | -4.9121 | -1.3292 | -3.1202 | 5.1201 | -1.4537 | 0.594 | 0.6299 | 0.9537 | 0.711 | -131.2149 | -6.0641 | 1.4231 | -0.2301 | -6.835 | -5.5516 | 1.2847 |  | -1.0293 | -2.453 | 4.013 | 3.3583 | 3.3476 | 1.038 | 10.7128 | 14.1399 | 14.7133 | 11.0197 | -0.0004 | -0.0029 | 0.0005 | 0.0037 | 0.0007 | -0.0009 | 0.0011 | -0.0149 | -0.0051 | -360.2265 | 17.4829 | -360.5435 | 17.7293 | -360.8697 | 18.1604 | -360.885 | 17.5321 | -352.7583 | 18.7805 | -352.7829 | 16.8381
11:54 | 2076 | 26.6227 | 196.2109 | 438.2685 | 444.5298 | -20.0128 | -46.7374 | 4.9473 | 2.3252 | -4.1565 | -4.8878 | -1.3098 | -3.0611 | 5.156 | -1.4136 | 0.5911 | 0.6255 | 0.9515 | 0.7094 | -131.2182 | -6.0065 | 1.452 | -0.1535 | -6.7853 | -5.5342 | 1.2568 |  | -0.9878 | -2.2869 | 4.0145 | 3.3619 | 3.3479 | 1.0375 | 10.6769 | 14.1504 | 14.6956 | 11.0414 | 0.0002 | -0.0026 | 0.0004 | 0.0037 | 0.0006 | -0.0005 | 0.0093 | 0.0041 | -0.009 | -360.1465 | 17.4521 | -360.5435 | 17.7457 | -360.8758 | 18.1645 | -360.8635 | 17.4829 | -352.7121 | 18.7497 | -352.7798 | 16.8587
11:54 | 2077 | 26.6089 | 196.2049 | 438.3188 | 444.4953 | -19.9888 | -46.7685 | 4.9011 | 2.3419 | -4.251 | -4.8903 | -1.3259 | -2.9906 | 5.1715 | -1.4345 | 0.5929 | 0.6296 | 0.9548 | 0.7106 | -131.1282 | -5.9349 | 1.4828 | -0.1928 | -6.7926 | -5.3978 | 1.3005 |  | -1.0199 | -2.3122 | 4.0143 | 3.3607 | 3.3478 | 1.0376 | 10.6861 | 14.1599 | 14.7586 | 11.05 | 0.0002 | -0.003 | 0.0004 | 0.0039 | 0.0006 | -0.0004 | 0.0194 | -0.0107 | -0.0023 | -360.2235 | 17.4439 | -360.485 | 17.7149 | -360.8481 | 18.1851 | -360.9466 | 17.5321 | -352.7552 | 18.7497 | -352.7521 | 16.8176
11:54 | 2078 | 26.6094 | 196.2254 | 438.1397 | 444.5516 | -20.0165 | -46.7125 | 4.9045 | 2.3211 | -4.233 | -4.9544 | -1.2926 | -2.9716 | 5.2461 | -1.4381 | 0.5925 | 0.6301 | 0.9526 | 0.7118 | -131.2195 | -5.9379 | 1.4734 | -0.3697 | -6.8027 | -5.3838 | 1.2243 |  | -1.017 | -2.3523 | 4.016 | 3.3613 | 3.3497 | 1.0388 | 10.6746 | 14.1249 | 14.7044 | 11.0219 | 0.0002 | -0.0029 | 0.0007 | 0.0039 | 0.0007 | -0.0007 | 0.0125 | 0.0034 | -0.0171 | -360.1988 | 17.4644 | -360.5158 | 17.6841 | -360.7743 | 18.144 | -360.8943 | 17.5198 | -352.7798 | 18.7682 | -352.7614 | 16.8032
11:54 | 2079 | 26.6747 | 196.2104 | 438.1596 | 444.5696 | -19.9999 | -46.6217 | 4.9135 | 2.2631 | -4.2107 | -5.0734 | -1.3285 | -3.0166 | 5.2242 | -1.375 | 0.5914 | 0.6327 | 0.9547 | 0.7104 | -131.1741 | -5.9989 | 1.4413 | -0.3114 | -6.8656 | -5.4264 | 1.3143 |  | -1.0531 | -2.3711 | 4.0151 | 3.3593 | 3.3489 | 1.038 | 10.6838 | 14.1516 | 14.7143 | 11.0193 | -0.0001 | -0.0026 | 0.001 | 0.0039 | 0.0005 | 0.0001 | 0.0073 | -0.0061 | -0.0111 | -360.1711 | 17.4623 | -360.565 | 17.7539 | -360.8943 | 18.1851 | -360.9035 | 17.5013 | -352.7337 | 18.762 | -352.7952 | 16.8587
11:54 | 2080 | 26.6809 | 196.2141 | 438.2566 | 444.5994 | -20.0557 | -46.7253 | 4.8988 | 2.3372 | -4.2169 | -4.9403 | -1.2945 | -3.0341 | 5.2036 | -1.4348 | 0.5925 | 0.6289 | 0.9537 | 0.7117 | -131.1054 | -5.9815 | 1.4772 | -0.3757 | -6.9003 | -5.4456 | 1.2173 |  | -1.0066 | -2.3604 | 4.0148 | 3.3618 | 3.3497 | 1.0377 | 10.6608 | 14.0934 | 14.6822 | 11.0089 | -0.0005 | -0.0023 | 0.0009 | 0.0035 | 0.0011 | -0.0007 | 0.0012 | -0.0073 | -0.0156 | -360.1404 | 17.4151 | -360.4604 | 17.7108 | -360.8512 | 18.2118 | -360.9651 | 17.4972 | -352.709 | 18.7169 | -352.6875 | 16.8074
11:54 | 2081 | 26.7318 | 196.2133 | 438.1785 | 444.6231 | -20.0845 | -46.6712 | 4.9222 | 2.4004 | -4.2215 | -4.9269 | -1.211 | -3.0791 | 5.1982 | -1.4533 | 0.5916 | 0.6274 | 0.9512 | 0.7119 | -131.1974 | -6.0144 | 1.4194 | -0.173 | -6.7728 | -5.3759 | 1.361 |  | -1.0359 | -2.3685 | 4.0151 | 3.3616 | 3.3528 | 1.0386 | 10.6435 | 14.1049 | 14.688 | 10.98 | -0.0002 | -0.0032 | 0.0012 | 0.0043 | 0.0007 | 0.0001 | 0.0094 | -0.0132 | -0.0104 | -360.2081 | 17.45 | -360.5066 | 17.7252 | -360.8143 | 18.183 | -360.9312 | 17.5116 | -352.749 | 18.7641 | -352.7337 | 16.8156
11:54 | 2082 | 26.7111 | 196.1788 | 438.2263 | 444.5723 | -20.0447 | -46.6091 | 4.8539 | 2.307 | -4.2412 | -4.8932 | -1.274 | -3.0919 | 5.2191 | -1.4378 | 0.5912 | 0.63 | 0.9542 | 0.7121 | -131.2888 | -6.0354 | 1.5005 | -0.1794 | -6.8211 | -5.4117 | 1.3755 |  | -1.0436 | -2.4087 | 4.0161 | 3.3579 | 3.3468 | 1.0386 | 10.6596 | 14.104 | 14.7061 | 11.0417 | 0.0002 | -0.0029 | 0.0008 | 0.0036 | 0.0013 | -0.0005 | 0.0123 | -0.0033 | 0.008 | -360.1681 | 17.4623 | -360.5527 | 17.7703 | -360.885 | 18.1871 | -360.8758 | 17.4726 | -352.7521 | 18.7703 | -352.7983 | 16.8525
11:54 | 2083 | 26.7648 | 196.1496 | 438.178 | 444.5223 | -19.9709 | -46.6938 | 4.9457 | 2.3907 | -4.3054 | -4.8736 | -1.2263 | -3.0323 | 5.1947 | -1.4273 | 0.5922 | 0.6338 | 0.952 | 0.7134 | -131.2878 | -6.0412 | 1.4789 | -0.1016 | -6.7939 | -5.4778 | 1.381 |  | -0.9342 | -2.4361 | 4.0159 | 3.3619 | 3.3499 | 1.038 | 10.6608 | 14.1107 | 14.7054 | 11.032 | -0.0003 | -0.003 | 0.0007 | 0.0038 | 0.0004 | -0.0005 | 0.0085 | -0.0129 | -0.038 | -360.1527 | 17.4274 | -360.4696 | 17.7334 | -360.845 | 18.2015 | -360.922 | 17.4993 | -352.7213 | 18.7395 | -352.7213 | 16.8381
11:54 | 2084 | 26.7276 | 196.1288 | 438.1966 | 444.5372 | -19.9471 | -46.631 | 4.9713 | 2.4453 | -4.2276 | -4.8923 | -1.302 | -2.9983 | 5.1707 | -1.4494 | 0.5928 | 0.6352 | 0.9563 | 0.7113 | -131.2295 | -5.9864 | 1.491 | -0.0875 | -6.7918 | -5.4982 | 1.3354 |  | -0.905 | -2.3082 | 4.0143 | 3.363 | 3.3499 | 1.0375 | 10.6816 | 14.1317 | 14.7163 | 11.0291 | -0.0004 | -0.0028 | 0.0002 | 0.0038 | 0.0009 | -0.0006 | -0.0018 | -0.0075 | -0.0289 | -360.2111 | 17.4808 | -360.5312 | 17.7252 | -360.8204 | 18.1604 | -360.9466 | 17.5547 | -352.7614 | 18.7846 | -352.7829 | 16.8197
11:54 | 2085 | 26.7063 | 196.0867 | 438.2623 | 444.617 | -19.9305 | -46.6979 | 4.9153 | 2.4062 | -4.1575 | -4.9329 | -1.2967 | -2.9971 | 5.1726 | -1.4364 | 0.5916 | 0.6345 | 0.954 | 0.7139 | -131.2674 | -5.9842 | 1.5352 | -0.3204 | -6.7857 | -5.4381 | 1.2549 |  | -0.9044 | -2.3013 | 4.0161 | 3.3607 | 3.3502 | 1.0386 | 10.7207 | 14.1774 | 14.7481 | 11.0496 | -0.0002 | -0.0028 | 0.0004 | 0.0038 | 0.0004 | -0.0002 | -0.0011 | -0.0031 | -0.0091 | -360.1527 | 17.4562 | -360.5281 | 17.7457 | -360.8543 | 18.1337 | -360.8543 | 17.5055 | -352.7367 | 18.7641 | -352.7921 | 16.8423
11:54 | 2086 | 26.7278 | 196.1921 | 438.1612 | 444.5528 | -19.9262 | -46.7561 | 4.931 | 2.3679 | -4.0547 | -4.8591 | -1.2819 | -2.9826 | 5.1246 | -1.4427 | 0.5918 | 0.6324 | 0.9556 | 0.7125 | -131.2691 | -5.8966 | 1.4815 | -0.0849 | -6.6934 | -5.3738 | 1.379 |  | -0.8919 | -2.3836 | 4.0146 | 3.3608 | 3.3489 | 1.0382 | 10.6759 | 14.1374 | 14.7442 | 11.0468 | -0.0002 | -0.0033 | 0.0006 | 0.0037 | 0.0003 | -0.0008 | 0.0069 | -0.0046 | -0.0034 | -360.1711 | 17.4397 | -360.4696 | 17.7539 | -360.885 | 18.2036 | -360.9527 | 17.5301 | -352.7583 | 18.7333 | -352.7275 | 16.8361
11:54 | 2087 | 26.7235 | 196.1439 | 438.2376 | 444.5438 | -20.1074 | -46.8482 | 4.8785 | 2.3803 | -4.1734 | -4.8493 | -1.2724 | -2.9819 | 5.1725 | -1.4619 | 0.5932 | 0.6347 | 0.9558 | 0.7136 | -131.2379 | -5.8894 | 1.5844 | -0.0273 | -6.7129 | -5.2724 | 1.4055 |  | -0.9403 | -2.3563 | 4.0147 | 3.3617 | 3.348 | 1.0397 | 10.6896 | 14.1111 | 14.7259 | 11.0482 | -0.0001 | -0.0031 | 0.0005 | 0.0035 | 0.001 | -0.0006 | -0.0036 | 0.0003 | -0.0102 | -360.2235 | 17.4439 | -360.4573 | 17.7046 | -360.805 | 18.1707 | -360.9312 | 17.5321 | -352.7337 | 18.7538 | -352.706 | 16.8032
11:55 | 2088 | 26.7918 | 196.3026 | 438.2688 | 444.5803 | -20.066 | -46.8774 | 4.917 | 2.4124 | -4.1178 | -4.7825 | -1.2285 | -2.9588 | 5.2277 | -1.3713 | 0.5922 | 0.6338 | 0.9551 | 0.711 | -131.2495 | -5.9625 | 1.5917 | -0.0304 | -6.6861 | -5.3304 | 1.3889 |  | -0.8902 | -2.4257 | 4.0146 | 3.3628 | 3.3474 | 1.0375 | 10.6933 | 14.1488 | 14.7373 | 11.0299 | -0.0005 | -0.0029 | 0.0004 | 0.0036 | 0.0004 | -0.0004 | 0.0042 | 0.004 | -0.0037 | -360.1773 | 17.4521 | -360.5804 | 17.7642 | -360.8758 | 18.1645 | -360.8666 | 17.5034 | -352.7614 | 18.7579 | -352.7829 | 16.8587
11:55 | 2089 | 26.8455 | 196.1576 | 438.2883 | 444.5279 | -20.0265 | -46.7997 | 4.9305 | 2.347 | -4.1506 | -4.882 | -1.3087 | -2.9788 | 5.1697 | -1.415 | 0.5928 | 0.6319 | 0.9536 | 0.7123 | -131.156 | -5.8995 | 1.5914 | -0.1428 | -6.7136 | -5.2704 | 1.3504 |  | -0.9568 | -2.36 | 4.0159 | 3.3639 | 3.3487 | 1.0385 | 10.6746 | 14.1249 | 14.7218 | 11.0623 | -0.0003 | -0.0031 | 0.0012 | 0.0039 | 0.0008 | -0.0006 | 0.0196 | 0.0058 | -0.0149 | -360.1281 | 17.4356 | -360.4912 | 17.7436 | -360.9158 | 18.1974 | -360.885 | 17.5055 | -352.6998 | 18.723 | -352.7398 | 16.8381
11:55 | 2090 | 26.8114 | 196.2727 | 438.2414 | 444.6197 | -19.9496 | -46.843 | 4.9456 | 2.3525 | -4.0752 | -4.7761 | -1.2678 | -3.0271 | 5.2214 | -1.3693 | 0.5927 | 0.6335 | 0.9563 | 0.7127 | -131.2619 | -6.0803 | 1.4867 | -0.2919 | -6.6933 | -5.3283 | 1.3588 |  | -0.9149 | -2.4201 | 4.0139 | 3.3626 | 3.3519 | 1.0389 | 10.6884 | 14.1218 | 14.6977 | 11.0233 | 0.0001 | -0.0033 | 0.0009 | 0.0037 | 0.0008 | -0.0002 | 0.0065 | -0.0152 | -0.0058 | -360.1804 | 17.45 | -360.4973 | 17.7252 | -360.8174 | 18.1748 | -360.9435 | 17.5363 | -352.7644 | 18.7661 | -352.749 | 16.8115
11:55 | 2091 | 26.8325 | 196.2163 | 438.363 | 444.6136 | -19.9596 | -46.8282 | 4.9594 | 2.4041 | -4.1207 | -4.9335 | -1.243 | -3.1248 | 5.3021 | -1.4448 | 0.594 | 0.6362 | 0.9524 | 0.7115 | -131.2873 | -6.0192 | 1.4548 | -0.2779 | -6.7391 | -5.4372 | 1.3668 |  | -0.9338 | -2.4615 | 4.0151 | 3.3615 | 3.3503 | 1.0369 | 10.6666 | 14.1338 | 14.7459 | 11.0089 | -0.0004 | -0.0035 | 0.0009 | 0.0042 | 0.0008 | -0.0009 | 0.0132 | -0.0143 | -0.0035 | -360.2204 | 17.4808 | -360.5589 | 17.7395 | -360.8697 | 18.144 | -360.8789 | 17.5137 | -352.7552 | 18.7805 | -352.7921 | 16.8402
11:55 | 2092 | 26.8549 | 196.249 | 438.3241 | 444.6112 | -19.9339 | -46.8289 | 4.957 | 2.3737 | -4.2554 | -4.8388 | -1.3712 | -3.0453 | 5.2539 | -1.3328 | 0.5933 | 0.6323 | 0.9529 | 0.7125 | -131.2961 | -5.9851 | 1.4077 | -0.1561 | -6.7408 | -5.3377 | 1.32 |  | -0.9492 | -2.4406 | 4.0151 | 3.3637 | 3.3519 | 1.0383 | 10.6803 | 14.1308 | 14.7055 | 11.0273 | -0.0003 | -0.0025 | 0.0006 | 0.004 | 0.0007 | -0.0001 | 0.0109 | -0.0154 | -0.0092 | -360.1558 | 17.4274 | -360.5189 | 17.7477 | -360.8358 | 18.1789 | -360.9066 | 17.4952 | -352.7121 | 18.7497 | -352.7767 | 16.8443
11:55 | 2093 | 26.8689 | 196.2946 | 438.2638 | 444.5304 | -19.997 | -46.8732 | 4.9969 | 2.3939 | -4.3088 | -4.9685 | -1.3366 | -3.063 | 5.2237 | -1.3191 | 0.5932 | 0.631 | 0.9576 | 0.7126 | -131.2807 | -6.0005 | 1.4638 | -0.1622 | -6.6536 | -5.4211 | 1.369 |  | -0.9321 | -2.4454 | 4.0145 | 3.363 | 3.3515 | 1.0391 | 10.6793 | 14.1294 | 14.7309 | 11.0443 | -0.0006 | -0.0031 | 0.0001 | 0.0037 | 0.0006 | -0.0008 | 0.0006 | -0.0117 | -0.0023 | -360.2081 | 17.4562 | -360.4819 | 17.7169 | -360.8481 | 18.181 | -360.9374 | 17.5445 | -352.7706 | 18.7456 | -352.7306 | 16.8135
11:55 | 2094 | 26.8462 | 196.2949 | 438.351 | 444.6277 | -20.0165 | -46.9047 | 4.9745 | 2.3867 | -4.3302 | -4.8611 | -1.278 | -3.1024 | 5.1846 | -1.3574 | 0.5928 | 0.6325 | 0.9559 | 0.7123 | -131.3383 | -6.0159 | 1.4036 | -0.3153 | -6.818 | -5.4433 | 1.3225 |  | -0.9145 | -2.2634 | 4.0154 | 3.3631 | 3.35 | 1.0383 | 10.6504 | 14.1292 | 14.6778 | 11.01 | 0 | -0.0031 | 0.0009 | 0.0037 | 0.0007 | -0.0003 | 0.0032 | 0.0066 | -0.0011 | -360.1558 | 17.45 | -360.5035 | 17.719 | -360.8112 | 18.1748 | -360.885 | 17.5034 | -352.749 | 18.7682 | -352.746 | 16.8156
11:55 | 2095 | 26.8586 | 196.2476 | 438.269 | 444.6306 | -20.0836 | -46.9 | 4.8618 | 2.3986 | -4.2724 | -4.8172 | -1.2051 | -3.0989 | 5.194 | -1.4001 | 0.5918 | 0.633 | 0.9567 | 0.7137 | -131.2114 | -6.0016 | 1.3969 | -0.2785 | -6.8155 | -5.3996 | 1.2695 |  | -0.9662 | -2.3822 | 4.0151 | 3.3585 | 3.349 | 1.0381 | 10.678 | 14.1053 | 14.7085 | 11.0367 | 0.0004 | -0.0032 | 0.0008 | 0.0036 | 0.0009 | -0.0005 | 0.0135 | -0.003 | -0.0091 | -360.1711 | 17.448 | -360.5373 | 17.7559 | -360.8912 | 18.1994 | -360.9097 | 17.489 | -352.749 | 18.7579 | -352.7737 | 16.8484
11:55 | 2096 | 26.8714 | 196.2088 | 438.1841 | 444.5687 | -20.0196 | -47.0093 | 4.8011 | 2.4003 | -4.3105 | -4.8061 | -1.1981 | -3.0021 | 5.2718 | -1.2641 | 0.593 | 0.6329 | 0.9557 | 0.7124 | -131.1891 | -6.0938 | 1.3996 | -0.4237 | -6.8412 | -5.4579 | 1.1808 |  | -0.8904 | -2.1954 | 4.0162 | 3.3622 | 3.348 | 1.0393 | 10.647 | 14.1082 | 14.7131 | 10.9956 | -0.0003 | -0.0029 | 0.0004 | 0.004 | 0.0006 | -0.0006 | 0.0168 | 0.0005 | 0.0126 | -360.1465 | 17.4274 | -360.4881 | 17.721 | -360.842 | 18.1769 | -360.9097 | 17.5075 | -352.7244 | 18.7333 | -352.706 | 16.8197
11:55 | 2097 | 26.9784 | 196.2457 | 438.3454 | 444.6858 | -20.1018 | -47.1012 | 4.9005 | 2.3533 | -4.37 | -4.8405 | -1.2642 | -3.0175 | 5.2765 | -1.3046 | 0.5913 | 0.634 | 0.9526 | 0.7135 | -131.1457 | -5.9032 | 1.4974 | -0.4298 | -6.7901 | -5.4138 | 1.2849 |  | -0.9222 | -2.2771 | 4.015 | 3.3603 | 3.3525 | 1.0372 | 10.6606 | 14.1344 | 14.7038 | 11.0421 | -0.0001 | -0.0025 | 0.0011 | 0.0039 | 0.0006 | -0.0003 | 0.0019 | -0.0024 | -0.0018 | -360.2173 | 17.4849 | -360.525 | 17.7416 | -360.8943 | 18.1728 | -360.8943 | 17.5157 | -352.7583 | 18.7744 | -352.7921 | 16.8299
11:55 | 2098 | 27.0159 | 196.2778 | 438.3875 | 444.7053 | -19.9958 | -47.0344 | 4.8909 | 2.3651 | -4.4287 | -5.0147 | -1.3251 | -3.0348 | 5.2213 | -1.3175 | 0.5927 | 0.6312 | 0.9547 | 0.7146 | -131.1411 | -6.0322 | 1.4655 | -0.4505 | -6.8255 | -5.4696 | 1.2301 |  | -0.8785 | -2.2675 | 4.0153 | 3.3623 | 3.3484 | 1.0373 | 10.6827 | 14.1331 | 14.7303 | 11.0182 | -0.0002 | -0.0029 | 0.0009 | 0.0037 | 0.0006 | -0.0011 | 0 | -0.0063 | -0.0088 | -360.1773 | 17.4459 | -360.5158 | 17.7231 | -360.845 | 18.1748 | -360.8543 | 17.4788 | -352.7029 | 18.7682 | -352.746 | 16.8197
11:55 | 2099 | 26.9172 | 196.2454 | 438.3608 | 444.6774 | -20.0012 | -46.9547 | 4.9198 | 2.4265 | -4.4027 | -4.8261 | -1.3055 | -3.0032 | 5.233 | -1.2308 | 0.5916 | 0.6316 | 0.9518 | 0.7138 | -131.1431 | -6.0562 | 1.4853 | -0.4502 | -6.7955 | -5.4839 | 1.2581 |  | -0.8712 | -2.3573 | 4.0145 | 3.3625 | 3.3522 | 1.0388 | 10.6953 | 14.175 | 14.7454 | 11.0764 | 0 | -0.0029 | 0.0004 | 0.0035 | 0.0004 | -0.0003 | 0.0136 | -0.009 | -0.0045 | -360.1619 | 17.4521 | -360.525 | 17.7416 | -360.8758 | 18.1953 | -360.9466 | 17.5178 | -352.7521 | 18.7559 | -352.7583 | 16.8361
11:55 | 2100 | 26.836 | 196.1866 | 438.2654 | 444.5907 | -19.9357 | -46.8358 | 4.918 | 2.4361 | -4.3724 | -4.9222 | -1.3025 | -3.0223 | 5.2182 | -1.298 | 0.5921 | 0.6352 | 0.9556 | 0.7137 | -131.181 | -5.9998 | 1.5372 | -0.4408 | -6.7581 | -5.483 | 1.2497 |  | -0.8631 | -2.2931 | 4.0156 | 3.3618 | 3.3509 | 1.0398 | 10.6688 | 14.1249 | 14.6986 | 10.9814 | -0.0001 | -0.0029 | 0.0005 | 0.0033 | 0.0006 | -0.0009 | -0.0027 | -0.0079 | -0.022 | -360.2111 | 17.4418 | -360.4727 | 17.7046 | -360.7897 | 18.1625 | -360.885 | 17.5034 | -352.749 | 18.7518 | -352.749 | 16.8074
11:55 | 2101 | 26.8739 | 196.2029 | 438.3676 | 444.5939 | -19.9331 | -46.8972 | 4.9445 | 2.42 | -4.3216 | -4.9676 | -1.3807 | -2.9962 | 5.3158 | -1.2446 | 0.5913 | 0.631 | 0.9544 | 0.712 | -131.2296 | -6.0793 | 1.4966 | -0.4255 | -6.7323 | -5.4137 | 1.2693 |  | -0.9551 | -2.2885 | 4.0133 | 3.3635 | 3.3495 | 1.0383 | 10.6805 | 14.1131 | 14.7023 | 11.0053 | -0.0004 | -0.0027 | 0.0005 | 0.0037 | 0.0004 | -0.0004 | -0.0034 | -0.0093 | -0.0219 | -360.2081 | 17.4521 | -360.5496 | 17.7436 | -360.8758 | 18.1871 | -360.9281 | 17.5239 | -352.7213 | 18.7744 | -352.786 | 16.8299
11:55 | 2102 | 26.751 | 196.1375 | 438.1961 | 444.5581 | -20.0079 | -47.0488 | 4.9199 | 2.4528 | -4.2962 | -4.99 | -1.3493 | -3.0393 | 5.195 | -1.2684 | 0.5911 | 0.6309 | 0.9518 | 0.7116 | -131.1784 | -5.8837 | 1.4859 | -0.4364 | -6.6955 | -5.4816 | 1.2479 |  | -0.9579 | -2.2212 | 4.0149 | 3.3637 | 3.3495 | 1.04 | 10.6608 | 14.1109 | 14.7238 | 11.0259 | 0.0001 | -0.0025 | 0.0002 | 0.0034 | 0.0008 | -0.0007 | -0.0033 | -0.0112 | -0.0204 | -360.1435 | 17.4315 | -360.4819 | 17.719 | -360.8297 | 18.1748 | -360.8974 | 17.5075 | -352.6998 | 18.7415 | -352.7398 | 16.8176
11:55 | 2103 | 26.8308 | 196.2568 | 438.3178 | 444.6073 | -19.9339 | -46.9845 | 4.9347 | 2.3613 | -4.3136 | -4.9369 | -1.3617 | -3.0636 | 5.1624 | -1.3029 | 0.5912 | 0.6309 | 0.9551 | 0.7134 | -131.2228 | -5.9422 | 1.4601 | -0.4526 | -6.7313 | -5.4251 | 1.2128 |  | -1.0215 | -2.2326 | 4.0145 | 3.3599 | 3.3486 | 1.0371 | 10.6504 | 14.0772 | 14.7125 | 11.0215 | -0.0003 | -0.0031 | 0.0008 | 0.0038 | 0.0006 | -0.0004 | -0.0001 | -0.0005 | -0.024 | -360.1958 | 17.4541 | -360.5127 | 17.7416 | -360.8512 | 18.1912 | -360.9374 | 17.528 | -352.7337 | 18.7682 | -352.7552 | 16.8238
11:55 | 2104 | 26.9657 | 196.3107 | 438.3109 | 444.7367 | -19.9398 | -46.9724 | 4.85 | 2.3739 | -4.262 | -4.822 | -1.3931 | -2.9 | 5.2385 | -1.2956 | 0.5932 | 0.6304 | 0.9527 | 0.7113 | -131.1639 | -5.8764 | 1.5629 | -0.4863 | -6.7007 | -5.4759 | 1.2471 |  | -0.9425 | -2.3095 | 4.0149 | 3.3621 | 3.3509 | 1.0391 | 10.6585 | 14.1027 | 14.7153 | 11.0064 | 0.0004 | -0.0029 | 0.0005 | 0.0034 | 0.0011 | -0.0004 | 0.0132 | -0.0143 | -0.0028 | -360.1373 | 17.4315 | -360.5281 | 17.7334 | -360.8204 | 18.1707 | -360.8943 | 17.4931 | -352.7275 | 18.7538 | -352.7398 | 16.8238
11:55 | 2105 | 26.92 | 196.2392 | 438.3016 | 444.6806 | -19.9562 | -46.9382 | 4.8934 | 2.4109 | -4.3055 | -4.8282 | -1.445 | -2.9786 | 5.2719 | -1.2182 | 0.5931 | 0.6366 | 0.9571 | 0.7116 | -131.1592 | -5.9043 | 1.5593 | -0.4182 | -6.5965 | -5.44 | 1.2734 |  | -0.9388 | -2.3396 | 4.0132 | 3.3597 | 3.3526 | 1.0377 | 10.6689 | 14.1363 | 14.7091 | 11.0222 | -0.0007 | -0.0029 | 0.0011 | 0.0038 | 0.0011 | -0.0004 | 0.0101 | -0.0116 | -0.0171 | -360.1835 | 17.4603 | -360.5312 | 17.7375 | -360.8574 | 18.1912 | -360.8912 | 17.5096 | -352.7614 | 18.7744 | -352.7706 | 16.8299
11:55 | 2106 | 26.8603 | 196.2409 | 438.2 | 444.7341 | -20.021 | -46.86 | 4.9166 | 2.4109 | -4.2946 | -4.7864 | -1.3963 | -2.937 | 5.3078 | -1.1627 | 0.5922 | 0.6329 | 0.953 | 0.7116 | -131.0763 | -5.9054 | 1.6275 | -0.4508 | -6.643 | -5.4171 | 1.329 |  | -0.9463 | -2.3275 | 4.0145 | 3.3668 | 3.3522 | 1.0393 | 10.6954 | 14.1341 | 14.7133 | 11.0255 | -0.0008 | -0.0028 | 0.0006 | 0.0035 | 0.0007 | -0.0003 | 0.0025 | -0.0008 | -0.0221 | -360.1127 | 17.4356 | -360.4942 | 17.7272 | -360.802 | 18.1707 | -360.882 | 17.5075 | -352.7152 | 18.7497 | -352.7706 | 16.8135
11:55 | 2107 | 26.8773 | 196.2217 | 438.2572 | 444.5816 | -20.0398 | -46.8955 | 4.9153 | 2.4755 | -4.235 | -4.7141 | -1.3946 | -2.9328 | 5.3487 | -1.1134 | 0.5932 | 0.6325 | 0.9549 | 0.7111 | -131.197 | -5.9217 | 1.5557 | -0.4483 | -6.5691 | -5.4274 | 1.3757 |  | -0.9053 | -2.4163 | 4.0146 | 3.3619 | 3.3507 | 1.0384 | 10.6757 | 14.155 | 14.7231 | 11.0576 | 0.0002 | -0.003 | 0 | 0.0034 | 0.0009 | -0.0008 | 0.0069 | -0.0195 | -0.0295 | -360.1896 | 17.448 | -360.5219 | 17.7498 | -360.8574 | 18.1912 | -360.9404 | 17.5096 | -352.7121 | 18.7661 | -352.7583 | 16.8156
11:55 | 2108 | 26.9699 | 196.2546 | 438.312 | 444.6851 | -20.119 | -46.9557 | 4.8782 | 2.5169 | -4.2526 | -4.7096 | -1.385 | -2.9439 | 5.3912 | -1.1098 | 0.5931 | 0.6319 | 0.9547 | 0.7102 | -131.0849 | -5.9882 | 1.6077 | -0.4662 | -6.5777 | -5.4707 | 1.2872 |  | -0.8847 | -2.3995 | 4.0136 | 3.3605 | 3.3463 | 1.0375 | 10.6896 | 14.1574 | 14.749 | 11.054 | -0.0008 | -0.0034 | 0.0006 | 0.0039 | 0.0002 | -0.0002 | 0.0041 | 0.0042 | -0.0131 | -360.1988 | 17.4397 | -360.4912 | 17.7231 | -360.8081 | 18.1666 | -360.882 | 17.5198 | -352.7121 | 18.7477 | -352.7398 | 16.8135
11:55 | 2109 | 26.9162 | 196.2411 | 438.2422 | 444.7136 | -20.1484 | -46.9096 | 4.9838 | 2.5688 | -4.1803 | -4.6455 | -1.2646 | -2.8552 | 5.3088 | -1.1226 | 0.5933 | 0.6331 | 0.9547 | 0.7095 | -131.0678 | -5.8918 | 1.6696 | -0.4622 | -6.6927 | -5.4283 | 1.289 |  | -0.894 | -2.4669 | 4.0149 | 3.3612 | 3.3481 | 1.0379 | 10.6723 | 14.1747 | 14.7317 | 11.0367 | 0.0003 | -0.003 | 0.0001 | 0.0034 | 0.0011 | -0.0007 | 0.0051 | -0.0095 | -0.0009 | -360.1896 | 17.4582 | -360.5373 | 17.7559 | -360.8666 | 18.1892 | -360.9189 | 17.5178 | -352.749 | 18.7661 | -352.7644 | 16.8279
11:55 | 2110 | 26.8225 | 196.2853 | 438.3163 | 444.5248 | -20.0072 | -46.8809 | 4.9635 | 2.5173 | -4.1842 | -4.7419 | -1.2743 | -2.9815 | 5.3276 | -1.2287 | 0.5923 | 0.6291 | 0.9538 | 0.7136 | -131.1019 | -5.9151 | 1.675 | -0.4383 | -6.6872 | -5.5677 | 1.295 |  | -0.8394 | -2.2522 | 4.0147 | 3.3609 | 3.3489 | 1.0386 | 10.6332 | 14.1232 | 14.6699 | 10.9877 | -0.0008 | -0.0031 | 0.0006 | 0.0041 | 0.0004 | -0.0003 | 0.0131 | -0.0125 | 0.0148 | -360.1496 | 17.4274 | -360.4881 | 17.7313 | -360.8204 | 18.1789 | -360.9066 | 17.5075 | -352.7213 | 18.7436 | -352.7183 | 16.8135
11:55 | 2111 | 26.7985 | 196.1735 | 438.347 | 444.5935 | -20.0376 | -46.893 | 4.9707 | 2.5261 | -4.1632 | -4.8389 | -1.3759 | -2.8987 | 5.4013 | -1.1941 | 0.5931 | 0.632 | 0.9557 | 0.7136 | -131.1648 | -5.9422 | 1.5783 | -0.2058 | -6.6668 | -5.3841 | 1.3243 |  | -0.8293 | -2.2769 | 4.0156 | 3.3631 | 3.3501 | 1.0382 | 10.6549 | 14.1574 | 14.6912 | 11.0251 | 0.0001 | -0.0026 | 0.0008 | 0.0041 | 0.0008 | -0.0008 | 0.002 | -0.0146 | -0.0145 | -360.1681 | 17.4521 | -360.525 | 17.7518 | -360.8512 | 18.1851 | -360.9251 | 17.5239 | -352.7306 | 18.7641 | -352.7583 | 16.8176
11:55 | 2112 | 26.9017 | 196.1592 | 438.3578 | 444.585 | -20.0205 | -46.8708 | 5.0532 | 2.4423 | -4.1858 | -4.8008 | -1.3534 | -2.9078 | 5.4145 | -1.2263 | 0.5921 | 0.6302 | 0.9566 | 0.7111 | -131.1992 | -5.9323 | 1.5227 | -0.2815 | -6.7016 | -5.4775 | 1.3307 |  | -0.8437 | -2.3585 | 4.0146 | 3.3656 | 3.348 | 1.0389 | 10.6908 | 14.1297 | 14.733 | 11.0609 | 0.0006 | -0.0035 | 0.001 | 0.0038 | 0.0014 | -0.0001 | -0.0037 | -0.0059 | -0.0181 | -360.1804 | 17.4377 | -360.5004 | 17.7272 | -360.8358 | 18.1666 | -360.9004 | 17.5055 | -352.7398 | 18.7538 | -352.7521 | 16.8156
11:55 | 2113 | 26.9074 | 196.2087 | 438.3757 | 444.5582 | -20.0297 | -47.0622 | 4.8532 | 2.4541 | -4.2175 | -4.7407 | -1.3625 | -2.9021 | 5.4238 | -1.1728 | 0.5931 | 0.6324 | 0.956 | 0.7132 | -131.2024 | -5.8889 | 1.5866 | -0.2493 | -6.7003 | -5.2889 | 1.2984 |  | -0.9264 | -2.3548 | 4.0137 | 3.3615 | 3.3481 | 1.0393 | 10.6724 | 14.134 | 14.7122 | 11.0432 | -0.0005 | -0.0029 | 0.0009 | 0.0041 | 0.0004 | -0.0006 | 0.024 | -0.0118 | -0.0194 | -360.165 | 17.4582 | -360.5404 | 17.7539 | -360.8758 | 18.1892 | -360.9097 | 17.5219 | -352.7213 | 18.7641 | -352.7706 | 16.834
11:55 | 2114 | 26.9675 | 196.1988 | 438.3558 | 444.6351 | -19.9631 | -47.0002 | 4.8803 | 2.4408 | -4.2329 | -4.7986 | -1.3739 | -2.9825 | 5.3612 | -1.1414 | 0.5922 | 0.6299 | 0.954 | 0.7109 | -131.1983 | -5.9732 | 1.5016 | -0.3976 | -6.8558 | -5.3957 | 1.2601 |  | -0.8557 | -2.2697 | 4.0145 | 3.3645 | 3.3515 | 1.0396 | 10.685 | 14.1181 | 14.7273 | 11.0089 | -0.0006 | -0.0026 | 0.0006 | 0.0038 | 0.0005 | -0.0004 | 0.0115 | -0.0112 | -0.0182 | -360.1711 | 17.4295 | -360.4635 | 17.7128 | -360.8235 | 18.1666 | -360.8912 | 17.5075 | -352.7244 | 18.7477 | -352.746 | 16.8012
11:55 | 2115 | 26.8939 | 196.1935 | 438.3634 | 444.6076 | -19.9916 | -47.0807 | 4.8302 | 2.4361 | -4.078 | -4.6451 | -1.3454 | -2.9547 | 5.371 | -1.1333 | 0.5924 | 0.6329 | 0.9564 | 0.7111 | -131.2488 | -5.9858 | 1.5249 | -0.3174 | -6.8105 | -5.3502 | 1.3571 |  | -0.8824 | -2.3866 | 4.0135 | 3.3619 | 3.3522 | 1.0388 | 10.6596 | 14.1503 | 14.7466 | 11.0244 | -0.0004 | -0.0033 | 0.0004 | 0.0033 | 0.0006 | -0.0002 | 0.0007 | -0.0181 | -0.017 | -360.2235 | 17.45 | -360.5312 | 17.7395 | -360.8358 | 18.1748 | -360.9066 | 17.5363 | -352.746 | 18.7744 | -352.7675 | 16.8217
11:55 | 2116 | 26.8558 | 196.2365 | 438.2829 | 444.5495 | -20.0053 | -46.9663 | 4.8947 | 2.3929 | -4.183 | -4.8409 | -1.3513 | -2.9827 | 5.3634 | -1.2233 | 0.5925 | 0.6335 | 0.9558 | 0.712 | -131.0646 | -6.002 | 1.5847 | -0.3955 | -6.8078 | -5.2954 | 1.3385 |  | -0.8531 | -2.4277 | 4.0145 | 3.3628 | 3.3478 | 1.0384 | 10.685 | 14.1586 | 14.6983 | 11.0435 | 0 | -0.0029 | 0.0006 | 0.0038 | 0.001 | -0.0006 | 0.0143 | 0.0032 | 0.008 | -360.1835 | 17.4336 | -360.4973 | 17.7395 | -360.8543 | 18.1666 | -360.8758 | 17.5055 | -352.6967 | 18.7559 | -352.7306 | 16.8156
11:55 | 2117 | 27.0383 | 196.1991 | 438.3654 | 444.6392 | -20.0899 | -47.1341 | 4.9101 | 2.4374 | -4.2132 | -4.8408 | -1.3121 | -2.9766 | 5.4248 | -1.2483 | 0.5917 | 0.6323 | 0.9572 | 0.7118 | -131.0272 | -5.8813 | 1.5531 | -0.3304 | -6.8196 | -5.3358 | 1.3318 |  | -0.9544 | -2.4844 | 4.0155 | 3.365 | 3.3511 | 1.0391 | 10.6654 | 14.1503 | 14.7177 | 11.0129 | 0.0001 | -0.0029 | 0.0007 | 0.0038 | 0.0005 | -0.0002 | 0.0257 | -0.0234 | -0.006 | -360.1927 | 17.4541 | -360.5127 | 17.7457 | -360.8697 | 18.2036 | -360.9435 | 17.5301 | -352.7675 | 18.7703 | -352.7521 | 16.8217
11:55 | 2118 | 26.9234 | 196.173 | 438.2162 | 444.5658 | -20.04 | -46.8966 | 4.9198 | 2.4831 | -4.2074 | -4.7504 | -1.3011 | -2.9827 | 5.3305 | -1.1636 | 0.5925 | 0.6346 | 0.9565 | 0.7112 | -131.0818 | -5.9579 | 1.5166 | -0.3373 | -6.7243 | -5.2832 | 1.4136 |  | -0.9101 | -2.441 | 4.0144 | 3.3622 | 3.3497 | 1.0384 | 10.7 | 14.1504 | 14.7303 | 11.0471 | -0.0004 | -0.0028 | 0.0006 | 0.0037 | 0.0011 | -0.0006 | 0.0237 | 0.0016 | -0.0117 | -360.1527 | 17.4336 | -360.4789 | 17.721 | -360.8143 | 18.1666 | -360.8912 | 17.5321 | -352.6967 | 18.7456 | -352.7398 | 16.8074
11:55 | 2119 | 27.0381 | 196.2213 | 438.4391 | 444.7093 | -20.0417 | -46.9935 | 4.9502 | 2.4785 | -4.1826 | -4.666 | -1.3418 | -3.013 | 5.3453 | -1.2092 | 0.5927 | 0.6313 | 0.9538 | 0.7126 | -131.1023 | -5.9753 | 1.5416 | -0.4896 | -6.743 | -5.2342 | 1.4518 |  | -0.8734 | -2.4008 | 4.0123 | 3.3623 | 3.3535 | 1.0396 | 10.6653 | 14.1331 | 14.684 | 11.0471 | -0.0002 | -0.0026 | 0.0011 | 0.0044 | 0.0003 | -0.0001 | 0.0135 | -0.012 | -0.0044 | -360.205 | 17.4603 | -360.5404 | 17.7518 | -360.8543 | 18.183 | -360.8974 | 17.5219 | -352.7429 | 18.7723 | -352.7983 | 16.832
11:55 | 2120 | 27.0026 | 196.2646 | 438.3473 | 444.6417 | -20.0992 | -46.9422 | 5.0164 | 2.4146 | -4.2032 | -4.8065 | -1.3617 | -3.0102 | 5.3299 | -1.2061 | 0.5925 | 0.6318 | 0.9538 | 0.7123 | -131.0959 | -5.9181 | 1.5923 | -0.3473 | -6.7642 | -5.3197 | 1.3573 |  | -0.8772 | -2.3186 | 4.0139 | 3.3617 | 3.3501 | 1.0382 | 10.6873 | 14.1378 | 14.701 | 11.0399 | 0.0001 | -0.0029 | 0.0006 | 0.0038 | 0.0008 | -0.0008 | 0.0086 | -0.0182 | -0.0233 | -360.1311 | 17.4233 | -360.4819 | 17.7252 | -360.8389 | 18.1645 | -360.8789 | 17.5075 | -352.6721 | 18.7456 | -352.7337 | 16.8217
11:55 | 2121 | 27.0313 | 196.2477 | 438.3083 | 444.6519 | -20.0523 | -47.0122 | 4.9232 | 2.4132 | -4.1791 | -4.8103 | -1.2994 | -2.9555 | 5.3703 | -1.1941 | 0.5925 | 0.6308 | 0.9583 | 0.7111 | -131.181 | -5.9376 | 1.5575 | -0.3492 | -6.7467 | -5.293 | 1.4145 |  | -0.8692 | -2.4461 | 4.0147 | 3.3595 | 3.3547 | 1.0402 | 10.6712 | 14.1272 | 14.7119 | 11.0302 | 0.0003 | -0.0029 | 0.0005 | 0.0037 | 0.0005 | -0.0005 | 0.0023 | 0.0028 | -0.0105 | -360.1835 | 17.4521 | -360.5219 | 17.7395 | -360.8635 | 18.1892 | -360.9035 | 17.5321 | -352.7244 | 18.7641 | -352.7367 | 16.8197
11:55 | 2122 | 27.0614 | 196.3227 | 438.3931 | 444.692 | -19.9439 | -46.9441 | 4.9441 | 2.4682 | -4.1658 | -4.8282 | -1.3437 | -3.057 | 5.3063 | -1.2291 | 0.5925 | 0.6328 | 0.9556 | 0.7132 | -131.1264 | -5.885 | 1.6334 | -0.1899 | -6.8018 | -5.2458 | 1.4219 |  | -0.8678 | -2.3848 | 4.0148 | 3.3597 | 3.3534 | 1.0407 | 10.7046 | 14.1436 | 14.7358 | 11.0399 | -0.0003 | -0.0027 | 0.001 | 0.0039 | 0.001 | -0.0004 | -0.0006 | -0.0075 | 0.0062 | -360.1342 | 17.4521 | -360.5127 | 17.7272 | -360.8174 | 18.1502 | -360.882 | 17.5116 | -352.7521 | 18.762 | -352.7921 | 16.8032
11:55 | 2123 | 27.0638 | 196.2987 | 438.3642 | 444.7068 | -19.8215 | -46.7669 | 5.1529 | 2.4691 | -4.2342 | -4.7696 | -1.3388 | -3.0496 | 5.3284 | -1.2255 | 0.5928 | 0.633 | 0.9565 | 0.7116 | -131.1899 | -5.8563 | 1.4743 | -0.3109 | -6.8366 | -5.3302 | 1.299 |  | -0.9001 | -2.4549 | 4.0127 | 3.3617 | 3.3509 | 1.0399 | 10.7047 | 14.1202 | 14.7452 | 11.058 | -0.0004 | -0.0025 | -0.0001 | 0.0029 | 0.0008 | -0.0008 | 0.0144 | -0.0118 | -0.0241 | -360.1835 | 17.448 | -360.5343 | 17.7621 | -360.845 | 18.1748 | -360.9189 | 17.526 | -352.7244 | 18.7579 | -352.7706 | 16.8279
11:55 | 2124 | 27.1046 | 196.3141 | 438.3312 | 444.7125 | -19.8464 | -46.8255 | 5.0602 | 2.553 | -4.2682 | -4.7679 | -1.35 | -3.0253 | 5.3274 | -1.2177 | 0.5927 | 0.6317 | 0.9559 | 0.7114 | -131.1416 | -5.9113 | 1.6235 | -0.4127 | -6.865 | -5.38 | 1.2876 |  | -0.9204 | -2.4306 | 4.0132 | 3.3604 | 3.3497 | 1.0386 | 10.6666 | 14.0934 | 14.7111 | 11.0205 | -0.0003 | -0.0032 | 0.0005 | 0.0038 | 0.0006 | -0.0005 | 0.005 | -0.008 | -0.0165 | -360.1681 | 17.4274 | -360.4758 | 17.7272 | -360.8481 | 18.1748 | -360.885 | 17.5075 | -352.7337 | 18.7436 | -352.7121 | 16.8135
11:55 | 2125 | 27.071 | 196.2989 | 438.3637 | 444.7597 | -19.8636 | -46.8883 | 4.9824 | 2.5647 | -4.1426 | -4.738 | -1.2534 | -3.0596 | 5.4154 | -1.2162 | 0.5927 | 0.6307 | 0.9596 | 0.7108 | -131.1654 | -5.9053 | 1.5479 | -0.5072 | -6.9222 | -5.347 | 1.2718 |  | -0.8409 | -2.4047 | 4.0128 | 3.3608 | 3.3483 | 1.0382 | 10.6885 | 14.1215 | 14.7303 | 11.0182 | 0.0004 | -0.0028 | 0.0007 | 0.0039 | 0.001 | -0.0008 | 0.0124 | 0.0021 | -0.0017 | -360.2173 | 17.4562 | -360.5004 | 17.7395 | -360.8358 | 18.1769 | -360.9127 | 17.526 | -352.7367 | 18.762 | -352.7552 | 16.8135
11:55 | 2126 | 27.0764 | 196.2855 | 438.3736 | 444.712 | -19.9118 | -46.9706 | 5.0607 | 2.5251 | -4.1443 | -4.837 | -1.3152 | -3.0448 | 5.4159 | -1.257 | 0.5936 | 0.6327 | 0.9554 | 0.7112 | -131.1631 | -5.8576 | 1.53 | -0.4614 | -6.862 | -5.4144 | 1.3678 |  | -0.8671 | -2.3953 | 4.0152 | 3.3602 | 3.3499 | 1.0386 | 10.6447 | 14.0944 | 14.6652 | 11.0162 | -0.0001 | -0.0031 | 0.0006 | 0.0039 | 0.0005 | -0.0004 | 0.0111 | -0.005 | -0.0077 | -360.1465 | 17.4377 | -360.5219 | 17.7334 | -360.8327 | 18.1707 | -360.8912 | 17.5055 | -352.7337 | 18.7559 | -352.746 | 16.8238
11:55 | 2127 | 27.0511 | 196.3393 | 438.4276 | 444.7241 | -19.8285 | -47.0093 | 5.0933 | 2.524 | -4.1238 | -4.7534 | -1.2852 | -2.9813 | 5.4578 | -1.2347 | 0.5922 | 0.6324 | 0.956 | 0.7113 | -131.2354 | -5.9632 | 1.5948 | -0.2732 | -6.8175 | -5.3945 | 1.3423 |  | -0.9031 | -2.4749 | 4.0148 | 3.3624 | 3.3477 | 1.0402 | 10.6643 | 14.1027 | 14.7095 | 11.0237 | -0.0003 | -0.0028 | 0.001 | 0.0039 | 0.001 | -0.0005 | 0.0021 | -0.0081 | -0.0325 | -360.1927 | 17.4459 | -360.525 | 17.7436 | -360.8327 | 18.1871 | -360.9404 | 17.5198 | -352.6967 | 18.7579 | -352.7767 | 16.8238
11:55 | 2128 | 27.0736 | 196.2753 | 438.4011 | 444.7089 | -19.8665 | -46.9461 | 5.1542 | 2.4699 | -4.1417 | -4.9229 | -1.3397 | -3.0309 | 5.4053 | -1.27 | 0.593 | 0.6311 | 0.9563 | 0.711 | -131.2947 | -5.9545 | 1.592 | -0.2682 | -6.7341 | -5.2998 | 1.4114 |  | -0.8332 | -2.4385 | 4.0127 | 3.3587 | 3.3468 | 1.0388 | 10.6689 | 14.1363 | 14.7207 | 11.0049 | -0.0003 | -0.0031 | 0.0006 | 0.0036 | 0.0008 | -0.0001 | -0.0025 | -0.0008 | -0.002 | -360.1773 | 17.4439 | -360.5219 | 17.7354 | -360.8574 | 18.181 | -360.9066 | 17.526 | -352.7367 | 18.7579 | -352.7737 | 16.8217
11:55 | 2129 | 27.1299 | 196.2974 | 438.4209 | 444.6453 | -19.8643 | -46.9023 | 5.1936 | 2.5321 | -4.1151 | -4.893 | -1.3719 | -2.9732 | 5.3884 | -1.3343 | 0.5937 | 0.6325 | 0.9573 | 0.7128 | -131.2056 | -5.9103 | 1.5717 | -0.2998 | -6.7256 | -5.3323 | 1.3758 |  | -0.8373 | -2.3934 | 4.0123 | 3.3605 | 3.3476 | 1.0373 | 10.6551 | 14.1512 | 14.7111 | 11.0147 | -0.0004 | -0.0033 | 0.0008 | 0.0038 | 0.0006 | -0.0008 | 0.003 | -0.0101 | -0.0142 | -360.1865 | 17.4582 | -360.5004 | 17.7231 | -360.8512 | 18.1748 | -360.9066 | 17.5178 | -352.7306 | 18.7559 | -352.7429 | 16.8074
11:55 | 2130 | 27.0936 | 196.2708 | 438.4002 | 444.5809 | -19.8788 | -46.9008 | 5.0596 | 2.4876 | -4.2085 | -4.8057 | -1.2872 | -2.9791 | 5.4574 | -1.2123 | 0.5925 | 0.6285 | 0.955 | 0.7131 | -131.1886 | -5.8473 | 1.6196 | -0.2202 | -6.7461 | -5.4573 | 1.4045 |  | -0.8307 | -2.4735 | 4.0137 | 3.3636 | 3.3489 | 1.0385 | 10.6838 | 14.1575 | 14.7327 | 11.0478 | 0.0001 | -0.0029 | 0.0009 | 0.0037 | 0.0006 | -0.0006 | -0.006 | -0.0115 | -0.019 | -360.1435 | 17.4377 | -360.5158 | 17.7252 | -360.842 | 18.1728 | -360.9035 | 17.5219 | -352.7244 | 18.7559 | -352.7521 | 16.8238
11:55 | 2131 | 27.1402 | 196.2971 | 438.5248 | 444.6434 | -19.8764 | -46.9749 | 5.0815 | 2.4423 | -4.189 | -4.9634 | -1.2592 | -3.0273 | 5.4476 | -1.2822 | 0.5924 | 0.6349 | 0.9577 | 0.7136 | -131.215 | -5.8757 | 1.5791 | -0.3076 | -6.7065 | -5.3809 | 1.4112 |  | -0.9071 | -2.4183 | 4.0143 | 3.361 | 3.3496 | 1.0382 | 10.7139 | 14.1586 | 14.7099 | 11.0377 | -0.0006 | -0.0028 | 0.0001 | 0.0031 | 0.0003 | -0.0007 | 0.0167 | -0.0213 | 0.0153 | -360.2265 | 17.448 | -360.5219 | 17.7375 | -360.845 | 18.1892 | -360.9097 | 17.5178 | -352.7121 | 18.76 | -352.7152 | 16.8176
11:55 | 2132 | 27.0474 | 196.269 | 438.3809 | 444.6534 | -19.8437 | -46.902 | 5.1125 | 2.4796 | -4.1642 | -4.875 | -1.2164 | -3.0849 | 5.3663 | -1.2858 | 0.5928 | 0.6321 | 0.9567 | 0.7116 | -131.1504 | -5.8743 | 1.6983 | -0.3624 | -6.7016 | -5.5169 | 1.4215 |  | -0.9001 | -2.3723 | 4.0149 | 3.3644 | 3.3505 | 1.0377 | 10.6793 | 14.1294 | 14.7136 | 11.0443 | -0.0009 | -0.0031 | 0.0004 | 0.0038 | 0.0007 | -0.0008 | 0.0006 | -0.0164 | -0.0219 | -360.1496 | 17.4356 | -360.5127 | 17.7334 | -360.8204 | 18.1666 | -360.9097 | 17.526 | -352.709 | 18.7538 | -352.7614 | 16.8156
11:55 | 2133 | 27.1204 | 196.3055 | 438.4252 | 444.6994 | -19.8195 | -46.8316 | 5.2038 | 2.6027 | -4.0591 | -4.8885 | -1.1298 | -3.0107 | 5.4383 | -1.1558 | 0.5923 | 0.6318 | 0.9537 | 0.7115 | -131.2083 | -5.8513 | 1.6158 | -0.4346 | -6.7633 | -5.4476 | 1.3287 |  | -0.7476 | -2.3259 | 4.014 | 3.3628 | 3.3491 | 1.0385 | 10.6872 | 14.1553 | 14.7426 | 11.0569 | 0.0002 | -0.0029 | 0.0007 | 0.0039 | 0.0007 | -0.0008 | 0.0166 | -0.0187 | -0.0135 | -360.2142 | 17.4418 | -360.5189 | 17.7621 | -360.8697 | 18.181 | -360.9097 | 17.526 | -352.7767 | 18.7538 | -352.7552 | 16.8299
11:55 | 2134 | 27.0417 | 196.2807 | 438.4962 | 444.6982 | -19.7898 | -46.7507 | 5.2324 | 2.5321 | -4.1579 | -4.9054 | -1.1435 | -3.0416 | 5.4628 | -1.1513 | 0.5927 | 0.634 | 0.9549 | 0.7123 | -131.2415 | -6.0056 | 1.5437 | -0.273 | -6.7137 | -5.3529 | 1.4051 |  | -0.7908 | -2.3584 | 4.0151 | 3.363 | 3.3477 | 1.0384 | 10.6677 | 14.1409 | 14.7714 | 11.0269 | -0.0005 | -0.0032 | 0.0003 | 0.0041 | 0.0009 | -0.0007 | 0.0053 | -0.0132 | -0.0112 | -360.1681 | 17.4377 | -360.4942 | 17.7334 | -360.8235 | 18.1933 | -360.9189 | 17.5137 | -352.706 | 18.7579 | -352.7337 | 16.8074
11:55 | 2135 | 27.1522 | 196.3598 | 438.5406 | 444.7678 | -19.8701 | -46.7882 | 5.1179 | 2.4915 | -4.1882 | -4.9685 | -1.2203 | -3.0499 | 5.3899 | -1.1955 | 0.5927 | 0.6331 | 0.9589 | 0.7137 | -131.1092 | -5.9055 | 1.6044 | -0.1722 | -6.6986 | -5.2998 | 1.4123 |  | -0.819 | -2.3095 | 4.0143 | 3.3651 | 3.3479 | 1.0393 | 10.6803 | 14.1483 | 14.7355 | 11.0616 | -0.0001 | -0.0026 | 0.0007 | 0.0039 | 0.0008 | -0.0003 | 0.0026 | -0.0096 | -0.019 | -360.2142 | 17.448 | -360.5343 | 17.7744 | -360.8297 | 18.1789 | -360.9189 | 17.5321 | -352.7337 | 18.7744 | -352.7829 | 16.8299
11:55 | 2136 | 27.1866 | 196.2995 | 438.4869 | 444.79 | -19.8352 | -46.7371 | 5.0815 | 2.5248 | -4.1931 | -4.9416 | -1.2001 | -2.9529 | 5.4629 | -1.153 | 0.5922 | 0.6343 | 0.9554 | 0.7131 | -131.2281 | -5.8812 | 1.6025 | -0.2902 | -6.7321 | -5.1712 | 1.402 |  | -0.9014 | -2.3377 | 4.0144 | 3.3636 | 3.3484 | 1.0375 | 10.6781 | 14.1283 | 14.7364 | 11.037 | -0.0006 | -0.0032 | 0.0004 | 0.0037 | 0.001 | -0.0006 | -0.0012 | -0.0187 | -0.0104 | -360.1465 | 17.4274 | -360.4727 | 17.7498 | -360.8358 | 18.1769 | -360.9035 | 17.5013 | -352.7121 | 18.7518 | -352.7398 | 16.8238
11:55 | 2137 | 27.1897 | 196.369 | 438.3805 | 444.6893 | -19.8582 | -46.7309 | 5.1276 | 2.4964 | -4.1737 | -4.9473 | -1.2796 | -2.8704 | 5.4951 | -1.2129 | 0.5922 | 0.6343 | 0.9551 | 0.7132 | -131.1899 | -5.9434 | 1.5134 | -0.2529 | -6.5975 | -5.2731 | 1.38 |  | -0.8266 | -2.4169 | 4.0148 | 3.3623 | 3.3505 | 1.0391 | 10.6804 | 14.1306 | 14.7207 | 11.028 | -0.0002 | -0.0032 | 0.0007 | 0.0039 | 0.0003 | 0.0001 | 0.0014 | -0.0213 | -0.0132 | -360.1804 | 17.4459 | -360.5343 | 17.7662 | -360.8635 | 18.181 | -360.9497 | 17.5424 | -352.7644 | 18.7579 | -352.7706 | 16.8238
11:55 | 2138 | 27.1348 | 196.3583 | 438.5103 | 444.738 | -19.9042 | -46.7552 | 5.0711 | 2.5332 | -4.1497 | -4.7848 | -1.1881 | -3.1115 | 5.4513 | -1.2569 | 0.5925 | 0.6333 | 0.952 | 0.7112 | -131.1456 | -5.9899 | 1.6126 | -0.2892 | -6.6785 | -5.3366 | 1.3595 |  | -0.9268 | -2.3754 | 4.015 | 3.3634 | 3.35 | 1.0397 | 10.6712 | 14.0982 | 14.6772 | 11.0013 | 0.0003 | -0.0031 | 0.001 | 0.0037 | 0.0007 | -0.001 | 0.0006 | -0.0015 | -0.0297 | -360.1804 | 17.448 | -360.4819 | 17.7272 | -360.8174 | 18.142 | -360.9004 | 17.5055 | -352.7367 | 18.7682 | -352.7275 | 16.7991
11:55 | 2139 | 27.0859 | 196.3607 | 438.368 | 444.6475 | -19.9992 | -46.8817 | 5.1125 | 2.455 | -4.2282 | -4.8298 | -1.2042 | -3.0303 | 5.5201 | -1.14 | 0.592 | 0.6312 | 0.9507 | 0.7115 | -131.1915 | -5.9757 | 1.6492 | -0.2789 | -6.7407 | -5.3079 | 1.3621 |  | -0.8355 | -2.2446 | 4.0141 | 3.3625 | 3.3484 | 1.0388 | 10.677 | 14.127 | 14.705 | 11.0075 | -0.0003 | -0.0027 | 0.0005 | 0.0036 | 0.0005 | -0.0003 | 0.0153 | -0.0027 | -0.0096 | -360.1835 | 17.4603 | -360.5681 | 17.7744 | -360.845 | 18.1563 | -360.9004 | 17.526 | -352.7275 | 18.7785 | -352.8198 | 16.8381
11:55 | 2140 | 27.1049 | 196.3376 | 438.3957 | 444.6339 | -19.9344 | -46.8237 | 5.0697 | 2.5023 | -4.2065 | -4.8147 | -1.2348 | -3.1217 | 5.4412 | -1.1556 | 0.593 | 0.6336 | 0.9539 | 0.7129 | -131.1932 | -5.9641 | 1.5886 | -0.3199 | -6.7036 | -5.2682 | 1.3617 |  | -0.7985 | -2.3429 | 4.0145 | 3.361 | 3.3501 | 1.0373 | 10.6884 | 14.1448 | 14.7198 | 11.041 | -0.0001 | -0.0025 | 0.0012 | 0.0044 | 0.0012 | -0.0003 | 0.0031 | -0.0077 | -0.0113 | -360.1373 | 17.4192 | -360.4696 | 17.7477 | -360.8481 | 18.1645 | -360.8912 | 17.4972 | -352.6875 | 18.7333 | -352.7183 | 16.8135
11:55 | 2141 | 27.1484 | 196.4145 | 438.3611 | 444.741 | -19.9226 | -46.8852 | 5.0418 | 2.494 | -4.2756 | -4.8757 | -1.2169 | -3.043 | 5.4295 | -1.2586 | 0.5933 | 0.6355 | 0.9543 | 0.7123 | -131.1844 | -5.8957 | 1.6509 | -0.2426 | -6.7379 | -5.2391 | 1.3992 |  | -0.801 | -2.4019 | 4.0129 | 3.362 | 3.3485 | 1.0382 | 10.692 | 14.1481 | 14.7449 | 11.0219 | -0.0002 | -0.0028 | 0.0006 | 0.0041 | 0.0004 | -0.0008 | 0.0202 | -0.0166 | -0.0073 | -360.2111 | 17.4418 | -360.4912 | 17.7375 | -360.8543 | 18.1769 | -360.9527 | 17.5568 | -352.7706 | 18.7456 | -352.7367 | 16.8032
11:55 | 2142 | 27.1353 | 196.4035 | 438.4099 | 444.707 | -19.9197 | -46.8706 | 5.121 | 2.5469 | -4.2442 | -4.7739 | -1.1331 | -3.0078 | 5.3981 | -1.1478 | 0.5926 | 0.6315 | 0.9532 | 0.7123 | -131.1466 | -5.8276 | 1.754 | -0.3121 | -6.6916 | -5.2074 | 1.4179 |  | -0.8194 | -2.3366 | 4.0142 | 3.365 | 3.35 | 1.0395 | 10.6884 | 14.1448 | 14.7545 | 11.0468 | 0.0001 | -0.0026 | 0.0004 | 0.0037 | 0.0008 | -0.0003 | 0.0109 | -0.007 | -0.0186 | -360.1835 | 17.448 | -360.5004 | 17.7416 | -360.802 | 18.144 | -360.9035 | 17.5239 | -352.7367 | 18.7661 | -352.7183 | 16.8012
11:55 | 2143 | 27.2697 | 196.339 | 438.4637 | 444.8061 | -19.9505 | -46.808 | 5.133 | 2.5788 | -4.2022 | -4.8425 | -1.1644 | -3.1413 | 5.3424 | -1.2642 | 0.5925 | 0.6322 | 0.9513 | 0.7125 | -131.1914 | -5.809 | 1.6488 | -0.2379 | -6.6676 | -5.2103 | 1.3544 |  | -0.8307 | -2.4156 | 4.0138 | 3.3616 | 3.3518 | 1.0387 | 10.7046 | 14.1553 | 14.7195 | 11.0626 | 0 | -0.0028 | 0.0005 | 0.0041 | 0.001 | -0.0005 | 0.0131 | -0.0104 | -0.0283 | -360.1465 | 17.4274 | -360.525 | 17.7909 | -360.8912 | 18.1789 | -360.9189 | 17.5055 | -352.7213 | 18.7518 | -352.786 | 16.8505
11:55 | 2144 | 27.2553 | 196.3654 | 438.3724 | 444.8313 | -19.9334 | -46.8152 | 5.1379 | 2.5906 | -4.0826 | -4.7103 | -1.0867 | -3.0921 | 5.3975 | -1.228 | 0.5913 | 0.6344 | 0.957 | 0.7125 | -131.2274 | -5.7932 | 1.5906 | -0.1674 | -6.717 | -5.2587 | 1.4163 |  | -0.8806 | -2.3535 | 4.0136 | 3.3628 | 3.3498 | 1.0388 | 10.6771 | 14.1152 | 14.7087 | 11.0024 | -0.0006 | -0.0027 | 0.0005 | 0.0035 | 0.0005 | -0.0004 | 0.0122 | -0.0124 | -0.0209 | -360.1342 | 17.4069 | -360.4481 | 17.7395 | -360.8574 | 18.1728 | -360.9035 | 17.526 | -352.6875 | 18.723 | -352.6967 | 16.8053
11:55 | 2145 | 27.3281 | 196.4388 | 438.4356 | 444.7883 | -20.004 | -46.8697 | 5.0232 | 2.6112 | -4.087 | -4.8283 | -1.1554 | -3.089 | 5.3996 | -1.2219 | 0.5922 | 0.6364 | 0.9577 | 0.7118 | -131.1747 | -5.7676 | 1.67 | -0.2491 | -6.7017 | -5.155 | 1.4438 |  | -0.8004 | -2.314 | 4.0134 | 3.3562 | 3.3459 | 1.0369 | 10.7033 | 14.1718 | 14.7607 | 11.055 | 0.0001 | -0.0024 | 0.0014 | 0.004 | 0.0015 | -0.0004 | 0.0087 | -0.0055 | -0.013 | -360.2111 | 17.4685 | -360.5404 | 17.7416 | -360.8112 | 18.1358 | -360.882 | 17.528 | -352.7337 | 18.7908 | -352.7767 | 16.8197
11:55 | 2146 | 27.3469 | 196.4361 | 438.5013 | 444.8339 | -20.0299 | -46.7949 | 5.0677 | 2.5689 | -4.0588 | -4.8553 | -1.1278 | -3.0963 | 5.3606 | -1.2016 | 0.5923 | 0.6346 | 0.955 | 0.7115 | -131.2727 | -5.838 | 1.6659 | -0.1955 | -6.7112 | -5.1609 | 1.523 |  | -0.8172 | -2.2911 | 4.0128 | 3.3578 | 3.353 | 1.0392 | 10.662 | 14.1292 | 14.7241 | 11.0562 | -0.0001 | -0.0032 | 0.0006 | 0.0041 | 0.0006 | -0.0003 | -0.002 | -0.0169 | -0.0199 | -360.1558 | 17.4541 | -360.5619 | 17.7867 | -360.8789 | 18.1461 | -360.8789 | 17.5075 | -352.6937 | 18.7682 | -352.7706 | 16.8423
11:55 | 2147 | 27.3316 | 196.4837 | 438.5004 | 444.8493 | -19.8106 | -46.6073 | 5.3253 | 2.629 | -4.1367 | -4.9134 | -1.1394 | -3.1358 | 5.425 | -1.2274 | 0.5916 | 0.6361 | 0.9544 | 0.7115 | -131.1807 | -5.8659 | 1.6441 | -0.2074 | -6.7329 | -5.2468 | 1.4841 |  | -0.76 | -2.2115 | 4.0143 | 3.3618 | 3.352 | 1.0399 | 10.647 | 14.1256 | 14.69 | 11.0187 | 0 | -0.0029 | 0.0007 | 0.0035 | 0.0004 | -0.0009 | 0.0273 | -0.0085 | 0.0003 | -360.1958 | 17.4151 | -360.4389 | 17.7395 | -360.8297 | 18.181 | -360.9374 | 17.5445 | -352.7213 | 18.7456 | -352.7029 | 16.8094
11:56 | 2148 | 27.3322 | 196.4656 | 438.4065 | 444.795 | -19.8527 | -46.7584 | 5.1472 | 2.6216 | -4.1807 | -4.8867 | -1.094 | -3.0337 | 5.4461 | -1.1669 | 0.5935 | 0.6349 | 0.9548 | 0.7118 | -131.208 | -5.814 | 1.7392 | -0.4133 | -6.7052 | -5.2831 | 1.4838 |  | -0.8212 | -2.2565 | 4.0131 | 3.3622 | 3.3513 | 1.0392 | 10.6712 | 14.1329 | 14.7003 | 11.0129 | -0.0005 | -0.0027 | 0.001 | 0.0039 | 0.0006 | -0.0008 | 0.0078 | -0.0179 | -0.0055 | -360.2327 | 17.4726 | -360.5158 | 17.7231 | -360.802 | 18.1379 | -360.882 | 17.5486 | -352.7737 | 18.7744 | -352.7552 | 16.7909
11:56 | 2149 | 27.3223 | 196.4719 | 438.4967 | 444.8789 | -19.7651 | -46.6833 | 5.3444 | 2.5843 | -4.1629 | -4.9486 | -1.039 | -3.1137 | 5.4101 | -1.2068 | 0.5936 | 0.6311 | 0.9525 | 0.7119 | -131.2362 | -5.8974 | 1.6391 | -0.3711 | -6.5869 | -5.1597 | 1.4851 |  | -0.8875 | -2.3438 | 4.0146 | 3.3621 | 3.3544 | 1.0381 | 10.6874 | 14.1374 | 14.7153 | 11.041 | -0.0005 | -0.0026 | 0.0006 | 0.0037 | 0.0011 | -0.0005 | 0.0302 | -0.0115 | -0.0013 | -360.1219 | 17.4397 | -360.5189 | 17.7744 | -360.8697 | 18.1584 | -360.8974 | 17.5198 | -352.7121 | 18.7559 | -352.786 | 16.8423
11:56 | 2150 | 27.3953 | 196.4249 | 438.5648 | 444.8257 | -19.8297 | -46.8333 | 5.2639 | 2.6702 | -4.1738 | -4.8039 | -1.1405 | -3.0461 | 5.4227 | -1.2294 | 0.5916 | 0.6365 | 0.9562 | 0.7118 | -131.1909 | -5.8067 | 1.6539 | -0.2656 | -6.5849 | -5.1776 | 1.5106 |  | -0.8983 | -2.344 | 4.0135 | 3.3642 | 3.3479 | 1.0394 | 10.6642 | 14.1028 | 14.7221 | 11.0233 | -0.0001 | -0.0034 | 0.0006 | 0.0036 | 0.0011 | -0.0006 | 0.0125 | 0.0041 | 0.0077 | -360.165 | 17.411 | -360.4666 | 17.7293 | -360.8666 | 18.1974 | -360.9374 | 17.5321 | -352.7367 | 18.7128 | -352.6813 | 16.8074
11:56 | 2151 | 27.2492 | 196.4378 | 438.5537 | 444.7783 | -19.8249 | -46.8092 | 5.1556 | 2.6237 | -4.1523 | -4.8275 | -1.1032 | -3.1091 | 5.4273 | -1.185 | 0.5918 | 0.633 | 0.9537 | 0.7114 | -131.1232 | -5.8005 | 1.6455 | -0.36 | -6.5846 | -5.2383 | 1.5234 |  | -0.9355 | -2.3348 | 4.0147 | 3.359 | 3.3506 | 1.0379 | 10.6655 | 14.1269 | 14.7271 | 11.0309 | -0.0003 | -0.0034 | 0.0007 | 0.0039 | 0.0005 | -0.0005 | 0.0096 | -0.0017 | 0.0054 | -360.2327 | 17.4377 | -360.4819 | 17.7354 | -360.8235 | 18.1604 | -360.9281 | 17.5506 | -352.7552 | 18.7579 | -352.7644 | 16.8197
11:56 | 2152 | 27.3588 | 196.477 | 438.5454 | 444.846 | -19.8561 | -46.8888 | 5.2138 | 2.5273 | -4.0492 | -4.7666 | -1.1018 | -3.1261 | 5.5281 | -1.0716 | 0.5921 | 0.6344 | 0.9564 | 0.7107 | -131.1476 | -5.8191 | 1.5848 | -0.4021 | -6.6044 | -5.198 | 1.5006 |  | -0.9255 | -2.3445 | 4.0139 | 3.3613 | 3.3508 | 1.0391 | 10.6932 | 14.1549 | 14.7684 | 11.0638 | -0.0003 | -0.0029 | 0.0004 | 0.0034 | 0.0008 | -0.0006 | 0.0059 | -0.0127 | -0.028 | -360.1835 | 17.4336 | -360.565 | 17.7765 | -360.882 | 18.1502 | -360.8266 | 17.4993 | -352.6629 | 18.7436 | -352.7829 | 16.8423
11:56 | 2153 | 27.3503 | 196.4705 | 438.486 | 444.8112 | -19.9055 | -46.8963 | 5.2058 | 2.5765 | -4.0716 | -4.7176 | -1.1215 | -3.1123 | 5.4746 | -1.1302 | 0.5937 | 0.6311 | 0.955 | 0.7105 | -131.1572 | -5.8853 | 1.5633 | -0.2855 | -6.6027 | -5.3504 | 1.4549 |  | -0.8731 | -2.4029 | 4.0139 | 3.3591 | 3.3496 | 1.0383 | 10.685 | 14.118 | 14.7262 | 11.0092 | -0.0004 | -0.0027 | 0.0007 | 0.0036 | 0.0007 | -0.0004 | 0.0104 | -0.017 | -0.0125 | -360.1527 | 17.4274 | -360.4912 | 17.7683 | -360.8881 | 18.1892 | -360.9343 | 17.5239 | -352.7121 | 18.7436 | -352.7552 | 16.8381
11:56 | 2154 | 27.2938 | 196.4261 | 438.4948 | 444.8284 | -19.8178 | -46.8694 | 5.1149 | 2.6473 | -4.0139 | -4.6689 | -1.0627 | -3.1143 | 5.455 | -1.1243 | 0.5934 | 0.631 | 0.9521 | 0.7109 | -131.2195 | -5.866 | 1.5814 | -0.3433 | -6.5419 | -5.382 | 1.4375 |  | -0.9009 | -2.3616 | 4.0134 | 3.3591 | 3.3521 | 1.0379 | 10.7059 | 14.1272 | 14.7292 | 11.0417 | -0.0003 | -0.0029 | 0.0007 | 0.0036 | 0.0007 | -0.0006 | 0.0023 | -0.0093 | -0.0095 | -360.1742 | 17.4418 | -360.5096 | 17.7231 | -360.7681 | 18.144 | -360.9035 | 17.5424 | -352.749 | 18.76 | -352.7152 | 16.7909
11:56 | 2155 | 27.3753 | 196.3988 | 438.4993 | 444.8761 | -19.857 | -46.8823 | 5.134 | 2.6223 | -4.0648 | -4.7661 | -1.0994 | -3.126 | 5.5067 | -1.0704 | 0.5935 | 0.6338 | 0.9557 | 0.7123 | -131.222 | -5.8582 | 1.5443 | -0.3265 | -6.5062 | -5.3167 | 1.5178 |  | -0.8231 | -2.2942 | 4.0143 | 3.3628 | 3.3516 | 1.0393 | 10.6815 | 14.132 | 14.7358 | 11.0457 | 0.0003 | -0.0034 | 0.0005 | 0.0036 | 0.0007 | -0.0003 | 0.0139 | -0.0052 | -0.0047 | -360.2235 | 17.4685 | -360.565 | 17.7744 | -360.842 | 18.1399 | -360.8943 | 17.5321 | -352.7644 | 18.7826 | -352.7952 | 16.8279
11:56 | 2156 | 27.4285 | 196.4342 | 438.5593 | 444.9628 | -19.7531 | -46.7745 | 5.2211 | 2.5995 | -4.0057 | -4.6361 | -1.0882 | -3.1545 | 5.4205 | -1.0563 | 0.5922 | 0.633 | 0.9532 | 0.7127 | -131.1977 | -5.8861 | 1.5442 | -0.3837 | -6.4843 | -5.2436 | 1.4648 |  | -0.8965 | -2.3439 | 4.0144 | 3.3636 | 3.3496 | 1.0392 | 10.6897 | 14.1572 | 14.7133 | 11.0197 | -0.0003 | -0.0029 | 0.0005 | 0.0037 | 0.0009 | -0.0013 | 0.017 | 0.0048 | -0.0052 | -360.1342 | 17.4131 | -360.4912 | 17.7559 | -360.8358 | 18.1687 | -360.9066 | 17.5137 | -352.6906 | 18.7251 | -352.706 | 16.8053
11:56 | 2157 | 27.3424 | 196.3086 | 438.4254 | 444.8849 | -19.8203 | -46.8957 | 5.2424 | 2.6069 | -4.0196 | -4.7817 | -1.141 | -3.203 | 5.4062 | -1.1498 | 0.5937 | 0.6295 | 0.9543 | 0.7102 | -131.1745 | -5.8619 | 1.6381 | -0.366 | -6.5543 | -5.1811 | 1.4176 |  | -0.8177 | -2.246 | 4.0135 | 3.3609 | 3.3491 | 1.039 | 10.6918 | 14.16 | 14.7481 | 11.0381 | -0.0002 | -0.0026 | 0.0011 | 0.004 | 0.0008 | -0.0001 | 0.0151 | -0.0044 | 0.004 | -360.2265 | 17.4336 | -360.5158 | 17.7498 | -360.8635 | 18.181 | -360.962 | 17.5547 | -352.7521 | 18.76 | -352.7398 | 16.8012
11:56 | 2158 | 27.3798 | 196.3457 | 438.5294 | 444.7846 | -19.7901 | -46.8006 | 5.2764 | 2.734 | -3.9631 | -4.7269 | -1.1851 | -3.1314 | 5.4115 | -1.0664 | 0.5935 | 0.6337 | 0.9506 | 0.7124 | -131.2031 | -5.85 | 1.6833 | -0.3618 | -6.6263 | -5.1932 | 1.3832 |  | -0.8676 | -2.2018 | 4.0137 | 3.3624 | 3.3498 | 1.0383 | 10.6769 | 14.1446 | 14.7187 | 11.024 | -0.0005 | -0.003 | 0.0004 | 0.0037 | 0.0009 | -0.0007 | 0.0033 | -0.0097 | -0.0251 | -360.1742 | 17.4336 | -360.5035 | 17.7395 | -360.8297 | 18.1543 | -360.8789 | 17.5157 | -352.6906 | 18.7477 | -352.7429 | 16.793
11:56 | 2159 | 27.4019 | 196.3704 | 438.6312 | 444.8687 | -19.8967 | -46.8498 | 5.2486 | 2.6583 | -3.9787 | -4.8271 | -1.2019 | -3.1721 | 5.4312 | -1.0316 | 0.5936 | 0.6339 | 0.9561 | 0.7131 | -131.1488 | -5.8155 | 1.6431 | -0.2533 | -6.5321 | -5.3367 | 1.3875 |  | -0.8269 | -2.2386 | 4.0141 | 3.3627 | 3.3515 | 1.0387 | 10.6458 | 14.1362 | 14.6907 | 11.0053 | 0 | -0.0031 | 0.0006 | 0.0037 | 0.0007 | -0.0006 | 0.0133 | 0.0007 | 0.0079 | -360.1773 | 17.4356 | -360.5435 | 17.7724 | -360.8635 | 18.1645 | -360.9466 | 17.5383 | -352.6967 | 18.76 | -352.7829 | 16.8115
11:56 | 2160 | 27.3702 | 196.3479 | 438.5576 | 444.7948 | -19.7896 | -46.8535 | 5.2896 | 2.7268 | -3.9206 | -4.7946 | -1.1387 | -3.1282 | 5.4304 | -1.0608 | 0.5927 | 0.6299 | 0.956 | 0.7121 | -131.1404 | -5.8054 | 1.7388 | -0.2328 | -6.6118 | -5.1924 | 1.4282 |  | -0.9149 | -2.3233 | 4.0133 | 3.3609 | 3.3547 | 1.039 | 10.6816 | 14.1375 | 14.7047 | 10.9887 | 0.0002 | -0.0028 | 0.0009 | 0.0039 | 0.0007 | 0 | 0.0037 | -0.0085 | -0.0152 | -360.1588 | 17.4254 | -360.4758 | 17.7313 | -360.8297 | 18.1502 | -360.8912 | 17.5178 | -352.666 | 18.7415 | -352.7121 | 16.7889
11:56 | 2161 | 27.4569 | 196.3034 | 438.5647 | 444.8833 | -19.8319 | -46.9893 | 5.2087 | 2.5953 | -3.9035 | -4.7756 | -1.1062 | -3.0362 | 5.4487 | -1.1428 | 0.5925 | 0.6305 | 0.9559 | 0.7133 | -131.1361 | -5.7649 | 1.6872 | -0.2687 | -6.6148 | -5.3014 | 1.3924 |  | -0.8736 | -2.2327 | 4.0123 | 3.3597 | 3.3456 | 1.0399 | 10.67 | 14.1375 | 14.7279 | 11.0349 | -0.0004 | -0.0028 | 0.0007 | 0.0041 | 0.0006 | -0.0007 | 0.0115 | 0.0036 | 0.0007 | -360.1773 | 17.45 | -360.5373 | 17.7621 | -360.8574 | 18.1604 | -360.9374 | 17.5321 | -352.7552 | 18.7723 | -352.7921 | 16.8094
11:56 | 2162 | 27.3692 | 196.3065 | 438.4718 | 444.8075 | -19.8429 | -46.8854 | 5.1858 | 2.6704 | -3.9406 | -4.8352 | -1.0807 | -3.0853 | 5.4971 | -1.09 | 0.5936 | 0.6272 | 0.9549 | 0.7138 | -131.1741 | -5.8345 | 1.6545 | -0.301 | -6.6686 | -5.2717 | 1.3309 |  | -0.7654 | -2.259 | 4.0153 | 3.3608 | 3.3495 | 1.038 | 10.6665 | 14.1226 | 14.7075 | 11.0082 | -0.0002 | -0.0027 | 0.001 | 0.0042 | 0.0005 | 0 | 0.0125 | -0.0027 | -0.006 | -360.1496 | 17.4295 | -360.4881 | 17.7498 | -360.8543 | 18.1543 | -360.8604 | 17.5096 | -352.6937 | 18.7497 | -352.7398 | 16.8012
11:56 | 2163 | 27.5096 | 196.3327 | 438.5391 | 444.8465 | -19.863 | -46.8483 | 5.2477 | 2.7177 | -3.8867 | -4.8324 | -1.11 | -2.9588 | 5.4477 | -1.0566 | 0.5935 | 0.6309 | 0.955 | 0.714 | -131.0942 | -5.7752 | 1.7833 | -0.1144 | -6.6798 | -5.17 | 1.3605 |  | -0.8131 | -2.243 | 4.0133 | 3.3637 | 3.3488 | 1.04 | 10.6745 | 14.1308 | 14.7402 | 11.033 | -0.0001 | -0.0034 | 0.0009 | 0.0038 | 0.001 | -0.0006 | 0.0138 | 0.0046 | -0.014 | -360.1619 | 17.4377 | -360.5404 | 17.7601 | -360.842 | 18.1707 | -360.9527 | 17.5506 | -352.7244 | 18.7538 | -352.7583 | 16.795
11:56 | 2164 | 27.4599 | 196.3798 | 438.5721 | 444.8958 | -19.8549 | -46.8596 | 5.2238 | 2.7544 | -3.7569 | -4.696 | -1.0668 | -3.109 | 5.4892 | -1.0955 | 0.5922 | 0.6347 | 0.9576 | 0.7141 | -131.2107 | -5.7844 | 1.8055 | -0.1195 | -6.5971 | -5.2168 | 1.3451 |  | -0.7838 | -2.2364 | 4.0144 | 3.3643 | 3.3488 | 1.0383 | 10.6781 | 14.1399 | 14.719 | 11.0139 | 0.0004 | -0.0029 | 0.0003 | 0.0031 | 0.0003 | -0.0005 | 0.0017 | -0.0109 | -0.022 | -360.1835 | 17.4439 | -360.4973 | 17.7395 | -360.8389 | 18.1461 | -360.9004 | 17.5363 | -352.7367 | 18.7559 | -352.746 | 16.7807
11:56 | 2165 | 27.4182 | 196.3052 | 438.4876 | 444.8336 | -19.8426 | -46.8997 | 5.2165 | 2.782 | -3.7646 | -4.6094 | -1.0261 | -2.9703 | 5.5495 | -1.1236 | 0.5924 | 0.6304 | 0.9534 | 0.7132 | -131.2174 | -5.7724 | 1.704 | 0.0095 | -6.6301 | -5.1339 | 1.3466 |  | -0.7606 | -2.1811 | 4.0133 | 3.3647 | 3.3535 | 1.0388 | 10.6954 | 14.1515 | 14.719 | 11.0486 | -0.0003 | -0.0028 | 0.0005 | 0.0039 | 0.0009 | -0.0006 | 0.0103 | -0.0188 | -0.0247 | -360.2173 | 17.4582 | -360.5312 | 17.758 | -360.8543 | 18.144 | -360.8789 | 17.526 | -352.746 | 18.7703 | -352.7552 | 16.8074
11:56 | 2166 | 27.5365 | 196.2541 | 438.5155 | 444.9505 | -19.8207 | -46.9572 | 5.1731 | 2.7233 | -3.7793 | -4.6232 | -1.0538 | -2.9951 | 5.4898 | -1.1136 | 0.5927 | 0.632 | 0.9527 | 0.7128 | -131.1933 | -5.8426 | 1.6633 | 0.0272 | -6.5701 | -5.1429 | 1.4346 |  | -0.8193 | -2.2234 | 4.0146 | 3.3601 | 3.3518 | 1.039 | 10.67 | 14.1375 | 14.7337 | 11.0291 | -0.0003 | -0.0024 | 0.0004 | 0.0034 | 0.0006 | -0.0007 | 0.0082 | -0.017 | -0.002 | -360.1188 | 17.4213 | -360.5158 | 17.7621 | -360.8758 | 18.1769 | -360.9066 | 17.5116 | -352.709 | 18.7436 | -352.749 | 16.8074
11:56 | 2167 | 27.4526 | 196.2528 | 438.3899 | 444.995 | -19.7996 | -46.95 | 5.2446 | 2.7056 | -3.7822 | -4.7597 | -1.0928 | -3.0262 | 5.5002 | -1.1019 | 0.5922 | 0.6318 | 0.9557 | 0.713 | -131.2559 | -5.7771 | 1.7055 | 0.0162 | -6.5191 | -5.1597 | 1.4542 |  | -0.7815 | -2.2447 | 4.0139 | 3.3613 | 3.3546 | 1.039 | 10.6781 | 14.1166 | 14.6775 | 11.0085 | -0.0003 | -0.0029 | 0.0006 | 0.0038 | 0.0006 | -0.0009 | 0.0176 | -0.015 | 0.0101 | -360.165 | 17.4151 | -360.4266 | 17.719 | -360.8174 | 18.1707 | -360.9281 | 17.5547 | -352.7521 | 18.7292 | -352.6844 | 16.7745
11:56 | 2168 | 27.4646 | 196.2298 | 438.3914 | 444.9706 | -19.8652 | -46.895 | 5.1565 | 2.7999 | -3.7335 | -4.68 | -1.1351 | -2.9767 | 5.5414 | -1.0619 | 0.5919 | 0.6309 | 0.9557 | 0.713 | -131.1868 | -5.8148 | 1.6985 | -0.0274 | -6.4988 | -5.2772 | 1.4402 |  | -0.8884 | -2.2844 | 4.0156 | 3.3629 | 3.3503 | 1.0395 | 10.6791 | 14.124 | 14.7283 | 11.0374 | 0.0001 | -0.0029 | 0.0007 | 0.0041 | 0.001 | -0.0001 | 0.0014 | -0.0009 | 0.0004 | -360.2111 | 17.4705 | -360.5496 | 17.7621 | -360.8697 | 18.144 | -360.9004 | 17.5506 | -352.746 | 18.7785 | -352.8044 | 16.8115
11:56 | 2169 | 27.609 | 196.2896 | 438.423 | 444.9371 | -19.7436 | -46.7662 | 5.2194 | 2.7892 | -3.7144 | -4.6106 | -1.0504 | -3.0283 | 5.5274 | -1.0693 | 0.5922 | 0.6326 | 0.9577 | 0.7146 | -131.182 | -5.7805 | 1.8082 | -0.0438 | -6.579 | -5.2464 | 1.3684 |  | -0.8312 | -2.2809 | 4.014 | 3.3636 | 3.3508 | 1.0397 | 10.6677 | 14.1352 | 14.7309 | 11.0269 | 0 | -0.0031 | 0.0009 | 0.0039 | 0.0009 | -0.0006 | 0.0253 | -0.0057 | -0.0067 | -360.1219 | 17.4213 | -360.4973 | 17.7683 | -360.882 | 18.1604 | -360.8635 | 17.4993 | -352.6783 | 18.7292 | -352.749 | 16.8258
11:56 | 2170 | 27.542 | 196.3079 | 438.5487 | 444.9959 | -19.6687 | -46.7187 | 5.3134 | 2.762 | -3.7028 | -4.7479 | -1.0749 | -3.0847 | 5.5061 | -1.0819 | 0.5938 | 0.6342 | 0.9551 | 0.714 | -131.122 | -5.8515 | 1.7147 | -0.0493 | -6.5362 | -5.1839 | 1.3681 |  | -0.8044 | -2.2555 | 4.0139 | 3.3623 | 3.3496 | 1.0384 | 10.662 | 14.1002 | 14.6999 | 10.993 | -0.0007 | -0.0031 | 0.001 | 0.004 | 0.001 | -0.0004 | 0.0183 | -0.0223 | -0.0028 | -360.1927 | 17.4233 | -360.5035 | 17.758 | -360.8758 | 18.1994 | -360.9466 | 17.5342 | -352.7552 | 18.7415 | -352.7244 | 16.8053
11:56 | 2171 | 27.4592 | 196.2622 | 438.4842 | 444.9276 | -19.6767 | -46.6947 | 5.2655 | 2.7877 | -3.6754 | -4.6956 | -1.076 | -3.0352 | 5.486 | -0.9915 | 0.591 | 0.6332 | 0.9547 | 0.7135 | -131.2237 | -5.8154 | 1.6131 | 0.012 | -6.4785 | -5.1784 | 1.4668 |  | -0.8171 | -2.2756 | 4.0139 | 3.3612 | 3.3528 | 1.0383 | 10.6618 | 14.1412 | 14.7157 | 11.0089 | -0.0001 | -0.0027 | 0.001 | 0.0039 | 0.0011 | -0.0002 | 0.0056 | -0.0132 | -0.0099 | -360.2111 | 17.4439 | -360.4912 | 17.719 | -360.7866 | 18.1214 | -360.8604 | 17.5301 | -352.7306 | 18.7703 | -352.7337 | 16.7704
11:56 | 2172 | 27.5671 | 196.3357 | 438.4835 | 444.9727 | -19.7611 | -46.6345 | 5.2695 | 2.7392 | -3.6607 | -4.6831 | -1.1398 | -3.097 | 5.505 | -1.0459 | 0.5931 | 0.6326 | 0.9576 | 0.7139 | -131.2153 | -5.8141 | 1.6629 | -0.0689 | -6.6195 | -5.2975 | 1.3592 |  | -0.833 | -2.3038 | 4.0144 | 3.3633 | 3.3507 | 1.0385 | 10.6679 | 14.0826 | 14.6862 | 11.0111 | -0.0005 | -0.0035 | 0 | 0.003 | 0.0009 | -0.0008 | -0.0031 | 0.0006 | -0.0104 | -360.1496 | 17.4623 | -360.5773 | 17.7867 | -360.9127 | 18.1543 | -360.8912 | 17.5137 | -352.7367 | 18.7744 | -352.8075 | 16.8361
11:56 | 2173 | 27.5579 | 196.3382 | 438.504 | 444.9988 | -19.7439 | -46.6477 | 5.2514 | 2.7509 | -3.7351 | -4.7894 | -1.049 | -3.1322 | 5.4517 | -1.0547 | 0.5913 | 0.6356 | 0.9506 | 0.7135 | -131.2288 | -5.8079 | 1.6227 | 0.0091 | -6.6338 | -5.1587 | 1.3918 |  | -0.7128 | -2.186 | 4.014 | 3.3618 | 3.3527 | 1.0386 | 10.6654 | 14.127 | 14.6819 | 11.0363 | -0.0003 | -0.0031 | 0.0006 | 0.0035 | 0.0007 | -0.0003 | -0.0093 | -0.0223 | -0.0146 | -360.1988 | 17.4048 | -360.4758 | 17.7334 | -360.8204 | 18.1728 | -360.9251 | 17.5239 | -352.7183 | 18.7251 | -352.6906 | 16.7909
11:56 | 2174 | 27.6193 | 196.3138 | 438.4436 | 444.9595 | -19.7648 | -46.734 | 5.2811 | 2.807 | -3.7443 | -4.7103 | -1.0694 | -3.1694 | 5.5065 | -0.9238 | 0.5914 | 0.6291 | 0.9514 | 0.714 | -131.2785 | -5.9008 | 1.6646 | -0.0798 | -6.6423 | -5.1898 | 1.4429 |  | -0.7956 | -2.2279 | 4.0145 | 3.3605 | 3.3518 | 1.0382 | 10.6435 | 14.1337 | 14.7159 | 11.0382 | -0.0005 | -0.0028 | 0.0003 | 0.0031 | 0.0004 | -0.0012 | 0.0009 | -0.0125 | -0.0072 | -360.2758 | 17.4562 | -360.4942 | 17.7293 | -360.8143 | 18.1543 | -360.9312 | 17.5629 | -352.7952 | 18.7723 | -352.7337 | 16.7786
11:56 | 2175 | 27.6525 | 196.3447 | 438.5371 | 444.947 | -19.7257 | -46.6943 | 5.3572 | 2.7068 | -3.8141 | -4.7487 | -1.0724 | -3.1535 | 5.4545 | -1.0527 | 0.5928 | 0.6317 | 0.9559 | 0.7153 | -131.239 | -5.9054 | 1.5946 | -0.0607 | -6.6143 | -5.1822 | 1.3665 |  | -0.8139 | -2.249 | 4.0148 | 3.3621 | 3.3511 | 1.0388 | 10.6596 | 14.1212 | 14.7513 | 11.0421 | -0.0007 | -0.003 | 0.0001 | 0.0038 | 0.0005 | -0.0003 | -0.0024 | 0.0034 | 0.02 | -360.1373 | 17.4418 | -360.5189 | 17.7457 | -360.8512 | 18.1502 | -360.842 | 17.5157 | -352.706 | 18.7436 | -352.7521 | 16.8094
11:56 | 2176 | 27.6019 | 196.317 | 438.5948 | 444.9395 | -19.6966 | -46.6891 | 5.3115 | 2.702 | -3.8758 | -4.7147 | -1.1717 | -3.1354 | 5.5299 | -1.0615 | 0.5916 | 0.6346 | 0.9515 | 0.7136 | -131.2085 | -5.8206 | 1.6208 | -0.1151 | -6.6025 | -5.1852 | 1.3538 |  | -0.7042 | -2.2495 | 4.0144 | 3.3606 | 3.3524 | 1.0407 | 10.7022 | 14.1532 | 14.7362 | 11.025 | 0.0003 | -0.0027 | 0.0013 | 0.0043 | 0.0008 | -0.0007 | 0.0061 | -0.0079 | -0.0114 | -360.1342 | 17.4007 | -360.4789 | 17.7621 | -360.8943 | 18.2077 | -360.9497 | 17.528 | -352.7244 | 18.7292 | -352.6844 | 16.8032
11:56 | 2177 | 27.6007 | 196.2614 | 438.4703 | 444.886 | -19.6849 | -46.6437 | 5.391 | 2.6884 | -3.8994 | -4.6917 | -1.1629 | -3.1746 | 5.5287 | -1.0073 | 0.5926 | 0.6354 | 0.9501 | 0.7135 | -131.1967 | -5.776 | 1.6972 | -0.069 | -6.5619 | -5.2519 | 1.4031 |  | -0.7154 | -2.183 | 4.0149 | 3.3612 | 3.3493 | 1.0389 | 10.6908 | 14.147 | 14.7794 | 11.0377 | 0 | -0.003 | 0.0005 | 0.0036 | 0.0002 | -0.0005 | -0.0029 | -0.0128 | -0.0183 | -360.1988 | 17.4274 | -360.4635 | 17.7375 | -360.8174 | 18.1584 | -360.9189 | 17.5465 | -352.7552 | 18.7497 | -352.7152 | 16.7909
11:56 | 2178 | 27.5849 | 196.3279 | 438.5005 | 444.8466 | -19.6731 | -46.7296 | 5.4306 | 2.772 | -3.9389 | -4.7474 | -1.0931 | -3.1561 | 5.5588 | -1.0275 | 0.5926 | 0.6365 | 0.9541 | 0.7134 | -131.1641 | -5.8033 | 1.7088 | -0.1162 | -6.5634 | -5.2339 | 1.3852 |  | -0.7015 | -2.2254 | 4.0139 | 3.3577 | 3.3516 | 1.0382 | 10.6757 | 14.1377 | 14.7231 | 11.0287 | -0.0003 | -0.0028 | 0.0001 | 0.0034 | 0.0006 | -0.0005 | 0.0132 | 0.0021 | 0.0066 | -360.1835 | 17.4582 | -360.565 | 17.7683 | -360.8943 | 18.1461 | -360.8574 | 17.5116 | -352.6998 | 18.7641 | -352.7767 | 16.8197
11:56 | 2179 | 27.6722 | 196.3097 | 438.5355 | 444.9841 | -19.7079 | -46.7962 | 5.418 | 2.7474 | -3.9526 | -4.7058 | -1.1362 | -3.1329 | 5.5949 | -0.8818 | 0.5942 | 0.6367 | 0.9541 | 0.7152 | -131.2316 | -5.7788 | 1.6947 | -0.1512 | -6.6045 | -5.2589 | 1.3434 |  | -0.7001 | -2.1747 | 4.0126 | 3.36 | 3.3509 | 1.0398 | 10.6641 | 14.1436 | 14.7531 | 11.0341 | -0.0005 | -0.0029 | 0.0005 | 0.0036 | 0.0006 | -0.0007 | -0.0081 | -0.0134 | -0.0284 | -360.1527 | 17.4213 | -360.5219 | 17.7683 | -360.8789 | 18.1728 | -360.9035 | 17.5055 | -352.7213 | 18.7456 | -352.7798 | 16.8094
11:56 | 2180 | 27.6208 | 196.2397 | 438.5672 | 444.92 | -19.6309 | -46.7881 | 5.4684 | 2.7311 | -4.0525 | -4.7293 | -1.0575 | -3.0939 | 5.5172 | -0.96 | 0.5936 | 0.6351 | 0.9546 | 0.7134 | -131.2277 | -5.8334 | 1.7527 | -0.1145 | -6.4868 | -5.1571 | 1.3534 |  | -0.7838 | -2.1589 | 4.0142 | 3.3585 | 3.3529 | 1.0399 | 10.6631 | 14.1304 | 14.7197 | 11.0284 | -0.0002 | -0.0031 | 0.0003 | 0.0032 | 0.0006 | -0.0006 | 0.011 | -0.0112 | 0.004 | -360.2358 | 17.45 | -360.5096 | 17.7354 | -360.8174 | 18.1563 | -360.922 | 17.5588 | -352.7398 | 18.7559 | -352.749 | 16.7766
11:56 | 2181 | 27.5673 | 196.2944 | 438.6269 | 444.8664 | -19.6278 | -46.8792 | 5.4695 | 2.6661 | -4.0939 | -4.7617 | -1.0793 | -3.2017 | 5.4765 | -0.9551 | 0.5939 | 0.6345 | 0.955 | 0.7144 | -131.2592 | -5.8673 | 1.6672 | -0.23 | -6.5107 | -5.1568 | 1.3837 |  | -0.8263 | -2.1617 | 4.0145 | 3.3599 | 3.3512 | 1.0382 | 10.6285 | 14.1072 | 14.6781 | 11.0172 | 0.0002 | -0.0031 | 0.0009 | 0.004 | 0.0011 | -0.0009 | 0.007 | 0.0099 | 0.0004 | -360.1804 | 17.4521 | -360.5343 | 17.7621 | -360.8358 | 18.1358 | -360.8727 | 17.526 | -352.7244 | 18.7579 | -352.7644 | 16.8074
11:56 | 2182 | 27.6859 | 196.2964 | 438.5333 | 444.9309 | -19.6727 | -46.804 | 5.5374 | 2.7092 | -4.1061 | -4.7774 | -1.1707 | -3.166 | 5.5301 | -0.9989 | 0.5941 | 0.6357 | 0.9546 | 0.7118 | -131.2418 | -5.9207 | 1.7571 | -0.3161 | -6.5285 | -5.2678 | 1.3438 |  | -0.7513 | -2.1935 | 4.0133 | 3.3611 | 3.3518 | 1.0397 | 10.647 | 14.143 | 14.6853 | 10.9779 | -0.0003 | -0.0031 | 0.0013 | 0.0041 | 0.0003 | -0.0004 | 0.0239 | -0.0071 | -0.0007 | -360.1958 | 17.4274 | -360.4973 | 17.7703 | -360.882 | 18.183 | -360.9281 | 17.5239 | -352.709 | 18.7456 | -352.7614 | 16.8053
11:56 | 2183 | 27.6163 | 196.2733 | 438.5563 | 445.0059 | -19.76 | -46.7298 | 5.5639 | 2.6725 | -4.097 | -4.7358 | -1.0966 | -3.2383 | 5.4316 | -1.0525 | 0.5947 | 0.6345 | 0.9572 | 0.7141 | -131.2642 | -5.9434 | 1.7245 | -0.1719 | -6.5605 | -5.2738 | 1.3994 |  | -0.6713 | -2.213 | 4.0151 | 3.3588 | 3.3516 | 1.0398 | 10.6803 | 14.154 | 14.7518 | 11.0504 | -0.0005 | -0.0028 | 0.0007 | 0.0035 | 0.0009 | -0.0008 | -0.0007 | 0.0006 | -0.0288 | -360.1835 | 17.4274 | -360.4881 | 17.7477 | -360.8143 | 18.1563 | -360.9374 | 17.5424 | -352.7398 | 18.7333 | -352.7183 | 16.7786
11:56 | 2184 | 27.6478 | 196.3534 | 438.551 | 444.9337 | -19.6801 | -46.7332 | 5.6141 | 2.7606 | -4.1091 | -4.7799 | -1.0504 | -3.1398 | 5.5378 | -0.9545 | 0.5941 | 0.6344 | 0.9566 | 0.7129 | -131.2599 | -5.8778 | 1.7742 | -0.2436 | -6.4707 | -5.0336 | 1.517 |  | -0.7626 | -2.1553 | 4.0152 | 3.361 | 3.3488 | 1.0394 | 10.6527 | 14.12 | 14.6979 | 11.0064 | -0.0001 | -0.0031 | 0.001 | 0.0043 | 0.0006 | -0.0003 | 0.0104 | -0.0105 | -0.0109 | -360.1773 | 17.4541 | -360.5712 | 17.7929 | -360.8758 | 18.1625 | -360.882 | 17.5198 | -352.7521 | 18.7579 | -352.7706 | 16.8156
11:56 | 2185 | 27.6707 | 196.4336 | 438.5231 | 444.9626 | -19.7133 | -46.7623 | 5.6883 | 2.7369 | -4.049 | -4.6366 | -1.061 | -3.1826 | 5.563 | -0.9311 | 0.5938 | 0.6332 | 0.9591 | 0.7124 | -131.2587 | -5.8332 | 1.6682 | -0.3123 | -6.4878 | -5.0874 | 1.4781 |  | -0.7007 | -2.1886 | 4.013 | 3.3606 | 3.3479 | 1.0377 | 10.7184 | 14.1636 | 14.7522 | 11.0355 | 0.0003 | -0.0028 | 0.0006 | 0.0038 | 0.0008 | -0.0002 | 0.0034 | 0.0009 | -0.0232 | -360.1865 | 17.4151 | -360.4758 | 17.7744 | -360.8697 | 18.1728 | -360.8789 | 17.5157 | -352.666 | 18.7312 | -352.706 | 16.8053
11:56 | 2186 | 27.6382 | 196.3335 | 438.5436 | 444.9557 | -19.7472 | -46.6909 | 5.6382 | 2.7806 | -4.0882 | -4.7517 | -1.0831 | -3.202 | 5.4606 | -0.9879 | 0.594 | 0.6325 | 0.9544 | 0.7123 | -131.1935 | -5.8209 | 1.6907 | -0.3656 | -6.5207 | -5.1733 | 1.413 |  | -0.7836 | -2.2544 | 4.015 | 3.36 | 3.348 | 1.0381 | 10.7058 | 14.1563 | 14.7314 | 11.041 | -0.0003 | -0.003 | 0.0006 | 0.0035 | 0.0005 | 0 | 0.0073 | -0.0069 | -0.0118 | -360.2142 | 17.4562 | -360.5373 | 17.7765 | -360.8512 | 18.1707 | -360.9066 | 17.5465 | -352.786 | 18.7682 | -352.7521 | 16.7971
11:56 | 2187 | 27.5919 | 196.3245 | 438.5796 | 444.9333 | -19.669 | -46.6978 | 5.6089 | 2.8398 | -4.0308 | -4.5728 | -1.0845 | -3.0565 | 5.5549 | -0.8937 | 0.5936 | 0.6343 | 0.9567 | 0.7124 | -131.2362 | -5.9728 | 1.649 | -0.1922 | -6.5168 | -5.2108 | 1.4251 |  | -0.7617 | -2.1966 | 4.0135 | 3.3592 | 3.3471 | 1.038 | 10.6942 | 14.1389 | 14.7129 | 11.0356 | -0.0005 | -0.0027 | 0.0008 | 0.0035 | 0.0004 | -0.0006 | 0.011 | -0.0109 | 0.0026 | -360.1865 | 17.4356 | -360.5158 | 17.7806 | -360.8235 | 18.1502 | -360.8881 | 17.5157 | -352.6844 | 18.7436 | -352.7367 | 16.8012
11:56 | 2188 | 27.6837 | 196.4614 | 438.5613 | 444.9463 | -19.6469 | -46.6292 | 5.6129 | 2.9026 | -4.0385 | -4.6115 | -1.0667 | -3.0699 | 5.6442 | -0.9859 | 0.5932 | 0.6348 | 0.9571 | 0.7146 | -131.1693 | -5.9293 | 1.7639 | -0.1121 | -6.5199 | -5.1692 | 1.4852 |  | -0.6996 | -2.1862 | 4.0127 | 3.3608 | 3.3505 | 1.0384 | 10.6654 | 14.1272 | 14.7235 | 11.0533 | 0.0002 | -0.0025 | 0.0004 | 0.0031 | 0.0009 | -0.0008 | 0.0039 | -0.0188 | -0.0037 | -360.165 | 17.4377 | -360.5096 | 17.7724 | -360.8574 | 18.1604 | -360.9281 | 17.5383 | -352.7306 | 18.7559 | -352.7367 | 16.8074
11:56 | 2189 | 27.6584 | 196.4458 | 438.631 | 444.9802 | -19.7045 | -46.6228 | 5.6702 | 2.9337 | -4.0102 | -4.6288 | -0.996 | -3.0986 | 5.6035 | -1.0043 | 0.5943 | 0.6298 | 0.9561 | 0.7134 | -131.0582 | -5.8368 | 1.724 | -0.0158 | -6.4441 | -5.1202 | 1.5148 |  | -0.6503 | -2.2208 | 4.0146 | 3.3619 | 3.3518 | 1.038 | 10.6505 | 14.1116 | 14.6699 | 10.9934 | -0.0001 | -0.0032 | 0.0006 | 0.0034 | 0 | -0.001 | 0.0149 | -0.0041 | 0.0018 | -360.1742 | 17.4315 | -360.4973 | 17.7621 | -360.8266 | 18.1296 | -360.9066 | 17.526 | -352.7337 | 18.7456 | -352.7398 | 16.7909
11:56 | 2190 | 27.6386 | 196.4546 | 438.5805 | 445.0302 | -19.6834 | -46.6395 | 5.5437 | 2.9553 | -3.9227 | -4.6059 | -0.9394 | -3.1427 | 5.5197 | -0.9866 | 0.5943 | 0.6328 | 0.9543 | 0.7142 | -131.1779 | -5.9224 | 1.7796 | -0.145 | -6.4872 | -5.0865 | 1.4144 |  | -0.5826 | -2.2297 | 4.0133 | 3.3599 | 3.3476 | 1.0386 | 10.6642 | 14.1261 | 14.6942 | 10.9998 | 0 | -0.003 | 0.0011 | 0.004 | 0.0012 | -0.0006 | 0.0098 | 0.0022 | -0.0081 | -360.1958 | 17.4315 | -360.5189 | 17.7765 | -360.8512 | 18.1399 | -360.9127 | 17.5301 | -352.746 | 18.7579 | -352.7614 | 16.8032
11:56 | 2191 | 27.6907 | 196.4092 | 438.5989 | 444.9686 | -19.7304 | -46.6087 | 5.4834 | 2.9107 | -3.8754 | -4.6485 | -0.9537 | -3.1464 | 5.5503 | -0.9856 | 0.5933 | 0.6357 | 0.9518 | 0.7138 | -131.1217 | -5.8839 | 1.7944 | -0.1742 | -6.6087 | -5.0975 | 1.4734 |  | -0.6583 | -2.2576 | 4.0157 | 3.36 | 3.3523 | 1.0384 | 10.6966 | 14.1005 | 14.7078 | 11.0443 | -0.0002 | -0.0027 | 0.0007 | 0.004 | 0.0005 | -0.0008 | 0.012 | 0.0007 | -0.0176 | -360.1619 | 17.4377 | -360.4881 | 17.7662 | -360.8481 | 18.1358 | -360.9158 | 17.5321 | -352.7367 | 18.7538 | -352.7275 | 16.7889
11:56 | 2192 | 27.7193 | 196.4255 | 438.6927 | 444.9981 | -19.6757 | -46.5846 | 5.5229 | 2.7595 | -3.8713 | -4.6072 | -0.9997 | -3.1436 | 5.5898 | -0.9789 | 0.5943 | 0.6317 | 0.9557 | 0.7128 | -131.1993 | -5.8581 | 1.7564 | -0.0995 | -6.5837 | -5.1626 | 1.4919 |  | -0.6266 | -2.3325 | 4.014 | 3.3601 | 3.3487 | 1.0383 | 10.6931 | 14.155 | 14.7174 | 11.0345 | -0.0004 | -0.0026 | 0.001 | 0.0039 | 0.0008 | -0.0008 | 0.0172 | -0.0045 | -0.014 | -360.1681 | 17.4336 | -360.5219 | 17.7826 | -360.8389 | 18.1009 | -360.8727 | 17.5178 | -352.6937 | 18.7497 | -352.7552 | 16.8094
11:56 | 2193 | 27.7524 | 196.4336 | 438.586 | 444.9671 | -19.6861 | -46.5422 | 5.4985 | 2.7578 | -3.8742 | -4.6841 | -1.0106 | -3.0831 | 5.6015 | -0.9823 | 0.593 | 0.637 | 0.9552 | 0.7127 | -131.0752 | -5.7688 | 1.8027 | -0.1096 | -6.6968 | -5.2424 | 1.3649 |  | -0.5772 | -2.2762 | 4.0156 | 3.3616 | 3.3512 | 1.0384 | 10.6815 | 14.1492 | 14.7347 | 11.0461 | -0.0002 | -0.0029 | 0.0007 | 0.0037 | 0.0003 | -0.0004 | 0.0214 | -0.0131 | -0.0063 | -360.1681 | 17.4439 | -360.4942 | 17.795 | -360.8881 | 18.1543 | -360.9066 | 17.5363 | -352.7244 | 18.7518 | -352.7644 | 16.8197
11:56 | 2194 | 27.7171 | 196.3745 | 438.6364 | 444.9103 | -19.7015 | -46.5362 | 5.5813 | 2.815 | -3.8173 | -4.5594 | -0.9627 | -3.0219 | 5.6096 | -1.039 | 0.593 | 0.6361 | 0.9578 | 0.7141 | -131.0872 | -5.8162 | 1.7872 | -0.1111 | -6.6493 | -5.1934 | 1.395 |  | -0.6666 | -2.2393 | 4.0148 | 3.3606 | 3.3505 | 1.0386 | 10.7001 | 14.1387 | 14.7524 | 11.0648 | 0.0001 | -0.0033 | 0 | 0.0033 | 0.001 | -0.0007 | 0.022 | -0.0203 | -0.0039 | -360.1588 | 17.4418 | -360.4881 | 17.7416 | -360.805 | 18.1235 | -360.8881 | 17.5342 | -352.6844 | 18.7415 | -352.7213 | 16.7766
11:56 | 2195 | 27.6703 | 196.4152 | 438.6869 | 445.0155 | -19.6329 | -46.6271 | 5.5094 | 2.7673 | -3.843 | -4.7142 | -1.0552 | -3.0796 | 5.5602 | -0.9929 | 0.5912 | 0.6326 | 0.9525 | 0.7124 | -131.0007 | -5.8024 | 1.7995 | -0.1281 | -6.6846 | -5.1522 | 1.3746 |  | -0.607 | -2.2984 | 4.0156 | 3.3627 | 3.352 | 1.0396 | 10.6747 | 14.1421 | 14.7034 | 11.028 | -0.0003 | -0.003 | 0.0009 | 0.0039 | 0.0003 | -0.0002 | 0.0097 | -0.0256 | -0.0044 | -360.2358 | 17.4603 | -360.5404 | 17.7888 | -360.8574 | 18.1235 | -360.885 | 17.5568 | -352.749 | 18.7703 | -352.786 | 16.8115
11:56 | 2196 | 27.7323 | 196.3212 | 438.6204 | 444.9527 | -19.6468 | -46.662 | 5.4846 | 2.8465 | -3.8649 | -4.7219 | -1.048 | -2.947 | 5.5736 | -0.9582 | 0.5936 | 0.6315 | 0.9555 | 0.7151 | -131.0855 | -5.8843 | 1.8381 | -0.0215 | -6.5855 | -5.266 | 1.4518 |  | -0.608 | -2.1774 | 4.0158 | 3.3629 | 3.3508 | 1.0401 | 10.6863 | 14.1187 | 14.736 | 11.0403 | -0.0004 | -0.003 | 0.0009 | 0.0038 | 0.0009 | -0.0006 | 0.0012 | -0.0141 | 0.0021 | -360.1465 | 17.4151 | -360.4819 | 17.7724 | -360.8574 | 18.1214 | -360.8604 | 17.5321 | -352.6937 | 18.7436 | -352.7244 | 16.8032
11:56 | 2197 | 27.7808 | 196.4109 | 438.607 | 444.9541 | -19.6675 | -46.5896 | 5.4697 | 2.8693 | -3.8285 | -4.6322 | -1.0685 | -3.0456 | 5.593 | -0.9311 | 0.594 | 0.6355 | 0.9532 | 0.7136 | -131.1435 | -5.8874 | 1.8482 | 0.0295 | -6.5907 | -5.0911 | 1.4939 |  | -0.6201 | -2.2321 | 4.0132 | 3.3584 | 3.3476 | 1.038 | 10.6563 | 14.1233 | 14.7288 | 11.0162 | -0.0003 | -0.0028 | 0.0008 | 0.0038 | 0.0004 | -0.0009 | 0.0252 | 0.0043 | 0.0064 | -360.1958 | 17.4274 | -360.4727 | 17.7601 | -360.845 | 18.1522 | -360.9312 | 17.5753 | -352.7644 | 18.7415 | -352.706 | 16.7868
11:56 | 2198 | 27.8211 | 196.4902 | 438.7884 | 445.0411 | -19.6141 | -46.5097 | 5.5885 | 2.7954 | -3.8606 | -4.6009 | -1.0004 | -3.0325 | 5.5892 | -0.9781 | 0.5937 | 0.6325 | 0.9573 | 0.7141 | -131.0848 | -5.8683 | 1.7793 | -0.0033 | -6.6251 | -5.0837 | 1.4572 |  | -0.5605 | -2.1617 | 4.0161 | 3.3627 | 3.3486 | 1.0377 | 10.6733 | 14.1471 | 14.7225 | 11.0085 | 0.0002 | -0.0032 | 0.0009 | 0.0037 | 0.0008 | -0.0004 | 0.0167 | -0.001 | -0.0203 | -360.2111 | 17.4521 | -360.5035 | 17.7621 | -360.8235 | 18.1214 | -360.9004 | 17.5568 | -352.7398 | 18.76 | -352.7306 | 16.7848
11:56 | 2199 | 27.7377 | 196.4701 | 438.6895 | 444.9763 | -19.6313 | -46.6001 | 5.6103 | 2.8697 | -3.7635 | -4.5573 | -1.0121 | -2.951 | 5.6553 | -0.9463 | 0.594 | 0.6331 | 0.9579 | 0.7137 | -131.0261 | -5.9114 | 1.772 | -0.0761 | -6.5906 | -5.2063 | 1.4064 |  | -0.6085 | -2.2389 | 4.014 | 3.3602 | 3.3485 | 1.0393 | 10.677 | 14.1328 | 14.7166 | 11.0363 | -0.0003 | -0.0033 | 0.0004 | 0.0036 | 0.0007 | -0.0011 | -0.0053 | -0.0253 | -0.0134 | -360.1096 | 17.4233 | -360.5343 | 17.7888 | -360.8881 | 18.1358 | -360.9004 | 17.526 | -352.6721 | 18.7312 | -352.789 | 16.8217
11:56 | 2200 | 27.751 | 196.4516 | 438.6401 | 445.0103 | -19.7398 | -46.7363 | 5.5678 | 2.8687 | -3.8492 | -4.5875 | -0.9437 | -3.0533 | 5.5417 | -0.9498 | 0.595 | 0.6349 | 0.956 | 0.7148 | -131.1797 | -5.9093 | 1.758 | -0.0248 | -6.5736 | -5.327 | 1.4106 |  | -0.5965 | -2.2755 | 4.0159 | 3.3594 | 3.3473 | 1.0387 | 10.6873 | 14.1666 | 14.7521 | 11.0345 | -0.0005 | -0.0027 | 0.0007 | 0.0039 | 0.0004 | -0.0006 | -0.0017 | -0.0042 | -0.0216 | -360.1496 | 17.4151 | -360.4819 | 17.7601 | -360.845 | 18.1461 | -360.9281 | 17.5568 | -352.7398 | 18.723 | -352.7121 | 16.7868
11:56 | 2201 | 27.775 | 196.46 | 438.6295 | 445.0104 | -19.7768 | -46.8802 | 5.4358 | 2.8983 | -3.7584 | -4.5905 | -1.0206 | -2.9507 | 5.6113 | -0.9673 | 0.594 | 0.6358 | 0.9557 | 0.7133 | -131.1847 | -5.885 | 1.8001 | -0.0884 | -6.593 | -5.2537 | 1.4412 |  | -0.4971 | -2.2542 | 4.0158 | 3.3609 | 3.3502 | 1.0392 | 10.7057 | 14.1566 | 14.7624 | 11.0633 | -0.0003 | -0.0029 | 0.0008 | 0.0041 | 0.0008 | -0.0004 | 0.0028 | -0.0075 | -0.016 | -360.2019 | 17.4705 | -360.5435 | 17.7744 | -360.8635 | 18.105 | -360.8543 | 17.5342 | -352.746 | 18.7703 | -352.7737 | 16.8115
11:56 | 2202 | 27.795 | 196.4339 | 438.6601 | 445.0725 | -19.8169 | -46.9185 | 5.3843 | 2.8595 | -3.6676 | -4.5149 | -1.0192 | -2.9719 | 5.681 | -0.9205 | 0.5939 | 0.6352 | 0.9545 | 0.7128 | -131.1221 | -5.9097 | 1.9072 | -0.0371 | -6.551 | -5.1855 | 1.4804 |  | -0.6712 | -2.2634 | 4.0146 | 3.3569 | 3.3498 | 1.0376 | 10.7242 | 14.1808 | 14.7338 | 11.0417 | 0.0001 | -0.0031 | 0.0007 | 0.0038 | 0.0003 | -0.0003 | 0.0026 | -0.0119 | -0.0125 | -360.1281 | 17.448 | -360.5373 | 17.8093 | -360.8912 | 18.1317 | -360.885 | 17.528 | -352.6783 | 18.7436 | -352.7675 | 16.8217
11:56 | 2203 | 27.7775 | 196.4488 | 438.6695 | 445.0488 | -19.7483 | -46.957 | 5.4857 | 2.82 | -3.6285 | -4.5915 | -0.9833 | -3.0144 | 5.6171 | -1.0131 | 0.5923 | 0.6371 | 0.9564 | 0.7139 | -131.0448 | -5.8651 | 1.877 | -0.0248 | -6.5288 | -5.0451 | 1.5014 |  | -0.7035 | -2.1851 | 4.0138 | 3.358 | 3.349 | 1.038 | 10.6942 | 14.1563 | 14.7429 | 11.0525 | 0.0002 | -0.0029 | 0.0009 | 0.0039 | 0.0011 | -0.0005 | 0.0118 | -0.0189 | -0.0222 | -360.2204 | 17.4172 | -360.4696 | 17.7477 | -360.7712 | 18.1194 | -360.922 | 17.5814 | -352.7552 | 18.7251 | -352.6998 | 16.7848
11:56 | 2204 | 27.7104 | 196.4065 | 438.5896 | 445.0948 | -19.7389 | -46.9001 | 5.5185 | 2.9157 | -3.6062 | -4.4811 | -0.9038 | -3.0722 | 5.5547 | -0.9855 | 0.5934 | 0.6341 | 0.9574 | 0.7138 | -131.0851 | -5.8888 | 1.7877 | -0.0621 | -6.6383 | -5.0661 | 1.4363 |  | -0.6973 | -2.2735 | 4.0143 | 3.3625 | 3.3489 | 1.0388 | 10.6815 | 14.1435 | 14.7521 | 11.0461 | -0.0003 | -0.0026 | 0.0006 | 0.0035 | 0.0002 | -0.0005 | 0.0106 | -0.0003 | -0.0038 | -360.2542 | 17.4747 | -360.5466 | 17.7867 | -360.8358 | 18.1132 | -360.885 | 17.5629 | -352.7952 | 18.7703 | -352.7767 | 16.7991
11:56 | 2205 | 27.7511 | 196.3793 | 438.6283 | 444.9557 | -19.7516 | -46.9436 | 5.6167 | 2.9069 | -3.623 | -4.4298 | -0.8813 | -2.9369 | 5.566 | -0.9586 | 0.5921 | 0.6351 | 0.9546 | 0.712 | -131.0775 | -5.9121 | 1.7455 | -0.0736 | -6.6946 | -5.2759 | 1.3702 |  | -0.6493 | -2.3416 | 4.0152 | 3.3602 | 3.3496 | 1.0394 | 10.669 | 14.1244 | 14.6944 | 11.0061 | -0.0002 | -0.0027 | 0.0002 | 0.0033 | 0.0006 | -0.0007 | 0.0014 | -0.0064 | -0.0254 | -360.1219 | 17.4028 | -360.485 | 17.7744 | -360.882 | 18.142 | -360.9066 | 17.5198 | -352.6721 | 18.7087 | -352.709 | 16.7991
11:56 | 2206 | 27.7411 | 196.3964 | 438.6443 | 444.9987 | -19.789 | -46.9117 | 5.5821 | 2.8863 | -3.6699 | -4.4401 | -0.8742 | -2.9132 | 5.5326 | -0.8929 | 0.5925 | 0.6348 | 0.9527 | 0.7106 | -131.1005 | -5.9669 | 1.7483 | 0.0045 | -6.5847 | -5.0727 | 1.5671 |  | -0.6477 | -2.4289 | 4.0156 | 3.3605 | 3.3514 | 1.0404 | 10.6411 | 14.1027 | 14.6805 | 10.9948 | -0.0002 | -0.0034 | 0.0008 | 0.0043 | 0.0009 | -0.0005 | -0.0081 | -0.0076 | -0.0089 | -360.1988 | 17.4356 | -360.4727 | 17.7683 | -360.8204 | 18.1543 | -361.002 | 17.5753 | -352.789 | 18.7395 | -352.7121 | 16.7909
11:56 | 2207 | 27.7843 | 196.3965 | 438.5944 | 445.0063 | -19.8359 | -46.9879 | 5.5335 | 2.8919 | -3.69 | -4.4275 | -0.9007 | -2.961 | 5.603 | -0.9788 | 0.5933 | 0.6373 | 0.9572 | 0.7127 | -131.1103 | -5.9282 | 1.7583 | 0.0474 | -6.6251 | -5.2122 | 1.476 |  | -0.6348 | -2.2724 | 4.0152 | 3.3641 | 3.3486 | 1.0387 | 10.662 | 14.1119 | 14.7183 | 11.01 | 0.0003 | -0.0031 | 0.0009 | 0.0035 | 0.0004 | -0.0009 | 0.0001 | -0.0139 | -0.0172 | -360.1588 | 17.4459 | -360.5312 | 17.7806 | -360.8389 | 18.1029 | -360.8604 | 17.5321 | -352.7121 | 18.7497 | -352.749 | 16.795
11:57 | 2208 | 27.8005 | 196.4422 | 438.5824 | 444.9775 | -19.7828 | -47.0368 | 5.5004 | 2.8071 | -3.6484 | -4.4797 | -0.9126 | -3.0678 | 5.5787 | -0.9795 | 0.5931 | 0.6359 | 0.9558 | 0.7134 | -131.1412 | -5.8599 | 1.8399 | -0.0342 | -6.5674 | -5.1384 | 1.4233 |  | -0.6267 | -2.1587 | 4.016 | 3.361 | 3.3466 | 1.0383 | 10.6816 | 14.1086 | 14.6989 | 11.0176 | -0.0002 | -0.0031 | 0.0005 | 0.0037 | 0.0011 | -0.0002 | 0.0096 | -0.0047 | -0.0052 | -360.0973 | 17.4315 | -360.525 | 17.8175 | -360.9497 | 18.1543 | -360.9158 | 17.5383 | -352.6813 | 18.7189 | -352.749 | 16.8156
11:57 | 2209 | 27.8593 | 196.4249 | 438.6631 | 445.1047 | -19.6951 | -46.9005 | 5.5642 | 2.7664 | -3.7724 | -4.4971 | -0.9793 | -3.0613 | 5.6461 | -1.0172 | 0.5944 | 0.6337 | 0.9517 | 0.7113 | -131.2053 | -5.8816 | 1.8483 | -0.0443 | -6.6151 | -5.1284 | 1.3661 |  | -0.6396 | -2.0759 | 4.0155 | 3.3601 | 3.3502 | 1.0384 | 10.6953 | 14.146 | 14.7501 | 11.0363 | 0 | -0.0022 | 0.0008 | 0.004 | 0.0004 | -0.0004 | 0.0034 | 0.0021 | -0.036 | -360.1865 | 17.4315 | -360.4635 | 17.7375 | -360.7927 | 18.1214 | -360.9127 | 17.5671 | -352.709 | 18.7251 | -352.6906 | 16.7683
11:57 | 2210 | 27.8382 | 196.4273 | 438.6577 | 445.0126 | -19.6075 | -46.7663 | 5.6178 | 2.8028 | -3.8198 | -4.4219 | -0.9388 | -3.0437 | 5.6999 | -0.9273 | 0.594 | 0.6353 | 0.9532 | 0.7098 | -131.1756 | -5.8288 | 1.8761 | -0.0311 | -6.5291 | -5.1427 | 1.4632 |  | -0.6223 | -2.1547 | 4.0148 | 3.3589 | 3.3497 | 1.0391 | 10.7151 | 14.1538 | 14.7391 | 11.0334 | 0.0001 | -0.0027 | 0.0001 | 0.0032 | 0.0004 | -0.0009 | 0.0034 | -0.0071 | -0.0144 | -360.2512 | 17.4788 | -360.5835 | 17.795 | -360.845 | 18.0988 | -360.885 | 17.5568 | -352.789 | 18.7846 | -352.8198 | 16.8094
11:57 | 2211 | 27.834 | 196.4318 | 438.6328 | 444.9738 | -19.6638 | -46.7982 | 5.5057 | 2.8887 | -3.7968 | -4.486 | -0.9205 | -2.963 | 5.622 | -1.0251 | 0.5947 | 0.6392 | 0.955 | 0.7114 | -131.0983 | -5.8954 | 1.8549 | -0.1619 | -6.5586 | -5.1603 | 1.3134 |  | -0.586 | -2.1005 | 4.0159 | 3.3596 | 3.3491 | 1.0391 | 10.6977 | 14.1482 | 14.7113 | 11.0562 | 0.0004 | -0.0028 | 0.0008 | 0.0034 | 0.0006 | -0.0001 | -0.0061 | -0.0103 | -0.0243 | -360.1188 | 17.411 | -360.4789 | 17.7806 | -360.8543 | 18.1276 | -360.8912 | 17.528 | -352.666 | 18.7087 | -352.7244 | 16.8012
11:57 | 2212 | 27.7983 | 196.4618 | 438.6025 | 445.0476 | -19.6124 | -46.7199 | 5.5464 | 2.8958 | -3.8086 | -4.4668 | -0.8954 | -3.0137 | 5.6389 | -0.946 | 0.5948 | 0.635 | 0.9568 | 0.7117 | -131.0813 | -5.8882 | 1.8 | -0.2492 | -6.5902 | -5.1403 | 1.3859 |  | -0.6618 | -2.2237 | 4.0151 | 3.362 | 3.3503 | 1.0388 | 10.685 | 14.1469 | 14.7146 | 11.0323 | -0.0001 | -0.0028 | 0.0005 | 0.0035 | 0.0009 | -0.0008 | 0.0003 | -0.0069 | -0.019 | -360.2019 | 17.4377 | -360.4604 | 17.7395 | -360.8204 | 18.1563 | -360.9743 | 17.5835 | -352.789 | 18.721 | -352.706 | 16.7766
11:57 | 2213 | 27.9089 | 196.5013 | 438.7035 | 445.1767 | -19.6778 | -46.7117 | 5.5507 | 2.8432 | -3.7974 | -4.4096 | -0.9058 | -3.0017 | 5.7369 | -0.7739 | 0.5953 | 0.6418 | 0.9551 | 0.7122 | -131.1313 | -5.8933 | 1.7774 | -0.2609 | -6.6264 | -5.2012 | 1.4776 |  | -0.5887 | -2.2959 | 4.0148 | 3.3611 | 3.3505 | 1.0404 | 10.6736 | 14.1118 | 14.6825 | 11.0046 | -0.0005 | -0.003 | 0.0003 | 0.003 | 0.0002 | -0.0004 | 0.0073 | -0.0069 | -0.0106 | -360.1865 | 17.448 | -360.5404 | 17.7642 | -360.8358 | 18.1194 | -360.8481 | 17.5445 | -352.7121 | 18.7333 | -352.7275 | 16.7971
11:57 | 2214 | 27.8716 | 196.5457 | 438.6333 | 445.1645 | -19.5322 | -46.7174 | 5.653 | 2.9083 | -3.7768 | -4.4793 | -0.9276 | -2.9869 | 5.6612 | -0.9426 | 0.5933 | 0.6361 | 0.9551 | 0.7117 | -131.1182 | -5.9038 | 1.825 | -0.205 | -6.5737 | -5.1741 | 1.4571 |  | -0.6011 | -2.2769 | 4.0161 | 3.3595 | 3.3469 | 1.0389 | 10.6607 | 14.1169 | 14.6912 | 11.0598 | -0.0003 | -0.0029 | 0.0008 | 0.0037 | 0.0013 | -0.0006 | 0.0144 | -0.0071 | -0.0005 | -360.125 | 17.4192 | -360.4942 | 17.7785 | -360.8974 | 18.1481 | -360.9097 | 17.5363 | -352.6967 | 18.7271 | -352.7583 | 16.8135
11:57 | 2215 | 27.8571 | 196.5894 | 438.6805 | 445.0346 | -19.5961 | -46.7664 | 5.7105 | 2.872 | -3.8383 | -4.4967 | -0.9805 | -2.9203 | 5.7092 | -0.9091 | 0.5953 | 0.6369 | 0.9575 | 0.7101 | -131.1332 | -5.7934 | 1.8281 | -0.2801 | -6.6057 | -5.1888 | 1.4446 |  | -0.6462 | -2.3368 | 4.0147 | 3.3651 | 3.3493 | 1.0378 | 10.6575 | 14.107 | 14.6944 | 11.0176 | -0.0001 | -0.0033 | 0.0005 | 0.0036 | 0.0008 | -0.0004 | 0.0077 | -0.0248 | 0.0026 | -360.2142 | 17.4213 | -360.5004 | 17.7724 | -360.8327 | 18.1296 | -360.9127 | 17.5547 | -352.749 | 18.7271 | -352.709 | 16.7766
11:57 | 2216 | 27.8523 | 196.5561 | 438.698 | 445.0414 | -19.5911 | -46.6652 | 5.7168 | 2.932 | -3.8317 | -4.4128 | -0.8797 | -2.8512 | 5.7197 | -0.9479 | 0.5948 | 0.636 | 0.9557 | 0.7115 | -131.1202 | -5.8809 | 1.7425 | -0.2629 | -6.5529 | -5.2172 | 1.3876 |  | -0.6261 | -2.2962 | 4.0144 | 3.3586 | 3.3465 | 1.0382 | 10.6538 | 14.1329 | 14.7177 | 11.0302 | -0.0001 | -0.003 | 0.0004 | 0.0037 | 0.0008 | -0.0007 | 0.0121 | -0.0106 | -0.0179 | -360.1496 | 17.45 | -360.5189 | 17.758 | -360.842 | 18.1235 | -360.8881 | 17.5465 | -352.7152 | 18.7518 | -352.7552 | 16.795
11:57 | 2217 | 27.8815 | 196.4487 | 438.6989 | 445.0268 | -19.6203 | -46.7432 | 5.6838 | 2.9783 | -3.7428 | -4.4485 | -0.8961 | -2.8379 | 5.767 | -0.869 | 0.5945 | 0.6389 | 0.9537 | 0.7121 | -131.1225 | -5.8867 | 1.7892 | -0.204 | -6.616 | -5.1743 | 1.3877 |  | -0.6017 | -2.2688 | 4.0147 | 3.3624 | 3.3473 | 1.0382 | 10.678 | 14.14 | 14.7143 | 11.0309 | -0.0004 | -0.0028 | 0.0008 | 0.0044 | 0.0007 | -0.0007 | 0.0076 | 0.0054 | -0.0088 | -360.1527 | 17.4274 | -360.5158 | 17.7601 | -360.8204 | 18.1276 | -360.922 | 17.5527 | -352.6906 | 18.723 | -352.7583 | 16.7909
11:57 | 2218 | 27.8421 | 196.4883 | 438.7319 | 444.9727 | -19.6184 | -46.7841 | 5.6223 | 2.9661 | -3.8192 | -4.4864 | -0.9385 | -2.8861 | 5.7564 | -0.9059 | 0.5931 | 0.6391 | 0.9515 | 0.71 | -131.1132 | -5.8319 | 1.8094 | -0.1063 | -6.5344 | -5.1308 | 1.4207 |  | -0.622 | -2.2907 | 4.0142 | 3.3622 | 3.3488 | 1.0391 | 10.6909 | 14.1409 | 14.7309 | 11.0269 | -0.0007 | -0.0027 | 0.0005 | 0.0038 | 0.0008 | 0.0002 | 0.0118 | 0.0101 | -0.0052 | -360.1773 | 17.4274 | -360.5127 | 17.7601 | -360.8512 | 18.1296 | -360.9035 | 17.5527 | -352.7244 | 18.7456 | -352.7583 | 16.7971
11:57 | 2219 | 27.8429 | 196.3939 | 438.691 | 445.0186 | -19.5845 | -46.7022 | 5.6445 | 2.9981 | -3.7265 | -4.4374 | -0.8999 | -2.9647 | 5.6773 | -0.9756 | 0.5938 | 0.6375 | 0.9544 | 0.7116 | -131.1792 | -5.9369 | 1.7443 | -0.1612 | -6.6396 | -5.0647 | 1.3658 |  | -0.5265 | -2.2397 | 4.0143 | 3.3616 | 3.3473 | 1.0397 | 10.7151 | 14.1307 | 14.7218 | 11.0565 | -0.0001 | -0.003 | 0.0008 | 0.004 | 0.0012 | -0.0004 | 0.0009 | -0.0048 | -0.0122 | -360.1558 | 17.4562 | -360.5466 | 17.7744 | -360.8758 | 18.1296 | -360.9127 | 17.5547 | -352.7306 | 18.7518 | -352.7552 | 16.7889
11:57 | 2220 | 27.816 | 196.3532 | 438.7473 | 445.0089 | -19.5247 | -46.7164 | 5.6768 | 2.9524 | -3.7421 | -4.3516 | -0.9733 | -2.9216 | 5.6212 | -0.9326 | 0.5935 | 0.6366 | 0.9551 | 0.709 | -131.2253 | -5.902 | 1.7164 | -0.1434 | -6.612 | -5.0894 | 1.4145 |  | -0.6031 | -2.3392 | 4.0148 | 3.3643 | 3.3464 | 1.0391 | 10.6944 | 14.179 | 14.7513 | 11.0421 | -0.0002 | -0.0033 | 0.0005 | 0.0032 | 0 | -0.0004 | 0.0098 | -0.0165 | -0.0048 | -360.1681 | 17.3946 | -360.4635 | 17.7436 | -360.8327 | 18.1399 | -360.8943 | 17.5424 | -352.7183 | 18.7128 | -352.6906 | 16.7786
11:57 | 2221 | 27.8863 | 196.4485 | 438.6741 | 445.0394 | -19.5281 | -46.6816 | 5.5834 | 2.8858 | -3.828 | -4.4634 | -0.9213 | -3.0278 | 5.6796 | -0.8665 | 0.5946 | 0.6396 | 0.9593 | 0.7109 | -131.1437 | -5.8581 | 1.7406 | -0.1987 | -6.6649 | -5.1464 | 1.3913 |  | -0.5885 | -2.2985 | 4.0149 | 3.3598 | 3.3502 | 1.04 | 10.6815 | 14.1319 | 14.7116 | 11.0576 | -0.0003 | -0.0026 | 0.001 | 0.0036 | 0.0013 | -0.0004 | 0.0068 | -0.0002 | 0.0046 | -360.165 | 17.4274 | -360.5219 | 17.7826 | -360.8389 | 18.1461 | -360.9497 | 17.5629 | -352.6998 | 18.7415 | -352.7614 | 16.7807
11:57 | 2222 | 27.8299 | 196.3617 | 438.7464 | 445.0027 | -19.5694 | -46.5271 | 5.5587 | 2.8264 | -3.7843 | -4.5124 | -0.9558 | -2.971 | 5.7531 | -0.7833 | 0.5921 | 0.6377 | 0.9537 | 0.7119 | -131.1999 | -5.9253 | 1.8411 | -0.1966 | -6.6482 | -5.049 | 1.3982 |  | -0.6444 | -2.3211 | 4.0141 | 3.3612 | 3.346 | 1.0381 | 10.6839 | 14.1168 | 14.7133 | 11.0197 | -0.0004 | -0.003 | 0.0006 | 0.0038 | 0.0006 | -0.0001 | 0.0054 | -0.0134 | -0.001 | -360.2081 | 17.4418 | -360.4973 | 17.7559 | -360.8297 | 18.1112 | -360.8604 | 17.5342 | -352.7306 | 18.7497 | -352.749 | 16.7889
11:57 | 2223 | 27.9641 | 196.3887 | 438.6014 | 444.9888 | -19.744 | -46.7487 | 5.4216 | 2.8057 | -3.6915 | -4.5421 | -0.8859 | -2.971 | 5.6612 | -0.9138 | 0.5936 | 0.6381 | 0.9544 | 0.7116 | -131.131 | -5.8767 | 1.8021 | -0.2266 | -6.5467 | -5.0898 | 1.464 |  | -0.6201 | -2.3323 | 4.0131 | 3.3577 | 3.3463 | 1.0377 | 10.6942 | 14.1389 | 14.7303 | 11.0645 | -0.0001 | -0.0029 | 0.0008 | 0.0035 | 0.0007 | -0.0009 | 0.0056 | -0.0103 | 0.0054 | -360.1588 | 17.4356 | -360.565 | 17.8032 | -360.9312 | 18.1604 | -360.8789 | 17.5239 | -352.6937 | 18.7353 | -352.789 | 16.8238
11:57 | 2224 | 28.0712 | 196.4437 | 438.7444 | 445.0515 | -19.6934 | -46.8443 | 5.4552 | 2.8828 | -3.7442 | -4.5225 | -0.9134 | -3.0116 | 5.7281 | -0.8694 | 0.5945 | 0.6419 | 0.9573 | 0.7124 | -131.1951 | -5.9568 | 1.8084 | -0.1933 | -6.6222 | -5.182 | 1.4142 |  | -0.6205 | -2.3741 | 4.0137 | 3.3602 | 3.3498 | 1.0381 | 10.6562 | 14.1294 | 14.702 | 11.0327 | 0.0002 | -0.0032 | 0.0003 | 0.004 | 0.0006 | -0.0009 | 0.0059 | -0.0029 | -0.0022 | -360.1465 | 17.411 | -360.4512 | 17.7293 | -360.8297 | 18.1337 | -360.9158 | 17.5547 | -352.7306 | 18.721 | -352.6967 | 16.7683
11:57 | 2225 | 27.9896 | 196.4623 | 438.8609 | 445.099 | -19.6628 | -46.7457 | 5.4029 | 2.9668 | -3.6573 | -4.4558 | -0.88 | -2.936 | 5.6842 | -0.8853 | 0.5947 | 0.6417 | 0.9554 | 0.7111 | -131.2123 | -5.901 | 1.8269 | -0.2311 | -6.5936 | -5.0895 | 1.3755 |  | -0.6306 | -2.2999 | 4.0139 | 3.3595 | 3.3489 | 1.0396 | 10.6781 | 14.1168 | 14.7075 | 11.0197 | -0.0001 | -0.0027 | 0.0009 | 0.0041 | 0.0008 | -0.0007 | 0.0011 | -0.0149 | -0.0148 | -360.245 | 17.4705 | -360.5773 | 17.7724 | -360.8512 | 18.105 | -360.882 | 17.5465 | -352.7552 | 18.7723 | -352.7983 | 16.7889
11:57 | 2226 | 27.9793 | 196.4585 | 438.7408 | 445.0856 | -19.6434 | -46.7011 | 5.5129 | 2.8637 | -3.7485 | -4.5117 | -0.904 | -3.0034 | 5.7493 | -0.8607 | 0.594 | 0.6397 | 0.955 | 0.7116 | -131.1849 | -5.9473 | 1.7512 | -0.1444 | -6.6245 | -5.0615 | 1.4341 |  | -0.6044 | -2.2164 | 4.0146 | 3.3594 | 3.346 | 1.0375 | 10.7092 | 14.16 | 14.7365 | 11.0496 | -0.0003 | -0.0026 | 0.0009 | 0.004 | 0.001 | -0.0005 | 0.0124 | -0.009 | -0.0113 | -360.1865 | 17.4274 | -360.5373 | 17.7826 | -360.885 | 18.1214 | -360.8789 | 17.5301 | -352.706 | 18.7395 | -352.7829 | 16.8197
11:57 | 2227 | 27.8911 | 196.5267 | 438.7821 | 445.1041 | -19.6108 | -46.6914 | 5.5769 | 2.9484 | -3.6636 | -4.4547 | -0.8818 | -2.9365 | 5.7576 | -0.7768 | 0.5942 | 0.6374 | 0.9539 | 0.7108 | -131.1252 | -5.9433 | 1.9138 | -0.0634 | -6.6106 | -5.12 | 1.4418 |  | -0.6365 | -2.2421 | 4.0143 | 3.3624 | 3.3513 | 1.0372 | 10.6584 | 14.155 | 14.7347 | 11.0114 | -0.0001 | -0.0028 | 0.0009 | 0.004 | 0.0003 | -0.0005 | -0.0003 | -0.0107 | -0.0097 | -360.1988 | 17.409 | -360.445 | 17.7334 | -360.8389 | 18.1502 | -360.9281 | 17.5568 | -352.7213 | 18.7148 | -352.6813 | 16.7601
11:57 | 2228 | 27.9995 | 196.5581 | 438.8183 | 445.1702 | -19.7108 | -46.6683 | 5.4323 | 2.9192 | -3.6252 | -4.2845 | -0.9389 | -2.9728 | 5.7822 | -0.8249 | 0.5945 | 0.6381 | 0.9533 | 0.711 | -131.1135 | -5.8943 | 1.9141 | -0.0842 | -6.5965 | -5.2491 | 1.439 |  | -0.6224 | -2.2639 | 4.0164 | 3.3609 | 3.348 | 1.0394 | 10.6861 | 14.154 | 14.7286 | 11.0099 | 0.0002 | -0.0029 | 0.0004 | 0.0037 | 0.0012 | -0.0003 | 0.008 | -0.0113 | -0.0061 | -360.2204 | 17.4521 | -360.5158 | 17.7457 | -360.8204 | 18.1296 | -360.922 | 17.565 | -352.789 | 18.762 | -352.7306 | 16.7745
11:57 | 2229 | 28.1108 | 196.5609 | 438.9244 | 445.1223 | -19.6316 | -46.6752 | 5.4597 | 2.9305 | -3.5639 | -4.3605 | -0.938 | -2.9814 | 5.8585 | -0.7187 | 0.5942 | 0.6354 | 0.959 | 0.7124 | -131.1553 | -5.8397 | 1.7872 | -0.0873 | -6.6106 | -5.1307 | 1.4436 |  | -0.6813 | -2.203 | 4.0154 | 3.3639 | 3.3471 | 1.038 | 10.6688 | 14.1076 | 14.7334 | 11.045 | -0.0001 | -0.0027 | 0.0004 | 0.0035 | 0.0006 | -0.0003 | 0.022 | -0.0114 | -0.012 | -360.1188 | 17.4295 | -360.5127 | 17.7867 | -360.885 | 18.1173 | -360.8789 | 17.5198 | -352.669 | 18.7374 | -352.7583 | 16.8053
11:57 | 2230 | 28.1298 | 196.5933 | 438.9372 | 445.1775 | -19.5748 | -46.5783 | 5.5493 | 2.985 | -3.5022 | -4.341 | -0.9146 | -2.9106 | 5.7747 | -0.7357 | 0.5948 | 0.6374 | 0.9547 | 0.7115 | -131.1815 | -5.8397 | 1.84 | -0.2335 | -6.4971 | -5.0958 | 1.5128 |  | -0.6659 | -2.1301 | 4.0137 | 3.3663 | 3.3499 | 1.0398 | 10.6379 | 14.1103 | 14.6733 | 11.0216 | -0.0006 | -0.0029 | 0.0003 | 0.0034 | 0.0005 | -0.001 | 0.0048 | -0.0166 | -0.0199 | -360.1373 | 17.4131 | -360.4819 | 17.7867 | -360.8727 | 18.1707 | -360.9374 | 17.5588 | -352.7337 | 18.7189 | -352.6998 | 16.8032
11:57 | 2231 | 28.0212 | 196.5482 | 438.7976 | 445.0577 | -19.5528 | -46.7231 | 5.5653 | 2.8923 | -3.4971 | -4.2559 | -0.9441 | -2.9283 | 5.8011 | -0.7253 | 0.5945 | 0.6337 | 0.9537 | 0.7103 | -131.1919 | -5.8386 | 1.9481 | -0.2453 | -6.5471 | -5.1177 | 1.4348 |  | -0.5788 | -2.1676 | 4.0132 | 3.3614 | 3.3479 | 1.0397 | 10.6561 | 14.1064 | 14.6567 | 11.0035 | -0.0001 | -0.0027 | 0.001 | 0.0036 | 0.0006 | 0.0001 | 0.0039 | -0.0008 | -0.0122 | -360.2173 | 17.4397 | -360.5035 | 17.7498 | -360.8112 | 18.1132 | -360.8943 | 17.5568 | -352.7429 | 18.7395 | -352.7244 | 16.7642
11:57 | 2232 | 28.0687 | 196.5055 | 438.8805 | 445.0709 | -19.6517 | -46.7953 | 5.517 | 2.9814 | -3.5611 | -4.3462 | -0.9006 | -2.8847 | 5.864 | -0.7173 | 0.5948 | 0.6366 | 0.9591 | 0.7096 | -131.1431 | -5.828 | 1.9334 | -0.3516 | -6.5382 | -5.0821 | 1.3837 |  | -0.6232 | -2.2429 | 4.0136 | 3.3624 | 3.3488 | 1.0382 | 10.662 | 14.1003 | 14.7299 | 11.0331 | 0.0002 | -0.0031 | 0.0005 | 0.0038 | 0.0007 | -0.0008 | 0.0057 | -0.0121 | -0.0163 | -360.1588 | 17.4603 | -360.5681 | 17.8032 | -360.8635 | 18.1214 | -360.8543 | 17.5198 | -352.7367 | 18.7477 | -352.7983 | 16.8238
11:57 | 2233 | 28.0485 | 196.4954 | 438.9124 | 445.1524 | -19.6148 | -46.8608 | 5.498 | 3.0376 | -3.6242 | -4.4349 | -0.9238 | -2.9244 | 5.8365 | -0.7923 | 0.5939 | 0.638 | 0.955 | 0.7108 | -131.1287 | -5.7932 | 1.9023 | -0.2656 | -6.559 | -5.0804 | 1.4159 |  | -0.6446 | -2.2319 | 4.0142 | 3.3647 | 3.3478 | 1.0372 | 10.6642 | 14.155 | 14.6942 | 11.0461 | 0.0005 | -0.0026 | 0.0009 | 0.0044 | 0.0007 | -0.0005 | 0.0007 | -0.0213 | -0.0064 | -360.1711 | 17.4315 | -360.5035 | 17.7662 | -360.8481 | 18.144 | -360.9281 | 17.5342 | -352.6875 | 18.7353 | -352.7275 | 16.7868
11:57 | 2234 | 28.059 | 196.5121 | 438.9004 | 445.1409 | -19.5643 | -46.6502 | 5.5546 | 3.0387 | -3.657 | -4.2937 | -0.9459 | -2.9356 | 5.7792 | -0.7899 | 0.5952 | 0.6389 | 0.9546 | 0.7118 | -131.2169 | -5.8977 | 1.8273 | -0.186 | -6.5961 | -5.1392 | 1.4005 |  | -0.6153 | -2.254 | 4.0136 | 3.3608 | 3.348 | 1.0379 | 10.6895 | 14.1519 | 14.7454 | 11.0475 | -0.0004 | -0.0028 | 0.0009 | 0.0043 | 0.0008 | -0.0006 | 0.0141 | -0.0104 | 0.0032 | -360.2265 | 17.4439 | -360.4973 | 17.7477 | -360.7958 | 18.1173 | -360.9558 | 17.5753 | -352.7829 | 18.7497 | -352.7552 | 16.7807
11:57 | 2235 | 28.1015 | 196.5759 | 438.899 | 445.0899 | -19.5923 | -46.7068 | 5.4788 | 3.0178 | -3.5917 | -4.3636 | -0.9641 | -2.903 | 5.7696 | -0.7853 | 0.5944 | 0.641 | 0.9544 | 0.7115 | -131.2028 | -5.8782 | 1.8931 | -0.1042 | -6.5266 | -5.0436 | 1.4139 |  | -0.585 | -2.2138 | 4.0142 | 3.3629 | 3.3478 | 1.0361 | 10.7382 | 14.1827 | 14.7912 | 11.0739 | -0.0005 | -0.0028 | 0.0003 | 0.0036 | 0.0002 | -0.0011 | 0.0094 | -0.0003 | 0.0003 | -360.1896 | 17.4356 | -360.5219 | 17.7703 | -360.8543 | 18.1235 | -360.8512 | 17.5383 | -352.7029 | 18.7312 | -352.7306 | 16.7889
11:57 | 2236 | 28.142 | 196.5614 | 438.8432 | 445.047 | -19.611 | -46.7766 | 5.5759 | 2.9676 | -3.5176 | -4.2394 | -1.0049 | -3.0176 | 5.813 | -0.757 | 0.595 | 0.6363 | 0.9557 | 0.7089 | -131.1148 | -5.8586 | 1.9591 | -0.0706 | -6.4474 | -5.0641 | 1.4444 |  | -0.522 | -2.1847 | 4.0143 | 3.3638 | 3.348 | 1.0378 | 10.6988 | 14.1553 | 14.731 | 11.0569 | 0.0002 | -0.0029 | 0.0009 | 0.0039 | 0.0008 | -0.0002 | 0.014 | -0.0078 | -0.009 | -360.1435 | 17.4295 | -360.5035 | 17.7806 | -360.8666 | 18.1625 | -360.9497 | 17.5506 | -352.7029 | 18.7436 | -352.749 | 16.8012
11:57 | 2237 | 28.1631 | 196.5188 | 438.8356 | 445.1626 | -19.6632 | -46.845 | 5.4821 | 2.8892 | -3.4979 | -4.4393 | -0.9851 | -2.986 | 5.8115 | -0.7277 | 0.5958 | 0.6358 | 0.9529 | 0.7106 | -131.1314 | -5.7072 | 2.0188 | -0.1775 | -6.4947 | -5.1058 | 1.3837 |  | -0.5024 | -2.1714 | 4.0137 | 3.3616 | 3.3501 | 1.0379 | 10.6897 | 14.1399 | 14.7364 | 11.0601 | 0.0001 | -0.0033 | 0.0007 | 0.0031 | 0.0007 | -0.0009 | 0.0123 | -0.0003 | -0.0198 | -360.1558 | 17.4274 | -360.5004 | 17.7539 | -360.8297 | 18.1276 | -360.8974 | 17.5445 | -352.6937 | 18.7353 | -352.7275 | 16.7848
11:57 | 2238 | 28.1024 | 196.4908 | 438.8098 | 445.1083 | -19.736 | -46.8625 | 5.4515 | 2.891 | -3.5216 | -4.4589 | -0.9155 | -2.8753 | 5.7713 | -0.7155 | 0.5965 | 0.6404 | 0.9512 | 0.7107 | -131.096 | -5.7856 | 1.918 | -0.1175 | -6.4813 | -5.0424 | 1.4402 |  | -0.533 | -2.0413 | 4.0144 | 3.3627 | 3.3483 | 1.0375 | 10.6632 | 14.1301 | 14.706 | 11.0118 | -0.0006 | -0.0029 | 0.0009 | 0.0038 | 0.0007 | -0.0003 | 0.0101 | -0.012 | -0.0047 | -360.1496 | 17.4418 | -360.5312 | 17.7785 | -360.8635 | 18.1379 | -360.922 | 17.5506 | -352.709 | 18.7456 | -352.749 | 16.8032
11:57 | 2239 | 28.0593 | 196.4891 | 438.8186 | 445.1612 | -19.6424 | -46.8672 | 5.4893 | 2.894 | -3.6216 | -4.5535 | -0.9902 | -2.9012 | 5.8553 | -0.7513 | 0.5938 | 0.6374 | 0.9491 | 0.7093 | -131.1158 | -5.7666 | 1.9909 | -0.1146 | -6.5586 | -5.0897 | 1.3781 |  | -0.5867 | -2.1211 | 4.0141 | 3.3644 | 3.352 | 1.0377 | 10.6504 | 14.1005 | 14.7194 | 11.0501 | -0.0005 | -0.0029 | 0.0009 | 0.0039 | 0.0009 | -0.0011 | 0.0062 | -0.0079 | -0.0137 | -360.1527 | 17.4151 | -360.4942 | 17.758 | -360.8297 | 18.1071 | -360.9004 | 17.5445 | -352.6844 | 18.7169 | -352.746 | 16.7827
11:57 | 2240 | 28.1049 | 196.5519 | 438.8587 | 445.154 | -19.689 | -46.8641 | 5.4439 | 2.8727 | -3.6295 | -4.538 | -0.9424 | -2.9312 | 5.8917 | -0.6429 | 0.5942 | 0.6386 | 0.9554 | 0.7094 | -131.0585 | -5.8709 | 1.9649 | -0.1568 | -6.5617 | -5.0756 | 1.4807 |  | -0.5312 | -2.1567 | 4.0125 | 3.3622 | 3.3442 | 1.0369 | 10.6955 | 14.1224 | 14.7122 | 11.0259 | 0 | -0.003 | 0.0006 | 0.004 | 0.0004 | -0.0005 | -0.0015 | -0.0059 | -0.0148 | -360.2235 | 17.45 | -360.5373 | 17.7765 | -360.8697 | 18.1153 | -360.9035 | 17.5609 | -352.786 | 18.762 | -352.746 | 16.8053
11:57 | 2241 | 28.1467 | 196.5179 | 438.859 | 445.1343 | -19.6876 | -46.7345 | 5.5175 | 2.9159 | -3.5194 | -4.3747 | -1.0072 | -2.9817 | 5.8508 | -0.6592 | 0.5928 | 0.6374 | 0.9536 | 0.7097 | -131.0554 | -5.8042 | 1.9832 | -0.1601 | -6.4295 | -5.1038 | 1.5562 |  | -0.5022 | -2.0798 | 4.0141 | 3.3629 | 3.3526 | 1.0385 | 10.6919 | 14.1424 | 14.7576 | 11.0504 | 0.0001 | -0.0034 | 0.0008 | 0.0043 | 0.0012 | -0.0007 | 0.0082 | -0.0231 | -0.019 | -360.1835 | 17.4439 | -360.5004 | 17.7539 | -360.8174 | 18.0947 | -360.8789 | 17.5178 | -352.6721 | 18.7415 | -352.7337 | 16.795
11:57 | 2242 | 28.0845 | 196.5857 | 438.8893 | 445.1381 | -19.6334 | -46.7091 | 5.5936 | 2.9159 | -3.608 | -4.5039 | -0.9403 | -2.86 | 5.9102 | -0.651 | 0.5938 | 0.6389 | 0.9523 | 0.7107 | -131.0884 | -5.8233 | 1.9776 | -0.3216 | -6.4492 | -5.1253 | 1.5229 |  | -0.4976 | -2.1013 | 4.0146 | 3.3631 | 3.3519 | 1.0374 | 10.7161 | 14.1553 | 14.7368 | 11.0511 | -0.0002 | -0.0029 | 0.001 | 0.0041 | 0.0007 | -0.0002 | 0.008 | -0.005 | -0.0138 | -360.1742 | 17.4315 | -360.5096 | 17.7785 | -360.8758 | 18.1194 | -360.9097 | 17.5506 | -352.7306 | 18.7333 | -352.7306 | 16.8115
11:57 | 2243 | 28.1182 | 196.5674 | 438.8558 | 445.0464 | -19.5156 | -46.5936 | 5.6079 | 2.9608 | -3.6607 | -4.4978 | -0.9254 | -2.8735 | 5.944 | -0.6294 | 0.5927 | 0.6344 | 0.9545 | 0.7102 | -131.1122 | -5.866 | 1.9718 | -0.3645 | -6.4909 | -5.0456 | 1.4788 |  | -0.5609 | -2.1753 | 4.0164 | 3.3629 | 3.3476 | 1.0388 | 10.7162 | 14.1841 | 14.7184 | 11.063 | -0.0003 | -0.0026 | 0.0006 | 0.0039 | 0.0007 | -0.0002 | 0.0056 | -0.0213 | -0.0054 | -360.2019 | 17.4295 | -360.4758 | 17.7252 | -360.7989 | 18.1009 | -360.8974 | 17.5609 | -352.7029 | 18.7148 | -352.709 | 16.7724
11:57 | 2244 | 28.0276 | 196.5392 | 438.7745 | 445.0693 | -19.5268 | -46.7406 | 5.6052 | 2.9641 | -3.5946 | -4.4868 | -0.9457 | -2.9583 | 5.7856 | -0.6627 | 0.5935 | 0.6323 | 0.9553 | 0.7107 | -131.1262 | -5.907 | 1.9193 | -0.2968 | -6.3993 | -5.0522 | 1.4969 |  | -0.6261 | -2.1383 | 4.0151 | 3.3608 | 3.3469 | 1.0385 | 10.7172 | 14.174 | 14.7451 | 11.0749 | -0.0003 | -0.0032 | 0.0008 | 0.0035 | 0.0007 | -0.0007 | 0.0087 | 0.0097 | -0.0073 | -360.2665 | 17.4705 | -360.5158 | 17.7559 | -360.8697 | 18.0968 | -360.8974 | 17.5691 | -352.789 | 18.7703 | -352.7275 | 16.7827
11:57 | 2245 | 28.1217 | 196.6478 | 438.9104 | 445.1619 | -19.5107 | -46.7012 | 5.6715 | 2.9659 | -3.635 | -4.4931 | -0.9794 | -2.99 | 5.7908 | -0.8414 | 0.5943 | 0.6336 | 0.9505 | 0.711 | -131.1887 | -5.8987 | 1.8368 | -0.211 | -6.4469 | -4.9869 | 1.4749 |  | -0.6318 | -2.1136 | 4.0142 | 3.364 | 3.3498 | 1.0393 | 10.6931 | 14.1666 | 14.7637 | 11.0345 | 0.0001 | -0.0029 | 0.0007 | 0.0035 | 0.0002 | -0.0005 | 0.0204 | -0.0188 | 0.0136 | -360.1188 | 17.4172 | -360.5343 | 17.7518 | -360.842 | 18.1132 | -360.8881 | 17.5116 | -352.6937 | 18.7251 | -352.7306 | 16.8094
11:57 | 2246 | 28.1135 | 196.6292 | 438.8605 | 445.1507 | -19.5584 | -46.6955 | 5.6038 | 2.9619 | -3.6086 | -4.4632 | -0.9512 | -2.9753 | 5.7509 | -0.8345 | 0.5942 | 0.6348 | 0.9543 | 0.7106 | -131.1174 | -5.8861 | 1.865 | -0.2584 | -6.4601 | -5.0561 | 1.4206 |  | -0.5698 | -2.1791 | 4.0159 | 3.3608 | 3.3473 | 1.0379 | 10.7094 | 14.1536 | 14.7139 | 11.0342 | -0.0002 | -0.0032 | 0.0006 | 0.0038 | 0.0008 | -0.0009 | 0.0146 | -0.0158 | 0.0026 | -360.1988 | 17.4172 | -360.4512 | 17.7477 | -360.845 | 18.1214 | -360.9558 | 17.5814 | -352.7306 | 18.7292 | -352.709 | 16.7766
11:57 | 2247 | 28.1054 | 196.5874 | 438.8657 | 445.0852 | -19.5464 | -46.6388 | 5.7061 | 2.9493 | -3.5559 | -4.4444 | -0.9537 | -2.9694 | 5.7724 | -0.8468 | 0.595 | 0.6365 | 0.9529 | 0.7106 | -131.1355 | -5.9668 | 1.84 | -0.2783 | -6.4142 | -5.0803 | 1.4901 |  | -0.5249 | -2.1933 | 4.015 | 3.3628 | 3.3481 | 1.0384 | 10.6977 | 14.1538 | 14.716 | 11.0508 | -0.0003 | -0.0026 | 0.0009 | 0.0039 | 0.0004 | -0.001 | 0.0073 | -0.0156 | -0.0117 | -360.2327 | 17.4521 | -360.5373 | 17.7559 | -360.8266 | 18.0763 | -360.8727 | 17.5527 | -352.7367 | 18.7579 | -352.7429 | 16.7991
11:57 | 2248 | 28.148 | 196.5281 | 438.8844 | 445.0756 | -19.5736 | -46.6008 | 5.7654 | 2.9174 | -3.4831 | -4.4677 | -0.9767 | -2.8934 | 5.8072 | -0.8106 | 0.5939 | 0.6339 | 0.9526 | 0.7116 | -131.0821 | -5.9634 | 1.8784 | -0.2716 | -6.3729 | -5.053 | 1.427 |  | -0.5611 | -2.2448 | 4.015 | 3.3617 | 3.3477 | 1.0385 | 10.7276 | 14.1614 | 14.71 | 11.0561 | 0.0003 | -0.0023 | 0.0005 | 0.0041 | 0.0011 | -0.0004 | 0.0217 | -0.0191 | 0.0064 | -360.1742 | 17.4397 | -360.5373 | 17.7991 | -360.922 | 18.1153 | -360.8727 | 17.5342 | -352.6998 | 18.7374 | -352.7583 | 16.8217
11:57 | 2249 | 28.2273 | 196.4788 | 438.8065 | 445.1082 | -19.5617 | -46.4615 | 5.6235 | 2.9402 | -3.4823 | -4.4671 | -0.9818 | -2.9315 | 5.8349 | -0.7794 | 0.5937 | 0.6326 | 0.9543 | 0.7099 | -131.0608 | -5.936 | 1.9565 | -0.222 | -6.3961 | -5.0681 | 1.4789 |  | -0.5375 | -2.2422 | 4.0149 | 3.3616 | 3.3467 | 1.0392 | 10.6562 | 14.1178 | 14.6788 | 11.0154 | 0.0001 | -0.003 | 0.0009 | 0.0045 | 0.0006 | -0.0005 | 0.008 | -0.0039 | 0.0037 | -360.1619 | 17.4192 | -360.4789 | 17.7498 | -360.8358 | 18.1153 | -360.9035 | 17.5629 | -352.7306 | 18.7271 | -352.6937 | 16.8012
11:57 | 2250 | 28.1847 | 196.5682 | 438.8654 | 445.1032 | -19.5062 | -46.3863 | 5.6778 | 3.0545 | -3.475 | -4.4407 | -0.9106 | -2.9869 | 5.8041 | -0.7769 | 0.5938 | 0.6348 | 0.9539 | 0.7119 | -131.0118 | -5.8261 | 1.9747 | -0.2003 | -6.4641 | -5.0664 | 1.4431 |  | -0.5166 | -2.1797 | 4.015 | 3.3636 | 3.3475 | 1.0386 | 10.6711 | 14.1273 | 14.7245 | 10.9836 | 0.0004 | -0.0027 | 0.001 | 0.004 | 0.0008 | -0.0008 | 0.0173 | -0.0041 | 0.0056 | -360.2296 | 17.4603 | -360.5404 | 17.7354 | -360.8081 | 18.0742 | -360.885 | 17.5691 | -352.7552 | 18.7641 | -352.7737 | 16.7848
11:57 | 2251 | 28.1862 | 196.6188 | 438.9049 | 445.1393 | -19.5521 | -46.3563 | 5.6179 | 2.9834 | -3.5412 | -4.457 | -0.938 | -2.9949 | 5.8128 | -0.7989 | 0.5952 | 0.6377 | 0.9543 | 0.7125 | -130.9807 | -5.7342 | 1.9748 | -0.1757 | -6.5117 | -5.0533 | 1.512 |  | -0.5472 | -2.1147 | 4.0146 | 3.3641 | 3.3476 | 1.0399 | 10.7243 | 14.1343 | 14.749 | 11.0482 | -0.0002 | -0.0028 | 0.0002 | 0.0034 | 0.0007 | -0.0002 | 0.0222 | -0.015 | 0.0109 | -360.1865 | 17.4521 | -360.5589 | 17.7806 | -360.8974 | 18.0906 | -360.8481 | 17.5568 | -352.6967 | 18.7436 | -352.7983 | 16.8217
11:57 | 2252 | 28.2213 | 196.5694 | 438.7964 | 445.1 | -19.5623 | -46.3905 | 5.6804 | 2.9738 | -3.5164 | -4.4878 | -0.9569 | -3.0008 | 5.8068 | -0.7559 | 0.5937 | 0.636 | 0.9498 | 0.711 | -131.0473 | -5.799 | 1.9646 | -0.228 | -6.5182 | -5.1104 | 1.4958 |  | -0.511 | -2.1288 | 4.0138 | 3.3648 | 3.3448 | 1.037 | 10.6943 | 14.1445 | 14.7524 | 11.036 | -0.0001 | -0.0023 | 0.0007 | 0.0038 | 0.0007 | -0.0006 | 0.0153 | -0.0188 | 0.0158 | -360.1896 | 17.4151 | -360.4696 | 17.7662 | -360.8327 | 18.1214 | -360.9189 | 17.5609 | -352.6998 | 18.7087 | -352.6721 | 16.7848
11:57 | 2253 | 28.1483 | 196.5423 | 438.8248 | 445.0235 | -19.5563 | -46.3768 | 5.7371 | 2.862 | -3.4911 | -4.531 | -0.9187 | -2.9311 | 5.7896 | -0.8317 | 0.5938 | 0.6324 | 0.954 | 0.7095 | -130.9864 | -5.7527 | 2.0292 | -0.0951 | -6.6475 | -5.1712 | 1.4982 |  | -0.5136 | -2.1445 | 4.0146 | 3.3632 | 3.3485 | 1.0381 | 10.6735 | 14.1409 | 14.6904 | 10.9981 | 0 | -0.0031 | 0.0011 | 0.0037 | 0.0008 | -0.0003 | 0.0069 | -0.0135 | 0.0031 | -360.2635 | 17.4459 | -360.4881 | 17.7293 | -360.7927 | 18.0988 | -360.9527 | 17.5978 | -352.7798 | 18.7312 | -352.7213 | 16.7724
11:57 | 2254 | 28.1459 | 196.6464 | 438.904 | 445.0735 | -19.5821 | -46.3272 | 5.8006 | 2.9221 | -3.621 | -4.5268 | -0.9591 | -2.9087 | 5.9231 | -0.7727 | 0.5962 | 0.6391 | 0.9559 | 0.7096 | -130.9663 | -5.632 | 1.9364 | -0.1501 | -6.5827 | -5.1284 | 1.5148 |  | -0.5189 | -2.0855 | 4.015 | 3.3636 | 3.3476 | 1.038 | 10.7106 | 14.1374 | 14.7095 | 10.989 | 0.0002 | -0.0028 | 0.0009 | 0.0037 | 0.0005 | -0.0004 | 0.016 | 0.0035 | 0.0076 | -360.1742 | 17.4541 | -360.5312 | 17.7559 | -360.8697 | 18.0824 | -360.8574 | 17.5404 | -352.7121 | 18.7333 | -352.7767 | 16.7848
11:57 | 2255 | 28.1519 | 196.6625 | 438.8979 | 445.1468 | -19.5632 | -46.3523 | 5.8351 | 2.9668 | -3.5516 | -4.4041 | -0.9393 | -3.0037 | 5.8616 | -0.7646 | 0.5946 | 0.6357 | 0.95 | 0.7108 | -130.9722 | -5.7179 | 2.0817 | -0.2835 | -6.4172 | -5.1016 | 1.5207 |  | -0.5379 | -2.2168 | 4.0156 | 3.363 | 3.3451 | 1.0391 | 10.6759 | 14.143 | 14.6968 | 11.0068 | -0.0004 | -0.003 | 0.0011 | 0.004 | 0.0008 | -0.0008 | -0.001 | 0.0015 | -0.0176 | -360.0973 | 17.4028 | -360.4881 | 17.7744 | -360.8912 | 18.1337 | -360.9158 | 17.5506 | -352.6937 | 18.6943 | -352.7398 | 16.8156
11:57 | 2256 | 28.2094 | 196.5866 | 438.9436 | 445.1022 | -19.5467 | -46.4 | 5.5927 | 2.882 | -3.5359 | -4.3509 | -0.9079 | -2.9591 | 5.867 | -0.713 | 0.5942 | 0.6387 | 0.9529 | 0.7105 | -130.992 | -5.7083 | 2.0232 | -0.3475 | -6.5325 | -5.1438 | 1.4206 |  | -0.5184 | -2.1266 | 4.0159 | 3.3631 | 3.348 | 1.0388 | 10.7173 | 14.1621 | 14.7719 | 11.0641 | -0.0003 | -0.0029 | 0.0006 | 0.0037 | 0.0008 | -0.0003 | 0.008 | -0.019 | -0.0058 | -360.1465 | 17.4192 | -360.4696 | 17.7518 | -360.8512 | 18.1132 | -360.9281 | 17.5712 | -352.7337 | 18.7045 | -352.6875 | 16.7827
11:57 | 2257 | 28.2336 | 196.6673 | 439.0578 | 445.2069 | -19.5775 | -46.3798 | 5.685 | 2.9712 | -3.5202 | -4.4967 | -0.9121 | -2.9654 | 5.8996 | -0.6815 | 0.5935 | 0.6381 | 0.9524 | 0.7107 | -131.0253 | -5.7261 | 1.9906 | -0.3317 | -6.5267 | -5.1739 | 1.4613 |  | -0.507 | -2.1461 | 4.0144 | 3.3601 | 3.3487 | 1.0384 | 10.7012 | 14.169 | 14.7317 | 11.0309 | -0.0001 | -0.0029 | 0.0005 | 0.0038 | 0.0012 | -0.0009 | 0.0069 | -0.0182 | 0.0128 | -360.2235 | 17.4664 | -360.5589 | 17.758 | -360.8297 | 18.0804 | -360.885 | 17.5691 | -352.7367 | 18.762 | -352.7614 | 16.7971
11:57 | 2258 | 28.2932 | 196.6153 | 439.0655 | 445.1988 | -19.5589 | -46.376 | 5.7633 | 3.0446 | -3.3939 | -4.4258 | -0.9654 | -2.9366 | 5.8993 | -0.6688 | 0.5937 | 0.6386 | 0.9529 | 0.7105 | -131.1028 | -5.7793 | 1.8846 | -0.354 | -6.5704 | -5.2274 | 1.4577 |  | -0.5387 | -2.1705 | 4.0145 | 3.3598 | 3.3511 | 1.0373 | 10.6851 | 14.1409 | 14.7194 | 11.0096 | 0.0001 | -0.0032 | 0.0005 | 0.0035 | 0.0004 | -0.0008 | 0.0085 | -0.002 | -0.0082 | -360.1527 | 17.4541 | -360.5712 | 17.7765 | -360.9035 | 18.0947 | -360.8512 | 17.5404 | -352.7183 | 18.7292 | -352.7737 | 16.8217
11:57 | 2259 | 28.3125 | 196.6033 | 439.0761 | 445.1613 | -19.5771 | -46.3886 | 5.7216 | 2.9857 | -3.526 | -4.4274 | -0.9516 | -2.9531 | 5.9403 | -0.7264 | 0.5939 | 0.6391 | 0.9516 | 0.7116 | -131.1498 | -5.7911 | 1.9754 | -0.2999 | -6.5648 | -5.1427 | 1.4957 |  | -0.6171 | -2.2263 | 4.014 | 3.3643 | 3.3526 | 1.0391 | 10.7197 | 14.147 | 14.7446 | 11.0666 | -0.0001 | -0.0031 | 0.0003 | 0.0035 | 0.001 | -0.0005 | 0.0084 | -0.0055 | -0.0081 | -360.1373 | 17.411 | -360.4696 | 17.7457 | -360.8635 | 18.1214 | -360.9312 | 17.565 | -352.7306 | 18.7066 | -352.7029 | 16.7991
11:57 | 2260 | 28.289 | 196.6376 | 439.1209 | 445.2618 | -19.5584 | -46.5107 | 5.7952 | 3.0196 | -3.4184 | -4.421 | -0.9643 | -2.9494 | 5.9551 | -0.6823 | 0.5945 | 0.6395 | 0.9552 | 0.7128 | -131.1019 | -5.7567 | 2.0417 | -0.3107 | -6.5082 | -5.1155 | 1.5477 |  | -0.6016 | -2.1956 | 4.0159 | 3.3595 | 3.3496 | 1.0376 | 10.6887 | 14.1325 | 14.7029 | 11.0371 | -0.0007 | -0.0028 | 0.0003 | 0.0032 | -0.0002 | -0.0009 | -0.0071 | -0.0262 | -0.031 | -360.2604 | 17.4562 | -360.4881 | 17.7169 | -360.802 | 18.0886 | -360.9374 | 17.602 | -352.7798 | 18.7353 | -352.7152 | 16.7745
11:57 | 2261 | 28.2866 | 196.703 | 439.1268 | 445.2172 | -19.4218 | -46.4123 | 5.8186 | 2.9764 | -3.4729 | -4.5174 | -0.9603 | -2.9658 | 5.9962 | -0.839 | 0.5917 | 0.6348 | 0.9499 | 0.7123 | -131.1607 | -5.8378 | 2.0074 | -0.2271 | -6.4704 | -5.1536 | 1.5763 |  | -0.5243 | -2.1307 | 4.0138 | 3.3601 | 3.35 | 1.037 | 10.7058 | 14.1621 | 14.7487 | 11.0583 | -0.0002 | -0.0029 | 0.0015 | 0.0037 | 0.0008 | -0.0008 | 0.0064 | -0.0117 | -0.0222 | -360.1773 | 17.4397 | -360.5127 | 17.7375 | -360.8481 | 18.0845 | -360.8604 | 17.5527 | -352.7244 | 18.7251 | -352.746 | 16.795
11:57 | 2262 | 28.2354 | 196.5252 | 439.0916 | 445.2067 | -19.4647 | -46.407 | 5.7437 | 3.0441 | -3.4117 | -4.3537 | -0.8431 | -2.9089 | 5.9221 | -0.7023 | 0.5926 | 0.6369 | 0.9528 | 0.7121 | -131.1489 | -5.8812 | 1.9631 | -0.2727 | -6.3768 | -5.1595 | 1.6011 |  | -0.5779 | -2.1187 | 4.0151 | 3.3593 | 3.3472 | 1.0379 | 10.6781 | 14.134 | 14.7122 | 11.0085 | -0.0003 | -0.0032 | 0.0005 | 0.0036 | 0.0008 | -0.0003 | 0.0129 | 0.0047 | 0.0026 | -360.1435 | 17.409 | -360.5035 | 17.758 | -360.8758 | 18.1379 | -360.9466 | 17.5527 | -352.6967 | 18.7004 | -352.7183 | 16.8115
11:57 | 2263 | 28.2767 | 196.6262 | 438.9418 | 445.2901 | -19.4197 | -46.4821 | 5.7464 | 3.0598 | -3.4835 | -4.3478 | -0.8014 | -2.9024 | 6.0879 | -0.6397 | 0.5935 | 0.6342 | 0.9509 | 0.7104 | -131.0888 | -5.8885 | 1.9109 | -0.1807 | -6.4466 | -5.168 | 1.558 |  | -0.588 | -2.0688 | 4.0147 | 3.362 | 3.3521 | 1.0375 | 10.6701 | 14.1315 | 14.7026 | 11.0299 | -0.0006 | -0.0034 | 0.0006 | 0.0036 | 0.0007 | -0.0003 | 0.0055 | -0.0125 | -0.0222 | -360.1527 | 17.3966 | -360.4727 | 17.7272 | -360.8143 | 18.1153 | -360.9343 | 17.5671 | -352.7306 | 18.6943 | -352.6967 | 16.795
11:57 | 2264 | 28.2528 | 196.6311 | 439.1061 | 445.2756 | -19.3682 | -46.5143 | 5.7464 | 3.0907 | -3.4313 | -4.4576 | -0.8569 | -2.9564 | 5.8649 | -0.7271 | 0.5928 | 0.6311 | 0.9495 | 0.7108 | -131.0792 | -5.8848 | 1.9593 | -0.1522 | -6.4695 | -5.1215 | 1.5222 |  | -0.6189 | -2.0511 | 4.0141 | 3.3606 | 3.3482 | 1.0374 | 10.6861 | 14.1829 | 14.7228 | 11.0446 | -0.0004 | -0.0028 | 0.0005 | 0.0039 | 0.001 | -0.0003 | 0.0063 | -0.0044 | -0.0158 | -360.2111 | 17.4623 | -360.5589 | 17.7518 | -360.8266 | 18.0906 | -360.8943 | 17.5588 | -352.7706 | 18.7497 | -352.7583 | 16.8115
11:57 | 2265 | 28.2954 | 196.6985 | 439.2496 | 445.3887 | -19.4101 | -46.4968 | 5.6262 | 3.1508 | -3.4229 | -4.3829 | -0.859 | -2.8496 | 6.007 | -0.6412 | 0.593 | 0.6334 | 0.9493 | 0.7098 | -131.0628 | -5.8225 | 1.9728 | -0.1975 | -6.422 | -5.088 | 1.5314 |  | -0.5226 | -2.0825 | 4.0146 | 3.3605 | 3.3477 | 1.0376 | 10.6769 | 14.1503 | 14.7582 | 11.0591 | -0.0005 | -0.0031 | 0.0001 | 0.0033 | 0.0004 | -0.0006 | -0.0009 | -0.0088 | 0.0026 | -360.125 | 17.4356 | -360.5096 | 17.7621 | -360.8943 | 18.0968 | -360.8574 | 17.528 | -352.6967 | 18.7169 | -352.7798 | 16.832
11:57 | 2266 | 28.3452 | 196.6862 | 439.3852 | 445.523 | -19.3542 | -46.4068 | 5.741 | 3.0647 | -3.431 | -4.4716 | -0.8918 | -2.8829 | 6.0132 | -0.5586 | 0.5942 | 0.6366 | 0.9528 | 0.7103 | -131.0173 | -5.8768 | 2.0219 | -0.2331 | -6.4812 | -5.1847 | 1.5393 |  | -0.4917 | -1.9181 | 4.0156 | 3.3617 | 3.3504 | 1.0376 | 10.6862 | 14.1479 | 14.7265 | 11.0338 | 0 | -0.003 | 0.0006 | 0.0039 | 0.0007 | -0.0007 | -0.001 | -0.0121 | 0.0044 | -360.1896 | 17.4213 | -360.5096 | 17.7539 | -360.8481 | 18.1214 | -360.9466 | 17.5794 | -352.7275 | 18.7148 | -352.709 | 16.8053
11:57 | 2267 | 28.3359 | 196.7237 | 439.3531 | 445.5368 | -19.3941 | -46.5046 | 5.7619 | 3.0004 | -3.4762 | -4.4603 | -0.9587 | -2.959 | 5.9636 | -0.682 | 0.5949 | 0.6388 | 0.9504 | 0.7097 | -131.0887 | -5.8629 | 2.0185 | -0.2349 | -6.5031 | -5.1518 | 1.5349 |  | -0.5081 | -1.927 | 4.0148 | 3.359 | 3.3486 | 1.038 | 10.6803 | 14.1426 | 14.7239 | 11.05 | 0.0003 | -0.0031 | 0.0003 | 0.0035 | 0.0007 | -0.0001 | 0.0195 | 0.0005 | 0.0042 | -360.2111 | 17.4377 | -360.4881 | 17.7067 | -360.7927 | 18.0721 | -360.9035 | 17.5814 | -352.749 | 18.7251 | -352.7121 | 16.7745
11:58 | 2268 | 28.3098 | 196.6895 | 439.3534 | 445.46 | -19.3162 | -46.4664 | 5.8146 | 3.0898 | -3.4639 | -4.4556 | -0.8097 | -2.9 | 5.8992 | -0.6277 | 0.5937 | 0.64 | 0.9513 | 0.71 | -131.1023 | -5.7566 | 2.0089 | -0.2056 | -6.4899 | -5.1998 | 1.5355 |  | -0.5092 | -1.8918 | 4.0143 | 3.3621 | 3.3517 | 1.0373 | 10.6828 | 14.1327 | 14.7329 | 11.0367 | -0.0005 | -0.0028 | 0.0006 | 0.0035 | 0.0009 | -0.0006 | -0.0054 | -0.0209 | -0.0193 | -360.1958 | 17.4562 | -360.5219 | 17.7662 | -360.8574 | 18.0886 | -360.8789 | 17.5753 | -352.7521 | 18.7518 | -352.789 | 16.8156
11:58 | 2269 | 28.2618 | 196.6132 | 439.3793 | 445.4302 | -19.3721 | -46.5151 | 5.7389 | 3.0139 | -3.4683 | -4.4411 | -0.9757 | -2.9548 | 5.9478 | -0.6778 | 0.5923 | 0.6362 | 0.9531 | 0.7109 | -131.0273 | -5.8353 | 2.0943 | -0.1473 | -6.4314 | -5.076 | 1.5624 |  | -0.5388 | -1.9597 | 4.014 | 3.3624 | 3.3488 | 1.0387 | 10.7137 | 14.1763 | 14.7478 | 11.025 | -0.0004 | -0.0023 | 0.0013 | 0.0045 | 0.0007 | 0 | 0.0177 | -0.0019 | -0.0093 | -360.0942 | 17.3946 | -360.4542 | 17.7498 | -360.8543 | 18.1194 | -360.9251 | 17.5321 | -352.6937 | 18.7004 | -352.6752 | 16.7971
11:58 | 2270 | 28.3979 | 196.691 | 439.4519 | 445.5142 | -19.4701 | -46.6111 | 5.7208 | 2.9883 | -3.5053 | -4.4665 | -0.8966 | -2.9131 | 5.9416 | -0.5961 | 0.594 | 0.6335 | 0.9528 | 0.7107 | -131.0284 | -5.8267 | 2.021 | -0.0561 | -6.4764 | -5.1279 | 1.5528 |  | -0.5551 | -2.0526 | 4.0135 | 3.3604 | 3.3459 | 1.0372 | 10.7081 | 14.1644 | 14.733 | 11.0551 | 0 | -0.003 | 0.001 | 0.0036 | 0.0008 | -0.001 | 0.0053 | -0.0035 | -0.0236 | -360.1958 | 17.4233 | -360.4819 | 17.7395 | -360.8512 | 18.1255 | -360.9651 | 17.5855 | -352.749 | 18.7189 | -352.7337 | 16.793
11:58 | 2271 | 28.3491 | 196.6956 | 439.3683 | 445.5379 | -19.3917 | -46.533 | 5.6866 | 2.926 | -3.4459 | -4.3445 | -0.9268 | -2.9288 | 5.9681 | -0.5665 | 0.5942 | 0.6374 | 0.9534 | 0.7108 | -131.0596 | -5.873 | 1.9474 | -0.0108 | -6.3841 | -5.068 | 1.5163 |  | -0.4865 | -2.1606 | 4.0142 | 3.3645 | 3.3493 | 1.0374 | 10.6977 | 14.1076 | 14.7218 | 11.0161 | 0.0001 | -0.0029 | 0.0006 | 0.0035 | 0.0006 | -0.0004 | 0.0143 | 0 | -0.0093 | -360.1835 | 17.4439 | -360.5343 | 17.7395 | -360.8204 | 18.0804 | -360.8604 | 17.5547 | -352.7244 | 18.7395 | -352.7398 | 16.7827
11:58 | 2272 | 28.3286 | 196.6708 | 439.5396 | 445.552 | -19.376 | -46.411 | 5.693 | 2.9538 | -3.4334 | -4.4534 | -0.9143 | -2.947 | 6.044 | -0.6472 | 0.5953 | 0.6416 | 0.9524 | 0.7124 | -131.1391 | -5.8301 | 1.9754 | -0.0072 | -6.3794 | -5.0227 | 1.6207 |  | -0.4723 | -2.2231 | 4.0146 | 3.3612 | 3.3519 | 1.0384 | 10.6815 | 14.1262 | 14.7184 | 11.0283 | 0.0001 | -0.0029 | 0.0006 | 0.0035 | 0.0009 | -0.0007 | 0.0043 | 0.006 | -0.0025 | -360.1619 | 17.4418 | -360.5527 | 17.7847 | -360.8974 | 18.0947 | -360.8635 | 17.5301 | -352.706 | 18.7251 | -352.789 | 16.832
11:58 | 2273 | 28.3533 | 196.7182 | 439.581 | 445.5632 | -19.3951 | -46.4171 | 5.7096 | 2.9672 | -3.439 | -4.2913 | -0.8539 | -2.9691 | 6.047 | -0.6395 | 0.594 | 0.6381 | 0.9512 | 0.7119 | -131.1642 | -5.9182 | 2.0817 | -0.0023 | -6.3438 | -4.9894 | 1.6264 |  | -0.4721 | -2.3054 | 4.0128 | 3.3594 | 3.3488 | 1.0377 | 10.6898 | 14.1395 | 14.7275 | 11.0382 | -0.0007 | -0.0029 | 0 | 0.0034 | 0.0007 | -0.0009 | -0.0037 | -0.0087 | -0.0278 | -360.1773 | 17.4315 | -360.4881 | 17.7436 | -360.8697 | 18.1214 | -360.8943 | 17.5588 | -352.706 | 18.7107 | -352.7244 | 16.8032
11:58 | 2274 | 28.4502 | 196.7412 | 439.5962 | 445.5975 | -19.3558 | -46.4059 | 5.7035 | 2.9699 | -3.4063 | -4.3648 | -0.8309 | -2.9976 | 6.0628 | -0.6596 | 0.5938 | 0.6345 | 0.9538 | 0.7113 | -131.1153 | -5.8026 | 2.1208 | 0.0108 | -6.3795 | -5.0078 | 1.683 |  | -0.4979 | -2.2797 | 4.0134 | 3.3653 | 3.3493 | 1.0391 | 10.6757 | 14.1261 | 14.7116 | 10.9941 | -0.0001 | -0.0025 | 0.0009 | 0.004 | 0.0009 | -0.0003 | 0.0095 | -0.0144 | -0.0208 | -360.205 | 17.4356 | -360.4942 | 17.7108 | -360.7866 | 18.0742 | -360.8943 | 17.5794 | -352.7337 | 18.7271 | -352.7337 | 16.7766
11:58 | 2275 | 28.401 | 196.6674 | 439.5568 | 445.5074 | -19.4375 | -46.5314 | 5.6727 | 3.027 | -3.4513 | -4.3396 | -0.8016 | -2.9034 | 6.0757 | -0.5604 | 0.5956 | 0.6369 | 0.9535 | 0.7125 | -131.0544 | -5.779 | 2.1442 | -0.0302 | -6.3792 | -5.0671 | 1.6822 |  | -0.5641 | -2.2457 | 4.0139 | 3.3659 | 3.3491 | 1.0373 | 10.67 | 14.1433 | 14.6932 | 11.0176 | 0.0001 | -0.0032 | 0.0006 | 0.0039 | 0.0011 | -0.0007 | 0.0109 | -0.01 | -0.01 | -360.2604 | 17.4603 | -360.5281 | 17.7436 | -360.8204 | 18.0927 | -360.9189 | 17.5732 | -352.7614 | 18.7559 | -352.7644 | 16.795
11:58 | 2276 | 28.3738 | 196.6088 | 439.4265 | 445.469 | -19.4413 | -46.4341 | 5.758 | 2.9948 | -3.5345 | -4.3691 | -0.8656 | -2.9533 | 6.0173 | -0.5507 | 0.5953 | 0.6371 | 0.9544 | 0.7111 | -131.0541 | -5.753 | 2.0978 | -0.135 | -6.352 | -5.0032 | 1.6416 |  | -0.5532 | -2.294 | 4.0135 | 3.3646 | 3.3491 | 1.0393 | 10.6632 | 14.1187 | 14.6955 | 11.023 | 0.0004 | -0.0029 | 0.0006 | 0.0037 | 0.0006 | 0.0001 | 0.0126 | -0.0156 | -0.0113 | -360.1311 | 17.4172 | -360.4973 | 17.7477 | -360.8512 | 18.1009 | -360.8789 | 17.5301 | -352.669 | 18.7107 | -352.7429 | 16.8094
11:58 | 2277 | 28.351 | 196.6575 | 439.404 | 445.4854 | -19.3921 | -46.4428 | 5.744 | 2.998 | -3.5378 | -4.4028 | -0.8942 | -2.8956 | 6.028 | -0.6235 | 0.5947 | 0.6389 | 0.9539 | 0.7131 | -131.0838 | -5.7471 | 2.0791 | -0.1943 | -6.4071 | -4.9572 | 1.6713 |  | -0.6212 | -2.3743 | 4.0131 | 3.3598 | 3.3454 | 1.039 | 10.6839 | 14.1341 | 14.7248 | 11.0428 | -0.0002 | -0.0027 | 0.0015 | 0.0043 | 0.0008 | -0.0007 | 0.0123 | -0.005 | -0.003 | -360.1435 | 17.4007 | -360.4512 | 17.7457 | -360.8543 | 18.1337 | -360.9466 | 17.5712 | -352.7244 | 18.6984 | -352.6875 | 16.8094
11:58 | 2278 | 28.3118 | 196.6291 | 439.5718 | 445.5576 | -19.4738 | -46.4559 | 5.7316 | 3.0431 | -3.5336 | -4.4025 | -0.8137 | -2.9092 | 5.9651 | -0.5766 | 0.595 | 0.6383 | 0.955 | 0.7129 | -130.9774 | -5.7685 | 2.0745 | -0.1879 | -6.3703 | -5.0517 | 1.6225 |  | -0.5718 | -2.2149 | 4.0142 | 3.3613 | 3.3488 | 1.0391 | 10.7047 | 14.1491 | 14.7221 | 11.0695 | -0.0003 | -0.0027 | 0.0007 | 0.0035 | 0.0005 | -0.0001 | 0.004 | 0.0009 | -0.0204 | -360.1865 | 17.4377 | -360.5096 | 17.7293 | -360.8327 | 18.0906 | -360.8912 | 17.5671 | -352.749 | 18.7271 | -352.7367 | 16.7807
11:58 | 2279 | 28.3785 | 196.6652 | 439.5892 | 445.5758 | -19.5158 | -46.416 | 5.7343 | 3.0524 | -3.4597 | -4.4022 | -0.8492 | -3.024 | 5.9544 | -0.6292 | 0.5945 | 0.6381 | 0.9552 | 0.7134 | -131.0284 | -5.8174 | 2.0767 | -0.2418 | -6.4115 | -5.0081 | 1.5907 |  | -0.5817 | -2.1616 | 4.0149 | 3.3656 | 3.3493 | 1.0385 | 10.7047 | 14.1666 | 14.7405 | 11.0287 | 0 | -0.003 | 0.001 | 0.0038 | 0.0007 | -0.0007 | 0.0023 | -0.0096 | -0.0132 | -360.1896 | 17.4459 | -360.5404 | 17.7601 | -360.8389 | 18.0742 | -360.8604 | 17.5424 | -352.7183 | 18.7353 | -352.786 | 16.8238
11:58 | 2280 | 28.3242 | 196.6965 | 439.6319 | 445.5445 | -19.4603 | -46.3754 | 5.7571 | 3.0165 | -3.4344 | -4.2675 | -0.8232 | -2.978 | 5.9803 | -0.6879 | 0.5943 | 0.6346 | 0.9506 | 0.7122 | -130.932 | -5.7496 | 2.2176 | -0.2516 | -6.4715 | -4.9963 | 1.6054 |  | -0.6204 | -2.1238 | 4.0139 | 3.363 | 3.3546 | 1.0385 | 10.7012 | 14.1343 | 14.7027 | 11.0482 | -0.0001 | -0.0031 | 0.0005 | 0.0037 | 0.0005 | -0.0007 | 0.0068 | -0.0115 | -0.0086 | -360.1804 | 17.4397 | -360.5312 | 17.7765 | -360.8635 | 18.1112 | -360.8912 | 17.5465 | -352.6813 | 18.7251 | -352.7767 | 16.8258
11:58 | 2281 | 28.4095 | 196.6291 | 439.7036 | 445.6305 | -19.4549 | -46.4441 | 5.7318 | 3.0647 | -3.5102 | -4.3328 | -0.8266 | -2.9018 | 5.9318 | -0.5165 | 0.5942 | 0.6356 | 0.9522 | 0.7122 | -131.0149 | -5.7841 | 1.9995 | -0.1519 | -6.4507 | -5.0584 | 1.5642 |  | -0.5241 | -2.107 | 4.0139 | 3.3661 | 3.3477 | 1.0373 | 10.6954 | 14.163 | 14.748 | 11.0486 | -0.0002 | -0.0027 | -0.0002 | 0.0033 | 0.0007 | -0.0005 | -0.0092 | -0.0087 | -0.0312 | -360.1896 | 17.4069 | -360.4296 | 17.719 | -360.8204 | 18.1091 | -360.9189 | 17.5773 | -352.746 | 18.7045 | -352.6906 | 16.7868
11:58 | 2282 | 28.4911 | 196.6275 | 439.663 | 445.6463 | -19.4304 | -46.4958 | 5.7851 | 3.1317 | -3.5097 | -4.3196 | -0.7632 | -3.0368 | 5.8216 | -0.656 | 0.5954 | 0.6391 | 0.9536 | 0.7115 | -130.9869 | -5.8161 | 2.0689 | -0.1133 | -6.3908 | -4.9965 | 1.6959 |  | -0.4961 | -2.0672 | 4.0145 | 3.3648 | 3.3522 | 1.0383 | 10.6424 | 14.1094 | 14.7087 | 10.9793 | -0.0006 | -0.0031 | 0.0008 | 0.0043 | 0.0002 | -0.0012 | 0.0128 | -0.0006 | 0.0004 | -360.2542 | 17.4562 | -360.5096 | 17.7354 | -360.8112 | 18.1029 | -360.9251 | 17.5999 | -352.8198 | 18.7497 | -352.749 | 16.7683
11:58 | 2283 | 28.4575 | 196.6892 | 439.7424 | 445.7112 | -19.4226 | -46.5892 | 5.6939 | 3.1532 | -3.4813 | -4.2263 | -0.769 | -3.0743 | 5.8291 | -0.6408 | 0.5939 | 0.6355 | 0.9535 | 0.7126 | -130.9896 | -5.7336 | 2.0623 | -0.1637 | -6.293 | -5.016 | 1.567 |  | -0.5 | -2.0842 | 4.0155 | 3.3635 | 3.352 | 1.0379 | 10.6977 | 14.1424 | 14.7286 | 11.0388 | 0.0004 | -0.0029 | 0.0004 | 0.0037 | 0.0002 | -0.0007 | 0.0204 | -0.0163 | 0.0161 | -360.1927 | 17.4254 | -360.4973 | 17.7354 | -360.8297 | 18.0763 | -360.8789 | 17.5465 | -352.7029 | 18.7271 | -352.7398 | 16.793
11:58 | 2284 | 28.4261 | 196.678 | 439.7071 | 445.7124 | -19.393 | -46.5351 | 5.7298 | 3.0991 | -3.5445 | -4.3048 | -0.856 | -3.0604 | 5.92 | -0.5939 | 0.5949 | 0.6396 | 0.955 | 0.7134 | -130.9826 | -5.7767 | 2.0922 | -0.1388 | -6.2596 | -5.022 | 1.7233 |  | -0.4434 | -1.9844 | 4.0155 | 3.3624 | 3.3523 | 1.0387 | 10.6851 | 14.1524 | 14.6952 | 11.0158 | 0 | -0.0035 | 0.0006 | 0.0037 | 0.0009 | -0.0008 | -0.0002 | -0.02 | -0.0165 | -360.1311 | 17.4172 | -360.525 | 17.7642 | -360.9035 | 18.1276 | -360.9435 | 17.5486 | -352.709 | 18.7128 | -352.7552 | 16.8279
11:58 | 2285 | 28.4533 | 196.683 | 439.7395 | 445.6604 | -19.4207 | -46.5595 | 5.7477 | 3.0565 | -3.5927 | -4.4118 | -0.9224 | -3.028 | 5.8798 | -0.6644 | 0.5958 | 0.6399 | 0.9568 | 0.7136 | -131.0239 | -5.6848 | 2.0868 | -0.1232 | -6.3803 | -5.0743 | 1.5919 |  | -0.4639 | -1.9761 | 4.0141 | 3.3624 | 3.3492 | 1.0373 | 10.6908 | 14.1295 | 14.732 | 11.0266 | 0 | -0.0031 | 0.0014 | 0.0043 | 0.0003 | -0.0003 | 0.0019 | -0.0097 | -0.0109 | -360.1465 | 17.3946 | -360.4604 | 17.7272 | -360.8512 | 18.1112 | -360.9066 | 17.5588 | -352.6813 | 18.7004 | -352.6937 | 16.7848
11:58 | 2286 | 28.3859 | 196.7855 | 439.7571 | 445.6542 | -19.4176 | -46.6526 | 5.7753 | 3.1013 | -3.5129 | -4.1878 | -0.8241 | -2.924 | 5.9769 | -0.5195 | 0.5945 | 0.6404 | 0.9531 | 0.7134 | -131.0644 | -5.8282 | 2.0418 | -0.1261 | -6.3869 | -5.0493 | 1.6259 |  | -0.4317 | -1.9413 | 4.0151 | 3.3655 | 3.3524 | 1.0387 | 10.6953 | 14.1749 | 14.7096 | 11.0189 | -0.0003 | -0.0026 | 0.0006 | 0.0032 | 0.0011 | -0.0001 | -0.0006 | -0.0006 | -0.0271 | -360.2235 | 17.4562 | -360.525 | 17.7252 | -360.842 | 18.1009 | -360.9004 | 17.5896 | -352.7798 | 18.7477 | -352.7583 | 16.793
11:58 | 2287 | 28.4216 | 196.7434 | 439.7515 | 445.663 | -19.3947 | -46.5992 | 5.782 | 3.0812 | -3.5346 | -4.2252 | -0.9321 | -2.9733 | 5.9279 | -0.5957 | 0.5948 | 0.6412 | 0.9525 | 0.7131 | -131.1001 | -5.8336 | 1.9532 | 0.0279 | -6.2988 | -4.9948 | 1.6847 |  | -0.4618 | -1.9729 | 4.0136 | 3.3641 | 3.3518 | 1.0388 | 10.6769 | 14.1561 | 14.7408 | 11.0417 | -0.0006 | -0.0031 | 0.0005 | 0.0033 | 0.0006 | -0.0002 | 0.0201 | -0.0012 | -0.0304 | -360.165 | 17.4439 | -360.5373 | 17.7354 | -360.842 | 18.0701 | -360.845 | 17.5363 | -352.7183 | 18.7312 | -352.7644 | 16.8094
11:58 | 2288 | 28.3538 | 196.8002 | 439.7023 | 445.7049 | -19.4252 | -46.6426 | 5.8881 | 3.1375 | -3.4856 | -4.2447 | -0.9184 | -2.9792 | 5.9043 | -0.5604 | 0.5949 | 0.6415 | 0.9543 | 0.7141 | -131.0615 | -5.7153 | 1.9731 | -0.1082 | -6.3491 | -4.8982 | 1.6866 |  | -0.4338 | -2.0427 | 4.0148 | 3.3607 | 3.352 | 1.0371 | 10.6954 | 14.1169 | 14.6912 | 11.0251 | -0.0001 | -0.003 | 0.0008 | 0.0039 | 0.0014 | -0.0006 | 0.0113 | -0.0061 | -0.0072 | -360.165 | 17.4315 | -360.5312 | 17.7477 | -360.8697 | 18.1173 | -360.8974 | 17.5547 | -352.7213 | 18.721 | -352.7706 | 16.8217
11:58 | 2289 | 28.4135 | 196.7092 | 439.7523 | 445.7876 | -19.473 | -46.649 | 5.7424 | 3.0958 | -3.4501 | -4.2638 | -0.9353 | -2.9653 | 5.9553 | -0.4977 | 0.5941 | 0.6407 | 0.9548 | 0.7123 | -131.1305 | -5.796 | 2.037 | -0.1668 | -6.2945 | -4.9868 | 1.6998 |  | -0.492 | -2.0419 | 4.014 | 3.3631 | 3.349 | 1.0367 | 10.6897 | 14.1515 | 14.7538 | 11.0601 | 0 | -0.0032 | 0.0001 | 0.0033 | 0.0007 | -0.0004 | 0.0078 | -0.0072 | -0.0184 | -360.1958 | 17.4151 | -360.4296 | 17.7005 | -360.8174 | 18.105 | -360.9312 | 17.5814 | -352.7429 | 18.6984 | -352.6875 | 16.7724
11:58 | 2290 | 28.5031 | 196.827 | 439.6762 | 445.7527 | -19.4388 | -46.6529 | 5.8412 | 3.0757 | -3.4552 | -4.3012 | -0.8506 | -2.9358 | 5.9407 | -0.5181 | 0.5953 | 0.6386 | 0.9519 | 0.7116 | -131.0661 | -5.8004 | 1.9598 | -0.1903 | -6.2088 | -5.0016 | 1.7685 |  | -0.5619 | -2.0287 | 4.0139 | 3.3609 | 3.3499 | 1.0371 | 10.7128 | 14.1457 | 14.719 | 11.0544 | -0.0005 | -0.0028 | 0.0003 | 0.0039 | 0.0008 | -0.0005 | 0.0235 | -0.0144 | -0.0061 | -360.2542 | 17.4541 | -360.5035 | 17.7128 | -360.805 | 18.1009 | -360.9189 | 17.5937 | -352.7644 | 18.7374 | -352.7244 | 16.7827
11:58 | 2291 | 28.4747 | 196.8555 | 439.7544 | 445.7521 | -19.507 | -46.6452 | 5.8103 | 3.0827 | -3.4437 | -4.2898 | -0.9189 | -2.8632 | 5.9041 | -0.5383 | 0.5958 | 0.6387 | 0.9529 | 0.7104 | -131.1131 | -5.7731 | 2.0138 | -0.1535 | -6.2309 | -4.9278 | 1.6641 |  | -0.5059 | -1.9593 | 4.0146 | 3.3628 | 3.3492 | 1.0366 | 10.6642 | 14.1492 | 14.7 | 11.0403 | -0.0002 | -0.0028 | 0.0007 | 0.0039 | 0.0009 | -0.0005 | 0.0044 | -0.0065 | -0.0139 | -360.1804 | 17.4377 | -360.5189 | 17.7416 | -360.8481 | 18.0804 | -360.8604 | 17.5445 | -352.7244 | 18.723 | -352.7675 | 16.8053
11:58 | 2292 | 28.503 | 196.8769 | 439.885 | 445.6657 | -19.4896 | -46.6545 | 5.7793 | 3.0242 | -3.4158 | -4.204 | -0.8861 | -2.901 | 5.8724 | -0.5419 | 0.5942 | 0.6397 | 0.9519 | 0.7109 | -131.1798 | -5.7641 | 1.9074 | -0.202 | -6.3293 | -4.8999 | 1.6714 |  | -0.5281 | -1.9297 | 4.0128 | 3.3619 | 3.3483 | 1.0385 | 10.7162 | 14.1725 | 14.7242 | 11.0457 | 0.0001 | -0.0031 | 0.001 | 0.0038 | 0.0007 | -0.0004 | 0.0066 | -0.0091 | -0.0064 | -360.1558 | 17.4048 | -360.4789 | 17.758 | -360.8974 | 18.1235 | -360.9497 | 17.5588 | -352.6967 | 18.7128 | -352.7367 | 16.8197
11:58 | 2293 | 28.482 | 196.8688 | 439.8958 | 445.775 | -19.5065 | -46.5714 | 5.8489 | 3.1023 | -3.3807 | -4.2792 | -0.8809 | -2.9211 | 5.9432 | -0.5097 | 0.5948 | 0.6423 | 0.9554 | 0.7122 | -131.1291 | -5.7618 | 1.9644 | -0.0626 | -6.295 | -4.9267 | 1.7177 |  | -0.4527 | -2.0175 | 4.0132 | 3.3582 | 3.3491 | 1.0362 | 10.6607 | 14.1341 | 14.719 | 11.0544 | 0.0006 | -0.003 | 0.0007 | 0.0036 | 0.0005 | -0.0011 | 0.0243 | -0.0093 | 0.0052 | -360.1865 | 17.4048 | -360.4758 | 17.721 | -360.8758 | 18.1112 | -360.922 | 17.5609 | -352.7213 | 18.6984 | -352.6906 | 16.7827
11:58 | 2294 | 28.572 | 196.9086 | 439.9792 | 445.876 | -19.4662 | -46.6295 | 5.8036 | 3.1555 | -3.2704 | -4.2031 | -0.8813 | -2.8977 | 5.9287 | -0.458 | 0.5953 | 0.6416 | 0.9544 | 0.711 | -131.1241 | -5.6655 | 2.0345 | -0.1545 | -6.246 | -4.9318 | 1.6441 |  | -0.4187 | -1.9393 | 4.0134 | 3.3624 | 3.3485 | 1.0383 | 10.6965 | 14.1528 | 14.7157 | 11.0204 | -0.0005 | -0.0029 | 0.0006 | 0.0032 | 0.0005 | -0.0003 | -0.0098 | -0.0143 | -0.0006 | -360.2204 | 17.4541 | -360.5219 | 17.721 | -360.8358 | 18.0824 | -360.885 | 17.5712 | -352.7429 | 18.7415 | -352.7429 | 16.793
11:58 | 2295 | 28.5529 | 196.8153 | 439.9008 | 445.8247 | -19.3903 | -46.5307 | 5.7958 | 3.1697 | -3.2452 | -4.1898 | -0.8022 | -2.9345 | 5.892 | -0.4887 | 0.5942 | 0.6393 | 0.9558 | 0.7125 | -131.0494 | -5.6483 | 2.1599 | -0.271 | -6.3649 | -4.9702 | 1.7017 |  | -0.4882 | -1.9945 | 4.0136 | 3.3617 | 3.3469 | 1.0372 | 10.6909 | 14.1178 | 14.6788 | 11.0501 | -0.0003 | -0.0024 | 0.0004 | 0.0031 | 0.0013 | -0.0006 | 0.0134 | -0.0083 | -0.0141 | -360.1804 | 17.4521 | -360.5743 | 17.7477 | -360.8758 | 18.0763 | -360.8266 | 17.5383 | -352.706 | 18.7477 | -352.7737 | 16.8176
11:58 | 2296 | 28.5311 | 196.6673 | 439.928 | 445.757 | -19.3699 | -46.5909 | 5.8836 | 3.1194 | -3.2352 | -4.2784 | -0.8513 | -2.8907 | 5.8797 | -0.5364 | 0.5939 | 0.6392 | 0.9517 | 0.7098 | -131.0823 | -5.6608 | 2.1939 | -0.3554 | -6.3528 | -5.1017 | 1.6149 |  | -0.4391 | -2.0016 | 4.0145 | 3.3609 | 3.3497 | 1.038 | 10.6735 | 14.1469 | 14.6973 | 11.0266 | 0.0003 | -0.0031 | 0.0008 | 0.0039 | 0.0006 | -0.0003 | 0.0116 | -0.0029 | 0.0059 | -360.1342 | 17.411 | -360.4789 | 17.7293 | -360.8604 | 18.1071 | -360.9004 | 17.5527 | -352.7244 | 18.7107 | -352.746 | 16.8094
11:58 | 2297 | 28.5948 | 196.7002 | 439.8096 | 445.786 | -19.4391 | -46.5736 | 5.7935 | 3.1737 | -3.2077 | -4.1296 | -0.7753 | -2.9408 | 5.8742 | -0.6536 | 0.595 | 0.6391 | 0.9533 | 0.7119 | -131.126 | -5.6149 | 2.2036 | -0.3276 | -6.2898 | -4.9062 | 1.6779 |  | -0.4676 | -2.0761 | 4.0131 | 3.359 | 3.3491 | 1.0384 | 10.6759 | 14.1374 | 14.721 | 10.9833 | -0.0002 | -0.003 | 0.0005 | 0.0038 | 0.001 | -0.0006 | 0.0044 | -0.0219 | -0.0182 | -360.2204 | 17.4336 | -360.4789 | 17.7005 | -360.8112 | 18.1009 | -360.9343 | 17.5917 | -352.7614 | 18.7271 | -352.7152 | 16.7683
11:58 | 2298 | 28.5411 | 196.7099 | 439.8764 | 445.7705 | -19.3948 | -46.5051 | 5.8385 | 3.1527 | -3.2894 | -4.2033 | -0.7649 | -2.9028 | 5.9575 | -0.553 | 0.5943 | 0.6393 | 0.954 | 0.7107 | -131.2228 | -5.7591 | 2.0913 | -0.2543 | -6.2348 | -4.7608 | 1.6828 |  | -0.4128 | -2.0209 | 4.0123 | 3.3629 | 3.3483 | 1.0384 | 10.6874 | 14.149 | 14.6979 | 11.0353 | -0.0002 | -0.0029 | 0.0006 | 0.0039 | 0.0005 | -0.0007 | 0.0036 | -0.006 | -0.0003 | -360.2142 | 17.4418 | -360.5066 | 17.7128 | -360.7897 | 18.0763 | -360.885 | 17.5753 | -352.7583 | 18.7415 | -352.7675 | 16.7786
11:58 | 2299 | 28.5771 | 196.7212 | 439.8278 | 445.7745 | -19.4875 | -46.4784 | 5.84 | 3.1075 | -3.3954 | -4.1518 | -0.9241 | -2.9113 | 5.971 | -0.5484 | 0.5955 | 0.6392 | 0.949 | 0.713 | -131.1457 | -5.7282 | 2.0807 | -0.2672 | -6.2101 | -4.8317 | 1.6957 |  | -0.3835 | -1.9995 | 4.0127 | 3.3594 | 3.3539 | 1.0401 | 10.6713 | 14.1037 | 14.6751 | 11.0136 | -0.0005 | -0.0028 | 0.0004 | 0.0037 | 0.0012 | -0.0001 | 0.0098 | -0.0033 | -0.0114 | -360.1496 | 17.4274 | -360.5404 | 17.758 | -360.8974 | 18.1071 | -360.922 | 17.5404 | -352.6875 | 18.7333 | -352.7614 | 16.8197
11:58 | 2300 | 28.5682 | 196.769 | 439.8603 | 445.7244 | -19.4229 | -46.4638 | 5.8889 | 3.2157 | -3.3823 | -4.1456 | -0.818 | -2.8257 | 5.967 | -0.52 | 0.5952 | 0.6388 | 0.9518 | 0.7127 | -131.206 | -5.7869 | 1.9932 | -0.1764 | -6.2175 | -4.9308 | 1.7423 |  | -0.4542 | -1.9224 | 4.0129 | 3.361 | 3.3496 | 1.0388 | 10.7024 | 14.1467 | 14.7194 | 11.0269 | 0.0002 | -0.003 | 0.0006 | 0.0034 | 0.0006 | -0.0004 | 0.0008 | 0.0102 | -0.0191 | -360.1558 | 17.3884 | -360.4512 | 17.7169 | -360.842 | 18.1173 | -360.9497 | 17.5609 | -352.7121 | 18.6984 | -352.709 | 16.793
11:58 | 2301 | 28.5924 | 196.797 | 439.8969 | 445.7701 | -19.4385 | -46.4338 | 5.9963 | 3.1793 | -3.4503 | -4.2464 | -0.8728 | -2.8215 | 6.0242 | -0.5341 | 0.5959 | 0.6386 | 0.9555 | 0.7136 | -131.1379 | -5.7491 | 2.1513 | -0.2572 | -6.2833 | -5.0814 | 1.7095 |  | -0.405 | -2.0139 | 4.0131 | 3.3618 | 3.3449 | 1.0369 | 10.6956 | 14.1685 | 14.7517 | 11.0205 | -0.0001 | -0.0035 | 0.0005 | 0.0038 | 0.0003 | -0.0006 | 0.0016 | -0.006 | -0.0084 | -360.2204 | 17.4521 | -360.525 | 17.719 | -360.8512 | 18.0927 | -360.9281 | 17.5896 | -352.7398 | 18.7436 | -352.7644 | 16.7807
11:58 | 2302 | 28.4776 | 196.7707 | 439.9392 | 445.7879 | -19.4631 | -46.4036 | 5.9867 | 3.127 | -3.4263 | -4.2062 | -0.8584 | -2.7867 | 5.9888 | -0.4796 | 0.5948 | 0.6378 | 0.9539 | 0.712 | -131.0249 | -5.6832 | 2.1104 | -0.348 | -6.2994 | -4.9612 | 1.6524 |  | -0.402 | -2.0211 | 4.0138 | 3.3618 | 3.349 | 1.0382 | 10.6896 | 14.1749 | 14.7501 | 11.0478 | -0.0001 | -0.0029 | 0.0008 | 0.0034 | 0.0008 | -0.0008 | -0.0077 | 0.0003 | -0.0283 | -360.1311 | 17.4418 | -360.5527 | 17.7436 | -360.8327 | 18.0721 | -360.8235 | 17.5301 | -352.7152 | 18.7456 | -352.7675 | 16.8053
11:58 | 2303 | 28.5619 | 196.7486 | 440.0053 | 445.7571 | -19.4154 | -46.3881 | 5.9273 | 3.0964 | -3.4346 | -4.2812 | -0.8453 | -2.8656 | 6.0379 | -0.5049 | 0.5952 | 0.6368 | 0.9547 | 0.7131 | -131.1107 | -5.6982 | 2.0679 | -0.259 | -6.3698 | -4.9862 | 1.7397 |  | -0.4647 | -1.9739 | 4.0134 | 3.364 | 3.3476 | 1.0379 | 10.6966 | 14.1584 | 14.7204 | 11.0555 | -0.0006 | -0.0028 | 0.0008 | 0.0036 | 0.0003 | -0.0006 | 0.0119 | -0.0079 | -0.0263 | -360.1711 | 17.4356 | -360.5312 | 17.7477 | -360.8758 | 18.1091 | -360.9097 | 17.5465 | -352.6967 | 18.723 | -352.7829 | 16.8115
11:58 | 2304 | 28.5878 | 196.6876 | 439.9599 | 445.7813 | -19.4148 | -46.4502 | 5.9826 | 3.1019 | -3.3877 | -4.2527 | -0.8284 | -2.8815 | 6.0581 | -0.4178 | 0.5945 | 0.64 | 0.9556 | 0.7128 | -131.1287 | -5.6684 | 2.0362 | -0.2702 | -6.2816 | -5.0008 | 1.71 |  | -0.4974 | -1.9104 | 4.0131 | 3.3629 | 3.3495 | 1.037 | 10.7093 | 14.1482 | 14.7576 | 11.0562 | -0.0006 | -0.003 | 0.0006 | 0.0037 | 0.001 | -0.0006 | 0.0015 | -0.0039 | -0.0201 | -360.1958 | 17.411 | -360.4758 | 17.7026 | -360.7835 | 18.0906 | -360.9374 | 17.5794 | -352.7583 | 18.7107 | -352.6783 | 16.7581
11:58 | 2305 | 28.5077 | 196.735 | 440.0082 | 445.7957 | -19.3893 | -46.4998 | 5.9634 | 3.1572 | -3.4233 | -4.1574 | -0.8075 | -2.9756 | 6.0544 | -0.4215 | 0.5952 | 0.6415 | 0.9561 | 0.7157 | -131.1076 | -5.6661 | 2.0543 | -0.2401 | -6.3024 | -4.9679 | 1.7103 |  | -0.4894 | -2.1403 | 4.0129 | 3.3619 | 3.3482 | 1.0389 | 10.7172 | 14.1683 | 14.7461 | 11.0745 | 0.0005 | -0.0028 | 0.001 | 0.0039 | 0.0003 | -0.0008 | 0.0038 | -0.0121 | 0.0024 | -360.2481 | 17.4644 | -360.5281 | 17.7293 | -360.845 | 18.0865 | -360.8912 | 17.5814 | -352.7952 | 18.7559 | -352.7706 | 16.7786
11:58 | 2306 | 28.5671 | 196.7779 | 440.0442 | 445.8565 | -19.4818 | -46.5192 | 6.0357 | 3.2031 | -3.4484 | -4.2288 | -0.8625 | -2.8728 | 6.0323 | -0.4431 | 0.5945 | 0.6383 | 0.9559 | 0.7142 | -131.1063 | -5.6408 | 2.1925 | -0.15 | -6.3237 | -4.9435 | 1.7648 |  | -0.3788 | -2.0934 | 4.0132 | 3.3658 | 3.3473 | 1.0396 | 10.7129 | 14.1398 | 14.7238 | 11.0374 | -0.0003 | -0.0033 | 0.0007 | 0.0039 | 0.0008 | -0.0005 | 0.0045 | -0.0099 | -0.0105 | -360.1527 | 17.4069 | -360.5158 | 17.7436 | -360.8604 | 18.0927 | -360.8697 | 17.5383 | -352.6967 | 18.7148 | -352.7429 | 16.7991
11:58 | 2307 | 28.6605 | 196.7978 | 440.108 | 445.9017 | -19.3751 | -46.4446 | 6.022 | 3.0764 | -3.4104 | -4.1594 | -0.8351 | -2.8824 | 6.0804 | -0.3832 | 0.5945 | 0.6359 | 0.9532 | 0.7132 | -131.0924 | -5.5888 | 2.2069 | -0.1656 | -6.4209 | -5.0375 | 1.6314 |  | -0.3583 | -2.0157 | 4.0139 | 3.3643 | 3.3528 | 1.0389 | 10.6919 | 14.1713 | 14.7344 | 11.0099 | -0.0004 | -0.0026 | 0.0007 | 0.0041 | 0.0008 | -0.0004 | 0.0055 | 0.0031 | -0.0055 | -360.1465 | 17.4048 | -360.4758 | 17.7436 | -360.8574 | 18.1461 | -360.9589 | 17.5712 | -352.7213 | 18.7025 | -352.6937 | 16.795
11:58 | 2308 | 28.6832 | 196.8683 | 440.1527 | 445.9009 | -19.417 | -46.4668 | 5.7972 | 3.1277 | -3.3994 | -4.2174 | -0.8091 | -2.8396 | 6.0715 | -0.4058 | 0.5957 | 0.6373 | 0.9561 | 0.7142 | -131.2585 | -5.7273 | 2.2288 | -0.1746 | -6.4726 | -5.1072 | 1.5851 |  | -0.3729 | -1.9853 | 4.0135 | 3.3642 | 3.3492 | 1.0395 | 10.6792 | 14.1584 | 14.6973 | 11.0323 | -0.0005 | -0.0031 | 0.0006 | 0.0037 | 0.0006 | -0.0005 | 0.0085 | 0.0033 | -0.0051 | -360.1896 | 17.4274 | -360.4881 | 17.7087 | -360.8081 | 18.0824 | -360.8974 | 17.5691 | -352.7275 | 18.7148 | -352.7183 | 16.7827
11:58 | 2309 | 28.7846 | 196.8725 | 440.1903 | 446.0115 | -19.3694 | -46.5006 | 5.9189 | 3.1345 | -3.3076 | -4.2209 | -0.8306 | -2.9 | 6.0203 | -0.4948 | 0.5967 | 0.6378 | 0.9561 | 0.7144 | -131.2016 | -5.6738 | 2.1226 | -0.11 | -6.356 | -5.0469 | 1.7407 |  | -0.4311 | -1.9911 | 4.0122 | 3.3636 | 3.3471 | 1.0379 | 10.6828 | 14.127 | 14.7166 | 11.0306 | -0.0001 | -0.0032 | 0.0007 | 0.0036 | 0.0009 | -0.0002 | 0.0022 | -0.0064 | -0.0104 | -360.1711 | 17.4521 | -360.5804 | 17.7662 | -360.9158 | 18.0906 | -360.8574 | 17.5465 | -352.7337 | 18.7477 | -352.7952 | 16.834
11:58 | 2310 | 28.7266 | 196.849 | 440.0978 | 445.9307 | -19.3525 | -46.6061 | 5.9885 | 2.9697 | -3.3864 | -4.3338 | -0.8991 | -2.961 | 6.03 | -0.4791 | 0.5962 | 0.6364 | 0.9554 | 0.7133 | -131.1303 | -5.5869 | 2.1107 | -0.1614 | -6.4048 | -4.9854 | 1.7115 |  | -0.4442 | -2.1248 | 4.0135 | 3.3627 | 3.3493 | 1.039 | 10.6631 | 14.1363 | 14.7034 | 11.0396 | 0.0001 | -0.0031 | 0.0009 | 0.0037 | 0.0005 | -0.0008 | 0.0066 | -0.0092 | -0.0157 | -360.1188 | 17.4028 | -360.4789 | 17.7395 | -360.8666 | 18.1009 | -360.8697 | 17.5301 | -352.6475 | 18.7128 | -352.746 | 16.8115
11:58 | 2311 | 28.7132 | 196.8032 | 439.9214 | 445.8945 | -19.3681 | -46.6168 | 5.9822 | 2.992 | -3.3119 | -4.0528 | -0.8916 | -2.9261 | 6.013 | -0.4434 | 0.5952 | 0.6412 | 0.9538 | 0.713 | -131.1906 | -5.7314 | 2.028 | -0.178 | -6.4335 | -4.912 | 1.713 |  | -0.3452 | -2.0459 | 4.0133 | 3.3646 | 3.3491 | 1.0391 | 10.7117 | 14.1618 | 14.764 | 11.036 | 0 | -0.0027 | 0.0009 | 0.0039 | 0.0009 | -0.0002 | 0 | -0.0083 | -0.0189 | -360.2296 | 17.4377 | -360.5219 | 17.7231 | -360.8143 | 18.1091 | -360.9497 | 17.5978 | -352.7583 | 18.7415 | -352.7675 | 16.8032
11:58 | 2312 | 28.7872 | 196.7879 | 440.0223 | 445.903 | -19.3873 | -46.6088 | 6.0206 | 3.0996 | -3.332 | -4.2965 | -0.8023 | -2.9181 | 6.0552 | -0.3962 | 0.5951 | 0.6397 | 0.9563 | 0.713 | -131.2062 | -5.7469 | 2.0615 | -0.1014 | -6.3411 | -4.9706 | 1.7975 |  | -0.3743 | -2.0633 | 4.0127 | 3.3627 | 3.3499 | 1.0394 | 10.6989 | 14.1781 | 14.7289 | 11.0692 | -0.0003 | -0.0026 | 0.0007 | 0.0036 | 0.0006 | 0 | 0.0073 | -0.0044 | -0.0235 | -360.2111 | 17.4521 | -360.5281 | 17.719 | -360.805 | 18.0598 | -360.8635 | 17.5629 | -352.7213 | 18.7477 | -352.7737 | 16.8012
11:58 | 2313 | 28.7192 | 196.8588 | 440.1005 | 446.0354 | -19.4308 | -46.65 | 6.0687 | 3.1548 | -3.3351 | -4.1801 | -0.8317 | -2.882 | 6.1072 | -0.4211 | 0.5954 | 0.6411 | 0.9556 | 0.7141 | -131.2159 | -5.78 | 2.0726 | -0.0959 | -6.4216 | -4.9777 | 1.7003 |  | -0.4269 | -2.1031 | 4.014 | 3.366 | 3.3505 | 1.0387 | 10.6966 | 14.1353 | 14.7204 | 11.0381 | 0.0001 | -0.0029 | 0.0005 | 0.0037 | 0.001 | -0.0008 | 0.0078 | -0.0107 | 0.0067 | -360.1711 | 17.4315 | -360.5435 | 17.7683 | -360.9035 | 18.1173 | -360.9251 | 17.5547 | -352.7121 | 18.7271 | -352.7706 | 16.8279
11:58 | 2314 | 28.7595 | 196.895 | 440.0873 | 446.0322 | -19.2924 | -46.6563 | 6.0752 | 3.1245 | -3.3308 | -4.3064 | -0.8019 | -2.9462 | 6.0726 | -0.4033 | 0.5954 | 0.6394 | 0.9546 | 0.7135 | -131.1792 | -5.8095 | 1.9822 | -0.1564 | -6.3381 | -5.0202 | 1.6667 |  | -0.4111 | -2.0913 | 4.0137 | 3.3618 | 3.3481 | 1.0375 | 10.7382 | 14.1771 | 14.7576 | 11.0677 | 0.0002 | -0.0028 | 0.0004 | 0.0039 | 0.0007 | 0 | 0.0069 | -0.0075 | -0.0164 | -360.1835 | 17.3905 | -360.4235 | 17.6964 | -360.8204 | 18.1173 | -360.9312 | 17.5691 | -352.7121 | 18.7004 | -352.6721 | 16.7889
11:58 | 2315 | 28.8773 | 196.8496 | 440.2154 | 446.0102 | -19.4033 | -46.648 | 6.0875 | 3.1121 | -3.2544 | -4.2177 | -0.7196 | -3.0038 | 6.1024 | -0.4371 | 0.5966 | 0.6415 | 0.9551 | 0.7146 | -131.1142 | -5.7462 | 2.11 | -0.1867 | -6.3879 | -5.0407 | 1.6672 |  | -0.4119 | -2.0456 | 4.0139 | 3.3617 | 3.3532 | 1.0386 | 10.6804 | 14.1654 | 14.7334 | 11.0392 | -0.0003 | -0.0029 | 0.0005 | 0.0037 | 0.0008 | -0.0011 | 0.0076 | -0.0037 | -0.012 | -360.2142 | 17.448 | -360.5066 | 17.7252 | -360.8574 | 18.1009 | -360.9466 | 17.5896 | -352.746 | 18.7415 | -352.7367 | 16.795
11:58 | 2316 | 28.8187 | 196.8743 | 440.1788 | 445.988 | -19.4654 | -46.6832 | 6.052 | 3.135 | -3.2568 | -4.3004 | -0.7752 | -2.9293 | 6.1077 | -0.4477 | 0.5956 | 0.6379 | 0.9546 | 0.7134 | -131.104 | -5.7507 | 2.1504 | -0.0167 | -6.4527 | -4.9763 | 1.63 |  | -0.3329 | -1.9756 | 4.0144 | 3.3658 | 3.3499 | 1.0374 | 10.6909 | 14.1235 | 14.6778 | 11.0042 | -0.0006 | -0.0027 | 0.0003 | 0.0032 | 0.0004 | -0.0006 | 0.0201 | -0.0063 | 0.0045 | -360.1435 | 17.4213 | -360.5312 | 17.7559 | -360.8697 | 18.0639 | -360.8358 | 17.5363 | -352.6783 | 18.7271 | -352.7614 | 16.832
11:58 | 2317 | 28.8031 | 196.8847 | 440.151 | 445.9907 | -19.4455 | -46.6654 | 6.1047 | 3.1097 | -3.1936 | -4.3031 | -0.8608 | -2.904 | 6.1419 | -0.5265 | 0.5931 | 0.6354 | 0.9554 | 0.7135 | -131.1138 | -5.7324 | 2.1247 | -0.1047 | -6.4557 | -4.9997 | 1.575 |  | -0.3285 | -2.0179 | 4.0141 | 3.3614 | 3.3489 | 1.0395 | 10.6539 | 14.1559 | 14.6993 | 10.9901 | 0 | -0.0027 | 0.0004 | 0.0037 | 0.0008 | -0.0006 | 0.0037 | 0.0006 | -0.0112 | -360.1773 | 17.4233 | -360.4973 | 17.758 | -360.9035 | 18.1255 | -360.9251 | 17.5506 | -352.7029 | 18.7292 | -352.7367 | 16.8279
11:58 | 2318 | 28.7826 | 196.8105 | 440.1619 | 445.9638 | -19.4465 | -46.7571 | 6.0264 | 3.0503 | -3.327 | -4.3241 | -0.8071 | -2.944 | 6.0694 | -0.4144 | 0.5941 | 0.6363 | 0.9515 | 0.7132 | -131.1416 | -5.8186 | 2.107 | -0.1353 | -6.4185 | -4.9888 | 1.6197 |  | -0.3065 | -1.93 | 4.015 | 3.3635 | 3.3505 | 1.0404 | 10.6782 | 14.1107 | 14.7054 | 11.032 | 0.0001 | -0.0032 | 0.0011 | 0.004 | 0.0006 | -0.0004 | 0.002 | -0.0129 | -0.0163 | -360.1988 | 17.4131 | -360.4666 | 17.6964 | -360.7712 | 18.0865 | -360.9281 | 17.5732 | -352.6967 | 18.7189 | -352.709 | 16.7848
11:58 | 2319 | 28.7126 | 196.7888 | 440.1738 | 445.9133 | -19.4741 | -46.7311 | 6.0316 | 3.1009 | -3.2032 | -4.2796 | -0.8783 | -2.916 | 6.0351 | -0.3641 | 0.5943 | 0.639 | 0.9523 | 0.7137 | -131.1049 | -5.786 | 1.9925 | -0.0858 | -6.3999 | -5.0563 | 1.639 |  | -0.3852 | -1.906 | 4.0141 | 3.3622 | 3.3533 | 1.0402 | 10.6931 | 14.1377 | 14.7231 | 11.0056 | 0.0003 | -0.0026 | 0.0009 | 0.0038 | 0.001 | -0.0002 | 0.0002 | -0.005 | 0 | -360.2081 | 17.4747 | -360.5466 | 17.7375 | -360.8512 | 18.0742 | -360.882 | 17.5712 | -352.7614 | 18.76 | -352.7829 | 16.8074
11:58 | 2320 | 28.7939 | 196.8407 | 440.2447 | 445.9476 | -19.4389 | -46.7332 | 6.05 | 3.135 | -3.1547 | -4.3214 | -0.7761 | -2.9424 | 6.0157 | -0.4266 | 0.5949 | 0.641 | 0.9516 | 0.7138 | -131.0359 | -5.6729 | 2.056 | 0.0134 | -6.3779 | -5.0253 | 1.6626 |  | -0.375 | -1.9209 | 4.0146 | 3.3607 | 3.3511 | 1.0388 | 10.6977 | 14.1771 | 14.717 | 11.0388 | -0.0004 | -0.0025 | 0.0009 | 0.0042 | 0.0007 | -0.0008 | 0.0014 | -0.0152 | -0.0154 | -360.1465 | 17.4213 | -360.5004 | 17.7334 | -360.8727 | 18.0763 | -360.8666 | 17.5445 | -352.7029 | 18.7189 | -352.7213 | 16.8135
11:58 | 2321 | 28.7727 | 196.9241 | 440.293 | 445.9393 | -19.4196 | -46.6705 | 6.0208 | 3.0924 | -3.2699 | -4.396 | -0.8675 | -2.9874 | 6.0129 | -0.3902 | 0.5949 | 0.6392 | 0.9547 | 0.7138 | -130.9675 | -5.7405 | 2.1192 | -0.0474 | -6.4747 | -5.1094 | 1.6731 |  | -0.361 | -1.8981 | 4.0131 | 3.3631 | 3.3516 | 1.0396 | 10.7254 | 14.1934 | 14.7457 | 11.0547 | -0.0004 | -0.0026 | 0.0006 | 0.0036 | 0.0007 | -0.0004 | 0.008 | -0.0009 | -0.0037 | -360.2204 | 17.4131 | -360.4789 | 17.7149 | -360.8666 | 18.1358 | -360.9374 | 17.5835 | -352.7429 | 18.7128 | -352.706 | 16.7991
11:58 | 2322 | 28.6735 | 196.8391 | 440.1363 | 445.9839 | -19.5308 | -46.6114 | 5.9591 | 3.1611 | -3.2252 | -4.344 | -0.7466 | -3.0396 | 6.0104 | -0.4091 | 0.5941 | 0.6383 | 0.9514 | 0.7128 | -130.9867 | -5.8477 | 2.1882 | -0.1495 | -6.4006 | -5.1626 | 1.6212 |  | -0.3854 | -1.9021 | 4.0137 | 3.3615 | 3.3509 | 1.0394 | 10.6666 | 14.1398 | 14.7122 | 11.0259 | 0.0002 | -0.0029 | -0.0002 | 0.0033 | 0.0009 | -0.0007 | -0.0002 | -0.0154 | -0.0055 | -360.2296 | 17.4151 | -360.4573 | 17.6944 | -360.7681 | 18.0927 | -360.9158 | 17.5671 | -352.7398 | 18.7292 | -352.6906 | 16.7724
11:58 | 2323 | 28.8454 | 196.8524 | 440.1869 | 446.0455 | -19.4747 | -46.6046 | 6.0183 | 3.1486 | -3.1797 | -4.2481 | -0.7855 | -3.0325 | 6.1217 | -0.3537 | 0.5944 | 0.6353 | 0.9533 | 0.711 | -130.98 | -5.745 | 2.2563 | -0.0419 | -6.4166 | -5.1096 | 1.633 |  | -0.3864 | -2.0505 | 4.0136 | 3.3617 | 3.3496 | 1.0387 | 10.6645 | 14.1312 | 14.6658 | 10.996 | -0.0004 | -0.0032 | 0.0005 | 0.0037 | 0.0006 | -0.0004 | 0.0054 | -0.0038 | 0.0026 | -360.1558 | 17.448 | -360.5527 | 17.7559 | -360.885 | 18.0906 | -360.885 | 17.5629 | -352.7306 | 18.7456 | -352.7737 | 16.834
11:58 | 2324 | 28.8606 | 196.7941 | 440.2382 | 446.0179 | -19.4319 | -46.5755 | 6.0215 | 3.2014 | -3.1381 | -4.2653 | -0.8042 | -3.0077 | 6.1173 | -0.4206 | 0.596 | 0.6377 | 0.9515 | 0.7137 | -130.9893 | -5.6626 | 2.2824 | -0.1183 | -6.3705 | -5.0148 | 1.6551 |  | -0.3725 | -1.9621 | 4.0135 | 3.3606 | 3.3462 | 1.0388 | 10.7 | 14.1273 | 14.7187 | 11.0587 | 0 | -0.0026 | 0.0006 | 0.0034 | 0.0012 | -0.0006 | 0.0014 | -0.0069 | -0.0184 | -360.085 | 17.3966 | -360.4604 | 17.7313 | -360.8912 | 18.1112 | -360.8943 | 17.5321 | -352.666 | 18.6922 | -352.7121 | 16.8217
11:58 | 2325 | 28.8718 | 196.8398 | 440.2413 | 446.0537 | -19.4451 | -46.5987 | 6.0316 | 3.2162 | -3.1913 | -4.3163 | -0.7821 | -2.972 | 6.1747 | -0.4036 | 0.5972 | 0.6359 | 0.9554 | 0.7128 | -130.9921 | -5.6102 | 2.2904 | -0.2337 | -6.401 | -5.0534 | 1.5547 |  | -0.4571 | -2.0652 | 4.0139 | 3.3623 | 3.352 | 1.0381 | 10.6943 | 14.1329 | 14.7235 | 11.0417 | -0.0003 | -0.0032 | 0.001 | 0.0039 | 0.0006 | -0.0004 | 0.0062 | -0.0081 | -0.0121 | -360.2173 | 17.4295 | -360.4912 | 17.7087 | -360.8327 | 18.1112 | -360.9343 | 17.5835 | -352.7521 | 18.7251 | -352.7306 | 16.8032
11:58 | 2326 | 28.91 | 196.8386 | 440.3426 | 446.0599 | -19.4483 | -46.5571 | 6.0435 | 3.222 | -3.1702 | -4.2519 | -0.7139 | -2.9018 | 6.1235 | -0.4394 | 0.5947 | 0.6378 | 0.955 | 0.7143 | -131.0159 | -5.7187 | 2.2638 | -0.2012 | -6.2973 | -4.9776 | 1.5069 |  | -0.3135 | -2.0437 | 4.0149 | 3.3624 | 3.3528 | 1.0394 | 10.6988 | 14.1552 | 14.73 | 11.0457 | 0.0003 | -0.0031 | 0.0014 | 0.0044 | 0.0006 | -0.0011 | 0.0003 | -0.014 | -0.0054 | -360.1988 | 17.4541 | -360.5496 | 17.721 | -360.8327 | 18.0598 | -360.8574 | 17.5527 | -352.7275 | 18.7497 | -352.749 | 16.8074
11:58 | 2327 | 28.9317 | 196.838 | 440.3582 | 446.0384 | -19.4006 | -46.5394 | 6.058 | 3.2041 | -3.2106 | -4.2434 | -0.7551 | -2.974 | 6.1387 | -0.4382 | 0.5955 | 0.6391 | 0.9535 | 0.7136 | -131.0933 | -5.7442 | 2.2918 | -0.1141 | -6.2753 | -4.9096 | 1.6074 |  | -0.3576 | -2.0459 | 4.0139 | 3.3606 | 3.3526 | 1.0404 | 10.6883 | 14.1624 | 14.7335 | 11.0576 | 0.0003 | -0.0032 | 0.0009 | 0.0035 | 0.0004 | -0.0004 | -0.0042 | -0.0006 | -0.0147 | -360.1742 | 17.4397 | -360.5435 | 17.7498 | -360.8789 | 18.0968 | -360.8881 | 17.5445 | -352.6998 | 18.7333 | -352.7706 | 16.834
11:59 | 2328 | 28.8701 | 196.8598 | 440.4156 | 446.0196 | -19.3852 | -46.5398 | 5.9955 | 3.0941 | -3.3291 | -4.2889 | -0.8148 | -3.0022 | 6.0738 | -0.4116 | 0.5957 | 0.6394 | 0.9537 | 0.7123 | -131.1037 | -5.7548 | 2.286 | -0.1895 | -6.3448 | -4.8581 | 1.6564 |  | -0.3171 | -1.9918 | 4.014 | 3.3641 | 3.3512 | 1.0399 | 10.7278 | 14.1899 | 14.7474 | 11.0515 | -0.0001 | -0.0026 | 0.0003 | 0.0035 | 0.0003 | -0.001 | 0.0057 | -0.0112 | 0.0011 | -360.165 | 17.4048 | -360.4419 | 17.7149 | -360.8574 | 18.1091 | -360.9527 | 17.5753 | -352.6813 | 18.7045 | -352.706 | 16.7848
11:59 | 2329 | 28.8839 | 196.879 | 440.442 | 446.0455 | -19.3276 | -46.508 | 6.0906 | 3.1673 | -3.3521 | -4.246 | -0.7913 | -2.987 | 6.1079 | -0.4844 | 0.5945 | 0.6402 | 0.9539 | 0.7133 | -131.0386 | -5.6429 | 2.3287 | -0.1099 | -6.2739 | -4.9207 | 1.7147 |  | -0.4727 | -1.9588 | 4.0126 | 3.3638 | 3.352 | 1.0378 | 10.7023 | 14.147 | 14.6983 | 11.0262 | -0.0005 | -0.0027 | 0.0007 | 0.0038 | 0.0009 | -0.0004 | 0.018 | -0.0112 | -0.0057 | -360.1804 | 17.4356 | -360.5004 | 17.7046 | -360.7835 | 18.0927 | -360.9158 | 17.5794 | -352.7829 | 18.7353 | -352.7121 | 16.7909
11:59 | 2330 | 28.8094 | 196.8069 | 440.3648 | 446.1245 | -19.3303 | -46.5231 | 6.1053 | 3.2694 | -3.3342 | -4.2748 | -0.7149 | -2.9632 | 6.1741 | -0.4223 | 0.5943 | 0.6373 | 0.9543 | 0.7134 | -131.1267 | -5.7085 | 2.2726 | 0.0097 | -6.2542 | -4.8359 | 1.6796 |  | -0.4159 | -1.9863 | 4.0142 | 3.3667 | 3.3534 | 1.0404 | 10.6932 | 14.1547 | 14.7616 | 11.0122 | -0.0005 | -0.0034 | 0.0001 | 0.0037 | 0.0006 | -0.0006 | -0.0101 | -0.0051 | -0.0057 | -360.1373 | 17.4356 | -360.525 | 17.7498 | -360.8635 | 18.0865 | -360.8912 | 17.5404 | -352.6752 | 18.7271 | -352.749 | 16.8156
11:59 | 2331 | 28.8122 | 196.8143 | 440.3594 | 446.0798 | -19.3519 | -46.4173 | 6.1865 | 3.2786 | -3.2349 | -4.2258 | -0.6616 | -2.9503 | 6.1498 | -0.3769 | 0.5951 | 0.6362 | 0.9536 | 0.713 | -131.0322 | -5.71 | 2.3556 | 0.1198 | -6.2271 | -4.8223 | 1.7151 |  | -0.3417 | -2.0648 | 4.0141 | 3.3647 | 3.3506 | 1.0393 | 10.6793 | 14.1583 | 14.7078 | 11.0385 | 0.0001 | -0.0029 | 0.0006 | 0.0041 | 0.0006 | -0.0007 | 0.0082 | -0.0155 | -0.0047 | -360.1004 | 17.3843 | -360.4389 | 17.7436 | -360.885 | 18.1214 | -360.8943 | 17.5445 | -352.6598 | 18.6881 | -352.7029 | 16.8156
11:59 | 2332 | 28.829 | 196.8883 | 440.4697 | 446.15 | -19.4182 | -46.457 | 6.0608 | 3.2058 | -3.3009 | -4.3698 | -0.7753 | -2.9916 | 6.1428 | -0.4604 | 0.5958 | 0.6414 | 0.9555 | 0.7143 | -130.9956 | -5.7113 | 2.3785 | 0.0639 | -6.272 | -4.832 | 1.6353 |  | -0.3441 | -1.9519 | 4.0142 | 3.364 | 3.352 | 1.0381 | 10.6815 | 14.1261 | 14.7058 | 11.0172 | -0.0003 | -0.003 | 0.0005 | 0.0038 | 0.0009 | -0.0002 | -0.0005 | -0.0191 | -0.0128 | -360.2358 | 17.4315 | -360.4942 | 17.7354 | -360.8543 | 18.1091 | -360.9004 | 17.5814 | -352.7552 | 18.7271 | -352.7152 | 16.8135
11:59 | 2333 | 28.9029 | 196.8661 | 440.4925 | 446.0768 | -19.335 | -46.4395 | 6.1688 | 3.1344 | -3.3881 | -4.1872 | -0.7783 | -2.9153 | 6.1688 | -0.3765 | 0.5945 | 0.638 | 0.9554 | 0.7133 | -130.9891 | -5.6462 | 2.2135 | 0.0333 | -6.2994 | -4.9466 | 1.6727 |  | -0.3099 | -1.9333 | 4.0131 | 3.3648 | 3.3494 | 1.0384 | 10.6805 | 14.1129 | 14.7128 | 10.9999 | -0.0005 | -0.0028 | 0.0005 | 0.0036 | 0.0008 | -0.001 | -0.0046 | -0.008 | -0.0217 | -360.1558 | 17.45 | -360.5589 | 17.7375 | -360.8204 | 18.0639 | -360.8174 | 17.5321 | -352.7398 | 18.7497 | -352.7614 | 16.8074
11:59 | 2334 | 28.8645 | 196.8427 | 440.6227 | 446.2035 | -19.2908 | -46.4037 | 6.0995 | 3.2122 | -3.3162 | -4.1989 | -0.6861 | -2.956 | 6.131 | -0.4141 | 0.5956 | 0.6392 | 0.9561 | 0.7125 | -131.0459 | -5.6613 | 2.2773 | 0.0483 | -6.4016 | -4.8865 | 1.7063 |  | -0.2967 | -1.9879 | 4.0136 | 3.365 | 3.3533 | 1.039 | 10.6724 | 14.1571 | 14.7064 | 11.0143 | 0 | -0.0028 | 0.0013 | 0.0043 | 0 | -0.0001 | 0.0032 | -0.0071 | -0.0059 | -360.1558 | 17.4315 | -360.5496 | 17.7559 | -360.8604 | 18.1071 | -360.9158 | 17.5404 | -352.6906 | 18.7436 | -352.7675 | 16.8443
11:59 | 2335 | 28.9425 | 196.8545 | 440.8229 | 446.3867 | -19.2512 | -46.3952 | 6.1551 | 3.1809 | -3.2613 | -4.1736 | -0.6201 | -2.9731 | 6.1705 | -0.4161 | 0.5961 | 0.6336 | 0.9525 | 0.7125 | -130.9968 | -5.6812 | 2.3206 | 0.0679 | -6.3567 | -4.8549 | 1.7161 |  | -0.3022 | -1.7838 | 4.0133 | 3.3629 | 3.3507 | 1.038 | 10.6942 | 14.1448 | 14.7429 | 11.041 | 0 | -0.0029 | 0.001 | 0.0036 | 0.001 | -0.0005 | 0.0097 | 0.0028 | -0.0158 | -360.1804 | 17.411 | -360.4635 | 17.6964 | -360.8174 | 18.0988 | -360.9189 | 17.5835 | -352.7398 | 18.6963 | -352.6537 | 16.7766
11:59 | 2336 | 28.8797 | 196.8387 | 440.7578 | 446.577 | -19.3528 | -46.3465 | 6.1674 | 3.1624 | -3.2605 | -4.1866 | -0.7037 | -2.8907 | 6.1339 | -0.3841 | 0.596 | 0.6375 | 0.9561 | 0.7148 | -130.9378 | -5.5459 | 2.3815 | 0.0453 | -6.4461 | -4.9631 | 1.645 |  | -0.3354 | -1.8043 | 4.0147 | 3.3652 | 3.3559 | 1.0387 | 10.7232 | 14.1504 | 14.7419 | 11.0529 | 0.0004 | -0.003 | 0.0004 | 0.0038 | 0.0006 | -0.0005 | 0.0064 | -0.0094 | 0.003 | -360.2327 | 17.448 | -360.4727 | 17.6964 | -360.8266 | 18.0742 | -360.8943 | 17.5835 | -352.746 | 18.7374 | -352.7429 | 16.7786
11:59 | 2337 | 28.905 | 196.8036 | 440.9345 | 446.6937 | -19.4319 | -46.4576 | 6.133 | 3.2381 | -3.3578 | -4.1382 | -0.6594 | -2.8507 | 6.2575 | -0.3075 | 0.5953 | 0.6355 | 0.9525 | 0.7152 | -130.989 | -5.5809 | 2.276 | -0.183 | -6.4306 | -4.9207 | 1.6247 |  | -0.2425 | -1.7734 | 4.0163 | 3.3628 | 3.3519 | 1.0398 | 10.7 | 14.1621 | 14.7487 | 11.0641 | -0.0003 | -0.0024 | 0.0005 | 0.0037 | 0.0007 | -0.0005 | 0.0253 | -0.0076 | 0.0022 | -360.1558 | 17.4315 | -360.5404 | 17.7457 | -360.8974 | 18.1009 | -360.882 | 17.5486 | -352.6813 | 18.7271 | -352.749 | 16.8279
11:59 | 2338 | 28.818 | 196.8476 | 441.0174 | 446.6868 | -19.3366 | -46.4401 | 6.0878 | 3.1844 | -3.2597 | -4.1631 | -0.6854 | -2.9069 | 6.1798 | -0.3507 | 0.5962 | 0.637 | 0.9545 | 0.7137 | -131.008 | -5.6153 | 2.3277 | -0.1716 | -6.4745 | -4.9524 | 1.6217 |  | -0.2681 | -1.7396 | 4.0146 | 3.3621 | 3.3516 | 1.0386 | 10.7012 | 14.169 | 14.7201 | 11.0193 | -0.0002 | -0.0024 | 0 | 0.0034 | 0.0005 | -0.0008 | 0.0096 | -0.0075 | -0.0138 | -360.0973 | 17.3925 | -360.4635 | 17.7067 | -360.8543 | 18.1194 | -360.9189 | 17.5588 | -352.6721 | 18.684 | -352.669 | 16.8156
11:59 | 2339 | 28.8339 | 196.7847 | 441.0866 | 446.687 | -19.3161 | -46.5088 | 6.0976 | 3.1976 | -3.2976 | -4.2033 | -0.7442 | -2.8773 | 6.22 | -0.3547 | 0.5957 | 0.6377 | 0.9539 | 0.7143 | -130.9764 | -5.5159 | 2.3515 | -0.1248 | -6.5116 | -5.0121 | 1.5935 |  | -0.26 | -1.967 | 4.0133 | 3.3627 | 3.3495 | 1.0384 | 10.6759 | 14.1547 | 14.7153 | 11.0179 | -0.0001 | -0.0031 | 0.0008 | 0.004 | 0.0002 | -0.0006 | 0.0172 | -0.0129 | -0.0005 | -360.1742 | 17.45 | -360.5066 | 17.7046 | -360.8081 | 18.1029 | -360.9066 | 17.5855 | -352.7644 | 18.7395 | -352.7367 | 16.8053
11:59 | 2340 | 28.9742 | 196.8538 | 441.0657 | 446.7796 | -19.2805 | -46.3089 | 6.1817 | 3.2216 | -3.2492 | -4.0904 | -0.691 | -2.8709 | 6.2954 | -0.3486 | 0.5955 | 0.6381 | 0.9535 | 0.7133 | -130.9146 | -5.5053 | 2.3599 | -0.0456 | -6.3767 | -4.9358 | 1.5794 |  | -0.2614 | -1.9511 | 4.0147 | 3.3686 | 3.3502 | 1.0392 | 10.6782 | 14.0992 | 14.6938 | 11.0147 | 0 | -0.0028 | 0.0009 | 0.0039 | 0.0008 | -0.0009 | 0.0074 | -0.0055 | -0.0209 | -360.2019 | 17.4459 | -360.5158 | 17.7149 | -360.8204 | 18.066 | -360.845 | 17.528 | -352.7121 | 18.7395 | -352.7583 | 16.8238
11:59 | 2341 | 28.9663 | 196.9215 | 441.2137 | 446.8832 | -19.3179 | -46.3255 | 6.2302 | 3.2311 | -3.2791 | -4.1593 | -0.6612 | -2.8386 | 6.2132 | -0.4406 | 0.5971 | 0.6397 | 0.9538 | 0.7169 | -130.9775 | -5.6147 | 2.339 | -0.1381 | -6.3791 | -4.8988 | 1.5967 |  | -0.3485 | -2.024 | 4.0146 | 3.3645 | 3.3506 | 1.039 | 10.6781 | 14.1398 | 14.7006 | 11.0259 | -0.0003 | -0.0028 | 0.0007 | 0.0036 | 0.0004 | -0.0007 | 0.0094 | -0.0133 | -0.0203 | -360.1681 | 17.4295 | -360.5404 | 17.7313 | -360.8697 | 18.1132 | -360.9127 | 17.5424 | -352.6998 | 18.723 | -352.789 | 16.8299
11:59 | 2342 | 29.0035 | 196.9149 | 441.182 | 446.9092 | -19.2498 | -46.3852 | 6.2311 | 3.2068 | -3.2897 | -4.0766 | -0.7432 | -2.8698 | 6.3049 | -0.3179 | 0.595 | 0.6414 | 0.9537 | 0.7152 | -130.96 | -5.6089 | 2.4244 | -0.1332 | -6.3237 | -4.9219 | 1.6327 |  | -0.2783 | -1.9427 | 4.0147 | 3.3653 | 3.3511 | 1.0382 | 10.6562 | 14.135 | 14.7067 | 11.0447 | -0.0006 | -0.0028 | 0.0006 | 0.0039 | 0.0009 | -0.0007 | 0.0047 | -0.0058 | -0.0136 | -360.1742 | 17.3925 | -360.4204 | 17.6759 | -360.7989 | 18.1071 | -360.922 | 17.5835 | -352.7183 | 18.6922 | -352.6937 | 16.7991
11:59 | 2343 | 29.0412 | 196.8715 | 441.3649 | 446.9696 | -19.2564 | -46.3145 | 6.1923 | 3.2234 | -3.2181 | -4.0479 | -0.6737 | -2.7752 | 6.2473 | -0.3052 | 0.5964 | 0.6413 | 0.9559 | 0.7131 | -131.0413 | -5.5502 | 2.455 | -0.1186 | -6.3214 | -4.9972 | 1.566 |  | -0.348 | -1.9259 | 4.0149 | 3.364 | 3.3488 | 1.04 | 10.7046 | 14.1667 | 14.7416 | 11.0341 | 0.0002 | -0.0027 | 0.0008 | 0.0038 | 0.0004 | -0.0003 | 0.0021 | 0.0044 | -0.013 | -360.2419 | 17.4521 | -360.5219 | 17.6902 | -360.8174 | 18.1071 | -360.8943 | 17.5937 | -352.7767 | 18.7497 | -352.746 | 16.8012
11:59 | 2344 | 29.0076 | 196.8169 | 441.4027 | 446.9463 | -19.2398 | -46.3522 | 6.1544 | 3.1665 | -3.4118 | -4.0636 | -0.6878 | -2.839 | 6.2573 | -0.2757 | 0.5949 | 0.6422 | 0.9546 | 0.7153 | -131.0393 | -5.6179 | 2.4454 | -0.0707 | -6.3269 | -4.8424 | 1.5899 |  | -0.2233 | -1.9681 | 4.0154 | 3.3657 | 3.3516 | 1.038 | 10.6781 | 14.1687 | 14.7354 | 11.0721 | 0 | -0.003 | 0.0001 | 0.0034 | 0.001 | -0.0005 | -0.0026 | -0.0173 | -0.0268 | -360.1404 | 17.4172 | -360.525 | 17.7169 | -360.8512 | 18.1071 | -360.8697 | 17.5445 | -352.6629 | 18.7128 | -352.746 | 16.8361
11:59 | 2345 | 28.9816 | 196.8617 | 441.3856 | 446.9428 | -19.2276 | -46.3872 | 6.2 | 3.2724 | -3.3333 | -4.0032 | -0.6504 | -2.8087 | 6.219 | -0.3884 | 0.5965 | 0.6391 | 0.9576 | 0.7158 | -131.0681 | -5.6646 | 2.4806 | -0.1614 | -6.4001 | -4.96 | 1.6189 |  | -0.1988 | -1.9366 | 4.0162 | 3.3637 | 3.3494 | 1.0388 | 10.7116 | 14.1389 | 14.7187 | 11.076 | -0.0001 | -0.0026 | 0.0006 | 0.0034 | 0.0004 | -0.0005 | 0.0112 | 0.0032 | -0.0059 | -360.1435 | 17.3966 | -360.4512 | 17.719 | -360.8758 | 18.1522 | -360.9527 | 17.5671 | -352.7244 | 18.7004 | -352.6967 | 16.8238
11:59 | 2346 | 29.0485 | 196.8855 | 441.3958 | 447.0348 | -19.2885 | -46.4357 | 6.1326 | 3.2302 | -3.359 | -4.0303 | -0.7427 | -2.7597 | 6.2899 | -0.3193 | 0.5961 | 0.6416 | 0.9553 | 0.7143 | -130.9923 | -5.6555 | 2.5307 | -0.0754 | -6.3465 | -4.9174 | 1.6127 |  | -0.2621 | -2.0526 | 4.0138 | 3.3635 | 3.3477 | 1.0384 | 10.7024 | 14.1641 | 14.7599 | 11.0558 | -0.0005 | -0.0026 | 0.0002 | 0.0037 | 0.0006 | -0.0011 | 0.02 | -0.0095 | -0.0072 | -360.1896 | 17.4315 | -360.5004 | 17.682 | -360.8174 | 18.105 | -360.9097 | 17.5773 | -352.7244 | 18.7189 | -352.7306 | 16.795
11:59 | 2347 | 28.9669 | 196.887 | 441.5204 | 447.0833 | -19.2558 | -46.4672 | 6.2451 | 3.1873 | -3.3443 | -4.0379 | -0.733 | -2.7615 | 6.3295 | -0.3338 | 0.5953 | 0.6382 | 0.957 | 0.7137 | -130.9974 | -5.7038 | 2.4126 | 0.0955 | -6.3306 | -4.8365 | 1.6576 |  | -0.3265 | -1.992 | 4.0152 | 3.365 | 3.35 | 1.0399 | 10.7071 | 14.1571 | 14.7585 | 11.049 | -0.0004 | -0.0032 | 0.0006 | 0.0035 | 0.0004 | -0.0009 | 0.0095 | -0.0089 | -0.0123 | -360.1619 | 17.4397 | -360.5404 | 17.721 | -360.8481 | 18.0927 | -360.8481 | 17.5301 | -352.7244 | 18.7415 | -352.7983 | 16.834
11:59 | 2348 | 29.0745 | 196.9528 | 441.5002 | 447.0766 | -19.2429 | -46.474 | 6.1704 | 3.2206 | -3.3521 | -4.1503 | -0.7136 | -2.8139 | 6.2879 | -0.332 | 0.5956 | 0.641 | 0.9565 | 0.7161 | -131.0773 | -5.6985 | 2.4681 | -0.145 | -6.2797 | -4.8041 | 1.6576 |  | -0.2481 | -1.9634 | 4.0142 | 3.3664 | 3.3463 | 1.0374 | 10.693 | 14.1667 | 14.7126 | 11.0341 | 0.0003 | -0.0029 | 0.001 | 0.0043 | 0.0003 | -0.0008 | 0.0141 | 0.0041 | 0.0019 | -360.1927 | 17.4254 | -360.5189 | 17.7272 | -360.8974 | 18.1153 | -360.9035 | 17.5445 | -352.6752 | 18.7271 | -352.7244 | 16.8176
11:59 | 2349 | 29.0851 | 196.8003 | 441.5904 | 447.114 | -19.2591 | -46.5128 | 6.1152 | 3.2245 | -3.3348 | -4.1085 | -0.6769 | -2.9132 | 6.1904 | -0.3502 | 0.5954 | 0.6403 | 0.9575 | 0.714 | -131.0898 | -5.6496 | 2.4104 | -0.0989 | -6.2891 | -4.7955 | 1.6829 |  | -0.2329 | -1.9723 | 4.0139 | 3.3659 | 3.3492 | 1.0387 | 10.6966 | 14.1409 | 14.7251 | 11.0443 | -0.0004 | -0.0033 | 0.0003 | 0.0037 | 0.0012 | -0.0006 | -0.0054 | -0.0092 | -0.0091 | -360.2173 | 17.4151 | -360.445 | 17.68 | -360.7927 | 18.1132 | -360.922 | 17.5773 | -352.7367 | 18.7169 | -352.6844 | 16.793
11:59 | 2350 | 29.0579 | 196.8638 | 441.6168 | 447.125 | -19.2767 | -46.4375 | 6.0981 | 3.2742 | -3.2989 | -4.1106 | -0.6653 | -2.9098 | 6.3079 | -0.3345 | 0.5958 | 0.6344 | 0.9535 | 0.714 | -131.1029 | -5.5622 | 2.4193 | -0.1686 | -6.2655 | -4.8459 | 1.6295 |  | -0.22 | -1.9875 | 4.0144 | 3.3674 | 3.3517 | 1.04 | 10.707 | 14.1747 | 14.749 | 11.0078 | -0.0006 | -0.0026 | 0.0007 | 0.0038 | 0.0004 | -0.0004 | 0.0087 | -0.004 | 0.006 | -360.2388 | 17.4521 | -360.5189 | 17.7026 | -360.8635 | 18.0968 | -360.885 | 17.5732 | -352.7737 | 18.7518 | -352.7337 | 16.7991
11:59 | 2351 | 29.1194 | 196.8621 | 441.5921 | 447.0841 | -19.269 | -46.3988 | 6.1229 | 3.3143 | -3.2724 | -4.0561 | -0.6058 | -2.896 | 6.2386 | -0.3758 | 0.5958 | 0.6366 | 0.9513 | 0.7153 | -130.971 | -5.5581 | 2.4796 | -0.0566 | -6.1727 | -4.7591 | 1.6954 |  | -0.2341 | -1.9171 | 4.014 | 3.3623 | 3.3486 | 1.0384 | 10.715 | 14.154 | 14.7691 | 11.033 | -0.0003 | -0.0028 | 0.0012 | 0.004 | 0.001 | -0.0008 | 0.0207 | -0.003 | -0.0154 | -360.1004 | 17.4069 | -360.4912 | 17.7005 | -360.8543 | 18.1255 | -360.8727 | 17.5198 | -352.669 | 18.7004 | -352.7152 | 16.8115
11:59 | 2352 | 29.0955 | 196.8403 | 441.6472 | 447.1702 | -19.1659 | -46.3206 | 6.1211 | 3.3265 | -3.2085 | -4.0551 | -0.56 | -2.9227 | 6.3684 | -0.239 | 0.5964 | 0.6367 | 0.9575 | 0.715 | -131.0264 | -5.5754 | 2.4085 | -0.0537 | -6.2147 | -4.8717 | 1.7009 |  | -0.1885 | -1.8537 | 4.0155 | 3.3624 | 3.3495 | 1.0402 | 10.6944 | 14.1386 | 14.7224 | 11.0537 | 0.0002 | -0.0031 | -0.0002 | 0.003 | 0.0005 | -0.0003 | 0.0145 | -0.0182 | -0.0073 | -360.1927 | 17.3987 | -360.4635 | 17.7005 | -360.8358 | 18.1379 | -360.9681 | 17.5712 | -352.7152 | 18.7066 | -352.6998 | 16.8032
11:59 | 2353 | 29.0313 | 196.8563 | 441.6554 | 447.1697 | -19.145 | -46.1989 | 6.2334 | 3.2719 | -3.2769 | -3.9773 | -0.6253 | -2.8736 | 6.3408 | -0.2007 | 0.5965 | 0.6381 | 0.9528 | 0.7153 | -130.9577 | -5.4906 | 2.4398 | -0.0364 | -6.1876 | -4.8489 | 1.658 |  | -0.2298 | -1.8793 | 4.0154 | 3.3634 | 3.3486 | 1.0384 | 10.6631 | 14.1363 | 14.7207 | 11.0222 | 0 | -0.0034 | 0.001 | 0.0046 | 0.0012 | -0.0005 | 0.0108 | 0.0049 | -0.0124 | -360.1588 | 17.4459 | -360.4819 | 17.6882 | -360.8081 | 18.0865 | -360.8512 | 17.5465 | -352.7121 | 18.7353 | -352.7244 | 16.7991
11:59 | 2354 | 29.0531 | 196.8717 | 441.6334 | 447.137 | -19.1566 | -46.2496 | 6.2689 | 3.3416 | -3.2835 | -4.0475 | -0.6675 | -2.8953 | 6.3013 | -0.4131 | 0.5968 | 0.637 | 0.9561 | 0.7159 | -130.98 | -5.5739 | 2.4581 | -0.0613 | -6.2997 | -4.8361 | 1.6796 |  | -0.2392 | -1.7925 | 4.0131 | 3.3647 | 3.3526 | 1.039 | 10.6851 | 14.1177 | 14.6836 | 11.01 | -0.0004 | -0.0027 | 0.0008 | 0.004 | 0.0005 | -0.0004 | 0.0175 | -0.0085 | -0.0002 | -360.1496 | 17.4397 | -360.5558 | 17.7395 | -360.8789 | 18.1173 | -360.8789 | 17.5342 | -352.6813 | 18.7538 | -352.8137 | 16.8443
11:59 | 2355 | 29.0327 | 196.849 | 441.69 | 447.1994 | -19.2285 | -46.2973 | 6.1149 | 3.365 | -3.3178 | -3.9993 | -0.5825 | -2.8931 | 6.2931 | -0.299 | 0.5971 | 0.6327 | 0.9521 | 0.7154 | -131.0765 | -5.5241 | 2.3866 | 0.0059 | -6.2788 | -4.8315 | 1.6552 |  | -0.2707 | -1.8536 | 4.0129 | 3.365 | 3.3494 | 1.0376 | 10.6734 | 14.1644 | 14.7273 | 11.0031 | -0.0002 | -0.0025 | 0.0006 | 0.0038 | 0.0012 | -0.0004 | 0.0037 | -0.0127 | 0.0115 | -360.1558 | 17.4131 | -360.4666 | 17.6861 | -360.8543 | 18.1235 | -360.922 | 17.5424 | -352.6906 | 18.7107 | -352.6875 | 16.7909
11:59 | 2356 | 29.0346 | 196.8988 | 441.6839 | 447.1818 | -19.1671 | -46.2693 | 6.3013 | 3.4506 | -3.3475 | -4.011 | -0.5747 | -2.8279 | 6.3306 | -0.2595 | 0.5969 | 0.6338 | 0.9551 | 0.7145 | -131.0472 | -5.5823 | 2.4355 | -0.0693 | -6.3542 | -4.9643 | 1.685 |  | -0.2725 | -1.9039 | 4.0136 | 3.3633 | 3.351 | 1.0389 | 10.6771 | 14.1327 | 14.6866 | 11.0136 | -0.0003 | -0.0032 | 0.001 | 0.0038 | 0.0002 | -0.0008 | 0.0005 | -0.0043 | -0.0037 | -360.2204 | 17.4459 | -360.4973 | 17.6759 | -360.7958 | 18.0906 | -360.9158 | 17.5794 | -352.7767 | 18.7497 | -352.7767 | 16.7848
11:59 | 2357 | 28.9933 | 196.8739 | 441.667 | 447.2362 | -19.2326 | -46.2012 | 6.3214 | 3.4577 | -3.2933 | -4.0611 | -0.5413 | -2.8963 | 6.2338 | -0.3254 | 0.5974 | 0.6365 | 0.9556 | 0.7156 | -131.017 | -5.5318 | 2.4642 | -0.0662 | -6.3538 | -4.8555 | 1.5831 |  | -0.3448 | -1.8849 | 4.0146 | 3.3654 | 3.3482 | 1.0381 | 10.7104 | 14.1609 | 14.7589 | 11.0341 | 0.0002 | -0.0029 | 0.0006 | 0.0039 | 0.0003 | -0.0008 | 0.0091 | -0.0194 | -0.0133 | -360.2019 | 17.4336 | -360.5004 | 17.7005 | -360.8697 | 18.0988 | -360.8543 | 17.5506 | -352.7244 | 18.7374 | -352.7552 | 16.8115
11:59 | 2358 | 28.9592 | 196.8838 | 441.7422 | 447.255 | -19.2935 | -46.4159 | 6.2213 | 3.4857 | -3.254 | -4.0033 | -0.5884 | -2.8753 | 6.2611 | -0.3255 | 0.5966 | 0.6371 | 0.9597 | 0.7149 | -131.0252 | -5.5096 | 2.3451 | 0.0364 | -6.2331 | -4.8283 | 1.6703 |  | -0.2639 | -1.7664 | 4.0151 | 3.3631 | 3.3523 | 1.0387 | 10.7161 | 14.1554 | 14.7205 | 11.0391 | 0 | -0.0026 | 0.0011 | 0.0041 | 0.0008 | -0.0003 | 0.0068 | 0.0025 | -0.0025 | -360.1496 | 17.4028 | -360.445 | 17.6923 | -360.8574 | 18.1399 | -360.9189 | 17.5321 | -352.6937 | 18.7148 | -352.7029 | 16.8176
11:59 | 2359 | 28.9327 | 196.8722 | 441.7359 | 447.1879 | -19.3107 | -46.4018 | 6.1419 | 3.5054 | -3.2342 | -4.0492 | -0.5943 | -2.8875 | 6.259 | -0.3311 | 0.5965 | 0.6368 | 0.9527 | 0.7149 | -131.1074 | -5.605 | 2.3165 | -0.0383 | -6.2148 | -4.7809 | 1.7087 |  | -0.2715 | -1.8322 | 4.014 | 3.3631 | 3.351 | 1.0369 | 10.7105 | 14.1724 | 14.7289 | 11.0403 | -0.0004 | -0.0026 | 0.0008 | 0.0037 | 0.0007 | -0.0001 | 0.0234 | 0.0062 | -0.0021 | -360.165 | 17.4131 | -360.5066 | 17.6841 | -360.8297 | 18.1358 | -360.9435 | 17.5753 | -352.7583 | 18.7251 | -352.7213 | 16.8074
11:59 | 2360 | 28.9667 | 196.9136 | 441.7952 | 447.1626 | -19.2724 | -46.3669 | 6.0361 | 3.4682 | -3.1677 | -4.12 | -0.5757 | -2.937 | 6.2735 | -0.3217 | 0.5964 | 0.6393 | 0.9557 | 0.7164 | -131.0781 | -5.5532 | 2.3968 | -0.0395 | -6.196 | -4.7639 | 1.6276 |  | -0.2997 | -1.8799 | 4.0125 | 3.3648 | 3.3488 | 1.0392 | 10.7058 | 14.1504 | 14.7419 | 11.0471 | 0.0001 | -0.0026 | 0.0003 | 0.0031 | 0.0009 | -0.0009 | 0.0123 | 0.0027 | -0.0119 | -360.1835 | 17.4192 | -360.5096 | 17.6985 | -360.8297 | 18.0845 | -360.8635 | 17.5363 | -352.7367 | 18.7353 | -352.7429 | 16.8197
11:59 | 2361 | 29.1469 | 196.9442 | 441.7549 | 447.2858 | -19.3212 | -46.4655 | 5.9685 | 3.5111 | -3.1273 | -4.0848 | -0.5836 | -2.9741 | 6.2338 | -0.3223 | 0.5977 | 0.6399 | 0.956 | 0.7162 | -131.0091 | -5.5646 | 2.4112 | -0.0125 | -6.2099 | -4.8112 | 1.684 |  | -0.2377 | -1.8305 | 4.0145 | 3.365 | 3.3485 | 1.0385 | 10.7141 | 14.1466 | 14.7125 | 11.0331 | 0 | -0.0034 | 0.0005 | 0.0036 | 0.0003 | -0.0007 | 0.0015 | -0.0054 | 0.0047 | -360.1465 | 17.4315 | -360.5373 | 17.7252 | -360.9035 | 18.1214 | -360.9004 | 17.5424 | -352.7121 | 18.7251 | -352.7675 | 16.8423
11:59 | 2362 | 29.0904 | 196.9197 | 441.7335 | 447.2421 | -19.3633 | -46.4137 | 6.0497 | 3.4949 | -3.0337 | -4.1337 | -0.5699 | -2.9287 | 6.3024 | -0.3739 | 0.5974 | 0.6401 | 0.9546 | 0.7164 | -131.051 | -5.5826 | 2.4093 | 0.1202 | -6.1506 | -4.7903 | 1.7678 |  | -0.2213 | -1.7812 | 4.0143 | 3.3649 | 3.3466 | 1.0383 | 10.663 | 14.1654 | 14.6755 | 11.0276 | 0.0001 | -0.0026 | 0.0004 | 0.0035 | 0.0008 | -0.0006 | 0.0091 | -0.0041 | -0.0091 | -360.1373 | 17.3987 | -360.4604 | 17.6759 | -360.8112 | 18.0988 | -360.8912 | 17.5547 | -352.6906 | 18.7128 | -352.6906 | 16.8032
11:59 | 2363 | 29.0883 | 196.8851 | 441.7696 | 447.3011 | -19.3158 | -46.4421 | 6.153 | 3.4683 | -3.0638 | -4.0633 | -0.642 | -2.9865 | 6.2408 | -0.3162 | 0.596 | 0.6383 | 0.9561 | 0.7161 | -131.0596 | -5.5305 | 2.3895 | 0.0762 | -6.1287 | -4.7592 | 1.7741 |  | -0.2668 | -1.8576 | 4.0134 | 3.3615 | 3.3504 | 1.0386 | 10.6792 | 14.1295 | 14.6973 | 11.0208 | -0.0006 | -0.0028 | 0.0008 | 0.004 | 0.0007 | -0.0003 | 0.008 | 0.007 | -0.0208 | -360.2358 | 17.4705 | -360.5466 | 17.6923 | -360.8358 | 18.1132 | -360.9004 | 17.5753 | -352.7644 | 18.7579 | -352.746 | 16.8279
11:59 | 2364 | 29.076 | 196.8957 | 441.8382 | 447.2628 | -19.3241 | -46.3898 | 6.1652 | 3.411 | -3.0419 | -4.1503 | -0.641 | -2.9393 | 6.2919 | -0.3288 | 0.5973 | 0.6346 | 0.9551 | 0.7152 | -131.0269 | -5.4723 | 2.4674 | 0.0377 | -6.1727 | -4.8739 | 1.7847 |  | -0.2558 | -1.7632 | 4.0141 | 3.3612 | 3.3504 | 1.0379 | 10.6713 | 14.1152 | 14.6856 | 11.0024 | -0.0004 | -0.0029 | 0.001 | 0.0045 | 0.0009 | -0.0005 | -0.0059 | -0.0113 | -0.0314 | -360.125 | 17.411 | -360.4912 | 17.7046 | -360.842 | 18.0906 | -360.882 | 17.5506 | -352.6813 | 18.723 | -352.7275 | 16.8299
11:59 | 2365 | 29.0747 | 196.9025 | 441.8172 | 447.3002 | -19.3459 | -46.4603 | 6.2569 | 3.3778 | -3.0391 | -4.2268 | -0.6475 | -3.0035 | 6.198 | -0.3434 | 0.5967 | 0.6364 | 0.9582 | 0.7155 | -131.0407 | -5.5429 | 2.386 | 0.1499 | -6.2029 | -4.7518 | 1.8012 |  | -0.2378 | -1.7701 | 4.0159 | 3.3638 | 3.3534 | 1.0403 | 10.6816 | 14.1549 | 14.6989 | 11.0233 | 0.0001 | -0.0029 | 0.0003 | 0.0032 | 0.0009 | -0.0003 | 0.0105 | -0.0137 | -0.0336 | -360.2142 | 17.4233 | -360.4512 | 17.7026 | -360.8912 | 18.1481 | -360.9466 | 17.5588 | -352.746 | 18.7271 | -352.7121 | 16.8381
11:59 | 2366 | 29.1282 | 197.0303 | 441.8636 | 447.4028 | -19.281 | -46.5282 | 6.2113 | 3.3893 | -3.0468 | -4.1331 | -0.4784 | -2.988 | 6.2094 | -0.4398 | 0.5957 | 0.6359 | 0.9582 | 0.7159 | -131.1402 | -5.5839 | 2.3263 | 0.1927 | -6.1047 | -4.6875 | 1.7963 |  | -0.2381 | -1.9326 | 4.0157 | 3.3625 | 3.345 | 1.038 | 10.7093 | 14.1771 | 14.7286 | 11.0446 | -0.0002 | -0.0033 | 0.0011 | 0.0039 | 0.001 | -0.0005 | 0.0106 | -0.003 | -0.0125 | -360.1588 | 17.411 | -360.4666 | 17.6718 | -360.7927 | 18.1071 | -360.9066 | 17.5527 | -352.6906 | 18.7107 | -352.7029 | 16.7971
11:59 | 2367 | 29.1734 | 196.992 | 441.9093 | 447.4379 | -19.3712 | -46.6276 | 6.1308 | 3.3827 | -3.0466 | -4.1356 | -0.5612 | -2.914 | 6.2235 | -0.3549 | 0.5946 | 0.6362 | 0.9542 | 0.7144 | -131.1524 | -5.6471 | 2.3472 | 0.1535 | -6.2812 | -4.7527 | 1.7142 |  | -0.2586 | -1.8633 | 4.0153 | 3.3634 | 3.348 | 1.0387 | 10.6827 | 14.1157 | 14.7129 | 11.0009 | -0.0003 | -0.0026 | 0.0009 | 0.0042 | 0.0011 | 0.0002 | 0.0192 | -0.0105 | 0.0027 | -360.2142 | 17.4459 | -360.5404 | 17.719 | -360.8758 | 18.105 | -360.9097 | 17.5506 | -352.7275 | 18.7292 | -352.7706 | 16.8505
11:59 | 2368 | 29.2132 | 197.0008 | 442.1126 | 447.5329 | -19.3572 | -46.7067 | 6.1403 | 3.4186 | -3.0265 | -4.0242 | -0.5144 | -2.8387 | 6.284 | -0.2962 | 0.5954 | 0.6361 | 0.9548 | 0.7127 | -131.2302 | -5.5703 | 2.3692 | 0.1368 | -6.2387 | -4.672 | 1.7364 |  | -0.2837 | -1.8699 | 4.015 | 3.3611 | 3.352 | 1.0372 | 10.6805 | 14.1245 | 14.6955 | 10.9826 | -0.0003 | -0.0028 | 0.0006 | 0.0037 | 0.0003 | -0.0008 | 0.0188 | -0.0085 | -0.006 | -360.125 | 17.3966 | -360.4604 | 17.7128 | -360.8604 | 18.1276 | -360.8912 | 17.5219 | -352.6598 | 18.7066 | -352.709 | 16.8361
11:59 | 2369 | 29.1621 | 196.9436 | 441.9454 | 447.526 | -19.3391 | -46.6767 | 6.1834 | 3.4104 | -3.1017 | -4.0302 | -0.6267 | -2.9192 | 6.1982 | -0.2915 | 0.5952 | 0.6361 | 0.9539 | 0.7144 | -131.1943 | -5.6783 | 2.3207 | 0.1718 | -6.1774 | -4.8114 | 1.7892 |  | -0.3288 | -1.8831 | 4.0162 | 3.3643 | 3.3477 | 1.0381 | 10.7094 | 14.1363 | 14.7207 | 11.0454 | 0.0003 | -0.003 | 0.0007 | 0.0039 | 0.0007 | -0.0005 | 0.0161 | -0.0245 | 0.0064 | -360.1958 | 17.4274 | -360.5066 | 17.7128 | -360.8297 | 18.1276 | -360.9158 | 17.5753 | -352.7367 | 18.723 | -352.746 | 16.8299
11:59 | 2370 | 29.2314 | 196.9306 | 441.982 | 447.5644 | -19.4327 | -46.611 | 6.1253 | 3.3158 | -3.1418 | -4.077 | -0.6112 | -2.9547 | 6.2005 | -0.344 | 0.5963 | 0.6355 | 0.954 | 0.7134 | -131.1077 | -5.7305 | 2.3521 | 0.1619 | -6.2328 | -4.878 | 1.6973 |  | -0.2544 | -1.8512 | 4.0155 | 3.3631 | 3.3507 | 1.0373 | 10.6584 | 14.155 | 14.7174 | 11.0634 | 0 | -0.0033 | 0.0006 | 0.004 | 0.0005 | -0.0004 | 0.0034 | -0.0045 | -0.0162 | -360.1988 | 17.4397 | -360.5281 | 17.6923 | -360.8112 | 18.0968 | -360.8758 | 17.5342 | -352.6783 | 18.7415 | -352.7244 | 16.8197
11:59 | 2371 | 29.2059 | 196.9717 | 441.9478 | 447.6031 | -19.375 | -46.6352 | 6.2296 | 3.3895 | -3.0264 | -3.9897 | -0.5952 | -2.9259 | 6.3313 | -0.3415 | 0.5975 | 0.6382 | 0.955 | 0.7152 | -131.1771 | -5.6233 | 2.3138 | -0.0309 | -6.2217 | -4.8366 | 1.6587 |  | -0.2864 | -1.8833 | 4.0153 | 3.3639 | 3.3506 | 1.0379 | 10.6977 | 14.1596 | 14.7449 | 11.045 | -0.0004 | -0.0028 | 0.0007 | 0.004 | 0.0006 | -0.0011 | -0.005 | -0.0184 | -0.0185 | -360.1188 | 17.4192 | -360.5373 | 17.7313 | -360.845 | 18.1029 | -360.8789 | 17.5465 | -352.7121 | 18.7251 | -352.7552 | 16.8505
11:59 | 2372 | 29.1748 | 196.9735 | 441.9642 | 447.6093 | -19.3411 | -46.5209 | 6.2693 | 3.4493 | -3.0327 | -4.0568 | -0.5743 | -2.9989 | 6.2897 | -0.3187 | 0.5965 | 0.6363 | 0.9538 | 0.7149 | -131.1274 | -5.6912 | 2.4389 | 0.1179 | -6.0977 | -4.7688 | 1.8231 |  | -0.2447 | -1.9131 | 4.0163 | 3.3635 | 3.3509 | 1.0373 | 10.6872 | 14.1495 | 14.7368 | 11.0049 | -0.0002 | -0.0026 | 0.0008 | 0.004 | 0.0006 | -0.0001 | -0.0024 | -0.0167 | -0.0018 | -360.1958 | 17.4048 | -360.445 | 17.7046 | -360.8481 | 18.1276 | -360.9189 | 17.5629 | -352.7183 | 18.7148 | -352.6998 | 16.8176
11:59 | 2373 | 29.1782 | 196.9692 | 441.9212 | 447.5898 | -19.2321 | -46.5189 | 6.3722 | 3.4643 | -3.018 | -4.1284 | -0.5904 | -2.9774 | 6.3146 | -0.267 | 0.5973 | 0.6367 | 0.953 | 0.7143 | -131.0814 | -5.6147 | 2.4492 | -0.0425 | -6.1476 | -4.7665 | 1.789 |  | -0.2409 | -1.8542 | 4.0162 | 3.3654 | 3.3513 | 1.0378 | 10.7267 | 14.2059 | 14.7623 | 11.0623 | -0.0005 | -0.0034 | 0.0003 | 0.0037 | 0.0004 | -0.001 | 0.006 | 0.0011 | -0.0062 | -360.1742 | 17.411 | -360.4635 | 17.6738 | -360.7712 | 18.1214 | -360.922 | 17.5547 | -352.7121 | 18.7148 | -352.7121 | 16.8135
11:59 | 2374 | 29.2079 | 197.0253 | 441.9646 | 447.5401 | -19.1742 | -46.5344 | 6.3603 | 3.5491 | -2.9851 | -3.9556 | -0.5402 | -3.0182 | 6.3437 | -0.2431 | 0.5966 | 0.6387 | 0.9543 | 0.716 | -131.0866 | -5.7557 | 2.3769 | 0.0357 | -6.1308 | -4.7526 | 1.7715 |  | -0.2591 | -1.7942 | 4.0157 | 3.362 | 3.3525 | 1.0387 | 10.6919 | 14.1655 | 14.6939 | 11.033 | 0.0001 | -0.0029 | 0.0006 | 0.0039 | 0.0008 | -0.0003 | 0.0235 | 0.0058 | -0.0028 | -360.1958 | 17.4377 | -360.5281 | 17.7334 | -360.8635 | 18.1029 | -360.885 | 17.5588 | -352.6906 | 18.7312 | -352.749 | 16.8505
11:59 | 2375 | 29.1897 | 197.0083 | 441.9388 | 447.5501 | -19.173 | -46.5285 | 6.3511 | 3.4674 | -3.0763 | -4.0984 | -0.6173 | -2.9761 | 6.3503 | -0.2204 | 0.5976 | 0.6378 | 0.9524 | 0.7148 | -131.0591 | -5.7779 | 2.3782 | 0.0206 | -6.1168 | -4.7386 | 1.827 |  | -0.3198 | -1.8505 | 4.0142 | 3.3617 | 3.3509 | 1.0374 | 10.6966 | 14.1756 | 14.7367 | 11.0385 | -0.0005 | -0.0029 | 0.0008 | 0.0039 | 0.0007 | -0.0006 | 0.0101 | -0.0219 | 0.0011 | -360.1034 | 17.3864 | -360.4973 | 17.719 | -360.8635 | 18.1132 | -360.8881 | 17.5198 | -352.6629 | 18.7004 | -352.7029 | 16.8464
11:59 | 2376 | 29.216 | 197.0104 | 442.0194 | 447.6051 | -19.2716 | -46.4944 | 6.2796 | 3.4563 | -3.0016 | -4.0881 | -0.6372 | -2.917 | 6.3819 | -0.2366 | 0.5965 | 0.6372 | 0.9535 | 0.7144 | -130.9543 | -5.6534 | 2.4398 | 0.0193 | -6.1555 | -4.7456 | 1.7818 |  | -0.3585 | -1.8507 | 4.0136 | 3.3643 | 3.3511 | 1.0359 | 10.6862 | 14.1481 | 14.7391 | 11.0276 | -0.0002 | -0.0027 | 0.001 | 0.0037 | 0.0007 | -0.0007 | 0.0332 | -0.0095 | -0.006 | -360.1896 | 17.411 | -360.4942 | 17.7169 | -360.842 | 18.1173 | -360.922 | 17.5671 | -352.7213 | 18.7333 | -352.7121 | 16.8299
11:59 | 2377 | 29.2162 | 196.983 | 442.0605 | 447.6677 | -19.409 | -46.6271 | 6.2223 | 3.4518 | -3.1194 | -4.064 | -0.5972 | -3.0297 | 6.2288 | -0.2372 | 0.5963 | 0.6376 | 0.9541 | 0.7142 | -131.0504 | -5.7119 | 2.3955 | 0.0468 | -6.1372 | -4.7126 | 1.8082 |  | -0.3216 | -1.9125 | 4.0149 | 3.367 | 3.3503 | 1.0376 | 10.7105 | 14.126 | 14.7221 | 11.0291 | 0.0001 | -0.0027 | 0.0006 | 0.0043 | 0.001 | 0.0002 | 0.0122 | -0.0199 | -0.0094 | -360.1773 | 17.4459 | -360.5343 | 17.7046 | -360.7989 | 18.0906 | -360.882 | 17.5465 | -352.7121 | 18.7518 | -352.7644 | 16.8156
11:59 | 2378 | 29.1637 | 196.9735 | 442.0233 | 447.6395 | -19.4263 | -46.6007 | 6.1503 | 3.421 | -3.0783 | -4.0582 | -0.617 | -3.0612 | 6.1951 | -0.3504 | 0.598 | 0.6398 | 0.9521 | 0.7139 | -131.1273 | -5.7713 | 2.3188 | -0.0117 | -6.0606 | -4.7929 | 1.7754 |  | -0.3041 | -2.0295 | 4.0149 | 3.366 | 3.3531 | 1.0369 | 10.7047 | 14.1608 | 14.7405 | 11.0229 | 0.0001 | -0.0032 | 0.0005 | 0.004 | 0.0007 | -0.0009 | 0.0069 | -0.0048 | -0.0063 | -360.1342 | 17.4131 | -360.4973 | 17.7169 | -360.8327 | 18.1009 | -360.8789 | 17.5445 | -352.7152 | 18.7292 | -352.7552 | 16.8402
11:59 | 2379 | 29.2045 | 196.9589 | 442.0155 | 447.6322 | -19.3875 | -46.6416 | 6.2628 | 3.4466 | -3.0133 | -4.0949 | -0.5894 | -3.0545 | 6.2624 | -0.2509 | 0.5966 | 0.6357 | 0.9559 | 0.7137 | -131.0577 | -5.7735 | 2.4214 | -0.0641 | -6.0952 | -4.7691 | 1.8262 |  | -0.3124 | -2.0603 | 4.0147 | 3.3609 | 3.3499 | 1.0376 | 10.6793 | 14.1409 | 14.702 | 11.0443 | 0.0001 | -0.0038 | 0.0005 | 0.0038 | 0.0006 | -0.0001 | 0.0112 | -0.0138 | 0.0136 | -360.1927 | 17.4192 | -360.4696 | 17.7108 | -360.8543 | 18.1358 | -360.9251 | 17.5588 | -352.6937 | 18.7333 | -352.6937 | 16.8238
11:59 | 2380 | 29.2038 | 196.9713 | 442.0722 | 447.6472 | -19.4306 | -46.6868 | 6.1839 | 3.4197 | -3.0065 | -4.0102 | -0.6121 | -2.9912 | 6.325 | -0.2492 | 0.5971 | 0.6348 | 0.9541 | 0.715 | -131.059 | -5.8 | 2.4487 | -0.047 | -6.0989 | -4.6318 | 1.8504 |  | -0.2836 | -1.9974 | 4.0154 | 3.3624 | 3.3526 | 1.038 | 10.7071 | 14.1396 | 14.7343 | 11.032 | -0.0005 | -0.0027 | -0.0001 | 0.0036 | 0.0006 | -0.0008 | 0.0118 | -0.015 | 0.0042 | -360.1558 | 17.411 | -360.4912 | 17.6964 | -360.802 | 18.1091 | -360.9097 | 17.5465 | -352.6906 | 18.7107 | -352.6906 | 16.8053
11:59 | 2381 | 29.1468 | 196.9506 | 442.0526 | 447.5911 | -19.3631 | -46.6332 | 6.1802 | 3.3957 | -2.9335 | -4.0537 | -0.5515 | -3.0571 | 6.2553 | -0.2576 | 0.5975 | 0.6375 | 0.9528 | 0.7152 | -131.0244 | -5.7653 | 2.4838 | -0.0521 | -6.086 | -4.8167 | 1.8118 |  | -0.3719 | -2.0056 | 4.0146 | 3.3623 | 3.3538 | 1.0367 | 10.6712 | 14.1328 | 14.7398 | 11.0363 | 0 | -0.0026 | 0 | 0.0032 | 0.0004 | -0.0004 | 0.0005 | -0.0187 | -0.0069 | -360.1927 | 17.4151 | -360.5127 | 17.7293 | -360.845 | 18.0988 | -360.885 | 17.5486 | -352.7121 | 18.7395 | -352.7244 | 16.8381
11:59 | 2382 | 29.144 | 196.9954 | 442.034 | 447.5985 | -19.4003 | -46.6554 | 6.1966 | 3.3563 | -3.056 | -4.1304 | -0.594 | -3.044 | 6.312 | -0.2274 | 0.5971 | 0.6378 | 0.9549 | 0.7149 | -130.9723 | -5.6556 | 2.4065 | 0.0003 | -6.1143 | -4.7321 | 1.7085 |  | -0.2777 | -1.9596 | 4.0143 | 3.3637 | 3.3535 | 1.0369 | 10.7025 | 14.1524 | 14.7415 | 11.0273 | -0.0001 | -0.0032 | 0.0007 | 0.0037 | 0.001 | -0.0008 | 0.0016 | -0.003 | -0.0341 | -360.1527 | 17.4192 | -360.5404 | 17.7252 | -360.8758 | 18.1276 | -360.8881 | 17.5363 | -352.6875 | 18.7292 | -352.7275 | 16.8402
11:59 | 2383 | 29.1804 | 196.9976 | 441.9991 | 447.6418 | -19.3503 | -46.5875 | 6.1346 | 3.4334 | -3.084 | -4.1496 | -0.5742 | -2.9684 | 6.3746 | -0.1633 | 0.5966 | 0.6353 | 0.9543 | 0.715 | -130.966 | -5.7204 | 2.4588 | 0.0787 | -6.1655 | -4.8053 | 1.8233 |  | -0.3054 | -1.9572 | 4.0153 | 3.3631 | 3.3523 | 1.0374 | 10.7034 | 14.1483 | 14.7586 | 11.0327 | 0.0002 | -0.0027 | 0.0012 | 0.004 | 0.0008 | -0.0004 | 0.0226 | 0.001 | 0.0003 | -360.1804 | 17.4007 | -360.4481 | 17.6944 | -360.8174 | 18.1071 | -360.8974 | 17.5465 | -352.6875 | 18.7148 | -352.7029 | 16.8074
11:59 | 2384 | 29.2337 | 197.0242 | 442.0311 | 447.7088 | -19.2798 | -46.583 | 6.1938 | 3.4096 | -3.0036 | -4.0752 | -0.4632 | -2.9794 | 6.3127 | -0.2547 | 0.5981 | 0.6363 | 0.9573 | 0.7153 | -130.9226 | -5.5356 | 2.4268 | 0.0562 | -6.1341 | -4.7509 | 1.7115 |  | -0.31 | -1.97 | 4.0154 | 3.3612 | 3.3477 | 1.0379 | 10.693 | 14.1667 | 14.7358 | 11.0572 | -0.0004 | -0.0028 | 0.0008 | 0.0035 | 0.0006 | -0.0009 | 0.0069 | -0.0164 | 0.0058 | -360.205 | 17.4418 | -360.5466 | 17.7026 | -360.8358 | 18.1194 | -360.9158 | 17.565 | -352.7367 | 18.7477 | -352.746 | 16.8402
11:59 | 2385 | 29.1548 | 197.0762 | 442.0928 | 447.6935 | -19.2955 | -46.5162 | 6.1418 | 3.4456 | -2.9922 | -4.1168 | -0.4264 | -2.9723 | 6.2787 | -0.1734 | 0.5979 | 0.6356 | 0.9547 | 0.7152 | -131.0132 | -5.5762 | 2.4251 | 0.0535 | -6.0883 | -4.7346 | 1.7268 |  | -0.3217 | -1.964 | 4.0158 | 3.3605 | 3.3529 | 1.0386 | 10.7058 | 14.1678 | 14.7303 | 11.0645 | -0.0003 | -0.0027 | 0.0004 | 0.0036 | 0.0006 | -0.0005 | -0.0015 | 0.0087 | -0.0052 | -360.1681 | 17.409 | -360.4727 | 17.7087 | -360.8266 | 18.1029 | -360.8727 | 17.5424 | -352.6967 | 18.723 | -352.6967 | 16.8258
11:59 | 2386 | 29.2733 | 197.1291 | 442.1093 | 447.6932 | -19.3624 | -46.5152 | 6.1558 | 3.4792 | -3.0029 | -4.1183 | -0.3641 | -2.8891 | 6.4118 | -0.1477 | 0.5973 | 0.6353 | 0.9524 | 0.7159 | -131.0403 | -5.6119 | 2.3492 | 0.0561 | -6.0741 | -4.7353 | 1.7398 |  | -0.284 | -2.0271 | 4.0139 | 3.3613 | 3.3509 | 1.0382 | 10.7012 | 14.1747 | 14.749 | 11.0367 | 0.0001 | -0.0028 | 0.0007 | 0.0038 | 0.0006 | -0.0004 | 0.0187 | -0.0016 | 0.0118 | -360.1742 | 17.4172 | -360.4881 | 17.7149 | -360.8235 | 18.1296 | -360.8974 | 17.5506 | -352.6906 | 18.7333 | -352.7337 | 16.8258
11:59 | 2387 | 29.1883 | 197.029 | 442.2018 | 447.6701 | -19.4293 | -46.5231 | 6.1971 | 3.4184 | -3.0058 | -4.035 | -0.352 | -2.9404 | 6.3867 | -0.2655 | 0.5974 | 0.6354 | 0.9535 | 0.7149 | -130.9899 | -5.5428 | 2.4488 | -0.0521 | -6.176 | -4.8341 | 1.6664 |  | -0.2306 | -1.9814 | 4.0126 | 3.3622 | 3.3464 | 1.0374 | 10.6956 | 14.1338 | 14.7517 | 11.0667 | 0 | -0.0031 | 0.0004 | 0.0038 | 0.0008 | -0.0006 | 0.0091 | -0.0132 | -0.0166 | -360.2019 | 17.411 | -360.5066 | 17.6985 | -360.8389 | 18.1071 | -360.8974 | 17.5568 | -352.6967 | 18.7251 | -352.7337 | 16.8299
12:00 | 2388 | 29.2521 | 197.0308 | 442.0638 | 447.6811 | -19.3499 | -46.4574 | 6.2122 | 3.3906 | -3.1254 | -3.9985 | -0.3445 | -2.8843 | 6.4145 | -0.2629 | 0.5978 | 0.6381 | 0.9537 | 0.7167 | -131.0073 | -5.6173 | 2.443 | -0.0561 | -6.1736 | -4.7489 | 1.6879 |  | -0.2968 | -2.053 | 4.0139 | 3.3634 | 3.3519 | 1.0377 | 10.6921 | 14.1362 | 14.7197 | 11.0111 | -0.0003 | -0.0029 | 0.0003 | 0.0036 | 0.0004 | -0.0001 | 0.0015 | -0.0013 | -0.0079 | -360.1804 | 17.4192 | -360.5127 | 17.6964 | -360.8143 | 18.1091 | -360.8604 | 17.5527 | -352.706 | 18.7292 | -352.7244 | 16.8299
12:00 | 2389 | 29.2499 | 197.0297 | 442.1692 | 447.6922 | -19.3828 | -46.4871 | 6.1548 | 3.4936 | -3.0922 | -3.8889 | -0.2628 | -2.8691 | 6.4879 | -0.2318 | 0.5969 | 0.6378 | 0.9529 | 0.7159 | -130.9924 | -5.5798 | 2.473 | 0.0304 | -6.1211 | -4.8072 | 1.8225 |  | -0.1965 | -1.9593 | 4.0134 | 3.366 | 3.348 | 1.038 | 10.6551 | 14.1454 | 14.6822 | 11.0205 | -0.0003 | -0.0027 | 0.0007 | 0.0037 | 0.0007 | -0.0009 | -0.0001 | -0.0137 | -0.0151 | -360.1988 | 17.4233 | -360.485 | 17.7128 | -360.8604 | 18.1029 | -360.9127 | 17.5588 | -352.6844 | 18.7292 | -352.7429 | 16.834
12:00 | 2390 | 29.2543 | 197.0231 | 442.1012 | 447.6662 | -19.3949 | -46.4445 | 6.2229 | 3.4438 | -3.0792 | -3.9041 | -0.2709 | -2.8993 | 6.4227 | -0.2147 | 0.5975 | 0.6359 | 0.9561 | 0.7151 | -130.9995 | -5.5599 | 2.521 | 0.103 | -6.1681 | -4.82 | 1.755 |  | -0.2217 | -1.9581 | 4.0154 | 3.3673 | 3.3488 | 1.0379 | 10.6862 | 14.1596 | 14.7334 | 11.0392 | -0.0005 | -0.003 | 0.0005 | 0.0036 | 0.0008 | -0.0002 | 0.0064 | -0.0092 | -0.0144 | -360.1711 | 17.411 | -360.485 | 17.6882 | -360.802 | 18.1091 | -360.9066 | 17.5424 | -352.6967 | 18.723 | -352.7152 | 16.8115
12:00 | 2391 | 29.2874 | 197.0221 | 442.1443 | 447.6542 | -19.29 | -46.3415 | 6.3395 | 3.4692 | -3.1273 | -3.8244 | -0.2152 | -2.8991 | 6.4292 | -0.1143 | 0.596 | 0.6384 | 0.9547 | 0.7169 | -131.0814 | -5.6794 | 2.3842 | 0.07 | -6.1771 | -4.8119 | 1.7274 |  | -0.2005 | -1.9856 | 4.0143 | 3.3635 | 3.3507 | 1.0375 | 10.7011 | 14.1575 | 14.7327 | 11.0132 | 0.0002 | -0.003 | 0.001 | 0.0043 | 0.0009 | -0.0006 | 0.0241 | -0.0153 | 0.0126 | -360.205 | 17.4295 | -360.5189 | 17.7149 | -360.845 | 18.1194 | -360.922 | 17.5712 | -352.7152 | 18.7415 | -352.7583 | 16.8423
12:00 | 2392 | 29.3215 | 197.0641 | 442.0695 | 447.7407 | -19.2815 | -46.31 | 6.3035 | 3.4859 | -3.0946 | -3.9628 | -0.3051 | -2.905 | 6.3181 | -0.1276 | 0.5971 | 0.641 | 0.9544 | 0.7156 | -131.1489 | -5.7229 | 2.3612 | 0.0897 | -6.0849 | -4.9096 | 1.7896 |  | -0.2783 | -1.9418 | 4.0149 | 3.3646 | 3.3547 | 1.0377 | 10.7336 | 14.1899 | 14.7705 | 11.0861 | -0.0004 | -0.003 | 0.0009 | 0.0036 | 0.0006 | -0.0001 | 0.02 | -0.0006 | 0.0035 | -360.1773 | 17.4213 | -360.4942 | 17.7005 | -360.8081 | 18.1214 | -360.8727 | 17.5486 | -352.6721 | 18.721 | -352.7244 | 16.8217
12:00 | 2393 | 29.2847 | 196.9673 | 442.0532 | 447.6885 | -19.2499 | -46.2774 | 6.4005 | 3.4699 | -3.1219 | -4.0593 | -0.2913 | -2.857 | 6.4118 | -0.1034 | 0.5964 | 0.6427 | 0.9542 | 0.7155 | -131.1074 | -5.6511 | 2.361 | 0.0191 | -6.1353 | -4.8234 | 1.7553 |  | -0.2452 | -1.8831 | 4.0144 | 3.3661 | 3.35 | 1.0379 | 10.7093 | 14.1713 | 14.7691 | 11.0215 | -0.0004 | -0.0026 | 0.0003 | 0.0038 | 0.0008 | -0.0007 | -0.0001 | -0.0108 | -0.0232 | -360.1773 | 17.4192 | -360.4819 | 17.7046 | -360.8697 | 18.1399 | -360.9066 | 17.5671 | -352.7183 | 18.7271 | -352.7152 | 16.8402
12:00 | 2394 | 29.2679 | 197.0108 | 442.0322 | 447.6024 | -19.2833 | -46.2439 | 6.335 | 3.4807 | -3.1988 | -3.9315 | -0.3219 | -2.893 | 6.363 | -0.1404 | 0.5973 | 0.6363 | 0.9565 | 0.7146 | -131.1168 | -5.7027 | 2.4802 | 0.0225 | -6.1818 | -4.9008 | 1.7426 |  | -0.2065 | -1.8322 | 4.0152 | 3.3634 | 3.3532 | 1.0385 | 10.729 | 14.1909 | 14.7245 | 11.0471 | -0.0005 | -0.003 | 0.0008 | 0.0038 | 0.0005 | -0.0005 | 0.0092 | -0.0135 | -0.0173 | -360.1804 | 17.4274 | -360.485 | 17.6882 | -360.8174 | 18.144 | -360.9127 | 17.5609 | -352.706 | 18.7271 | -352.6998 | 16.8135
12:00 | 2395 | 29.2829 | 197.0031 | 442.1609 | 447.6865 | -19.2331 | -46.239 | 6.3733 | 3.4371 | -3.1407 | -3.8264 | -0.3145 | -2.9105 | 6.4186 | -0.0563 | 0.5974 | 0.6388 | 0.9566 | 0.7151 | -131.1266 | -5.6875 | 2.3584 | 0.1519 | -6.2403 | -4.8353 | 1.7747 |  | -0.3158 | -1.9317 | 4.0159 | 3.3649 | 3.354 | 1.0374 | 10.6759 | 14.149 | 14.7095 | 11.0179 | 0.0001 | -0.0029 | 0.0005 | 0.0038 | 0.001 | -0.0003 | 0.019 | -0.0057 | 0.008 | -360.1342 | 17.4131 | -360.5096 | 17.7108 | -360.8327 | 18.1296 | -360.9004 | 17.5506 | -352.6998 | 18.723 | -352.746 | 16.8423
12:00 | 2396 | 29.3178 | 197.0586 | 442.0632 | 447.7002 | -19.3416 | -46.2697 | 6.422 | 3.3755 | -3.1953 | -3.9371 | -0.3644 | -2.9295 | 6.3609 | -0.057 | 0.5963 | 0.6371 | 0.9574 | 0.7154 | -131.0306 | -5.7298 | 2.4412 | 0.1802 | -6.1641 | -4.7745 | 1.8241 |  | -0.2452 | -2.0196 | 4.015 | 3.3643 | 3.3556 | 1.0371 | 10.6944 | 14.1386 | 14.7224 | 11.0306 | 0 | -0.0031 | 0.0009 | 0.0042 | 0.0007 | -0.0012 | 0.0157 | -0.0014 | 0.0004 | -360.1681 | 17.4254 | -360.5004 | 17.719 | -360.8789 | 18.1604 | -360.9066 | 17.5465 | -352.6906 | 18.7333 | -352.7614 | 16.834
12:00 | 2397 | 29.3158 | 197.0458 | 442.1948 | 447.7749 | -19.3102 | -46.2761 | 6.4435 | 3.4507 | -3.1081 | -3.9343 | -0.3812 | -2.9115 | 6.4001 | -0.0821 | 0.5963 | 0.6385 | 0.9568 | 0.7161 | -131.1089 | -5.642 | 2.3376 | 0.1603 | -6.1088 | -4.6431 | 1.8385 |  | -0.2697 | -2.0119 | 4.0152 | 3.3648 | 3.3513 | 1.0371 | 10.6759 | 14.1432 | 14.7268 | 11.0064 | -0.0006 | -0.0029 | 0.0012 | 0.0041 | 0.0004 | -0.0001 | 0.0218 | -0.0014 | 0.0074 | -360.1465 | 17.4172 | -360.4696 | 17.6882 | -360.8081 | 18.1481 | -360.9035 | 17.5527 | -352.6906 | 18.7271 | -352.6844 | 16.8115
12:00 | 2398 | 29.3412 | 197.0714 | 442.1634 | 447.7478 | -19.2625 | -46.2626 | 6.4487 | 3.5126 | -3.1414 | -3.8649 | -0.3522 | -2.929 | 6.3866 | -0.202 | 0.5983 | 0.638 | 0.9571 | 0.7168 | -131.1082 | -5.6243 | 2.46 | 0.0656 | -6.1727 | -4.8333 | 1.8503 |  | -0.291 | -2.0485 | 4.0156 | 3.3642 | 3.3543 | 1.0393 | 10.6883 | 14.1971 | 14.7393 | 11.0287 | -0.0002 | -0.0023 | 0.0005 | 0.0041 | 0.0011 | -0.0005 | 0.0268 | -0.0109 | 0.0047 | -360.2142 | 17.448 | -360.5373 | 17.7046 | -360.8235 | 18.1379 | -360.9097 | 17.5609 | -352.7583 | 18.7477 | -352.7583 | 16.8238
12:00 | 2399 | 29.3683 | 197.1222 | 442.176 | 447.7567 | -19.2642 | -46.398 | 6.3703 | 3.5948 | -3.0561 | -3.9593 | -0.2845 | -2.8745 | 6.4669 | -0.0749 | 0.5969 | 0.638 | 0.9525 | 0.7151 | -131.1188 | -5.708 | 2.3325 | 0.1404 | -6.1066 | -4.8066 | 1.8228 |  | -0.2746 | -2.0607 | 4.015 | 3.3623 | 3.3502 | 1.0376 | 10.6943 | 14.1561 | 14.7466 | 11.0244 | 0.0001 | -0.0031 | 0.0008 | 0.0043 | 0.0006 | -0.0005 | 0.0216 | -0.0269 | 0.0149 | -360.1681 | 17.4131 | -360.485 | 17.6985 | -360.7897 | 18.1235 | -360.8789 | 17.528 | -352.6721 | 18.7189 | -352.7337 | 16.8299
12:00 | 2400 | 29.3044 | 197.0705 | 442.1812 | 447.7449 | -19.2383 | -46.4082 | 6.4176 | 3.5336 | -3.149 | -3.9452 | -0.2691 | -2.895 | 6.4794 | -0.0235 | 0.5963 | 0.6349 | 0.9539 | 0.717 | -131.0935 | -5.7299 | 2.435 | 0.0097 | -6.1461 | -4.7669 | 1.7973 |  | -0.3014 | -2.0091 | 4.0151 | 3.3626 | 3.3543 | 1.0368 | 10.7022 | 14.1936 | 14.7525 | 11.0254 | 0 | -0.003 | 0.001 | 0.0036 | 0.001 | -0.0005 | -0.0022 | -0.0153 | -0.0161 | -360.2296 | 17.4233 | -360.4758 | 17.7149 | -360.8604 | 18.1666 | -360.9004 | 17.5424 | -352.6967 | 18.7189 | -352.7337 | 16.834
12:00 | 2401 | 29.3274 | 197.0432 | 442.0556 | 447.7386 | -19.1724 | -46.3297 | 6.4562 | 3.4703 | -3.1686 | -4.0046 | -0.3641 | -2.9105 | 6.3422 | -0.0451 | 0.5963 | 0.6367 | 0.9529 | 0.7155 | -131.08 | -5.6703 | 2.3123 | -0.1053 | -6.0897 | -4.8776 | 1.7798 |  | -0.2494 | -2.0311 | 4.0147 | 3.3631 | 3.3498 | 1.036 | 10.7 | 14.162 | 14.7361 | 11.0298 | -0.0001 | -0.0026 | 0.0002 | 0.0037 | 0.0007 | -0.0004 | 0.0137 | -0.0133 | -0.0214 | -360.1742 | 17.3987 | -360.4573 | 17.6656 | -360.7958 | 18.1481 | -360.9343 | 17.5363 | -352.6906 | 18.7025 | -352.6906 | 16.8032
12:00 | 2402 | 29.4189 | 197.0766 | 442.1362 | 447.8386 | -19.1511 | -46.3246 | 6.5375 | 3.4372 | -3.1925 | -4.0008 | -0.4047 | -2.8377 | 6.4604 | -0.0187 | 0.5975 | 0.6379 | 0.9575 | 0.715 | -131.0174 | -5.6394 | 2.3502 | -0.1096 | -6.1435 | -4.8341 | 1.6964 |  | -0.2401 | -1.957 | 4.0155 | 3.3644 | 3.3515 | 1.0372 | 10.6667 | 14.1914 | 14.709 | 11.0039 | -0.0005 | -0.0028 | 0.0007 | 0.0038 | 0.0005 | -0.001 | -0.0018 | -0.0052 | -0.0163 | -360.1896 | 17.4418 | -360.5343 | 17.7005 | -360.8327 | 18.1502 | -360.8974 | 17.5424 | -352.7275 | 18.7353 | -352.7337 | 16.8361
12:00 | 2403 | 29.4075 | 197.1732 | 442.1881 | 447.9268 | -19.2061 | -46.2109 | 6.548 | 3.5433 | -3.2305 | -3.9126 | -0.276 | -2.9795 | 6.394 | -0.0674 | 0.5974 | 0.636 | 0.9576 | 0.7153 | -131.0978 | -5.7183 | 2.2799 | -0.0763 | -6.1008 | -4.7965 | 1.7355 |  | -0.2237 | -1.8246 | 4.0155 | 3.3622 | 3.353 | 1.0375 | 10.6839 | 14.1572 | 14.7248 | 11.0428 | 0.0002 | -0.0031 | 0.0003 | 0.0034 | 0.0008 | -0.0001 | 0.0061 | -0.0022 | 0.0006 | -360.1435 | 17.4069 | -360.5035 | 17.7169 | -360.8327 | 18.1194 | -360.8543 | 17.5157 | -352.6475 | 18.7148 | -352.7367 | 16.8505
12:00 | 2404 | 29.3501 | 197.1741 | 442.2176 | 447.8299 | -19.2192 | -46.1796 | 6.5015 | 3.5815 | -3.2249 | -3.9143 | -0.347 | -2.9723 | 6.3963 | -0.1253 | 0.5957 | 0.6338 | 0.9545 | 0.7149 | -131.0414 | -5.7038 | 2.3935 | -0.1249 | -6.1039 | -4.8406 | 1.7464 |  | -0.2292 | -1.8735 | 4.0155 | 3.3674 | 3.3502 | 1.037 | 10.6736 | 14.1233 | 14.6999 | 11.0219 | -0.0001 | -0.0036 | 0.0004 | 0.0036 | 0.0004 | -0.0008 | 0.013 | -0.0059 | -0.0044 | -360.1373 | 17.4315 | -360.525 | 17.7067 | -360.8789 | 18.181 | -360.9066 | 17.5342 | -352.7244 | 18.7374 | -352.7275 | 16.8423
12:00 | 2405 | 29.3875 | 197.0428 | 442.1515 | 447.8727 | -19.2262 | -46.1552 | 6.6425 | 3.5954 | -3.2266 | -3.8901 | -0.3587 | -3.0199 | 6.3502 | -0.165 | 0.5965 | 0.6372 | 0.9554 | 0.7155 | -131.1012 | -5.7878 | 2.3283 | -0.0455 | -6.1252 | -4.8009 | 1.7908 |  | -0.2727 | -1.816 | 4.0166 | 3.3656 | 3.3531 | 1.0384 | 10.6537 | 14.1562 | 14.7129 | 11.0182 | 0.0001 | -0.0025 | 0.001 | 0.0044 | 0.0007 | -0.0003 | -0.0024 | -0.0148 | -0.0157 | -360.1742 | 17.409 | -360.4758 | 17.6697 | -360.7897 | 18.142 | -360.8727 | 17.5383 | -352.709 | 18.7312 | -352.7029 | 16.8115
12:00 | 2406 | 29.4036 | 197.0353 | 442.2478 | 447.8475 | -19.1913 | -46.1117 | 6.5595 | 3.5209 | -3.28 | -3.905 | -0.3307 | -3.0315 | 6.4038 | -0.1599 | 0.597 | 0.6414 | 0.9574 | 0.7144 | -131.044 | -5.7524 | 2.3618 | -0.0912 | -6.184 | -4.7679 | 1.7213 |  | -0.2101 | -1.8102 | 4.0158 | 3.3632 | 3.3514 | 1.0378 | 10.7034 | 14.1772 | 14.776 | 11.0327 | -0.0002 | -0.0027 | 0.0007 | 0.0038 | 0.0005 | -0.0008 | 0.0104 | -0.0192 | 0.0098 | -360.2204 | 17.4521 | -360.5343 | 17.7128 | -360.845 | 18.1214 | -360.8727 | 17.5486 | -352.7398 | 18.7723 | -352.7644 | 16.834
12:00 | 2407 | 29.4061 | 197.0056 | 442.173 | 447.9034 | -19.0945 | -46.1332 | 6.5805 | 3.5894 | -3.1027 | -3.8339 | -0.169 | -3.0131 | 6.3144 | -0.1481 | 0.5955 | 0.6371 | 0.9562 | 0.7165 | -131.0929 | -5.7236 | 2.416 | 0.0246 | -6.2497 | -4.818 | 1.7209 |  | -0.2423 | -1.9334 | 4.0166 | 3.3634 | 3.352 | 1.0385 | 10.714 | 14.1872 | 14.7657 | 11.0501 | -0.0002 | -0.0031 | 0.0004 | 0.0037 | 0.0006 | -0.0009 | -0.0024 | -0.0068 | -0.0014 | -360.1404 | 17.4028 | -360.4881 | 17.6861 | -360.8235 | 18.142 | -360.8635 | 17.5055 | -352.6537 | 18.721 | -352.6967 | 16.832
12:00 | 2408 | 29.3797 | 197.0383 | 442.2803 | 447.9008 | -19.1616 | -46.1781 | 6.6019 | 3.5865 | -3.0963 | -3.9112 | -0.268 | -3.0002 | 6.3611 | -0.1094 | 0.5963 | 0.6377 | 0.9563 | 0.7138 | -131.0714 | -5.7713 | 2.3604 | 0.087 | -6.2652 | -4.8093 | 1.7083 |  | -0.2874 | -1.9865 | 4.0145 | 3.3637 | 3.3495 | 1.038 | 10.7231 | 14.1623 | 14.7672 | 11.0233 | 0.0003 | -0.0031 | 0.0008 | 0.0037 | 0.0005 | -0.0003 | 0.008 | -0.0127 | -0.0145 | -360.1988 | 17.4172 | -360.4666 | 17.6923 | -360.8512 | 18.1625 | -360.9497 | 17.5588 | -352.7521 | 18.7374 | -352.6967 | 16.8217
12:00 | 2409 | 29.4048 | 197.0692 | 442.2703 | 447.9705 | -19.1614 | -46.2757 | 6.5352 | 3.6473 | -3.0447 | -3.7725 | -0.1951 | -3.0673 | 6.4159 | -0.1157 | 0.5962 | 0.641 | 0.955 | 0.7162 | -131.0316 | -5.6554 | 2.4436 | 0.1506 | -6.1711 | -4.7967 | 1.7196 |  | -0.2095 | -1.9226 | 4.0143 | 3.3649 | 3.3482 | 1.0382 | 10.7256 | 14.1639 | 14.7472 | 11.0504 | -0.0005 | -0.0031 | 0.0003 | 0.003 | 0.0009 | -0.0007 | 0.004 | -0.0137 | -0.0227 | -360.1711 | 17.4233 | -360.4573 | 17.6636 | -360.7681 | 18.1337 | -360.8912 | 17.5301 | -352.6937 | 18.7415 | -352.6906 | 16.8074
12:00 | 2410 | 29.4185 | 197.0484 | 442.2941 | 447.8921 | -19.2589 | -46.2941 | 6.4925 | 3.6262 | -3.0247 | -3.8554 | -0.2776 | -2.9982 | 6.3947 | -0.0014 | 0.5956 | 0.6382 | 0.9593 | 0.7155 | -131.0923 | -5.6774 | 2.4805 | 0.1276 | -6.2024 | -4.747 | 1.7594 |  | -0.2 | -1.9123 | 4.0143 | 3.3641 | 3.3499 | 1.0375 | 10.6735 | 14.1467 | 14.7136 | 11.0269 | -0.0007 | -0.0026 | 0.0009 | 0.0041 | 0.0005 | 0 | 0.0194 | -0.0135 | 0.0147 | -360.1927 | 17.4356 | -360.5435 | 17.7272 | -360.9035 | 18.1481 | -360.8943 | 17.5301 | -352.7029 | 18.7497 | -352.7706 | 16.8525
12:00 | 2411 | 29.4635 | 197.1093 | 442.2231 | 447.9211 | -19.2693 | -46.2683 | 6.4565 | 3.527 | -3.0784 | -3.9095 | -0.3627 | -3.0208 | 6.3632 | -0.096 | 0.596 | 0.6378 | 0.9561 | 0.7148 | -131.0633 | -5.8078 | 2.4145 | 0.0879 | -6.1281 | -4.7225 | 1.7292 |  | -0.2691 | -1.9501 | 4.0138 | 3.3664 | 3.3483 | 1.0376 | 10.6701 | 14.1547 | 14.7037 | 11.0179 | -0.0003 | -0.0031 | 0.001 | 0.0044 | 0.0009 | -0.0006 | 0.0101 | -0.0028 | 0.0001 | -360.1373 | 17.3905 | -360.4635 | 17.6985 | -360.8604 | 18.1666 | -360.8912 | 17.5075 | -352.6598 | 18.7066 | -352.6967 | 16.834
12:00 | 2412 | 29.5153 | 197.1018 | 442.2781 | 447.9861 | -19.2667 | -46.3399 | 6.496 | 3.6484 | -3.0891 | -3.9463 | -0.395 | -2.955 | 6.4331 | 0.0222 | 0.5956 | 0.6359 | 0.9515 | 0.7159 | -131.0267 | -5.6549 | 2.3928 | 0.1664 | -6.1084 | -4.5991 | 1.7795 |  | -0.2328 | -2.0178 | 4.0151 | 3.3643 | 3.3497 | 1.0376 | 10.6679 | 14.1232 | 14.7104 | 11.0165 | -0.0001 | -0.0032 | 0.0005 | 0.0038 | 0.0002 | -0.0006 | 0.0036 | -0.0003 | -0.0203 | -360.2111 | 17.4274 | -360.4819 | 17.7005 | -360.8604 | 18.1563 | -360.9281 | 17.5527 | -352.7029 | 18.7312 | -352.7306 | 16.8361
12:00 | 2413 | 29.533 | 197.1606 | 442.325 | 448.0475 | -19.2832 | -46.3845 | 6.3408 | 3.5898 | -3.108 | -3.9267 | -0.3676 | -2.8733 | 6.4858 | -0.0666 | 0.5975 | 0.6353 | 0.955 | 0.715 | -130.9963 | -5.76 | 2.4803 | 0.1269 | -6.1936 | -4.7071 | 1.7097 |  | -0.1739 | -1.9928 | 4.014 | 3.3641 | 3.3517 | 1.0361 | 10.6641 | 14.1262 | 14.73 | 11.0283 | 0 | -0.0034 | 0.0008 | 0.0043 | 0.0008 | -0.0003 | -0.0022 | -0.0196 | -0.0208 | -360.1927 | 17.4418 | -360.4973 | 17.682 | -360.842 | 18.1153 | -360.8327 | 17.5178 | -352.7152 | 18.7579 | -352.7429 | 16.8402
12:00 | 2414 | 29.5578 | 197.1209 | 442.2992 | 448.0889 | -19.3035 | -46.3025 | 6.3806 | 3.6496 | -3.0011 | -3.9342 | -0.3556 | -2.8801 | 6.4854 | -0.0598 | 0.5968 | 0.637 | 0.9545 | 0.7158 | -131.053 | -5.6544 | 2.5235 | 0.1748 | -6.0789 | -4.6903 | 1.7747 |  | -0.1477 | -1.8925 | 4.015 | 3.3671 | 3.3504 | 1.0374 | 10.7013 | 14.1513 | 14.7238 | 11.0316 | -0.0005 | -0.0025 | 0.0007 | 0.0039 | 0.0005 | -0.0005 | 0.0138 | -0.0141 | -0.001 | -360.1496 | 17.4377 | -360.565 | 17.7169 | -360.8574 | 18.1522 | -360.9004 | 17.528 | -352.6752 | 18.76 | -352.789 | 16.8607
12:00 | 2415 | 29.584 | 197.1202 | 442.4347 | 448.1106 | -19.2861 | -46.2751 | 6.3801 | 3.6378 | -2.9985 | -3.906 | -0.3156 | -2.9138 | 6.4324 | -0.1143 | 0.5976 | 0.6379 | 0.9559 | 0.7152 | -131.0389 | -5.7202 | 2.5032 | 0.1743 | -6.116 | -4.8439 | 1.8068 |  | -0.2237 | -1.9918 | 4.014 | 3.3648 | 3.3482 | 1.0377 | 10.7209 | 14.1827 | 14.7276 | 11.0392 | -0.0004 | -0.0026 | 0 | 0.0034 | 0.0005 | -0.0002 | -0.0035 | -0.0109 | -0.0234 | -360.1373 | 17.3823 | -360.4327 | 17.6759 | -360.8204 | 18.142 | -360.9004 | 17.5321 | -352.6875 | 18.7128 | -352.6783 | 16.832
12:00 | 2416 | 29.5681 | 197.1091 | 442.4352 | 448.0181 | -19.3627 | -46.3089 | 6.4231 | 3.7158 | -2.9671 | -3.9193 | -0.3288 | -2.8686 | 6.429 | -0.0202 | 0.5973 | 0.6387 | 0.9551 | 0.7151 | -131.0551 | -5.6988 | 2.5532 | 0.206 | -6.0768 | -4.6664 | 1.8253 |  | -0.3556 | -1.9715 | 4.0131 | 3.3651 | 3.3518 | 1.037 | 10.7103 | 14.1959 | 14.7437 | 11.0449 | -0.0001 | -0.0035 | 0.0008 | 0.0036 | 0.001 | -0.0005 | 0.0074 | -0.0097 | -0.0131 | -360.2265 | 17.4377 | -360.4819 | 17.6779 | -360.8174 | 18.142 | -360.9343 | 17.5671 | -352.7398 | 18.762 | -352.7213 | 16.8135
12:00 | 2417 | 29.5541 | 197.0326 | 442.3415 | 447.9253 | -19.3377 | -46.4713 | 6.3297 | 3.6827 | -2.8333 | -3.8109 | -0.249 | -2.8323 | 6.5009 | 0.0104 | 0.5992 | 0.6354 | 0.956 | 0.7158 | -131.0527 | -5.6982 | 2.4143 | 0.1325 | -6.1211 | -4.7867 | 1.867 |  | -0.3006 | -1.9473 | 4.0142 | 3.3648 | 3.3539 | 1.0374 | 10.7335 | 14.2131 | 14.7947 | 11.0742 | 0.0002 | -0.0029 | 0.0004 | 0.0033 | 0.0002 | -0.0006 | 0.009 | -0.0109 | -0.0101 | -360.1342 | 17.4131 | -360.4789 | 17.6882 | -360.8266 | 18.1296 | -360.8512 | 17.5096 | -352.7121 | 18.7456 | -352.709 | 16.8443
12:00 | 2418 | 29.5724 | 197.065 | 442.4234 | 447.9766 | -19.2586 | -46.356 | 6.3547 | 3.6227 | -2.99 | -3.8174 | -0.2618 | -2.8299 | 6.4482 | 0.0267 | 0.5973 | 0.6307 | 0.9553 | 0.7139 | -131.0877 | -5.8194 | 2.3534 | 0.033 | -6.1125 | -4.7339 | 1.752 |  | -0.329 | -2.0419 | 4.0147 | 3.3669 | 3.3503 | 1.0379 | 10.7186 | 14.1746 | 14.7538 | 11.0313 | -0.0001 | -0.0028 | 0.0007 | 0.0038 | 0.0006 | -0.0012 | 0.0022 | -0.0101 | -0.0104 | -360.1558 | 17.4172 | -360.525 | 17.7108 | -360.882 | 18.1789 | -360.9312 | 17.5239 | -352.666 | 18.723 | -352.7583 | 16.8525
12:00 | 2419 | 29.5763 | 197.0726 | 442.3268 | 447.9714 | -19.2547 | -46.2816 | 6.4938 | 3.6338 | -3.0167 | -3.8687 | -0.2309 | -2.8718 | 6.5343 | 0.0163 | 0.598 | 0.6357 | 0.9538 | 0.7151 | -131.0086 | -5.7554 | 2.3939 | 0.075 | -6.1564 | -4.727 | 1.8204 |  | -0.2095 | -1.9341 | 4.0135 | 3.363 | 3.3481 | 1.0373 | 10.7196 | 14.1761 | 14.7804 | 11.0663 | -0.0002 | -0.0026 | 0.0012 | 0.0039 | 0.0005 | -0.0004 | 0.0128 | -0.0163 | -0.0082 | -360.1281 | 17.3843 | -360.4389 | 17.6923 | -360.8358 | 18.142 | -360.8912 | 17.5404 | -352.669 | 18.7045 | -352.6906 | 16.8279
12:00 | 2420 | 29.5694 | 197.0953 | 442.3833 | 448.0054 | -19.2387 | -46.3773 | 6.4495 | 3.5196 | -3.0396 | -3.9653 | -0.3147 | -2.8849 | 6.4905 | 0.0245 | 0.5985 | 0.6353 | 0.956 | 0.7165 | -131.0587 | -5.806 | 2.3877 | 0.2037 | -6.0066 | -4.7539 | 1.8489 |  | -0.1941 | -1.8705 | 4.0139 | 3.3642 | 3.3493 | 1.0369 | 10.6885 | 14.1561 | 14.7177 | 11.0244 | 0.0005 | -0.0026 | 0.0004 | 0.0038 | 0.0009 | -0.0007 | 0.0079 | -0.0166 | -0.0162 | -360.2235 | 17.4603 | -360.5343 | 17.7026 | -360.8512 | 18.142 | -360.8943 | 17.5445 | -352.749 | 18.7661 | -352.746 | 16.8381
12:00 | 2421 | 29.5498 | 197.0974 | 442.4173 | 448.0039 | -19.2156 | -46.3479 | 6.4813 | 3.6303 | -2.9151 | -3.8535 | -0.3153 | -2.9956 | 6.4746 | 0.0134 | 0.5973 | 0.6357 | 0.9511 | 0.7153 | -131.0482 | -5.6803 | 2.5342 | -0.0181 | -6.0972 | -4.6858 | 1.7603 |  | -0.2177 | -1.8792 | 4.0152 | 3.3667 | 3.3494 | 1.037 | 10.6873 | 14.1261 | 14.7231 | 11.0172 | 0.0003 | -0.003 | 0.0007 | 0.004 | 0.0004 | -0.0007 | -0.0068 | -0.0035 | -0.0329 | -360.1496 | 17.4233 | -360.5219 | 17.7087 | -360.8604 | 18.1194 | -360.8635 | 17.5055 | -352.6413 | 18.7436 | -352.7398 | 16.8484
12:00 | 2422 | 29.5917 | 197.0686 | 442.4363 | 448.0406 | -19.228 | -46.3306 | 6.5011 | 3.6023 | -3.0038 | -3.9628 | -0.3524 | -2.9579 | 6.5386 | -0.0632 | 0.5991 | 0.6374 | 0.9564 | 0.7165 | -131.1046 | -5.7473 | 2.4822 | -0.1028 | -6.1083 | -4.7029 | 1.7812 |  | -0.1712 | -1.7927 | 4.0165 | 3.366 | 3.3473 | 1.0387 | 10.6839 | 14.1515 | 14.748 | 11.0255 | -0.0001 | -0.0027 | 0.0006 | 0.0041 | 0.0007 | -0.001 | -0.0068 | -0.0014 | 0.0005 | -360.1835 | 17.411 | -360.4819 | 17.7026 | -360.8727 | 18.1728 | -360.9404 | 17.5445 | -352.6937 | 18.7333 | -352.7275 | 16.8402
12:00 | 2423 | 29.5826 | 197.1424 | 442.4165 | 447.9713 | -19.2409 | -46.3498 | 6.4001 | 3.5141 | -2.9649 | -3.8558 | -0.4313 | -2.9295 | 6.4932 | -0.0562 | 0.5975 | 0.6364 | 0.9574 | 0.715 | -131.0922 | -5.6948 | 2.5252 | -0.0419 | -6.2008 | -4.7236 | 1.7772 |  | -0.209 | -1.806 | 4.014 | 3.3663 | 3.3534 | 1.0371 | 10.7011 | 14.1517 | 14.7559 | 11.0594 | -0.0001 | -0.0027 | 0.0002 | 0.0033 | 0.0008 | -0.0006 | 0.0144 | -0.0043 | -0.019 | -360.205 | 17.4131 | -360.4758 | 17.6656 | -360.7773 | 18.1173 | -360.8943 | 17.5445 | -352.7275 | 18.7477 | -352.7029 | 16.8115
12:00 | 2424 | 29.5879 | 197.1473 | 442.4205 | 447.9735 | -19.1845 | -46.3746 | 6.5322 | 3.5485 | -2.8727 | -3.818 | -0.4606 | -2.9147 | 6.5319 | -0.1162 | 0.5986 | 0.6356 | 0.9531 | 0.7159 | -131.0816 | -5.6823 | 2.3685 | -0.0403 | -6.1389 | -4.5797 | 1.81 |  | -0.1926 | -1.8037 | 4.0154 | 3.3679 | 3.3524 | 1.0381 | 10.6966 | 14.1642 | 14.732 | 11.0381 | 0.0002 | -0.0026 | 0.0009 | 0.0038 | 0.0005 | -0.0007 | 0.0078 | -0.0073 | -0.0219 | -360.1958 | 17.4418 | -360.5343 | 17.7149 | -360.8635 | 18.1502 | -360.9035 | 17.5445 | -352.7183 | 18.7538 | -352.7737 | 16.8484
12:00 | 2425 | 29.5938 | 197.136 | 442.4697 | 447.9227 | -19.2058 | -46.2761 | 6.4023 | 3.5766 | -2.8505 | -3.8197 | -0.4302 | -2.8023 | 6.631 | 0.0182 | 0.5979 | 0.6342 | 0.9546 | 0.7158 | -131.0497 | -5.6591 | 2.394 | -0.0747 | -6.1429 | -4.6057 | 1.807 |  | -0.1991 | -1.8424 | 4.0145 | 3.3658 | 3.3502 | 1.0386 | 10.6898 | 14.1512 | 14.688 | 11.0205 | -0.0002 | -0.0032 | 0.0007 | 0.0037 | 0.0008 | -0.0007 | 0.0046 | -0.0062 | -0.0177 | -360.1588 | 17.3925 | -360.4604 | 17.682 | -360.8174 | 18.1584 | -360.9004 | 17.5137 | -352.666 | 18.7128 | -352.6875 | 16.832
12:00 | 2426 | 29.6308 | 197.1254 | 442.363 | 447.9269 | -19.2369 | -46.251 | 6.5071 | 3.5692 | -2.8002 | -3.8598 | -0.4876 | -2.9112 | 6.5404 | -0.079 | 0.5985 | 0.6333 | 0.9557 | 0.717 | -131.0388 | -5.7066 | 2.4463 | -0.1829 | -6.0792 | -4.8639 | 1.8799 |  | -0.1755 | -1.7831 | 4.0126 | 3.3661 | 3.3506 | 1.0389 | 10.6874 | 14.1491 | 14.7395 | 11.0291 | 0.0002 | -0.0024 | 0.0007 | 0.0035 | 0.0006 | -0.0004 | 0.0193 | -0.0046 | 0.0059 | -360.2173 | 17.4356 | -360.5219 | 17.7128 | -360.8358 | 18.144 | -360.9281 | 17.5527 | -352.7552 | 18.7538 | -352.746 | 16.834
12:00 | 2427 | 29.6257 | 197.2151 | 442.431 | 448.0465 | -19.2297 | -46.3714 | 6.4549 | 3.5469 | -2.8252 | -3.8346 | -0.371 | -2.9775 | 6.5354 | -0.1699 | 0.5982 | 0.637 | 0.9547 | 0.7172 | -131.0177 | -5.7192 | 2.4195 | -0.0972 | -6.0243 | -4.8184 | 1.8251 |  | -0.2043 | -1.8604 | 4.0138 | 3.3654 | 3.3508 | 1.0387 | 10.6735 | 14.1758 | 14.7146 | 11.0497 | -0.0002 | -0.0025 | 0.0008 | 0.0039 | 0.0009 | -0.0008 | 0.0162 | -0.0114 | -0.0188 | -360.1188 | 17.409 | -360.5035 | 17.7128 | -360.8174 | 18.1194 | -360.8389 | 17.5096 | -352.6598 | 18.7415 | -352.7306 | 16.8423
12:00 | 2428 | 29.6881 | 197.1954 | 442.5225 | 448.1415 | -19.2241 | -46.3181 | 6.4078 | 3.5532 | -2.8763 | -3.8787 | -0.4104 | -2.94 | 6.568 | -0.0419 | 0.5982 | 0.6381 | 0.9558 | 0.7157 | -131.0795 | -5.7096 | 2.3946 | 0.002 | -5.9785 | -4.6633 | 1.8894 |  | -0.1721 | -1.7345 | 4.0137 | 3.3687 | 3.3514 | 1.0378 | 10.6943 | 14.1503 | 14.7408 | 11.0533 | -0.0004 | -0.003 | 0.0008 | 0.0039 | 0.0005 | -0.0006 | 0.0047 | 0.0038 | -0.0055 | -360.1681 | 17.4254 | -360.5096 | 17.721 | -360.8974 | 18.1604 | -360.9004 | 17.5363 | -352.669 | 18.7333 | -352.7213 | 16.8484
12:00 | 2429 | 29.6383 | 197.1096 | 442.4262 | 448.0598 | -19.2903 | -46.258 | 6.4349 | 3.6049 | -2.825 | -3.9172 | -0.282 | -2.8524 | 6.4937 | -0.1053 | 0.5976 | 0.637 | 0.9586 | 0.7174 | -130.978 | -5.684 | 2.4913 | 0.0312 | -6.0747 | -4.7468 | 1.8462 |  | -0.1422 | -1.9212 | 4.0142 | 3.3641 | 3.3497 | 1.0391 | 10.6792 | 14.1644 | 14.7504 | 11.0724 | 0 | -0.0032 | 0.0008 | 0.0039 | 0.0002 | -0.0012 | 0.0018 | 0.0016 | -0.0235 | -360.1773 | 17.4254 | -360.4573 | 17.6656 | -360.7804 | 18.1358 | -360.8881 | 17.5301 | -352.7183 | 18.7395 | -352.6998 | 16.8156
12:00 | 2430 | 29.6833 | 197.0875 | 442.527 | 448.0759 | -19.3271 | -46.3551 | 6.476 | 3.6089 | -2.9454 | -3.8747 | -0.3922 | -2.8996 | 6.5178 | -0.0487 | 0.5975 | 0.6373 | 0.9568 | 0.7168 | -131.0389 | -5.7304 | 2.4824 | 0.0665 | -6.0761 | -4.6859 | 1.8338 |  | -0.1473 | -1.8667 | 4.0147 | 3.366 | 3.3499 | 1.0406 | 10.6839 | 14.163 | 14.7596 | 11.0313 | 0.0001 | -0.0029 | 0.0006 | 0.0039 | 0.0006 | -0.0004 | 0.0057 | -0.0247 | 0.0006 | -360.165 | 17.448 | -360.5496 | 17.7108 | -360.842 | 18.1337 | -360.8943 | 17.5486 | -352.7029 | 18.76 | -352.7583 | 16.8525
12:00 | 2431 | 29.7334 | 197.1997 | 442.4419 | 448.0851 | -19.2789 | -46.3194 | 6.465 | 3.6256 | -2.9435 | -3.9138 | -0.3974 | -2.9714 | 6.5147 | -0.0668 | 0.5967 | 0.6358 | 0.9553 | 0.7165 | -131.0098 | -5.699 | 2.4323 | 0.0702 | -6.0292 | -4.728 | 1.8552 |  | -0.1983 | -1.8449 | 4.0131 | 3.3634 | 3.348 | 1.0395 | 10.678 | 14.1805 | 14.749 | 11.002 | -0.0004 | -0.0028 | 0.0005 | 0.0036 | 0.0009 | -0.0006 | 0.0138 | -0.0078 | -0.0044 | -360.1742 | 17.3966 | -360.4542 | 17.6964 | -360.8266 | 18.1461 | -360.8943 | 17.5219 | -352.6783 | 18.723 | -352.7213 | 16.8423
12:00 | 2432 | 29.6884 | 197.1455 | 442.4442 | 448.1298 | -19.1751 | -46.2763 | 6.4867 | 3.6066 | -2.9275 | -4.0175 | -0.3494 | -3.0032 | 6.4893 | -0.0225 | 0.5966 | 0.6338 | 0.9546 | 0.7163 | -131.0871 | -5.8127 | 2.4165 | 0.1307 | -6.0098 | -4.7571 | 1.8195 |  | -0.1696 | -1.7895 | 4.0154 | 3.3663 | 3.3526 | 1.0381 | 10.6839 | 14.1688 | 14.748 | 11.0313 | -0.0004 | -0.0025 | 0.001 | 0.0039 | 0.0009 | -0.0005 | 0.0044 | -0.0023 | -0.0082 | -360.2419 | 17.4315 | -360.4789 | 17.6697 | -360.8358 | 18.1625 | -360.9004 | 17.5568 | -352.746 | 18.7456 | -352.6998 | 16.8217
12:00 | 2433 | 29.7599 | 197.2501 | 442.4421 | 448.1474 | -19.1425 | -46.1524 | 6.5552 | 3.589 | -2.9222 | -3.9923 | -0.3694 | -2.8992 | 6.4004 | -0.007 | 0.5969 | 0.6368 | 0.955 | 0.7172 | -130.9869 | -5.699 | 2.4586 | 0.0307 | -6.0322 | -4.711 | 1.8774 |  | -0.2124 | -1.8307 | 4.016 | 3.365 | 3.3492 | 1.0391 | 10.6966 | 14.1872 | 14.7714 | 11.0616 | -0.0001 | -0.0032 | 0.0011 | 0.0039 | 0.0008 | -0.0002 | 0.0113 | 0.001 | -0.0107 | -360.1619 | 17.4131 | -360.4727 | 17.6759 | -360.7958 | 18.1337 | -360.885 | 17.5239 | -352.6875 | 18.7292 | -352.7213 | 16.834
12:00 | 2434 | 29.7373 | 197.2062 | 442.6505 | 448.1463 | -19.1358 | -46.2537 | 6.4718 | 3.5452 | -2.9172 | -3.9232 | -0.383 | -2.9552 | 6.4396 | -0.1803 | 0.597 | 0.6344 | 0.9538 | 0.7155 | -131.0284 | -5.7192 | 2.2996 | 0.0607 | -6.043 | -4.7799 | 1.8842 |  | -0.2053 | -1.8947 | 4.0147 | 3.3651 | 3.3508 | 1.0382 | 10.7036 | 14.1421 | 14.7497 | 11.0338 | 0 | -0.0033 | 0.0008 | 0.0033 | 0.0009 | -0.0005 | 0.0034 | -0.0034 | -0.0232 | -360.1835 | 17.4192 | -360.5219 | 17.7108 | -360.8758 | 18.1522 | -360.9097 | 17.5363 | -352.6844 | 18.7374 | -352.7521 | 16.8464
12:00 | 2435 | 29.6922 | 197.1776 | 442.4745 | 448.1273 | -19.2273 | -46.3097 | 6.5158 | 3.5703 | -2.937 | -3.9706 | -0.3277 | -2.962 | 6.4818 | -0.157 | 0.5948 | 0.6344 | 0.9559 | 0.7161 | -131.0787 | -5.6893 | 2.3318 | 0.1072 | -6.1806 | -4.8006 | 1.7978 |  | -0.1676 | -1.8868 | 4.0151 | 3.3663 | 3.3508 | 1.0379 | 10.7243 | 14.198 | 14.7906 | 11.0478 | -0.0005 | -0.0031 | 0.0014 | 0.0046 | 0.0003 | 0.0001 | -0.0044 | -0.0138 | -0.0287 | -360.1127 | 17.4028 | -360.4604 | 17.6841 | -360.842 | 18.1522 | -360.9035 | 17.5363 | -352.6844 | 18.7128 | -352.7183 | 16.8381
12:00 | 2436 | 29.7758 | 197.2193 | 442.4615 | 448.135 | -19.1636 | -46.2032 | 6.469 | 3.6314 | -2.9217 | -3.9026 | -0.2688 | -3.0216 | 6.4938 | -0.1053 | 0.5953 | 0.6357 | 0.9584 | 0.7165 | -130.9957 | -5.6794 | 2.4484 | 0.2079 | -6.1176 | -4.7184 | 1.8428 |  | -0.1074 | -1.9355 | 4.0159 | 3.3634 | 3.3506 | 1.039 | 10.714 | 14.1816 | 14.7841 | 11.0381 | -0.0005 | -0.0029 | 0.0005 | 0.0038 | 0.0012 | -0.0006 | -0.0052 | -0.0058 | -0.0219 | -360.2081 | 17.4356 | -360.5096 | 17.7005 | -360.8512 | 18.1379 | -360.8697 | 17.5486 | -352.749 | 18.7497 | -352.7121 | 16.834
12:00 | 2437 | 29.7346 | 197.1464 | 442.4969 | 448.0723 | -19.1457 | -46.193 | 6.4947 | 3.6747 | -2.9318 | -3.7729 | -0.3066 | -2.9052 | 6.4925 | -0.1082 | 0.5973 | 0.6368 | 0.9531 | 0.7172 | -130.9841 | -5.7518 | 2.3995 | 0.281 | -6.0909 | -4.7203 | 1.8116 |  | -0.1468 | -1.9032 | 4.0165 | 3.3656 | 3.348 | 1.038 | 10.6759 | 14.1605 | 14.7095 | 10.9833 | -0.0001 | -0.0023 | 0.0005 | 0.0039 | 0.0005 | -0.0005 | -0.0031 | -0.0163 | -0.0221 | -360.1496 | 17.4295 | -360.5158 | 17.7067 | -360.8327 | 18.1317 | -360.8758 | 17.5096 | -352.706 | 18.7415 | -352.7521 | 16.8423
12:00 | 2438 | 29.7328 | 197.1695 | 442.5038 | 448.0243 | -19.1849 | -46.2099 | 6.587 | 3.6392 | -2.9296 | -3.819 | -0.3018 | -2.9565 | 6.4898 | -0.0955 | 0.5964 | 0.6367 | 0.9529 | 0.7167 | -130.9746 | -5.5977 | 2.4288 | 0.2947 | -6.0125 | -4.7212 | 1.8253 |  | -0.1383 | -1.9321 | 4.0141 | 3.3652 | 3.3494 | 1.0386 | 10.6977 | 14.1423 | 14.7681 | 11.0219 | 0.0002 | -0.0032 | 0.0005 | 0.0038 | 0.0008 | -0.0009 | 0.0118 | 0.0034 | -0.0088 | -360.1988 | 17.4131 | -360.4881 | 17.7169 | -360.845 | 18.1543 | -360.9189 | 17.5465 | -352.6844 | 18.7251 | -352.7152 | 16.8443
12:00 | 2439 | 29.7052 | 197.1717 | 442.5227 | 448.0366 | -19.1757 | -46.1675 | 6.6095 | 3.6112 | -2.9034 | -3.8032 | -0.3157 | -2.9219 | 6.5051 | -0.1154 | 0.595 | 0.638 | 0.9577 | 0.7166 | -131.041 | -5.722 | 2.4061 | 0.3287 | -6.0587 | -4.6897 | 1.8087 |  | -0.1502 | -1.92 | 4.0129 | 3.3623 | 3.3513 | 1.038 | 10.7047 | 14.178 | 14.7684 | 11.0407 | 0 | -0.003 | 0.0001 | 0.0029 | 0.0002 | -0.0007 | -0.0082 | -0.0072 | -0.0176 | -360.1742 | 17.4274 | -360.4389 | 17.6615 | -360.8081 | 18.1214 | -360.882 | 17.5486 | -352.7213 | 18.7353 | -352.6967 | 16.8197
12:00 | 2440 | 29.7524 | 197.1168 | 442.4978 | 448.1043 | -19.182 | -46.2459 | 6.5953 | 3.7222 | -2.8957 | -3.7987 | -0.293 | -2.8228 | 6.5269 | -0.0223 | 0.5964 | 0.6393 | 0.958 | 0.7178 | -131.0509 | -5.6942 | 2.4986 | 0.3048 | -6.1339 | -4.649 | 1.8847 |  | -0.1442 | -1.8042 | 4.0132 | 3.3619 | 3.3489 | 1.0382 | 10.6735 | 14.1409 | 14.6904 | 11.0385 | -0.0005 | -0.0031 | 0.0008 | 0.0037 | 0.0011 | -0.0008 | 0.0117 | -0.0128 | -0.0042 | -360.1896 | 17.4377 | -360.5004 | 17.7149 | -360.8358 | 18.1399 | -360.8974 | 17.5383 | -352.7121 | 18.7395 | -352.7614 | 16.8464
12:00 | 2441 | 29.7444 | 197.0951 | 442.5471 | 448.0611 | -19.0942 | -46.15 | 6.7578 | 3.7256 | -2.9263 | -3.7996 | -0.2914 | -2.8317 | 6.5592 | -0.0212 | 0.5967 | 0.6402 | 0.9547 | 0.7168 | -131.1504 | -5.8416 | 2.4116 | 0.3197 | -6.1258 | -4.6826 | 1.8001 |  | -0.0996 | -1.8083 | 4.0155 | 3.3636 | 3.35 | 1.0385 | 10.7172 | 14.1798 | 14.7451 | 11.0518 | 0 | -0.0026 | 0.0011 | 0.0039 | 0.001 | -0.0001 | -0.0015 | -0.0026 | -0.0251 | -360.1435 | 17.4028 | -360.4758 | 17.6902 | -360.845 | 18.1563 | -360.8727 | 17.5137 | -352.6783 | 18.7189 | -352.7213 | 16.8525
12:00 | 2442 | 29.7387 | 197.2379 | 442.5739 | 448.1041 | -19.1561 | -46.1456 | 6.6733 | 3.7384 | -2.8444 | -3.6846 | -0.2286 | -2.8234 | 6.5715 | 0.0538 | 0.5974 | 0.6386 | 0.9558 | 0.7154 | -131.1198 | -5.7896 | 2.3969 | 0.3854 | -6.1928 | -4.6296 | 1.9287 |  | -0.1496 | -1.8058 | 4.0151 | 3.3668 | 3.3485 | 1.0379 | 10.7105 | 14.1664 | 14.7626 | 11.0522 | 0.0002 | -0.0031 | 0.0005 | 0.0034 | 0.0006 | -0.0009 | 0.0064 | -0.0053 | -0.0194 | -360.1588 | 17.4192 | -360.4881 | 17.7046 | -360.8358 | 18.1666 | -360.9497 | 17.5527 | -352.6721 | 18.7251 | -352.7121 | 16.8402
12:00 | 2443 | 29.805 | 197.2317 | 442.6455 | 448.1751 | -19.0453 | -46.1076 | 6.7138 | 3.6657 | -2.9424 | -3.7815 | -0.3654 | -2.8855 | 6.6015 | 0.041 | 0.5973 | 0.6396 | 0.9566 | 0.717 | -131.0139 | -5.7457 | 2.4967 | 0.3349 | -6.0875 | -4.6338 | 1.8982 |  | -0.1475 | -1.8103 | 4.0153 | 3.3649 | 3.3489 | 1.0376 | 10.7206 | 14.2183 | 14.8034 | 11.0832 | 0.0004 | -0.0024 | 0.001 | 0.0041 | 0.0011 | -0.0002 | 0.0065 | -0.0172 | -0.0155 | -360.1927 | 17.4233 | -360.4912 | 17.7026 | -360.8204 | 18.1379 | -360.8912 | 17.5363 | -352.7306 | 18.7415 | -352.7244 | 16.8381
12:00 | 2444 | 29.8298 | 197.1933 | 442.6073 | 448.0551 | -19.0661 | -46.2414 | 6.6733 | 3.6979 | -2.9232 | -3.6433 | -0.1924 | -2.8906 | 6.6536 | 0.0797 | 0.5976 | 0.6394 | 0.9547 | 0.7163 | -131.0563 | -5.7039 | 2.5167 | 0.2386 | -6.1613 | -4.6137 | 1.8384 |  | -0.1935 | -1.9091 | 4.0139 | 3.3623 | 3.3534 | 1.0385 | 10.678 | 14.1632 | 14.7433 | 11.0482 | -0.0002 | -0.0027 | 0.0004 | 0.0035 | 0.0006 | -0.0004 | 0.0059 | -0.0073 | -0.0084 | -360.1435 | 17.4274 | -360.5096 | 17.719 | -360.8604 | 18.1522 | -360.8635 | 17.5055 | -352.7029 | 18.7374 | -352.7306 | 16.8525
12:00 | 2445 | 29.7709 | 197.1862 | 442.6919 | 448.1122 | -19.0962 | -46.2993 | 6.7853 | 3.5886 | -2.9302 | -3.7809 | -0.2742 | -2.8962 | 6.6116 | -0.0013 | 0.5974 | 0.6399 | 0.9554 | 0.716 | -131.1642 | -5.7248 | 2.431 | 0.2454 | -6.237 | -4.8088 | 1.7925 |  | -0.1239 | -1.8617 | 4.0158 | 3.3647 | 3.3512 | 1.0371 | 10.6655 | 14.1383 | 14.7261 | 11.0082 | -0.0005 | -0.0028 | 0.0004 | 0.0037 | 0.0008 | -0.0005 | 0.0021 | -0.0114 | -0.0223 | -360.1742 | 17.4069 | -360.4881 | 17.7026 | -360.8358 | 18.1604 | -360.885 | 17.5301 | -352.6875 | 18.7312 | -352.7213 | 16.8587
12:00 | 2446 | 29.7862 | 197.2303 | 442.5539 | 448.1157 | -19.1103 | -46.4067 | 6.6991 | 3.648 | -2.9037 | -3.8381 | -0.2316 | -2.9708 | 6.6151 | -0.0538 | 0.5957 | 0.639 | 0.9542 | 0.7163 | -131.0643 | -5.7361 | 2.5192 | 0.2578 | -6.268 | -4.6416 | 1.7944 |  | -0.197 | -1.9465 | 4.015 | 3.3657 | 3.3491 | 1.0386 | 10.6689 | 14.1479 | 14.7728 | 11.0049 | 0.0003 | -0.003 | 0.0006 | 0.0038 | 0.0007 | -0.0004 | 0.0066 | 0.0073 | -0.0076 | -360.165 | 17.4254 | -360.485 | 17.6902 | -360.802 | 18.1666 | -360.9127 | 17.5445 | -352.6752 | 18.7312 | -352.7121 | 16.8238
12:00 | 2447 | 29.7926 | 197.2279 | 442.5916 | 448.1524 | -19.118 | -46.4185 | 6.6687 | 3.6638 | -2.8961 | -3.7866 | -0.3043 | -2.8822 | 6.6368 | -0.0511 | 0.5987 | 0.6373 | 0.9562 | 0.7169 | -131.0283 | -5.7141 | 2.5183 | 0.2293 | -6.1808 | -4.6653 | 1.7808 |  | -0.1978 | -1.9809 | 4.0131 | 3.3652 | 3.3473 | 1.0364 | 10.684 | 14.1396 | 14.7574 | 11.0262 | 0 | -0.0034 | 0.0005 | 0.0033 | 0.0008 | -0.0012 | 0.0209 | -0.0089 | -0.0042 | -360.2327 | 17.4295 | -360.4942 | 17.7005 | -360.8143 | 18.144 | -360.8758 | 17.5445 | -352.7367 | 18.76 | -352.746 | 16.8381
12:01 | 2448 | 29.7682 | 197.2098 | 442.7132 | 448.1151 | -19.2721 | -46.4503 | 6.5639 | 3.6255 | -2.9378 | -3.8564 | -0.3355 | -2.8517 | 6.6152 | -0.1255 | 0.5983 | 0.6402 | 0.9529 | 0.7166 | -131.1726 | -5.7671 | 2.4509 | 0.1435 | -6.2665 | -4.6602 | 1.7228 |  | -0.1993 | -1.8477 | 4.014 | 3.3629 | 3.3491 | 1.0362 | 10.6596 | 14.1386 | 14.7108 | 11.0017 | -0.0001 | -0.0025 | 0.0008 | 0.004 | 0.0008 | -0.0001 | -0.0004 | -0.0044 | -0.0076 | -360.125 | 17.4254 | -360.5158 | 17.7067 | -360.8481 | 18.1625 | -360.885 | 17.5198 | -352.6383 | 18.723 | -352.7183 | 16.8505
12:01 | 2449 | 29.8066 | 197.198 | 442.5432 | 448.0569 | -19.2829 | -46.3736 | 6.5328 | 3.5498 | -2.9392 | -3.7373 | -0.3029 | -2.888 | 6.5959 | 0.006 | 0.5975 | 0.6415 | 0.958 | 0.7171 | -131.1555 | -5.699 | 2.372 | 0.0251 | -6.2808 | -4.8238 | 1.7619 |  | -0.1356 | -1.8067 | 4.0154 | 3.3608 | 3.3491 | 1.0374 | 10.7311 | 14.1879 | 14.8115 | 11.0597 | -0.0001 | -0.0025 | 0.0007 | 0.0038 | 0.001 | -0.0005 | 0.0072 | 0.0025 | 0.0039 | -360.1496 | 17.4048 | -360.4635 | 17.7087 | -360.8481 | 18.1994 | -360.9251 | 17.5301 | -352.7306 | 18.7292 | -352.6967 | 16.8525
12:01 | 2450 | 29.7878 | 197.1902 | 442.5917 | 448.0629 | -19.2541 | -46.3466 | 6.5621 | 3.6259 | -2.8641 | -3.8384 | -0.2102 | -2.8872 | 6.6272 | 0.0247 | 0.5977 | 0.6398 | 0.9524 | 0.7163 | -131.1388 | -5.717 | 2.4303 | -0.0403 | -6.1478 | -4.7345 | 1.7606 |  | -0.1809 | -1.7916 | 4.0148 | 3.3632 | 3.3495 | 1.0367 | 10.7221 | 14.1607 | 14.78 | 11.0291 | -0.0002 | -0.0031 | 0.001 | 0.0039 | 0.0005 | -0.0002 | 0.0158 | -0.0072 | 0.0064 | -360.1311 | 17.411 | -360.485 | 17.6779 | -360.805 | 18.1687 | -360.9004 | 17.5342 | -352.6783 | 18.7148 | -352.6844 | 16.8279
12:01 | 2451 | 29.7706 | 197.1489 | 442.5364 | 448.0647 | -19.2285 | -46.4063 | 6.4951 | 3.6373 | -2.8225 | -3.6745 | -0.1286 | -2.9678 | 6.6244 | -0.0371 | 0.5982 | 0.6413 | 0.955 | 0.7163 | -131.1742 | -5.6822 | 2.5042 | -0.0405 | -6.131 | -4.7498 | 1.6956 |  | -0.1731 | -1.7983 | 4.0142 | 3.3634 | 3.3493 | 1.0355 | 10.7 | 14.1851 | 14.7477 | 11.0471 | 0.0002 | -0.0033 | 0.0007 | 0.0037 | 0.0008 | -0.0007 | 0.0248 | -0.0108 | -0.0056 | -360.1927 | 17.4439 | -360.5158 | 17.719 | -360.8574 | 18.1584 | -360.885 | 17.5342 | -352.7183 | 18.76 | -352.7675 | 16.8505
12:01 | 2452 | 29.8135 | 197.1418 | 442.6747 | 448.0979 | -19.2316 | -46.3833 | 6.5454 | 3.6743 | -2.8843 | -3.7722 | -0.185 | -2.8984 | 6.541 | -0.0099 | 0.5959 | 0.6398 | 0.9563 | 0.7155 | -131.127 | -5.5241 | 2.5038 | 0.189 | -6.1222 | -4.7332 | 1.7589 |  | -0.2112 | -1.816 | 4.0144 | 3.3619 | 3.3514 | 1.0371 | 10.6955 | 14.1744 | 14.7296 | 11.0432 | -0.0004 | -0.003 | 0.0004 | 0.0033 | 0.0007 | -0.0007 | -0.0058 | -0.0117 | -0.0227 | -360.1373 | 17.4131 | -360.4973 | 17.7231 | -360.8758 | 18.1645 | -360.8574 | 17.489 | -352.6475 | 18.7189 | -352.709 | 16.8607
12:01 | 2453 | 29.7859 | 197.1625 | 442.6424 | 448.0998 | -19.2579 | -46.4229 | 6.5633 | 3.5916 | -2.8542 | -3.7547 | -0.1758 | -2.8969 | 6.5384 | 0.0054 | 0.5971 | 0.6378 | 0.953 | 0.7162 | -131.1881 | -5.6795 | 2.4005 | 0.2527 | -6.0886 | -4.7445 | 1.7264 |  | -0.18 | -1.8342 | 4.0148 | 3.3616 | 3.3517 | 1.0373 | 10.7093 | 14.1771 | 14.7865 | 11.0446 | -0.0003 | -0.0026 | 0.0006 | 0.0038 | 0.0006 | -0.0003 | 0.0015 | -0.0152 | -0.0192 | -360.1711 | 17.4172 | -360.485 | 17.7108 | -360.8758 | 18.1851 | -360.9004 | 17.528 | -352.706 | 18.723 | -352.7152 | 16.8546
12:01 | 2454 | 29.8429 | 197.1652 | 442.6859 | 448.1776 | -19.2247 | -46.3664 | 6.5627 | 3.5915 | -2.8549 | -3.7488 | -0.1054 | -2.9196 | 6.6629 | 0.0216 | 0.599 | 0.6401 | 0.9532 | 0.7154 | -131.1097 | -5.7179 | 2.3755 | 0.2482 | -6.181 | -4.6734 | 1.7492 |  | -0.1147 | -1.738 | 4.0147 | 3.3626 | 3.3544 | 1.0383 | 10.6585 | 14.1374 | 14.7558 | 11.0179 | -0.0004 | -0.0032 | 0.0004 | 0.004 | 0.0012 | -0.0009 | -0.0052 | -0.0095 | -0.0098 | -360.2204 | 17.4295 | -360.5158 | 17.6697 | -360.7958 | 18.1502 | -360.885 | 17.5219 | -352.709 | 18.7538 | -352.6906 | 16.8197
12:01 | 2455 | 29.777 | 197.1517 | 442.7291 | 448.1838 | -19.2298 | -46.3669 | 6.6136 | 3.6153 | -2.7502 | -3.7151 | -0.0486 | -2.8457 | 6.695 | 0.0517 | 0.5989 | 0.6383 | 0.9533 | 0.7154 | -131.1684 | -5.6143 | 2.4714 | 0.1199 | -6.1933 | -4.9247 | 1.8549 |  | -0.1064 | -1.7649 | 4.0148 | 3.3642 | 3.3495 | 1.0378 | 10.6874 | 14.1607 | 14.7452 | 11.0407 | 0.0004 | -0.0029 | 0.0008 | 0.0037 | 0.0004 | -0.0005 | 0.0096 | -0.0078 | -0.0098 | -360.1865 | 17.4418 | -360.5404 | 17.7169 | -360.8512 | 18.1502 | -360.8666 | 17.5137 | -352.749 | 18.76 | -352.7767 | 16.8607
12:01 | 2456 | 29.877 | 197.1778 | 442.6266 | 448.2325 | -19.3052 | -46.4532 | 6.5209 | 3.6594 | -2.7473 | -3.7304 | -0.1323 | -2.8818 | 6.805 | 0.0575 | 0.5977 | 0.6389 | 0.956 | 0.7151 | -131.2234 | -5.6805 | 2.4118 | 0.1327 | -6.1847 | -4.7357 | 1.8932 |  | -0.1376 | -1.7969 | 4.014 | 3.3635 | 3.353 | 1.0368 | 10.6769 | 14.1561 | 14.7582 | 11.0129 | 0 | -0.003 | 0.0007 | 0.0041 | 0.001 | -0.0007 | 0.012 | -0.0057 | -0.0061 | -360.1435 | 17.3987 | -360.4727 | 17.6985 | -360.8389 | 18.1748 | -360.8974 | 17.4993 | -352.669 | 18.7292 | -352.6844 | 16.832
12:01 | 2457 | 29.8293 | 197.2335 | 442.6291 | 448.2287 | -19.2249 | -46.4607 | 6.5021 | 3.6023 | -2.7469 | -3.6571 | -0.2153 | -2.8689 | 6.724 | 0.119 | 0.5984 | 0.6376 | 0.9551 | 0.7159 | -131.1737 | -5.5794 | 2.4675 | 0.0069 | -6.1105 | -4.6273 | 1.9018 |  | -0.1913 | -1.8414 | 4.0144 | 3.3622 | 3.3503 | 1.036 | 10.7035 | 14.1713 | 14.7691 | 11.033 | -0.0001 | -0.0024 | 0.001 | 0.0039 | 0.0007 | -0.0001 | 0.0046 | -0.0038 | -0.0047 | -360.2265 | 17.4028 | -360.4389 | 17.6759 | -360.8081 | 18.1789 | -360.9497 | 17.5527 | -352.7337 | 18.7353 | -352.669 | 16.8217
12:01 | 2458 | 29.8216 | 197.1295 | 442.6711 | 448.202 | -19.2391 | -46.4897 | 6.5032 | 3.597 | -2.7503 | -3.7309 | -0.2192 | -2.8452 | 6.6548 | 0.0716 | 0.5982 | 0.6392 | 0.9536 | 0.7171 | -131.2264 | -5.5978 | 2.4282 | 0.0755 | -6.1253 | -4.6439 | 1.9412 |  | -0.218 | -1.8476 | 4.0142 | 3.3679 | 3.3538 | 1.0385 | 10.7242 | 14.1809 | 14.7927 | 11.0586 | -0.0003 | -0.0026 | 0.0009 | 0.0041 | 0.0015 | -0.0005 | 0.0165 | -0.0059 | -0.0124 | -360.1711 | 17.4295 | -360.5066 | 17.6902 | -360.802 | 18.1666 | -360.9004 | 17.5239 | -352.7152 | 18.7579 | -352.7367 | 16.832
12:01 | 2459 | 29.8086 | 197.1573 | 442.6549 | 448.1664 | -19.2287 | -46.3899 | 6.5075 | 3.6283 | -2.7174 | -3.6753 | -0.1901 | -2.9649 | 6.6612 | 0.0453 | 0.5969 | 0.6371 | 0.9526 | 0.7163 | -131.1803 | -5.5373 | 2.3766 | 0.0009 | -6.2097 | -4.6712 | 1.7637 |  | -0.1807 | -1.9552 | 4.0147 | 3.3625 | 3.3511 | 1.0382 | 10.7186 | 14.186 | 14.799 | 11.0143 | -0.0003 | -0.0035 | 0.0009 | 0.0038 | 0.0004 | -0.0006 | 0.0156 | -0.0202 | 0.0082 | -360.1373 | 17.4028 | -360.5158 | 17.7313 | -360.8666 | 18.1625 | -360.8604 | 17.4972 | -352.6629 | 18.7251 | -352.709 | 16.8689
12:01 | 2460 | 29.8678 | 197.1162 | 442.6534 | 448.2268 | -19.2508 | -46.497 | 6.4668 | 3.6309 | -2.686 | -3.756 | -0.1267 | -2.9241 | 6.6868 | -0.0948 | 0.5978 | 0.6395 | 0.9522 | 0.717 | -131.2354 | -5.6144 | 2.3462 | -0.0245 | -6.2586 | -4.6432 | 1.772 |  | -0.252 | -1.9147 | 4.0149 | 3.3596 | 3.3521 | 1.0381 | 10.715 | 14.1772 | 14.7934 | 11.0847 | 0.0002 | -0.0028 | 0.0011 | 0.0037 | 0.0008 | -0.0006 | 0.0092 | -0.004 | -0.0096 | -360.1342 | 17.409 | -360.4727 | 17.7169 | -360.9189 | 18.1953 | -360.9312 | 17.5301 | -352.7152 | 18.721 | -352.6937 | 16.8423
12:01 | 2461 | 29.8282 | 197.2573 | 442.761 | 448.3259 | -19.1886 | -46.4732 | 6.4944 | 3.5559 | -2.6313 | -3.7496 | -0.3097 | -2.7831 | 6.7437 | 0.0712 | 0.5978 | 0.6362 | 0.9542 | 0.7163 | -131.1781 | -5.6363 | 2.3702 | 0.0447 | -6.2565 | -4.6747 | 1.7952 |  | -0.2123 | -1.9069 | 4.0151 | 3.3608 | 3.3505 | 1.0375 | 10.6943 | 14.1792 | 14.764 | 11.0129 | -0.0005 | -0.0029 | 0.0005 | 0.0037 | 0.0006 | -0.0004 | 0.0025 | -0.0148 | -0.0155 | -360.1927 | 17.4295 | -360.4942 | 17.68 | -360.7804 | 18.1543 | -360.8727 | 17.5219 | -352.7398 | 18.7518 | -352.709 | 16.8115
12:01 | 2462 | 29.8541 | 197.1528 | 442.7222 | 448.2632 | -19.1377 | -46.4474 | 6.4767 | 3.5779 | -2.6878 | -3.7037 | -0.3813 | -2.8646 | 6.6528 | 0.0332 | 0.5968 | 0.6381 | 0.9494 | 0.7176 | -131.1125 | -5.6339 | 2.4606 | 0.0512 | -6.2501 | -4.6147 | 1.7761 |  | -0.1811 | -1.7616 | 4.0125 | 3.3634 | 3.3503 | 1.0373 | 10.6862 | 14.177 | 14.7334 | 11.0565 | -0.0003 | -0.0029 | 0.0007 | 0.0042 | 0.0006 | -0.0009 | 0.0061 | 0.0011 | -0.0068 | -360.1742 | 17.4685 | -360.5681 | 17.7313 | -360.8758 | 18.1379 | -360.845 | 17.5157 | -352.7244 | 18.7785 | -352.8044 | 16.8505
12:01 | 2463 | 29.836 | 197.2061 | 442.7528 | 448.2393 | -19.0568 | -46.4057 | 6.655 | 3.6278 | -2.6822 | -3.7937 | -0.3726 | -2.9048 | 6.7326 | 0.1258 | 0.5967 | 0.6358 | 0.9517 | 0.7177 | -131.2137 | -5.5721 | 2.4853 | 0.095 | -6.1318 | -4.6088 | 1.8457 |  | -0.2212 | -1.8606 | 4.0139 | 3.3609 | 3.35 | 1.0369 | 10.7127 | 14.1633 | 14.7617 | 11.0421 | 0.0006 | -0.0027 | 0.001 | 0.0044 | 0.001 | -0.0005 | 0.023 | -0.007 | 0.0056 | -360.1342 | 17.3946 | -360.4635 | 17.7108 | -360.8204 | 18.1584 | -360.885 | 17.5075 | -352.6444 | 18.7312 | -352.7367 | 16.8299
12:01 | 2464 | 29.8347 | 197.1676 | 442.7301 | 448.217 | -19.0253 | -46.3788 | 6.6769 | 3.632 | -2.666 | -3.6482 | -0.3709 | -2.8731 | 6.6488 | 0.0836 | 0.5988 | 0.6401 | 0.951 | 0.7166 | -131.1259 | -5.6545 | 2.4597 | 0.1502 | -6.2075 | -4.6553 | 1.8948 |  | -0.1439 | -1.8032 | 4.0148 | 3.3627 | 3.3519 | 1.0359 | 10.7093 | 14.1887 | 14.7749 | 11.0273 | 0.0002 | -0.0032 | 0.0005 | 0.0037 | 0.0001 | -0.0006 | -0.004 | -0.0032 | -0.0187 | -360.2081 | 17.4295 | -360.4789 | 17.6841 | -360.8297 | 18.1871 | -360.9527 | 17.5547 | -352.7614 | 18.7436 | -352.6813 | 16.8032
12:01 | 2465 | 29.8646 | 197.1485 | 442.7424 | 448.2834 | -19.0798 | -46.3249 | 6.7008 | 3.6996 | -2.6548 | -3.5963 | -0.4085 | -2.8142 | 6.7051 | 0.1025 | 0.5982 | 0.6368 | 0.9565 | 0.7167 | -131.1432 | -5.6136 | 2.4597 | 0.0901 | -6.1732 | -4.6544 | 1.833 |  | -0.1708 | -1.8693 | 4.0144 | 3.3641 | 3.3502 | 1.0372 | 10.6608 | 14.1571 | 14.7238 | 11.0201 | -0.0004 | -0.0029 | 0.0005 | 0.0036 | 0.0016 | -0.0003 | 0.0025 | -0.0112 | -0.022 | -360.1988 | 17.4418 | -360.5035 | 17.68 | -360.7897 | 18.1522 | -360.8758 | 17.526 | -352.7275 | 18.7518 | -352.706 | 16.8074
12:01 | 2466 | 29.9648 | 197.1953 | 442.7548 | 448.2476 | -18.9845 | -46.2847 | 6.7023 | 3.5798 | -2.78 | -3.7243 | -0.433 | -2.9077 | 6.6696 | 0.1161 | 0.5983 | 0.6381 | 0.9542 | 0.7161 | -131.2273 | -5.6153 | 2.5523 | 0.1913 | -6.2254 | -4.6884 | 1.7965 |  | -0.1834 | -1.8811 | 4.0152 | 3.3641 | 3.352 | 1.0381 | 10.7011 | 14.1692 | 14.7512 | 11.0359 | -0.0001 | -0.0025 | 0.0008 | 0.0036 | 0.0006 | 0.0001 | 0.0201 | -0.005 | 0.0156 | -360.1219 | 17.4315 | -360.5189 | 17.7477 | -360.8881 | 18.1728 | -360.9158 | 17.5116 | -352.6906 | 18.7538 | -352.749 | 16.8546
12:01 | 2467 | 29.9997 | 197.125 | 442.7418 | 448.3786 | -18.9407 | -46.2886 | 6.7238 | 3.7838 | -2.6547 | -3.7073 | -0.3007 | -2.8479 | 6.7095 | 0.1258 | 0.5975 | 0.6382 | 0.9548 | 0.7162 | -131.1775 | -5.6386 | 2.5867 | 0.3083 | -6.1669 | -4.5643 | 1.9109 |  | -0.1716 | -1.8898 | 4.0146 | 3.3676 | 3.3523 | 1.0379 | 10.662 | 14.1235 | 14.7183 | 11.0158 | 0 | -0.0025 | 0.001 | 0.004 | 0.0008 | -0.0006 | 0 | -0.0003 | -0.0112 | -360.1281 | 17.3823 | -360.4604 | 17.7067 | -360.845 | 18.1871 | -360.8881 | 17.5116 | -352.6906 | 18.7148 | -352.6844 | 16.8279
12:01 | 2468 | 29.9416 | 197.1135 | 442.6894 | 448.2972 | -18.9308 | -46.1813 | 6.7915 | 3.6958 | -2.6918 | -3.7202 | -0.3083 | -2.8222 | 6.7185 | 0.239 | 0.5989 | 0.6393 | 0.9558 | 0.7164 | -131.2512 | -5.7102 | 2.5012 | 0.2173 | -6.2084 | -4.6223 | 1.8638 |  | -0.186 | -1.9801 | 4.0138 | 3.365 | 3.3508 | 1.0374 | 10.6815 | 14.1666 | 14.7231 | 11.0172 | 0.0001 | -0.003 | 0.0007 | 0.0039 | 0.0007 | 0 | 0.0005 | -0.0081 | -0.0154 | -360.2173 | 17.4521 | -360.485 | 17.6944 | -360.8512 | 18.1645 | -360.9251 | 17.5506 | -352.7644 | 18.7703 | -352.7367 | 16.8197
12:01 | 2469 | 29.8909 | 197.2071 | 442.8542 | 448.324 | -19.0123 | -46.3035 | 6.6828 | 3.6579 | -2.6705 | -3.6643 | -0.3625 | -2.9461 | 6.7159 | 0.0619 | 0.5987 | 0.6369 | 0.9537 | 0.7171 | -131.1987 | -5.7162 | 2.5735 | 0.1981 | -6.0546 | -4.5752 | 1.9504 |  | -0.2403 | -2.007 | 4.0153 | 3.3674 | 3.3525 | 1.0384 | 10.6851 | 14.1756 | 14.7541 | 11.0327 | -0.0002 | -0.0026 | 0.0003 | 0.0037 | 0.0006 | -0.0008 | 0.0149 | -0.0106 | -0.0083 | -360.1404 | 17.4459 | -360.5343 | 17.7087 | -360.8235 | 18.1337 | -360.842 | 17.487 | -352.6598 | 18.7538 | -352.7398 | 16.8464
12:01 | 2470 | 29.8558 | 197.0945 | 442.5552 | 448.2129 | -19.0117 | -46.3134 | 6.7163 | 3.6774 | -2.7397 | -3.8385 | -0.4044 | -2.8589 | 6.7305 | 0.0353 | 0.5989 | 0.6405 | 0.9551 | 0.7171 | -131.285 | -5.7508 | 2.4272 | 0.1718 | -5.9801 | -4.5071 | 1.9286 |  | -0.1798 | -2.0258 | 4.0136 | 3.3661 | 3.3521 | 1.0379 | 10.6829 | 14.1441 | 14.7261 | 10.9967 | -0.0006 | -0.0029 | 0.0003 | 0.0039 | 0.0005 | -0.0006 | 0.0029 | -0.0077 | -0.0134 | -360.1711 | 17.4336 | -360.525 | 17.7272 | -360.8974 | 18.181 | -360.9158 | 17.5096 | -352.669 | 18.7477 | -352.7552 | 16.8525
12:01 | 2471 | 29.8695 | 197.2489 | 442.7459 | 448.2756 | -19.1245 | -46.4076 | 6.6598 | 3.6337 | -2.795 | -3.836 | -0.3713 | -2.8571 | 6.7419 | 0.0338 | 0.5987 | 0.6397 | 0.9541 | 0.7168 | -131.1659 | -5.6592 | 2.4339 | 0.2091 | -6.1046 | -4.7167 | 1.8924 |  | -0.1811 | -2.043 | 4.0144 | 3.3652 | 3.354 | 1.0383 | 10.7001 | 14.1445 | 14.7582 | 11.036 | -0.0003 | -0.003 | 0.0004 | 0.0037 | 0.0012 | -0.0001 | 0.0022 | -0.0177 | -0.0099 | -360.165 | 17.4069 | -360.4235 | 17.6574 | -360.7681 | 18.1584 | -360.9251 | 17.5404 | -352.749 | 18.7292 | -352.666 | 16.7971
12:01 | 2472 | 29.999 | 197.2083 | 442.7663 | 448.264 | -19.1103 | -46.3523 | 6.7047 | 3.7231 | -2.7959 | -3.6724 | -0.3475 | -2.753 | 6.6604 | 0.1275 | 0.5981 | 0.639 | 0.952 | 0.7174 | -131.291 | -5.7412 | 2.4695 | 0.278 | -6.0779 | -4.5468 | 1.9117 |  | -0.1757 | -1.8606 | 4.0144 | 3.3646 | 3.3512 | 1.0385 | 10.7035 | 14.177 | 14.7507 | 11.0276 | 0 | -0.0031 | 0.0003 | 0.0033 | 0.0008 | -0.0006 | -0.0009 | -0.0045 | -0.0262 | -360.2665 | 17.45 | -360.4973 | 17.6944 | -360.8297 | 18.1481 | -360.9035 | 17.5445 | -352.7429 | 18.7785 | -352.7306 | 16.8258
12:01 | 2473 | 30.0253 | 197.3735 | 442.7351 | 448.2863 | -19.0473 | -46.2688 | 6.6966 | 3.7168 | -2.8202 | -3.6457 | -0.4846 | -2.791 | 6.6997 | 0.1159 | 0.5977 | 0.6365 | 0.9501 | 0.7166 | -131.1811 | -5.7253 | 2.513 | 0.2329 | -6.0443 | -4.6061 | 1.9463 |  | -0.1092 | -1.9174 | 4.015 | 3.3609 | 3.3495 | 1.0364 | 10.6712 | 14.1386 | 14.6703 | 11.0075 | -0.0004 | -0.0031 | 0.0006 | 0.0034 | 0.0007 | -0.0003 | 0.0087 | -0.0129 | 0.0031 | -360.1558 | 17.4233 | -360.4881 | 17.7067 | -360.8666 | 18.1584 | -360.8327 | 17.4931 | -352.669 | 18.7374 | -352.7275 | 16.8443
12:01 | 2474 | 29.9744 | 197.2467 | 442.7908 | 448.2463 | -19.0825 | -46.2429 | 6.7302 | 3.6859 | -2.8649 | -3.6271 | -0.3654 | -2.7786 | 6.6563 | 0.2221 | 0.5993 | 0.6372 | 0.9544 | 0.7166 | -131.1902 | -5.7406 | 2.5447 | 0.2663 | -5.998 | -4.5893 | 2.0076 |  | -0.0529 | -1.8351 | 4.0151 | 3.3621 | 3.3521 | 1.0388 | 10.7138 | 14.182 | 14.7699 | 11.0485 | -0.0003 | -0.0023 | 0.0005 | 0.0039 | 0.0012 | -0.0006 | 0.0303 | -0.0185 | 0.017 | -360.1096 | 17.4007 | -360.4881 | 17.721 | -360.8881 | 18.2097 | -360.9712 | 17.528 | -352.6875 | 18.7333 | -352.7121 | 16.8484
12:01 | 2475 | 30.0788 | 197.3128 | 442.8193 | 448.3472 | -19.0155 | -46.1974 | 6.8199 | 3.657 | -2.8375 | -3.6456 | -0.5107 | -2.7479 | 6.6638 | 0.1957 | 0.5972 | 0.642 | 0.9545 | 0.7174 | -131.2371 | -5.7759 | 2.5158 | 0.2433 | -6.0122 | -4.5705 | 1.9578 |  | -0.1767 | -1.9223 | 4.0135 | 3.3641 | 3.3487 | 1.0395 | 10.729 | 14.1792 | 14.7408 | 11.0302 | 0 | -0.0026 | 0.0009 | 0.0034 | 0.0002 | -0.0004 | 0.0155 | -0.0098 | 0.0057 | -360.1773 | 17.4048 | -360.445 | 17.6779 | -360.8143 | 18.1625 | -360.9097 | 17.5342 | -352.6937 | 18.7333 | -352.6413 | 16.7991
12:01 | 2476 | 30.0278 | 197.3438 | 442.8243 | 448.4015 | -18.9613 | -46.1828 | 6.8677 | 3.6768 | -2.7976 | -3.7868 | -0.4251 | -2.7658 | 6.6159 | 0.099 | 0.5977 | 0.6385 | 0.9521 | 0.7185 | -131.2354 | -5.7106 | 2.5123 | 0.3034 | -5.9117 | -4.4676 | 2.0592 |  | -0.1493 | -1.9168 | 4.0136 | 3.3648 | 3.3513 | 1.0389 | 10.7231 | 14.2028 | 14.7787 | 11.0233 | 0.0002 | -0.003 | 0.0012 | 0.0042 | 0.001 | -0.0002 | 0.0099 | -0.0104 | -0.017 | -360.2235 | 17.4705 | -360.5466 | 17.721 | -360.8635 | 18.1522 | -360.8697 | 17.5219 | -352.7306 | 18.7846 | -352.7583 | 16.8361
12:01 | 2477 | 30.117 | 197.2699 | 442.7856 | 448.3783 | -19.0628 | -46.1994 | 6.801 | 3.7535 | -2.7707 | -3.725 | -0.2754 | -2.765 | 6.5162 | 0.2114 | 0.5987 | 0.6398 | 0.9566 | 0.7185 | -131.1036 | -5.5544 | 2.6383 | 0.3245 | -5.9247 | -4.4273 | 2.0185 |  | -0.1538 | -1.9653 | 4.0142 | 3.3639 | 3.3486 | 1.0383 | 10.7289 | 14.2142 | 14.7777 | 11.0121 | 0.0001 | -0.003 | 0.0005 | 0.0038 | 0.0003 | -0.0003 | 0 | -0.0064 | -0.0223 | -360.1281 | 17.4069 | -360.5158 | 17.721 | -360.8666 | 18.1625 | -360.845 | 17.4788 | -352.6537 | 18.7415 | -352.7213 | 16.8464
12:01 | 2478 | 30.0309 | 197.2833 | 442.7181 | 448.2879 | -19.0941 | -46.1323 | 6.7406 | 3.6873 | -2.899 | -3.8036 | -0.3579 | -2.7619 | 6.485 | 0.0224 | 0.5965 | 0.6371 | 0.9518 | 0.7179 | -131.1254 | -5.5417 | 2.6118 | 0.2334 | -5.9453 | -4.4531 | 2.0093 |  | -0.123 | -1.9345 | 4.0142 | 3.361 | 3.3504 | 1.0396 | 10.6874 | 14.1722 | 14.7452 | 11.0522 | -0.0007 | -0.0032 | 0.0002 | 0.004 | 0.0011 | -0.0004 | 0.0173 | -0.0133 | -0.0058 | -360.2111 | 17.4151 | -360.4819 | 17.7026 | -360.842 | 18.2015 | -360.9312 | 17.5404 | -352.709 | 18.7456 | -352.7152 | 16.8299
12:01 | 2479 | 30.1032 | 197.2948 | 442.7278 | 448.3986 | -19.0794 | -46.2176 | 6.7578 | 3.7555 | -2.764 | -3.6036 | -0.3031 | -2.7658 | 6.5363 | 0.1601 | 0.5977 | 0.6388 | 0.9539 | 0.7182 | -131.1341 | -5.6064 | 2.5767 | 0.2399 | -5.9932 | -4.4868 | 1.935 |  | -0.1483 | -1.8806 | 4.0147 | 3.3635 | 3.3485 | 1.0388 | 10.693 | 14.1727 | 14.7368 | 11.0164 | -0.0005 | -0.0026 | 0.0005 | 0.004 | 0.001 | -0.0001 | 0.0072 | -0.0069 | 0.0001 | -360.205 | 17.4336 | -360.4666 | 17.6738 | -360.7897 | 18.1358 | -360.8974 | 17.5301 | -352.7367 | 18.7538 | -352.6813 | 16.7991
12:01 | 2480 | 30.0778 | 197.2471 | 442.766 | 448.455 | -19.1104 | -46.1572 | 6.7884 | 3.6982 | -2.8713 | -3.5835 | -0.3674 | -2.7119 | 6.6382 | 0.1661 | 0.5972 | 0.6426 | 0.9534 | 0.7176 | -131.0657 | -5.6558 | 2.5616 | 0.2853 | -6.0517 | -4.5237 | 2.0307 |  | -0.1898 | -1.8501 | 4.0151 | 3.3633 | 3.3499 | 1.0412 | 10.699 | 14.1836 | 14.7673 | 11.0179 | -0.0001 | -0.0034 | 0.0003 | 0.0037 | 0.0007 | -0.0008 | -0.0002 | -0.0146 | -0.0156 | -360.2019 | 17.4521 | -360.5343 | 17.7169 | -360.842 | 18.1584 | -360.8881 | 17.5219 | -352.709 | 18.7826 | -352.7706 | 16.8361
12:01 | 2481 | 29.9845 | 197.2738 | 442.7607 | 448.4309 | -19.0954 | -46.1025 | 6.7954 | 3.6911 | -2.7484 | -3.5818 | -0.4077 | -2.7792 | 6.5724 | 0.1459 | 0.5983 | 0.6379 | 0.955 | 0.7175 | -131.1562 | -5.6664 | 2.5347 | 0.2538 | -6.0923 | -4.5559 | 1.9648 |  | -0.0399 | -1.9118 | 4.0141 | 3.3612 | 3.3517 | 1.0395 | 10.6736 | 14.1464 | 14.7172 | 11.0046 | 0.0001 | -0.003 | 0.0004 | 0.0036 | 0.0007 | -0.0009 | 0.0058 | -0.0099 | -0.0102 | -360.0973 | 17.3884 | -360.4512 | 17.7005 | -360.8481 | 18.181 | -360.9097 | 17.4911 | -352.6506 | 18.7251 | -352.6906 | 16.8279
12:01 | 2482 | 29.946 | 197.241 | 442.7696 | 448.325 | -19.0641 | -46.3322 | 6.7129 | 3.686 | -2.7168 | -3.5363 | -0.4306 | -2.7812 | 6.5933 | 0.0945 | 0.5977 | 0.643 | 0.9507 | 0.7158 | -131.1563 | -5.7053 | 2.5373 | 0.1324 | -6.1367 | -4.5094 | 1.9455 |  | -0.0172 | -1.8499 | 4.0156 | 3.3647 | 3.3506 | 1.0392 | 10.6677 | 14.1583 | 14.7425 | 10.9923 | -0.0004 | -0.0031 | 0.0012 | 0.0038 | 0.0003 | -0.0004 | 0.0017 | 0.005 | -0.0121 | -360.1865 | 17.411 | -360.4666 | 17.6985 | -360.8574 | 18.1933 | -360.9589 | 17.5486 | -352.706 | 18.7415 | -352.6537 | 16.8176
12:01 | 2483 | 29.9747 | 197.2339 | 442.8033 | 448.3993 | -18.9182 | -46.2438 | 6.8176 | 3.7125 | -2.7036 | -3.5879 | -0.3906 | -2.7145 | 6.6451 | 0.1861 | 0.5972 | 0.6376 | 0.9529 | 0.7169 | -131.1688 | -5.741 | 2.5468 | 0.2296 | -6.0566 | -4.4576 | 1.9587 |  | -0.048 | -1.8831 | 4.0139 | 3.362 | 3.3512 | 1.0385 | 10.6909 | 14.1755 | 14.7472 | 11.0504 | -0.0006 | -0.003 | 0.0009 | 0.0039 | 0.0007 | -0.0008 | 0.0126 | -0.0103 | -0.0027 | -360.1835 | 17.4439 | -360.4973 | 17.6923 | -360.7897 | 18.1399 | -360.8574 | 17.5157 | -352.6844 | 18.7538 | -352.709 | 16.8156
12:01 | 2484 | 29.9911 | 197.2822 | 442.7341 | 448.3936 | -19.0266 | -46.3033 | 6.8448 | 3.6915 | -2.6603 | -3.4751 | -0.4203 | -2.7536 | 6.6237 | 0.1217 | 0.5994 | 0.639 | 0.9525 | 0.7177 | -131.1872 | -5.5921 | 2.5823 | 0.3226 | -5.9673 | -4.5937 | 2.0839 |  | -0.0658 | -1.895 | 4.0146 | 3.3608 | 3.3512 | 1.0385 | 10.6976 | 14.189 | 14.7539 | 11.0612 | 0.0001 | -0.0028 | 0.0011 | 0.0044 | 0.0005 | -0.0004 | -0.0078 | -0.0128 | -0.0216 | -360.1465 | 17.4315 | -360.5589 | 17.7457 | -360.9004 | 18.1748 | -360.8789 | 17.4952 | -352.6598 | 18.7723 | -352.7552 | 16.8669
12:01 | 2485 | 30.0413 | 197.3435 | 442.9086 | 448.3671 | -19.1124 | -46.2848 | 6.7833 | 3.7195 | -2.6256 | -3.364 | -0.3559 | -2.7768 | 6.6045 | 0.1664 | 0.5982 | 0.64 | 0.9523 | 0.7169 | -131.2228 | -5.7532 | 2.499 | 0.2687 | -6.0219 | -4.4908 | 2.0528 |  | -0.0224 | -1.929 | 4.0147 | 3.3627 | 3.3497 | 1.0379 | 10.7405 | 14.2026 | 14.8066 | 11.0583 | 0.0001 | -0.0033 | 0.0005 | 0.004 | 0.0009 | -0.0005 | -0.004 | -0.0186 | -0.0262 | -360.1435 | 17.409 | -360.4666 | 17.7026 | -360.8327 | 18.1666 | -360.9097 | 17.5075 | -352.6229 | 18.7353 | -352.6813 | 16.8217
12:01 | 2486 | 29.9779 | 197.309 | 442.8253 | 448.3094 | -19.1275 | -46.3471 | 6.7203 | 3.6806 | -2.6929 | -3.4925 | -0.3538 | -2.7306 | 6.7345 | 0.0698 | 0.5971 | 0.6378 | 0.9545 | 0.7163 | -131.2299 | -5.6982 | 2.6313 | 0.1986 | -6.0466 | -4.4902 | 2.0815 |  | -0.077 | -1.9462 | 4.0149 | 3.3624 | 3.3524 | 1.0388 | 10.7162 | 14.1783 | 14.7531 | 11.0341 | -0.0001 | -0.0028 | 0.0004 | 0.0042 | 0.0007 | 0 | 0.0207 | -0.0015 | 0.0004 | -360.2235 | 17.4418 | -360.5035 | 17.6882 | -360.802 | 18.1666 | -360.922 | 17.5568 | -352.7675 | 18.7682 | -352.706 | 16.8156
12:01 | 2487 | 30.0717 | 197.3639 | 442.8221 | 448.4315 | -19.1288 | -46.344 | 6.7189 | 3.6959 | -2.6972 | -3.5308 | -0.322 | -2.6895 | 6.6695 | 0.1994 | 0.5981 | 0.6392 | 0.9547 | 0.7178 | -131.1323 | -5.7284 | 2.5097 | 0.2223 | -5.9864 | -4.4593 | 2.1 |  | -0.1476 | -1.9243 | 4.0146 | 3.3626 | 3.3527 | 1.0384 | 10.7058 | 14.2082 | 14.7998 | 11.0529 | -0.0002 | -0.0027 | 0.0004 | 0.0035 | 0.0008 | -0.001 | 0.0043 | 0.0023 | -0.0068 | -360.2019 | 17.4521 | -360.4973 | 17.7108 | -360.805 | 18.1296 | -360.8574 | 17.5116 | -352.7029 | 18.7641 | -352.7275 | 16.8197
12:01 | 2488 | 30.1096 | 197.3136 | 442.8197 | 448.395 | -19.0545 | -46.3263 | 6.7633 | 3.741 | -2.7116 | -3.3863 | -0.3647 | -2.7614 | 6.6672 | 0.1592 | 0.5986 | 0.6405 | 0.953 | 0.7168 | -131.1369 | -5.6169 | 2.5137 | 0.2929 | -5.9761 | -4.4259 | 2.1227 |  | -0.0675 | -1.9738 | 4.0138 | 3.3588 | 3.3515 | 1.039 | 10.7255 | 14.199 | 14.7736 | 11.0204 | -0.0002 | -0.003 | 0.0003 | 0.0035 | 0.0003 | -0.0004 | 0.0028 | -0.0039 | 0.005 | -360.1742 | 17.4151 | -360.4912 | 17.7477 | -360.8604 | 18.183 | -360.9097 | 17.5096 | -352.666 | 18.7436 | -352.7029 | 16.8505
12:01 | 2489 | 30.1109 | 197.3008 | 442.878 | 448.3995 | -19.0738 | -46.2726 | 6.732 | 3.7922 | -2.642 | -3.3393 | -0.3844 | -2.7524 | 6.6122 | 0.1531 | 0.5988 | 0.6398 | 0.9527 | 0.7151 | -131.2237 | -5.7218 | 2.4905 | 0.2499 | -5.9897 | -4.4288 | 2.1007 |  | 0.0017 | -2.0101 | 4.0149 | 3.3649 | 3.3494 | 1.0374 | 10.7002 | 14.1384 | 14.7619 | 11.0309 | 0.0004 | -0.0028 | 0.0003 | 0.0031 | 0.0007 | -0.0012 | 0.0079 | -0.0129 | -0.0151 | -360.1465 | 17.3925 | -360.4481 | 17.7005 | -360.8143 | 18.1933 | -360.9497 | 17.5321 | -352.666 | 18.723 | -352.6321 | 16.8074
12:01 | 2490 | 30.0868 | 197.2639 | 442.827 | 448.3353 | -19.0682 | -46.3452 | 6.8145 | 3.7518 | -2.713 | -3.4602 | -0.4097 | -2.7588 | 6.6652 | 0.0927 | 0.598 | 0.6407 | 0.9505 | 0.7168 | -131.212 | -5.671 | 2.5504 | 0.331 | -6.0016 | -4.4618 | 2.0624 |  | -0.1356 | -1.9684 | 4.015 | 3.3659 | 3.3481 | 1.0385 | 10.6921 | 14.1651 | 14.7255 | 11.0169 | -0.0003 | -0.0032 | 0.001 | 0.0035 | 0.0007 | -0.0007 | -0.0103 | -0.0161 | -0.0257 | -360.1681 | 17.4233 | -360.4819 | 17.7252 | -360.8112 | 18.1584 | -360.9127 | 17.5321 | -352.709 | 18.7579 | -352.6937 | 16.8217
12:01 | 2491 | 30.1172 | 197.3229 | 442.8307 | 448.4401 | -19.0751 | -46.3185 | 6.8995 | 3.762 | -2.6796 | -3.4613 | -0.2576 | -2.7214 | 6.6613 | 0.1561 | 0.5989 | 0.6405 | 0.9535 | 0.7164 | -131.18 | -5.701 | 2.6081 | 0.3179 | -6.0913 | -4.4285 | 2.0047 |  | -0.1643 | -1.975 | 4.0153 | 3.3642 | 3.3513 | 1.0379 | 10.6921 | 14.1536 | 14.737 | 11.0342 | -0.0003 | -0.0025 | 0.0008 | 0.0038 | 0.0005 | -0.0002 | 0.0036 | -0.0118 | -0.0211 | -360.1773 | 17.4336 | -360.5435 | 17.7436 | -360.8727 | 18.1563 | -360.8389 | 17.4952 | -352.6813 | 18.7518 | -352.7121 | 16.8464
12:01 | 2492 | 30.094 | 197.3023 | 442.8509 | 448.3847 | -19.0675 | -46.1478 | 6.8779 | 3.6725 | -2.7773 | -3.5667 | -0.3154 | -2.8131 | 6.6412 | 0.151 | 0.5973 | 0.6396 | 0.9548 | 0.7173 | -131.1302 | -5.6716 | 2.6338 | 0.2216 | -6.1332 | -4.5592 | 1.9893 |  | -0.0475 | -1.8553 | 4.0161 | 3.3609 | 3.3506 | 1.039 | 10.7117 | 14.1734 | 14.735 | 11.0129 | -0.0003 | -0.0026 | 0.0009 | 0.0042 | 0.0009 | -0.0007 | 0.0097 | -0.0066 | 0.0092 | -360.1096 | 17.4172 | -360.4942 | 17.7539 | -360.8881 | 18.181 | -360.8727 | 17.5034 | -352.6629 | 18.7456 | -352.7306 | 16.8628
12:01 | 2493 | 30.0771 | 197.2843 | 442.8936 | 448.448 | -19.1063 | -46.0074 | 6.8587 | 3.7259 | -2.7959 | -3.4427 | -0.353 | -2.8896 | 6.5699 | 0.1372 | 0.599 | 0.6433 | 0.9552 | 0.7163 | -131.1601 | -5.79 | 2.6131 | 0.1577 | -6.1091 | -4.5613 | 1.9801 |  | -0.1521 | -1.9201 | 4.0146 | 3.3621 | 3.3496 | 1.0386 | 10.7278 | 14.213 | 14.7879 | 11.0688 | -0.0001 | -0.0032 | 0.0008 | 0.0038 | 0.0007 | 0.0001 | 0.0195 | -0.0192 | -0.008 | -360.1527 | 17.4192 | -360.4542 | 17.7108 | -360.802 | 18.1728 | -360.9004 | 17.5342 | -352.6967 | 18.7333 | -352.6629 | 16.8032
12:01 | 2494 | 30.1766 | 197.3478 | 442.8411 | 448.421 | -19.1415 | -45.9871 | 6.9194 | 3.7292 | -2.7146 | -3.3991 | -0.3329 | -2.833 | 6.7294 | 0.2612 | 0.5976 | 0.6399 | 0.9563 | 0.7167 | -131.0882 | -5.6869 | 2.5835 | 0.1053 | -6.1992 | -4.5551 | 2.0015 |  | -0.0252 | -1.8539 | 4.0143 | 3.3658 | 3.3481 | 1.0385 | 10.7174 | 14.185 | 14.7582 | 11.0302 | -0.0001 | -0.0032 | -0.0003 | 0.0034 | 0.0008 | -0.0009 | 0.0319 | 0.0087 | -0.0028 | -360.2173 | 17.4541 | -360.5158 | 17.719 | -360.805 | 18.1522 | -360.8727 | 17.5424 | -352.7552 | 18.7867 | -352.7367 | 16.832
12:01 | 2495 | 30.1603 | 197.3998 | 442.8445 | 448.4844 | -19.0362 | -45.8856 | 6.9247 | 3.7596 | -2.7208 | -3.4714 | -0.3663 | -2.8038 | 6.6323 | 0.1408 | 0.598 | 0.64 | 0.9572 | 0.7157 | -131.155 | -5.7483 | 2.5132 | 0.0462 | -6.2469 | -4.5483 | 1.999 |  | -0.0129 | -1.8315 | 4.0142 | 3.3626 | 3.349 | 1.0373 | 10.7117 | 14.1675 | 14.7687 | 11.0594 | -0.0007 | -0.0029 | 0.0004 | 0.0037 | 0.0001 | -0.0007 | 0.0008 | -0.0107 | -0.0023 | -360.1865 | 17.4397 | -360.5004 | 17.7313 | -360.8389 | 18.1563 | -360.8604 | 17.5055 | -352.6937 | 18.7661 | -352.7152 | 16.834
12:01 | 2496 | 30.1257 | 197.2907 | 442.8261 | 448.4782 | -19.0152 | -45.9694 | 6.8546 | 3.7673 | -2.7005 | -3.6452 | -0.4112 | -2.8549 | 6.771 | 0.1333 | 0.5979 | 0.6395 | 0.9529 | 0.7169 | -131.1965 | -5.6991 | 2.4838 | 0.0172 | -6.2373 | -4.6675 | 2.0153 |  | 0.0356 | -1.8547 | 4.0144 | 3.3605 | 3.3472 | 1.0386 | 10.7255 | 14.1526 | 14.7667 | 11.0555 | -0.0004 | -0.0027 | -0.0001 | 0.0029 | 0.0008 | -0.0007 | 0.0001 | -0.0082 | -0.0078 | -360.1527 | 17.4069 | -360.4727 | 17.7313 | -360.845 | 18.1974 | -360.9281 | 17.5116 | -352.6629 | 18.7436 | -352.6875 | 16.8381
12:01 | 2497 | 30.1511 | 197.2098 | 442.8794 | 448.4028 | -18.9698 | -45.9856 | 6.8775 | 3.8782 | -2.68 | -3.5343 | -0.3797 | -2.896 | 6.7153 | 0.1615 | 0.5989 | 0.6397 | 0.9554 | 0.718 | -131.1675 | -5.7807 | 2.5377 | 0.0109 | -6.1741 | -4.6473 | 1.9683 |  | -0.0637 | -1.8423 | 4.015 | 3.365 | 3.3474 | 1.0382 | 10.6955 | 14.1802 | 14.7585 | 11.0143 | -0.0003 | -0.0034 | 0.0008 | 0.0038 | 0.0001 | -0.0008 | 0.0015 | -0.0092 | -0.0101 | -360.2019 | 17.409 | -360.4419 | 17.7005 | -360.8235 | 18.183 | -360.9281 | 17.5383 | -352.6937 | 18.7312 | -352.6383 | 16.7971
12:01 | 2498 | 30.1545 | 197.3098 | 442.8327 | 448.4732 | -18.9703 | -45.9391 | 6.8715 | 3.788 | -2.6859 | -3.5969 | -0.418 | -2.872 | 6.7167 | 0.1064 | 0.6 | 0.6402 | 0.9563 | 0.7192 | -131.1566 | -5.7024 | 2.6969 | 0.2377 | -6.1902 | -4.6035 | 1.951 |  | 0.0032 | -1.719 | 4.0143 | 3.3646 | 3.3485 | 1.0386 | 10.7023 | 14.1817 | 14.7562 | 11.0204 | 0 | -0.0032 | 0.0011 | 0.0043 | 0.0007 | -0.0006 | 0.0057 | -0.0105 | 0.0064 | -360.1927 | 17.4397 | -360.5219 | 17.7128 | -360.8081 | 18.1666 | -360.9066 | 17.528 | -352.7306 | 18.7682 | -352.7367 | 16.8361
12:01 | 2499 | 30.1749 | 197.3978 | 442.8123 | 448.4862 | -18.8633 | -45.9004 | 6.8236 | 3.8646 | -2.6687 | -3.6338 | -0.3563 | -2.759 | 6.7517 | 0.2728 | 0.6003 | 0.642 | 0.9545 | 0.7173 | -131.1638 | -5.6495 | 2.5786 | 0.1605 | -6.1827 | -4.5532 | 1.9835 |  | -0.0334 | -1.8271 | 4.0139 | 3.3635 | 3.3485 | 1.039 | 10.7058 | 14.2084 | 14.8008 | 11.0352 | -0.0005 | -0.0031 | 0.0006 | 0.0035 | 0.0003 | -0.0004 | 0.017 | -0.009 | -0.009 | -360.125 | 17.4213 | -360.5096 | 17.7477 | -360.8974 | 18.1666 | -360.845 | 17.4931 | -352.6444 | 18.7497 | -352.7244 | 16.8505
12:01 | 2500 | 30.1276 | 197.3276 | 442.7853 | 448.4428 | -18.9663 | -46.0246 | 6.853 | 3.811 | -2.7585 | -3.5719 | -0.3749 | -2.8607 | 6.7496 | 0.164 | 0.598 | 0.6386 | 0.9568 | 0.7186 | -131.1236 | -5.6357 | 2.5248 | 0.0728 | -6.1531 | -4.583 | 1.8979 |  | -0.0542 | -1.877 | 4.0136 | 3.3613 | 3.35 | 1.0398 | 10.7128 | 14.163 | 14.7653 | 11.0601 | -0.0004 | -0.0027 | 0.0002 | 0.0038 | 0.0009 | -0.0003 | 0.0102 | 0.0067 | -0.017 | -360.1465 | 17.4069 | -360.5127 | 17.7395 | -360.8604 | 18.1851 | -360.8727 | 17.5096 | -352.6475 | 18.7415 | -352.709 | 16.8402
12:01 | 2501 | 30.1536 | 197.3589 | 442.9133 | 448.4539 | -18.8699 | -45.93 | 6.8319 | 3.737 | -2.9172 | -3.6685 | -0.4359 | -2.8447 | 6.718 | 0.2241 | 0.5982 | 0.6391 | 0.9555 | 0.7175 | -131.0866 | -5.6652 | 2.5067 | 0.1247 | -6.1978 | -4.6705 | 1.9648 |  | -0.115 | -1.9528 | 4.0145 | 3.3638 | 3.3486 | 1.0393 | 10.7046 | 14.1842 | 14.7658 | 11.0511 | 0.0002 | -0.003 | 0.0009 | 0.0043 | 0.0008 | -0.0004 | 0.0038 | -0.0059 | -0.004 | -360.2142 | 17.4213 | -360.4666 | 17.6985 | -360.8081 | 18.1687 | -360.9189 | 17.5404 | -352.7244 | 18.7415 | -352.6967 | 16.8074
12:01 | 2502 | 30.2189 | 197.35 | 442.9164 | 448.3628 | -18.9334 | -45.9 | 6.9037 | 3.7574 | -2.8937 | -3.5572 | -0.3554 | -2.8875 | 6.7707 | 0.189 | 0.599 | 0.6392 | 0.9531 | 0.7173 | -131.1382 | -5.6282 | 2.5673 | 0.1127 | -6.1582 | -4.5012 | 1.8899 |  | -0.0783 | -1.9314 | 4.0145 | 3.3641 | 3.3497 | 1.0395 | 10.7197 | 14.1989 | 14.7841 | 11.0612 | -0.0003 | -0.0033 | -0.0001 | 0.0037 | 0.0004 | -0.0007 | 0.0073 | -0.0166 | -0.0135 | -360.2173 | 17.4459 | -360.5127 | 17.7169 | -360.7743 | 18.1399 | -360.882 | 17.5342 | -352.7183 | 18.7785 | -352.7521 | 16.8258
12:01 | 2503 | 30.1093 | 197.3152 | 442.8871 | 448.3937 | -19.0281 | -46.0832 | 6.7661 | 3.8528 | -2.8442 | -3.5244 | -0.3947 | -2.8464 | 6.6872 | 0.2509 | 0.5984 | 0.6399 | 0.9524 | 0.7179 | -131.0978 | -5.6561 | 2.716 | 0.1383 | -6.0452 | -4.6535 | 1.8648 |  | -0.0616 | -1.8054 | 4.0134 | 3.3634 | 3.3503 | 1.0389 | 10.7093 | 14.154 | 14.7691 | 11.0273 | -0.0002 | -0.0028 | 0.0005 | 0.0038 | 0.0014 | -0.0005 | 0.0145 | -0.009 | 0.0028 | -360.1835 | 17.4315 | -360.5219 | 17.7272 | -360.8604 | 18.1666 | -360.8697 | 17.5075 | -352.6998 | 18.762 | -352.7306 | 16.8381
12:01 | 2504 | 30.2159 | 197.3498 | 442.8852 | 448.4175 | -19.0843 | -46.1699 | 6.8245 | 3.8179 | -2.7791 | -3.5897 | -0.3963 | -2.8891 | 6.6368 | 0.243 | 0.5988 | 0.6405 | 0.9545 | 0.7194 | -131.0899 | -5.6725 | 2.6921 | 0.1686 | -6.1195 | -4.5334 | 1.9744 |  | -0.021 | -1.8158 | 4.0139 | 3.365 | 3.353 | 1.0385 | 10.693 | 14.1783 | 14.7705 | 11.0052 | -0.0004 | -0.0027 | 0.0006 | 0.0038 | 0.0006 | -0.0003 | 0.0051 | -0.0084 | -0.0184 | -360.165 | 17.3843 | -360.4266 | 17.7067 | -360.8327 | 18.1851 | -360.9158 | 17.5178 | -352.6906 | 18.721 | -352.6721 | 16.8238
12:01 | 2505 | 30.1532 | 197.2533 | 442.9623 | 448.5309 | -19.0746 | -46.1381 | 6.7722 | 3.9297 | -2.7345 | -3.5528 | -0.3307 | -2.7658 | 6.7649 | 0.2056 | 0.5983 | 0.6413 | 0.9589 | 0.7178 | -131.0667 | -5.6182 | 2.656 | 0.2098 | -6.0183 | -4.5484 | 1.9986 |  | 0.0085 | -1.8797 | 4.0149 | 3.3621 | 3.353 | 1.04 | 10.6932 | 14.1721 | 14.75 | 11.0295 | -0.0004 | -0.0029 | 0.0006 | 0.0036 | 0.0009 | -0.0005 | 0.0058 | -0.0104 | -0.0119 | -360.1835 | 17.4233 | -360.4696 | 17.7128 | -360.8235 | 18.1851 | -360.9404 | 17.5486 | -352.6906 | 18.7415 | -352.6813 | 16.8053
12:01 | 2506 | 30.1407 | 197.2317 | 442.9391 | 448.4131 | -19.0658 | -46.106 | 6.7756 | 3.8543 | -2.7488 | -3.5941 | -0.3548 | -2.8052 | 6.7606 | 0.2416 | 0.5982 | 0.6401 | 0.9547 | 0.7187 | -131.1712 | -5.6585 | 2.5435 | 0.2131 | -6.0599 | -4.5331 | 1.9795 |  | 0.0083 | -1.8275 | 4.0145 | 3.363 | 3.3483 | 1.0397 | 10.6804 | 14.171 | 14.6976 | 10.9934 | 0.0004 | -0.0029 | 0.0011 | 0.0039 | 0.0002 | -0.0006 | 0.0061 | 0.0069 | 0.0023 | -360.1988 | 17.4254 | -360.5004 | 17.7169 | -360.8174 | 18.144 | -360.8543 | 17.5137 | -352.6813 | 18.762 | -352.7183 | 16.832
12:01 | 2507 | 30.1885 | 197.3451 | 442.8011 | 448.5308 | -19.156 | -46.1266 | 6.7513 | 3.9149 | -2.7873 | -3.6464 | -0.3037 | -2.8209 | 6.7404 | 0.2414 | 0.5995 | 0.6384 | 0.9555 | 0.7187 | -131.1258 | -5.5864 | 2.5664 | 0.1906 | -6.0903 | -4.4696 | 1.9246 |  | 0.0424 | -1.812 | 4.0158 | 3.365 | 3.3484 | 1.0392 | 10.7208 | 14.2177 | 14.8107 | 11.0616 | 0 | -0.0031 | 0.0008 | 0.0037 | 0.0011 | -0.0007 | 0.0004 | -0.0105 | -0.0117 | -360.1742 | 17.4315 | -360.5373 | 17.7744 | -360.9189 | 18.1748 | -360.9035 | 17.5034 | -352.6721 | 18.7559 | -352.7552 | 16.8669
12:02 | 2508 | 30.2223 | 197.2651 | 442.7904 | 448.5011 | -19.1059 | -46.1298 | 6.7805 | 3.9554 | -2.7591 | -3.6865 | -0.3266 | -2.8475 | 6.7227 | 0.2769 | 0.5987 | 0.6404 | 0.955 | 0.7195 | -131.1639 | -5.6581 | 2.5766 | 0.0911 | -6.1315 | -4.5398 | 1.9539 |  | 0.0232 | -1.8613 | 4.0145 | 3.3644 | 3.3497 | 1.0375 | 10.7313 | 14.1816 | 14.7609 | 11.0439 | -0.0001 | -0.0024 | 0.0004 | 0.0036 | 0.0004 | -0.0005 | 0.008 | -0.0149 | 0.0037 | -360.1311 | 17.4048 | -360.4666 | 17.7128 | -360.8235 | 18.1789 | -360.9035 | 17.4972 | -352.6352 | 18.7374 | -352.669 | 16.8299
12:02 | 2509 | 30.3158 | 197.3909 | 442.9509 | 448.5142 | -19.0403 | -46.1573 | 6.8202 | 3.9471 | -2.6026 | -3.6073 | -0.2565 | -2.8515 | 6.7808 | 0.1804 | 0.5987 | 0.6394 | 0.9557 | 0.7197 | -131.1456 | -5.5733 | 2.6039 | 0.1388 | -6.0813 | -4.5825 | 1.9306 |  | 0.0222 | -1.907 | 4.0153 | 3.3636 | 3.3497 | 1.0382 | 10.7092 | 14.1947 | 14.806 | 11.0612 | -0.0002 | -0.0027 | 0.0008 | 0.0042 | 0.0008 | -0.0003 | 0.0159 | -0.0154 | -0.0252 | -360.2296 | 17.4377 | -360.5035 | 17.7087 | -360.7897 | 18.1707 | -360.9558 | 17.5486 | -352.746 | 18.7703 | -352.7152 | 16.8197
12:02 | 2510 | 30.3381 | 197.4397 | 442.9393 | 448.5647 | -19.0342 | -46.1143 | 6.8193 | 3.848 | -2.5867 | -3.519 | -0.2766 | -2.8492 | 6.7351 | 0.2098 | 0.598 | 0.6398 | 0.9554 | 0.7193 | -131.1477 | -5.6395 | 2.5766 | 0.0987 | -6.0856 | -4.5974 | 1.8796 |  | 0.1421 | -1.8 | 4.0159 | 3.3653 | 3.3506 | 1.0393 | 10.7301 | 14.1921 | 14.7838 | 11.0655 | 0.0001 | -0.0028 | 0.0001 | 0.0033 | 0.0007 | -0.0008 | -0.0077 | -0.0068 | -0.006 | -360.2142 | 17.4459 | -360.4942 | 17.7128 | -360.805 | 18.1317 | -360.8481 | 17.5137 | -352.7029 | 18.7723 | -352.709 | 16.8299
12:02 | 2511 | 30.2832 | 197.3882 | 442.9487 | 448.5003 | -19.0146 | -46.0196 | 6.8119 | 3.8803 | -2.484 | -3.5679 | -0.2114 | -2.8953 | 6.6484 | 0.219 | 0.5995 | 0.6385 | 0.9563 | 0.7176 | -131.0962 | -5.5121 | 2.574 | 0.0678 | -6.0768 | -4.5807 | 1.9109 |  | 0.0179 | -1.8144 | 4.0141 | 3.3622 | 3.3486 | 1.0388 | 10.7185 | 14.1691 | 14.7733 | 11.0478 | 0.0002 | -0.003 | 0.0008 | 0.0042 | 0.0009 | -0.0003 | 0.0193 | -0.0107 | -0.0081 | -360.1804 | 17.4274 | -360.5066 | 17.7416 | -360.8943 | 18.1933 | -360.9066 | 17.5157 | -352.6813 | 18.7497 | -352.7275 | 16.8525
12:02 | 2512 | 30.2199 | 197.4082 | 443.0199 | 448.5459 | -18.9447 | -46.0649 | 6.8335 | 3.8015 | -2.5601 | -3.4808 | -0.2755 | -2.8678 | 6.6928 | 0.1678 | 0.5972 | 0.6384 | 0.9547 | 0.7196 | -131.1025 | -5.5909 | 2.5332 | 0.2151 | -6.1063 | -4.5379 | 1.9555 |  | 0.0155 | -1.8353 | 4.014 | 3.3636 | 3.3516 | 1.0385 | 10.6792 | 14.1644 | 14.7562 | 11.0089 | -0.0002 | -0.0024 | 0.0008 | 0.004 | 0.0012 | -0.0005 | 0.0168 | -0.013 | 0.0062 | -360.1558 | 17.3987 | -360.4173 | 17.6902 | -360.7989 | 18.1912 | -360.9281 | 17.5342 | -352.6813 | 18.7271 | -352.6752 | 16.793
12:02 | 2513 | 30.2718 | 197.5392 | 443.0827 | 448.6314 | -19.092 | -46.099 | 6.7903 | 3.8137 | -2.533 | -3.5061 | -0.2109 | -2.843 | 6.7039 | 0.1352 | 0.5985 | 0.6387 | 0.9556 | 0.7177 | -131.1008 | -5.6866 | 2.5011 | 0.2015 | -6.0323 | -4.5361 | 1.9651 |  | 0.026 | -1.8831 | 4.0155 | 3.3658 | 3.3502 | 1.04 | 10.6713 | 14.1384 | 14.7156 | 11.0425 | -0.0002 | -0.0027 | 0.0004 | 0.0036 | 0.0003 | -0.0006 | 0.0044 | 0.0049 | -0.0068 | -360.1742 | 17.4377 | -360.4881 | 17.7169 | -360.7989 | 18.1769 | -360.9466 | 17.5527 | -352.7183 | 18.762 | -352.7121 | 16.8094
12:02 | 2514 | 30.3643 | 197.5352 | 442.9835 | 448.5401 | -18.9971 | -46.1187 | 6.8349 | 3.8313 | -2.5263 | -3.5475 | -0.2941 | -2.8267 | 6.7216 | 0.0754 | 0.5989 | 0.6377 | 0.9536 | 0.7174 | -131.0841 | -5.533 | 2.6657 | 0.2778 | -6.0301 | -4.4898 | 1.9286 |  | -0.0297 | -1.9821 | 4.0148 | 3.3655 | 3.3504 | 1.0379 | 10.6689 | 14.1653 | 14.7381 | 10.9934 | -0.0002 | -0.0031 | 0.0009 | 0.0037 | 0.0009 | -0.0009 | 0.022 | -0.0147 | -0.0219 | -360.1496 | 17.4192 | -360.5096 | 17.7272 | -360.8543 | 18.1502 | -360.8297 | 17.4972 | -352.6783 | 18.7538 | -352.7029 | 16.8299
12:02 | 2515 | 30.3054 | 197.472 | 443.0422 | 448.5756 | -19.1394 | -46.1303 | 6.8332 | 3.8831 | -2.5279 | -3.5086 | -0.2857 | -2.7959 | 6.8121 | 0.1212 | 0.6 | 0.643 | 0.9549 | 0.7202 | -131.1421 | -5.559 | 2.6479 | 0.3055 | -6.0575 | -4.4772 | 2.0209 |  | -0.0369 | -1.9643 | 4.0159 | 3.365 | 3.3502 | 1.04 | 10.6897 | 14.1513 | 14.7817 | 11.0259 | 0.0001 | -0.0033 | 0.0006 | 0.0035 | 0.0004 | -0.0004 | 0.0172 | -0.0106 | -0.0125 | -360.1281 | 17.409 | -360.4912 | 17.7498 | -360.8912 | 18.2118 | -360.922 | 17.5034 | -352.6629 | 18.7415 | -352.7121 | 16.8443
12:02 | 2516 | 30.2943 | 197.422 | 443.0621 | 448.5178 | -19.1708 | -46.1955 | 6.7489 | 3.8156 | -2.5939 | -3.4328 | -0.3179 | -2.8407 | 6.8149 | 0.2022 | 0.6004 | 0.6434 | 0.9536 | 0.7192 | -131.1638 | -5.6141 | 2.545 | 0.1858 | -6.0562 | -4.4957 | 1.9162 |  | 0.0154 | -1.96 | 4.0146 | 3.3651 | 3.3508 | 1.0375 | 10.6886 | 14.1386 | 14.7282 | 11.0421 | -0.0004 | -0.0031 | 0.0001 | 0.0033 | 0.0007 | -0.0005 | -0.0072 | -0.0034 | -0.0136 | -360.2019 | 17.4131 | -360.445 | 17.6923 | -360.8204 | 18.1769 | -360.9158 | 17.5301 | -352.6721 | 18.7333 | -352.669 | 16.7991
12:02 | 2517 | 30.245 | 197.445 | 443.0273 | 448.6041 | -19.1463 | -46.2365 | 6.7469 | 3.8441 | -2.528 | -3.4201 | -0.2631 | -2.8606 | 6.7733 | 0.2438 | 0.5998 | 0.6436 | 0.953 | 0.7187 | -131.1193 | -5.5281 | 2.7189 | 0.3072 | -6.0731 | -4.5427 | 1.9545 |  | 0.0939 | -1.8505 | 4.0142 | 3.3667 | 3.3512 | 1.0391 | 10.7278 | 14.1783 | 14.7763 | 11.0457 | -0.0004 | -0.0029 | 0.0006 | 0.004 | 0.0009 | -0.0004 | 0.0049 | -0.0091 | 0.0046 | -360.2142 | 17.4623 | -360.5373 | 17.721 | -360.8143 | 18.1563 | -360.8666 | 17.5321 | -352.7244 | 18.7805 | -352.7552 | 16.8238
12:02 | 2518 | 30.3609 | 197.4541 | 443.0392 | 448.6108 | -19.1477 | -46.2249 | 6.7449 | 3.8362 | -2.5876 | -3.5653 | -0.2616 | -2.833 | 6.8087 | 0.2103 | 0.6004 | 0.6416 | 0.9556 | 0.7178 | -131.1468 | -5.5478 | 2.6899 | 0.3367 | -6.0636 | -4.4947 | 1.9826 |  | -0.0913 | -1.9222 | 4.0161 | 3.3657 | 3.3529 | 1.0404 | 10.7302 | 14.186 | 14.7701 | 11.0316 | 0 | -0.0029 | 0.0006 | 0.0036 | 0.0007 | -0.0004 | 0.0149 | -0.007 | -0.0171 | -360.1435 | 17.4213 | -360.5127 | 17.7252 | -360.8604 | 18.144 | -360.8512 | 17.4993 | -352.6475 | 18.7579 | -352.7398 | 16.8197
12:02 | 2519 | 30.3364 | 197.5234 | 443.0641 | 448.6489 | -19.0875 | -46.2879 | 6.7687 | 3.9201 | -2.5527 | -3.5359 | -0.2172 | -2.8459 | 6.8421 | 0.2588 | 0.5998 | 0.6429 | 0.9525 | 0.7191 | -131.1306 | -5.566 | 2.6064 | 0.1342 | -6.1287 | -4.5997 | 1.9269 |  | -0.0169 | -1.8599 | 4.0146 | 3.3633 | 3.3515 | 1.0393 | 10.7152 | 14.1593 | 14.7544 | 11.0515 | -0.0002 | -0.0034 | 0.0005 | 0.004 | 0.0006 | -0.0009 | 0.0098 | -0.0062 | -0.0287 | -360.1711 | 17.4192 | -360.4604 | 17.7231 | -360.8574 | 18.2056 | -360.9189 | 17.528 | -352.6967 | 18.7436 | -352.6752 | 16.8217
12:02 | 2520 | 30.3336 | 197.487 | 443.0666 | 448.6004 | -18.971 | -46.164 | 6.7629 | 3.8966 | -2.569 | -3.5482 | -0.2064 | -2.8039 | 6.8285 | 0.1598 | 0.5998 | 0.6417 | 0.9514 | 0.7179 | -131.1296 | -5.4677 | 2.657 | 0.0872 | -6.0335 | -4.4916 | 1.9491 |  | -0.0023 | -1.8069 | 4.0144 | 3.3665 | 3.35 | 1.0387 | 10.7057 | 14.1681 | 14.7787 | 11.0579 | -0.0001 | -0.0031 | 0.001 | 0.0038 | 0.0006 | -0.0006 | 0.0165 | -0.0093 | -0.0005 | -360.1896 | 17.411 | -360.4327 | 17.6779 | -360.7835 | 18.1769 | -360.9312 | 17.5363 | -352.709 | 18.7353 | -352.6567 | 16.7786
12:02 | 2521 | 30.3119 | 197.5199 | 443.109 | 448.5905 | -18.9277 | -46.136 | 6.8831 | 3.8526 | -2.5634 | -3.4943 | -0.1873 | -2.9095 | 6.7384 | 0.1396 | 0.5997 | 0.6441 | 0.9534 | 0.717 | -131.0309 | -5.5218 | 2.6681 | 0.2392 | -5.994 | -4.4917 | 2.0051 |  | -0.0252 | -1.8848 | 4.0155 | 3.3658 | 3.3492 | 1.0391 | 10.7047 | 14.1724 | 14.81 | 11.0403 | -0.0008 | -0.0031 | 0.0006 | 0.0037 | 0.001 | -0.0005 | 0.0043 | -0.0063 | -0.0197 | -360.165 | 17.4459 | -360.5435 | 17.7313 | -360.8235 | 18.1789 | -360.8943 | 17.5198 | -352.7213 | 18.7785 | -352.7367 | 16.8279
12:02 | 2522 | 30.2998 | 197.3727 | 443.0504 | 448.5344 | -18.9856 | -46.1798 | 6.8786 | 3.8875 | -2.5269 | -3.548 | -0.2219 | -2.9255 | 6.8204 | 0.2399 | 0.5994 | 0.6406 | 0.9533 | 0.7169 | -131.0687 | -5.4692 | 2.704 | 0.2887 | -6.0236 | -4.5657 | 2.0319 |  | -0.074 | -1.7542 | 4.0153 | 3.3662 | 3.3511 | 1.0397 | 10.6942 | 14.1909 | 14.7535 | 11.024 | -0.0003 | -0.0028 | 0.0006 | 0.0036 | 0.0006 | -0.0002 | 0.0066 | -0.0125 | -0.0239 | -360.1219 | 17.3925 | -360.485 | 17.7436 | -360.8881 | 18.1789 | -360.8697 | 17.4849 | -352.629 | 18.7189 | -352.6998 | 16.8361
12:02 | 2523 | 30.3607 | 197.4016 | 443.0847 | 448.5521 | -18.9122 | -46.1143 | 6.9855 | 3.8462 | -2.592 | -3.5069 | -0.1372 | -2.9011 | 6.7771 | 0.2544 | 0.5991 | 0.6413 | 0.9553 | 0.7172 | -131.1516 | -5.4702 | 2.7628 | 0.2149 | -6.0131 | -4.4966 | 2.0667 |  | -0.0826 | -1.7915 | 4.0156 | 3.3672 | 3.3497 | 1.0395 | 10.7209 | 14.1885 | 14.7449 | 11.0565 | -0.0001 | -0.0036 | 0.0002 | 0.0028 | 0.0011 | -0.0004 | 0.0061 | -0.0002 | -0.0088 | -360.1496 | 17.411 | -360.4666 | 17.7334 | -360.8512 | 18.2056 | -360.9558 | 17.528 | -352.706 | 18.7374 | -352.6813 | 16.8217
12:02 | 2524 | 30.2859 | 197.3398 | 443.0245 | 448.5615 | -18.8318 | -46.0219 | 7.0433 | 3.9503 | -2.6053 | -3.5439 | -0.1778 | -2.8582 | 6.7771 | 0.2553 | 0.5993 | 0.637 | 0.9562 | 0.7174 | -131.0755 | -5.4608 | 2.7389 | 0.2051 | -5.9804 | -4.4507 | 2.051 |  | 0.0318 | -1.6553 | 4.0146 | 3.3684 | 3.3492 | 1.0379 | 10.7023 | 14.1817 | 14.7736 | 11.0204 | 0.0002 | -0.0028 | 0.0007 | 0.0038 | 0.0004 | -0.0001 | 0.0121 | -0.0119 | -0.0049 | -360.1835 | 17.4356 | -360.4819 | 17.6861 | -360.8081 | 18.1461 | -360.885 | 17.5137 | -352.706 | 18.7579 | -352.6721 | 16.7848
12:02 | 2525 | 30.3333 | 197.4106 | 442.9842 | 448.5446 | -18.8638 | -46.0095 | 7.0915 | 3.8802 | -2.4411 | -3.371 | -0.1279 | -2.8856 | 6.737 | 0.2109 | 0.5988 | 0.6392 | 0.9534 | 0.7176 | -131.0409 | -5.4306 | 2.6991 | 0.2191 | -5.9535 | -4.4623 | 2.0612 |  | 0.031 | -1.5469 | 4.0147 | 3.3651 | 3.347 | 1.0386 | 10.6746 | 14.2001 | 14.7391 | 11.0219 | -0.0003 | -0.0029 | 0.0006 | 0.0038 | 0.0008 | -0.0007 | 0.0126 | 0.0006 | 0.015 | -360.1927 | 17.4541 | -360.5558 | 17.7539 | -360.8727 | 18.1584 | -360.8604 | 17.5137 | -352.7029 | 18.7764 | -352.7706 | 16.8402
12:02 | 2526 | 30.3223 | 197.4036 | 443.0587 | 448.5023 | -18.915 | -46.1047 | 6.9211 | 3.8995 | -2.5003 | -3.3472 | -0.1704 | -2.9759 | 6.7144 | 0.1491 | 0.6001 | 0.641 | 0.9563 | 0.7197 | -131.0788 | -5.4306 | 2.6793 | 0.1099 | -5.975 | -4.4067 | 2.1026 |  | -0.0406 | -1.6354 | 4.0156 | 3.3663 | 3.3523 | 1.0397 | 10.6863 | 14.142 | 14.7544 | 11.0342 | -0.0003 | -0.0029 | 0.0005 | 0.0039 | 0.0006 | 0.0001 | 0.0138 | -0.0172 | -0.0074 | -360.1342 | 17.3966 | -360.4481 | 17.7046 | -360.8112 | 18.1769 | -360.8974 | 17.5096 | -352.6444 | 18.721 | -352.6783 | 16.8115
12:02 | 2527 | 30.3389 | 197.4104 | 443.0525 | 448.6476 | -18.9947 | -46.1598 | 6.9589 | 3.9175 | -2.5851 | -3.3622 | -0.1947 | -2.9046 | 6.7904 | 0.3093 | 0.5981 | 0.6386 | 0.9529 | 0.7175 | -131.0519 | -5.4267 | 2.6167 | 0.1669 | -5.9341 | -4.3843 | 2.0984 |  | 0.0073 | -1.6197 | 4.0146 | 3.3672 | 3.3509 | 1.0393 | 10.7289 | 14.191 | 14.7545 | 11.0294 | 0.0004 | -0.0027 | 0.0012 | 0.0044 | 0.001 | -0.0006 | 0.0025 | 0.0017 | -0.024 | -360.2265 | 17.4233 | -360.4573 | 17.7046 | -360.8112 | 18.1892 | -360.9589 | 17.5547 | -352.7583 | 18.7641 | -352.6906 | 16.795
12:02 | 2528 | 30.3705 | 197.4569 | 442.9985 | 448.6361 | -18.8474 | -46.0713 | 6.9885 | 3.9306 | -2.526 | -3.3523 | -0.1398 | -2.812 | 6.8219 | 0.3271 | 0.5993 | 0.6419 | 0.9516 | 0.718 | -131.1715 | -5.5303 | 2.402 | 0.171 | -5.9273 | -4.3742 | 2.0343 |  | 0.0215 | -1.6354 | 4.0161 | 3.3655 | 3.3506 | 1.0397 | 10.7094 | 14.1767 | 14.7775 | 11.0573 | 0.0001 | -0.003 | 0.0005 | 0.0038 | 0.0005 | -0.0008 | 0.0058 | -0.0009 | -0.0185 | -360.1896 | 17.4315 | -360.4881 | 17.6985 | -360.7989 | 18.1461 | -360.8512 | 17.5198 | -352.6721 | 18.7641 | -352.6937 | 16.7991
12:02 | 2529 | 30.3753 | 197.3777 | 442.9381 | 448.5124 | -18.8686 | -46.1311 | 6.9919 | 3.9263 | -2.4527 | -3.4675 | -0.2176 | -2.8896 | 6.8075 | 0.3124 | 0.5988 | 0.6391 | 0.9526 | 0.7168 | -131.1148 | -5.5988 | 2.4101 | 0.2467 | -5.863 | -4.366 | 2.0919 |  | 0.047 | -1.7236 | 4.0156 | 3.3638 | 3.3534 | 1.0379 | 10.707 | 14.1979 | 14.7606 | 11.0367 | -0.0005 | -0.0028 | 0.0007 | 0.0035 | 0.0004 | -0.0005 | 0.0027 | -0.0098 | -0.024 | -360.1404 | 17.411 | -360.5189 | 17.7662 | -360.9066 | 18.1994 | -360.9189 | 17.5137 | -352.6629 | 18.7436 | -352.7213 | 16.8402
12:02 | 2530 | 30.3164 | 197.408 | 442.9428 | 448.5986 | -18.8682 | -46.237 | 6.9352 | 3.8886 | -2.4026 | -3.26 | -0.194 | -2.8267 | 6.7357 | 0.2321 | 0.598 | 0.6387 | 0.952 | 0.7169 | -131.1242 | -5.4985 | 2.3892 | 0.2902 | -5.8663 | -4.3993 | 2.0964 |  | 0.0343 | -1.6976 | 4.0156 | 3.3661 | 3.3497 | 1.039 | 10.6794 | 14.1638 | 14.7578 | 11.0566 | -0.0005 | -0.0027 | 0.0004 | 0.0033 | 0.0004 | -0.0011 | 0.0088 | -0.0274 | -0.0189 | -360.1742 | 17.3761 | -360.4204 | 17.7046 | -360.8174 | 18.181 | -360.8881 | 17.5198 | -352.6598 | 18.7066 | -352.626 | 16.8053
12:02 | 2531 | 30.3256 | 197.3963 | 443.0189 | 448.6729 | -18.872 | -46.1931 | 6.8671 | 3.8154 | -2.5066 | -3.54 | -0.2128 | -2.8355 | 6.7301 | 0.332 | 0.5988 | 0.6382 | 0.9538 | 0.7178 | -131.1377 | -5.596 | 2.4915 | 0.2958 | -5.8358 | -4.4249 | 2.1138 |  | -0.0564 | -1.7535 | 4.0153 | 3.3703 | 3.3519 | 1.0393 | 10.6851 | 14.1814 | 14.7714 | 11.0443 | 0 | -0.0031 | 0.0005 | 0.003 | 0.0002 | -0.0004 | -0.0063 | -0.0017 | -0.0033 | -360.2081 | 17.4439 | -360.5158 | 17.7231 | -360.8204 | 18.1687 | -360.8912 | 17.5383 | -352.7306 | 18.7723 | -352.7367 | 16.8135
12:02 | 2532 | 30.3855 | 197.4704 | 443.0696 | 448.6884 | -18.9028 | -46.0991 | 6.9882 | 3.9586 | -2.4492 | -3.5233 | -0.2411 | -2.8064 | 6.7932 | 0.2845 | 0.5986 | 0.6398 | 0.9561 | 0.7183 | -131.1808 | -5.5355 | 2.527 | 0.2294 | -5.9123 | -4.4933 | 2.1264 |  | 0.0289 | -1.6669 | 4.0158 | 3.3665 | 3.3496 | 1.0399 | 10.7034 | 14.183 | 14.7644 | 11.0616 | 0.0003 | -0.0027 | 0.0006 | 0.0038 | 0.0009 | -0.0008 | 0.009 | -0.0093 | -0.011 | -360.1219 | 17.4274 | -360.5435 | 17.7395 | -360.845 | 18.1502 | -360.7958 | 17.4705 | -352.6598 | 18.7559 | -352.7121 | 16.834
12:02 | 2533 | 30.3736 | 197.4889 | 443.1049 | 448.6865 | -18.8887 | -46.1166 | 6.9208 | 3.9164 | -2.5641 | -3.5088 | -0.2745 | -2.8433 | 6.7324 | 0.3174 | 0.5979 | 0.6365 | 0.9536 | 0.7189 | -131.1158 | -5.4847 | 2.5222 | 0.2307 | -5.9192 | -4.5681 | 2.0853 |  | -0.0251 | -1.7268 | 4.0148 | 3.3671 | 3.35 | 1.0397 | 10.7059 | 14.2139 | 14.7813 | 11.0533 | -0.0002 | -0.0032 | 0.0006 | 0.0041 | 0.0001 | -0.0004 | 0.0093 | -0.0096 | -0.0218 | -360.1681 | 17.4192 | -360.5158 | 17.7272 | -360.8543 | 18.2036 | -360.9158 | 17.526 | -352.6875 | 18.7497 | -352.7367 | 16.8299
12:02 | 2534 | 30.4394 | 197.46 | 443.091 | 448.6108 | -18.9383 | -46.1392 | 6.8497 | 3.8952 | -2.5116 | -3.4711 | -0.2497 | -2.9378 | 6.7206 | 0.3285 | 0.5984 | 0.6402 | 0.956 | 0.718 | -131.0608 | -5.4479 | 2.538 | 0.1346 | -5.9746 | -4.4995 | 2.0615 |  | -0.0283 | -1.7313 | 4.016 | 3.3647 | 3.3506 | 1.0393 | 10.7172 | 14.1682 | 14.7856 | 11.0518 | 0 | -0.0023 | 0.0009 | 0.0038 | 0.0011 | -0.0007 | 0.0119 | -0.0032 | -0.0226 | -360.2019 | 17.4315 | -360.4573 | 17.6841 | -360.7835 | 18.1543 | -360.8635 | 17.5424 | -352.7614 | 18.7477 | -352.6752 | 16.7889
12:02 | 2535 | 30.4459 | 197.5249 | 443.1127 | 448.7063 | -18.8775 | -46.1036 | 6.932 | 3.9099 | -2.5358 | -3.3685 | -0.2254 | -2.8772 | 6.8151 | 0.3764 | 0.5987 | 0.6399 | 0.9554 | 0.7173 | -131.16 | -5.4731 | 2.5049 | 0.118 | -5.9773 | -4.5439 | 2.0522 |  | -0.013 | -1.7944 | 4.0155 | 3.3666 | 3.3504 | 1.0403 | 10.6758 | 14.1953 | 14.7337 | 11.0176 | 0 | -0.0028 | 0 | 0.0036 | 0.0003 | -0.0001 | 0.0071 | -0.0128 | -0.0007 | -360.2081 | 17.4582 | -360.5343 | 17.7293 | -360.842 | 18.1563 | -360.8943 | 17.5219 | -352.7213 | 18.7887 | -352.7521 | 16.8197
12:02 | 2536 | 30.4407 | 197.5841 | 443.1485 | 448.7328 | -18.8668 | -46.0938 | 6.8787 | 3.9786 | -2.585 | -3.3614 | -0.237 | -2.9443 | 6.7612 | 0.3542 | 0.5992 | 0.6406 | 0.953 | 0.7167 | -131.1219 | -5.4779 | 2.3975 | 0.0807 | -5.9641 | -4.6308 | 2.0687 |  | 0.0403 | -1.8206 | 4.0147 | 3.3652 | 3.3496 | 1.0387 | 10.6944 | 14.1847 | 14.7329 | 11.0425 | -0.0003 | -0.0033 | 0.0002 | 0.0037 | 0.0009 | -0.0007 | 0.022 | -0.0015 | -0.0013 | -360.1188 | 17.4007 | -360.4573 | 17.7169 | -360.8543 | 18.1871 | -360.8881 | 17.489 | -352.6444 | 18.7271 | -352.6813 | 16.8156
12:02 | 2537 | 30.4723 | 197.5956 | 443.0936 | 448.7166 | -18.8869 | -46.0757 | 6.9011 | 3.8628 | -2.6234 | -3.5154 | -0.3 | -2.9117 | 6.7967 | 0.3628 | 0.5988 | 0.6392 | 0.9505 | 0.7176 | -131.1569 | -5.4814 | 2.4666 | 0.0364 | -6.0324 | -4.554 | 2.0461 |  | -0.0159 | -1.7591 | 4.0148 | 3.3696 | 3.3526 | 1.0397 | 10.7209 | 14.1712 | 14.7218 | 11.0045 | -0.0001 | -0.0031 | 0.0008 | 0.0036 | 0.001 | -0.0002 | 0.0047 | -0.0144 | -0.0188 | -360.1742 | 17.4048 | -360.4296 | 17.7067 | -360.8327 | 18.2077 | -360.9804 | 17.5363 | -352.7183 | 18.7333 | -352.6537 | 16.7991
12:02 | 2538 | 30.4911 | 197.5928 | 443.1663 | 448.7636 | -18.9247 | -46.0962 | 6.9239 | 3.8867 | -2.576 | -3.5756 | -0.2099 | -2.8572 | 6.847 | 0.3332 | 0.599 | 0.6397 | 0.9543 | 0.7167 | -131.1554 | -5.4177 | 2.5396 | 0.011 | -5.9544 | -4.5295 | 2.0202 |  | 0.0801 | -1.8237 | 4.0162 | 3.3661 | 3.3514 | 1.0403 | 10.7072 | 14.1684 | 14.7506 | 11.044 | -0.0007 | -0.0027 | 0.0006 | 0.0035 | 0.0005 | -0.0008 | 0.0092 | -0.0035 | -0.0016 | -360.1896 | 17.4213 | -360.4727 | 17.7087 | -360.802 | 18.142 | -360.8912 | 17.5198 | -352.6721 | 18.7538 | -352.6752 | 16.7971
12:02 | 2539 | 30.4266 | 197.6054 | 443.1368 | 448.7335 | -18.856 | -46.0853 | 6.9954 | 3.9952 | -2.531 | -3.5111 | -0.184 | -2.9324 | 6.7999 | 0.3749 | 0.5994 | 0.6405 | 0.9534 | 0.7167 | -131.0992 | -5.4082 | 2.4964 | 0.0648 | -5.9383 | -4.7046 | 2.094 |  | 0.0312 | -1.8669 | 4.0158 | 3.3665 | 3.3513 | 1.0398 | 10.6758 | 14.1607 | 14.7337 | 11.0349 | -0.0001 | -0.0027 | 0.0012 | 0.0038 | 0.0006 | -0.0004 | 0.0035 | -0.0101 | -0.0071 | -360.1742 | 17.448 | -360.5435 | 17.7683 | -360.8912 | 18.181 | -360.8512 | 17.5096 | -352.7152 | 18.7703 | -352.749 | 16.8546
12:02 | 2540 | 30.4141 | 197.4945 | 443.0911 | 448.6091 | -18.8967 | -46.0728 | 7.0098 | 3.9522 | -2.4919 | -3.382 | -0.1042 | -2.9522 | 6.828 | 0.2969 | 0.5983 | 0.6449 | 0.9588 | 0.7166 | -131.1552 | -5.4242 | 2.4575 | 0.0449 | -5.9392 | -4.5233 | 2.0867 |  | 0.1047 | -1.7849 | 4.0161 | 3.3652 | 3.3493 | 1.0394 | 10.692 | 14.171 | 14.7612 | 11.0454 | 0 | -0.0034 | 0.0008 | 0.0035 | 0.0007 | -0.0004 | 0.0163 | 0.003 | -0.0029 | -360.1465 | 17.4192 | -360.4912 | 17.7293 | -360.8327 | 18.1748 | -360.8481 | 17.4993 | -352.6475 | 18.7353 | -352.706 | 16.8217
12:02 | 2541 | 30.4849 | 197.5865 | 443.1281 | 448.6686 | -18.8604 | -46.1182 | 7.0206 | 4.1148 | -2.5107 | -3.4966 | -0.1526 | -3.016 | 6.7164 | 0.1729 | 0.5976 | 0.6383 | 0.9555 | 0.7163 | -131.0874 | -5.4473 | 2.4906 | 0.0641 | -5.9063 | -4.4122 | 2.1446 |  | -0.0338 | -1.7637 | 4.0149 | 3.3649 | 3.3521 | 1.0388 | 10.7013 | 14.1918 | 14.7585 | 11.0721 | 0.0001 | -0.0031 | 0.0005 | 0.0039 | 0.0008 | -0.001 | 0.008 | -0.0172 | -0.0075 | -360.2081 | 17.4274 | -360.5035 | 17.7416 | -360.845 | 18.1892 | -360.9558 | 17.5527 | -352.7213 | 18.7518 | -352.6998 | 16.8094
12:02 | 2542 | 30.5172 | 197.5988 | 443.1419 | 448.7251 | -18.9762 | -46.1467 | 7.0447 | 4.0122 | -2.4692 | -3.5381 | -0.18 | -2.9814 | 6.7551 | 0.2175 | 0.5968 | 0.6388 | 0.9532 | 0.7151 | -131.1198 | -5.3578 | 2.6074 | 0.1209 | -6.0461 | -4.5934 | 2.0163 |  | 0.0899 | -1.6409 | 4.013 | 3.3657 | 3.3503 | 1.0385 | 10.715 | 14.2004 | 14.7644 | 11.0616 | -0.0003 | -0.0027 | 0.001 | 0.0042 | 0.0007 | -0.0001 | -0.0032 | -0.0013 | -0.0129 | -360.1742 | 17.4397 | -360.4942 | 17.7354 | -360.7989 | 18.1481 | -360.8543 | 17.5219 | -352.6967 | 18.7682 | -352.709 | 16.7991
12:02 | 2543 | 30.4518 | 197.5298 | 443.1327 | 448.7236 | -19.0452 | -46.2919 | 7.135 | 3.9347 | -2.5039 | -3.4974 | -0.2282 | -2.9466 | 6.7112 | 0.3743 | 0.5962 | 0.6407 | 0.9544 | 0.7176 | -131.0235 | -5.3595 | 2.5833 | 0.1841 | -5.9882 | -4.5658 | 2.0861 |  | 0.0748 | -1.6944 | 4.0156 | 3.3662 | 3.3502 | 1.0403 | 10.7209 | 14.2174 | 14.8086 | 11.045 | -0.0004 | -0.0029 | 0.0004 | 0.0037 | 0.001 | -0.0007 | 0.0159 | -0.0041 | -0.0088 | -360.1465 | 17.4254 | -360.5096 | 17.7765 | -360.8543 | 18.1851 | -360.9158 | 17.5157 | -352.6475 | 18.76 | -352.7275 | 16.8381
12:02 | 2544 | 30.5121 | 197.5155 | 443.1033 | 448.7335 | -19.0566 | -46.2759 | 7.0529 | 3.8923 | -2.5608 | -3.5487 | -0.2407 | -3.0608 | 6.7289 | 0.3651 | 0.5988 | 0.6438 | 0.953 | 0.7159 | -131.0469 | -5.3771 | 2.6531 | 0.224 | -5.8999 | -4.6738 | 2.0622 |  | 0.0962 | -1.7144 | 4.0144 | 3.3661 | 3.3544 | 1.041 | 10.7242 | 14.2213 | 14.8148 | 11.0821 | 0.0001 | -0.003 | 0.0006 | 0.004 | 0.0006 | -0.0003 | 0.0084 | -0.014 | -0.001 | -360.1034 | 17.4007 | -360.4327 | 17.721 | -360.8081 | 18.183 | -360.885 | 17.5075 | -352.6629 | 18.7374 | -352.6537 | 16.8053
12:02 | 2545 | 30.5452 | 197.6514 | 443.1399 | 448.7903 | -19.0747 | -46.3173 | 7.0366 | 3.9197 | -2.4495 | -3.5103 | -0.2441 | -3.0772 | 6.7726 | 0.3122 | 0.5974 | 0.6395 | 0.9511 | 0.7159 | -131.0089 | -5.3288 | 2.6716 | 0.2577 | -5.9798 | -4.5859 | 2.1005 |  | -0.0018 | -1.7526 | 4.0147 | 3.3648 | 3.3543 | 1.0401 | 10.6977 | 14.2117 | 14.7449 | 11.0681 | -0.0002 | -0.0032 | 0.0002 | 0.0034 | 0.0008 | -0.001 | 0.01 | 0.0012 | -0.0196 | -360.1711 | 17.4397 | -360.5127 | 17.7477 | -360.8327 | 18.1666 | -360.9189 | 17.5301 | -352.6783 | 18.76 | -352.7275 | 16.8156
12:02 | 2546 | 30.5218 | 197.5502 | 443.2327 | 448.7598 | -19.0013 | -46.2708 | 7.0079 | 3.8851 | -2.4054 | -3.486 | -0.2113 | -2.9859 | 6.7912 | 0.425 | 0.5991 | 0.6401 | 0.9557 | 0.7166 | -131.0227 | -5.4001 | 2.5546 | 0.2263 | -5.8848 | -4.4874 | 2.0702 |  | 0.041 | -1.7713 | 4.0135 | 3.3654 | 3.3509 | 1.0405 | 10.6886 | 14.1964 | 14.7861 | 11.0363 | -0.0002 | -0.0027 | 0.0007 | 0.0038 | 0.0002 | -0.0006 | 0.0051 | 0.0024 | -0.0205 | -360.1465 | 17.409 | -360.4758 | 17.7334 | -360.805 | 18.1461 | -360.8666 | 17.5055 | -352.6875 | 18.7436 | -352.6967 | 16.8156
12:02 | 2547 | 30.5381 | 197.6386 | 443.1677 | 448.7972 | -18.9442 | -46.225 | 6.9909 | 3.8802 | -2.3681 | -3.4639 | -0.1968 | -2.8597 | 6.7384 | 0.4271 | 0.5975 | 0.6385 | 0.9531 | 0.716 | -130.9287 | -5.2857 | 2.555 | 0.2324 | -5.9264 | -4.5911 | 2.0978 |  | 0.0921 | -1.7187 | 4.0152 | 3.3667 | 3.3525 | 1.0401 | 10.6965 | 14.1933 | 14.7736 | 11.0031 | -0.0003 | -0.0025 | 0.0015 | 0.0043 | 0.0006 | -0.0007 | 0.0347 | -0.0175 | 0.0021 | -360.1711 | 17.4254 | -360.5035 | 17.7518 | -360.8481 | 18.1625 | -360.9066 | 17.526 | -352.6813 | 18.7538 | -352.7121 | 16.8258
12:02 | 2548 | 30.5954 | 197.6473 | 443.1834 | 448.7897 | -19.0657 | -46.3469 | 6.9045 | 3.8911 | -2.3224 | -3.4831 | -0.2521 | -2.9343 | 6.7817 | 0.4242 | 0.5988 | 0.6386 | 0.9547 | 0.7177 | -130.943 | -5.249 | 2.5623 | 0.2688 | -5.8632 | -4.5088 | 2.0335 |  | 0.0971 | -1.6318 | 4.0154 | 3.3666 | 3.3503 | 1.0388 | 10.7105 | 14.178 | 14.7684 | 11.0291 | -0.0002 | -0.0032 | 0.0008 | 0.0035 | 0.0007 | -0.0006 | -0.0035 | -0.0037 | -0.0055 | -360.1465 | 17.4233 | -360.4666 | 17.7108 | -360.802 | 18.1502 | -360.8604 | 17.5075 | -352.6937 | 18.7477 | -352.6937 | 16.8012
12:02 | 2549 | 30.5609 | 197.5492 | 443.1333 | 448.6641 | -18.9815 | -46.2878 | 6.9678 | 3.9541 | -2.334 | -3.3107 | -0.2104 | -2.8895 | 6.7898 | 0.433 | 0.5989 | 0.6384 | 0.9545 | 0.7162 | -130.9971 | -5.2574 | 2.5532 | 0.0543 | -5.8455 | -4.5377 | 2.0207 |  | 0.0409 | -1.6402 | 4.0153 | 3.3648 | 3.3483 | 1.0404 | 10.7163 | 14.178 | 14.751 | 11.0118 | 0.0002 | -0.0031 | 0.0007 | 0.0046 | 0.0007 | 0.0002 | 0.0034 | -0.0204 | -0.0134 | -360.1681 | 17.4397 | -360.5312 | 17.7457 | -360.8235 | 18.1522 | -360.922 | 17.5383 | -352.709 | 18.7703 | -352.7275 | 16.8381
12:02 | 2550 | 30.5657 | 197.6038 | 443.2444 | 448.7052 | -19.0001 | -46.138 | 6.957 | 3.9791 | -2.2173 | -3.3736 | -0.2705 | -2.8623 | 6.7527 | 0.4174 | 0.5977 | 0.6374 | 0.9551 | 0.7169 | -130.9799 | -5.2878 | 2.6102 | 0.1385 | -5.8176 | -4.4815 | 2.0691 |  | 0.0265 | -1.7704 | 4.014 | 3.3672 | 3.3532 | 1.0406 | 10.7139 | 14.1817 | 14.7736 | 11.0377 | -0.0001 | -0.0028 | 0.0003 | 0.0038 | 0.0008 | -0.0006 | 0.0228 | -0.0097 | 0.0065 | -360.1711 | 17.4233 | -360.4789 | 17.7293 | -360.8635 | 18.1563 | -360.8635 | 17.5055 | -352.6537 | 18.7456 | -352.706 | 16.8094
12:02 | 2551 | 30.535 | 197.5695 | 443.2037 | 448.7286 | -19.0368 | -46.2552 | 6.9939 | 3.9422 | -2.249 | -3.4321 | -0.2032 | -2.8619 | 6.8194 | 0.5027 | 0.5992 | 0.6441 | 0.9539 | 0.7165 | -130.9809 | -5.2373 | 2.6081 | 0.1078 | -5.8925 | -4.4801 | 2.0111 |  | 0.0717 | -1.814 | 4.014 | 3.3636 | 3.3486 | 1.0403 | 10.7115 | 14.2085 | 14.7903 | 11.0811 | -0.0002 | -0.0022 | 0 | 0.0039 | 0.001 | -0.0001 | 0.0013 | -0.0012 | -0.0117 | -360.1527 | 17.4151 | -360.4389 | 17.7272 | -360.8358 | 18.181 | -360.9281 | 17.528 | -352.7029 | 18.7456 | -352.6844 | 16.8197
12:02 | 2552 | 30.5628 | 197.5562 | 443.2556 | 448.7963 | -18.9811 | -46.0736 | 7.0138 | 3.9577 | -2.3158 | -3.4662 | -0.218 | -2.908 | 6.8092 | 0.3985 | 0.598 | 0.6394 | 0.9571 | 0.7171 | -131.0672 | -5.3517 | 2.5711 | 0.1826 | -5.9055 | -4.5433 | 2.0496 |  | 0.1151 | -1.743 | 4.0167 | 3.3643 | 3.3496 | 1.0401 | 10.6724 | 14.1685 | 14.7227 | 11.0205 | -0.0004 | -0.003 | 0.0004 | 0.0041 | 0.0009 | -0.0005 | 0.0114 | -0.0027 | -0.0033 | -360.165 | 17.4131 | -360.4789 | 17.7169 | -360.8112 | 18.1666 | -360.9435 | 17.5506 | -352.706 | 18.7415 | -352.6629 | 16.7909
12:02 | 2553 | 30.6573 | 197.6637 | 443.2764 | 448.7877 | -19.0419 | -46.0923 | 6.9762 | 3.9533 | -2.2703 | -3.5035 | -0.1872 | -2.8378 | 6.8372 | 0.4799 | 0.5982 | 0.6407 | 0.9582 | 0.717 | -131.0045 | -5.323 | 2.6649 | 0.1201 | -5.894 | -4.4888 | 2.0774 |  | 0.104 | -1.7968 | 4.0158 | 3.366 | 3.3538 | 1.0401 | 10.6816 | 14.1664 | 14.7452 | 11.0118 | 0.0004 | -0.0027 | 0.0007 | 0.0035 | 0.0004 | -0.0008 | 0.0087 | -0.0082 | -0.0033 | -360.1896 | 17.4233 | -360.5066 | 17.7436 | -360.8297 | 18.1317 | -360.842 | 17.5178 | -352.6844 | 18.76 | -352.7183 | 16.8279
12:02 | 2554 | 30.6349 | 197.5423 | 443.2229 | 448.7509 | -19.0495 | -46.0445 | 6.9626 | 3.9643 | -2.2043 | -3.5333 | -0.2187 | -2.8297 | 6.8902 | 0.4754 | 0.5985 | 0.6418 | 0.9575 | 0.7171 | -131.0642 | -5.3948 | 2.5832 | 0.0774 | -5.8975 | -4.5314 | 2.0265 |  | 0.103 | -1.76 | 4.0156 | 3.3645 | 3.349 | 1.0411 | 10.6978 | 14.1709 | 14.7833 | 11.0053 | -0.0003 | -0.0033 | 0.001 | 0.0041 | 0.0006 | -0.0009 | 0.0254 | 0.0018 | 0.0073 | -360.1158 | 17.4192 | -360.4819 | 17.7642 | -360.9281 | 18.1748 | -360.8789 | 17.5096 | -352.6567 | 18.7333 | -352.709 | 16.8423
12:02 | 2555 | 30.6502 | 197.5802 | 443.2742 | 448.8045 | -18.9918 | -45.9865 | 6.8537 | 3.9385 | -2.3334 | -3.4672 | -0.2713 | -2.8013 | 6.9612 | 0.5338 | 0.598 | 0.6426 | 0.9551 | 0.7165 | -131.0499 | -5.3115 | 2.5552 | 0.0888 | -5.9164 | -4.5665 | 2.1371 |  | 0.1311 | -1.7862 | 4.0165 | 3.3642 | 3.3524 | 1.0412 | 10.6873 | 14.1724 | 14.7347 | 11.0287 | -0.0001 | -0.0023 | 0.0011 | 0.0039 | 0.0006 | -0.0006 | 0.027 | -0.0094 | -0.0182 | -360.1465 | 17.4131 | -360.4512 | 17.7046 | -360.8204 | 18.1543 | -360.885 | 17.5465 | -352.6875 | 18.7395 | -352.669 | 16.7971
12:02 | 2556 | 30.6331 | 197.6748 | 443.2295 | 448.7897 | -18.9698 | -45.9995 | 6.8 | 3.8978 | -2.3905 | -3.4301 | -0.3293 | -2.7286 | 6.9515 | 0.4799 | 0.5978 | 0.6399 | 0.9506 | 0.7146 | -131.1536 | -5.3804 | 2.6004 | 0.0837 | -5.8925 | -4.499 | 2.11 |  | 0.0676 | -1.8276 | 4.0145 | 3.3639 | 3.3548 | 1.0402 | 10.7197 | 14.1644 | 14.7967 | 11.0493 | 0 | -0.0026 | 0.0007 | 0.0036 | 0.001 | -0.0007 | 0.0154 | -0.0078 | 0.0012 | -360.205 | 17.4664 | -360.5619 | 17.7436 | -360.8512 | 18.1337 | -360.8974 | 17.5404 | -352.7244 | 18.7846 | -352.7644 | 16.8197
12:02 | 2557 | 30.5908 | 197.5984 | 443.298 | 448.7958 | -18.8736 | -45.9461 | 6.9659 | 4.0192 | -2.2264 | -3.2957 | -0.2447 | -2.8477 | 6.9403 | 0.3779 | 0.597 | 0.6409 | 0.9525 | 0.7164 | -131.0884 | -5.3787 | 2.6732 | 0.1106 | -5.9341 | -4.4387 | 2.1298 |  | 0.0481 | -1.7625 | 4.0162 | 3.3664 | 3.3492 | 1.0414 | 10.692 | 14.1943 | 14.7912 | 11.0508 | 0.0001 | -0.0032 | 0.0002 | 0.0036 | 0.0006 | -0.0005 | 0.0148 | -0.0174 | -0.0188 | -360.125 | 17.4151 | -360.485 | 17.7477 | -360.842 | 18.1399 | -360.8604 | 17.5157 | -352.6567 | 18.7477 | -352.7213 | 16.8361
12:02 | 2558 | 30.5428 | 197.6504 | 443.2427 | 448.8431 | -18.834 | -45.8753 | 7.0127 | 3.9614 | -2.197 | -3.3341 | -0.1691 | -2.8098 | 7.0072 | 0.4027 | 0.5969 | 0.6407 | 0.9519 | 0.7171 | -131.0658 | -5.3773 | 2.6203 | 0.2158 | -5.8272 | -4.3635 | 2.175 |  | 0.0864 | -1.6835 | 4.0147 | 3.3636 | 3.3469 | 1.0406 | 10.6942 | 14.22 | 14.7719 | 11.041 | -0.0003 | -0.0031 | 0.0005 | 0.0039 | 0.001 | -0.0004 | 0.0077 | -0.0083 | -0.0014 | -360.1896 | 17.4048 | -360.4604 | 17.7293 | -360.845 | 18.1974 | -360.9374 | 17.5568 | -352.7275 | 18.7333 | -352.6567 | 16.8115
12:02 | 2559 | 30.636 | 197.5715 | 443.3092 | 448.8308 | -18.8538 | -45.9182 | 7.0112 | 3.9563 | -2.2757 | -3.4241 | -0.2412 | -2.7965 | 6.9629 | 0.4741 | 0.5972 | 0.6416 | 0.9556 | 0.7172 | -131.0914 | -5.3307 | 2.6621 | 0.2771 | -5.8072 | -4.417 | 2.1094 |  | 0.0831 | -1.6903 | 4.0151 | 3.3665 | 3.3506 | 1.0408 | 10.7175 | 14.208 | 14.7977 | 11.0363 | -0.0004 | -0.0029 | 0.0001 | 0.0036 | 0.0007 | -0.0002 | 0.0038 | -0.0136 | -0.0266 | -360.1773 | 17.4131 | -360.4727 | 17.7067 | -360.7712 | 18.1358 | -360.8758 | 17.5527 | -352.6906 | 18.7374 | -352.6721 | 16.7868
12:02 | 2560 | 30.6249 | 197.5939 | 443.2158 | 448.7618 | -18.8717 | -45.9677 | 7.0259 | 3.9692 | -2.3467 | -3.3525 | -0.2043 | -2.8211 | 6.9974 | 0.4911 | 0.5973 | 0.6425 | 0.9548 | 0.7151 | -131.0229 | -5.3654 | 2.6296 | 0.2867 | -5.7864 | -4.5602 | 2.1694 |  | 0.0754 | -1.7446 | 4.0146 | 3.3632 | 3.3502 | 1.0405 | 10.7047 | 14.178 | 14.7742 | 11.0349 | -0.0003 | -0.0027 | 0.0006 | 0.0036 | 0.0005 | -0.0005 | -0.0027 | 0.0034 | -0.0177 | -360.1496 | 17.4397 | -360.5343 | 17.7662 | -360.9004 | 18.1543 | -360.8697 | 17.5321 | -352.666 | 18.7579 | -352.746 | 16.8464
12:02 | 2561 | 30.6522 | 197.6458 | 443.3705 | 448.8848 | -18.8409 | -45.8316 | 7.1301 | 3.8947 | -2.3293 | -3.4608 | -0.2022 | -2.8488 | 6.9314 | 0.4476 | 0.5974 | 0.6434 | 0.9545 | 0.7161 | -131.055 | -5.3231 | 2.729 | 0.365 | -5.845 | -4.4272 | 2.1706 |  | 0.0702 | -1.777 | 4.0147 | 3.3616 | 3.3476 | 1.0397 | 10.6701 | 14.1663 | 14.7616 | 11.0179 | 0 | -0.0032 | 0.0011 | 0.004 | 0.0006 | -0.001 | 0.0111 | -0.0006 | -0.0256 | -360.0758 | 17.3884 | -360.4727 | 17.7601 | -360.8912 | 18.1625 | -360.8697 | 17.5055 | -352.6198 | 18.7107 | -352.6752 | 16.8258
12:02 | 2562 | 30.6516 | 197.6679 | 443.4725 | 448.8806 | -18.9208 | -45.893 | 7.0052 | 4.0177 | -2.3424 | -3.3219 | -0.1624 | -2.9191 | 6.8435 | 0.4325 | 0.5971 | 0.6422 | 0.9571 | 0.7162 | -131.0104 | -5.3069 | 2.6219 | 0.2584 | -5.9212 | -4.4102 | 2.1339 |  | -0.0303 | -1.7482 | 4.0148 | 3.365 | 3.3516 | 1.0392 | 10.7221 | 14.2127 | 14.7973 | 11.058 | -0.0001 | -0.0033 | 0.0007 | 0.0037 | 0.0006 | -0.0003 | 0.0231 | -0.0111 | -0.0219 | -360.1988 | 17.4131 | -360.4912 | 17.7354 | -360.8358 | 18.1625 | -360.9312 | 17.5445 | -352.7152 | 18.7436 | -352.709 | 16.8074
12:02 | 2563 | 30.7558 | 197.7225 | 443.4446 | 448.8231 | -18.932 | -46.0268 | 6.8978 | 3.9903 | -2.2869 | -3.3857 | -0.1298 | -2.8561 | 6.8303 | 0.4161 | 0.5983 | 0.6376 | 0.9525 | 0.7171 | -131.0128 | -5.269 | 2.6312 | 0.2542 | -5.9832 | -4.4668 | 2.1394 |  | 0.0364 | -1.7507 | 4.0144 | 3.3684 | 3.3506 | 1.0408 | 10.7254 | 14.1818 | 14.7862 | 11.0547 | -0.0003 | -0.0029 | 0.0013 | 0.0038 | 0.0008 | -0.0005 | 0.015 | 0 | 0.0127 | -360.2111 | 17.45 | -360.5035 | 17.7272 | -360.8174 | 18.1296 | -360.8543 | 17.528 | -352.6906 | 18.7661 | -352.7121 | 16.7991
12:02 | 2564 | 30.682 | 197.6622 | 443.2989 | 448.7776 | -18.9684 | -46.0363 | 6.9354 | 4.0144 | -2.2855 | -3.2918 | -0.1701 | -2.7938 | 6.8547 | 0.4035 | 0.5971 | 0.6409 | 0.9517 | 0.716 | -131.0236 | -5.3561 | 2.6 | 0.268 | -6.0187 | -4.39 | 2.0652 |  | 0.0862 | -1.6819 | 4.0151 | 3.3672 | 3.3492 | 1.0411 | 10.7116 | 14.22 | 14.7835 | 11.0641 | -0.0006 | -0.0031 | 0.0006 | 0.0034 | 0.0005 | -0.0004 | 0.0027 | -0.0028 | -0.0198 | -360.1711 | 17.4336 | -360.5127 | 17.758 | -360.8881 | 18.1399 | -360.8635 | 17.5383 | -352.6998 | 18.7456 | -352.7367 | 16.8258
12:02 | 2565 | 30.6943 | 197.5919 | 443.3537 | 448.903 | -18.9323 | -45.9817 | 7.0682 | 4.0199 | -2.3558 | -3.335 | -0.2492 | -2.8102 | 6.8165 | 0.524 | 0.5985 | 0.6394 | 0.952 | 0.7164 | -131.002 | -5.3635 | 2.6839 | 0.1897 | -5.9747 | -4.4579 | 2.0703 |  | -0.0135 | -1.7618 | 4.0147 | 3.365 | 3.3497 | 1.0412 | 10.7231 | 14.2085 | 14.7672 | 11.0926 | 0 | -0.0029 | 0.0001 | 0.0035 | 0.0009 | -0.0006 | 0.0211 | -0.004 | 0.0021 | -360.1804 | 17.4048 | -360.4573 | 17.7457 | -360.8512 | 18.1666 | -360.885 | 17.5342 | -352.6752 | 18.7251 | -352.6567 | 16.793
12:02 | 2566 | 30.6876 | 197.5722 | 443.3542 | 448.7735 | -18.9594 | -46.0388 | 7.0131 | 3.9391 | -2.3185 | -3.2816 | -0.2968 | -2.7043 | 6.9262 | 0.4621 | 0.5989 | 0.6411 | 0.9529 | 0.7164 | -131.0037 | -5.3442 | 2.7122 | 0.1424 | -5.9625 | -4.5064 | 2.1304 |  | 0.019 | -1.8112 | 4.0155 | 3.3643 | 3.3487 | 1.0414 | 10.744 | 14.1945 | 14.7865 | 11.0619 | -0.0001 | -0.0035 | 0.0006 | 0.0037 | 0.0007 | -0.0003 | 0.0065 | -0.0106 | -0.0196 | -360.2019 | 17.4233 | -360.4881 | 17.7293 | -360.8143 | 18.1584 | -360.922 | 17.5486 | -352.6844 | 18.7395 | -352.7183 | 16.7991
12:02 | 2567 | 30.6575 | 197.6259 | 443.3497 | 448.8321 | -18.9143 | -45.9693 | 7.1039 | 3.9689 | -2.2127 | -3.1674 | -0.2081 | -2.7128 | 6.9394 | 0.4538 | 0.5992 | 0.6417 | 0.9522 | 0.7163 | -131.0433 | -5.3078 | 2.5948 | 0.1479 | -5.9267 | -4.5344 | 2.0632 |  | 0.0937 | -1.6831 | 4.0144 | 3.3635 | 3.3524 | 1.0404 | 10.7208 | 14.2002 | 14.8097 | 11.0908 | 0.0001 | -0.003 | 0.0004 | 0.0035 | 0.001 | -0.0001 | 0.0093 | -0.0193 | -0.0029 | -360.1958 | 17.4295 | -360.4973 | 17.7395 | -360.842 | 18.1481 | -360.8604 | 17.5219 | -352.6752 | 18.7415 | -352.6906 | 16.795
12:03 | 2568 | 30.7147 | 197.5889 | 443.4166 | 448.831 | -18.937 | -46.0461 | 7.0816 | 4.042 | -2.3218 | -3.102 | -0.1832 | -2.7157 | 6.8951 | 0.473 | 0.5992 | 0.6422 | 0.9537 | 0.715 | -131.0575 | -5.3119 | 2.6949 | 0.0546 | -5.8554 | -4.491 | 2.1106 |  | 0.1022 | -1.6356 | 4.0165 | 3.3663 | 3.3542 | 1.0395 | 10.7013 | 14.1687 | 14.7643 | 11.0548 | -0.0002 | -0.0027 | 0.0006 | 0.0037 | 0.0007 | -0.0007 | 0.0177 | -0.0103 | -0.0163 | -360.1681 | 17.4151 | -360.485 | 17.7416 | -360.8327 | 18.1645 | -360.9097 | 17.5342 | -352.6937 | 18.7415 | -352.6937 | 16.8032
12:03 | 2569 | 30.7115 | 197.5851 | 443.3022 | 448.806 | -18.977 | -46.1445 | 6.9953 | 4.0266 | -2.2994 | -3.1104 | -0.131 | -2.7014 | 6.9744 | 0.5561 | 0.5977 | 0.6411 | 0.9536 | 0.7152 | -130.9595 | -5.2996 | 2.8209 | 0.099 | -5.842 | -4.497 | 2.0949 |  | 0.1467 | -1.7406 | 4.0156 | 3.3623 | 3.354 | 1.0407 | 10.6793 | 14.1814 | 14.7714 | 11.0154 | -0.0003 | -0.003 | 0.0011 | 0.0039 | 0.0005 | -0.0006 | 0.0101 | 0.0059 | 0.0024 | -360.1988 | 17.4213 | -360.485 | 17.7375 | -360.8297 | 18.1584 | -360.8758 | 17.5321 | -352.6752 | 18.7374 | -352.669 | 16.795
12:03 | 2570 | 30.6655 | 197.6876 | 443.2871 | 448.8488 | -18.8395 | -46.1271 | 7.1145 | 4.0432 | -2.2875 | -3.1647 | -0.1943 | -2.7082 | 6.9772 | 0.4762 | 0.5985 | 0.6413 | 0.9562 | 0.7158 | -130.9939 | -5.3712 | 2.6693 | 0.0567 | -5.8627 | -4.5976 | 2.0854 |  | 0.088 | -1.7774 | 4.0144 | 3.3657 | 3.3534 | 1.041 | 10.6918 | 14.1946 | 14.7992 | 11.0789 | 0.0002 | -0.003 | 0 | 0.0035 | 0.0014 | -0.0008 | 0.0216 | -0.002 | -0.0221 | -360.1435 | 17.4274 | -360.5004 | 17.7395 | -360.8235 | 18.1502 | -360.8697 | 17.5239 | -352.6752 | 18.7497 | -352.7213 | 16.7991
12:03 | 2571 | 30.6084 | 197.5858 | 443.2421 | 448.8878 | -18.785 | -46.1409 | 7.079 | 4.0108 | -2.2792 | -3.1471 | -0.0585 | -2.7787 | 6.8431 | 0.4233 | 0.5986 | 0.6388 | 0.9543 | 0.7166 | -131.1081 | -5.4173 | 2.5103 | 0.073 | -5.8473 | -4.5748 | 2.0965 |  | 0.0657 | -1.7638 | 4.0159 | 3.3647 | 3.3482 | 1.0402 | 10.6944 | 14.1558 | 14.7503 | 11.0136 | -0.0001 | -0.0031 | 0.0012 | 0.0043 | 0.0001 | -0.0005 | 0.0181 | -0.0007 | -0.0245 | -360.1865 | 17.4377 | -360.4973 | 17.7498 | -360.8543 | 18.1687 | -360.8912 | 17.5342 | -352.7244 | 18.7559 | -352.709 | 16.8135
12:03 | 2572 | 30.6419 | 197.6451 | 443.3517 | 448.8404 | -18.6821 | -45.9531 | 7.2039 | 4.0366 | -2.2336 | -3.2025 | -0.0908 | -2.7467 | 6.8258 | 0.4407 | 0.5976 | 0.6404 | 0.9543 | 0.7164 | -131.1116 | -5.3459 | 2.645 | 0.078 | -5.9879 | -4.6029 | 2.0541 |  | 0.1178 | -1.7087 | 4.0142 | 3.363 | 3.3484 | 1.0402 | 10.7161 | 14.1958 | 14.7542 | 11.0453 | -0.0002 | -0.0023 | 0.0011 | 0.0038 | 0.0016 | -0.0002 | 0.0175 | -0.002 | -0.0293 | -360.1465 | 17.4028 | -360.4481 | 17.7231 | -360.8389 | 18.1461 | -360.8912 | 17.5424 | -352.6629 | 18.7251 | -352.6906 | 16.8032
12:03 | 2573 | 30.7715 | 197.5609 | 443.3556 | 448.7997 | -18.7519 | -46.008 | 7.1686 | 4.0007 | -2.2544 | -3.0994 | -0.0854 | -2.7823 | 6.8536 | 0.3979 | 0.598 | 0.6397 | 0.9546 | 0.7166 | -131.0287 | -5.3597 | 2.7229 | 0.0438 | -5.9297 | -4.7418 | 2.0568 |  | 0.1228 | -1.634 | 4.0142 | 3.3621 | 3.3505 | 1.0411 | 10.7093 | 14.206 | 14.7518 | 11.0215 | -0.0001 | -0.0025 | 0.0003 | 0.0033 | 0.0004 | -0.0005 | 0.0263 | -0.0029 | -0.0126 | -360.2142 | 17.4418 | -360.4881 | 17.7231 | -360.7927 | 18.1563 | -360.9312 | 17.5445 | -352.7244 | 18.7579 | -352.6721 | 16.7786
12:03 | 2574 | 30.7095 | 197.5058 | 443.2562 | 448.8318 | -18.7852 | -46.1134 | 7.1652 | 3.9645 | -2.2394 | -3.1636 | -0.0765 | -2.7518 | 6.9162 | 0.3804 | 0.5979 | 0.6402 | 0.9552 | 0.717 | -131.0654 | -5.3879 | 2.6652 | 0.0024 | -5.8975 | -4.542 | 2.107 |  | 0.2046 | -1.7036 | 4.0156 | 3.3611 | 3.3467 | 1.0403 | 10.7279 | 14.1721 | 14.7616 | 11.041 | 0.0001 | -0.0031 | 0.0004 | 0.0038 | 0.0006 | -0.0007 | 0.0035 | -0.0097 | -0.0115 | -360.1865 | 17.4192 | -360.4758 | 17.7231 | -360.8112 | 18.1379 | -360.8389 | 17.5096 | -352.709 | 18.7456 | -352.706 | 16.8012
12:03 | 2575 | 30.8565 | 197.5509 | 443.4473 | 448.889 | -18.7581 | -46.107 | 7.1181 | 4.0111 | -2.2933 | -3.0785 | -0.1476 | -2.7887 | 6.883 | 0.4281 | 0.5979 | 0.6403 | 0.9549 | 0.7167 | -131.056 | -5.3345 | 2.642 | 0.0406 | -5.863 | -4.5049 | 2.0923 |  | 0.2227 | -1.8266 | 4.015 | 3.3683 | 3.3484 | 1.04 | 10.7243 | 14.1807 | 14.7906 | 11.0247 | 0.0001 | -0.003 | 0.0006 | 0.0041 | 0.001 | -0.0003 | -0.0033 | -0.0038 | -0.0201 | -360.1527 | 17.4007 | -360.4789 | 17.7498 | -360.8758 | 18.1892 | -360.9404 | 17.526 | -352.6567 | 18.7333 | -352.6813 | 16.8094
12:03 | 2576 | 30.8195 | 197.5263 | 443.3375 | 448.8699 | -18.7759 | -46.0741 | 7.154 | 3.9272 | -2.4214 | -3.1904 | -0.097 | -2.7087 | 6.9414 | 0.436 | 0.5984 | 0.643 | 0.9515 | 0.7169 | -131.0624 | -5.4217 | 2.5308 | 0.095 | -5.903 | -4.5614 | 2.0877 |  | 0.155 | -1.7528 | 4.0151 | 3.3605 | 3.3464 | 1.0412 | 10.6957 | 14.174 | 14.7553 | 11.027 | -0.0003 | -0.0029 | 0.0007 | 0.0036 | 0.0004 | -0.0007 | 0.0057 | -0.001 | -0.0089 | -360.1435 | 17.3987 | -360.445 | 17.7128 | -360.802 | 18.1502 | -360.8974 | 17.5588 | -352.7029 | 18.7333 | -352.6475 | 16.7786
12:03 | 2577 | 30.8516 | 197.6072 | 443.4498 | 448.9383 | -18.7245 | -46.1369 | 7.2248 | 4.0233 | -2.3207 | -3.1954 | -0.0825 | -2.7161 | 7.0164 | 0.482 | 0.5966 | 0.6456 | 0.9539 | 0.7186 | -131.0497 | -5.4189 | 2.5556 | 0.028 | -5.9476 | -4.4728 | 2.1285 |  | 0.2007 | -1.754 | 4.0147 | 3.3614 | 3.3467 | 1.0418 | 10.6712 | 14.1561 | 14.735 | 11.0302 | 0.0001 | -0.0023 | 0.0014 | 0.0041 | 0.0009 | -0.0004 | 0.0039 | -0.014 | -0.009 | -360.1927 | 17.4582 | -360.5343 | 17.7498 | -360.8789 | 18.142 | -360.8789 | 17.526 | -352.7152 | 18.7703 | -352.7706 | 16.8135
12:03 | 2578 | 30.8597 | 197.6803 | 443.4402 | 448.8492 | -18.8131 | -46.2135 | 7.1353 | 4.0517 | -2.3171 | -3.187 | -0.0636 | -2.7113 | 6.9194 | 0.4842 | 0.5979 | 0.6398 | 0.9558 | 0.7173 | -130.9648 | -5.3775 | 2.699 | 0.0951 | -5.9272 | -4.366 | 2.1768 |  | 0.1974 | -1.7873 | 4.0128 | 3.3638 | 3.3508 | 1.0403 | 10.7209 | 14.171 | 14.7902 | 11.0338 | -0.0001 | -0.0031 | 0.0007 | 0.0038 | 0.0004 | -0.0008 | 0.0081 | -0.0058 | -0.0069 | -360.1127 | 17.3987 | -360.4758 | 17.7498 | -360.8697 | 18.144 | -360.8481 | 17.4952 | -352.6352 | 18.7333 | -352.7183 | 16.8135
12:03 | 2579 | 30.8973 | 197.5606 | 443.4338 | 448.9355 | -18.8473 | -46.1921 | 7.0804 | 4.0558 | -2.4056 | -3.211 | -0.1403 | -2.7372 | 6.8724 | 0.5086 | 0.5984 | 0.642 | 0.9547 | 0.717 | -130.9914 | -5.2668 | 2.6482 | 0.1543 | -5.8953 | -4.4547 | 2.1488 |  | 0.1471 | -1.7632 | 4.0146 | 3.3619 | 3.3488 | 1.041 | 10.7336 | 14.2013 | 14.8042 | 11.0518 | 0.0001 | -0.0032 | 0.0007 | 0.0035 | 0.0011 | -0.0005 | 0.0135 | -0.0141 | -0.0135 | -360.165 | 17.4172 | -360.4573 | 17.7149 | -360.8266 | 18.1851 | -360.962 | 17.5568 | -352.7306 | 18.7333 | -352.6906 | 16.7848
12:03 | 2580 | 30.8628 | 197.5777 | 443.4259 | 448.9959 | -18.9359 | -46.2152 | 7.0406 | 4.1601 | -2.2671 | -3.134 | -0.0012 | -2.7976 | 6.9347 | 0.5141 | 0.5972 | 0.6409 | 0.9526 | 0.7169 | -131.0983 | -5.3999 | 2.5344 | 0.0643 | -5.8866 | -4.4338 | 2.1276 |  | 0.1348 | -1.7092 | 4.0141 | 3.3613 | 3.348 | 1.0404 | 10.6873 | 14.1725 | 14.7647 | 11.0283 | -0.0004 | -0.003 | 0.0013 | 0.0036 | 0.001 | -0.0001 | 0.0137 | -0.0121 | -0.0089 | -360.2235 | 17.4356 | -360.5004 | 17.7067 | -360.7681 | 18.1112 | -360.8574 | 17.5424 | -352.7152 | 18.7579 | -352.6875 | 16.7786
12:03 | 2581 | 30.8204 | 197.5452 | 443.4399 | 448.9194 | -18.8542 | -46.1096 | 7.0946 | 4.1642 | -2.2709 | -3.1546 | 0.0112 | -2.868 | 6.8881 | 0.532 | 0.5976 | 0.6377 | 0.9544 | 0.7176 | -131.0959 | -5.3206 | 2.5637 | -0.0346 | -5.9296 | -4.4185 | 2.1141 |  | 0.1056 | -1.7839 | 4.0151 | 3.3641 | 3.3472 | 1.0405 | 10.7139 | 14.2222 | 14.7736 | 11.0609 | -0.0007 | -0.0028 | 0.0004 | 0.0035 | 0.0011 | -0.0005 | 0.0124 | -0.0012 | -0.0107 | -360.1342 | 17.4315 | -360.5373 | 17.7559 | -360.8666 | 18.1748 | -360.8758 | 17.5239 | -352.7029 | 18.7538 | -352.7521 | 16.8258
12:03 | 2582 | 30.8727 | 197.6505 | 443.6048 | 448.9475 | -18.9031 | -46.076 | 7.0205 | 4.1326 | -2.2819 | -3.2477 | 0.0141 | -2.8814 | 6.8758 | 0.4378 | 0.5981 | 0.638 | 0.9557 | 0.7182 | -131.1073 | -5.3791 | 2.5467 | 0.055 | -5.8923 | -4.398 | 2.114 |  | 0.1674 | -1.8238 | 4.0142 | 3.3637 | 3.3522 | 1.041 | 10.7105 | 14.1896 | 14.78 | 11.0176 | -0.0001 | -0.0031 | 0.0008 | 0.0042 | 0.0006 | -0.0002 | -0.0099 | -0.0031 | -0.0068 | -360.1404 | 17.374 | -360.4081 | 17.7067 | -360.7927 | 18.1728 | -360.9281 | 17.5301 | -352.6629 | 18.7107 | -352.6198 | 16.7786
12:03 | 2583 | 30.9489 | 197.6747 | 443.5382 | 448.9197 | -18.9533 | -46.1265 | 7.0687 | 4.1721 | -2.159 | -3.166 | 0.062 | -2.7455 | 6.9374 | 0.5035 | 0.5983 | 0.6394 | 0.955 | 0.7185 | -131.0625 | -5.3545 | 2.6139 | 0.0379 | -6.0389 | -4.5573 | 2.048 |  | 0.135 | -1.6927 | 4.0157 | 3.3626 | 3.3507 | 1.04 | 10.7093 | 14.2001 | 14.7855 | 11.045 | 0 | -0.0034 | 0.0008 | 0.0042 | 0.0011 | -0.0005 | 0.0161 | -0.011 | -0.0173 | -360.1804 | 17.4356 | -360.4912 | 17.7272 | -360.8235 | 18.1625 | -360.9558 | 17.5629 | -352.7213 | 18.7477 | -352.6967 | 16.793
12:03 | 2584 | 30.9776 | 197.719 | 443.5548 | 449.0049 | -18.9425 | -46.0454 | 7.0481 | 4.1621 | -2.139 | -3.2378 | -0.0083 | -2.6905 | 7.0003 | 0.5359 | 0.5971 | 0.6436 | 0.9562 | 0.7166 | -131.0019 | -5.298 | 2.6287 | 0.0491 | -6.0071 | -4.5447 | 2.0501 |  | 0.15 | -1.7079 | 4.0133 | 3.3645 | 3.3502 | 1.0392 | 10.6771 | 14.173 | 14.7608 | 11.0371 | -0.0002 | -0.0031 | 0.0008 | 0.0041 | 0.0007 | -0.0002 | 0.0184 | 0.0027 | -0.0067 | -360.1281 | 17.4213 | -360.5004 | 17.7436 | -360.8512 | 18.1235 | -360.842 | 17.5096 | -352.6444 | 18.7353 | -352.7614 | 16.8217
12:03 | 2585 | 30.9539 | 197.6987 | 443.6559 | 449.0986 | -18.9347 | -46.1136 | 7.1175 | 4.1252 | -2.2497 | -3.1625 | 0.037 | -2.7078 | 7.0414 | 0.4703 | 0.5997 | 0.6437 | 0.9549 | 0.7171 | -131.0037 | -5.3356 | 2.6052 | 0.0942 | -5.8346 | -4.4178 | 2.1506 |  | 0.1435 | -1.6619 | 4.0151 | 3.3632 | 3.3525 | 1.0395 | 10.692 | 14.2001 | 14.7739 | 11.0276 | -0.0006 | -0.003 | 0.0014 | 0.0047 | 0.0013 | -0.0003 | -0.0052 | -0.0077 | -0.0028 | -360.1835 | 17.4233 | -360.485 | 17.7498 | -360.9035 | 18.1748 | -360.9066 | 17.526 | -352.6937 | 18.7415 | -352.6967 | 16.8197
12:03 | 2586 | 31.0181 | 197.7265 | 443.5952 | 449.1072 | -18.9379 | -46.1753 | 6.995 | 4.1003 | -2.1845 | -3.1184 | -0.0997 | -2.7683 | 7.0182 | 0.6018 | 0.5984 | 0.6398 | 0.9546 | 0.7165 | -131.0438 | -5.3711 | 2.5548 | 0.1145 | -5.797 | -4.4237 | 2.1369 |  | 0.126 | -1.6157 | 4.0139 | 3.3647 | 3.3505 | 1.0414 | 10.6956 | 14.1974 | 14.7574 | 11.0147 | -0.0005 | -0.0031 | 0.0005 | 0.0033 | 0.0008 | -0.0006 | 0.0057 | 0.0024 | -0.0239 | -360.2019 | 17.4131 | -360.4666 | 17.6985 | -360.7804 | 18.1358 | -360.922 | 17.5383 | -352.6783 | 18.7415 | -352.7029 | 16.7848
12:03 | 2587 | 30.9782 | 197.6336 | 443.6051 | 448.984 | -19.0198 | -46.0729 | 6.9831 | 4.1186 | -2.1974 | -3.0321 | 0.0294 | -2.7925 | 6.9715 | 0.5094 | 0.5988 | 0.6418 | 0.9553 | 0.7191 | -131.0912 | -5.3888 | 2.5875 | 0.0736 | -5.7864 | -4.3798 | 2.1806 |  | 0.074 | -1.6934 | 4.015 | 3.3628 | 3.3516 | 1.0407 | 10.7196 | 14.2108 | 14.7804 | 11.0258 | 0.0001 | -0.0029 | 0.0007 | 0.0035 | 0.0008 | -0.0001 | 0.0169 | -0.0101 | -0.0066 | -360.2111 | 17.4356 | -360.5435 | 17.7477 | -360.8327 | 18.1337 | -360.882 | 17.5363 | -352.7213 | 18.7579 | -352.749 | 16.8299
12:03 | 2588 | 30.9933 | 197.7359 | 443.5705 | 449.0167 | -18.9461 | -46.0979 | 7.1284 | 4.0992 | -2.1624 | -3.1837 | 0.055 | -2.7438 | 6.9358 | 0.5303 | 0.5994 | 0.6401 | 0.9562 | 0.7172 | -131.0811 | -5.3418 | 2.5179 | 0.0987 | -5.7405 | -4.3533 | 2.128 |  | 0.0656 | -1.7435 | 4.0142 | 3.3632 | 3.3516 | 1.0418 | 10.7301 | 14.2094 | 14.7954 | 11.0482 | -0.0002 | -0.0036 | 0.0005 | 0.0035 | 0.0007 | -0.0007 | -0.0064 | -0.0023 | -0.0111 | -360.1558 | 17.3905 | -360.4573 | 17.7087 | -360.8297 | 18.1543 | -360.8758 | 17.5157 | -352.6352 | 18.723 | -352.669 | 16.8074
12:03 | 2589 | 30.9623 | 197.6555 | 443.5682 | 448.9509 | -18.966 | -46.1296 | 7.0337 | 4.159 | -2.2252 | -3.2121 | 0.0198 | -2.8223 | 6.9784 | 0.5764 | 0.5988 | 0.6396 | 0.954 | 0.7179 | -130.9839 | -5.3997 | 2.6103 | 0.1332 | -5.6995 | -4.4191 | 2.1435 |  | 0.1354 | -1.7125 | 4.0146 | 3.364 | 3.3527 | 1.0401 | 10.7324 | 14.2062 | 14.7992 | 11.0673 | -0.0002 | -0.0027 | -0.0003 | 0.003 | 0.0002 | -0.0002 | 0.0157 | -0.0029 | -0.0064 | -360.2111 | 17.4274 | -360.4819 | 17.7313 | -360.8143 | 18.1584 | -360.9312 | 17.5609 | -352.6875 | 18.7456 | -352.6967 | 16.8094
12:03 | 2590 | 30.9511 | 197.7257 | 443.5795 | 448.9643 | -18.8508 | -46.0633 | 7.019 | 4.2089 | -2.1872 | -3.1445 | 0.0116 | -2.8206 | 7.0104 | 0.5199 | 0.5988 | 0.6394 | 0.9561 | 0.7161 | -131.0669 | -5.3557 | 2.6018 | 0.0575 | -5.7271 | -4.4265 | 2.1417 |  | 0.1851 | -1.6277 | 4.0143 | 3.3606 | 3.3537 | 1.0408 | 10.7347 | 14.2085 | 14.8077 | 11.0406 | -0.0003 | -0.0025 | 0.0006 | 0.0038 | 0.0014 | -0.0007 | -0.0023 | -0.0117 | -0.0123 | -360.1435 | 17.4151 | -360.485 | 17.719 | -360.8081 | 18.1563 | -360.8758 | 17.5178 | -352.6721 | 18.7333 | -352.6783 | 16.793
12:03 | 2591 | 30.9882 | 197.7867 | 443.5366 | 448.9686 | -18.7356 | -46.0104 | 7.2154 | 4.2186 | -2.2282 | -3.1315 | 0.0253 | -2.8298 | 6.9162 | 0.4888 | 0.598 | 0.6409 | 0.9581 | 0.7174 | -131.0828 | -5.3943 | 2.571 | -0.0476 | -5.7985 | -4.4428 | 2.1836 |  | 0.0915 | -1.6818 | 4.0141 | 3.3622 | 3.3514 | 1.0399 | 10.6966 | 14.1989 | 14.7957 | 11.0323 | 0.0001 | -0.0028 | 0.0006 | 0.0038 | 0.0007 | -0.0003 | 0.0064 | -0.0122 | -0.0127 | -360.1496 | 17.4254 | -360.5158 | 17.7559 | -360.842 | 18.1584 | -360.9097 | 17.5465 | -352.6721 | 18.7395 | -352.709 | 16.8094
12:03 | 2592 | 31.0365 | 197.7297 | 443.6902 | 449.066 | -18.8336 | -45.9877 | 7.2707 | 4.2297 | -2.2006 | -3.2061 | 0.0612 | -2.9359 | 6.9147 | 0.4091 | 0.5998 | 0.6379 | 0.9557 | 0.7169 | -131.0831 | -5.3762 | 2.6723 | 0.0499 | -5.8724 | -4.4458 | 2.1275 |  | 0.0865 | -1.7304 | 4.0145 | 3.3638 | 3.354 | 1.0411 | 10.6885 | 14.1792 | 14.7466 | 11.0302 | 0.0001 | -0.0031 | 0.0005 | 0.0037 | 0.0012 | -0.0005 | 0.018 | -0.0024 | 0.018 | -360.165 | 17.3905 | -360.4419 | 17.7252 | -360.8389 | 18.1481 | -360.8974 | 17.5363 | -352.6721 | 18.7189 | -352.6598 | 16.8012
12:03 | 2593 | 31.0209 | 197.6879 | 443.4636 | 448.9872 | -18.7938 | -45.908 | 7.1534 | 4.1205 | -2.2582 | -3.2888 | 0.0665 | -2.7615 | 6.971 | 0.4821 | 0.598 | 0.6371 | 0.9579 | 0.7161 | -131.0717 | -5.4003 | 2.6275 | 0.0146 | -5.9472 | -4.435 | 2.0995 |  | 0.0867 | -1.7892 | 4.0154 | 3.3643 | 3.3531 | 1.041 | 10.7209 | 14.1885 | 14.797 | 11.0392 | -0.0004 | -0.0029 | 0.0004 | 0.0033 | 0.0005 | -0.0005 | -0.002 | -0.0066 | -0.0082 | -360.1958 | 17.4315 | -360.5527 | 17.7662 | -360.845 | 18.1666 | -360.8974 | 17.5363 | -352.6998 | 18.7497 | -352.7121 | 16.8156
12:03 | 2594 | 31.0203 | 197.682 | 443.5379 | 449.1227 | -18.7769 | -45.8789 | 7.1597 | 4.0804 | -2.2268 | -3.2886 | -0.0235 | -2.7745 | 6.9951 | 0.4928 | 0.597 | 0.6401 | 0.9558 | 0.7139 | -131.1605 | -5.3547 | 2.6296 | 0.2125 | -5.8754 | -4.3931 | 2.1815 |  | 0.1379 | -1.7567 | 4.0153 | 3.3615 | 3.3531 | 1.0386 | 10.6747 | 14.1767 | 14.7312 | 11.0169 | 0 | -0.0027 | 0.0006 | 0.0033 | 0.0006 | -0.001 | 0.0078 | 0.001 | 0.0013 | -360.1619 | 17.4151 | -360.4912 | 17.7416 | -360.845 | 18.1399 | -360.8327 | 17.5198 | -352.626 | 18.7353 | -352.706 | 16.8115
12:03 | 2595 | 30.9336 | 197.6376 | 443.5585 | 448.9639 | -18.758 | -45.9231 | 7.2427 | 4.1549 | -2.1908 | -3.2494 | -0.014 | -2.8255 | 6.9952 | 0.3574 | 0.598 | 0.638 | 0.9554 | 0.7166 | -131.1225 | -5.3928 | 2.627 | 0.2887 | -5.7657 | -4.3455 | 2.1595 |  | 0.1163 | -1.7416 | 4.0166 | 3.3652 | 3.3521 | 1.0416 | 10.7082 | 14.1814 | 14.7425 | 11.0212 | -0.0001 | -0.0029 | 0.0007 | 0.0038 | 0.001 | -0.0001 | 0.0194 | -0.0048 | -0.0106 | -360.1988 | 17.4233 | -360.4973 | 17.7498 | -360.8204 | 18.1563 | -360.9374 | 17.5691 | -352.706 | 18.7374 | -352.6906 | 16.8094
12:03 | 2596 | 31.0789 | 197.6792 | 443.5572 | 449.0673 | -18.7605 | -45.8621 | 7.1997 | 4.1271 | -2.1837 | -3.2484 | 0.0497 | -2.8332 | 7.0311 | 0.3846 | 0.599 | 0.6406 | 0.9543 | 0.7173 | -131.1362 | -5.3462 | 2.5642 | 0.2215 | -5.7859 | -4.3714 | 2.1761 |  | 0.0687 | -1.7054 | 4.0135 | 3.3625 | 3.3476 | 1.0392 | 10.7209 | 14.2173 | 14.7786 | 11.0396 | 0.0001 | -0.0031 | 0.0007 | 0.004 | 0.0007 | -0.0005 | 0.0052 | -0.017 | -0.0207 | -360.1773 | 17.4213 | -360.4727 | 17.7108 | -360.7927 | 18.1194 | -360.8727 | 17.5383 | -352.6813 | 18.7497 | -352.6752 | 16.7827
12:03 | 2597 | 31.0234 | 197.6908 | 443.5184 | 449.0347 | -18.7828 | -45.8506 | 7.2838 | 4.1777 | -2.2004 | -3.1328 | 0.0763 | -2.7843 | 7.0211 | 0.4301 | 0.5978 | 0.6397 | 0.9548 | 0.7164 | -131.0799 | -5.4388 | 2.5687 | 0.1926 | -5.8242 | -4.3701 | 2.1779 |  | 0.0735 | -1.6901 | 4.0156 | 3.3671 | 3.3531 | 1.0394 | 10.7174 | 14.2023 | 14.7408 | 11.0129 | -0.0003 | -0.003 | 0.0012 | 0.0041 | 0.0012 | -0.0003 | 0.0005 | -0.0068 | -0.0231 | -360.1742 | 17.4336 | -360.525 | 17.7744 | -360.882 | 18.1235 | -360.885 | 17.5506 | -352.6721 | 18.7579 | -352.7244 | 16.8156
12:03 | 2598 | 30.9502 | 197.6166 | 443.4116 | 449.1194 | -18.7684 | -45.9672 | 7.1389 | 4.1331 | -2.2384 | -3.2447 | -0.0571 | -2.7976 | 7.022 | 0.5049 | 0.5964 | 0.638 | 0.9499 | 0.7152 | -131.1614 | -5.4176 | 2.5163 | 0.2122 | -5.833 | -4.346 | 2.1026 |  | 0.1839 | -1.7279 | 4.0152 | 3.3624 | 3.3534 | 1.0395 | 10.7081 | 14.2048 | 14.7678 | 11.0493 | -0.0003 | -0.0022 | 0.0008 | 0.0042 | 0.0007 | -0.0004 | 0.0083 | -0.0168 | -0.015 | -360.1496 | 17.3884 | -360.4481 | 17.7293 | -360.8297 | 18.1481 | -360.8974 | 17.5198 | -352.666 | 18.7087 | -352.6352 | 16.793
12:03 | 2599 | 30.9698 | 197.6435 | 443.4954 | 449.1541 | -18.7234 | -45.8932 | 7.1213 | 4.1276 | -2.3069 | -3.1719 | 0.0554 | -2.7755 | 7.0375 | 0.4598 | 0.598 | 0.6421 | 0.956 | 0.7167 | -131.1263 | -5.4561 | 2.6378 | 0.1702 | -5.8649 | -4.4109 | 2.0548 |  | 0.138 | -1.7583 | 4.0138 | 3.3585 | 3.3497 | 1.0392 | 10.6873 | 14.213 | 14.8053 | 11.0803 | 0 | -0.0028 | 0.0008 | 0.0039 | 0.0006 | -0.0008 | 0.0034 | -0.0096 | -0.0069 | -360.2111 | 17.4233 | -360.4758 | 17.7375 | -360.8358 | 18.1379 | -360.9251 | 17.5671 | -352.7213 | 18.7374 | -352.7029 | 16.7889
12:03 | 2600 | 30.9828 | 197.6734 | 443.5917 | 449.1873 | -18.7428 | -45.9092 | 7.2244 | 4.0628 | -2.2518 | -3.1714 | 0.0615 | -2.7609 | 6.937 | 0.5298 | 0.5985 | 0.6396 | 0.9513 | 0.7156 | -131.1665 | -5.5991 | 2.4886 | 0.1473 | -5.881 | -4.4304 | 2.0468 |  | 0.0184 | -1.8126 | 4.0141 | 3.3609 | 3.3506 | 1.0366 | 10.7232 | 14.2082 | 14.7824 | 11.0125 | 0.0003 | -0.0031 | 0.0005 | 0.0036 | 0.0006 | 0.0001 | -0.0077 | -0.0166 | -0.0155 | -360.1496 | 17.4233 | -360.5343 | 17.758 | -360.8358 | 18.0927 | -360.8358 | 17.5137 | -352.6475 | 18.7128 | -352.7152 | 16.8299
12:03 | 2601 | 30.9606 | 197.7611 | 443.6005 | 449.1989 | -18.7108 | -45.9853 | 7.2554 | 4.1199 | -2.24 | -3.2044 | 0.0469 | -2.7661 | 6.9571 | 0.4139 | 0.5985 | 0.6407 | 0.957 | 0.7168 | -131.1852 | -5.5566 | 2.5732 | 0.1012 | -5.9018 | -4.3843 | 2.1001 |  | 0.1594 | -1.7254 | 4.015 | 3.3624 | 3.353 | 1.0378 | 10.7117 | 14.2023 | 14.7813 | 11.0533 | 0.0001 | -0.0029 | 0.0008 | 0.0039 | 0.0011 | -0.0008 | -0.0017 | -0.014 | -0.0246 | -360.1558 | 17.411 | -360.5219 | 17.7806 | -360.9066 | 18.144 | -360.9189 | 17.5157 | -352.6537 | 18.6861 | -352.7429 | 16.8566
12:03 | 2602 | 31.0162 | 197.7963 | 443.6455 | 449.2696 | -18.7361 | -45.9359 | 7.3014 | 4.1574 | -2.1888 | -3.2716 | 0.0718 | -2.7325 | 7.0024 | 0.4362 | 0.5981 | 0.6421 | 0.9584 | 0.7163 | -131.1112 | -5.591 | 2.6221 | -0.0639 | -5.8448 | -4.3995 | 2.0686 |  | 0.1594 | -1.8008 | 4.0165 | 3.3631 | 3.3516 | 1.038 | 10.6863 | 14.1825 | 14.7197 | 11.0169 | -0.0005 | -0.0029 | 0.0003 | 0.0032 | 0.0001 | -0.0005 | 0.0095 | -0.0082 | -0.0081 | -360.1742 | 17.4069 | -360.445 | 17.7149 | -360.7897 | 18.105 | -360.9158 | 17.5568 | -352.6967 | 18.6922 | -352.669 | 16.8012
12:03 | 2603 | 31.0502 | 197.8303 | 443.8147 | 449.3196 | -18.7848 | -45.8573 | 7.2395 | 4.2323 | -2.2398 | -3.1923 | 0.0653 | -2.7603 | 7.0306 | 0.4402 | 0.5972 | 0.6373 | 0.9578 | 0.7156 | -131.1845 | -5.5486 | 2.654 | 0.1858 | -5.751 | -4.3818 | 2.1543 |  | 0.1205 | -1.8395 | 4.015 | 3.3664 | 3.3539 | 1.0364 | 10.6942 | 14.214 | 14.7882 | 11.0298 | -0.0001 | -0.0025 | 0.0006 | 0.0037 | 0.001 | -0.0005 | 0.0036 | -0.0146 | -0.0109 | -360.2573 | 17.4582 | -360.5435 | 17.7662 | -360.8389 | 18.0927 | -360.8604 | 17.5547 | -352.7213 | 18.7477 | -352.7552 | 16.8546
12:03 | 2604 | 31.0345 | 197.7762 | 443.8043 | 449.2604 | -18.7602 | -45.8341 | 7.2395 | 4.1662 | -2.263 | -3.2466 | 0.0833 | -2.8851 | 6.9931 | 0.4626 | 0.5985 | 0.6386 | 0.9521 | 0.7155 | -131.2434 | -5.664 | 2.6145 | 0.2732 | -5.7398 | -4.3563 | 2.1975 |  | 0.169 | -1.8547 | 4.0148 | 3.36 | 3.352 | 1.0369 | 10.7163 | 14.1953 | 14.8089 | 11.0522 | -0.0001 | -0.0033 | 0.0008 | 0.0037 | 0.0002 | -0.0007 | 0.0158 | -0.015 | -0.0119 | -360.1096 | 17.3884 | -360.4666 | 17.7683 | -360.845 | 18.1276 | -360.8635 | 17.528 | -352.6106 | 18.6861 | -352.6783 | 16.8525
12:03 | 2605 | 31.0141 | 197.7303 | 443.7695 | 449.3708 | -18.8182 | -45.9603 | 7.1878 | 4.1839 | -2.1799 | -3.2598 | 0.0553 | -2.7924 | 7.0414 | 0.4691 | 0.5994 | 0.6416 | 0.9562 | 0.7176 | -131.2101 | -5.6226 | 2.5863 | 0.1218 | -5.7816 | -4.3415 | 2.1874 |  | 0.1582 | -1.7917 | 4.0135 | 3.3607 | 3.3505 | 1.0376 | 10.7243 | 14.2501 | 14.8138 | 11.0767 | -0.0001 | -0.0029 | 0.0006 | 0.0038 | 0.0006 | -0.0008 | 0.0046 | -0.0062 | -0.0067 | -360.1988 | 17.3905 | -360.4389 | 17.7128 | -360.7804 | 18.1399 | -360.9404 | 17.5794 | -352.709 | 18.6984 | -352.6229 | 16.8094
12:03 | 2606 | 31.1304 | 197.8482 | 443.7725 | 449.3519 | -18.8254 | -46.0436 | 7.1508 | 4.1581 | -2.2426 | -3.3554 | 0.119 | -2.7447 | 6.9383 | 0.5187 | 0.5986 | 0.6411 | 0.9559 | 0.7181 | -131.1684 | -5.6111 | 2.5777 | 0.0755 | -5.8301 | -4.418 | 2.1621 |  | 0.1012 | -1.6754 | 4.015 | 3.367 | 3.351 | 1.0377 | 10.7301 | 14.2154 | 14.7848 | 11.0421 | -0.0003 | -0.0025 | 0.0011 | 0.0045 | 0.0007 | -0.0005 | 0.0083 | -0.0069 | -0.0082 | -360.2019 | 17.4315 | -360.5158 | 17.7621 | -360.8266 | 18.105 | -360.8943 | 17.5568 | -352.6752 | 18.7189 | -352.7029 | 16.834
12:03 | 2607 | 31.0472 | 197.8579 | 443.7526 | 449.4477 | -18.8101 | -46.0307 | 7.2346 | 4.1277 | -2.2052 | -3.2666 | 0.1413 | -2.8296 | 6.9295 | 0.5144 | 0.5969 | 0.6407 | 0.9548 | 0.7156 | -131.1737 | -5.6508 | 2.6293 | 0.2121 | -5.7619 | -4.2483 | 2.2219 |  | 0.1269 | -1.7578 | 4.016 | 3.3637 | 3.3494 | 1.0364 | 10.7439 | 14.2351 | 14.8049 | 11.0847 | -0.0002 | -0.0027 | 0.0008 | 0.0042 | 0.0004 | 0.0001 | 0.0021 | -0.012 | -0.0194 | -360.0634 | 17.3782 | -360.4881 | 17.7683 | -360.882 | 18.1296 | -360.8543 | 17.5178 | -352.6352 | 18.6799 | -352.6752 | 16.871
12:03 | 2608 | 31.1184 | 197.833 | 443.7078 | 449.3923 | -18.7522 | -45.9737 | 7.2115 | 4.1179 | -2.1847 | -3.2397 | 0.0374 | -2.8489 | 6.9301 | 0.4681 | 0.5969 | 0.64 | 0.9582 | 0.7153 | -131.1314 | -5.5879 | 2.6662 | 0.1791 | -5.7362 | -4.3288 | 2.2091 |  | 0.1286 | -1.6728 | 4.016 | 3.3632 | 3.3507 | 1.0366 | 10.7151 | 14.2521 | 14.7912 | 11.0276 | 0 | -0.0033 | 0.0001 | 0.0038 | 0.0008 | -0.0006 | 0.0067 | -0.0102 | 0.0104 | -360.1835 | 17.4028 | -360.4696 | 17.7457 | -360.8297 | 18.144 | -360.9097 | 17.5609 | -352.6875 | 18.6737 | -352.666 | 16.8361
12:03 | 2609 | 31.0281 | 197.7829 | 443.7284 | 449.4704 | -18.7258 | -45.8566 | 7.3232 | 4.1274 | -2.222 | -3.3325 | 0.1158 | -2.8685 | 6.8922 | 0.4529 | 0.599 | 0.6411 | 0.9544 | 0.716 | -131.2148 | -5.6414 | 2.582 | 0.1444 | -5.7465 | -4.3463 | 2.1416 |  | 0.0217 | -1.803 | 4.0165 | 3.3646 | 3.3505 | 1.0373 | 10.7071 | 14.2207 | 14.7817 | 11.0432 | -0.0001 | -0.0036 | 0.0008 | 0.0037 | -0.0001 | -0.0004 | 0.0076 | -0.0081 | -0.0071 | -360.2358 | 17.45 | -360.4973 | 17.7436 | -360.8297 | 18.0927 | -360.8358 | 17.5486 | -352.7183 | 18.7169 | -352.7121 | 16.8299
12:03 | 2610 | 30.9997 | 197.78 | 443.6761 | 449.3049 | -18.7241 | -45.8875 | 7.2938 | 4.2538 | -2.1595 | -3.1821 | 0.1304 | -2.8535 | 6.9333 | 0.4119 | 0.5985 | 0.6411 | 0.9536 | 0.7182 | -131.2135 | -5.5682 | 2.5952 | 0.1693 | -5.7361 | -4.35 | 2.1711 |  | 0.0456 | -1.809 | 4.0155 | 3.3645 | 3.3515 | 1.0388 | 10.7093 | 14.2232 | 14.7565 | 11.045 | -0.0004 | -0.0029 | 0.0014 | 0.0039 | 0.0008 | -0.0008 | 0.0091 | -0.0131 | -0.0055 | -360.1558 | 17.4213 | -360.5496 | 17.7683 | -360.8666 | 18.1194 | -360.9004 | 17.5301 | -352.669 | 18.7045 | -352.7367 | 16.8505
12:03 | 2611 | 31.1051 | 197.7904 | 443.7101 | 449.2998 | -18.7122 | -45.9002 | 7.3226 | 4.2051 | -2.0925 | -3.219 | 0.2167 | -2.8132 | 6.9785 | 0.3657 | 0.5977 | 0.6398 | 0.9563 | 0.718 | -131.076 | -5.5661 | 2.7027 | 0.086 | -5.8275 | -4.3892 | 2.1094 |  | 0.1196 | -1.6657 | 4.0163 | 3.3639 | 3.3527 | 1.0372 | 10.7336 | 14.213 | 14.7705 | 11.0515 | -0.0002 | -0.0029 | 0.0007 | 0.0038 | 0.0003 | -0.0005 | 0.0067 | -0.0007 | -0.0348 | -360.1804 | 17.3864 | -360.4604 | 17.7354 | -360.802 | 18.1317 | -360.8789 | 17.5609 | -352.6875 | 18.6676 | -352.6629 | 16.8279
12:03 | 2612 | 31.1169 | 197.861 | 443.7693 | 449.3592 | -18.7678 | -45.9044 | 7.3276 | 4.1734 | -2.017 | -3.1281 | 0.1774 | -2.7786 | 6.975 | 0.4811 | 0.598 | 0.642 | 0.9566 | 0.718 | -131.0999 | -5.5295 | 2.6238 | 0.0815 | -5.7392 | -4.4709 | 2.1852 |  | 0.0871 | -1.7147 | 4.0161 | 3.3618 | 3.3543 | 1.0357 | 10.7174 | 14.2197 | 14.7756 | 11.0417 | -0.0002 | -0.0033 | 0.0009 | 0.004 | 0.0005 | -0.001 | 0.019 | -0.0067 | 0.0062 | -360.2019 | 17.4315 | -360.4942 | 17.7252 | -360.805 | 18.1235 | -360.9158 | 17.5691 | -352.6937 | 18.7066 | -352.6721 | 16.8032
12:03 | 2613 | 31.0558 | 197.9269 | 443.8199 | 449.3232 | -18.7231 | -45.9337 | 7.3218 | 4.0995 | -2.1221 | -3.1968 | 0.1396 | -2.7207 | 7.1108 | 0.6125 | 0.5984 | 0.6421 | 0.9588 | 0.7176 | -131.0465 | -5.6096 | 2.6823 | 0.198 | -5.7447 | -4.335 | 2.1504 |  | 0.0676 | -1.6642 | 4.0159 | 3.3631 | 3.3517 | 1.0374 | 10.7392 | 14.248 | 14.8074 | 11.0565 | 0.0001 | -0.0028 | 0.0009 | 0.004 | 0.0003 | -0.0005 | 0.0262 | 0.0114 | 0.0148 | -360.1034 | 17.4151 | -360.5035 | 17.7642 | -360.8204 | 18.1276 | -360.8574 | 17.5404 | -352.6537 | 18.7025 | -352.706 | 16.8566
12:03 | 2614 | 31.1365 | 197.8395 | 443.6948 | 449.3629 | -18.6897 | -45.9609 | 7.3698 | 4.0779 | -2.1877 | -3.2793 | 0.1109 | -2.6765 | 7.0586 | 0.6435 | 0.5989 | 0.6412 | 0.9541 | 0.7178 | -131.0468 | -5.4967 | 2.7531 | 0.2002 | -5.7883 | -4.4493 | 2.1689 |  | 0.0205 | -1.7286 | 4.0156 | 3.3642 | 3.352 | 1.036 | 10.7313 | 14.2163 | 14.7551 | 11.0208 | -0.0001 | -0.0028 | 0.0004 | 0.004 | 0.0012 | -0.0005 | 0.0281 | 0.0027 | 0.0022 | -360.1311 | 17.4007 | -360.4727 | 17.7375 | -360.8481 | 18.1379 | -360.9097 | 17.5506 | -352.6629 | 18.6758 | -352.6844 | 16.8197
12:03 | 2615 | 31.1176 | 197.7857 | 443.714 | 449.3921 | -18.6956 | -46.0145 | 7.3391 | 4.1922 | -2.1463 | -3.205 | 0.1798 | -2.7417 | 7.0073 | 0.5767 | 0.6004 | 0.6441 | 0.9561 | 0.718 | -131.1293 | -5.5376 | 2.6784 | 0.1585 | -5.7399 | -4.3441 | 2.1387 |  | 0.0994 | -1.7022 | 4.0153 | 3.3612 | 3.3518 | 1.0364 | 10.7231 | 14.2373 | 14.7835 | 11.0352 | -0.0002 | -0.0025 | 0.0008 | 0.0038 | 0.001 | -0.0002 | 0.0013 | -0.0118 | -0.0082 | -360.1865 | 17.4213 | -360.4973 | 17.758 | -360.8143 | 18.1153 | -360.9066 | 17.5568 | -352.6598 | 18.6984 | -352.709 | 16.8443
12:03 | 2616 | 31.1865 | 197.838 | 443.7995 | 449.3716 | -18.8792 | -46.1891 | 7.1401 | 4.2153 | -2.2004 | -3.076 | 0.1628 | -2.868 | 6.8913 | 0.527 | 0.5996 | 0.6376 | 0.9558 | 0.7156 | -131.1812 | -5.5907 | 2.683 | 0.1813 | -5.7466 | -4.3612 | 2.1084 |  | 0.0653 | -1.6821 | 4.0159 | 3.3636 | 3.3519 | 1.0353 | 10.7359 | 14.2383 | 14.8127 | 11.0713 | 0.0003 | -0.0028 | 0.0006 | 0.0038 | 0.0008 | -0.0003 | 0.0096 | 0.0006 | -0.0062 | -360.1219 | 17.4213 | -360.4696 | 17.7436 | -360.845 | 18.1235 | -360.8574 | 17.5445 | -352.6598 | 18.684 | -352.6567 | 16.8299
12:03 | 2617 | 31.1809 | 197.8295 | 443.7794 | 449.3456 | -18.7843 | -46.0529 | 7.249 | 4.1412 | -2.119 | -3.1592 | 0.1062 | -2.8762 | 6.9235 | 0.4841 | 0.5998 | 0.6416 | 0.9558 | 0.7167 | -131.165 | -5.6083 | 2.6831 | 0.1982 | -5.7404 | -4.3502 | 2.15 |  | 0.11 | -1.6145 | 4.016 | 3.3627 | 3.3546 | 1.0376 | 10.6793 | 14.2102 | 14.7588 | 11.0215 | -0.0001 | -0.0032 | 0.0005 | 0.0035 | 0.0012 | -0.0003 | 0.0117 | -0.0061 | -0.0034 | -360.1342 | 17.4172 | -360.5066 | 17.7436 | -360.8327 | 18.1502 | -360.8974 | 17.5629 | -352.6629 | 18.6984 | -352.709 | 16.8361
12:03 | 2618 | 31.2223 | 197.9036 | 443.7821 | 449.3225 | -18.8208 | -46.1445 | 7.2351 | 4.1407 | -2.1242 | -3.3241 | 0.0874 | -2.8161 | 6.9905 | 0.5717 | 0.6014 | 0.6408 | 0.9583 | 0.7175 | -131.1379 | -5.6428 | 2.6982 | 0.2262 | -5.7949 | -4.4799 | 2.0836 |  | 0.0701 | -1.7035 | 4.0164 | 3.3656 | 3.3571 | 1.0371 | 10.6631 | 14.1768 | 14.7728 | 11.0742 | 0.0002 | -0.0025 | 0.001 | 0.0043 | 0.0008 | -0.0005 | 0.0123 | -0.0119 | -0.0166 | -360.1558 | 17.4172 | -360.4912 | 17.7334 | -360.805 | 18.1091 | -360.8481 | 17.5404 | -352.6752 | 18.6963 | -352.669 | 16.8217
12:03 | 2619 | 31.2471 | 197.8812 | 443.8363 | 449.2791 | -18.7797 | -46.0994 | 7.1993 | 4.1933 | -2.0908 | -3.1504 | 0.1161 | -2.7728 | 7.0668 | 0.6329 | 0.5992 | 0.6415 | 0.9549 | 0.7192 | -131.2022 | -5.5998 | 2.6515 | 0.2467 | -5.6745 | -4.4427 | 2.1446 |  | 0.0962 | -1.6656 | 4.0151 | 3.3595 | 3.3522 | 1.0364 | 10.6864 | 14.1822 | 14.7349 | 11.0003 | -0.0006 | -0.0027 | 0.0006 | 0.0034 | 0.001 | -0.0008 | 0.0067 | -0.0074 | -0.0236 | -360.165 | 17.4377 | -360.5312 | 17.7559 | -360.8389 | 18.1296 | -360.8974 | 17.5465 | -352.6844 | 18.7148 | -352.749 | 16.8464
12:03 | 2620 | 31.2075 | 197.813 | 443.8258 | 449.2771 | -18.8689 | -46.1354 | 7.2042 | 4.2291 | -1.9871 | -3.2064 | 0.2717 | -2.843 | 7.0658 | 0.5522 | 0.5995 | 0.6418 | 0.9579 | 0.7173 | -131.1181 | -5.5755 | 2.6737 | 0.2134 | -5.7662 | -4.4006 | 2.2173 |  | 0.1459 | -1.5335 | 4.0154 | 3.3628 | 3.3514 | 1.0365 | 10.7174 | 14.2082 | 14.7998 | 11.0702 | 0.0001 | -0.0025 | 0.0011 | 0.0042 | 0.0005 | -0.0003 | 0.0097 | -0.0188 | -0.0168 | -360.125 | 17.3905 | -360.4389 | 17.7334 | -360.8358 | 18.1276 | -360.8635 | 17.5424 | -352.6106 | 18.6737 | -352.669 | 16.8217
12:03 | 2621 | 31.1503 | 197.84 | 443.7206 | 449.2622 | -18.7959 | -46.1033 | 7.1463 | 4.1406 | -2.0871 | -3.2125 | 0.1409 | -2.7905 | 7.12 | 0.6627 | 0.5995 | 0.6442 | 0.9594 | 0.7187 | -131.1134 | -5.5792 | 2.7076 | 0.2327 | -5.7438 | -4.4244 | 2.115 |  | 0.1925 | -1.6524 | 4.0147 | 3.3645 | 3.3501 | 1.0357 | 10.7324 | 14.2409 | 14.776 | 11.0731 | 0.0004 | -0.0029 | 0.0008 | 0.0037 | 0.001 | -0.001 | 0.0026 | 0.0074 | -0.0069 | -360.2142 | 17.4151 | -360.4481 | 17.7293 | -360.845 | 18.1358 | -360.9589 | 17.5855 | -352.709 | 18.6943 | -352.669 | 16.8176
12:03 | 2622 | 31.2256 | 197.8453 | 443.8475 | 449.3262 | -18.8606 | -46.0595 | 7.1741 | 4.1942 | -2.0076 | -3.2747 | 0.1033 | -2.7935 | 7.0513 | 0.6257 | 0.5989 | 0.6405 | 0.9564 | 0.7176 | -131.0652 | -5.5944 | 2.7389 | 0.2946 | -5.716 | -4.3661 | 2.18 |  | 0.2427 | -1.6188 | 4.0152 | 3.3637 | 3.3524 | 1.0364 | 10.7382 | 14.2232 | 14.8318 | 11.045 | 0 | -0.0029 | 0.0003 | 0.0036 | 0.0003 | -0.0006 | 0.0123 | -0.0086 | 0.0151 | -360.1619 | 17.4274 | -360.4819 | 17.7087 | -360.7773 | 18.1071 | -360.8604 | 17.5424 | -352.6752 | 18.7045 | -352.6875 | 16.8135
12:03 | 2623 | 31.3123 | 197.8823 | 443.8727 | 449.3668 | -18.8595 | -46.1036 | 7.1523 | 4.1998 | -2.039 | -3.2155 | 0.0658 | -2.8507 | 7.0282 | 0.642 | 0.5983 | 0.6415 | 0.9517 | 0.7167 | -131.0999 | -5.5705 | 2.7554 | 0.3077 | -5.6863 | -4.3677 | 2.24 |  | 0.2026 | -1.7072 | 4.0159 | 3.366 | 3.3516 | 1.0367 | 10.7267 | 14.2406 | 14.797 | 11.0565 | -0.0002 | -0.0025 | 0.0007 | 0.0038 | 0.0009 | -0.0007 | 0.0107 | -0.0131 | -0.0256 | -360.1281 | 17.4213 | -360.5312 | 17.7703 | -360.885 | 18.1481 | -360.8912 | 17.5445 | -352.666 | 18.6861 | -352.7306 | 16.8546
12:03 | 2624 | 31.3281 | 197.9397 | 443.9086 | 449.4877 | -18.8859 | -46.1881 | 7.0952 | 4.2919 | -2.0765 | -3.2393 | 0.0969 | -2.8355 | 6.9844 | 0.6444 | 0.5997 | 0.6441 | 0.9553 | 0.7184 | -131.0645 | -5.5636 | 2.6931 | 0.3145 | -5.633 | -4.3153 | 2.2825 |  | 0.1648 | -1.8283 | 4.0171 | 3.3654 | 3.3511 | 1.0377 | 10.7349 | 14.2137 | 14.7919 | 11.0017 | -0.0007 | -0.0028 | 0.0003 | 0.0034 | 0.0004 | -0.0004 | 0.0175 | -0.0012 | -0.0053 | -360.1465 | 17.3782 | -360.4204 | 17.719 | -360.8143 | 18.1379 | -360.9097 | 17.5568 | -352.6475 | 18.6635 | -352.629 | 16.8176
12:03 | 2625 | 31.3472 | 197.8897 | 443.8452 | 449.4234 | -18.8306 | -46.1427 | 7.2394 | 4.2055 | -2.0983 | -3.2923 | 0.1205 | -2.8515 | 6.9826 | 0.6445 | 0.5993 | 0.6379 | 0.9559 | 0.717 | -131.1569 | -5.5943 | 2.6263 | 0.3338 | -5.6243 | -4.2778 | 2.1766 |  | 0.2025 | -1.702 | 4.0155 | 3.3639 | 3.354 | 1.0362 | 10.7152 | 14.2173 | 14.7612 | 11.0627 | 0 | -0.0029 | 0.0004 | 0.0036 | 0.0006 | -0.0006 | 0.004 | -0.0138 | -0.0205 | -360.2358 | 17.4439 | -360.5035 | 17.7313 | -360.8112 | 18.1029 | -360.8789 | 17.5629 | -352.6875 | 18.7148 | -352.6967 | 16.8176
12:03 | 2626 | 31.2407 | 198.0082 | 443.8645 | 449.3892 | -18.7697 | -46.2668 | 7.1097 | 4.2285 | -1.9973 | -3.2063 | 0.1944 | -2.7821 | 7.1026 | 0.5902 | 0.5983 | 0.6442 | 0.9538 | 0.7171 | -131.1753 | -5.5634 | 2.617 | 0.3089 | -5.6904 | -4.2841 | 2.2123 |  | 0.1389 | -1.7454 | 4.0159 | 3.3616 | 3.3539 | 1.0364 | 10.7313 | 14.2163 | 14.8015 | 11.0612 | 0.0001 | -0.0032 | 0.001 | 0.0041 | 0.0009 | -0.0009 | -0.0003 | -0.02 | -0.0082 | -360.1342 | 17.4274 | -360.5281 | 17.7621 | -360.8758 | 18.1235 | -360.842 | 17.5198 | -352.6567 | 18.7004 | -352.746 | 16.8669
12:03 | 2627 | 31.2862 | 198.0522 | 443.9347 | 449.476 | -18.783 | -46.1644 | 7.1844 | 4.2416 | -2.0653 | -3.1432 | 0.1704 | -2.7486 | 6.986 | 0.6205 | 0.6001 | 0.6436 | 0.958 | 0.7183 | -131.2077 | -5.597 | 2.4851 | 0.341 | -5.7146 | -4.2964 | 2.2052 |  | 0.1889 | -1.7216 | 4.0163 | 3.3622 | 3.352 | 1.0381 | 10.7209 | 14.2174 | 14.7681 | 11.0334 | 0 | -0.0026 | 0.0006 | 0.0034 | 0.0002 | -0.0006 | 0.0011 | -0.0119 | -0.019 | -360.1404 | 17.4028 | -360.4666 | 17.7272 | -360.8512 | 18.1296 | -360.8974 | 17.5547 | -352.666 | 18.684 | -352.6937 | 16.8238
12:04 | 2628 | 31.2118 | 197.9256 | 443.8184 | 449.3497 | -18.7361 | -46.1656 | 7.1791 | 4.2991 | -2.0885 | -3.2038 | 0.2001 | -2.7639 | 7.0528 | 0.7242 | 0.6005 | 0.6429 | 0.9553 | 0.7195 | -131.1291 | -5.6285 | 2.6318 | 0.3117 | -5.6892 | -4.3749 | 2.2304 |  | 0.2116 | -1.6487 | 4.0151 | 3.3629 | 3.3528 | 1.0375 | 10.7209 | 14.2117 | 14.7623 | 11.045 | -0.0003 | -0.0028 | 0.0004 | 0.0037 | 0.0012 | -0.0008 | -0.0067 | 0.0054 | 0.0115 | -360.2604 | 17.4397 | -360.4881 | 17.7231 | -360.7773 | 18.105 | -360.8881 | 17.5794 | -352.7367 | 18.7148 | -352.7306 | 16.8258
12:04 | 2629 | 31.3237 | 197.9483 | 443.9769 | 449.3633 | -18.7639 | -46.1032 | 7.1715 | 4.1889 | -2.1396 | -3.1342 | 0.1766 | -2.8044 | 6.9907 | 0.5554 | 0.5997 | 0.6408 | 0.9585 | 0.7177 | -131.1964 | -5.5348 | 2.7359 | 0.2838 | -5.6474 | -4.2788 | 2.1565 |  | 0.2122 | -1.7043 | 4.0157 | 3.3665 | 3.3529 | 1.0375 | 10.729 | 14.185 | 14.7756 | 11.0129 | 0.0001 | -0.0029 | 0.0004 | 0.0036 | 0.0002 | -0.0005 | 0.0022 | -0.0192 | -0.0069 | -360.1465 | 17.4172 | -360.5096 | 17.7252 | -360.805 | 18.0988 | -360.8204 | 17.528 | -352.6537 | 18.6943 | -352.6998 | 16.8299
12:04 | 2630 | 31.275 | 197.9172 | 443.872 | 449.4357 | -18.7437 | -46.1595 | 7.0744 | 4.1498 | -2.1651 | -3.2007 | 0.1776 | -2.8324 | 7.052 | 0.5132 | 0.5985 | 0.6416 | 0.953 | 0.7179 | -131.2317 | -5.559 | 2.5609 | 0.3411 | -5.7294 | -4.2959 | 2.2219 |  | 0.2053 | -1.7196 | 4.0154 | 3.3679 | 3.3546 | 1.037 | 10.7462 | 14.2317 | 14.7903 | 11.0695 | 0.0004 | -0.0027 | 0.0003 | 0.0035 | 0.0013 | -0.0003 | 0.0172 | -0.0056 | 0.0185 | -360.165 | 17.4131 | -360.4881 | 17.7457 | -360.8912 | 18.1625 | -360.922 | 17.5506 | -352.709 | 18.682 | -352.6937 | 16.8464
12:04 | 2631 | 31.3445 | 198.1078 | 443.9978 | 449.5095 | -18.7615 | -46.065 | 7.1384 | 4.2027 | -2.1145 | -3.1772 | 0.1214 | -2.8449 | 7.0097 | 0.6245 | 0.5997 | 0.6404 | 0.9552 | 0.7174 | -131.2108 | -5.6123 | 2.5838 | 0.3002 | -5.7277 | -4.2624 | 2.1603 |  | 0.2374 | -1.7624 | 4.0166 | 3.3673 | 3.3514 | 1.0376 | 10.7071 | 14.2265 | 14.7759 | 11.0432 | -0.0008 | -0.0033 | 0.0008 | 0.0038 | 0.0004 | -0.0005 | -0.0085 | 0.0014 | -0.02 | -360.1681 | 17.3966 | -360.4266 | 17.7005 | -360.7589 | 18.1235 | -360.8974 | 17.5568 | -352.6998 | 18.6799 | -352.6537 | 16.8074
12:04 | 2632 | 31.2352 | 198.0221 | 443.8301 | 449.4354 | -18.766 | -46.0036 | 7.1378 | 4.2508 | -2.0731 | -3.2068 | 0.1717 | -2.9541 | 6.9842 | 0.593 | 0.5998 | 0.6428 | 0.9562 | 0.7199 | -131.2812 | -5.6044 | 2.6191 | 0.3712 | -5.7389 | -4.3527 | 2.2291 |  | 0.1448 | -1.8412 | 4.016 | 3.3648 | 3.3504 | 1.037 | 10.7578 | 14.2374 | 14.8366 | 11.0695 | -0.0002 | -0.0024 | 0.0011 | 0.0038 | 0.001 | -0.0006 | 0.0103 | 0.0087 | -0.0227 | -360.2173 | 17.4254 | -360.5035 | 17.7395 | -360.8481 | 18.1153 | -360.8543 | 17.5506 | -352.6752 | 18.7004 | -352.7121 | 16.8361
12:04 | 2633 | 31.219 | 198.0191 | 443.9298 | 449.4556 | -18.7015 | -46.0153 | 7.2382 | 4.1846 | -2.0071 | -3.1846 | 0.2759 | -2.9173 | 6.9486 | 0.4182 | 0.5991 | 0.643 | 0.9522 | 0.7174 | -131.3304 | -5.7028 | 2.5834 | 0.3265 | -5.772 | -4.2929 | 2.1588 |  | 0.1628 | -1.7155 | 4.0157 | 3.3656 | 3.3535 | 1.0363 | 10.736 | 14.2091 | 14.7759 | 11.0605 | -0.0004 | -0.0034 | 0.0004 | 0.0039 | 0.0008 | -0.0003 | 0.0084 | -0.001 | -0.0108 | -360.1527 | 17.4028 | -360.485 | 17.7375 | -360.8327 | 18.1337 | -360.9004 | 17.5506 | -352.669 | 18.7025 | -352.6844 | 16.8525
12:04 | 2634 | 31.213 | 197.9577 | 443.9017 | 449.4665 | -18.7686 | -45.9624 | 7.1767 | 4.1355 | -1.984 | -3.2655 | 0.2422 | -2.9059 | 6.9565 | 0.5017 | 0.5986 | 0.6418 | 0.9552 | 0.7184 | -131.2698 | -5.5442 | 2.7105 | 0.3655 | -5.6878 | -4.2017 | 2.2918 |  | 0.1618 | -1.7659 | 4.0144 | 3.3663 | 3.3551 | 1.0356 | 10.7071 | 14.1918 | 14.7585 | 11.0201 | 0 | -0.0032 | 0.0008 | 0.004 | 0.0004 | -0.0008 | 0.018 | -0.0041 | -0.0038 | -360.1958 | 17.4151 | -360.4789 | 17.7252 | -360.8081 | 18.1132 | -360.8727 | 17.5568 | -352.6567 | 18.6963 | -352.6875 | 16.8299
12:04 | 2635 | 31.2124 | 197.9714 | 443.7022 | 449.3723 | -18.7804 | -45.979 | 7.2423 | 4.1812 | -1.9753 | -3.1828 | 0.2582 | -2.8185 | 7.0019 | 0.6179 | 0.5993 | 0.6401 | 0.9534 | 0.7185 | -131.2963 | -5.5915 | 2.627 | 0.3043 | -5.7041 | -4.2666 | 2.235 |  | 0.1049 | -1.6215 | 4.0148 | 3.3657 | 3.3535 | 1.0373 | 10.73 | 14.2213 | 14.7859 | 11.0475 | 0.0001 | -0.0029 | 0.001 | 0.0038 | 0.0009 | -0.0007 | -0.0016 | 0.0029 | -0.0154 | -360.1711 | 17.4439 | -360.5004 | 17.7416 | -360.8481 | 18.1399 | -360.8789 | 17.5609 | -352.6844 | 18.7169 | -352.709 | 16.8423
12:04 | 2636 | 31.2494 | 197.9779 | 443.6054 | 449.385 | -18.7776 | -45.9186 | 7.1845 | 4.1465 | -2.0486 | -3.3626 | 0.1963 | -2.8117 | 7.0338 | 0.6314 | 0.599 | 0.6423 | 0.9534 | 0.7188 | -131.2996 | -5.5036 | 2.6516 | 0.299 | -5.6032 | -4.2029 | 2.1767 |  | 0.157 | -1.732 | 4.0154 | 3.3625 | 3.3534 | 1.037 | 10.7613 | 14.2582 | 14.8223 | 11.0847 | -0.0004 | -0.0026 | 0.0003 | 0.0035 | 0.0001 | -0.0008 | 0.0169 | -0.0096 | -0.0207 | -360.1127 | 17.3987 | -360.4389 | 17.7149 | -360.805 | 18.1194 | -360.8666 | 17.5363 | -352.6413 | 18.6779 | -352.6783 | 16.8279
12:04 | 2637 | 31.3228 | 198.0326 | 443.8513 | 449.3906 | -18.7087 | -45.7973 | 7.3295 | 4.0885 | -2.1327 | -3.3924 | 0.1652 | -2.7692 | 7.0805 | 0.7024 | 0.5989 | 0.6416 | 0.9547 | 0.72 | -131.2893 | -5.6329 | 2.6962 | 0.2987 | -5.6173 | -4.2148 | 2.2126 |  | 0.1817 | -1.7195 | 4.0154 | 3.3638 | 3.3556 | 1.0373 | 10.685 | 14.2047 | 14.7783 | 11.0266 | 0 | -0.0028 | 0.0009 | 0.0038 | 0.001 | -0.0006 | 0.0068 | -0.0106 | -0.0028 | -360.2358 | 17.4397 | -360.4942 | 17.7354 | -360.8327 | 18.1255 | -360.9127 | 17.5671 | -352.6998 | 18.7087 | -352.6998 | 16.8299
12:04 | 2638 | 31.2865 | 197.9837 | 443.8601 | 449.406 | -18.7635 | -45.8355 | 7.2681 | 4.1206 | -2.0999 | -3.287 | 0.21 | -2.8354 | 7.0854 | 0.6738 | 0.5997 | 0.6424 | 0.958 | 0.7195 | -131.2648 | -5.578 | 2.6603 | 0.3464 | -5.5836 | -4.2486 | 2.2675 |  | 0.1703 | -1.7397 | 4.0135 | 3.3688 | 3.353 | 1.0369 | 10.7164 | 14.2357 | 14.8136 | 11.0468 | 0.0001 | -0.0034 | 0.0003 | 0.0035 | 0.0006 | -0.0003 | -0.0014 | -0.0106 | -0.0204 | -360.1804 | 17.4172 | -360.4912 | 17.7375 | -360.7866 | 18.0865 | -360.8574 | 17.5568 | -352.706 | 18.7004 | -352.6998 | 16.832
12:04 | 2639 | 31.2006 | 197.9832 | 443.8519 | 449.4323 | -18.6832 | -45.8368 | 7.3444 | 4.1601 | -2.074 | -3.1177 | 0.1974 | -2.7951 | 7.0886 | 0.6786 | 0.5998 | 0.6419 | 0.957 | 0.7189 | -131.2446 | -5.5615 | 2.6282 | 0.2671 | -5.5991 | -4.2109 | 2.2211 |  | 0.2033 | -1.7347 | 4.0141 | 3.3646 | 3.3517 | 1.0352 | 10.7209 | 14.2521 | 14.7623 | 11.045 | 0.0004 | -0.0026 | 0.001 | 0.0039 | 0.0008 | -0.0008 | 0.0109 | -0.0095 | -0.0318 | -360.1804 | 17.4254 | -360.5127 | 17.7354 | -360.8574 | 18.1214 | -360.8574 | 17.5506 | -352.666 | 18.6984 | -352.706 | 16.8381
12:04 | 2640 | 31.2339 | 197.9736 | 443.8736 | 449.3642 | -18.7338 | -45.9441 | 7.2899 | 4.285 | -1.9988 | -3.101 | 0.1828 | -2.8976 | 7.0831 | 0.7421 | 0.5994 | 0.6395 | 0.9563 | 0.7189 | -131.2329 | -5.5323 | 2.6312 | 0.3059 | -5.6464 | -4.1687 | 2.2451 |  | 0.1107 | -1.8432 | 4.0143 | 3.3661 | 3.3485 | 1.0355 | 10.7348 | 14.237 | 14.8103 | 11.0302 | -0.0003 | -0.0025 | 0.0012 | 0.0043 | 0.0005 | -0.0001 | 0.0077 | -0.0163 | -0.0129 | -360.1865 | 17.3987 | -360.4358 | 17.721 | -360.8358 | 18.1399 | -360.922 | 17.5609 | -352.6906 | 18.6922 | -352.6813 | 16.8197
12:04 | 2641 | 31.2921 | 198.012 | 443.831 | 449.4599 | -18.7694 | -46.048 | 7.2856 | 4.2507 | -1.9668 | -3.048 | 0.2119 | -2.8119 | 7.0609 | 0.6601 | 0.5999 | 0.6412 | 0.9538 | 0.719 | -131.234 | -5.4945 | 2.6019 | 0.2651 | -5.5523 | -4.1708 | 2.2548 |  | 0.0785 | -1.7741 | 4.0146 | 3.3631 | 3.3495 | 1.0377 | 10.699 | 14.2183 | 14.75 | 11.0006 | -0.0003 | -0.0023 | 0.0007 | 0.004 | 0.001 | -0.0008 | 0.023 | -0.0029 | -0.0202 | -360.1865 | 17.4069 | -360.4481 | 17.6964 | -360.7527 | 18.1153 | -360.8881 | 17.5568 | -352.6598 | 18.6963 | -352.666 | 16.793
12:04 | 2642 | 31.3516 | 198.0391 | 443.875 | 449.5166 | -18.7496 | -45.9315 | 7.2385 | 4.2758 | -2.0427 | -3.0904 | 0.1534 | -2.7228 | 7.1531 | 0.7473 | 0.5989 | 0.6405 | 0.9546 | 0.7202 | -131.2079 | -5.5052 | 2.5204 | 0.2231 | -5.6272 | -4.1957 | 2.2932 |  | 0.135 | -1.801 | 4.0151 | 3.3624 | 3.3529 | 1.0364 | 10.7382 | 14.229 | 14.7855 | 11.045 | 0.0002 | -0.0031 | 0.0011 | 0.0043 | 0.0002 | -0.0004 | 0.0063 | -0.0154 | -0.0227 | -360.1773 | 17.4213 | -360.5373 | 17.7539 | -360.8758 | 18.1296 | -360.882 | 17.5383 | -352.6598 | 18.7087 | -352.7675 | 16.8607
12:04 | 2643 | 31.3405 | 198.0498 | 443.9536 | 449.4204 | -18.8152 | -45.9963 | 7.2482 | 4.254 | -1.9896 | -3.063 | 0.14 | -2.8407 | 7.1137 | 0.7099 | 0.6009 | 0.6408 | 0.9556 | 0.7168 | -131.2428 | -5.6357 | 2.6482 | 0.2657 | -5.5804 | -4.1813 | 2.2563 |  | 0.1173 | -1.7678 | 4.0147 | 3.3645 | 3.3558 | 1.0362 | 10.7186 | 14.2324 | 14.7943 | 11.037 | 0.0003 | -0.0029 | 0.0008 | 0.0038 | 0.0006 | -0.0007 | 0.0169 | -0.0089 | 0.002 | -360.1558 | 17.3679 | -360.4389 | 17.7272 | -360.842 | 18.144 | -360.9004 | 17.5321 | -352.6506 | 18.6532 | -352.6383 | 16.8238
12:04 | 2644 | 31.282 | 198.0122 | 443.9561 | 449.4299 | -18.7468 | -46.0502 | 7.3385 | 4.2797 | -2.0083 | -3.0637 | 0.1821 | -2.7955 | 7.0673 | 0.6923 | 0.5994 | 0.6371 | 0.953 | 0.7188 | -131.2597 | -5.5573 | 2.6739 | 0.3349 | -5.5236 | -4.1445 | 2.2949 |  | 0.1958 | -1.8221 | 4.0149 | 3.3661 | 3.3539 | 1.0367 | 10.692 | 14.1884 | 14.7497 | 11.0222 | -0.0001 | -0.0023 | 0.0002 | 0.0034 | 0.0009 | -0.0006 | 0.0026 | -0.0183 | -0.0283 | -360.2481 | 17.4418 | -360.5004 | 17.7108 | -360.8143 | 18.1235 | -360.8974 | 17.5855 | -352.7121 | 18.7107 | -352.7029 | 16.8258
12:04 | 2645 | 31.3066 | 198.0431 | 443.9553 | 449.4592 | -18.7661 | -45.9331 | 7.3165 | 4.2551 | -1.9609 | -3.1962 | 0.1799 | -2.832 | 7.0995 | 0.6943 | 0.5999 | 0.6385 | 0.9546 | 0.7207 | -131.2877 | -5.5118 | 2.6584 | 0.3003 | -5.5463 | -4.2512 | 2.2196 |  | 0.1237 | -1.8079 | 4.0158 | 3.3657 | 3.3523 | 1.0367 | 10.7476 | 14.2438 | 14.7932 | 11.0663 | -0.0005 | -0.0027 | 0.0005 | 0.0037 | 0.0004 | -0.0004 | -0.0012 | 0.0024 | -0.0191 | -360.1619 | 17.4295 | -360.5189 | 17.7313 | -360.7927 | 18.0988 | -360.8204 | 17.5198 | -352.6475 | 18.7087 | -352.6998 | 16.8464
12:04 | 2646 | 31.4559 | 198.0753 | 444.0246 | 449.5072 | -18.733 | -45.9426 | 7.2476 | 4.2836 | -1.9559 | -3.08 | 0.2138 | -2.7935 | 7.0492 | 0.5904 | 0.5989 | 0.6385 | 0.9551 | 0.7199 | -131.2573 | -5.5414 | 2.6592 | 0.2447 | -5.5691 | -4.2266 | 2.172 |  | 0.0777 | -1.8262 | 4.0155 | 3.368 | 3.3539 | 1.0366 | 10.7059 | 14.2428 | 14.7987 | 11.0533 | -0.0001 | -0.003 | 0.0002 | 0.0035 | 0.0004 | -0.0012 | 0.0057 | -0.0199 | -0.01 | -360.1619 | 17.4028 | -360.5096 | 17.7395 | -360.8789 | 18.1379 | -360.9097 | 17.5445 | -352.6537 | 18.684 | -352.7183 | 16.8381
12:04 | 2647 | 31.4682 | 197.9808 | 443.9385 | 449.4706 | -18.7274 | -45.9913 | 7.2763 | 4.2643 | -1.9842 | -3.0464 | 0.1947 | -2.8434 | 7.0628 | 0.7068 | 0.6007 | 0.6413 | 0.956 | 0.72 | -131.2266 | -5.5609 | 2.675 | 0.2849 | -5.5163 | -4.2405 | 2.216 |  | 0.0996 | -1.7483 | 4.0149 | 3.3672 | 3.3525 | 1.0382 | 10.7406 | 14.2195 | 14.7513 | 11.0363 | 0.0001 | -0.0031 | 0.0005 | 0.004 | 0.0005 | -0.0001 | 0.0066 | -0.0119 | -0.0123 | -360.2388 | 17.4213 | -360.4481 | 17.6944 | -360.7958 | 18.1091 | -360.922 | 17.5855 | -352.7367 | 18.6922 | -352.6844 | 16.8135
12:04 | 2648 | 31.4192 | 198.0631 | 443.8894 | 449.452 | -18.7476 | -45.9221 | 7.2242 | 4.2635 | -1.9745 | -3.0897 | 0.1964 | -2.7271 | 7.0553 | 0.8252 | 0.5995 | 0.6417 | 0.955 | 0.7211 | -131.1188 | -5.4828 | 2.6806 | 0.2506 | -5.4725 | -4.2072 | 2.2441 |  | 0.1329 | -1.7603 | 4.0156 | 3.3669 | 3.3533 | 1.0368 | 10.7462 | 14.2374 | 14.7961 | 11.0579 | -0.0004 | -0.003 | 0.0009 | 0.0043 | 0.0012 | -0.0004 | -0.0013 | -0.0038 | -0.0221 | -360.2173 | 17.45 | -360.5096 | 17.7169 | -360.7958 | 18.0804 | -360.842 | 17.5506 | -352.7152 | 18.7271 | -352.7213 | 16.8176
12:04 | 2649 | 31.4551 | 198.113 | 443.9791 | 449.5238 | -18.7732 | -45.8651 | 7.2108 | 4.3008 | -1.979 | -3.0335 | 0.1929 | -2.7808 | 7.0817 | 0.7894 | 0.5996 | 0.6366 | 0.956 | 0.72 | -131.1946 | -5.5402 | 2.5481 | 0.301 | -5.5772 | -4.1942 | 2.1764 |  | 0.125 | -1.7432 | 4.0155 | 3.3644 | 3.3536 | 1.0372 | 10.7082 | 14.2394 | 14.7551 | 11.0381 | -0.0003 | -0.0027 | 0.0005 | 0.0035 | 0.0003 | -0.0004 | -0.0024 | -0.0111 | -0.0146 | -360.1342 | 17.4172 | -360.5066 | 17.7518 | -360.8697 | 18.1214 | -360.8789 | 17.5445 | -352.7029 | 18.6984 | -352.7121 | 16.8607
12:04 | 2650 | 31.4476 | 197.9843 | 443.9585 | 449.3922 | -18.6869 | -45.9386 | 7.3011 | 4.2946 | -1.975 | -2.9338 | 0.2445 | -2.8302 | 6.9814 | 0.7248 | 0.6003 | 0.6385 | 0.9561 | 0.7202 | -131.1905 | -5.5275 | 2.5994 | 0.3096 | -5.5489 | -4.1333 | 2.2074 |  | 0.0815 | -1.7871 | 4.0143 | 3.3643 | 3.3529 | 1.0372 | 10.7394 | 14.23 | 14.7916 | 11.0407 | -0.0004 | -0.0029 | 0.0006 | 0.0039 | 0.001 | -0.0005 | 0.0161 | -0.0046 | -0.0097 | -360.165 | 17.3823 | -360.4112 | 17.6944 | -360.8081 | 18.1194 | -360.9281 | 17.5588 | -352.6537 | 18.6655 | -352.629 | 16.8032
12:04 | 2651 | 31.447 | 197.9871 | 443.964 | 449.5068 | -18.7886 | -45.8572 | 7.2068 | 4.2868 | -1.9495 | -2.983 | 0.208 | -2.7912 | 7.0899 | 0.7971 | 0.6 | 0.6405 | 0.9576 | 0.7212 | -131.1023 | -5.5648 | 2.5149 | 0.4094 | -5.5631 | -4.1959 | 2.1625 |  | 0.1834 | -1.792 | 4.0152 | 3.3662 | 3.3497 | 1.0361 | 10.7509 | 14.2419 | 14.8284 | 11.0515 | 0.0002 | -0.0029 | 0.0006 | 0.0037 | 0.0003 | -0.0004 | 0.0087 | 0.0067 | 0.0055 | -360.245 | 17.4459 | -360.5066 | 17.7169 | -360.8143 | 18.0968 | -360.9066 | 17.5691 | -352.6998 | 18.7066 | -352.7152 | 16.8156
12:04 | 2652 | 31.4565 | 198.0588 | 444.047 | 449.5263 | -18.7911 | -45.8943 | 7.2375 | 4.3411 | -1.973 | -2.8443 | 0.2669 | -2.7349 | 7.1739 | 0.7895 | 0.5999 | 0.639 | 0.9515 | 0.7201 | -131.1464 | -5.5527 | 2.6619 | 0.619 | -5.5951 | -4.202 | 2.1763 |  | 0.0957 | -1.7902 | 4.0137 | 3.3646 | 3.3496 | 1.0377 | 10.721 | 14.2229 | 14.8065 | 11.0457 | -0.0002 | -0.0036 | 0.0003 | 0.0029 | 0.0006 | -0.0008 | 0.0015 | 0.0089 | -0.0051 | -360.1158 | 17.3946 | -360.5096 | 17.7416 | -360.8266 | 18.0824 | -360.8235 | 17.5137 | -352.6321 | 18.6881 | -352.706 | 16.8525
12:04 | 2653 | 31.4589 | 198.1118 | 444.024 | 449.5061 | -18.7959 | -45.894 | 7.2518 | 4.2526 | -1.9468 | -3.0988 | 0.1725 | -2.7383 | 7.1799 | 0.793 | 0.5998 | 0.6442 | 0.9556 | 0.7222 | -131.0183 | -5.6111 | 2.684 | 0.5512 | -5.697 | -4.221 | 2.2731 |  | 0.2034 | -1.6177 | 4.0143 | 3.3623 | 3.3482 | 1.0375 | 10.7232 | 14.2198 | 14.794 | 11.0356 | -0.0003 | -0.0028 | 0.0007 | 0.0037 | 0.0011 | -0.0001 | 0.0179 | -0.0134 | -0.0137 | -360.1896 | 17.4131 | -360.4819 | 17.7518 | -360.8943 | 18.1276 | -360.9127 | 17.5527 | -352.6844 | 18.6943 | -352.7152 | 16.8464
12:04 | 2654 | 31.4477 | 198.1081 | 443.9259 | 449.5228 | -18.671 | -45.8697 | 7.2741 | 4.2731 | -1.9291 | -3.0162 | 0.169 | -2.718 | 7.1134 | 0.7084 | 0.5988 | 0.6409 | 0.9531 | 0.7202 | -131.155 | -5.582 | 2.6085 | 0.5359 | -5.7134 | -4.2324 | 2.3057 |  | 0.1352 | -1.7273 | 4.0146 | 3.3667 | 3.3533 | 1.0379 | 10.7141 | 14.1811 | 14.7693 | 11.0277 | -0.0003 | -0.0032 | 0.0006 | 0.0036 | 0.0004 | -0.0007 | 0.0137 | -0.0003 | -0.0196 | -360.1896 | 17.4192 | -360.4604 | 17.6923 | -360.7712 | 18.0865 | -360.8943 | 17.565 | -352.6567 | 18.7004 | -352.6813 | 16.8032
12:04 | 2655 | 31.4454 | 198.1066 | 443.9553 | 449.5162 | -18.7642 | -45.8415 | 7.3021 | 4.2308 | -1.9955 | -2.9713 | 0.1843 | -2.812 | 7.1622 | 0.6602 | 0.5997 | 0.6429 | 0.9559 | 0.7223 | -131.1963 | -5.6189 | 2.5267 | 0.4874 | -5.7315 | -4.2476 | 2.2422 |  | 0.1493 | -1.7211 | 4.0153 | 3.3642 | 3.3517 | 1.037 | 10.7094 | 14.1999 | 14.7555 | 11.0569 | 0.0002 | -0.0032 | 0.0008 | 0.0038 | 0.0009 | -0.0009 | 0.0046 | -0.0203 | 0.015 | -360.1958 | 17.4459 | -360.5373 | 17.7498 | -360.8543 | 18.0721 | -360.8666 | 17.5588 | -352.6844 | 18.723 | -352.7183 | 16.8423
12:04 | 2656 | 31.4666 | 198.0367 | 443.9218 | 449.4867 | -18.7891 | -45.8222 | 7.2871 | 4.3142 | -1.9922 | -3.1432 | 0.212 | -2.8142 | 7.1355 | 0.7214 | 0.5995 | 0.6418 | 0.9542 | 0.7205 | -131.2303 | -5.6157 | 2.5678 | 0.5 | -5.6835 | -4.2173 | 2.2202 |  | 0.1371 | -1.7138 | 4.0149 | 3.3678 | 3.3516 | 1.0389 | 10.7173 | 14.2143 | 14.7845 | 11.0406 | 0.0002 | -0.0028 | 0.0012 | 0.0044 | 0.0005 | -0.0005 | 0.021 | -0.0036 | 0.0134 | -360.1465 | 17.3925 | -360.4666 | 17.7272 | -360.8235 | 18.1132 | -360.8604 | 17.5424 | -352.6598 | 18.6779 | -352.6752 | 16.8238
12:04 | 2657 | 31.4682 | 198.1157 | 443.942 | 449.4848 | -18.8715 | -45.9072 | 7.2521 | 4.2848 | -1.9363 | -3.0443 | 0.1735 | -2.8191 | 7.211 | 0.7548 | 0.5987 | 0.6421 | 0.9582 | 0.7197 | -131.3002 | -5.7445 | 2.5452 | 0.4722 | -5.6894 | -4.3536 | 2.1967 |  | 0.1533 | -1.7602 | 4.014 | 3.3649 | 3.3527 | 1.039 | 10.7545 | 14.2278 | 14.842 | 11.0728 | -0.0001 | -0.0028 | 0.0005 | 0.004 | 0.0008 | -0.0008 | 0.0013 | -0.0177 | -0.0238 | -360.2081 | 17.409 | -360.4666 | 17.721 | -360.8389 | 18.0988 | -360.8912 | 17.5896 | -352.6906 | 18.6881 | -352.6629 | 16.8156
12:04 | 2658 | 31.5143 | 198.0861 | 443.9952 | 449.5373 | -18.8657 | -45.9167 | 7.2637 | 4.2627 | -1.945 | -3.061 | 0.2089 | -2.7372 | 7.1284 | 0.8102 | 0.5995 | 0.6422 | 0.9581 | 0.7201 | -131.1913 | -5.5741 | 2.5459 | 0.3019 | -5.6579 | -4.1824 | 2.1566 |  | 0.193 | -1.8287 | 4.0156 | 3.3681 | 3.3512 | 1.0374 | 10.7161 | 14.2363 | 14.7484 | 11.0395 | -0.0004 | -0.0024 | 0.0008 | 0.0039 | 0.0007 | 0 | -0.0045 | -0.013 | -0.0119 | -360.2111 | 17.4274 | -360.5035 | 17.7272 | -360.805 | 18.0968 | -360.8881 | 17.5629 | -352.6813 | 18.7148 | -352.709 | 16.8299
12:04 | 2659 | 31.5253 | 198.1164 | 443.9566 | 449.6215 | -18.8447 | -45.8837 | 7.3255 | 4.2686 | -1.9431 | -2.9394 | 0.1685 | -2.7534 | 7.1784 | 0.7505 | 0.5984 | 0.6372 | 0.9577 | 0.7193 | -131.207 | -5.5396 | 2.5945 | 0.3275 | -5.6638 | -4.1253 | 2.2274 |  | 0.0816 | -1.8233 | 4.016 | 3.3632 | 3.3519 | 1.0373 | 10.752 | 14.2374 | 14.8308 | 11.0695 | 0 | -0.003 | 0.001 | 0.0038 | 0.0006 | -0.0008 | 0.0079 | -0.0026 | -0.0227 | -360.1404 | 17.411 | -360.4912 | 17.7354 | -360.8481 | 18.0988 | -360.882 | 17.5547 | -352.6413 | 18.6696 | -352.6998 | 16.8279
12:04 | 2660 | 31.5199 | 198.1293 | 443.9686 | 449.5251 | -18.7527 | -45.761 | 7.3849 | 4.2737 | -1.9744 | -3.0885 | 0.1385 | -2.7462 | 7.1831 | 0.7201 | 0.5992 | 0.6363 | 0.9551 | 0.7215 | -131.192 | -5.4613 | 2.6514 | 0.3113 | -5.6324 | -4.1948 | 2.2426 |  | 0.1242 | -1.7424 | 4.0144 | 3.3646 | 3.3541 | 1.038 | 10.7395 | 14.2415 | 14.8021 | 11.041 | 0.0001 | -0.0033 | 0 | 0.003 | 0.0001 | -0.0006 | -0.0045 | -0.0054 | -0.0292 | -360.1958 | 17.4172 | -360.4819 | 17.7375 | -360.8297 | 18.105 | -360.8912 | 17.5691 | -352.669 | 18.6902 | -352.6937 | 16.832
12:04 | 2661 | 31.5229 | 198.0306 | 443.8604 | 449.5116 | -18.76 | -45.7709 | 7.3251 | 4.3449 | -1.9892 | -2.9931 | 0.2007 | -2.7462 | 7.22 | 0.7855 | 0.5978 | 0.6395 | 0.9522 | 0.7202 | -131.2123 | -5.4839 | 2.727 | 0.31 | -5.7056 | -4.1858 | 2.2586 |  | 0.2115 | -1.6687 | 4.0156 | 3.3675 | 3.3506 | 1.0373 | 10.7163 | 14.2069 | 14.751 | 11.0407 | -0.0003 | -0.0027 | 0.0004 | 0.0037 | 0.0012 | -0.0006 | -0.0061 | -0.0106 | -0.0294 | -360.1681 | 17.4048 | -360.4942 | 17.721 | -360.802 | 18.0927 | -360.8789 | 17.5547 | -352.629 | 18.682 | -352.6752 | 16.8135
12:04 | 2662 | 31.4954 | 197.9993 | 443.955 | 449.6229 | -18.7502 | -45.8637 | 7.3418 | 4.2457 | -1.9248 | -3.0238 | 0.2073 | -2.8036 | 7.136 | 0.7774 | 0.5986 | 0.6403 | 0.9546 | 0.7207 | -131.2135 | -5.4154 | 2.7366 | 0.2944 | -5.7134 | -4.3241 | 2.182 |  | 0.2228 | -1.6921 | 4.0162 | 3.3667 | 3.3532 | 1.0381 | 10.7002 | 14.225 | 14.7666 | 11.0429 | -0.0005 | -0.0027 | 0.0005 | 0.0035 | 0.0003 | -0.0006 | -0.0102 | -0.0003 | -0.0151 | -360.1896 | 17.4254 | -360.4881 | 17.7559 | -360.8666 | 18.1153 | -360.885 | 17.5671 | -352.6875 | 18.7066 | -352.709 | 16.8443
12:04 | 2663 | 31.5164 | 198.0088 | 444.0122 | 449.6272 | -18.6979 | -45.891 | 7.2385 | 4.2623 | -1.9429 | -3.1802 | 0.1896 | -2.7756 | 7.1001 | 0.807 | 0.5996 | 0.64 | 0.9532 | 0.7212 | -131.3308 | -5.4294 | 2.6506 | 0.4773 | -5.602 | -4.1535 | 2.2482 |  | 0.2388 | -1.6523 | 4.015 | 3.3646 | 3.352 | 1.0379 | 10.7058 | 14.1851 | 14.7882 | 11.0471 | 0.0003 | -0.0029 | 0.0007 | 0.004 | 0.001 | -0.0004 | 0.0011 | -0.0061 | -0.0168 | -360.1311 | 17.4069 | -360.4604 | 17.7108 | -360.7866 | 18.0886 | -360.8727 | 17.565 | -352.6475 | 18.6779 | -352.6937 | 16.8074
12:04 | 2664 | 31.55 | 198.0968 | 443.9737 | 449.4998 | -18.7364 | -45.904 | 7.3441 | 4.2876 | -1.9756 | -3.0788 | 0.1778 | -2.6997 | 7.1859 | 0.8144 | 0.5988 | 0.6427 | 0.9555 | 0.7207 | -131.2288 | -5.4522 | 2.6746 | 0.273 | -5.5866 | -4.1992 | 2.2813 |  | 0.1972 | -1.7098 | 4.0148 | 3.3675 | 3.3506 | 1.0374 | 10.7314 | 14.1988 | 14.7425 | 11.0096 | 0.0002 | -0.0032 | 0.0009 | 0.0044 | 0.0007 | -0.0003 | 0.0019 | -0.0198 | -0.0162 | -360.1927 | 17.4356 | -360.5066 | 17.7354 | -360.845 | 18.0845 | -360.8943 | 17.5753 | -352.6752 | 18.6984 | -352.7398 | 16.8361
12:04 | 2665 | 31.511 | 198.1473 | 444.0899 | 449.5752 | -18.6945 | -45.8659 | 7.3014 | 4.322 | -1.9518 | -3.008 | 0.1516 | -2.7413 | 7.1614 | 0.7513 | 0.5977 | 0.641 | 0.9532 | 0.7207 | -131.1975 | -5.4915 | 2.7453 | 0.2097 | -5.6309 | -4.1262 | 2.1549 |  | 0.1879 | -1.7338 | 4.0162 | 3.3635 | 3.3501 | 1.0373 | 10.7475 | 14.2499 | 14.7896 | 11.0482 | -0.0001 | -0.0024 | 0.0002 | 0.0035 | 0.0005 | 0 | -0.001 | -0.0189 | -0.009 | -360.1342 | 17.4151 | -360.4573 | 17.721 | -360.842 | 18.0886 | -360.8697 | 17.5588 | -352.6537 | 18.6902 | -352.6967 | 16.8279
12:04 | 2666 | 31.4875 | 198.1399 | 443.9097 | 449.5734 | -18.772 | -45.9858 | 7.2734 | 4.3179 | -1.9967 | -3.0173 | 0.1443 | -2.7329 | 7.1433 | 0.6976 | 0.5987 | 0.6417 | 0.9516 | 0.72 | -131.2139 | -5.4889 | 2.7371 | 0.3288 | -5.5175 | -4.16 | 2.1841 |  | 0.2141 | -1.7253 | 4.0153 | 3.3632 | 3.3489 | 1.0394 | 10.7324 | 14.206 | 14.7981 | 11.033 | -0.0003 | -0.0026 | 0.0011 | 0.0039 | 0.0008 | -0.0008 | 0.0184 | -0.0079 | -0.0214 | -360.1927 | 17.4069 | -360.4573 | 17.721 | -360.8266 | 18.1009 | -360.8912 | 17.5671 | -352.669 | 18.6717 | -352.6506 | 16.8258
12:04 | 2667 | 31.483 | 198.1315 | 444.0305 | 449.5052 | -18.7442 | -45.9651 | 7.3492 | 4.2707 | -1.9726 | -3.2162 | 0.0671 | -2.7785 | 7.1977 | 0.759 | 0.5989 | 0.6395 | 0.9514 | 0.7206 | -131.2047 | -5.3835 | 2.7949 | 0.3622 | -5.5347 | -4.2031 | 2.2198 |  | 0.2983 | -1.6259 | 4.0156 | 3.3639 | 3.3517 | 1.038 | 10.7428 | 14.2627 | 14.7794 | 11.0782 | -0.0003 | -0.0028 | 0.0012 | 0.0043 | 0.0005 | -0.0001 | 0.0165 | -0.015 | -0.0089 | -360.2019 | 17.4295 | -360.4789 | 17.7108 | -360.8112 | 18.1194 | -360.9466 | 17.5937 | -352.7244 | 18.6963 | -352.6813 | 16.8197
12:04 | 2668 | 31.5363 | 198.0832 | 444.0187 | 449.559 | -18.615 | -45.748 | 7.4236 | 4.3229 | -1.883 | -3.091 | 0.1895 | -2.7843 | 7.1845 | 0.7336 | 0.5993 | 0.6386 | 0.9541 | 0.7212 | -131.2058 | -5.4492 | 2.7666 | 0.3356 | -5.5996 | -4.2682 | 2.1644 |  | 0.2721 | -1.7242 | 4.0154 | 3.3663 | 3.3476 | 1.0375 | 10.7463 | 14.2082 | 14.794 | 11.0529 | 0 | -0.0034 | 0.0008 | 0.0036 | 0.001 | -0.0008 | 0.0114 | -0.0004 | 0.0106 | -360.1773 | 17.4172 | -360.4666 | 17.7149 | -360.7927 | 18.0721 | -360.8389 | 17.5547 | -352.6598 | 18.682 | -352.666 | 16.8258
12:04 | 2669 | 31.55 | 198.068 | 443.9279 | 449.4994 | -18.584 | -45.7577 | 7.4483 | 4.3132 | -1.8905 | -3.0376 | 0.2174 | -2.7168 | 7.1164 | 0.7437 | 0.5991 | 0.6412 | 0.9529 | 0.7199 | -131.1624 | -5.4594 | 2.7934 | 0.0426 | -5.6674 | -4.4674 | 2.1034 |  | 0.2628 | -1.7547 | 4.016 | 3.3682 | 3.3482 | 1.0373 | 10.7395 | 14.2183 | 14.7847 | 11.041 | -0.0002 | -0.0034 | 0.001 | 0.0038 | 0.0001 | -0.0004 | 0.0238 | -0.0139 | -0.0023 | -360.1465 | 17.4192 | -360.5004 | 17.7457 | -360.8666 | 18.1173 | -360.9158 | 17.5547 | -352.6537 | 18.6861 | -352.7213 | 16.8505
12:04 | 2670 | 31.4873 | 198.1312 | 444.082 | 449.581 | -18.627 | -45.817 | 7.525 | 4.3018 | -1.8891 | -3.0637 | 0.1215 | -2.7246 | 7.1423 | 0.6667 | 0.5997 | 0.6416 | 0.9546 | 0.7206 | -131.1784 | -5.419 | 2.8412 | 0.1288 | -5.6031 | -4.2532 | 2.1728 |  | 0.1751 | -1.8504 | 4.0146 | 3.3694 | 3.3488 | 1.0392 | 10.744 | 14.2407 | 14.7923 | 11.0677 | -0.0002 | -0.0027 | 0.0008 | 0.004 | 0.0011 | -0.0007 | 0.0093 | -0.0053 | -0.0199 | -360.1496 | 17.3884 | -360.4389 | 17.7108 | -360.802 | 18.105 | -360.9158 | 17.5671 | -352.6567 | 18.6553 | -352.6598 | 16.8279
12:04 | 2671 | 31.6395 | 198.1449 | 444.0625 | 449.6035 | -18.6532 | -45.7669 | 7.4905 | 4.2779 | -1.8248 | -3.1858 | 0.2311 | -2.7426 | 7.0947 | 0.7412 | 0.5975 | 0.6403 | 0.9524 | 0.7211 | -131.2367 | -5.5307 | 2.6857 | 0.169 | -5.6088 | -4.2441 | 2.1668 |  | 0.2169 | -1.8015 | 4.0153 | 3.3703 | 3.3504 | 1.0385 | 10.6886 | 14.2369 | 14.7745 | 11.0537 | -0.0003 | -0.0031 | 0.0004 | 0.0036 | 0.0003 | -0.0005 | -0.0085 | -0.0059 | -0.0319 | -360.2327 | 17.4459 | -360.525 | 17.7293 | -360.8081 | 18.0927 | -360.8881 | 17.5671 | -352.706 | 18.7169 | -352.7244 | 16.832
12:04 | 2672 | 31.6111 | 198.1555 | 444.09 | 449.6281 | -18.6715 | -45.7066 | 7.5018 | 4.3056 | -1.8578 | -3.157 | 0.1806 | -2.6637 | 7.1427 | 0.6807 | 0.5998 | 0.6392 | 0.9562 | 0.7214 | -131.1675 | -5.4899 | 2.6915 | 0.2992 | -5.5423 | -4.1606 | 2.1644 |  | 0.1864 | -1.7925 | 4.0156 | 3.3681 | 3.3476 | 1.0393 | 10.7348 | 14.2314 | 14.8171 | 11.0702 | 0.0001 | -0.0032 | 0.0003 | 0.0039 | 0.0008 | -0.0007 | 0.0012 | -0.0132 | -0.0025 | -360.0973 | 17.4172 | -360.5035 | 17.7436 | -360.8697 | 18.1029 | -360.8481 | 17.5424 | -352.6321 | 18.6881 | -352.7367 | 16.8607
12:04 | 2673 | 31.6515 | 198.1906 | 444.1184 | 449.6552 | -18.6752 | -45.7918 | 7.4793 | 4.3069 | -1.7992 | -3.0951 | 0.253 | -2.6658 | 7.1691 | 0.7574 | 0.5996 | 0.6429 | 0.9566 | 0.7211 | -131.2128 | -5.5652 | 2.6505 | 0.2995 | -5.6098 | -4.1804 | 2.1457 |  | 0.2351 | -1.7665 | 4.0159 | 3.3653 | 3.352 | 1.0389 | 10.7682 | 14.242 | 14.8179 | 11.0569 | 0.0001 | -0.0029 | 0.0002 | 0.0036 | 0.001 | -0.0001 | 0.0211 | 0.0007 | 0.0075 | -360.1835 | 17.3987 | -360.4542 | 17.7005 | -360.805 | 18.1029 | -360.8912 | 17.5814 | -352.6813 | 18.6655 | -352.6567 | 16.8115
12:04 | 2674 | 31.5434 | 198.1476 | 444.1594 | 449.604 | -18.6417 | -45.7348 | 7.4764 | 4.3284 | -1.8865 | -3.0105 | 0.2574 | -2.7001 | 7.1488 | 0.7223 | 0.5987 | 0.643 | 0.9545 | 0.7201 | -131.1635 | -5.6355 | 2.6528 | 0.2675 | -5.5451 | -4.2386 | 2.1693 |  | 0.2223 | -1.7336 | 4.015 | 3.3655 | 3.3497 | 1.0382 | 10.744 | 14.2523 | 14.8212 | 11.0446 | -0.0007 | -0.0029 | 0.0008 | 0.0042 | 0.0006 | -0.0003 | 0.0052 | -0.0059 | -0.0123 | -360.2327 | 17.4562 | -360.5096 | 17.7252 | -360.8174 | 18.0742 | -360.8881 | 17.5896 | -352.7337 | 18.7292 | -352.7398 | 16.8423
12:04 | 2675 | 31.5351 | 198.0867 | 444.1096 | 449.6512 | -18.6039 | -45.6074 | 7.4925 | 4.3576 | -1.8319 | -2.9366 | 0.336 | -2.7265 | 7.207 | 0.7414 | 0.6003 | 0.6397 | 0.9547 | 0.7207 | -131.1544 | -5.5036 | 2.6917 | 0.2624 | -5.6024 | -4.3037 | 2.1495 |  | 0.2498 | -1.7236 | 4.0159 | 3.3669 | 3.3513 | 1.0391 | 10.7197 | 14.2453 | 14.7504 | 11.0493 | -0.0002 | -0.0027 | 0.001 | 0.004 | 0.001 | -0.0001 | 0.0101 | 0.0069 | -0.0138 | -360.1465 | 17.409 | -360.4819 | 17.7272 | -360.8297 | 18.0824 | -360.8574 | 17.5383 | -352.6198 | 18.6779 | -352.6752 | 16.8361
12:04 | 2676 | 31.6324 | 198.1093 | 444.1809 | 449.7185 | -18.655 | -45.7258 | 7.453 | 4.3917 | -1.8077 | -3.1436 | 0.2581 | -2.743 | 7.156 | 0.7517 | 0.6006 | 0.6407 | 0.9558 | 0.7204 | -131.2147 | -5.5345 | 2.6657 | 0.2441 | -5.6024 | -4.214 | 2.2101 |  | 0.334 | -1.7067 | 4.0152 | 3.3644 | 3.3486 | 1.0374 | 10.7256 | 14.2277 | 14.812 | 11.0501 | 0 | -0.0032 | 0.0008 | 0.0038 | 0.0003 | -0.0004 | 0.0156 | -0.0076 | -0.0072 | -360.1804 | 17.3987 | -360.4542 | 17.7128 | -360.8266 | 18.1317 | -360.9374 | 17.5917 | -352.7275 | 18.6799 | -352.6506 | 16.8197
12:04 | 2677 | 31.572 | 198.1534 | 444.0959 | 449.7291 | -18.6527 | -45.6843 | 7.5009 | 4.4359 | -1.8529 | -3.0622 | 0.2984 | -2.6966 | 7.2172 | 0.7732 | 0.6004 | 0.6434 | 0.9532 | 0.7182 | -131.1975 | -5.444 | 2.6308 | 0.3348 | -5.5265 | -4.2052 | 2.1522 |  | 0.3023 | -1.7566 | 4.0167 | 3.3646 | 3.3503 | 1.0393 | 10.7348 | 14.2197 | 14.8103 | 11.0302 | -0.0001 | -0.0032 | 0.001 | 0.0039 | 0.0011 | -0.0009 | 0.0107 | -0.0091 | -0.0178 | -360.2265 | 17.4172 | -360.4604 | 17.6861 | -360.7589 | 18.0865 | -360.885 | 17.5732 | -352.7121 | 18.6922 | -352.6721 | 16.8094
12:04 | 2678 | 31.64 | 198.1376 | 444.0426 | 449.7229 | -18.6567 | -45.7667 | 7.4133 | 4.4617 | -1.8091 | -2.8768 | 0.331 | -2.697 | 7.2086 | 0.7522 | 0.6 | 0.6423 | 0.9545 | 0.721 | -131.2711 | -5.4024 | 2.7105 | 0.223 | -5.5775 | -4.3015 | 2.1839 |  | 0.2862 | -1.7973 | 4.016 | 3.3623 | 3.3502 | 1.0385 | 10.7162 | 14.2303 | 14.7937 | 11.0341 | -0.0001 | -0.0026 | 0.0008 | 0.0037 | 0.0005 | -0.0006 | 0.004 | -0.0065 | -0.0193 | -360.1219 | 17.4233 | -360.5158 | 17.7518 | -360.8635 | 18.0968 | -360.8758 | 17.5404 | -352.6383 | 18.6799 | -352.6967 | 16.8423
12:04 | 2679 | 31.603 | 198.1615 | 444.1273 | 449.6946 | -18.6839 | -45.7167 | 7.5297 | 4.474 | -1.8856 | -3.1418 | 0.2993 | -2.6972 | 7.1545 | 0.7034 | 0.601 | 0.645 | 0.9538 | 0.7199 | -131.1965 | -5.3562 | 2.7072 | 0.1926 | -5.5857 | -4.279 | 2.1842 |  | 0.2914 | -1.713 | 4.0154 | 3.3641 | 3.3494 | 1.0381 | 10.7104 | 14.213 | 14.8168 | 11.0457 | -0.0004 | -0.0028 | 0.0005 | 0.0037 | 0.0009 | -0.0008 | 0.008 | -0.0111 | -0.0123 | -360.1588 | 17.3884 | -360.4604 | 17.7231 | -360.8204 | 18.1379 | -360.9527 | 17.5773 | -352.7121 | 18.6717 | -352.6783 | 16.8299
12:04 | 2680 | 31.5998 | 198.1089 | 443.9711 | 449.579 | -18.7037 | -45.6925 | 7.4609 | 4.4756 | -1.7706 | -3.0187 | 0.3189 | -2.656 | 7.1425 | 0.7722 | 0.601 | 0.6459 | 0.9545 | 0.7202 | -131.2065 | -5.377 | 2.841 | 0.2124 | -5.6943 | -4.3615 | 2.1707 |  | 0.2002 | -1.6152 | 4.0159 | 3.3636 | 3.3469 | 1.0384 | 10.6943 | 14.1965 | 14.7813 | 11.0129 | 0.0002 | -0.0029 | 0.0003 | 0.0038 | 0.0004 | -0.0001 | 0.0054 | -0.0194 | -0.0184 | -360.1711 | 17.4007 | -360.4696 | 17.6964 | -360.7681 | 18.066 | -360.8543 | 17.5671 | -352.669 | 18.682 | -352.6906 | 16.8094
12:04 | 2681 | 31.5733 | 198.0548 | 443.9919 | 449.6217 | -18.6267 | -45.7782 | 7.3988 | 4.497 | -1.7945 | -2.9845 | 0.3584 | -2.6794 | 7.1232 | 0.7752 | 0.6006 | 0.6401 | 0.954 | 0.7211 | -131.2006 | -5.4611 | 2.7443 | 0.3475 | -5.7238 | -4.3418 | 2.1541 |  | 0.2127 | -1.5903 | 4.0166 | 3.3654 | 3.3474 | 1.0393 | 10.752 | 14.2606 | 14.8019 | 11.0637 | 0.0003 | -0.003 | 0.0002 | 0.0034 | 0.0009 | -0.0006 | 0.0121 | 0.0001 | -0.026 | -360.1804 | 17.4356 | -360.5496 | 17.7703 | -360.9097 | 18.1112 | -360.8666 | 17.5465 | -352.6752 | 18.6963 | -352.7337 | 16.8669
12:04 | 2682 | 31.5637 | 198.0862 | 444.0966 | 449.6293 | -18.6051 | -45.7688 | 7.4762 | 4.4201 | -1.8735 | -3.056 | 0.3486 | -2.6546 | 7.1385 | 0.7938 | 0.6001 | 0.6433 | 0.9548 | 0.7208 | -131.2027 | -5.4593 | 2.8373 | 0.4899 | -5.7539 | -4.3519 | 2.1622 |  | 0.2183 | -1.6938 | 4.0135 | 3.3649 | 3.3491 | 1.0372 | 10.745 | 14.2422 | 14.8363 | 11.0507 | 0 | -0.0028 | 0.0008 | 0.0039 | 0.0004 | -0.0007 | 0.0031 | -0.0023 | -0.005 | -360.1465 | 17.4007 | -360.4573 | 17.721 | -360.8358 | 18.1153 | -360.8697 | 17.5547 | -352.6383 | 18.6717 | -352.6783 | 16.832
12:04 | 2683 | 31.6539 | 198.099 | 444.1537 | 449.65 | -18.7329 | -45.7442 | 7.4927 | 4.4072 | -1.8781 | -3.0396 | 0.446 | -2.6511 | 7.2317 | 0.8567 | 0.5995 | 0.6405 | 0.9513 | 0.72 | -131.2312 | -5.5329 | 2.8459 | 0.4383 | -5.691 | -4.2741 | 2.2108 |  | 0.2664 | -1.6125 | 4.0161 | 3.3648 | 3.3491 | 1.0391 | 10.707 | 14.2208 | 14.7711 | 11.0428 | -0.0004 | -0.0027 | 0.0008 | 0.0039 | 0.0003 | -0.0008 | 0.0139 | -0.0127 | 0.0175 | -360.1773 | 17.4274 | -360.5004 | 17.7026 | -360.7743 | 18.0783 | -360.8881 | 17.5753 | -352.7121 | 18.7087 | -352.669 | 16.8012
12:04 | 2684 | 31.6789 | 198.1722 | 444.197 | 449.6494 | -18.671 | -45.6832 | 7.5841 | 4.3245 | -1.8091 | -3.0563 | 0.3577 | -2.683 | 7.1902 | 0.7644 | 0.5983 | 0.643 | 0.9534 | 0.7216 | -131.2296 | -5.4169 | 2.8616 | 0.544 | -5.6459 | -4.2914 | 2.223 |  | 0.3013 | -1.6443 | 4.0153 | 3.3636 | 3.3509 | 1.0375 | 10.7278 | 14.2361 | 14.8053 | 11.0457 | 0.0002 | -0.0026 | 0.001 | 0.0041 | 0.0006 | -0.0005 | -0.0003 | -0.0157 | 0.0075 | -360.1988 | 17.4439 | -360.5219 | 17.7518 | -360.845 | 18.0906 | -360.8266 | 17.5527 | -352.6998 | 18.7169 | -352.7706 | 16.8525
12:04 | 2685 | 31.6899 | 198.1595 | 444.1609 | 449.6321 | -18.5965 | -45.5994 | 7.4761 | 4.3858 | -1.8059 | -3.053 | 0.3668 | -2.6581 | 7.1737 | 0.7189 | 0.5997 | 0.6419 | 0.9544 | 0.7193 | -131.2118 | -5.5953 | 2.8099 | 0.4776 | -5.6925 | -4.3166 | 2.1821 |  | 0.2963 | -1.6531 | 4.017 | 3.3655 | 3.3513 | 1.0381 | 10.7279 | 14.2243 | 14.78 | 11.058 | 0.0003 | -0.0031 | 0.0005 | 0.0038 | 0.0006 | -0.0003 | 0.0073 | -0.0042 | -0.0136 | -360.1065 | 17.372 | -360.4112 | 17.7149 | -360.8327 | 18.1091 | -360.8727 | 17.5445 | -352.5952 | 18.6573 | -352.6598 | 16.8238
12:04 | 2686 | 31.6573 | 198.1842 | 444.1116 | 449.7049 | -18.6548 | -45.5672 | 7.5753 | 4.4736 | -1.7802 | -3.0742 | 0.3866 | -2.6034 | 7.2126 | 0.8352 | 0.601 | 0.6429 | 0.9565 | 0.7201 | -131.1909 | -5.5036 | 2.8126 | 0.4764 | -5.781 | -4.3 | 2.1109 |  | 0.2747 | -1.8107 | 4.0156 | 3.3667 | 3.3494 | 1.0377 | 10.7163 | 14.2069 | 14.7626 | 11.0233 | -0.0002 | -0.003 | 0.0005 | 0.0035 | 0.0012 | -0.0006 | 0.0081 | -0.0139 | -0.0034 | -360.2542 | 17.4356 | -360.4573 | 17.7128 | -360.8143 | 18.1009 | -360.9281 | 17.604 | -352.7614 | 18.7087 | -352.6752 | 16.8176
12:04 | 2687 | 31.5636 | 198.2154 | 444.1588 | 449.6039 | -18.6748 | -45.6701 | 7.6113 | 4.43 | -1.8001 | -2.9954 | 0.3765 | -2.5934 | 7.2479 | 0.7418 | 0.5999 | 0.6423 | 0.9544 | 0.7204 | -131.1748 | -5.434 | 2.9116 | 0.4524 | -5.7307 | -4.2751 | 2.1272 |  | 0.2979 | -1.7971 | 4.0147 | 3.366 | 3.3464 | 1.038 | 10.7013 | 14.2091 | 14.7527 | 11.0201 | 0.0002 | -0.0022 | 0.0004 | 0.0036 | 0.0002 | -0.0005 | 0.0146 | -0.018 | -0.0184 | -360.165 | 17.4192 | -360.4912 | 17.7169 | -360.7989 | 18.0763 | -360.845 | 17.5568 | -352.6967 | 18.7128 | -352.6844 | 16.8197
12:05 | 2688 | 31.609 | 198.1976 | 444.1511 | 449.5934 | -18.6716 | -45.7231 | 7.4167 | 4.373 | -1.8593 | -2.9957 | 0.5088 | -2.5727 | 7.2168 | 0.8223 | 0.6004 | 0.6411 | 0.9543 | 0.7201 | -131.1558 | -5.4247 | 2.8892 | 0.5958 | -5.6409 | -4.2761 | 2.2358 |  | 0.3144 | -1.7296 | 4.0153 | 3.3676 | 3.3505 | 1.039 | 10.7187 | 14.209 | 14.7285 | 11.0205 | -0.0003 | -0.0029 | 0.0005 | 0.0034 | 0.0009 | -0.001 | 0.008 | -0.012 | -0.008 | -360.125 | 17.3966 | -360.4666 | 17.7395 | -360.8789 | 18.1255 | -360.8943 | 17.5527 | -352.6506 | 18.6635 | -352.6844 | 16.8381
12:05 | 2689 | 31.6321 | 198.2046 | 444.1196 | 449.6791 | -18.6752 | -45.7277 | 7.5823 | 4.389 | -1.8082 | -3.0884 | 0.568 | -2.5804 | 7.1873 | 0.8419 | 0.5998 | 0.6427 | 0.9554 | 0.7207 | -131.2288 | -5.3687 | 2.8684 | 0.5774 | -5.6031 | -4.2046 | 2.2266 |  | 0.275 | -1.7862 | 4.0159 | 3.3655 | 3.3483 | 1.0386 | 10.7277 | 14.2363 | 14.8005 | 11.0222 | 0.0004 | -0.0026 | 0.001 | 0.0041 | 0.0005 | -0.0003 | 0.0093 | -0.0022 | 0.0083 | -360.1465 | 17.4028 | -360.4266 | 17.7149 | -360.805 | 18.1194 | -360.9343 | 17.5814 | -352.6844 | 18.6881 | -352.6598 | 16.8279
12:05 | 2690 | 31.7408 | 198.2155 | 444.113 | 449.6348 | -18.7033 | -45.7634 | 7.4637 | 4.3682 | -1.8456 | -2.9885 | 0.5821 | -2.6006 | 7.1422 | 0.8768 | 0.6009 | 0.6386 | 0.9571 | 0.7198 | -131.2207 | -5.3138 | 2.88 | 0.3975 | -5.6216 | -4.181 | 2.1815 |  | 0.2583 | -1.7483 | 4.0148 | 3.3646 | 3.3522 | 1.0387 | 10.7313 | 14.222 | 14.7899 | 11.0439 | -0.0001 | -0.0033 | 0.0009 | 0.004 | 0.0007 | -0.0009 | 0.0064 | -0.0092 | -0.0098 | -360.1588 | 17.4315 | -360.4942 | 17.7149 | -360.8112 | 18.0742 | -360.8266 | 17.5588 | -352.6844 | 18.7128 | -352.7183 | 16.8238
12:05 | 2691 | 31.7238 | 198.156 | 444.0314 | 449.6909 | -18.6769 | -45.7147 | 7.571 | 4.3446 | -1.8074 | -2.9894 | 0.5508 | -2.6444 | 7.0919 | 0.784 | 0.5995 | 0.6429 | 0.9573 | 0.7196 | -131.2086 | -5.2941 | 2.7923 | 0.39 | -5.6672 | -4.2152 | 2.2029 |  | 0.2782 | -1.7072 | 4.0168 | 3.3672 | 3.3538 | 1.0391 | 10.7509 | 14.2363 | 14.7947 | 11.0511 | -0.0003 | -0.0025 | 0.0011 | 0.004 | 0.0005 | 0 | 0.0217 | -0.0054 | -0.0115 | -360.1219 | 17.4295 | -360.5343 | 17.7539 | -360.9004 | 18.1153 | -360.8574 | 17.5445 | -352.6752 | 18.7128 | -352.7367 | 16.8464
12:05 | 2692 | 31.6519 | 198.0566 | 444.049 | 449.6376 | -18.7136 | -45.7955 | 7.3774 | 4.3163 | -1.8133 | -3.0098 | 0.6245 | -2.6421 | 7.1251 | 0.8795 | 0.5999 | 0.6402 | 0.9543 | 0.7195 | -131.1657 | -5.3562 | 2.8681 | 0.3924 | -5.674 | -4.1213 | 2.2915 |  | 0.2516 | -1.6782 | 4.016 | 3.3625 | 3.3531 | 1.0392 | 10.729 | 14.2372 | 14.794 | 11.0702 | -0.0002 | -0.0026 | 0.001 | 0.0037 | 0.0007 | -0.0007 | 0.0265 | -0.0002 | -0.0205 | -360.1558 | 17.3925 | -360.4296 | 17.6923 | -360.8204 | 18.105 | -360.8697 | 17.5609 | -352.6598 | 18.682 | -352.6537 | 16.8135
12:05 | 2693 | 31.637 | 198.1164 | 444.1004 | 449.696 | -18.7255 | -45.7609 | 7.4949 | 4.429 | -1.8129 | -3.0601 | 0.5599 | -2.6464 | 7.1756 | 0.8488 | 0.5984 | 0.6466 | 0.9554 | 0.7181 | -131.1472 | -5.3214 | 2.7671 | 0.3525 | -5.6838 | -4.1897 | 2.1628 |  | 0.2919 | -1.7086 | 4.017 | 3.3652 | 3.3516 | 1.0392 | 10.7463 | 14.2372 | 14.7766 | 11.0529 | -0.0003 | -0.0034 | 0.0003 | 0.0036 | 0.0008 | -0.0003 | 0.0105 | -0.0087 | -0.0104 | -360.2081 | 17.448 | -360.4912 | 17.6964 | -360.8143 | 18.0742 | -360.8943 | 17.5691 | -352.7183 | 18.7374 | -352.706 | 16.7971
12:05 | 2694 | 31.6443 | 198.0147 | 443.9812 | 449.6563 | -18.7928 | -45.7738 | 7.5084 | 4.3492 | -1.8341 | -3.0418 | 0.5598 | -2.6275 | 7.146 | 0.9437 | 0.5987 | 0.6466 | 0.9549 | 0.7193 | -131.1502 | -5.3465 | 2.7711 | 0.2978 | -5.736 | -4.3073 | 2.148 |  | 0.3589 | -1.6368 | 4.016 | 3.3648 | 3.3513 | 1.0385 | 10.7162 | 14.2418 | 14.7752 | 11.0345 | 0 | -0.0029 | 0.0008 | 0.0042 | 0.001 | -0.0004 | -0.0014 | -0.012 | -0.0169 | -360.1619 | 17.4192 | -360.4758 | 17.7169 | -360.845 | 18.0763 | -360.8666 | 17.5547 | -352.6598 | 18.7128 | -352.7367 | 16.8361
12:05 | 2695 | 31.6995 | 198.1336 | 444.0633 | 449.6369 | -18.6311 | -45.7103 | 7.524 | 4.3586 | -1.8422 | -3.0216 | 0.5358 | -2.5908 | 7.1363 | 0.835 | 0.5996 | 0.6434 | 0.9535 | 0.7191 | -131.1481 | -5.3642 | 2.8017 | 0.1445 | -5.622 | -4.2464 | 2.1721 |  | 0.3088 | -1.6938 | 4.0171 | 3.3683 | 3.3466 | 1.038 | 10.7245 | 14.2148 | 14.7517 | 11.0436 | -0.0006 | -0.0031 | 0.0002 | 0.0036 | 0.0009 | -0.0007 | -0.0045 | -0.0036 | -0.0052 | -360.1342 | 17.409 | -360.4389 | 17.6944 | -360.845 | 18.1173 | -360.8912 | 17.565 | -352.6567 | 18.6861 | -352.6506 | 16.8156
12:05 | 2696 | 31.6675 | 198.1016 | 444.0489 | 449.6175 | -18.6781 | -45.6727 | 7.5526 | 4.3449 | -1.7841 | -2.9535 | 0.5571 | -2.6705 | 7.2284 | 0.8599 | 0.6018 | 0.6458 | 0.9596 | 0.7211 | -131.1283 | -5.3766 | 2.9474 | 0.2587 | -5.7033 | -4.2752 | 2.1397 |  | 0.3237 | -1.7216 | 4.0165 | 3.3653 | 3.3477 | 1.039 | 10.7082 | 14.2392 | 14.7599 | 11.0327 | -0.0004 | -0.0028 | 0.0005 | 0.0039 | 0.0008 | -0.0004 | 0.0051 | -0.0149 | -0.0215 | -360.2111 | 17.4254 | -360.4819 | 17.6718 | -360.7804 | 18.1091 | -360.9035 | 17.5835 | -352.706 | 18.7107 | -352.6906 | 16.8032
12:05 | 2697 | 31.7258 | 198.1294 | 443.925 | 449.6526 | -18.664 | -45.7896 | 7.4657 | 4.5069 | -1.7496 | -3.032 | 0.6526 | -2.6704 | 7.135 | 0.8677 | 0.6022 | 0.6473 | 0.9557 | 0.7209 | -131.0914 | -5.4073 | 2.8434 | 0.4398 | -5.7639 | -4.2497 | 2.0926 |  | 0.2831 | -1.7809 | 4.0185 | 3.37 | 3.3495 | 1.0396 | 10.7244 | 14.2149 | 14.7643 | 11.049 | -0.0001 | -0.0035 | 0.0007 | 0.0037 | 0.0007 | -0.0008 | 0.0186 | -0.0139 | -0.0177 | -360.1527 | 17.4233 | -360.4727 | 17.7005 | -360.8081 | 18.0763 | -360.8174 | 17.5506 | -352.6475 | 18.7004 | -352.6906 | 16.8238
12:05 | 2698 | 31.7096 | 198.2025 | 444.0257 | 449.6544 | -18.7639 | -45.8296 | 7.3997 | 4.3575 | -1.8161 | -2.7937 | 0.6198 | -2.6805 | 7.1221 | 0.8309 | 0.6012 | 0.6412 | 0.9538 | 0.7196 | -131.1228 | -5.3356 | 2.8235 | 0.5017 | -5.7463 | -4.3573 | 2.14 |  | 0.2832 | -1.7092 | 4.0175 | 3.3667 | 3.3496 | 1.0399 | 10.7325 | 14.2348 | 14.7855 | 11.0276 | 0.0002 | -0.0029 | 0.0008 | 0.0039 | 0.0004 | -0.0001 | 0.0002 | -0.0142 | -0.0238 | -360.1404 | 17.4172 | -360.4881 | 17.7149 | -360.882 | 18.1255 | -360.9189 | 17.5691 | -352.669 | 18.7045 | -352.7275 | 16.8423
12:05 | 2699 | 31.7515 | 198.1878 | 444.0719 | 449.6444 | -18.7192 | -45.78 | 7.5036 | 4.3744 | -1.8137 | -2.926 | 0.603 | -2.6541 | 7.1653 | 0.7871 | 0.5998 | 0.6444 | 0.9569 | 0.7199 | -131.1076 | -5.3938 | 2.879 | 0.5109 | -5.6833 | -4.2591 | 2.172 |  | 0.2953 | -1.8786 | 4.0172 | 3.3655 | 3.3469 | 1.0404 | 10.7289 | 14.2432 | 14.7787 | 11.0406 | -0.0001 | -0.0036 | 0.0007 | 0.0042 | 0.0007 | -0.0007 | 0.0124 | -0.0041 | -0.0051 | -360.1342 | 17.3864 | -360.4419 | 17.68 | -360.7927 | 18.0886 | -360.8912 | 17.5588 | -352.666 | 18.6881 | -352.6598 | 16.8176
12:05 | 2700 | 31.6857 | 198.1133 | 444.1824 | 449.6678 | -18.7226 | -45.8008 | 7.459 | 4.3816 | -1.8208 | -2.9685 | 0.5507 | -2.6533 | 7.1678 | 0.8774 | 0.6017 | 0.6431 | 0.9555 | 0.7209 | -131.1595 | -5.3779 | 2.897 | 0.431 | -5.7158 | -4.3961 | 2.0832 |  | 0.3385 | -1.7794 | 4.0172 | 3.367 | 3.3513 | 1.0391 | 10.737 | 14.2281 | 14.8152 | 11.0663 | -0.0002 | -0.0025 | 0.0011 | 0.0039 | 0.0006 | 0 | 0.0062 | -0.0178 | -0.0155 | -360.1742 | 17.4562 | -360.4942 | 17.7046 | -360.845 | 18.0968 | -360.8327 | 17.5814 | -352.7213 | 18.721 | -352.7306 | 16.8279
12:05 | 2701 | 31.7112 | 198.1129 | 444.0719 | 449.7781 | -18.7583 | -45.7929 | 7.469 | 4.3824 | -1.768 | -2.926 | 0.4988 | -2.5266 | 7.2629 | 0.8505 | 0.6004 | 0.6458 | 0.9545 | 0.7196 | -131.1438 | -5.3396 | 2.8528 | 0.484 | -5.6177 | -4.2616 | 2.1668 |  | 0.2848 | -1.7352 | 4.0168 | 3.367 | 3.35 | 1.0388 | 10.7578 | 14.2434 | 14.803 | 11.0691 | 0.0002 | -0.0028 | 0.0004 | 0.0036 | 0.0008 | -0.0007 | -0.003 | -0.0085 | -0.0294 | -360.1465 | 17.411 | -360.4881 | 17.6964 | -360.8327 | 18.0865 | -360.8512 | 17.5445 | -352.6598 | 18.7025 | -352.7152 | 16.8279
12:05 | 2702 | 31.7147 | 198.0455 | 444.183 | 449.7518 | -18.7136 | -45.8942 | 7.4292 | 4.3342 | -1.7394 | -2.9295 | 0.4808 | -2.5541 | 7.2439 | 0.8933 | 0.6011 | 0.6467 | 0.9571 | 0.7197 | -131.0324 | -5.215 | 2.9257 | 0.3753 | -5.6016 | -4.2063 | 2.1926 |  | 0.2648 | -1.6298 | 4.0157 | 3.3669 | 3.3484 | 1.0388 | 10.7071 | 14.2207 | 14.7817 | 10.997 | 0 | -0.0032 | 0.0007 | 0.0037 | 0.0005 | -0.0005 | 0.0223 | -0.0083 | -0.0052 | -360.1835 | 17.411 | -360.4666 | 17.6718 | -360.7897 | 18.1009 | -360.8789 | 17.5732 | -352.6506 | 18.6881 | -352.6567 | 16.8074
12:05 | 2703 | 31.7531 | 198.0644 | 444.1919 | 449.696 | -18.739 | -45.7743 | 7.3728 | 4.4231 | -1.7556 | -2.8962 | 0.5096 | -2.5617 | 7.294 | 0.9275 | 0.5991 | 0.6444 | 0.9575 | 0.7193 | -131.0968 | -5.2178 | 3.0208 | 0.3642 | -5.5936 | -4.2423 | 2.1647 |  | 0.2266 | -1.5958 | 4.0158 | 3.369 | 3.3494 | 1.0394 | 10.729 | 14.2256 | 14.7592 | 11.0298 | -0.0002 | -0.0027 | 0.0009 | 0.0039 | 0.0005 | -0.0006 | 0.0141 | -0.0089 | -0.0077 | -360.2481 | 17.4377 | -360.5066 | 17.6944 | -360.8266 | 18.1071 | -360.882 | 17.5835 | -352.6875 | 18.7128 | -352.7337 | 16.8279
12:05 | 2704 | 31.7033 | 197.977 | 444.1197 | 449.6505 | -18.7802 | -45.7628 | 7.478 | 4.3913 | -1.7269 | -2.8854 | 0.5012 | -2.6269 | 7.2683 | 0.9374 | 0.6001 | 0.6442 | 0.9563 | 0.72 | -131.1402 | -5.2652 | 2.9179 | 0.4081 | -5.6073 | -4.2155 | 2.2216 |  | 0.236 | -1.6453 | 4.0165 | 3.3653 | 3.3526 | 1.0391 | 10.6967 | 14.216 | 14.753 | 11.0273 | -0.0003 | -0.0026 | 0.0003 | 0.0038 | 0.0006 | -0.001 | 0.0057 | -0.0035 | -0.0109 | -360.1373 | 17.4028 | -360.4542 | 17.6923 | -360.8235 | 18.0906 | -360.8358 | 17.5506 | -352.6444 | 18.6922 | -352.6598 | 16.8197
12:05 | 2705 | 31.7422 | 198.1474 | 444.1568 | 449.6586 | -18.7626 | -45.7192 | 7.4984 | 4.3379 | -1.807 | -2.877 | 0.5177 | -2.5983 | 7.2329 | 0.8866 | 0.6003 | 0.6461 | 0.9593 | 0.7192 | -131.1196 | -5.4129 | 2.8122 | 0.405 | -5.6516 | -4.2179 | 2.1624 |  | 0.2782 | -1.7229 | 4.0171 | 3.3665 | 3.3472 | 1.0402 | 10.7152 | 14.1942 | 14.7439 | 11.028 | -0.0003 | -0.0029 | 0.0012 | 0.0042 | 0.0004 | -0.0004 | 0.0181 | -0.002 | -0.0124 | -360.1681 | 17.4254 | -360.4696 | 17.7026 | -360.845 | 18.1153 | -360.9189 | 17.5712 | -352.6783 | 18.7066 | -352.7152 | 16.8197
12:05 | 2706 | 31.7535 | 198.0767 | 444.165 | 449.6846 | -18.8269 | -45.7392 | 7.5027 | 4.3728 | -1.7692 | -2.8619 | 0.4241 | -2.6663 | 7.2288 | 0.9423 | 0.6003 | 0.6436 | 0.9547 | 0.7188 | -131.0806 | -5.3 | 2.7497 | 0.3559 | -5.7044 | -4.1699 | 2.1673 |  | 0.2499 | -1.7885 | 4.0185 | 3.3665 | 3.3493 | 1.0411 | 10.7484 | 14.2459 | 14.8125 | 11.0825 | 0.0003 | -0.0029 | 0.0007 | 0.0038 | 0.0015 | -0.0002 | -0.0053 | -0.0088 | -0.0265 | -360.1373 | 17.4192 | -360.4666 | 17.6964 | -360.8081 | 18.0886 | -360.8727 | 17.5671 | -352.6783 | 18.6943 | -352.7029 | 16.8238
12:05 | 2707 | 31.7727 | 198.1345 | 444.1665 | 449.7081 | -18.8436 | -45.7055 | 7.4871 | 4.3212 | -1.7862 | -2.8831 | 0.4322 | -2.5819 | 7.1874 | 0.94 | 0.6008 | 0.6438 | 0.9502 | 0.7188 | -131.1554 | -5.4065 | 2.6791 | 0.3692 | -5.7031 | -4.1999 | 2.1436 |  | 0.257 | -1.638 | 4.0189 | 3.3632 | 3.3525 | 1.0404 | 10.7325 | 14.229 | 14.7855 | 11.0334 | 0.0001 | -0.003 | 0.0003 | 0.0035 | 0.0006 | -0.0003 | 0.0162 | -0.001 | 0.0144 | -360.1404 | 17.4131 | -360.4758 | 17.6985 | -360.805 | 18.0865 | -360.8297 | 17.5445 | -352.6475 | 18.6963 | -352.6721 | 16.8135
12:05 | 2708 | 31.8167 | 198.1103 | 444.2053 | 449.7291 | -18.7018 | -45.7524 | 7.5394 | 4.2629 | -1.782 | -2.7882 | 0.4624 | -2.5645 | 7.2224 | 0.9517 | 0.6004 | 0.6438 | 0.9528 | 0.7199 | -131.1498 | -5.4425 | 2.6626 | 0.5199 | -5.7181 | -4.1428 | 2.2143 |  | 0.2778 | -1.6159 | 4.0163 | 3.3683 | 3.3488 | 1.0375 | 10.7289 | 14.2257 | 14.795 | 11.0294 | 0.0004 | -0.0019 | 0.0011 | 0.0039 | 0.001 | -0.0005 | -0.0037 | -0.0142 | -0.0115 | -360.1835 | 17.4254 | -360.5219 | 17.7149 | -360.8481 | 18.1153 | -360.9066 | 17.5773 | -352.6629 | 18.7107 | -352.7183 | 16.8381
12:05 | 2709 | 31.747 | 198.1226 | 444.1787 | 449.6466 | -18.7801 | -45.8102 | 7.484 | 4.344 | -1.7036 | -2.7653 | 0.5385 | -2.6164 | 7.2769 | 0.8763 | 0.6006 | 0.6416 | 0.9543 | 0.7194 | -131.0858 | -5.3154 | 2.7189 | 0.589 | -5.6586 | -4.141 | 2.3021 |  | 0.272 | -1.6355 | 4.0167 | 3.3651 | 3.351 | 1.0386 | 10.7417 | 14.2383 | 14.8069 | 11.0771 | -0.0003 | -0.0026 | 0.0001 | 0.0033 | 0.0005 | -0.0003 | -0.0019 | -0.0044 | -0.011 | -360.1927 | 17.4048 | -360.4666 | 17.7026 | -360.8204 | 18.0824 | -360.8512 | 17.5609 | -352.6629 | 18.6881 | -352.6444 | 16.8176
12:05 | 2710 | 31.7708 | 198.1936 | 444.1351 | 449.6139 | -18.7628 | -45.8676 | 7.4231 | 4.3226 | -1.7287 | -2.8736 | 0.5334 | -2.5852 | 7.3141 | 0.9715 | 0.6002 | 0.6431 | 0.9549 | 0.7213 | -130.9863 | -5.3543 | 2.7665 | 0.5308 | -5.6475 | -4.1148 | 2.3167 |  | 0.1996 | -1.731 | 4.0159 | 3.3664 | 3.3492 | 1.0406 | 10.7048 | 14.1951 | 14.7836 | 11.0356 | -0.0003 | -0.0034 | 0.0006 | 0.0037 | 0.0006 | -0.001 | 0.0014 | -0.0044 | -0.0318 | -360.1773 | 17.4233 | -360.4696 | 17.7005 | -360.8143 | 18.0906 | -360.8481 | 17.5568 | -352.666 | 18.6943 | -352.6906 | 16.8115
12:05 | 2711 | 31.8211 | 198.1701 | 444.1656 | 449.6788 | -18.745 | -45.8804 | 7.4526 | 4.3381 | -1.7469 | -2.7183 | 0.4752 | -2.4985 | 7.2629 | 1.0107 | 0.5995 | 0.6416 | 0.9539 | 0.7194 | -131.0155 | -5.3007 | 2.7285 | 0.4608 | -5.6705 | -4.1984 | 2.2917 |  | 0.2891 | -1.6954 | 4.0149 | 3.3662 | 3.3513 | 1.039 | 10.7 | 14.214 | 14.7592 | 11.0356 | 0.0001 | -0.0034 | 0.0012 | 0.0042 | 0.0006 | -0.0003 | 0.0027 | -0.0056 | -0.0247 | -360.1896 | 17.4295 | -360.5127 | 17.721 | -360.845 | 18.1071 | -360.8758 | 17.5691 | -352.6998 | 18.7128 | -352.7029 | 16.8381
12:05 | 2712 | 31.8909 | 198.2265 | 444.2267 | 449.6574 | -18.6355 | -45.8087 | 7.499 | 4.3442 | -1.805 | -2.7762 | 0.5158 | -2.4291 | 7.2906 | 0.9838 | 0.5995 | 0.6417 | 0.9532 | 0.7183 | -130.9798 | -5.3014 | 2.7168 | 0.4348 | -5.6959 | -4.1803 | 2.2468 |  | 0.2271 | -1.6922 | 4.0172 | 3.368 | 3.3539 | 1.0402 | 10.713 | 14.1971 | 14.7495 | 11.0039 | -0.0005 | -0.0032 | 0.0002 | 0.0037 | 0.0007 | -0.0007 | 0.0042 | -0.0013 | -0.0203 | -360.1558 | 17.409 | -360.4604 | 17.68 | -360.765 | 18.0906 | -360.8635 | 17.5486 | -352.6444 | 18.6943 | -352.6783 | 16.8074
12:05 | 2713 | 31.9326 | 198.2387 | 444.2651 | 449.7373 | -18.6992 | -45.8551 | 7.5465 | 4.3549 | -1.7978 | -2.8517 | 0.5527 | -2.5743 | 7.1854 | 0.9255 | 0.5994 | 0.6434 | 0.9508 | 0.7207 | -131.0517 | -5.4324 | 2.6606 | 0.5078 | -5.7029 | -4.104 | 2.3244 |  | 0.3048 | -1.5202 | 4.0172 | 3.3676 | 3.3527 | 1.0392 | 10.7117 | 14.2254 | 14.7929 | 11.0186 | -0.0004 | -0.0027 | 0.0008 | 0.0039 | 0.0007 | -0.0005 | 0.0021 | -0.0246 | -0.0236 | -360.1711 | 17.4233 | -360.5066 | 17.7128 | -360.8204 | 18.0906 | -360.9189 | 17.5691 | -352.666 | 18.7087 | -352.7121 | 16.8197
12:05 | 2714 | 31.8599 | 198.1377 | 444.1627 | 449.6741 | -18.6566 | -45.7819 | 7.5959 | 4.4264 | -1.8225 | -2.6674 | 0.5516 | -2.5303 | 7.291 | 0.9852 | 0.6009 | 0.6404 | 0.9541 | 0.7213 | -130.9749 | -5.3971 | 2.7686 | 0.4905 | -5.6463 | -4.1618 | 2.2997 |  | 0.25 | -1.6035 | 4.0171 | 3.3625 | 3.3516 | 1.0389 | 10.7474 | 14.2676 | 14.8438 | 11.0532 | -0.0001 | -0.003 | 0.0009 | 0.0041 | 0.0008 | -0.0004 | 0.0043 | -0.0017 | -0.0211 | -360.1988 | 17.4172 | -360.4942 | 17.7046 | -360.8174 | 18.0947 | -360.8727 | 17.5609 | -352.6875 | 18.7087 | -352.709 | 16.8258
12:05 | 2715 | 31.8852 | 198.2183 | 444.1792 | 449.7787 | -18.6398 | -45.6987 | 7.6138 | 4.4634 | -1.7547 | -2.7229 | 0.5904 | -2.5889 | 7.2473 | 1.022 | 0.5992 | 0.6428 | 0.9543 | 0.7212 | -131.0789 | -5.3361 | 2.822 | 0.483 | -5.5629 | -4.0803 | 2.2977 |  | 0.3329 | -1.6212 | 4.0164 | 3.3669 | 3.3482 | 1.0395 | 10.7487 | 14.2509 | 14.7957 | 11.0381 | -0.0001 | -0.0031 | 0.0002 | 0.0035 | 0.0009 | -0.0007 | 0.0046 | -0.0018 | -0.0091 | -360.1558 | 17.4028 | -360.4604 | 17.6944 | -360.7927 | 18.0968 | -360.8666 | 17.5486 | -352.6167 | 18.6943 | -352.6629 | 16.8217
12:05 | 2716 | 31.9433 | 198.2051 | 444.2009 | 449.7608 | -18.6606 | -45.6137 | 7.6079 | 4.4269 | -1.7443 | -2.7653 | 0.537 | -2.6461 | 7.2261 | 0.9392 | 0.5988 | 0.643 | 0.9571 | 0.7206 | -131.0289 | -5.3239 | 2.8039 | 0.3693 | -5.6479 | -4.0426 | 2.243 |  | 0.2524 | -1.7053 | 4.0176 | 3.3679 | 3.349 | 1.0383 | 10.7693 | 14.2665 | 14.8377 | 11.0922 | -0.0001 | -0.0028 | 0.0011 | 0.0038 | 0.0008 | 0 | -0.0004 | -0.0073 | -0.0306 | -360.1896 | 17.4295 | -360.485 | 17.7087 | -360.8574 | 18.1132 | -360.9004 | 17.5835 | -352.7029 | 18.7189 | -352.7275 | 16.8258
12:05 | 2717 | 31.9142 | 198.1862 | 444.2168 | 449.7844 | -18.688 | -45.7442 | 7.5357 | 4.4165 | -1.7747 | -2.7421 | 0.5088 | -2.5514 | 7.3237 | 1.0041 | 0.6005 | 0.6431 | 0.9549 | 0.7198 | -130.9776 | -5.2635 | 2.7727 | 0.4135 | -5.6616 | -4.0988 | 2.2294 |  | 0.2926 | -1.6399 | 4.0177 | 3.365 | 3.3511 | 1.0414 | 10.7568 | 14.2591 | 14.7984 | 11.0576 | -0.0008 | -0.0028 | 0.0003 | 0.0031 | 0.0006 | -0.001 | 0.022 | -0.0129 | 0.0025 | -360.1404 | 17.4131 | -360.4881 | 17.6902 | -360.7773 | 18.0886 | -360.8912 | 17.5527 | -352.6444 | 18.6984 | -352.6967 | 16.832
12:05 | 2718 | 31.9265 | 198.193 | 444.1445 | 449.7161 | -18.6641 | -45.7324 | 7.5668 | 4.5059 | -1.7501 | -2.7752 | 0.5716 | -2.4897 | 7.3172 | 0.9647 | 0.6003 | 0.6415 | 0.9516 | 0.7195 | -131.0577 | -5.2899 | 2.9376 | 0.3678 | -5.5998 | -4.1403 | 2.2473 |  | 0.2369 | -1.7308 | 4.0178 | 3.3654 | 3.3485 | 1.0405 | 10.7268 | 14.1998 | 14.7833 | 11.0226 | -0.0002 | -0.0027 | 0.0008 | 0.0035 | 0.0005 | -0.0007 | 0.0208 | -0.0184 | -0.0007 | -360.1496 | 17.4254 | -360.4758 | 17.7005 | -360.8204 | 18.0988 | -360.8543 | 17.5506 | -352.669 | 18.6902 | -352.6937 | 16.8299
12:05 | 2719 | 31.8051 | 198.2208 | 444.1977 | 449.6577 | -18.6175 | -45.5547 | 7.5904 | 4.4326 | -1.7484 | -2.6309 | 0.5148 | -2.5034 | 7.2942 | 1.0194 | 0.6006 | 0.6424 | 0.9564 | 0.7196 | -131.0816 | -5.2636 | 2.9083 | 0.3971 | -5.6866 | -4.1526 | 2.2248 |  | 0.257 | -1.6813 | 4.0187 | 3.3649 | 3.3491 | 1.0395 | 10.7324 | 14.2234 | 14.8212 | 11.0273 | -0.0001 | -0.0033 | 0.0009 | 0.0042 | 0.0013 | -0.0006 | -0.0029 | -0.0176 | -0.0024 | -360.1865 | 17.4172 | -360.4727 | 17.7128 | -360.8143 | 18.1153 | -360.9097 | 17.5814 | -352.6906 | 18.7045 | -352.7521 | 16.8566
12:05 | 2720 | 31.8701 | 198.1964 | 444.1563 | 449.5775 | -18.6697 | -45.6131 | 7.5652 | 4.4165 | -1.7718 | -2.7501 | 0.515 | -2.5191 | 7.2337 | 1.0351 | 0.6004 | 0.64 | 0.9528 | 0.7197 | -131.0971 | -5.2399 | 2.8853 | 0.3659 | -5.6582 | -4.1753 | 2.2554 |  | 0.2661 | -1.7681 | 4.0183 | 3.3711 | 3.3513 | 1.0401 | 10.7268 | 14.2287 | 14.7891 | 11.04 | -0.0001 | -0.0031 | 0.0005 | 0.0039 | 0.0005 | -0.0005 | 0.0171 | -0.0136 | -0.0273 | -360.1435 | 17.4028 | -360.4666 | 17.6882 | -360.7804 | 18.0804 | -360.8481 | 17.5568 | -352.6567 | 18.6963 | -352.6721 | 16.8258
12:05 | 2721 | 31.874 | 198.1552 | 444.1256 | 449.6874 | -18.7495 | -45.5867 | 7.5672 | 4.4622 | -1.7481 | -2.6861 | 0.4833 | -2.5507 | 7.2514 | 0.9389 | 0.6007 | 0.6442 | 0.9532 | 0.7219 | -131.0861 | -5.2725 | 2.8538 | 0.364 | -5.5714 | -4.171 | 2.3089 |  | 0.3231 | -1.6913 | 4.0181 | 3.365 | 3.3469 | 1.0399 | 10.7047 | 14.2244 | 14.7984 | 11.0229 | -0.0002 | -0.0024 | 0.0005 | 0.0039 | 0.0012 | 0 | 0.0337 | -0.0021 | 0.0091 | -360.2019 | 17.4254 | -360.5096 | 17.7169 | -360.8174 | 18.105 | -360.8758 | 17.5588 | -352.666 | 18.7087 | -352.7213 | 16.8381
12:05 | 2722 | 31.9854 | 198.2431 | 444.2119 | 449.6935 | -18.7834 | -45.6216 | 7.5585 | 4.5171 | -1.7644 | -2.626 | 0.5471 | -2.6315 | 7.3334 | 0.9163 | 0.6003 | 0.6444 | 0.9562 | 0.7211 | -131.1158 | -5.1913 | 2.8828 | 0.3888 | -5.5988 | -4.1832 | 2.2293 |  | 0.3354 | -1.6403 | 4.0159 | 3.3656 | 3.3477 | 1.0382 | 10.7382 | 14.2407 | 14.8039 | 11.0388 | -0.0003 | -0.0027 | 0.0007 | 0.0041 | 0.001 | -0.0003 | 0.0083 | -0.0068 | 0.0013 | -360.1865 | 17.4192 | -360.4789 | 17.7128 | -360.8574 | 18.1132 | -360.8697 | 17.5629 | -352.6721 | 18.7087 | -352.7029 | 16.8525
12:05 | 2723 | 31.9615 | 198.3149 | 444.1644 | 449.6935 | -18.7955 | -45.654 | 7.504 | 4.5725 | -1.7377 | -2.6714 | 0.5573 | -2.5877 | 7.326 | 0.9456 | 0.6004 | 0.6437 | 0.9558 | 0.721 | -131.1582 | -5.2964 | 2.7973 | 0.4258 | -5.5862 | -4.1634 | 2.2049 |  | 0.3889 | -1.6248 | 4.0175 | 3.3651 | 3.3484 | 1.0406 | 10.7522 | 14.237 | 14.8219 | 11.0417 | 0.0003 | -0.003 | 0.0004 | 0.0034 | 0.0005 | -0.0004 | 0.0068 | -0.0104 | -0.0092 | -360.1496 | 17.4048 | -360.4635 | 17.6779 | -360.7681 | 18.0947 | -360.8697 | 17.5568 | -352.6352 | 18.6943 | -352.6537 | 16.8258
12:05 | 2724 | 31.9233 | 198.2117 | 444.2329 | 449.731 | -18.7731 | -45.7793 | 7.4743 | 4.5069 | -1.7915 | -2.7331 | 0.4747 | -2.6303 | 7.3043 | 1.0144 | 0.6006 | 0.6429 | 0.9547 | 0.7206 | -131.0307 | -5.2618 | 2.7546 | 0.413 | -5.5736 | -4.1168 | 2.325 |  | 0.3226 | -1.5787 | 4.0183 | 3.368 | 3.3491 | 1.0406 | 10.7464 | 14.2428 | 14.7813 | 11.0475 | 0.0001 | -0.003 | 0.0007 | 0.0037 | 0.0007 | -0.0008 | 0.0304 | -0.0094 | 0.0069 | -360.2235 | 17.4439 | -360.5066 | 17.7108 | -360.8481 | 18.1009 | -360.8727 | 17.5814 | -352.7183 | 18.7251 | -352.7213 | 16.8402
12:05 | 2725 | 31.8924 | 198.1549 | 444.2277 | 449.6766 | -18.7678 | -45.7896 | 7.5161 | 4.5319 | -1.8424 | -2.7819 | 0.4571 | -2.6771 | 7.2563 | 0.9332 | 0.6007 | 0.6446 | 0.9566 | 0.72 | -131.0226 | -5.1642 | 2.9287 | 0.398 | -5.6254 | -4.1974 | 2.3039 |  | 0.3059 | -1.6655 | 4.0163 | 3.3663 | 3.3517 | 1.0393 | 10.767 | 14.2526 | 14.8176 | 11.0554 | 0 | -0.0023 | 0.0009 | 0.0036 | 0.0006 | 0 | 0.0145 | -0.0064 | -0.0018 | -360.1373 | 17.4131 | -360.4758 | 17.6923 | -360.7897 | 18.0845 | -360.845 | 17.5506 | -352.6537 | 18.6963 | -352.709 | 16.8361
12:05 | 2726 | 31.9115 | 198.2324 | 444.1821 | 449.7332 | -18.751 | -45.7662 | 7.4248 | 4.4951 | -1.8115 | -2.6387 | 0.4876 | -2.5066 | 7.4123 | 1.0605 | 0.6014 | 0.6434 | 0.9581 | 0.7216 | -131.0016 | -5.1412 | 2.8655 | 0.4175 | -5.5996 | -4.226 | 2.3472 |  | 0.3757 | -1.652 | 4.0172 | 3.3652 | 3.3518 | 1.0404 | 10.7175 | 14.208 | 14.7803 | 11.0363 | -0.0004 | -0.0028 | 0.0004 | 0.0036 | 0.0008 | -0.0007 | 0.024 | -0.0058 | -0.0114 | -360.2019 | 17.4172 | -360.4635 | 17.7087 | -360.8666 | 18.1029 | -360.882 | 17.5691 | -352.6875 | 18.6984 | -352.6998 | 16.8443
12:05 | 2727 | 32.0376 | 198.232 | 444.1709 | 449.6762 | -18.7359 | -45.8521 | 7.4025 | 4.557 | -1.8565 | -2.6861 | 0.5033 | -2.5693 | 7.3569 | 1.0042 | 0.6014 | 0.6436 | 0.9536 | 0.7212 | -131.0599 | -5.2302 | 2.8221 | 0.4247 | -5.5772 | -4.3685 | 2.3426 |  | 0.34 | -1.6685 | 4.0183 | 3.3639 | 3.347 | 1.0394 | 10.7267 | 14.2001 | 14.7681 | 11.0161 | 0.0003 | -0.0026 | 0.0012 | 0.0042 | 0.0004 | -0.0008 | 0.0013 | -0.0133 | -0.0107 | -360.2081 | 17.4028 | -360.4512 | 17.6882 | -360.7773 | 18.105 | -360.9251 | 17.565 | -352.6967 | 18.7087 | -352.6721 | 16.8176
12:05 | 2728 | 32.0256 | 198.2315 | 444.165 | 449.6313 | -18.7161 | -45.6705 | 7.4063 | 4.4847 | -1.8234 | -2.7537 | 0.4259 | -2.5941 | 7.3526 | 1.1137 | 0.6018 | 0.6441 | 0.9553 | 0.7202 | -131.03 | -5.143 | 2.8768 | 0.3797 | -5.5664 | -4.1478 | 2.325 |  | 0.4148 | -1.6259 | 4.0171 | 3.3658 | 3.3488 | 1.0399 | 10.7151 | 14.2232 | 14.7912 | 11.0334 | 0 | -0.003 | 0.0006 | 0.0037 | 0.001 | -0.0006 | 0.0098 | -0.0132 | 0.001 | -360.1527 | 17.411 | -360.4573 | 17.6861 | -360.8143 | 18.0906 | -360.8666 | 17.5568 | -352.6475 | 18.7045 | -352.6844 | 16.8258
12:05 | 2729 | 32.0644 | 198.1936 | 444.1953 | 449.6359 | -18.7363 | -45.649 | 7.5157 | 4.5232 | -1.8086 | -2.7322 | 0.5041 | -2.637 | 7.2505 | 1.0806 | 0.6022 | 0.6441 | 0.9554 | 0.7215 | -130.9974 | -5.1052 | 2.8587 | 0.4085 | -5.5512 | -4.1498 | 2.2351 |  | 0.3923 | -1.5736 | 4.0179 | 3.3643 | 3.3507 | 1.0379 | 10.7048 | 14.201 | 14.7789 | 11.0122 | -0.0001 | -0.0029 | 0.0006 | 0.0036 | 0.0002 | -0.0008 | 0.0092 | -0.0035 | 0.0128 | -360.1527 | 17.4274 | -360.5189 | 17.7149 | -360.8666 | 18.1112 | -360.8912 | 17.5588 | -352.6783 | 18.7128 | -352.7306 | 16.8587
12:05 | 2730 | 32.1002 | 198.2217 | 444.3122 | 449.6607 | -18.653 | -45.6523 | 7.4253 | 4.525 | -1.7381 | -2.7018 | 0.526 | -2.65 | 7.2933 | 1.0502 | 0.6019 | 0.6383 | 0.9534 | 0.7204 | -130.9623 | -5.149 | 2.7739 | 0.421 | -5.5238 | -4.1364 | 2.2701 |  | 0.3834 | -1.6221 | 4.0172 | 3.3609 | 3.35 | 1.0387 | 10.7 | 14.2315 | 14.7603 | 11.0063 | 0.0002 | -0.0021 | 0.0004 | 0.0037 | 0.0009 | -0.0007 | 0.0073 | -0.0122 | -0.008 | -360.1281 | 17.3843 | -360.4266 | 17.6985 | -360.8235 | 18.0968 | -360.8604 | 17.5445 | -352.6413 | 18.6696 | -352.6629 | 16.8423
12:05 | 2731 | 32.0187 | 198.1236 | 444.1698 | 449.5786 | -18.6319 | -45.6794 | 7.522 | 4.5077 | -1.6976 | -2.7009 | 0.5148 | -2.6555 | 7.2731 | 1.0821 | 0.6017 | 0.638 | 0.9555 | 0.7219 | -130.9488 | -5.1738 | 2.8659 | 0.4554 | -5.6081 | -4.1962 | 2.2854 |  | 0.4061 | -1.6586 | 4.0178 | 3.363 | 3.3503 | 1.0395 | 10.7002 | 14.1961 | 14.7724 | 11.0371 | -0.0004 | -0.0033 | 0.0006 | 0.0033 | 0.0008 | -0.0004 | 0.0044 | -0.0093 | -0.0235 | -360.2081 | 17.4315 | -360.4881 | 17.6985 | -360.8297 | 18.1132 | -360.9281 | 17.5814 | -352.709 | 18.7189 | -352.6783 | 16.834
12:05 | 2732 | 32.0671 | 198.1763 | 444.3485 | 449.7191 | -18.6688 | -45.5639 | 7.5045 | 4.6071 | -1.7227 | -2.6513 | 0.4826 | -2.6508 | 7.2908 | 1.1461 | 0.6005 | 0.6396 | 0.9598 | 0.7203 | -131.0151 | -5.1451 | 2.9346 | 0.4491 | -5.6061 | -4.2157 | 2.2525 |  | 0.3993 | -1.5686 | 4.0165 | 3.3641 | 3.3499 | 1.0389 | 10.7301 | 14.2326 | 14.7664 | 11.0424 | 0.0002 | -0.003 | 0.0008 | 0.0039 | 0.0008 | -0.0004 | 0.0054 | 0.0002 | -0.0022 | -360.1558 | 17.4254 | -360.4881 | 17.6861 | -360.7958 | 18.0701 | -360.8604 | 17.5629 | -352.6875 | 18.7128 | -352.7213 | 16.8299
12:05 | 2733 | 31.9233 | 197.997 | 444.3014 | 449.6447 | -18.6739 | -45.5323 | 7.5827 | 4.6369 | -1.7255 | -2.7682 | 0.3557 | -2.4741 | 7.3311 | 1.1567 | 0.6019 | 0.6408 | 0.9588 | 0.7207 | -131.0325 | -5.1357 | 2.8318 | 0.4977 | -5.5395 | -4.1195 | 2.2953 |  | 0.3485 | -1.6477 | 4.0163 | 3.3662 | 3.3492 | 1.0392 | 10.7451 | 14.2419 | 14.7937 | 11.0457 | -0.0002 | -0.0031 | 0.0009 | 0.0038 | 0.0012 | 0.0001 | 0.0041 | -0.0128 | -0.0123 | -360.1527 | 17.4151 | -360.5035 | 17.6944 | -360.8266 | 18.0763 | -360.8543 | 17.5465 | -352.6444 | 18.7025 | -352.706 | 16.8423
12:05 | 2734 | 31.9409 | 198.0856 | 444.2928 | 449.685 | -18.7325 | -45.7162 | 7.3974 | 4.6077 | -1.6803 | -2.6667 | 0.4614 | -2.468 | 7.3295 | 1.1858 | 0.6012 | 0.6423 | 0.9566 | 0.7204 | -131.0709 | -5.215 | 2.8073 | 0.5297 | -5.5391 | -4.0475 | 2.3371 |  | 0.3575 | -1.7614 | 4.0172 | 3.365 | 3.3459 | 1.0394 | 10.7406 | 14.2311 | 14.8092 | 11.0537 | -0.0008 | -0.0028 | 0.0007 | 0.0035 | 0.0004 | -0.0006 | 0.0184 | -0.0016 | 0.0035 | -360.1742 | 17.4233 | -360.4912 | 17.7149 | -360.8543 | 18.1153 | -360.9127 | 17.5712 | -352.6752 | 18.7025 | -352.7306 | 16.8464
12:05 | 2735 | 31.9923 | 198.081 | 444.2915 | 449.6794 | -18.6635 | -45.6517 | 7.4915 | 4.5652 | -1.7423 | -2.6481 | 0.4931 | -2.4548 | 7.369 | 1.2067 | 0.603 | 0.6438 | 0.9546 | 0.7211 | -131.0442 | -5.1212 | 2.8293 | 0.6468 | -5.4929 | -4.1724 | 2.3832 |  | 0.3567 | -1.64 | 4.0162 | 3.3638 | 3.3495 | 1.0386 | 10.7152 | 14.1942 | 14.7555 | 10.9818 | -0.0001 | -0.0029 | 0.0011 | 0.0044 | 0.0007 | -0.0007 | 0.0056 | 0.0028 | -0.0205 | -360.1773 | 17.409 | -360.445 | 17.6697 | -360.7866 | 18.0865 | -360.885 | 17.5814 | -352.6937 | 18.6861 | -352.666 | 16.8299
12:05 | 2736 | 32.0263 | 198.1129 | 444.2895 | 449.642 | -18.6557 | -45.679 | 7.4787 | 4.5633 | -1.7566 | -2.8359 | 0.4856 | -2.5548 | 7.3269 | 1.1456 | 0.5999 | 0.6422 | 0.9545 | 0.7201 | -131.0224 | -5.0868 | 2.8887 | 0.5565 | -5.4933 | -4.0686 | 2.3818 |  | 0.3923 | -1.5783 | 4.0186 | 3.365 | 3.3518 | 1.0399 | 10.7314 | 14.2161 | 14.783 | 11.0674 | -0.0003 | -0.0034 | 0.0004 | 0.0033 | 0.0005 | -0.0004 | 0.0202 | -0.0104 | -0.0046 | -360.1958 | 17.4397 | -360.4758 | 17.6656 | -360.7835 | 18.0721 | -360.8297 | 17.5732 | -352.7183 | 18.7169 | -352.669 | 16.8156
12:05 | 2737 | 31.9863 | 198.0402 | 444.3655 | 449.7243 | -18.6964 | -45.6284 | 7.502 | 4.5205 | -1.7971 | -2.839 | 0.4669 | -2.5274 | 7.284 | 1.1445 | 0.6032 | 0.6444 | 0.9551 | 0.7195 | -131.0503 | -5.0797 | 2.8805 | 0.5065 | -5.5417 | -4.0907 | 2.3438 |  | 0.2999 | -1.7393 | 4.0165 | 3.3662 | 3.3483 | 1.0386 | 10.7023 | 14.2511 | 14.7794 | 11.0493 | -0.0002 | -0.003 | 0.0006 | 0.0042 | 0.0007 | -0.001 | 0.0256 | -0.0086 | -0.0088 | -360.1219 | 17.4439 | -360.5127 | 17.7313 | -360.885 | 18.1071 | -360.8789 | 17.5691 | -352.666 | 18.7066 | -352.7337 | 16.8669
12:05 | 2738 | 32.0426 | 198.1654 | 444.3188 | 449.6946 | -18.6815 | -45.6527 | 7.4524 | 4.4927 | -1.7697 | -2.8337 | 0.4921 | -2.5705 | 7.396 | 1.1262 | 0.6005 | 0.642 | 0.955 | 0.7197 | -130.9997 | -5.101 | 2.9603 | 0.5625 | -5.526 | -4.1233 | 2.3672 |  | 0.4274 | -1.5188 | 4.017 | 3.3665 | 3.3463 | 1.0391 | 10.7244 | 14.244 | 14.7827 | 11.0313 | -0.0005 | -0.0029 | 0.0009 | 0.0039 | 0.0008 | -0.0003 | 0.0066 | -0.0043 | -0.0343 | -360.1496 | 17.3946 | -360.4081 | 17.6738 | -360.8174 | 18.1132 | -360.8912 | 17.5712 | -352.6567 | 18.6758 | -352.6598 | 16.8197
12:05 | 2739 | 32.011 | 198.1877 | 444.2274 | 449.6776 | -18.586 | -45.5562 | 7.5193 | 4.5581 | -1.7343 | -2.8148 | 0.5121 | -2.6079 | 7.3239 | 1.1359 | 0.601 | 0.6438 | 0.9581 | 0.7206 | -130.9885 | -5.1051 | 3.0253 | 0.5488 | -5.5192 | -4.1441 | 2.336 |  | 0.4131 | -1.6318 | 4.0171 | 3.3668 | 3.3497 | 1.0396 | 10.7381 | 14.241 | 14.8176 | 11.0496 | -0.0001 | -0.0026 | 0.0006 | 0.0035 | 0.0007 | -0.0006 | 0.0174 | -0.005 | -0.0022 | -360.1835 | 17.4172 | -360.445 | 17.6697 | -360.7804 | 18.0947 | -360.9035 | 17.5794 | -352.6967 | 18.7025 | -352.6721 | 16.8053
12:05 | 2740 | 32.017 | 198.2099 | 444.2986 | 449.6226 | -18.6028 | -45.5556 | 7.4536 | 4.4869 | -1.7289 | -2.8299 | 0.4078 | -2.5779 | 7.3725 | 1.1021 | 0.6013 | 0.6434 | 0.9545 | 0.7189 | -130.9582 | -5.0492 | 2.885 | 0.5584 | -5.5414 | -4.1285 | 2.3311 |  | 0.4079 | -1.6676 | 4.0176 | 3.3664 | 3.349 | 1.0395 | 10.7313 | 14.228 | 14.8315 | 11.0666 | -0.0003 | -0.0035 | 0.0008 | 0.0035 | 0.0006 | -0.0004 | 0.0036 | -0.0187 | -0.0302 | -360.1742 | 17.4459 | -360.5343 | 17.7231 | -360.8635 | 18.0906 | -360.8543 | 17.5629 | -352.6875 | 18.7333 | -352.749 | 16.8566
12:05 | 2741 | 32.022 | 198.1846 | 444.2151 | 449.6454 | -18.6251 | -45.5629 | 7.4804 | 4.4871 | -1.7029 | -2.7354 | 0.4446 | -2.4955 | 7.3789 | 1.1209 | 0.6013 | 0.6411 | 0.9558 | 0.7196 | -131.0154 | -5.1434 | 2.9461 | 0.5358 | -5.5365 | -4.123 | 2.3282 |  | 0.4237 | -1.6751 | 4.0182 | 3.3675 | 3.3496 | 1.0397 | 10.7093 | 14.2348 | 14.7855 | 11.0623 | 0.0001 | -0.0029 | 0.001 | 0.0038 | 0.0009 | -0.0004 | 0.0146 | -0.0142 | -0.0187 | -360.1034 | 17.3761 | -360.4542 | 17.7046 | -360.8574 | 18.105 | -360.8789 | 17.5342 | -352.629 | 18.682 | -352.6629 | 16.8525
12:05 | 2742 | 31.9888 | 198.2537 | 444.2731 | 449.6162 | -18.6414 | -45.4884 | 7.4692 | 4.5005 | -1.685 | -2.853 | 0.5919 | -2.542 | 7.3892 | 1.1737 | 0.6022 | 0.6428 | 0.9567 | 0.7209 | -131.1091 | -5.1852 | 2.8651 | 0.5348 | -5.4417 | -4.1234 | 2.3511 |  | 0.4283 | -1.6287 | 4.0181 | 3.3704 | 3.351 | 1.0395 | 10.7416 | 14.2327 | 14.779 | 11.0536 | -0.0001 | -0.0025 | 0.0006 | 0.0037 | 0.0009 | -0.0003 | 0.0125 | -0.0009 | -0.013 | -360.165 | 17.3884 | -360.4235 | 17.6656 | -360.805 | 18.0988 | -360.8881 | 17.5712 | -352.6813 | 18.682 | -352.6383 | 16.8135
12:05 | 2743 | 32.0358 | 198.2248 | 444.1237 | 449.6788 | -18.547 | -45.4156 | 7.5233 | 4.5635 | -1.7575 | -2.8572 | 0.4619 | -2.5119 | 7.3346 | 1.2338 | 0.6027 | 0.6473 | 0.9591 | 0.7187 | -131.0411 | -5.0913 | 2.9146 | 0.5062 | -5.4572 | -4.143 | 2.4131 |  | 0.4014 | -1.6906 | 4.0172 | 3.3663 | 3.3487 | 1.0392 | 10.699 | 14.2241 | 14.75 | 11.0006 | -0.0003 | -0.0027 | 0.0005 | 0.0037 | 0.0001 | -0.0006 | 0.0073 | -0.0048 | -0.002 | -360.245 | 17.4459 | -360.5035 | 17.6902 | -360.8389 | 18.0865 | -360.885 | 17.5835 | -352.7183 | 18.7538 | -352.749 | 16.832
12:05 | 2744 | 32.0009 | 198.1934 | 444.1132 | 449.5795 | -18.5112 | -45.4949 | 7.4913 | 4.5735 | -1.762 | -2.8457 | 0.4158 | -2.6942 | 7.3294 | 1.1755 | 0.6009 | 0.6429 | 0.9559 | 0.7198 | -131.0311 | -5.1028 | 2.9736 | 0.499 | -5.4342 | -4.0398 | 2.4313 |  | 0.5429 | -1.655 | 4.0174 | 3.3663 | 3.3496 | 1.0391 | 10.7173 | 14.2317 | 14.7787 | 11.0464 | 0.0002 | -0.0028 | 0.0008 | 0.0041 | 0.0011 | -0.0003 | 0.0082 | -0.0121 | -0.022 | -360.1404 | 17.4192 | -360.4973 | 17.7005 | -360.8358 | 18.0763 | -360.8174 | 17.526 | -352.6444 | 18.7169 | -352.7152 | 16.8546
12:05 | 2745 | 32.0747 | 198.2471 | 444.2267 | 449.6411 | -18.6223 | -45.4827 | 7.4544 | 4.5837 | -1.6822 | -2.7419 | 0.4859 | -2.731 | 7.3398 | 1.0224 | 0.6009 | 0.6415 | 0.9561 | 0.7209 | -130.9134 | -5.0924 | 2.9933 | 0.6217 | -5.4773 | -3.9913 | 2.3811 |  | 0.4351 | -1.7128 | 4.0171 | 3.3672 | 3.3511 | 1.0409 | 10.7128 | 14.2324 | 14.7885 | 11.037 | 0.0002 | -0.0032 | 0.0006 | 0.0038 | 0.0005 | -0.0004 | -0.0065 | -0.0105 | -0.0227 | -360.1773 | 17.4048 | -360.4758 | 17.6738 | -360.842 | 18.105 | -360.882 | 17.5588 | -352.666 | 18.6984 | -352.6998 | 16.8238
12:05 | 2746 | 32.0485 | 198.2515 | 444.1955 | 449.6576 | -18.6634 | -45.4916 | 7.4923 | 4.5614 | -1.7016 | -2.7866 | 0.4668 | -2.7279 | 7.309 | 1.0118 | 0.6014 | 0.6394 | 0.9565 | 0.7195 | -130.9314 | -5.0531 | 2.9007 | 0.5647 | -5.523 | -4.0665 | 2.3598 |  | 0.4074 | -1.6213 | 4.0183 | 3.367 | 3.3499 | 1.0408 | 10.7475 | 14.2441 | 14.8243 | 11.0598 | -0.0001 | -0.0028 | 0.0006 | 0.0038 | 0.0007 | -0.001 | 0.0079 | -0.0082 | -0.0003 | -360.245 | 17.4315 | -360.4696 | 17.6553 | -360.8081 | 18.0927 | -360.9189 | 17.5999 | -352.7213 | 18.721 | -352.7213 | 16.8115
12:05 | 2747 | 32.0094 | 198.23 | 444.1185 | 449.6923 | -18.5625 | -45.5549 | 7.5253 | 4.4533 | -1.665 | -2.7413 | 0.4775 | -2.6948 | 7.4119 | 1.2176 | 0.6009 | 0.6423 | 0.9563 | 0.7202 | -130.8973 | -5.0482 | 2.9493 | 0.5887 | -5.4418 | -4.0275 | 2.3791 |  | 0.3956 | -1.5662 | 4.0161 | 3.3655 | 3.3473 | 1.0402 | 10.7162 | 14.2418 | 14.7926 | 11.0461 | 0.0002 | -0.0024 | 0.0007 | 0.004 | 0.0003 | -0.0005 | 0.0093 | -0.0069 | -0.0072 | -360.1896 | 17.4295 | -360.4881 | 17.6615 | -360.7897 | 18.0516 | -360.7989 | 17.5506 | -352.6537 | 18.7271 | -352.709 | 16.8197
12:06 | 2748 | 31.9991 | 198.2714 | 444.3165 | 449.6978 | -18.5473 | -45.5966 | 7.599 | 4.4508 | -1.6665 | -2.7324 | 0.4484 | -2.6926 | 7.4125 | 1.132 | 0.6009 | 0.6384 | 0.9562 | 0.7205 | -130.9371 | -4.993 | 2.8792 | 0.6066 | -5.4189 | -4.0641 | 2.3961 |  | 0.399 | -1.6874 | 4.0167 | 3.3646 | 3.3489 | 1.0406 | 10.7394 | 14.2416 | 14.78 | 11.0291 | 0.0001 | -0.0033 | 0.0006 | 0.0039 | 0.0006 | -0.0007 | 0.0062 | -0.0007 | -0.0191 | -360.1711 | 17.4192 | -360.5127 | 17.7046 | -360.8697 | 18.1112 | -360.8881 | 17.5588 | -352.6844 | 18.7025 | -352.709 | 16.8505
12:06 | 2749 | 31.9772 | 198.222 | 444.2621 | 449.6441 | -18.5003 | -45.3864 | 7.6119 | 4.5627 | -1.6423 | -2.6423 | 0.5812 | -2.6766 | 7.4082 | 1.106 | 0.6006 | 0.6403 | 0.9521 | 0.72 | -131.0404 | -5.148 | 2.9163 | 0.5827 | -5.4945 | -4.0229 | 2.3909 |  | 0.4331 | -1.5398 | 4.0158 | 3.3636 | 3.349 | 1.0393 | 10.7324 | 14.2235 | 14.7992 | 11.0442 | 0.0004 | -0.0029 | 0.0008 | 0.0036 | 0.0006 | 0 | 0.0221 | -0.0097 | -0.0134 | -360.1927 | 17.4048 | -360.4173 | 17.6533 | -360.8174 | 18.1214 | -360.9127 | 17.5855 | -352.7429 | 18.6922 | -352.6537 | 16.8115
12:06 | 2750 | 32.0025 | 198.2498 | 444.2372 | 449.6968 | -18.564 | -45.4595 | 7.6059 | 4.537 | -1.6952 | -2.6009 | 0.5001 | -2.6433 | 7.3358 | 1.1801 | 0.6017 | 0.6365 | 0.9557 | 0.7225 | -131.1001 | -5.0982 | 2.8716 | 0.6136 | -5.4744 | -4.0598 | 2.3881 |  | 0.3781 | -1.668 | 4.0167 | 3.3644 | 3.3491 | 1.0414 | 10.7464 | 14.2197 | 14.8103 | 11.0764 | -0.0001 | -0.003 | 0.0007 | 0.0039 | 0.0006 | -0.0008 | 0.0169 | -0.0114 | 0.0035 | -360.1927 | 17.4048 | -360.4327 | 17.6328 | -360.7743 | 18.0968 | -360.8697 | 17.5794 | -352.709 | 18.7004 | -352.6475 | 16.7909
12:06 | 2751 | 32.0409 | 198.2258 | 444.2233 | 449.8101 | -18.5787 | -45.4154 | 7.5967 | 4.5266 | -1.7169 | -2.7404 | 0.4882 | -2.6197 | 7.5318 | 1.2845 | 0.6018 | 0.64 | 0.9538 | 0.7205 | -131.0333 | -5.0434 | 2.8772 | 0.5871 | -5.342 | -4.0341 | 2.4404 |  | 0.3697 | -1.7078 | 4.0161 | 3.3639 | 3.3473 | 1.0402 | 10.7106 | 14.2125 | 14.75 | 11.041 | 0 | -0.0022 | 0.0006 | 0.0039 | 0.0008 | -0.0003 | 0.0026 | -0.0039 | -0.0073 | -360.1927 | 17.4439 | -360.5127 | 17.6944 | -360.8697 | 18.1112 | -360.8727 | 17.5629 | -352.7029 | 18.7353 | -352.7183 | 16.8525
12:06 | 2752 | 32.0771 | 198.271 | 444.1142 | 449.7299 | -18.4886 | -45.3559 | 7.672 | 4.5806 | -1.6095 | -2.6259 | 0.5244 | -2.583 | 7.4539 | 1.2762 | 0.6018 | 0.6385 | 0.9507 | 0.7195 | -131.0131 | -5.0859 | 2.8525 | 0.5564 | -5.3131 | -3.9643 | 2.3881 |  | 0.42 | -1.6203 | 4.016 | 3.3616 | 3.3474 | 1.04 | 10.7232 | 14.2198 | 14.7766 | 11.0356 | -0.0002 | -0.0027 | 0.0006 | 0.0033 | 0.001 | -0.0005 | 0.0052 | -0.0152 | -0.0172 | -360.0788 | 17.3884 | -360.4912 | 17.68 | -360.842 | 18.1153 | -360.8327 | 17.5424 | -352.6321 | 18.6881 | -352.6967 | 16.8402
12:06 | 2753 | 32.0871 | 198.2489 | 444.2978 | 449.6565 | -18.4323 | -45.3267 | 7.57 | 4.5943 | -1.6551 | -2.7389 | 0.4572 | -2.5592 | 7.4476 | 1.276 | 0.6011 | 0.6371 | 0.9503 | 0.7188 | -131.0352 | -5.0203 | 2.873 | 0.5607 | -5.3203 | -3.9689 | 2.4359 |  | 0.4042 | -1.6477 | 4.0173 | 3.3655 | 3.3465 | 1.0421 | 10.7349 | 14.2311 | 14.7977 | 11.0652 | -0.0002 | -0.0033 | 0.0007 | 0.0038 | 0.0009 | -0.0006 | -0.0063 | -0.02 | -0.0265 | -360.1865 | 17.4048 | -360.4758 | 17.6738 | -360.8758 | 18.1379 | -360.8758 | 17.5712 | -352.6752 | 18.7045 | -352.6813 | 16.8381
12:06 | 2754 | 32.0845 | 198.2563 | 444.2127 | 449.6167 | -18.385 | -45.3459 | 7.7584 | 4.633 | -1.6851 | -2.7729 | 0.5059 | -2.6148 | 7.4691 | 1.1694 | 0.6016 | 0.6403 | 0.9523 | 0.7183 | -131.0682 | -5.0017 | 2.9239 | 0.5705 | -5.3988 | -3.9365 | 2.4255 |  | 0.3984 | -1.7182 | 4.0162 | 3.3654 | 3.3484 | 1.0414 | 10.7197 | 14.2163 | 14.7899 | 11.0497 | 0 | -0.003 | 0.0005 | 0.004 | 0.0006 | -0.0005 | 0.0025 | -0.0181 | 0.0082 | -360.1681 | 17.4233 | -360.5004 | 17.6492 | -360.7866 | 18.1173 | -360.9097 | 17.5712 | -352.7121 | 18.7292 | -352.706 | 16.8115
12:06 | 2755 | 32.1047 | 198.2571 | 444.2634 | 449.6121 | -18.4212 | -45.2676 | 7.7689 | 4.5443 | -1.7685 | -2.68 | 0.4966 | -2.7014 | 7.3859 | 1.1719 | 0.6028 | 0.6411 | 0.9518 | 0.7196 | -131.0751 | -5.1193 | 3.0255 | 0.4867 | -5.4162 | -4.0157 | 2.4179 |  | 0.4931 | -1.5913 | 4.0176 | 3.3672 | 3.352 | 1.041 | 10.7186 | 14.2266 | 14.8232 | 11.0428 | -0.0006 | -0.0029 | 0.0005 | 0.0036 | 0.0009 | -0.0008 | 0.0062 | -0.0106 | -0.0053 | -360.1804 | 17.4418 | -360.4881 | 17.6656 | -360.8081 | 18.0927 | -360.8358 | 17.5404 | -352.6875 | 18.7271 | -352.6752 | 16.8258
12:06 | 2756 | 32.1834 | 198.3715 | 444.3411 | 449.7025 | -18.3058 | -45.2001 | 7.8702 | 4.6126 | -1.8447 | -2.7914 | 0.4848 | -2.7446 | 7.38 | 1.06 | 0.6027 | 0.6414 | 0.9582 | 0.7193 | -131.1306 | -5.0264 | 2.8882 | 0.4816 | -5.3795 | -3.9738 | 2.3312 |  | 0.4107 | -1.6343 | 4.0186 | 3.3638 | 3.3501 | 1.0401 | 10.7475 | 14.2383 | 14.7954 | 11.0424 | -0.0001 | -0.0028 | 0.0005 | 0.0033 | 0.0005 | -0.0001 | 0.0047 | -0.001 | -0.0194 | -360.1804 | 17.4131 | -360.5127 | 17.6964 | -360.842 | 18.1296 | -360.8758 | 17.5568 | -352.6567 | 18.721 | -352.7521 | 16.8402
12:06 | 2757 | 32.1805 | 198.263 | 444.2065 | 449.6958 | -18.3971 | -45.2071 | 7.8573 | 4.5601 | -1.8966 | -2.777 | 0.5004 | -2.6217 | 7.4159 | 1.067 | 0.6024 | 0.6418 | 0.9583 | 0.7196 | -131.1461 | -5.0968 | 2.8661 | 0.5024 | -5.4223 | -3.9687 | 2.4384 |  | 0.4615 | -1.6384 | 4.0168 | 3.3673 | 3.3514 | 1.0402 | 10.7336 | 14.236 | 14.781 | 11.0403 | 0.0004 | -0.0031 | 0.0006 | 0.0035 | 0.0007 | -0.001 | 0.0043 | -0.004 | 0.0095 | -360.1773 | 17.3966 | -360.4142 | 17.6492 | -360.8081 | 18.1132 | -360.8481 | 17.5424 | -352.6567 | 18.6922 | -352.6506 | 16.8156
12:06 | 2758 | 32.1562 | 198.2672 | 444.229 | 449.7329 | -18.4694 | -45.3586 | 7.842 | 4.5649 | -1.8999 | -2.9422 | 0.4843 | -2.6884 | 7.3787 | 1.1469 | 0.6011 | 0.6388 | 0.9532 | 0.7189 | -131.0616 | -5.0237 | 2.8693 | 0.4087 | -5.3808 | -3.9887 | 2.4056 |  | 0.5009 | -1.6544 | 4.0173 | 3.3691 | 3.3498 | 1.0411 | 10.7197 | 14.2106 | 14.7909 | 11.0666 | 0.0001 | -0.0032 | 0.0006 | 0.0033 | 0.0008 | -0.0001 | 0.0034 | -0.0145 | -0.0213 | -360.205 | 17.4213 | -360.4942 | 17.6759 | -360.8389 | 18.1173 | -360.9097 | 17.5629 | -352.6906 | 18.7148 | -352.6937 | 16.8238
12:06 | 2759 | 32.2345 | 198.2808 | 444.288 | 449.817 | -18.3987 | -45.3748 | 7.7979 | 4.6179 | -1.809 | -2.8913 | 0.5118 | -2.6709 | 7.3522 | 1.0975 | 0.6013 | 0.6404 | 0.9541 | 0.7214 | -131.0526 | -5.0576 | 2.8154 | 0.4177 | -5.3417 | -4.0104 | 2.3816 |  | 0.4684 | -1.6311 | 4.018 | 3.3662 | 3.3486 | 1.0399 | 10.7244 | 14.2555 | 14.7943 | 11.0255 | -0.0006 | -0.0027 | 0.0007 | 0.0039 | 0.0007 | -0.0006 | -0.0006 | -0.0063 | -0.0166 | -360.165 | 17.4172 | -360.485 | 17.6492 | -360.8204 | 18.1112 | -360.8635 | 17.5465 | -352.6629 | 18.721 | -352.7029 | 16.8176
12:06 | 2760 | 32.2187 | 198.3501 | 444.2443 | 449.8531 | -18.4256 | -45.3232 | 7.8267 | 4.6688 | -1.7614 | -2.8269 | 0.4115 | -2.7359 | 7.3498 | 1.0836 | 0.6002 | 0.6396 | 0.9536 | 0.7205 | -131.058 | -4.9669 | 2.7862 | 0.4251 | -5.4257 | -4.0243 | 2.3302 |  | 0.4708 | -1.6805 | 4.0178 | 3.3681 | 3.352 | 1.0389 | 10.7255 | 14.2394 | 14.7957 | 11.0381 | -0.0006 | -0.003 | 0.0006 | 0.0037 | 0.0004 | -0.0008 | -0.0106 | -0.015 | -0.0153 | -360.1619 | 17.3905 | -360.4758 | 17.6738 | -360.8174 | 18.1214 | -360.8912 | 17.5506 | -352.6629 | 18.6984 | -352.666 | 16.8299
12:06 | 2761 | 32.2305 | 198.2631 | 444.2616 | 449.7243 | -18.5108 | -45.4644 | 7.8185 | 4.6572 | -1.8232 | -2.8425 | 0.4585 | -2.6773 | 7.3886 | 1.0818 | 0.6013 | 0.6417 | 0.9544 | 0.7202 | -131.0852 | -5.06 | 2.8064 | 0.5097 | -5.3233 | -3.9398 | 2.4036 |  | 0.4889 | -1.716 | 4.0184 | 3.3657 | 3.3493 | 1.041 | 10.7739 | 14.2481 | 14.82 | 11.0734 | 0.0004 | -0.0027 | 0.001 | 0.0042 | 0.0013 | -0.0004 | 0.0051 | -0.0074 | -0.0087 | -360.1558 | 17.4131 | -360.4789 | 17.6636 | -360.805 | 18.1399 | -360.9035 | 17.5568 | -352.6813 | 18.7087 | -352.6906 | 16.8217
12:06 | 2762 | 32.1872 | 198.2018 | 444.2752 | 449.725 | -18.5322 | -45.4564 | 7.8752 | 4.7384 | -1.8266 | -2.7026 | 0.4141 | -2.6443 | 7.3537 | 1.1711 | 0.6022 | 0.6424 | 0.957 | 0.7208 | -131.0202 | -5.029 | 2.7808 | 0.3738 | -5.3502 | -4.0199 | 2.3246 |  | 0.4932 | -1.6796 | 4.0172 | 3.3642 | 3.3515 | 1.0387 | 10.7035 | 14.2406 | 14.7739 | 11.0508 | -0.0005 | -0.0036 | 0.0012 | 0.0045 | 0.0008 | -0.0009 | -0.0043 | -0.0042 | -0.0077 | -360.1896 | 17.411 | -360.4542 | 17.6512 | -360.7897 | 18.0968 | -360.8666 | 17.5486 | -352.6506 | 18.7128 | -352.6721 | 16.8032
12:06 | 2763 | 32.1852 | 198.3009 | 444.2647 | 449.8063 | -18.5269 | -45.4333 | 7.8808 | 4.6866 | -1.8479 | -2.7832 | 0.4338 | -2.6285 | 7.4002 | 1.1249 | 0.6013 | 0.6416 | 0.9533 | 0.72 | -131.0183 | -5.0448 | 2.8367 | 0.3798 | -5.3722 | -4.1472 | 2.3157 |  | 0.5067 | -1.674 | 4.0161 | 3.3674 | 3.3537 | 1.041 | 10.7162 | 14.2419 | 14.7879 | 11.0515 | -0.0001 | -0.0026 | 0.0008 | 0.0039 | 0.0007 | -0.0003 | 0.0099 | 0.0033 | 0.0093 | -360.2081 | 17.4377 | -360.5435 | 17.6985 | -360.8727 | 18.1194 | -360.8481 | 17.5527 | -352.706 | 18.7415 | -352.6998 | 16.8464
12:06 | 2764 | 32.1738 | 198.3883 | 444.318 | 449.7673 | -18.5316 | -45.4663 | 7.7716 | 4.6974 | -1.776 | -2.6882 | 0.4254 | -2.622 | 7.4138 | 1.0469 | 0.6006 | 0.6452 | 0.9579 | 0.7205 | -131.0615 | -5.0358 | 2.8087 | 0.4875 | -5.3084 | -4.0371 | 2.2879 |  | 0.5474 | -1.6686 | 4.0163 | 3.3674 | 3.3509 | 1.0414 | 10.714 | 14.2103 | 14.783 | 11.0443 | -0.0002 | -0.0028 | 0.0004 | 0.0036 | 0.0006 | -0.0005 | 0.0105 | -0.0072 | -0.0088 | -360.1435 | 17.4048 | -360.5096 | 17.68 | -360.845 | 18.1255 | -360.8727 | 17.5239 | -352.6383 | 18.7128 | -352.7029 | 16.832
12:06 | 2765 | 32.1969 | 198.3195 | 444.3165 | 449.7076 | -18.5652 | -45.5545 | 7.7223 | 4.6383 | -1.7633 | -2.8172 | 0.3732 | -2.5244 | 7.4681 | 1.1019 | 0.6011 | 0.6437 | 0.9562 | 0.7196 | -130.9965 | -5.0019 | 2.8998 | 0.59 | -5.3266 | -3.9916 | 2.3205 |  | 0.5017 | -1.5451 | 4.017 | 3.3663 | 3.35 | 1.0397 | 10.7279 | 14.2127 | 14.78 | 11.0291 | -0.0001 | -0.003 | 0.0009 | 0.0037 | 0.0006 | -0.0003 | -0.0051 | -0.0069 | -0.0325 | -360.1835 | 17.4048 | -360.4512 | 17.6697 | -360.7958 | 18.1276 | -360.9004 | 17.5712 | -352.6875 | 18.7148 | -352.6444 | 16.8094
12:06 | 2766 | 32.1699 | 198.3673 | 444.3146 | 449.8064 | -18.5651 | -45.4651 | 7.7457 | 4.6672 | -1.797 | -2.7678 | 0.3607 | -2.629 | 7.3974 | 1.1095 | 0.6022 | 0.6421 | 0.9534 | 0.7204 | -131.0117 | -5.0719 | 2.8956 | 0.6076 | -5.3774 | -4.1015 | 2.325 |  | 0.5183 | -1.6595 | 4.0164 | 3.3677 | 3.3477 | 1.0419 | 10.7324 | 14.2351 | 14.8281 | 11.0904 | 0.0003 | -0.0031 | 0.0007 | 0.0034 | 0.0008 | -0.0007 | 0.0126 | -0.0159 | 0.0057 | -360.2265 | 17.4541 | -360.5312 | 17.6738 | -360.8112 | 18.1029 | -360.8974 | 17.565 | -352.746 | 18.762 | -352.7337 | 16.834
12:06 | 2767 | 32.2693 | 198.4358 | 444.3054 | 449.8196 | -18.4573 | -45.5389 | 7.6822 | 4.7319 | -1.6615 | -2.809 | 0.4239 | -2.6751 | 7.4042 | 1.0952 | 0.6023 | 0.6448 | 0.9554 | 0.7201 | -131.045 | -5.218 | 2.8267 | 0.6347 | -5.3939 | -4.0092 | 2.3383 |  | 0.4689 | -1.6429 | 4.0179 | 3.3672 | 3.3482 | 1.0392 | 10.7117 | 14.2195 | 14.7803 | 11.0652 | -0.0002 | -0.0027 | 0.0005 | 0.0036 | 0.0006 | -0.0002 | 0.0037 | -0.0089 | 0.0011 | -360.1404 | 17.409 | -360.4727 | 17.6759 | -360.842 | 18.0886 | -360.8204 | 17.5239 | -352.666 | 18.721 | -352.6937 | 16.834
12:06 | 2768 | 32.2678 | 198.4584 | 444.438 | 449.9911 | -18.4694 | -45.4732 | 7.8656 | 4.6848 | -1.6852 | -2.8361 | 0.4189 | -2.64 | 7.4301 | 1.2594 | 0.6023 | 0.6422 | 0.9481 | 0.7193 | -131.0099 | -5.2145 | 2.8477 | 0.5853 | -5.4701 | -3.9812 | 2.322 |  | 0.4277 | -1.5843 | 4.0169 | 3.3686 | 3.3429 | 1.0393 | 10.7093 | 14.229 | 14.7623 | 10.9988 | -0.0001 | -0.0022 | 0.0007 | 0.0039 | 0.0007 | -0.001 | 0.0037 | -0.0082 | 0.0072 | -360.2204 | 17.4007 | -360.4758 | 17.6882 | -360.8481 | 18.1379 | -360.9158 | 17.5424 | -352.6475 | 18.7169 | -352.669 | 16.8381
12:06 | 2769 | 32.2023 | 198.486 | 444.3512 | 449.8038 | -18.5726 | -45.4471 | 7.8659 | 4.6826 | -1.6608 | -2.8344 | 0.4407 | -2.6767 | 7.4399 | 1.1504 | 0.601 | 0.6435 | 0.952 | 0.7196 | -131.0164 | -5.0788 | 2.867 | 0.5558 | -5.4859 | -4.0384 | 2.3913 |  | 0.4432 | -1.5577 | 4.0161 | 3.3616 | 3.3461 | 1.04 | 10.7231 | 14.2142 | 14.795 | 11.0525 | 0.0002 | -0.0027 | 0.0007 | 0.0038 | 0.0008 | -0.0005 | 0.0093 | 0.0031 | -0.0146 | -360.1958 | 17.411 | -360.4542 | 17.6553 | -360.8297 | 18.1235 | -360.9374 | 17.5876 | -352.7275 | 18.7271 | -352.6906 | 16.8238
12:06 | 2770 | 32.2578 | 198.4388 | 444.3904 | 449.8679 | -18.4838 | -45.419 | 7.856 | 4.6583 | -1.6118 | -2.7501 | 0.4557 | -2.6176 | 7.4329 | 1.2904 | 0.6015 | 0.6443 | 0.955 | 0.7202 | -130.9385 | -4.9882 | 2.9382 | 0.5863 | -5.4778 | -4.0758 | 2.307 |  | 0.4082 | -1.6457 | 4.0166 | 3.3645 | 3.3469 | 1.0409 | 10.7302 | 14.244 | 14.7711 | 11.0544 | 0.0003 | -0.0028 | 0.0006 | 0.0043 | 0.0008 | -0.0006 | 0.0202 | -0.0268 | -0.0174 | -360.1742 | 17.4192 | -360.4573 | 17.6492 | -360.7558 | 18.0947 | -360.8574 | 17.5404 | -352.6844 | 18.723 | -352.6906 | 16.8135
12:06 | 2771 | 32.2447 | 198.459 | 444.309 | 449.8764 | -18.4773 | -45.5241 | 7.7841 | 4.6987 | -1.6506 | -2.7816 | 0.3259 | -2.6631 | 7.4988 | 1.2351 | 0.6012 | 0.6423 | 0.9542 | 0.7183 | -130.9725 | -5.0173 | 2.8924 | 0.5969 | -5.4858 | -4.0771 | 2.3598 |  | 0.4456 | -1.6333 | 4.0167 | 3.3637 | 3.3502 | 1.0404 | 10.752 | 14.249 | 14.7845 | 11.0348 | 0.0001 | -0.0028 | 0.0008 | 0.0041 | 0.0011 | -0.0001 | 0.0053 | -0.0181 | 0.0005 | -360.1435 | 17.4213 | -360.525 | 17.6985 | -360.8758 | 18.1153 | -360.8574 | 17.5321 | -352.6629 | 18.7333 | -352.7306 | 16.8525
12:06 | 2772 | 32.2814 | 198.4856 | 444.313 | 449.8567 | -18.4875 | -45.4946 | 7.7691 | 4.7579 | -1.6831 | -2.8132 | 0.3542 | -2.7081 | 7.3734 | 1.2668 | 0.6016 | 0.6425 | 0.953 | 0.7217 | -131.019 | -5.0505 | 2.791 | 0.391 | -5.6103 | -4.0463 | 2.3316 |  | 0.4872 | -1.6368 | 4.0164 | 3.3671 | 3.348 | 1.0418 | 10.7602 | 14.2569 | 14.8488 | 11.0782 | -0.0002 | -0.0025 | 0.0004 | 0.0032 | 0.0007 | -0.0006 | 0.0125 | -0.0094 | -0.0097 | -360.1465 | 17.3905 | -360.4942 | 17.6923 | -360.8604 | 18.1481 | -360.9281 | 17.5404 | -352.6537 | 18.7128 | -352.6875 | 16.8607
12:06 | 2773 | 32.2792 | 198.4428 | 444.3844 | 449.8825 | -18.4208 | -45.292 | 7.8898 | 4.7604 | -1.5349 | -2.8755 | 0.4055 | -2.6143 | 7.3812 | 1.2565 | 0.6021 | 0.6428 | 0.9542 | 0.7196 | -130.9119 | -5.0993 | 2.8901 | 0.3293 | -5.5577 | -4.0681 | 2.3305 |  | 0.5235 | -1.6991 | 4.0163 | 3.3651 | 3.3471 | 1.0403 | 10.7152 | 14.2287 | 14.7775 | 11.0284 | 0.0002 | -0.0024 | 0.001 | 0.0037 | 0.0006 | -0.0008 | 0.0187 | -0.001 | -0.0049 | -360.1281 | 17.3884 | -360.4327 | 17.6656 | -360.8143 | 18.1132 | -360.8758 | 17.5424 | -352.666 | 18.6922 | -352.626 | 16.8238
12:06 | 2774 | 32.2509 | 198.3726 | 444.3596 | 449.8495 | -18.4493 | -45.3634 | 7.9292 | 4.7 | -1.5511 | -2.9738 | 0.308 | -2.6237 | 7.3804 | 1.2248 | 0.6034 | 0.6431 | 0.9551 | 0.7209 | -131.0556 | -5.1246 | 2.8915 | 0.3991 | -5.523 | -4.0681 | 2.3155 |  | 0.5476 | -1.6345 | 4.0155 | 3.3674 | 3.3504 | 1.0414 | 10.7024 | 14.2105 | 14.7494 | 10.9919 | 0.0001 | -0.0032 | 0.0011 | 0.0037 | 0.001 | 0.0001 | 0.0104 | -0.0134 | -0.0243 | -360.2204 | 17.45 | -360.5096 | 17.6718 | -360.845 | 18.1296 | -360.882 | 17.565 | -352.7152 | 18.7518 | -352.709 | 16.832
12:06 | 2775 | 32.2362 | 198.3608 | 444.2303 | 449.8255 | -18.3469 | -45.4099 | 7.9589 | 4.6657 | -1.5686 | -2.8048 | 0.3993 | -2.6817 | 7.3179 | 1.1212 | 0.6027 | 0.6429 | 0.9549 | 0.7211 | -131.0978 | -5.0495 | 2.8349 | 0.3566 | -5.4874 | -4.1234 | 2.3751 |  | 0.5528 | -1.5907 | 4.016 | 3.3668 | 3.3492 | 1.0403 | 10.7152 | 14.194 | 14.7718 | 11.0284 | -0.0001 | -0.003 | 0.0007 | 0.0041 | 0.0009 | -0.0008 | 0.0043 | -0.0088 | -0.014 | -360.1373 | 17.4254 | -360.5127 | 17.6923 | -360.8512 | 18.0988 | -360.8081 | 17.5424 | -352.6844 | 18.7312 | -352.746 | 16.8669
12:06 | 2776 | 32.2325 | 198.3537 | 444.3492 | 449.8683 | -18.3685 | -45.2811 | 8.0177 | 4.6157 | -1.5619 | -2.7543 | 0.3761 | -2.5631 | 7.4378 | 1.2064 | 0.6025 | 0.6417 | 0.9545 | 0.7216 | -131.0853 | -4.9621 | 2.8947 | 0.4436 | -5.5263 | -4.0104 | 2.2974 |  | 0.5593 | -1.578 | 4.0169 | 3.3672 | 3.3488 | 1.0416 | 10.7129 | 14.2091 | 14.7527 | 11.0085 | -0.0007 | -0.0031 | 0.0009 | 0.0037 | 0.0003 | -0.0005 | 0.0026 | -0.0153 | -0.0039 | -360.1496 | 17.4007 | -360.4758 | 17.6677 | -360.8112 | 18.1112 | -360.8666 | 17.5219 | -352.6229 | 18.7087 | -352.6906 | 16.8279
12:06 | 2777 | 32.2705 | 198.4394 | 444.272 | 449.8984 | -18.4763 | -45.3348 | 7.9763 | 4.6748 | -1.5024 | -2.7953 | 0.3766 | -2.5199 | 7.4053 | 1.2316 | 0.6035 | 0.6407 | 0.9567 | 0.7209 | -131.0589 | -5.0987 | 2.8268 | 0.524 | -5.5351 | -4.0517 | 2.2726 |  | 0.4935 | -1.6961 | 4.0169 | 3.3641 | 3.3508 | 1.0405 | 10.7313 | 14.2222 | 14.7678 | 11.0435 | -0.0005 | -0.0027 | 0.0008 | 0.004 | 0.0014 | -0.0005 | 0.004 | -0.0059 | 0.0014 | -360.2081 | 17.411 | -360.4819 | 17.6902 | -360.8358 | 18.1214 | -360.9189 | 17.5691 | -352.6813 | 18.723 | -352.6844 | 16.8381
12:06 | 2778 | 32.2806 | 198.3843 | 444.2466 | 449.8882 | -18.47 | -45.2394 | 7.8514 | 4.6942 | -1.447 | -2.6459 | 0.3428 | -2.6684 | 7.3802 | 1.1452 | 0.6039 | 0.6414 | 0.9576 | 0.7214 | -131.0521 | -5.0597 | 2.8212 | 0.5257 | -5.5448 | -4.0869 | 2.2858 |  | 0.5122 | -1.7228 | 4.0173 | 3.3679 | 3.3494 | 1.0408 | 10.7071 | 14.1974 | 14.769 | 11.0609 | 0.0002 | -0.0031 | 0.0007 | 0.0037 | 0.0004 | -0.0005 | 0.0151 | 0.0001 | -0.0025 | -360.1865 | 17.4172 | -360.4635 | 17.6512 | -360.7681 | 18.1091 | -360.8666 | 17.5506 | -352.7183 | 18.7374 | -352.7029 | 16.8299
12:06 | 2779 | 32.2268 | 198.3581 | 444.3449 | 449.8962 | -18.4383 | -45.1595 | 7.8415 | 4.7207 | -1.3796 | -2.672 | 0.4415 | -2.6461 | 7.4103 | 1.0948 | 0.6023 | 0.6413 | 0.9522 | 0.7203 | -131.02 | -4.921 | 2.8599 | 0.5596 | -5.5351 | -4.0347 | 2.2121 |  | 0.5636 | -1.6466 | 4.0163 | 3.3662 | 3.3472 | 1.0409 | 10.707 | 14.2094 | 14.8011 | 11.0713 | -0.0001 | -0.0033 | 0.0006 | 0.0038 | 0.0014 | -0.0003 | 0.0076 | -0.0125 | 0.0036 | -360.1619 | 17.4151 | -360.4727 | 17.6738 | -360.8266 | 18.1091 | -360.8543 | 17.5383 | -352.6537 | 18.7148 | -352.6598 | 16.8381
12:06 | 2780 | 32.1129 | 198.3845 | 444.2201 | 449.8163 | -18.3798 | -45.1645 | 7.8323 | 4.6866 | -1.4392 | -2.7604 | 0.426 | -2.5622 | 7.386 | 1.2322 | 0.6021 | 0.6414 | 0.9558 | 0.7224 | -131.0551 | -5.0119 | 2.8071 | 0.4679 | -5.5106 | -4.1054 | 2.3018 |  | 0.5396 | -1.6891 | 4.0162 | 3.3679 | 3.3486 | 1.042 | 10.7614 | 14.2579 | 14.797 | 11.0623 | -0.0002 | -0.0025 | 0.0005 | 0.0035 | 0.0005 | -0.0003 | 0.0021 | -0.0185 | -0.014 | -360.1804 | 17.4192 | -360.5066 | 17.6861 | -360.842 | 18.1379 | -360.9127 | 17.5588 | -352.6844 | 18.7292 | -352.6967 | 16.8464
12:06 | 2781 | 32.163 | 198.472 | 444.2209 | 449.9218 | -18.4009 | -45.1953 | 7.8378 | 4.6467 | -1.5108 | -2.6811 | 0.4365 | -2.4783 | 7.3775 | 1.1316 | 0.6021 | 0.6428 | 0.9557 | 0.7214 | -131.0722 | -4.8737 | 2.9327 | 0.5122 | -5.5354 | -4.0262 | 2.3281 |  | 0.4984 | -1.7615 | 4.0163 | 3.3684 | 3.3498 | 1.0406 | 10.7326 | 14.2056 | 14.8007 | 11.0631 | -0.0005 | -0.003 | 0.0007 | 0.0037 | 0.0006 | -0.0007 | 0.0111 | -0.0025 | -0.0027 | -360.1527 | 17.3987 | -360.4604 | 17.6594 | -360.805 | 18.1132 | -360.8697 | 17.5445 | -352.6629 | 18.7169 | -352.6875 | 16.8361
12:06 | 2782 | 32.2695 | 198.4526 | 444.3422 | 449.8098 | -18.3356 | -45.0994 | 7.9444 | 4.6877 | -1.5617 | -2.7661 | 0.4079 | -2.4889 | 7.3799 | 1.113 | 0.6026 | 0.6434 | 0.9539 | 0.7235 | -131.0645 | -4.9773 | 2.8483 | 0.4953 | -5.5511 | -4.0195 | 2.3035 |  | 0.4741 | -1.7606 | 4.0168 | 3.3657 | 3.3465 | 1.0406 | 10.7011 | 14.2096 | 14.7964 | 11.0478 | 0.0002 | -0.0029 | 0.0009 | 0.0036 | 0.001 | -0.0007 | 0.0225 | -0.0126 | -0.0038 | -360.1681 | 17.4254 | -360.5096 | 17.6656 | -360.805 | 18.1173 | -360.8727 | 17.5424 | -352.6537 | 18.7169 | -352.6998 | 16.8299
12:06 | 2783 | 32.2519 | 198.424 | 444.3041 | 449.8123 | -18.3431 | -45.1479 | 7.892 | 4.6003 | -1.5972 | -2.7876 | 0.3719 | -2.5468 | 7.4434 | 1.2292 | 0.6025 | 0.6468 | 0.9533 | 0.7223 | -130.9969 | -4.8822 | 2.9314 | 0.4394 | -5.6436 | -4.0645 | 2.254 |  | 0.4205 | -1.7228 | 4.0158 | 3.3678 | 3.3482 | 1.0407 | 10.7453 | 14.2299 | 14.8021 | 11.0237 | 0 | -0.0037 | 0.0007 | 0.0038 | 0.0004 | -0.0002 | 0.022 | -0.01 | 0.0163 | -360.1804 | 17.4151 | -360.4942 | 17.6902 | -360.8758 | 18.1276 | -360.8881 | 17.5609 | -352.6783 | 18.7251 | -352.706 | 16.8607
12:06 | 2784 | 32.3464 | 198.4218 | 444.2345 | 449.7585 | -18.294 | -45.1891 | 7.8733 | 4.6673 | -1.6282 | -2.7609 | 0.3478 | -2.527 | 7.4141 | 1.2883 | 0.6034 | 0.6469 | 0.9549 | 0.7218 | -130.9925 | -4.8742 | 2.9494 | 0.6598 | -5.5244 | -3.9847 | 2.3284 |  | 0.4403 | -1.7384 | 4.0149 | 3.3679 | 3.3453 | 1.0438 | 10.722 | 14.2186 | 14.7521 | 11.0287 | 0 | -0.003 | 0.0009 | 0.0039 | 0.0008 | -0.0007 | 0.023 | -0.014 | -0.0194 | -360.1527 | 17.3966 | -360.4512 | 17.6553 | -360.8174 | 18.1071 | -360.8697 | 17.5424 | -352.6444 | 18.7004 | -352.6598 | 16.834
12:06 | 2785 | 32.3812 | 198.4081 | 444.3002 | 449.8077 | -18.2161 | -45.1938 | 7.9347 | 4.7257 | -1.5658 | -2.7446 | 0.4073 | -2.582 | 7.329 | 1.2238 | 0.6015 | 0.6433 | 0.9554 | 0.7209 | -130.9749 | -4.8687 | 2.9523 | 0.6456 | -5.5774 | -4.1089 | 2.3047 |  | 0.5589 | -1.5848 | 4.0163 | 3.3675 | 3.347 | 1.0432 | 10.7449 | 14.2425 | 14.8153 | 11.0846 | -0.0003 | -0.0026 | 0.001 | 0.004 | 0.0011 | -0.0001 | 0.0232 | -0.0228 | -0.0009 | -360.2235 | 17.4295 | -360.485 | 17.6759 | -360.8358 | 18.1173 | -360.8758 | 17.5609 | -352.7337 | 18.7395 | -352.6967 | 16.834
12:06 | 2786 | 32.2616 | 198.3991 | 444.2753 | 449.8097 | -18.2882 | -45.2128 | 7.889 | 4.7921 | -1.5522 | -2.7651 | 0.4568 | -2.6604 | 7.2903 | 1.0789 | 0.6025 | 0.6462 | 0.9538 | 0.7219 | -130.9902 | -4.9286 | 2.8215 | 0.6433 | -5.4855 | -4.0496 | 2.2985 |  | 0.4878 | -1.6088 | 4.0163 | 3.3675 | 3.3489 | 1.0421 | 10.7244 | 14.2265 | 14.7643 | 11.0374 | -0.0005 | -0.0031 | 0.0002 | 0.0035 | 0.0009 | -0.0008 | 0.0122 | -0.0002 | -0.0046 | -360.1281 | 17.4254 | -360.5096 | 17.682 | -360.8389 | 18.1132 | -360.885 | 17.5404 | -352.6906 | 18.7251 | -352.7306 | 16.8689
12:06 | 2787 | 32.3143 | 198.4253 | 444.2494 | 449.8007 | -18.3641 | -45.2513 | 7.8785 | 4.8042 | -1.4581 | -2.6059 | 0.464 | -2.6549 | 7.3084 | 1.0944 | 0.6004 | 0.645 | 0.9529 | 0.7211 | -130.9062 | -4.9055 | 2.8943 | 0.6016 | -5.5977 | -4.0573 | 2.2361 |  | 0.5327 | -1.618 | 4.0145 | 3.365 | 3.3488 | 1.041 | 10.7555 | 14.2352 | 14.8118 | 11.0381 | 0.0004 | -0.0026 | 0.0007 | 0.0037 | 0.0007 | -0.0005 | 0.0099 | -0.0167 | -0.0172 | -360.1096 | 17.4048 | -360.4542 | 17.6594 | -360.8081 | 18.1173 | -360.8727 | 17.5198 | -352.6198 | 18.7066 | -352.6937 | 16.834
12:06 | 2788 | 32.2706 | 198.4912 | 444.2627 | 449.8361 | -18.3463 | -45.2974 | 7.8553 | 4.7993 | -1.5551 | -2.7218 | 0.4543 | -2.6206 | 7.3373 | 1.1159 | 0.6021 | 0.6433 | 0.9507 | 0.7193 | -130.9632 | -4.9245 | 2.9175 | 0.6861 | -5.5747 | -4.019 | 2.2574 |  | 0.5721 | -1.5967 | 4.0162 | 3.3702 | 3.3504 | 1.0428 | 10.7348 | 14.2081 | 14.8045 | 11.0533 | -0.0003 | -0.0029 | 0.0001 | 0.0033 | 0.0009 | -0.0008 | 0.004 | -0.0117 | -0.0094 | -360.1711 | 17.409 | -360.4881 | 17.68 | -360.8481 | 18.1296 | -360.9251 | 17.5671 | -352.6844 | 18.7087 | -352.6752 | 16.8443
12:06 | 2789 | 32.2439 | 198.4472 | 444.268 | 449.7772 | -18.352 | -45.3085 | 7.8562 | 4.7701 | -1.416 | -2.6224 | 0.6506 | -2.6374 | 7.3798 | 1.18 | 0.6022 | 0.6432 | 0.9546 | 0.7197 | -130.9622 | -4.9445 | 2.8867 | 0.6614 | -5.5277 | -3.9276 | 2.3545 |  | 0.4997 | -1.6281 | 4.0172 | 3.3673 | 3.3463 | 1.0428 | 10.7152 | 14.2289 | 14.7786 | 11.0454 | -0.0003 | -0.0029 | 0.001 | 0.0039 | 0.0005 | 0.0001 | 0.0054 | -0.0195 | 0.0104 | -360.2173 | 17.4233 | -360.4789 | 17.6512 | -360.7866 | 18.0988 | -360.8789 | 17.5588 | -352.7244 | 18.7312 | -352.7121 | 16.8299
12:06 | 2790 | 32.2563 | 198.4524 | 444.2088 | 449.8402 | -18.3671 | -45.2187 | 7.948 | 4.7392 | -1.4732 | -2.7651 | 0.5515 | -2.616 | 7.3626 | 1.1929 | 0.6009 | 0.6459 | 0.955 | 0.7215 | -130.901 | -4.9033 | 3.0697 | 0.5266 | -5.461 | -3.9459 | 2.3727 |  | 0.5116 | -1.64 | 4.0169 | 3.3655 | 3.3468 | 1.0412 | 10.7094 | 14.1884 | 14.7439 | 11.028 | 0.0001 | -0.0024 | 0.0011 | 0.0037 | 0.0005 | -0.001 | 0.007 | -0.0102 | -0.0064 | -360.1804 | 17.4213 | -360.485 | 17.6718 | -360.8297 | 18.0906 | -360.8081 | 17.5363 | -352.6783 | 18.721 | -352.6937 | 16.8402
12:06 | 2791 | 32.3326 | 198.4749 | 444.2549 | 449.807 | -18.3125 | -45.3266 | 8.0161 | 4.7647 | -1.4995 | -2.7644 | 0.5757 | -2.634 | 7.3646 | 1.2829 | 0.6019 | 0.6444 | 0.9532 | 0.7205 | -130.91 | -4.943 | 2.9742 | 0.5534 | -5.3585 | -3.8513 | 2.3707 |  | 0.5324 | -1.6791 | 4.0162 | 3.3672 | 3.3457 | 1.042 | 10.7372 | 14.2102 | 14.7646 | 11.0678 | 0.0001 | -0.0034 | 0.0007 | 0.0036 | 0.0008 | -0.0006 | -0.0034 | -0.0055 | -0.0156 | -360.1742 | 17.4131 | -360.5035 | 17.6964 | -360.8727 | 18.1563 | -360.9097 | 17.5445 | -352.6506 | 18.723 | -352.6752 | 16.8689
12:06 | 2792 | 32.2642 | 198.4567 | 444.3615 | 449.8189 | -18.3469 | -45.1887 | 7.9926 | 4.6648 | -1.4843 | -2.7267 | 0.5852 | -2.5431 | 7.4278 | 1.2704 | 0.6026 | 0.6428 | 0.9508 | 0.7195 | -131.0035 | -4.9476 | 2.9094 | 0.5125 | -5.3754 | -3.8639 | 2.421 |  | 0.5714 | -1.615 | 4.0169 | 3.3684 | 3.3492 | 1.0425 | 10.7347 | 14.2026 | 14.8066 | 11.0699 | 0.0001 | -0.0029 | 0.0006 | 0.004 | 0.0007 | -0.0004 | 0.02 | -0.0052 | -0.0192 | -360.1865 | 17.3987 | -360.4173 | 17.6451 | -360.8358 | 18.1296 | -360.9097 | 17.5671 | -352.6906 | 18.7025 | -352.6783 | 16.8279
12:06 | 2793 | 32.3443 | 198.4912 | 444.3556 | 449.8542 | -18.3009 | -45.1154 | 8.0305 | 4.6454 | -1.4074 | -2.9178 | 0.5952 | -2.5817 | 7.4951 | 1.2892 | 0.6017 | 0.6431 | 0.9554 | 0.721 | -130.9675 | -4.969 | 2.9552 | 0.4952 | -5.2842 | -3.805 | 2.3996 |  | 0.537 | -1.6005 | 4.0163 | 3.371 | 3.3499 | 1.0437 | 10.7393 | 14.2594 | 14.8063 | 11.0626 | 0 | -0.0025 | 0.0008 | 0.0038 | 0.0008 | -0.0008 | 0.0033 | -0.0051 | -0.0188 | -360.2081 | 17.4233 | -360.4696 | 17.641 | -360.7497 | 18.0988 | -360.8666 | 17.5506 | -352.669 | 18.7148 | -352.6598 | 16.8135
12:06 | 2794 | 32.3729 | 198.5617 | 444.4183 | 449.9748 | -18.266 | -45.1233 | 8.0979 | 4.671 | -1.4077 | -2.8059 | 0.6624 | -2.5274 | 7.5227 | 1.2851 | 0.6027 | 0.6416 | 0.9545 | 0.7202 | -130.8945 | -4.941 | 2.8172 | 0.5535 | -5.3115 | -3.9747 | 2.361 |  | 0.5746 | -1.5289 | 4.0161 | 3.3628 | 3.3455 | 1.0411 | 10.7405 | 14.2315 | 14.8182 | 11.0583 | 0 | -0.0023 | 0.0004 | 0.0039 | 0.0007 | 0 | 0.018 | -0.0077 | -0.005 | -360.1773 | 17.4315 | -360.5466 | 17.6985 | -360.8604 | 18.1173 | -360.8666 | 17.5506 | -352.6906 | 18.7374 | -352.7244 | 16.8689
12:06 | 2795 | 32.3277 | 198.4848 | 444.3466 | 449.9214 | -18.3081 | -45.1303 | 8.0833 | 4.6623 | -1.4137 | -2.7679 | 0.6381 | -2.5956 | 7.57 | 1.2927 | 0.601 | 0.6435 | 0.953 | 0.7217 | -130.9392 | -4.9991 | 2.8862 | 0.6534 | -5.3493 | -3.9403 | 2.4052 |  | 0.5518 | -1.4703 | 4.0181 | 3.368 | 3.3477 | 1.0427 | 10.7405 | 14.2314 | 14.8056 | 11.0529 | 0.0002 | -0.0028 | 0.0012 | 0.0043 | 0.0011 | -0.0009 | 0.0279 | -0.014 | 0.0037 | -360.1034 | 17.372 | -360.4389 | 17.6718 | -360.8481 | 18.1255 | -360.8789 | 17.528 | -352.626 | 18.684 | -352.666 | 16.8484
12:06 | 2796 | 32.3358 | 198.4993 | 444.4261 | 449.9604 | -18.3626 | -45.1832 | 8.1354 | 4.6515 | -1.4396 | -2.8254 | 0.6679 | -2.5561 | 7.5656 | 1.2734 | 0.6025 | 0.6418 | 0.9568 | 0.7219 | -130.9484 | -4.9766 | 2.9168 | 0.6714 | -5.4017 | -3.9604 | 2.4149 |  | 0.5659 | -1.4503 | 4.017 | 3.3647 | 3.3479 | 1.0404 | 10.7197 | 14.2336 | 14.8188 | 11.0323 | -0.0003 | -0.0028 | 0.0012 | 0.0039 | 0.0008 | -0.0003 | 0.0169 | -0.0139 | -0.0087 | -360.2081 | 17.3987 | -360.4419 | 17.6574 | -360.805 | 18.1214 | -360.9004 | 17.5609 | -352.6813 | 18.7045 | -352.6567 | 16.8217
12:06 | 2797 | 32.3212 | 198.5045 | 444.2422 | 449.9674 | -18.3834 | -45.1282 | 8.0221 | 4.6915 | -1.4513 | -2.819 | 0.6333 | -2.6039 | 7.4646 | 1.2546 | 0.6032 | 0.6449 | 0.9521 | 0.7225 | -130.9535 | -4.8689 | 2.899 | 0.6425 | -5.4136 | -3.9811 | 2.4498 |  | 0.6203 | -1.5047 | 4.017 | 3.3659 | 3.3448 | 1.0429 | 10.7151 | 14.2117 | 14.7334 | 11.0334 | -0.0002 | -0.0026 | 0.0008 | 0.0034 | 0.0009 | -0.0008 | 0.0223 | 0.0033 | 0.0047 | -360.2481 | 17.4439 | -360.5066 | 17.6718 | -360.7897 | 18.105 | -360.8912 | 17.565 | -352.7337 | 18.7579 | -352.7583 | 16.8484
12:06 | 2798 | 32.2969 | 198.5585 | 444.299 | 449.9186 | -18.3313 | -45.1523 | 7.9557 | 4.6279 | -1.4326 | -2.7886 | 0.564 | -2.5878 | 7.4841 | 1.1126 | 0.6032 | 0.645 | 0.956 | 0.7209 | -130.9549 | -4.8702 | 2.9046 | 0.564 | -5.433 | -3.9883 | 2.3954 |  | 0.4834 | -1.5705 | 4.0147 | 3.3642 | 3.348 | 1.042 | 10.6956 | 14.1974 | 14.7517 | 11.0147 | -0.0007 | -0.003 | 0.0007 | 0.0037 | 0.0005 | -0.0007 | 0.0076 | -0.0027 | -0.0095 | -360.1219 | 17.4151 | -360.5066 | 17.6882 | -360.8358 | 18.0886 | -360.8297 | 17.5116 | -352.6475 | 18.7087 | -352.7029 | 16.8546
12:06 | 2799 | 32.3219 | 198.5195 | 444.408 | 449.9444 | -18.3947 | -45.1693 | 8.0406 | 4.683 | -1.5034 | -2.745 | 0.5456 | -2.5555 | 7.4663 | 1.1424 | 0.6011 | 0.6399 | 0.9519 | 0.7201 | -130.9103 | -4.9271 | 2.9062 | 0.5923 | -5.4113 | -3.9916 | 2.395 |  | 0.553 | -1.4892 | 4.0176 | 3.367 | 3.3469 | 1.0431 | 10.7117 | 14.2197 | 14.7698 | 11.0129 | 0 | -0.003 | 0.0007 | 0.0039 | 0.001 | -0.0005 | 0.0108 | -0.0117 | 0.0077 | -360.1681 | 17.4172 | -360.5035 | 17.6759 | -360.8635 | 18.1379 | -360.8912 | 17.5547 | -352.6321 | 18.7087 | -352.6967 | 16.8566
12:06 | 2800 | 32.3686 | 198.5837 | 444.4068 | 449.9717 | -18.29 | -45.16 | 8.0328 | 4.6484 | -1.442 | -2.7492 | 0.58 | -2.5586 | 7.5578 | 1.2033 | 0.6033 | 0.6457 | 0.956 | 0.7218 | -130.8486 | -5.0113 | 2.8766 | 0.5509 | -5.4192 | -4.0058 | 2.3523 |  | 0.5867 | -1.5003 | 4.0167 | 3.3686 | 3.3487 | 1.0415 | 10.7175 | 14.2136 | 14.7908 | 11.0309 | 0 | -0.0034 | 0.0005 | 0.0038 | 0.0008 | -0.0007 | 0.0159 | -0.0063 | -0.0168 | -360.1927 | 17.4028 | -360.4604 | 17.6615 | -360.7989 | 18.1379 | -360.9066 | 17.5773 | -352.706 | 18.7169 | -352.6721 | 16.8381
12:06 | 2801 | 32.384 | 198.5152 | 444.3874 | 449.8507 | -18.2988 | -45.0981 | 7.9805 | 4.6891 | -1.4753 | -2.7501 | 0.5716 | -2.5017 | 7.5481 | 1.2508 | 0.6014 | 0.6431 | 0.9522 | 0.7206 | -130.8581 | -4.8993 | 2.9102 | 0.6282 | -5.455 | -4.0324 | 2.4395 |  | 0.5661 | -1.5567 | 4.0159 | 3.3661 | 3.3501 | 1.0416 | 10.7441 | 14.2289 | 14.7902 | 11.0338 | -0.0005 | -0.0029 | 0.0006 | 0.004 | 0.0004 | -0.0005 | 0.016 | -0.0043 | -0.0114 | -360.205 | 17.4172 | -360.4789 | 17.6451 | -360.7866 | 18.1029 | -360.8358 | 17.5465 | -352.6629 | 18.7333 | -352.6937 | 16.8258
12:06 | 2802 | 32.3998 | 198.5904 | 444.5166 | 449.9514 | -18.3503 | -45.1204 | 7.9643 | 4.7344 | -1.4778 | -2.6471 | 0.603 | -2.4972 | 7.5802 | 1.2731 | 0.602 | 0.6386 | 0.9511 | 0.7192 | -130.866 | -4.9385 | 2.9006 | 0.543 | -5.3599 | -4.0359 | 2.4275 |  | 0.5224 | -1.5928 | 4.017 | 3.3666 | 3.3478 | 1.0423 | 10.7428 | 14.2339 | 14.8036 | 11.0374 | -0.0005 | -0.0027 | 0 | 0.0034 | 0.001 | -0.0002 | 0.0244 | -0.02 | -0.0065 | -360.205 | 17.4315 | -360.525 | 17.6964 | -360.8727 | 18.1481 | -360.8574 | 17.5547 | -352.669 | 18.7292 | -352.7213 | 16.8628
12:06 | 2803 | 32.3731 | 198.5125 | 444.47 | 449.888 | -18.3621 | -45.271 | 7.9737 | 4.8012 | -1.5371 | -2.6537 | 0.6442 | -2.5303 | 7.5859 | 1.2684 | 0.6022 | 0.6407 | 0.951 | 0.7218 | -130.7918 | -4.8489 | 2.9869 | 0.5048 | -5.3942 | -4.022 | 2.3851 |  | 0.4815 | -1.6328 | 4.0162 | 3.3698 | 3.3475 | 1.0428 | 10.7106 | 14.2241 | 14.7905 | 11.0641 | -0.0005 | -0.0032 | 0.0005 | 0.0037 | 0.0003 | -0.0008 | 0.0104 | -0.0076 | -0.0244 | -360.1527 | 17.3782 | -360.4481 | 17.6615 | -360.8327 | 18.1748 | -360.8974 | 17.5404 | -352.6721 | 18.6922 | -352.669 | 16.8443
12:06 | 2804 | 32.3739 | 198.499 | 444.4018 | 449.7889 | -18.4028 | -45.3161 | 8.012 | 4.7686 | -1.4907 | -2.4918 | 0.6919 | -2.5281 | 7.5896 | 1.2498 | 0.6019 | 0.6385 | 0.9529 | 0.7208 | -130.9097 | -4.9741 | 2.922 | 0.4899 | -5.3717 | -4.0202 | 2.3228 |  | 0.4802 | -1.5719 | 4.0166 | 3.3678 | 3.3445 | 1.0435 | 10.7382 | 14.2348 | 14.797 | 11.0681 | 0 | -0.0029 | 0.0007 | 0.0037 | 0.0011 | -0.0006 | 0.0189 | -0.0004 | -0.0053 | -360.1988 | 17.4048 | -360.445 | 17.641 | -360.8112 | 18.1502 | -360.9343 | 17.5712 | -352.6875 | 18.6984 | -352.6383 | 16.8094
12:06 | 2805 | 32.5131 | 198.5459 | 444.4518 | 449.9227 | -18.2324 | -45.1548 | 7.9226 | 4.7973 | -1.4825 | -2.5643 | 0.6757 | -2.5041 | 7.6174 | 1.2387 | 0.6016 | 0.6437 | 0.954 | 0.7211 | -131.0277 | -4.9797 | 2.9754 | 0.4729 | -5.4278 | -4.0525 | 2.2888 |  | 0.4789 | -1.5712 | 4.0166 | 3.3667 | 3.3447 | 1.0417 | 10.729 | 14.2082 | 14.7824 | 11.0645 | -0.0004 | -0.0033 | 0.0007 | 0.0035 | 0.0007 | 0 | 0.0054 | -0.0067 | -0.0034 | -360.245 | 17.4356 | -360.5158 | 17.6697 | -360.8112 | 18.1379 | -360.9004 | 17.5547 | -352.7029 | 18.7395 | -352.7183 | 16.8505
12:06 | 2806 | 32.4739 | 198.4422 | 444.4372 | 449.894 | -18.3756 | -45.2728 | 7.9804 | 4.7873 | -1.4909 | -2.5208 | 0.6581 | -2.6135 | 7.5957 | 1.1646 | 0.6014 | 0.6424 | 0.9522 | 0.7204 | -130.9584 | -4.9529 | 2.9868 | 0.4441 | -5.452 | -4.0265 | 2.3282 |  | 0.5215 | -1.489 | 4.0172 | 3.3685 | 3.3474 | 1.0421 | 10.7393 | 14.2419 | 14.8226 | 11.0572 | -0.0001 | -0.0024 | 0.0012 | 0.0041 | 0.001 | -0.0008 | 0.0033 | -0.0073 | -0.0276 | -360.1342 | 17.3966 | -360.485 | 17.6841 | -360.8666 | 18.1358 | -360.8389 | 17.5034 | -352.6167 | 18.7004 | -352.7029 | 16.8628
12:06 | 2807 | 32.4508 | 198.4121 | 444.2924 | 449.8495 | -18.4112 | -45.2243 | 7.9754 | 4.7427 | -1.4821 | -2.5926 | 0.6206 | -2.5676 | 7.5588 | 1.2034 | 0.602 | 0.643 | 0.9555 | 0.7208 | -130.9096 | -4.8915 | 2.9973 | 0.4906 | -5.3809 | -3.892 | 2.39 |  | 0.535 | -1.4535 | 4.0178 | 3.3663 | 3.3482 | 1.043 | 10.7404 | 14.2492 | 14.7914 | 11.046 | 0.0003 | -0.0026 | 0.0009 | 0.0038 | 0.0008 | 0.0001 | 0.0146 | -0.0049 | -0.0159 | -360.1619 | 17.4069 | -360.5096 | 17.6861 | -360.8727 | 18.183 | -360.8974 | 17.526 | -352.669 | 18.7148 | -352.7121 | 16.8689
12:07 | 2808 | 32.5379 | 198.5201 | 444.411 | 449.8805 | -18.3495 | -45.2091 | 7.8773 | 4.7593 | -1.4625 | -2.6883 | 0.6312 | -2.5404 | 7.5076 | 1.166 | 0.603 | 0.6433 | 0.9558 | 0.7214 | -130.875 | -4.8708 | 3.0193 | 0.4507 | -5.3445 | -4.0442 | 2.4272 |  | 0.5648 | -1.571 | 4.0162 | 3.3665 | 3.3488 | 1.0416 | 10.7313 | 14.2511 | 14.7851 | 11.0435 | 0 | -0.0031 | 0.0006 | 0.0038 | 0.0005 | -0.0009 | 0.013 | 0.006 | -0.012 | -360.1804 | 17.4007 | -360.4573 | 17.6369 | -360.7773 | 18.1337 | -360.885 | 17.5363 | -352.6875 | 18.7066 | -352.666 | 16.8238
12:07 | 2809 | 32.5803 | 198.4861 | 444.4918 | 449.9947 | -18.3483 | -45.1494 | 7.8734 | 4.6893 | -1.4755 | -2.6922 | 0.5726 | -2.5997 | 7.4955 | 1.1568 | 0.6015 | 0.6462 | 0.9556 | 0.7201 | -130.8782 | -4.9409 | 2.9955 | 0.6072 | -5.4947 | -4.0951 | 2.4286 |  | 0.6035 | -1.5615 | 4.0152 | 3.3668 | 3.3488 | 1.0412 | 10.706 | 14.1847 | 14.7619 | 11.054 | 0.0003 | -0.003 | 0.0004 | 0.0033 | 0.0006 | -0.0004 | -0.0027 | -0.016 | -0.0186 | -360.2265 | 17.4562 | -360.5466 | 17.6738 | -360.8358 | 18.1255 | -360.8358 | 17.5424 | -352.6967 | 18.7374 | -352.7275 | 16.8423
12:07 | 2810 | 32.4423 | 198.5089 | 444.4118 | 449.8771 | -18.3585 | -45.1913 | 7.8757 | 4.7968 | -1.3758 | -2.599 | 0.6258 | -2.6663 | 7.4408 | 1.1746 | 0.6022 | 0.646 | 0.9577 | 0.7213 | -130.9437 | -4.8806 | 2.9749 | 0.6151 | -5.4905 | -3.9776 | 2.4693 |  | 0.6231 | -1.5496 | 4.0165 | 3.3704 | 3.3504 | 1.0418 | 10.7267 | 14.229 | 14.797 | 11.045 | -0.0004 | -0.0027 | 0.0001 | 0.0034 | 0.0008 | -0.0006 | 0.0128 | -0.0143 | -0.0163 | -360.1465 | 17.4172 | -360.5004 | 17.682 | -360.882 | 18.142 | -360.8297 | 17.5178 | -352.669 | 18.721 | -352.7337 | 16.8669
12:07 | 2811 | 32.5075 | 198.5637 | 444.5492 | 449.9463 | -18.3863 | -45.2135 | 7.8679 | 4.7414 | -1.4182 | -2.6404 | 0.7108 | -2.5434 | 7.5744 | 1.2716 | 0.6018 | 0.6387 | 0.9524 | 0.7223 | -130.9941 | -4.9728 | 2.925 | 0.6788 | -5.4334 | -3.9569 | 2.4773 |  | 0.6144 | -1.5169 | 4.0157 | 3.3662 | 3.3465 | 1.042 | 10.7035 | 14.229 | 14.7507 | 11.045 | -0.0003 | -0.0026 | 0.001 | 0.0042 | 0.001 | -0.0005 | 0.015 | -0.019 | -0.0267 | -360.1896 | 17.3905 | -360.4419 | 17.6677 | -360.8235 | 18.1625 | -360.8943 | 17.5342 | -352.6537 | 18.7004 | -352.6413 | 16.8279
12:07 | 2812 | 32.5688 | 198.602 | 444.472 | 449.8749 | -18.3078 | -45.2694 | 8.0075 | 4.7794 | -1.4673 | -2.5371 | 0.5934 | -2.4724 | 7.61 | 1.2516 | 0.6017 | 0.6434 | 0.954 | 0.7196 | -130.9462 | -4.9518 | 2.9333 | 0.6762 | -5.4845 | -3.9451 | 2.4362 |  | 0.6049 | -1.5871 | 4.016 | 3.3657 | 3.348 | 1.0422 | 10.7301 | 14.2094 | 14.7722 | 11.054 | 0.0002 | -0.0029 | 0.0006 | 0.0036 | 0.0008 | -0.0003 | 0.0153 | -0.0056 | -0.0074 | -360.245 | 17.4172 | -360.4604 | 17.643 | -360.7897 | 18.1481 | -360.9374 | 17.5691 | -352.7337 | 18.7312 | -352.6721 | 16.8176
12:07 | 2813 | 32.5892 | 198.4738 | 444.5392 | 449.9317 | -18.3125 | -45.3468 | 7.7763 | 4.8098 | -1.4207 | -2.6576 | 0.6565 | -2.4887 | 7.6293 | 1.2782 | 0.6028 | 0.6439 | 0.9532 | 0.7202 | -130.9608 | -4.9027 | 2.9799 | 0.646 | -5.5123 | -3.9905 | 2.4351 |  | 0.6347 | -1.5323 | 4.0165 | 3.3705 | 3.3503 | 1.0419 | 10.7105 | 14.2185 | 14.7973 | 11.0638 | 0.0002 | -0.0029 | 0.0005 | 0.0038 | 0.0008 | -0.0009 | -0.003 | -0.0006 | -0.0158 | -360.1742 | 17.4172 | -360.4881 | 17.6594 | -360.7773 | 18.1214 | -360.8574 | 17.5198 | -352.6937 | 18.7333 | -352.669 | 16.8258
12:07 | 2814 | 32.5975 | 198.5 | 444.5215 | 449.9524 | -18.2954 | -45.3973 | 7.8683 | 4.6528 | -1.514 | -2.7272 | 0.733 | -2.5994 | 7.6123 | 1.2758 | 0.6015 | 0.6455 | 0.9535 | 0.7213 | -130.9174 | -4.9176 | 2.9744 | 0.6395 | -5.5599 | -4.0635 | 2.3868 |  | 0.6334 | -1.5404 | 4.0166 | 3.3681 | 3.3494 | 1.0424 | 10.7174 | 14.2372 | 14.8113 | 11.0702 | 0 | -0.0025 | 0.0012 | 0.0041 | 0.0004 | -0.0002 | 0.0222 | -0.0103 | 0.0204 | -360.1835 | 17.411 | -360.5373 | 17.7108 | -360.882 | 18.1728 | -360.9004 | 17.5239 | -352.6813 | 18.7353 | -352.7244 | 16.8731
12:07 | 2815 | 32.5819 | 198.5012 | 444.507 | 449.9223 | -18.3338 | -45.3046 | 7.7834 | 4.6401 | -1.4703 | -2.634 | 0.6828 | -2.5857 | 7.6055 | 1.2035 | 0.6018 | 0.6449 | 0.9537 | 0.7219 | -130.9474 | -4.9982 | 3.0258 | 0.6147 | -5.4807 | -4.0059 | 2.4176 |  | 0.6158 | -1.5304 | 4.016 | 3.3673 | 3.3451 | 1.0437 | 10.7325 | 14.229 | 14.7681 | 11.045 | -0.0003 | -0.0025 | 0.0012 | 0.0034 | 0.001 | -0.0004 | 0.0051 | -0.0089 | -0.0272 | -360.1158 | 17.3761 | -360.4296 | 17.6677 | -360.8143 | 18.1543 | -360.8697 | 17.5219 | -352.6506 | 18.6984 | -352.6383 | 16.8505
12:07 | 2816 | 32.6059 | 198.4872 | 444.5368 | 449.9778 | -18.3849 | -45.2859 | 7.9575 | 4.6877 | -1.4167 | -2.5637 | 0.6469 | -2.5122 | 7.5882 | 1.2925 | 0.6015 | 0.6405 | 0.9529 | 0.7201 | -130.9178 | -4.9484 | 2.9899 | 0.457 | -5.4837 | -4.0583 | 2.3768 |  | 0.6071 | -1.6401 | 4.016 | 3.3671 | 3.3491 | 1.0426 | 10.7197 | 14.2337 | 14.8025 | 11.0609 | 0.0003 | -0.0027 | 0.0007 | 0.0041 | 0.0002 | -0.0003 | 0.0206 | -0.0139 | -0.0015 | -360.2388 | 17.4295 | -360.4789 | 17.6656 | -360.8204 | 18.1522 | -360.9127 | 17.5609 | -352.6998 | 18.7333 | -352.706 | 16.834
12:07 | 2817 | 32.5739 | 198.4635 | 444.4174 | 449.9072 | -18.4666 | -45.3539 | 7.8872 | 4.6884 | -1.4001 | -2.5012 | 0.7094 | -2.4789 | 7.6164 | 1.3166 | 0.6021 | 0.6443 | 0.9548 | 0.72 | -130.8455 | -4.9135 | 3.0452 | 0.4672 | -5.4128 | -3.9733 | 2.4132 |  | 0.6783 | -1.4767 | 4.0181 | 3.3661 | 3.3455 | 1.0439 | 10.7082 | 14.2277 | 14.7541 | 11.0327 | 0.0003 | -0.0033 | 0.0008 | 0.0039 | 0.0005 | -0.0012 | 0.0052 | -0.0109 | -0.0223 | -360.1958 | 17.4315 | -360.5096 | 17.6738 | -360.8143 | 18.1112 | -360.8235 | 17.5198 | -352.6813 | 18.7477 | -352.706 | 16.8484
12:07 | 2818 | 32.6083 | 198.4632 | 444.4734 | 449.8502 | -18.4076 | -45.3247 | 7.9545 | 4.7382 | -1.3582 | -2.4835 | 0.6529 | -2.4934 | 7.7061 | 1.3437 | 0.6019 | 0.6455 | 0.9542 | 0.7218 | -130.9704 | -4.9505 | 3.122 | 0.4132 | -5.4815 | -4.0851 | 2.3296 |  | 0.6617 | -1.3894 | 4.0169 | 3.3657 | 3.3497 | 1.0428 | 10.7313 | 14.2164 | 14.7678 | 11.0204 | -0.0001 | -0.0026 | 0.0007 | 0.0039 | 0.0006 | -0.0005 | -0.0046 | -0.0006 | -0.0028 | -360.1281 | 17.4213 | -360.5281 | 17.6902 | -360.8204 | 18.1399 | -360.8574 | 17.5157 | -352.6567 | 18.7333 | -352.7244 | 16.8566
12:07 | 2819 | 32.4846 | 198.5139 | 444.3454 | 449.8748 | -18.3687 | -45.3161 | 8.0526 | 4.7864 | -1.3351 | -2.6087 | 0.7859 | -2.5102 | 7.6521 | 1.3161 | 0.6029 | 0.6452 | 0.9548 | 0.7205 | -130.9996 | -5.0154 | 3.0366 | 0.5442 | -5.4591 | -4.0849 | 2.3496 |  | 0.7456 | -1.4333 | 4.0163 | 3.3683 | 3.3471 | 1.0422 | 10.7209 | 14.2115 | 14.7786 | 11.028 | -0.0003 | -0.0025 | 0.0009 | 0.0045 | 0.0009 | -0.0006 | 0.0266 | -0.0045 | -0.0102 | -360.1835 | 17.4048 | -360.4666 | 17.6861 | -360.8481 | 18.1728 | -360.9281 | 17.5404 | -352.6937 | 18.7312 | -352.6937 | 16.8546
12:07 | 2820 | 32.5122 | 198.4815 | 444.3621 | 449.8452 | -18.3681 | -45.3154 | 8.0418 | 4.8402 | -1.4846 | -2.5772 | 0.7104 | -2.5292 | 7.6856 | 1.337 | 0.6012 | 0.6454 | 0.9509 | 0.7203 | -130.9677 | -4.8717 | 3.1867 | 0.7045 | -5.4077 | -3.9922 | 2.4072 |  | 0.8023 | -1.4453 | 4.0167 | 3.3671 | 3.3474 | 1.043 | 10.7186 | 14.2266 | 14.7596 | 11.0255 | -0.0001 | -0.0029 | 0.0006 | 0.0035 | 0.0008 | -0.0006 | 0.0093 | -0.0005 | 0.0036 | -360.1773 | 17.3966 | -360.4296 | 17.6451 | -360.7466 | 18.1235 | -360.8758 | 17.5486 | -352.6844 | 18.7169 | -352.6721 | 16.8258
12:07 | 2821 | 32.509 | 198.5316 | 444.3759 | 449.8962 | -18.2917 | -45.2557 | 8.1245 | 4.795 | -1.4232 | -2.5484 | 0.7057 | -2.5774 | 7.7187 | 1.3929 | 0.6015 | 0.6438 | 0.9512 | 0.7187 | -130.9266 | -4.8747 | 3.1299 | 0.684 | -5.4904 | -4.1039 | 2.3746 |  | 0.7514 | -1.4672 | 4.0177 | 3.368 | 3.3512 | 1.0432 | 10.714 | 14.2336 | 14.7957 | 11.067 | 0.0004 | -0.0031 | 0.0006 | 0.0034 | 0.0007 | -0.0005 | 0.0118 | 0.0044 | -0.008 | -360.245 | 17.4418 | -360.5004 | 17.6759 | -360.8297 | 18.1461 | -360.8912 | 17.5486 | -352.6937 | 18.7703 | -352.7029 | 16.834
12:07 | 2822 | 32.5217 | 198.5344 | 444.4392 | 449.8919 | -18.2851 | -45.162 | 8.1201 | 4.7333 | -1.5404 | -2.6477 | 0.6294 | -2.5199 | 7.6673 | 1.4 | 0.6018 | 0.642 | 0.9514 | 0.7213 | -130.8996 | -4.8355 | 3.1434 | 0.5378 | -5.498 | -4.0929 | 2.3455 |  | 0.7307 | -1.4348 | 4.0177 | 3.3653 | 3.3505 | 1.0429 | 10.7358 | 14.2558 | 14.8138 | 11.0536 | -0.0001 | -0.003 | 0.0011 | 0.0041 | 0.0009 | -0.0003 | 0.0248 | -0.0127 | -0.0193 | -360.1465 | 17.4048 | -360.4789 | 17.6841 | -360.805 | 18.1379 | -360.8635 | 17.5198 | -352.6537 | 18.7251 | -352.706 | 16.8628
12:07 | 2823 | 32.5435 | 198.4693 | 444.4435 | 449.8788 | -18.3697 | -45.24 | 7.9589 | 4.7056 | -1.5865 | -2.5392 | 0.6474 | -2.5913 | 7.7089 | 1.3096 | 0.6024 | 0.643 | 0.9512 | 0.7206 | -130.88 | -4.909 | 3.2208 | 0.4327 | -5.4377 | -4.2456 | 2.3736 |  | 0.7709 | -1.4392 | 4.0167 | 3.365 | 3.3505 | 1.0424 | 10.6978 | 14.2115 | 14.7612 | 11.028 | -0.0002 | -0.0025 | 0.0006 | 0.0037 | 0.0006 | -0.0002 | 0.0035 | -0.0053 | -0.0235 | -360.1619 | 17.3946 | -360.4481 | 17.6738 | -360.8789 | 18.1707 | -360.8881 | 17.5383 | -352.6352 | 18.721 | -352.6844 | 16.8423
12:07 | 2824 | 32.5453 | 198.5564 | 444.4547 | 449.916 | -18.4236 | -45.2733 | 7.9861 | 4.7077 | -1.5365 | -2.5889 | 0.7174 | -2.5515 | 7.7194 | 1.2786 | 0.6026 | 0.6445 | 0.954 | 0.7199 | -130.889 | -4.8788 | 3.1878 | 0.5024 | -5.5134 | -4.0834 | 2.2821 |  | 0.7218 | -1.4853 | 4.0171 | 3.364 | 3.349 | 1.0427 | 10.722 | 14.2186 | 14.81 | 11.0576 | -0.0002 | -0.003 | 0.0005 | 0.0044 | 0.0011 | -0.0001 | 0.0112 | -0.0114 | 0.0009 | -360.165 | 17.4069 | -360.485 | 17.6779 | -360.802 | 18.1481 | -360.9251 | 17.5527 | -352.6844 | 18.7333 | -352.7183 | 16.8484
12:07 | 2825 | 32.6669 | 198.5562 | 444.4328 | 449.9527 | -18.343 | -45.2135 | 8.0131 | 4.6834 | -1.5573 | -2.5543 | 0.6337 | -2.5406 | 7.696 | 1.1685 | 0.6014 | 0.6461 | 0.9503 | 0.7212 | -130.9086 | -4.8934 | 3.2245 | 0.63 | -5.4239 | -3.9411 | 2.396 |  | 0.7934 | -1.5132 | 4.0171 | 3.3646 | 3.3496 | 1.0433 | 10.7359 | 14.2499 | 14.7954 | 11.0598 | 0.0003 | -0.003 | 0.0004 | 0.0044 | 0.0005 | -0.0001 | 0.0082 | -0.0146 | -0.0125 | -360.1988 | 17.4213 | -360.4542 | 17.6718 | -360.8266 | 18.1173 | -360.8204 | 17.5239 | -352.6598 | 18.7271 | -352.669 | 16.832
12:07 | 2826 | 32.5368 | 198.4121 | 444.3302 | 449.874 | -18.359 | -45.2053 | 8.1101 | 4.667 | -1.6086 | -2.5541 | 0.6621 | -2.5731 | 7.7198 | 1.2217 | 0.602 | 0.6454 | 0.9533 | 0.7206 | -130.867 | -4.7946 | 3.2629 | 0.6238 | -5.4894 | -3.9736 | 2.3908 |  | 0.7644 | -1.3458 | 4.0166 | 3.3642 | 3.3485 | 1.0423 | 10.7498 | 14.2234 | 14.827 | 11.0388 | -0.0001 | -0.003 | 0.0006 | 0.004 | 0.0008 | -0.0009 | 0.019 | -0.0158 | -0.0102 | -360.1773 | 17.4254 | -360.5404 | 17.6985 | -360.8758 | 18.1563 | -360.9066 | 17.5363 | -352.6629 | 18.7395 | -352.7244 | 16.8689
12:07 | 2827 | 32.6465 | 198.6199 | 444.5146 | 449.9853 | -18.3737 | -45.1895 | 8.1312 | 4.6811 | -1.6355 | -2.5203 | 0.5993 | -2.5784 | 7.6666 | 1.2601 | 0.6032 | 0.6469 | 0.95 | 0.7206 | -130.8705 | -4.8527 | 3.2197 | 0.5675 | -5.4508 | -3.997 | 2.4049 |  | 0.7418 | -1.3442 | 4.015 | 3.3657 | 3.3472 | 1.0418 | 10.7151 | 14.2232 | 14.7855 | 11.045 | -0.0003 | -0.0026 | 0.0011 | 0.0044 | 0.0008 | -0.0003 | 0.0156 | -0.0097 | -0.0145 | -360.1588 | 17.3925 | -360.4542 | 17.6553 | -360.805 | 18.1461 | -360.8666 | 17.528 | -352.6475 | 18.7271 | -352.6567 | 16.8464
12:07 | 2828 | 32.5613 | 198.6019 | 444.4899 | 449.8814 | -18.4099 | -45.2146 | 8.0532 | 4.6549 | -1.6385 | -2.4783 | 0.7455 | -2.5774 | 7.6519 | 1.2489 | 0.6021 | 0.6471 | 0.9487 | 0.7212 | -130.8449 | -4.8555 | 3.2949 | 0.5622 | -5.4594 | -3.9515 | 2.4275 |  | 0.7478 | -1.3346 | 4.0154 | 3.3666 | 3.3473 | 1.0435 | 10.7555 | 14.2524 | 14.7876 | 11.0558 | -0.0002 | -0.0027 | 0.0008 | 0.0041 | 0.0008 | -0.0008 | 0.0012 | 0.0063 | 0.0031 | -360.1711 | 17.4213 | -360.4912 | 17.6615 | -360.7866 | 18.1399 | -360.9004 | 17.5363 | -352.6537 | 18.7312 | -352.7121 | 16.834
12:07 | 2829 | 32.5826 | 198.5804 | 444.4836 | 449.9991 | -18.4499 | -45.2478 | 8.0398 | 4.7154 | -1.5142 | -2.5524 | 0.7543 | -2.6212 | 7.6383 | 1.258 | 0.6027 | 0.6453 | 0.9531 | 0.7208 | -130.9436 | -4.9032 | 3.2325 | 0.4006 | -5.4692 | -4.0456 | 2.438 |  | 0.737 | -1.3458 | 4.0146 | 3.3624 | 3.3468 | 1.0435 | 10.7579 | 14.2198 | 14.794 | 11.0298 | 0.0004 | -0.003 | 0.0008 | 0.0036 | 0.0005 | -0.0005 | 0.0178 | -0.004 | 0.0025 | -360.165 | 17.4151 | -360.4973 | 17.68 | -360.8297 | 18.1604 | -360.8881 | 17.5445 | -352.709 | 18.7436 | -352.7183 | 16.8546
12:07 | 2830 | 32.6526 | 198.5838 | 444.457 | 449.9569 | -18.4736 | -45.239 | 7.9709 | 4.7146 | -1.6032 | -2.5865 | 0.741 | -2.6228 | 7.6587 | 1.2618 | 0.6033 | 0.6456 | 0.953 | 0.7211 | -130.9624 | -4.8591 | 3.2979 | 0.5797 | -5.4729 | -4.0442 | 2.4302 |  | 0.7674 | -1.3527 | 4.016 | 3.365 | 3.3516 | 1.0448 | 10.7382 | 14.2406 | 14.8202 | 11.0681 | 0 | -0.0027 | 0.0007 | 0.0041 | 0.0006 | -0.0007 | 0.0196 | 0.0015 | 0.0113 | -360.1496 | 17.3987 | -360.4696 | 17.6656 | -360.8112 | 18.1276 | -360.8727 | 17.5342 | -352.6136 | 18.723 | -352.6783 | 16.834
12:07 | 2831 | 32.6364 | 198.5428 | 444.5843 | 449.9521 | -18.3948 | -45.2294 | 8.0116 | 4.7667 | -1.6158 | -2.4721 | 0.6963 | -2.5269 | 7.6329 | 1.2725 | 0.6033 | 0.6479 | 0.9523 | 0.7198 | -130.9163 | -4.855 | 3.256 | 0.5535 | -5.4072 | -3.8984 | 2.4125 |  | 0.6031 | -1.475 | 4.0163 | 3.3667 | 3.3446 | 1.0427 | 10.7417 | 14.2382 | 14.8001 | 11.0775 | -0.0001 | -0.0026 | 0.0006 | 0.0037 | 0.0005 | -0.0007 | 0.0049 | -0.0019 | -0.0105 | -360.2111 | 17.4192 | -360.5066 | 17.6923 | -360.845 | 18.1543 | -360.9035 | 17.5465 | -352.6967 | 18.7518 | -352.6906 | 16.8484
12:07 | 2832 | 32.6068 | 198.5485 | 444.4907 | 449.8952 | -18.4128 | -45.2326 | 8.094 | 4.8016 | -1.5849 | -2.4447 | 0.7287 | -2.605 | 7.5821 | 1.0986 | 0.6026 | 0.643 | 0.9513 | 0.7195 | -130.8441 | -4.8079 | 3.2954 | 0.5013 | -5.3635 | -4.0402 | 2.3673 |  | 0.6492 | -1.3507 | 4.0157 | 3.3643 | 3.3483 | 1.044 | 10.714 | 14.2277 | 14.7483 | 11.0327 | -0.0005 | -0.0027 | 0.0003 | 0.0037 | 0.0007 | -0.0001 | 0.0032 | -0.0048 | -0.0226 | -360.1496 | 17.409 | -360.4727 | 17.6594 | -360.7989 | 18.1296 | -360.8697 | 17.5321 | -352.6537 | 18.7292 | -352.6875 | 16.8423
12:07 | 2833 | 32.6301 | 198.545 | 444.4617 | 449.9185 | -18.542 | -45.3315 | 8.0414 | 4.8008 | -1.5227 | -2.3122 | 0.7264 | -2.6215 | 7.5904 | 1.2142 | 0.6019 | 0.6448 | 0.9519 | 0.7196 | -130.9941 | -4.8884 | 3.2256 | 0.4182 | -5.475 | -3.9904 | 2.3678 |  | 0.6511 | -1.4191 | 4.0161 | 3.3688 | 3.3489 | 1.0457 | 10.7117 | 14.2253 | 14.7861 | 11.0479 | 0.0004 | -0.003 | 0.0007 | 0.0045 | 0.0008 | -0.0006 | 0.0097 | 0.0095 | -0.0041 | -360.1896 | 17.411 | -360.4635 | 17.6738 | -360.8389 | 18.1543 | -360.8727 | 17.5301 | -352.669 | 18.7292 | -352.6721 | 16.8361
12:07 | 2834 | 32.6436 | 198.5963 | 444.4039 | 449.8976 | -18.4836 | -45.3143 | 7.9791 | 4.7962 | -1.5478 | -2.5446 | 0.7083 | -2.7514 | 7.5567 | 1.1888 | 0.6015 | 0.6447 | 0.9505 | 0.7209 | -130.9149 | -4.9395 | 3.2397 | 0.4801 | -5.439 | -4.0039 | 2.408 |  | 0.639 | -1.5099 | 4.0151 | 3.3654 | 3.3451 | 1.0433 | 10.7106 | 14.1952 | 14.7558 | 11.0237 | 0 | -0.0032 | 0.0009 | 0.0043 | 0.0005 | -0.0003 | 0.0027 | -0.0182 | -0.0034 | -360.1896 | 17.411 | -360.5035 | 17.6861 | -360.845 | 18.1563 | -360.9343 | 17.5486 | -352.6783 | 18.723 | -352.6906 | 16.8546
12:07 | 2835 | 32.6436 | 198.5272 | 444.4426 | 449.7891 | -18.5291 | -45.2108 | 8.0381 | 4.8485 | -1.5189 | -2.4583 | 0.7655 | -2.674 | 7.5137 | 1.1915 | 0.6033 | 0.6478 | 0.9526 | 0.7201 | -130.891 | -4.8832 | 3.3134 | 0.5926 | -5.5125 | -3.9806 | 2.4193 |  | 0.7066 | -1.457 | 4.0167 | 3.3662 | 3.3504 | 1.0424 | 10.714 | 14.2278 | 14.8072 | 11.0323 | 0.0001 | -0.0024 | 0.0002 | 0.0034 | 0.0006 | -0.0007 | 0.0312 | 0.0066 | 0.0101 | -360.1711 | 17.4007 | -360.4635 | 17.641 | -360.7927 | 18.1379 | -360.8635 | 17.5198 | -352.6598 | 18.7251 | -352.669 | 16.8299
12:07 | 2836 | 32.6563 | 198.5297 | 444.5018 | 449.8221 | -18.4812 | -45.1271 | 8.0227 | 4.7615 | -1.5046 | -2.4907 | 0.7959 | -2.6117 | 7.5701 | 1.1763 | 0.6035 | 0.6453 | 0.9521 | 0.7196 | -130.8905 | -4.7281 | 3.28 | 0.6401 | -5.4759 | -3.962 | 2.3491 |  | 0.7454 | -1.399 | 4.0152 | 3.3667 | 3.3464 | 1.0426 | 10.721 | 14.2171 | 14.7891 | 11.0457 | -0.0002 | -0.0029 | 0.0007 | 0.0036 | 0.0004 | -0.0004 | 0.0062 | -0.0037 | -0.0053 | -360.2019 | 17.4233 | -360.5066 | 17.6861 | -360.8512 | 18.1481 | -360.882 | 17.5465 | -352.6813 | 18.7415 | -352.7213 | 16.8464
12:07 | 2837 | 32.6068 | 198.3932 | 444.3667 | 449.8068 | -18.4772 | -45.1139 | 8.0533 | 4.8091 | -1.4432 | -2.4905 | 0.7861 | -2.5585 | 7.6273 | 1.2191 | 0.6023 | 0.6475 | 0.9499 | 0.7187 | -130.9218 | -4.8387 | 3.2326 | 0.5164 | -5.5119 | -3.9887 | 2.3515 |  | 0.736 | -1.4441 | 4.0142 | 3.3645 | 3.3459 | 1.0426 | 10.7382 | 14.2579 | 14.8144 | 11.0565 | 0.0002 | -0.0026 | 0.0005 | 0.0033 | 0.0006 | -0.0007 | 0.0103 | -0.0076 | -0.008 | -360.165 | 17.4192 | -360.5219 | 17.682 | -360.8574 | 18.144 | -360.8635 | 17.5239 | -352.6844 | 18.7456 | -352.7644 | 16.8731
12:07 | 2838 | 32.6693 | 198.4783 | 444.4143 | 449.8659 | -18.5091 | -45.285 | 7.9952 | 4.7148 | -1.4713 | -2.2936 | 0.7592 | -2.542 | 7.6477 | 1.2877 | 0.6028 | 0.6467 | 0.9485 | 0.7193 | -130.8909 | -4.7984 | 3.2505 | 0.5449 | -5.5037 | -4.0744 | 2.2771 |  | 0.7612 | -1.36 | 4.0149 | 3.3647 | 3.3464 | 1.0427 | 10.7128 | 14.2151 | 14.7943 | 11.0313 | -0.0001 | -0.0031 | 0.0006 | 0.0037 | 0.0003 | -0.0005 | -0.0013 | -0.0168 | 0.005 | -360.1496 | 17.3987 | -360.4481 | 17.6656 | -360.8266 | 18.1481 | -360.8604 | 17.5116 | -352.6352 | 18.7148 | -352.6537 | 16.8361
12:07 | 2839 | 32.5407 | 198.4056 | 444.2433 | 449.7739 | -18.3733 | -45.109 | 8.1433 | 4.8333 | -1.418 | -2.2942 | 0.8737 | -2.6177 | 7.6806 | 1.2503 | 0.601 | 0.6462 | 0.9501 | 0.7194 | -130.9518 | -4.8899 | 3.2233 | 0.6105 | -5.4481 | -3.9263 | 2.3248 |  | 0.833 | -1.3832 | 4.014 | 3.3648 | 3.3501 | 1.0437 | 10.7325 | 14.2406 | 14.8144 | 11.0681 | -0.0002 | -0.0029 | 0.0012 | 0.0043 | 0.0004 | -0.0007 | 0.0066 | -0.0132 | -0.013 | -360.1896 | 17.4172 | -360.4789 | 17.6636 | -360.7958 | 18.1728 | -360.9097 | 17.5588 | -352.7029 | 18.7436 | -352.6967 | 16.8381
12:07 | 2840 | 32.6643 | 198.565 | 444.3208 | 449.8842 | -18.4382 | -45.0989 | 8.067 | 4.875 | -1.376 | -2.3939 | 0.7843 | -2.6035 | 7.5613 | 1.2043 | 0.602 | 0.6455 | 0.9547 | 0.72 | -130.98 | -4.8718 | 3.2174 | 0.6412 | -5.4144 | -3.9613 | 2.281 |  | 0.761 | -1.39 | 4.0147 | 3.3663 | 3.3512 | 1.0437 | 10.7117 | 14.2312 | 14.7987 | 11.0417 | -0.0004 | -0.0025 | 0.0004 | 0.0036 | 0.0008 | -0.0008 | 0.0066 | 0.0056 | -0.0069 | -360.1988 | 17.4377 | -360.5035 | 17.6677 | -360.8143 | 18.1276 | -360.8666 | 17.5383 | -352.7275 | 18.7723 | -352.7398 | 16.8484
12:07 | 2841 | 32.7281 | 198.5905 | 444.3248 | 449.8766 | -18.4381 | -45.1508 | 7.9965 | 4.8017 | -1.3299 | -2.4468 | 0.806 | -2.5626 | 7.6373 | 1.2028 | 0.6019 | 0.6459 | 0.9553 | 0.7201 | -130.9936 | -4.8611 | 3.1517 | 0.6228 | -5.4295 | -3.8656 | 2.3039 |  | 0.6909 | -1.4124 | 4.0144 | 3.3634 | 3.3476 | 1.0435 | 10.736 | 14.2265 | 14.7874 | 11.0548 | -0.0005 | -0.0032 | 0.0005 | 0.0039 | 0.0002 | -0.0006 | 0.0281 | 0.0012 | 0.0121 | -360.1065 | 17.3905 | -360.4819 | 17.6759 | -360.8297 | 18.1296 | -360.8512 | 17.5137 | -352.6167 | 18.7271 | -352.6967 | 16.8464
12:07 | 2842 | 32.7218 | 198.4878 | 444.343 | 449.8689 | -18.436 | -45.1537 | 8.016 | 4.8132 | -1.3181 | -2.5649 | 0.8109 | -2.5381 | 7.6494 | 1.3189 | 0.6029 | 0.6463 | 0.9501 | 0.7194 | -131.0861 | -4.9214 | 3.0702 | 0.7578 | -5.4221 | -3.8924 | 2.4171 |  | 0.6502 | -1.3497 | 4.015 | 3.3635 | 3.3486 | 1.0433 | 10.7174 | 14.2081 | 14.7698 | 11.0302 | 0.0002 | -0.0031 | 0.0009 | 0.0038 | 0.0009 | -0.0007 | 0.0301 | -0.0135 | -0.0132 | -360.1865 | 17.4069 | -360.4296 | 17.6636 | -360.8389 | 18.1789 | -360.9127 | 17.5527 | -352.6783 | 18.723 | -352.6537 | 16.834
12:07 | 2843 | 32.6707 | 198.4525 | 444.3643 | 449.864 | -18.2679 | -44.9464 | 8.1736 | 4.8503 | -1.3099 | -2.5727 | 0.8055 | -2.4896 | 7.6344 | 1.2575 | 0.6018 | 0.6448 | 0.9531 | 0.7206 | -130.99 | -4.8845 | 3.2359 | 0.718 | -5.3946 | -3.8593 | 2.3863 |  | 0.7151 | -1.3997 | 4.0148 | 3.3609 | 3.3502 | 1.045 | 10.7094 | 14.2231 | 14.7786 | 11.0685 | -0.0004 | -0.0035 | 0.0002 | 0.0034 | 0.0004 | -0.0007 | 0.0055 | 0.0004 | -0.0221 | -360.1404 | 17.4295 | -360.4696 | 17.6369 | -360.805 | 18.1543 | -360.9189 | 17.5568 | -352.7244 | 18.7538 | -352.6937 | 16.8258
12:07 | 2844 | 32.7557 | 198.5075 | 444.4149 | 449.9542 | -18.2229 | -45.0375 | 8.1607 | 4.912 | -1.2828 | -2.465 | 0.7652 | -2.6036 | 7.7301 | 1.2627 | 0.6024 | 0.6432 | 0.9517 | 0.7193 | -130.9453 | -4.8388 | 3.3082 | 0.7537 | -5.4312 | -3.796 | 2.4035 |  | 0.7311 | -1.3658 | 4.0158 | 3.3669 | 3.3487 | 1.0431 | 10.6968 | 14.2157 | 14.7567 | 11.0454 | -0.0008 | -0.003 | 0.0006 | 0.0034 | 0.0011 | -0.0006 | 0.0095 | -0.0074 | -0.0005 | -360.1496 | 17.411 | -360.4696 | 17.6553 | -360.8081 | 18.1235 | -360.8174 | 17.5096 | -352.6752 | 18.7436 | -352.6813 | 16.834
12:07 | 2845 | 32.686 | 198.6062 | 444.38 | 449.9981 | -18.3566 | -44.9481 | 8.1402 | 4.776 | -1.3317 | -2.5144 | 0.7744 | -2.5553 | 7.6637 | 1.2472 | 0.6014 | 0.6435 | 0.9521 | 0.7215 | -131.0041 | -4.8412 | 3.2359 | 0.6856 | -5.4514 | -3.8929 | 2.3663 |  | 0.7091 | -1.3584 | 4.0147 | 3.3657 | 3.3481 | 1.0451 | 10.7105 | 14.236 | 14.7984 | 11.0518 | -0.0003 | -0.0026 | 0.0003 | 0.003 | 0.0005 | -0.0002 | 0.0147 | -0.0136 | 0.0025 | -360.1373 | 17.3987 | -360.4789 | 17.7005 | -360.8727 | 18.1666 | -360.9281 | 17.5178 | -352.6383 | 18.723 | -352.6875 | 16.8546
12:07 | 2846 | 32.5504 | 198.5786 | 444.4389 | 449.8936 | -18.3736 | -45.1411 | 7.9705 | 4.7736 | -1.3274 | -2.4794 | 0.7216 | -2.6048 | 7.6661 | 1.3466 | 0.6015 | 0.6437 | 0.9517 | 0.7211 | -130.8991 | -4.6756 | 3.2546 | 0.6444 | -5.3815 | -3.8349 | 2.4535 |  | 0.6362 | -1.4328 | 4.0144 | 3.3661 | 3.3477 | 1.0431 | 10.7394 | 14.2418 | 14.8042 | 11.0403 | 0 | -0.0034 | 0.001 | 0.0038 | 0.0007 | -0.0008 | 0.0317 | -0.0115 | -0.0055 | -360.1865 | 17.4028 | -360.4727 | 17.6759 | -360.8481 | 18.1687 | -360.9281 | 17.5568 | -352.7121 | 18.7251 | -352.6629 | 16.8464
12:07 | 2847 | 32.6216 | 198.524 | 444.3926 | 449.8503 | -18.3854 | -45.1177 | 7.9909 | 4.7618 | -1.3446 | -2.3278 | 0.6912 | -2.5932 | 7.7025 | 1.3452 | 0.6011 | 0.6454 | 0.9561 | 0.7221 | -130.821 | -4.6518 | 3.3534 | 0.6598 | -5.4482 | -3.9224 | 2.3634 |  | 0.7247 | -1.3138 | 4.0154 | 3.3633 | 3.3481 | 1.0437 | 10.7405 | 14.2257 | 14.8008 | 11.041 | -0.0001 | -0.003 | 0.0011 | 0.0041 | 0.0005 | 0.0002 | 0.0172 | -0.0072 | 0.0044 | -360.125 | 17.4131 | -360.4512 | 17.6533 | -360.7681 | 18.1153 | -360.8604 | 17.5321 | -352.6783 | 18.7333 | -352.6475 | 16.832
12:07 | 2848 | 32.5802 | 198.5027 | 444.4032 | 449.8343 | -18.4553 | -45.1621 | 7.9528 | 4.7995 | -1.2702 | -2.4398 | 0.7856 | -2.5857 | 7.7473 | 1.3891 | 0.6017 | 0.6405 | 0.9532 | 0.7207 | -130.8947 | -4.7004 | 3.312 | 0.6372 | -5.421 | -3.951 | 2.3438 |  | 0.7214 | -1.3207 | 4.0144 | 3.3627 | 3.3488 | 1.0425 | 10.7359 | 14.2152 | 14.7954 | 11.0713 | -0.0004 | -0.0029 | 0.0011 | 0.0042 | 0.0009 | -0.0007 | 0.0142 | -0.0079 | -0.0288 | -360.1773 | 17.4295 | -360.5435 | 17.7108 | -360.8912 | 18.1502 | -360.8174 | 17.5116 | -352.6629 | 18.7518 | -352.7398 | 16.8669
12:07 | 2849 | 32.698 | 198.6303 | 444.4104 | 449.8959 | -18.3719 | -45.2114 | 7.981 | 4.7658 | -1.3558 | -2.4748 | 0.6961 | -2.5655 | 7.7382 | 1.458 | 0.6012 | 0.6422 | 0.9531 | 0.7214 | -130.9223 | -4.7141 | 3.2091 | 0.5692 | -5.3161 | -3.9276 | 2.4006 |  | 0.6754 | -1.3305 | 4.014 | 3.3628 | 3.3489 | 1.045 | 10.7602 | 14.2511 | 14.8372 | 11.0897 | -0.0003 | -0.0027 | 0.0005 | 0.004 | 0.0008 | -0.0001 | 0.0065 | 0.0024 | 0.0222 | -360.1219 | 17.409 | -360.4881 | 17.7026 | -360.8697 | 18.1625 | -360.9004 | 17.5096 | -352.6444 | 18.7189 | -352.706 | 16.8648
12:07 | 2850 | 32.7053 | 198.5079 | 444.3891 | 449.8428 | -18.4463 | -45.1882 | 7.9603 | 4.8615 | -1.3644 | -2.4068 | 0.7595 | -2.6023 | 7.7013 | 1.4167 | 0.6018 | 0.6417 | 0.95 | 0.7214 | -130.8988 | -4.7505 | 3.3131 | 0.4735 | -5.3815 | -3.924 | 2.423 |  | 0.6815 | -1.2904 | 4.0143 | 3.3632 | 3.3485 | 1.0433 | 10.7243 | 14.198 | 14.7964 | 11.0189 | 0.0004 | -0.0029 | 0.0006 | 0.0041 | 0.0005 | -0.0003 | 0.0188 | -0.0086 | -0.0006 | -360.2081 | 17.4069 | -360.4327 | 17.6471 | -360.7835 | 18.1461 | -360.8635 | 17.5445 | -352.666 | 18.7271 | -352.6413 | 16.8094
12:07 | 2851 | 32.7366 | 198.5567 | 444.5311 | 449.9388 | -18.4551 | -45.2343 | 7.8589 | 4.8983 | -1.3567 | -2.4917 | 0.7652 | -2.5116 | 7.7616 | 1.3596 | 0.6017 | 0.6428 | 0.9506 | 0.7218 | -130.8727 | -4.7297 | 3.3855 | 0.4872 | -5.3806 | -3.8727 | 2.4366 |  | 0.7895 | -1.2243 | 4.0151 | 3.3643 | 3.3515 | 1.0444 | 10.7405 | 14.2429 | 14.8229 | 11.0529 | 0.0003 | -0.0029 | 0.0004 | 0.0036 | 0.0007 | -0.0011 | 0.0061 | -0.0057 | -0.005 | -360.2265 | 17.4582 | -360.5496 | 17.6882 | -360.8081 | 18.1379 | -360.8789 | 17.5568 | -352.7367 | 18.7805 | -352.7429 | 16.8361
12:07 | 2852 | 32.7698 | 198.5737 | 444.5508 | 450.0605 | -18.4564 | -45.2979 | 7.9346 | 4.88 | -1.3612 | -2.519 | 0.7793 | -2.5501 | 7.7457 | 1.4114 | 0.6007 | 0.6434 | 0.95 | 0.7224 | -130.8349 | -4.8315 | 3.2777 | 0.5412 | -5.3705 | -3.8907 | 2.356 |  | 0.827 | -1.2639 | 4.0143 | 3.3641 | 3.3522 | 1.0444 | 10.7129 | 14.1974 | 14.7806 | 11.0725 | -0.0001 | -0.0027 | 0.0007 | 0.0038 | 0.0006 | -0.0002 | 0.024 | -0.0053 | -0.0079 | -360.1711 | 17.4151 | -360.5004 | 17.6759 | -360.8358 | 18.142 | -360.8481 | 17.5219 | -352.666 | 18.7395 | -352.7121 | 16.8484
12:07 | 2853 | 32.8122 | 198.4393 | 444.3944 | 449.9653 | -18.4697 | -45.2271 | 7.9486 | 4.8762 | -1.3469 | -2.3352 | 0.8005 | -2.5482 | 7.7206 | 1.3838 | 0.6016 | 0.6427 | 0.949 | 0.7211 | -130.8319 | -4.7941 | 3.2841 | 0.5826 | -5.4111 | -3.8678 | 2.4066 |  | 0.7936 | -1.2505 | 4.0146 | 3.3641 | 3.3481 | 1.0432 | 10.7486 | 14.2106 | 14.8083 | 11.0435 | -0.0002 | -0.0029 | 0.0017 | 0.0041 | 0.0009 | -0.0009 | 0.0044 | -0.0098 | -0.0087 | -360.1865 | 17.4069 | -360.4512 | 17.6923 | -360.8574 | 18.1871 | -360.9189 | 17.5383 | -352.6629 | 18.7271 | -352.6752 | 16.8443
12:07 | 2854 | 32.7684 | 198.5223 | 444.4542 | 450.0072 | -18.4471 | -45.246 | 8.0052 | 4.9014 | -1.2462 | -2.362 | 0.8284 | -2.3631 | 7.8741 | 1.4674 | 0.6028 | 0.6449 | 0.9487 | 0.7232 | -130.9236 | -4.7883 | 3.233 | 0.5665 | -5.3946 | -3.8742 | 2.4861 |  | 0.7451 | -1.2858 | 4.0142 | 3.3665 | 3.345 | 1.0433 | 10.7279 | 14.2011 | 14.7684 | 11.0522 | 0.0003 | -0.0027 | 0.001 | 0.0036 | 0.0007 | -0.0006 | 0.0075 | -0.0051 | 0 | -360.1988 | 17.4028 | -360.445 | 17.6533 | -360.7927 | 18.1645 | -360.9251 | 17.5568 | -352.7121 | 18.7189 | -352.6598 | 16.832
12:07 | 2855 | 32.7962 | 198.5255 | 444.6105 | 450.1052 | -18.3779 | -45.2134 | 8.019 | 4.9009 | -1.3649 | -2.3816 | 0.8061 | -2.4541 | 7.6949 | 1.4059 | 0.6017 | 0.646 | 0.9488 | 0.7233 | -130.8647 | -4.7899 | 3.2306 | 0.5284 | -5.4319 | -3.8224 | 2.409 |  | 0.7343 | -1.4048 | 4.0135 | 3.3668 | 3.348 | 1.0427 | 10.7001 | 14.208 | 14.7398 | 11.0306 | 0.0002 | -0.0034 | 0.0016 | 0.0042 | 0.0012 | -0.0003 | 0.0088 | -0.0048 | -0.017 | -360.1711 | 17.4274 | -360.4789 | 17.6677 | -360.7989 | 18.1625 | -360.8604 | 17.5342 | -352.669 | 18.7436 | -352.6813 | 16.8279
12:07 | 2856 | 32.8109 | 198.6211 | 444.4656 | 450.034 | -18.3313 | -45.3313 | 7.8859 | 4.8577 | -1.2082 | -2.3953 | 0.8194 | -2.3883 | 7.7222 | 1.398 | 0.6028 | 0.6456 | 0.9511 | 0.7221 | -130.9448 | -4.769 | 3.2438 | 0.4328 | -5.4905 | -3.9336 | 2.3784 |  | 0.7618 | -1.4002 | 4.0148 | 3.3661 | 3.3495 | 1.0426 | 10.7347 | 14.249 | 14.7903 | 11.0464 | 0 | -0.0025 | 0.0008 | 0.0038 | 0.0003 | -0.0006 | 0.0109 | -0.0096 | -0.0251 | -360.1465 | 17.4254 | -360.5435 | 17.7169 | -360.8604 | 18.1769 | -360.882 | 17.528 | -352.6413 | 18.7415 | -352.7798 | 16.8772
12:07 | 2857 | 32.8196 | 198.5209 | 444.4158 | 450.0872 | -18.4242 | -45.2972 | 7.9795 | 4.8912 | -1.2673 | -2.3254 | 0.8901 | -2.4957 | 7.734 | 1.3518 | 0.6024 | 0.6433 | 0.9534 | 0.722 | -130.8242 | -4.603 | 3.3451 | 0.3198 | -5.4559 | -3.9996 | 2.3357 |  | 0.8327 | -1.4293 | 4.0136 | 3.3646 | 3.3497 | 1.0437 | 10.7463 | 14.2373 | 14.8066 | 11.0641 | -0.0002 | -0.0025 | 0.0004 | 0.0037 | 0.0012 | -0.0002 | 0.0316 | -0.0076 | -0.0261 | -360.1742 | 17.3823 | -360.4573 | 17.6697 | -360.8174 | 18.1728 | -360.8943 | 17.5034 | -352.6383 | 18.7087 | -352.6567 | 16.8423
12:07 | 2858 | 32.7846 | 198.5268 | 444.469 | 450.0551 | -18.3901 | -45.3105 | 7.9451 | 4.9802 | -1.2526 | -2.1992 | 0.8836 | -2.5371 | 7.6506 | 1.2336 | 0.6019 | 0.6431 | 0.9494 | 0.7216 | -130.8848 | -4.6149 | 3.2141 | 0.3182 | -5.4625 | -3.9824 | 2.31 |  | 0.7745 | -1.4327 | 4.0136 | 3.3653 | 3.3518 | 1.0436 | 10.7533 | 14.2266 | 14.8059 | 11.0486 | -0.0003 | -0.0031 | 0.0004 | 0.0038 | 0.0004 | -0.0006 | -0.0028 | -0.0093 | -0.0097 | -360.1865 | 17.411 | -360.4789 | 17.6759 | -360.8174 | 18.181 | -360.9066 | 17.5404 | -352.6752 | 18.7271 | -352.6875 | 16.8381
12:07 | 2859 | 32.9325 | 198.6437 | 444.5458 | 450.0227 | -18.4905 | -45.3916 | 8.0715 | 5.0631 | -1.2069 | -2.2536 | 0.8849 | -2.5616 | 7.6977 | 1.3752 | 0.6012 | 0.6438 | 0.9494 | 0.7209 | -130.8423 | -4.6847 | 3.3081 | 0.3264 | -5.4499 | -3.9244 | 2.3001 |  | 0.788 | -1.4734 | 4.015 | 3.365 | 3.3477 | 1.043 | 10.7106 | 14.253 | 14.8021 | 11.0699 | 0.0001 | -0.0025 | -0.0003 | 0.0033 | 0.0005 | -0.0008 | 0.0189 | -0.0069 | -0.0117 | -360.1958 | 17.4439 | -360.5066 | 17.6841 | -360.8235 | 18.1666 | -360.842 | 17.5178 | -352.6998 | 18.7641 | -352.7337 | 16.8443
12:07 | 2860 | 32.8658 | 198.5945 | 444.464 | 450.0364 | -18.2975 | -45.2657 | 8.1217 | 4.9751 | -1.1894 | -2.2684 | 0.8646 | -2.5791 | 7.7601 | 1.3969 | 0.6027 | 0.6411 | 0.951 | 0.722 | -130.8209 | -4.6629 | 3.3232 | 0.3897 | -5.2935 | -3.922 | 2.4082 |  | 0.8517 | -1.4106 | 4.015 | 3.3617 | 3.3454 | 1.0448 | 10.7002 | 14.2308 | 14.7608 | 11.0255 | -0.0003 | -0.0032 | 0.0006 | 0.0034 | 0.001 | -0.0004 | 0.0155 | -0.0037 | 0.0128 | -360.1373 | 17.4069 | -360.4758 | 17.6779 | -360.8081 | 18.1481 | -360.8574 | 17.5013 | -352.6167 | 18.7292 | -352.6967 | 16.8361
12:07 | 2861 | 32.9278 | 198.5841 | 444.5621 | 450.0353 | -18.2796 | -45.2128 | 8.1464 | 5.0196 | -1.3253 | -2.207 | 0.8953 | -2.5664 | 7.7516 | 1.4273 | 0.6013 | 0.6469 | 0.9551 | 0.7225 | -130.9658 | -4.665 | 3.3779 | 0.3512 | -5.3653 | -3.89 | 2.3151 |  | 0.732 | -1.4336 | 4.0139 | 3.366 | 3.3472 | 1.0432 | 10.7267 | 14.2231 | 14.7844 | 11.0165 | -0.0003 | -0.0025 | 0.0012 | 0.0041 | 0.0006 | -0.0006 | -0.0008 | -0.0003 | -0.0173 | -360.1988 | 17.4151 | -360.4942 | 17.7005 | -360.8481 | 18.1851 | -360.9404 | 17.5363 | -352.7183 | 18.7374 | -352.6783 | 16.8423
12:07 | 2862 | 32.9643 | 198.6351 | 444.5563 | 450.0734 | -18.1811 | -45.0875 | 8.0768 | 4.9582 | -1.351 | -2.4257 | 0.7835 | -2.593 | 7.6789 | 1.4317 | 0.6019 | 0.6431 | 0.9511 | 0.7213 | -130.9208 | -4.6442 | 3.3866 | 0.3074 | -5.4014 | -3.8798 | 2.4121 |  | 0.7048 | -1.3776 | 4.0138 | 3.3649 | 3.3472 | 1.0427 | 10.7382 | 14.2291 | 14.7749 | 11.0446 | -0.0002 | -0.0026 | 0.0011 | 0.0037 | 0.0008 | -0.0009 | 0.0031 | -0.0152 | -0.002 | -360.1865 | 17.4048 | -360.4696 | 17.6594 | -360.8081 | 18.1522 | -360.8758 | 17.5301 | -352.6813 | 18.7292 | -352.6937 | 16.8381
12:07 | 2863 | 32.9018 | 198.6042 | 444.5954 | 450.1323 | -18.211 | -45.0848 | 8.0308 | 4.9606 | -1.25 | -2.3232 | 0.8279 | -2.4811 | 7.7497 | 1.4251 | 0.601 | 0.6465 | 0.9527 | 0.721 | -130.9293 | -4.7255 | 3.3064 | 0.4324 | -5.4514 | -3.8679 | 2.3769 |  | 0.7892 | -1.3413 | 4.014 | 3.3607 | 3.344 | 1.0433 | 10.7589 | 14.2329 | 14.8091 | 11.0532 | 0.0003 | -0.003 | 0.0014 | 0.0046 | 0.0008 | 0.0001 | 0.0234 | -0.0134 | -0.0161 | -360.1773 | 17.4336 | -360.4635 | 17.6697 | -360.842 | 18.1666 | -360.8574 | 17.5239 | -352.6783 | 18.7395 | -352.6875 | 16.8402
12:07 | 2864 | 32.9256 | 198.5727 | 444.5598 | 450.0492 | -18.2893 | -44.9358 | 8.1124 | 5.019 | -1.2065 | -2.4336 | 0.857 | -2.6519 | 7.7418 | 1.4622 | 0.6004 | 0.6469 | 0.9522 | 0.7206 | -130.9525 | -4.7577 | 3.2847 | 0.4778 | -5.443 | -4.0028 | 2.3617 |  | 0.7934 | -1.3501 | 4.015 | 3.3645 | 3.3486 | 1.045 | 10.7555 | 14.2582 | 14.8339 | 11.0673 | 0.0002 | -0.003 | 0.0007 | 0.0038 | 0.0006 | -0.0007 | 0.0184 | -0.0096 | -0.0088 | -360.1742 | 17.4151 | -360.485 | 17.6882 | -360.8297 | 18.1871 | -360.8635 | 17.5383 | -352.6813 | 18.7477 | -352.709 | 16.8689
12:07 | 2865 | 32.9227 | 198.6517 | 444.5519 | 450.037 | -18.2763 | -45.0401 | 8.0746 | 5.0158 | -1.2622 | -2.3442 | 0.8803 | -2.5749 | 7.7475 | 1.3506 | 0.6031 | 0.6446 | 0.954 | 0.7218 | -130.9619 | -4.6789 | 3.3082 | 0.36 | -5.4757 | -3.9595 | 2.3771 |  | 0.8035 | -1.3402 | 4.0133 | 3.3643 | 3.3472 | 1.0446 | 10.7555 | 14.2582 | 14.7934 | 11.0673 | -0.0007 | -0.0029 | 0.0002 | 0.0035 | 0.0007 | 0.0002 | 0.0158 | -0.014 | -0.01 | -360.1527 | 17.4028 | -360.4512 | 17.6574 | -360.7897 | 18.1584 | -360.882 | 17.5157 | -352.6444 | 18.7333 | -352.6598 | 16.8238
12:07 | 2866 | 32.8715 | 198.6174 | 444.537 | 450.0715 | -18.2169 | -45.0959 | 8.1344 | 4.9829 | -1.2377 | -2.3176 | 0.7764 | -2.5285 | 7.7946 | 1.4907 | 0.6014 | 0.6446 | 0.9496 | 0.7195 | -130.9821 | -4.6109 | 3.2762 | 0.457 | -5.4554 | -3.9364 | 2.363 |  | 0.7867 | -1.3683 | 4.0132 | 3.3638 | 3.349 | 1.0434 | 10.7498 | 14.2523 | 14.7749 | 11.0735 | 0 | -0.0027 | 0.0007 | 0.004 | 0.0009 | -0.0006 | 0.0148 | -0.014 | 0.0038 | -360.205 | 17.4172 | -360.5035 | 17.68 | -360.8327 | 18.1687 | -360.9097 | 17.5383 | -352.6906 | 18.7518 | -352.709 | 16.8381
12:07 | 2867 | 32.9807 | 198.6294 | 444.6481 | 450.1095 | -18.1645 | -44.9365 | 8.247 | 4.931 | -1.2944 | -2.385 | 0.7722 | -2.5437 | 7.7436 | 1.4446 | 0.6016 | 0.644 | 0.9523 | 0.7192 | -130.9439 | -4.5667 | 3.4389 | 0.4703 | -5.4522 | -3.8442 | 2.4605 |  | 0.762 | -1.5074 | 4.0157 | 3.361 | 3.3467 | 1.0434 | 10.721 | 14.2114 | 14.8181 | 11.0746 | -0.0001 | -0.0033 | 0.0006 | 0.0038 | 0.0004 | -0.0006 | 0.008 | -0.0164 | -0.0099 | -360.1435 | 17.4172 | -360.4819 | 17.68 | -360.805 | 18.183 | -360.8974 | 17.5157 | -352.6537 | 18.7579 | -352.7029 | 16.8484
12:08 | 2868 | 33.0249 | 198.5943 | 444.5601 | 450.0992 | -18.1412 | -44.9522 | 8.2716 | 4.9003 | -1.3517 | -2.3961 | 0.7753 | -2.5009 | 7.7448 | 1.5672 | 0.601 | 0.645 | 0.952 | 0.7198 | -130.9543 | -4.5469 | 3.4684 | 0.4019 | -5.3947 | -3.8759 | 2.4106 |  | 0.7639 | -1.4693 | 4.014 | 3.3626 | 3.3501 | 1.0436 | 10.6955 | 14.2034 | 14.7817 | 11.0548 | 0.0001 | -0.0032 | 0.0009 | 0.0037 | 0.0012 | -0.0008 | 0.0256 | -0.0159 | -0.0214 | -360.165 | 17.3802 | -360.445 | 17.682 | -360.8358 | 18.1584 | -360.8697 | 17.5096 | -352.6567 | 18.7312 | -352.6813 | 16.8484
12:08 | 2869 | 32.9594 | 198.6399 | 444.5255 | 450.108 | -18.1366 | -44.9212 | 8.2473 | 5.012 | -1.2422 | -2.2988 | 0.8539 | -2.4831 | 7.7667 | 1.5846 | 0.6034 | 0.645 | 0.9523 | 0.7205 | -130.9723 | -4.4818 | 3.3765 | 0.3618 | -5.4601 | -3.8224 | 2.4531 |  | 0.7676 | -1.4508 | 4.0137 | 3.3662 | 3.3471 | 1.0433 | 10.7013 | 14.209 | 14.769 | 11.0147 | -0.0004 | -0.0025 | 0.001 | 0.0036 | 0.0004 | -0.0005 | 0.0001 | -0.0062 | -0.0088 | -360.2173 | 17.4213 | -360.4912 | 17.6841 | -360.8543 | 18.1851 | -360.9158 | 17.5424 | -352.6998 | 18.7579 | -352.6844 | 16.832
12:08 | 2870 | 32.9868 | 198.6044 | 444.563 | 450.0123 | -18.2222 | -44.9784 | 8.216 | 4.9722 | -1.2368 | -2.3323 | 0.8317 | -2.4275 | 7.7535 | 1.5332 | 0.603 | 0.6464 | 0.953 | 0.7198 | -130.9611 | -4.6208 | 3.3079 | 0.4245 | -5.4285 | -3.8949 | 2.4349 |  | 0.7796 | -1.4851 | 4.0145 | 3.3614 | 3.3466 | 1.0432 | 10.7081 | 14.1817 | 14.7909 | 11.032 | 0 | -0.0025 | 0.0008 | 0.0034 | 0.0008 | -0.0003 | 0.0103 | 0.0052 | -0.0071 | -360.2081 | 17.4151 | -360.4573 | 17.6553 | -360.8204 | 18.1625 | -360.8666 | 17.528 | -352.666 | 18.7518 | -352.6998 | 16.8135
12:08 | 2871 | 33.0072 | 198.7124 | 444.6465 | 450.0818 | -18.2523 | -45.071 | 8.2175 | 5.0296 | -1.2421 | -2.3483 | 0.8205 | -2.4471 | 7.7619 | 1.4147 | 0.6026 | 0.6467 | 0.9538 | 0.72 | -130.9153 | -4.555 | 3.2994 | 0.286 | -5.5099 | -3.8688 | 2.3956 |  | 0.8812 | -1.4547 | 4.014 | 3.3642 | 3.3467 | 1.0433 | 10.744 | 14.2291 | 14.8155 | 11.0504 | 0.0001 | -0.0028 | 0.0008 | 0.0039 | 0.0011 | -0.0008 | 0.014 | -0.0148 | 0.0026 | -360.1927 | 17.4192 | -360.5004 | 17.6841 | -360.842 | 18.1235 | -360.842 | 17.5075 | -352.6413 | 18.7559 | -352.7306 | 16.8299
12:08 | 2872 | 32.8633 | 198.6522 | 444.5236 | 450.0645 | -18.2569 | -45.0173 | 8.2488 | 4.9994 | -1.2493 | -2.4428 | 0.7854 | -2.5679 | 7.6313 | 1.3846 | 0.6023 | 0.6466 | 0.9515 | 0.7211 | -130.8399 | -4.592 | 3.3612 | 0.2601 | -5.4018 | -3.9026 | 2.4564 |  | 0.7679 | -1.4788 | 4.0121 | 3.362 | 3.3452 | 1.0445 | 10.7474 | 14.2443 | 14.8311 | 11.0594 | 0.0002 | -0.0032 | 0.0006 | 0.0037 | 0.0001 | -0.0005 | 0.0169 | 0.0022 | -0.0167 | -360.1804 | 17.4213 | -360.5281 | 17.7005 | -360.8727 | 18.1892 | -360.8943 | 17.5178 | -352.6567 | 18.7559 | -352.7183 | 16.8648
12:08 | 2873 | 32.9426 | 198.6613 | 444.5413 | 450.1032 | -18.2114 | -44.9881 | 8.1911 | 4.9988 | -1.2514 | -2.2601 | 0.8083 | -2.5423 | 7.6648 | 1.3901 | 0.6027 | 0.6466 | 0.954 | 0.7198 | -130.904 | -4.5853 | 3.2515 | 0.2471 | -5.4285 | -3.9945 | 2.4271 |  | 0.7807 | -1.4368 | 4.0136 | 3.364 | 3.3504 | 1.0438 | 10.7578 | 14.2492 | 14.8145 | 11.0518 | 0 | -0.0025 | 0 | 0.0038 | 0.0011 | -0.0004 | 0.001 | -0.0113 | -0.0061 | -360.1588 | 17.3802 | -360.4142 | 17.6636 | -360.8204 | 18.1666 | -360.8789 | 17.5404 | -352.6506 | 18.7107 | -352.6413 | 16.8279
12:08 | 2874 | 32.8309 | 198.6073 | 444.5648 | 450.1142 | -18.2182 | -45.0875 | 8.1362 | 4.9714 | -1.3371 | -2.4757 | 0.7803 | -2.6021 | 7.6236 | 1.3504 | 0.6029 | 0.6486 | 0.9553 | 0.7202 | -130.9326 | -4.5367 | 3.3052 | 0.2671 | -5.4425 | -3.9067 | 2.3866 |  | 0.8024 | -1.4925 | 4.0131 | 3.3626 | 3.3444 | 1.0436 | 10.7545 | 14.2163 | 14.7725 | 11.0439 | -0.0002 | -0.0027 | 0.0008 | 0.0039 | 0.0007 | -0.0002 | 0.0066 | -0.0052 | 0.0176 | -360.2296 | 17.4377 | -360.4912 | 17.6574 | -360.7989 | 18.1666 | -360.8943 | 17.5424 | -352.7644 | 18.762 | -352.6721 | 16.8135
12:08 | 2875 | 32.9112 | 198.6557 | 444.5003 | 450.0784 | -18.2184 | -45.0917 | 8.169 | 4.9614 | -1.2403 | -2.3754 | 0.6833 | -2.5379 | 7.7242 | 1.3991 | 0.6027 | 0.6436 | 0.9524 | 0.7207 | -130.9071 | -4.5509 | 3.2946 | 0.2874 | -5.4168 | -3.912 | 2.3535 |  | 0.7916 | -1.4159 | 4.0139 | 3.363 | 3.3504 | 1.0424 | 10.7209 | 14.2059 | 14.797 | 11.0623 | -0.0001 | -0.0042 | 0.0005 | 0.0038 | 0.0008 | -0.0006 | 0.0086 | -0.0102 | -0.0077 | -360.2142 | 17.4213 | -360.5004 | 17.6697 | -360.8358 | 18.1563 | -360.8389 | 17.5137 | -352.7029 | 18.7641 | -352.7398 | 16.8402
12:08 | 2876 | 32.9147 | 198.5454 | 444.5951 | 450.0644 | -18.2732 | -45.0555 | 8.1627 | 4.9312 | -1.314 | -2.3537 | 0.7165 | -2.6214 | 7.7649 | 1.4938 | 0.602 | 0.6435 | 0.9527 | 0.7213 | -130.8398 | -4.4495 | 3.3004 | 0.3089 | -5.3061 | -3.8818 | 2.446 |  | 0.8002 | -1.3885 | 4.0148 | 3.363 | 3.3474 | 1.0444 | 10.7153 | 14.217 | 14.7649 | 11.0461 | 0.0003 | -0.0031 | 0.0005 | 0.0032 | 0.0002 | -0.0006 | 0.0189 | -0.01 | -0.019 | -360.1034 | 17.3843 | -360.4635 | 17.6779 | -360.8389 | 18.1769 | -360.8604 | 17.4952 | -352.586 | 18.721 | -352.6813 | 16.8381
12:08 | 2877 | 32.9292 | 198.5629 | 444.4009 | 450.0925 | -18.3451 | -45.0701 | 8.0931 | 4.958 | -1.2357 | -2.36 | 0.6459 | -2.5782 | 7.6941 | 1.4697 | 0.6041 | 0.6459 | 0.9529 | 0.7229 | -130.8636 | -4.4833 | 3.2922 | 0.2956 | -5.4279 | -4.0447 | 2.3724 |  | 0.8405 | -1.3644 | 4.0137 | 3.3591 | 3.3435 | 1.0428 | 10.7059 | 14.1964 | 14.7687 | 11.0306 | -0.0003 | -0.0031 | 0.0012 | 0.0041 | 0.0009 | -0.0009 | -0.0045 | -0.0107 | -0.0157 | -360.2358 | 17.4028 | -360.4542 | 17.6759 | -360.8358 | 18.2056 | -360.9404 | 17.5486 | -352.7152 | 18.7333 | -352.6629 | 16.832
12:08 | 2878 | 32.9398 | 198.6031 | 444.4315 | 450.0559 | -18.3068 | -45.0601 | 8.0833 | 4.9527 | -1.2174 | -2.4126 | 0.6634 | -2.4873 | 7.7367 | 1.4866 | 0.602 | 0.6467 | 0.9516 | 0.7206 | -130.8926 | -4.4603 | 3.3387 | 0.2647 | -5.4479 | -4.0265 | 2.3522 |  | 0.7604 | -1.3333 | 4.0149 | 3.3622 | 3.3467 | 1.0434 | 10.6977 | 14.2001 | 14.7739 | 11.045 | 0.0001 | -0.0022 | 0.0007 | 0.0036 | 0.0008 | -0.0007 | 0.0104 | -0.0021 | -0.018 | -360.1835 | 17.4028 | -360.4512 | 17.6574 | -360.7497 | 18.1481 | -360.8666 | 17.5321 | -352.7029 | 18.7292 | -352.6844 | 16.8279
12:08 | 2879 | 32.888 | 198.6847 | 444.4945 | 450.0737 | -18.364 | -45.0881 | 8.0997 | 4.9969 | -1.1439 | -2.3687 | 0.6341 | -2.4896 | 7.6798 | 1.5001 | 0.6025 | 0.6431 | 0.9511 | 0.72 | -130.8851 | -4.5906 | 3.3364 | 0.2626 | -5.3858 | -4.0141 | 2.3722 |  | 0.8019 | -1.4534 | 4.0142 | 3.3647 | 3.3502 | 1.0441 | 10.7417 | 14.2151 | 14.7769 | 11.0601 | -0.0004 | -0.0028 | 0.0006 | 0.0036 | 0.0008 | -0.0007 | 0.0182 | -0.0091 | -0.0043 | -360.2111 | 17.4336 | -360.5373 | 17.6779 | -360.8543 | 18.1543 | -360.8112 | 17.5055 | -352.6906 | 18.7518 | -352.7244 | 16.8443
12:08 | 2880 | 32.968 | 198.6994 | 444.5246 | 450.0612 | -18.2969 | -45.0767 | 8.0725 | 4.9079 | -1.2233 | -2.3885 | 0.6372 | -2.5023 | 7.7149 | 1.5937 | 0.601 | 0.6444 | 0.9525 | 0.7199 | -130.8776 | -4.5874 | 3.4568 | 0.2607 | -5.3607 | -3.9009 | 2.3585 |  | 0.7684 | -1.5167 | 4.016 | 3.3598 | 3.3484 | 1.0452 | 10.7348 | 14.2254 | 14.8045 | 11.0533 | 0.0003 | -0.003 | 0.0003 | 0.0036 | 0.0008 | -0.0003 | 0.0023 | -0.0056 | -0.0056 | -360.1404 | 17.409 | -360.5004 | 17.7108 | -360.8974 | 18.1871 | -360.885 | 17.5137 | -352.6721 | 18.7477 | -352.7244 | 16.8731
12:08 | 2881 | 33.0116 | 198.7654 | 444.583 | 450.1927 | -18.1865 | -45.0291 | 8.1424 | 4.9097 | -1.1931 | -2.5334 | 0.747 | -2.4951 | 7.7634 | 1.5399 | 0.6028 | 0.6425 | 0.9539 | 0.7216 | -130.8932 | -4.5493 | 3.3668 | 0.2478 | -5.334 | -3.893 | 2.4072 |  | 0.7882 | -1.4277 | 4.0151 | 3.3652 | 3.351 | 1.0452 | 10.773 | 14.2579 | 14.8028 | 11.0334 | -0.0001 | -0.0029 | 0.0003 | 0.0032 | 0.0005 | -0.0003 | 0.0174 | -0.0027 | 0.0051 | -360.1158 | 17.3864 | -360.4266 | 17.6553 | -360.805 | 18.1707 | -360.8727 | 17.5096 | -352.6629 | 18.7251 | -352.6383 | 16.8279
12:08 | 2882 | 32.9693 | 198.7139 | 444.5128 | 450.1186 | -18.2403 | -44.9575 | 8.1398 | 4.8289 | -1.2189 | -2.63 | 0.7313 | -2.5189 | 7.775 | 1.4267 | 0.6026 | 0.647 | 0.9517 | 0.7204 | -130.8596 | -4.5658 | 3.4184 | 0.261 | -5.3515 | -3.9044 | 2.3092 |  | 0.7924 | -1.4986 | 4.016 | 3.3687 | 3.351 | 1.0446 | 10.7463 | 14.2198 | 14.8056 | 11.076 | -0.0006 | -0.0027 | 0.0007 | 0.0041 | 0.0011 | -0.0003 | 0.0121 | -0.0115 | -0.0197 | -360.1927 | 17.4213 | -360.4666 | 17.6492 | -360.7958 | 18.1604 | -360.8943 | 17.5445 | -352.7121 | 18.7497 | -352.6813 | 16.8135
12:08 | 2883 | 33.0135 | 198.6447 | 444.4883 | 450.132 | -18.2165 | -44.9192 | 8.2052 | 4.9146 | -1.2046 | -2.5656 | 0.8133 | -2.4924 | 7.7315 | 1.5356 | 0.6014 | 0.6444 | 0.9505 | 0.7198 | -130.8579 | -4.6699 | 3.3815 | 0.3263 | -5.3538 | -3.9365 | 2.3315 |  | 0.7935 | -1.4908 | 4.0142 | 3.3626 | 3.3466 | 1.0451 | 10.729 | 14.2487 | 14.7998 | 11.0529 | -0.0001 | -0.0025 | 0.0009 | 0.0036 | 0.0004 | -0.0006 | 0.0147 | -0.0033 | -0.0113 | -360.1988 | 17.4459 | -360.5312 | 17.68 | -360.842 | 18.142 | -360.8666 | 17.528 | -352.706 | 18.7744 | -352.746 | 16.8546
12:08 | 2884 | 32.9803 | 198.6189 | 444.4759 | 450.0212 | -18.2996 | -44.9426 | 8.177 | 4.9521 | -1.3057 | -2.6374 | 0.7928 | -2.413 | 7.7618 | 1.4903 | 0.6026 | 0.647 | 0.9522 | 0.7205 | -130.8853 | -4.6472 | 3.3534 | 0.3916 | -5.3011 | -4.0137 | 2.3951 |  | 0.7212 | -1.4483 | 4.0142 | 3.3631 | 3.3494 | 1.0443 | 10.6932 | 14.2185 | 14.7858 | 11.0407 | 0.0001 | -0.0032 | 0.0006 | 0.0035 | 0.0007 | -0.0009 | 0.0142 | -0.0025 | 0.0077 | -360.1342 | 17.3987 | -360.4696 | 17.6738 | -360.8297 | 18.1502 | -360.8358 | 17.5013 | -352.626 | 18.7271 | -352.6998 | 16.8443
12:08 | 2885 | 33.0027 | 198.7571 | 444.5594 | 450.1826 | -18.3155 | -44.9536 | 8.232 | 4.9907 | -1.3001 | -2.4916 | 0.8041 | -2.5124 | 7.7589 | 1.4478 | 0.6032 | 0.645 | 0.9557 | 0.7205 | -130.8628 | -4.6338 | 3.3802 | 0.4292 | -5.2663 | -3.8679 | 2.4274 |  | 0.7401 | -1.4354 | 4.0144 | 3.3615 | 3.3494 | 1.0451 | 10.729 | 14.2256 | 14.794 | 11.0414 | -0.0001 | -0.0031 | 0.0008 | 0.0036 | 0.0008 | 0.0001 | 0.0026 | -0.0131 | -0.0119 | -360.2235 | 17.3987 | -360.4512 | 17.6759 | -360.8358 | 18.1974 | -360.9158 | 17.528 | -352.666 | 18.721 | -352.6444 | 16.8402
12:08 | 2886 | 33.0054 | 198.6677 | 444.6006 | 450.087 | -18.2878 | -44.8832 | 8.1778 | 4.9381 | -1.2999 | -2.5034 | 0.8086 | -2.4987 | 7.7303 | 1.4837 | 0.6038 | 0.6483 | 0.9525 | 0.7198 | -130.8936 | -4.563 | 3.2995 | 0.519 | -5.2458 | -3.8919 | 2.484 |  | 0.794 | -1.3154 | 4.0151 | 3.3646 | 3.3485 | 1.0432 | 10.7117 | 14.2311 | 14.7745 | 11.0594 | -0.0003 | -0.0029 | 0.0008 | 0.0038 | 0.0009 | -0.0012 | 0.0253 | -0.0219 | -0.0002 | -360.2296 | 17.4069 | -360.445 | 17.6553 | -360.7835 | 18.1728 | -360.9251 | 17.5547 | -352.7337 | 18.7538 | -352.6813 | 16.8217
12:08 | 2887 | 32.8721 | 198.6154 | 444.5393 | 450.0774 | -18.3077 | -44.8296 | 8.1275 | 4.9892 | -1.2988 | -2.5117 | 0.8771 | -2.4443 | 7.8034 | 1.5378 | 0.6019 | 0.6454 | 0.9537 | 0.7203 | -130.8953 | -4.5432 | 3.3488 | 0.5636 | -5.222 | -3.8377 | 2.4867 |  | 0.8222 | -1.3105 | 4.0146 | 3.3635 | 3.3467 | 1.0436 | 10.7486 | 14.2395 | 14.8083 | 11.0435 | -0.0002 | -0.0025 | 0.0006 | 0.0038 | 0.0005 | -0.0005 | 0.0102 | -0.0257 | -0.0083 | -360.1742 | 17.409 | -360.4819 | 17.6574 | -360.7958 | 18.144 | -360.8358 | 17.5137 | -352.6721 | 18.7436 | -352.6629 | 16.8279
12:08 | 2888 | 32.9225 | 198.634 | 444.5507 | 450.0908 | -18.2796 | -44.8697 | 8.1713 | 4.9977 | -1.3216 | -2.5504 | 0.8114 | -2.4143 | 7.8242 | 1.5927 | 0.6029 | 0.6445 | 0.9533 | 0.7202 | -130.9413 | -4.6262 | 3.4087 | 0.514 | -5.3067 | -3.8605 | 2.4388 |  | 0.7137 | -1.3247 | 4.0138 | 3.3608 | 3.3514 | 1.0439 | 10.7578 | 14.249 | 14.8019 | 11.0695 | 0.0002 | -0.0029 | 0.0004 | 0.0037 | 0.0011 | -0.0004 | 0.01 | 0.0027 | -0.0248 | -360.1588 | 17.4213 | -360.5404 | 17.6964 | -360.8727 | 18.1892 | -360.882 | 17.5096 | -352.6475 | 18.7333 | -352.6998 | 16.8566
12:08 | 2889 | 32.9296 | 198.6146 | 444.6001 | 450.182 | -18.3019 | -44.9233 | 8.1014 | 5.0577 | -1.1939 | -2.4716 | 0.9322 | -2.4482 | 7.8102 | 1.6588 | 0.6032 | 0.6443 | 0.9524 | 0.7205 | -130.888 | -4.6321 | 3.3864 | 0.6188 | -5.266 | -3.8581 | 2.4956 |  | 0.8252 | -1.4643 | 4.0139 | 3.3636 | 3.3504 | 1.0442 | 10.7487 | 14.2336 | 14.7783 | 11.0439 | 0 | -0.0033 | 0.0007 | 0.004 | 0.0011 | -0.0002 | -0.0036 | -0.0174 | -0.0223 | -360.1619 | 17.3802 | -360.4266 | 17.68 | -360.8358 | 18.1851 | -360.8974 | 17.5321 | -352.6906 | 18.7128 | -352.6629 | 16.8423
12:08 | 2890 | 33.0031 | 198.5882 | 444.5432 | 450.1947 | -18.3199 | -44.9124 | 8.0029 | 4.8891 | -1.203 | -2.6108 | 0.9182 | -2.3705 | 7.8733 | 1.5424 | 0.6034 | 0.6443 | 0.9491 | 0.7197 | -130.7951 | -4.6413 | 3.3952 | 0.6631 | -5.2707 | -3.9243 | 2.4569 |  | 0.7687 | -1.4761 | 4.014 | 3.3623 | 3.3502 | 1.0448 | 10.7359 | 14.2499 | 14.7838 | 11.0482 | -0.0002 | -0.0031 | 0.0007 | 0.0042 | 0.0003 | -0.0002 | -0.0066 | -0.0142 | -0.0135 | -360.2081 | 17.4151 | -360.4758 | 17.6574 | -360.762 | 18.142 | -360.8974 | 17.5116 | -352.6567 | 18.7456 | -352.6567 | 16.8115
12:08 | 2891 | 33.0666 | 198.6486 | 444.5794 | 450.1941 | -18.3482 | -44.9109 | 8.0237 | 4.9493 | -1.2142 | -2.5188 | 0.9431 | -2.3615 | 7.8411 | 1.4892 | 0.6033 | 0.6465 | 0.9546 | 0.7203 | -130.8437 | -4.6006 | 3.3069 | 0.5792 | -5.3178 | -3.8621 | 2.493 |  | 0.7491 | -1.3686 | 4.0141 | 3.3623 | 3.3489 | 1.0447 | 10.751 | 14.2358 | 14.78 | 11.0522 | -0.0004 | -0.0026 | 0.0009 | 0.0039 | 0.0006 | -0.0007 | 0.0136 | -0.0098 | -0.0007 | -360.1527 | 17.4336 | -360.5343 | 17.7108 | -360.8697 | 18.1625 | -360.8512 | 17.5157 | -352.6937 | 18.7497 | -352.7183 | 16.871
12:08 | 2892 | 32.9844 | 198.6455 | 444.5671 | 450.1181 | -18.3119 | -44.8328 | 8.1358 | 4.9735 | -1.041 | -2.4578 | 0.9422 | -2.3277 | 7.8509 | 1.6128 | 0.6039 | 0.6434 | 0.9534 | 0.7219 | -130.8626 | -4.639 | 3.2977 | 0.5399 | -5.2948 | -3.7947 | 2.527 |  | 0.7091 | -1.3921 | 4.0153 | 3.363 | 3.3455 | 1.0438 | 10.7268 | 14.1998 | 14.7775 | 11.0111 | -0.0004 | -0.0029 | 0.0004 | 0.0035 | 0.0004 | -0.0007 | 0.0147 | -0.015 | 0.015 | -360.1435 | 17.3905 | -360.4573 | 17.6738 | -360.845 | 18.1728 | -360.8635 | 17.4952 | -352.6813 | 18.7333 | -352.669 | 16.8381
12:08 | 2893 | 33.0019 | 198.6167 | 444.5622 | 450.1964 | -18.1638 | -44.7762 | 8.2725 | 4.9104 | -1.1367 | -2.3377 | 1.0534 | -2.3086 | 7.8884 | 1.6232 | 0.602 | 0.6463 | 0.9527 | 0.7219 | -130.9145 | -4.6662 | 3.3559 | 0.5345 | -5.3425 | -3.8594 | 2.489 |  | 0.7654 | -1.396 | 4.0162 | 3.3623 | 3.3479 | 1.045 | 10.7128 | 14.2208 | 14.7711 | 11.0139 | 0.0002 | -0.0032 | 0.001 | 0.0039 | 0.0011 | -0.0006 | 0.0019 | -0.0094 | -0.0263 | -360.1711 | 17.3946 | -360.4696 | 17.6594 | -360.805 | 18.1666 | -360.9035 | 17.5239 | -352.7029 | 18.7251 | -352.6567 | 16.8115
12:08 | 2894 | 33.044 | 198.6947 | 444.6273 | 450.2752 | -18.1303 | -44.7328 | 8.276 | 4.9463 | -1.2004 | -2.4058 | 1.0422 | -2.3189 | 7.8408 | 1.619 | 0.6022 | 0.6455 | 0.9515 | 0.7228 | -130.9279 | -4.7057 | 3.2876 | 0.5296 | -5.3351 | -3.7935 | 2.4996 |  | 0.7511 | -1.4138 | 4.0149 | 3.361 | 3.3506 | 1.0443 | 10.7164 | 14.2125 | 14.8021 | 11.0122 | -0.0001 | -0.003 | 0.0008 | 0.0034 | 0.0005 | -0.0004 | 0.0212 | -0.0047 | 0.0002 | -360.2173 | 17.4541 | -360.5158 | 17.6902 | -360.8358 | 18.1666 | -360.8727 | 17.5363 | -352.749 | 18.7805 | -352.7614 | 16.8361
12:08 | 2895 | 33.0294 | 198.6335 | 444.6098 | 450.2517 | -18.1178 | -44.6495 | 8.2236 | 4.9044 | -1.1194 | -2.4426 | 0.98 | -2.5531 | 7.7916 | 1.5213 | 0.6028 | 0.643 | 0.9519 | 0.7213 | -130.8777 | -4.7586 | 3.2892 | 0.6389 | -5.3275 | -3.8016 | 2.5016 |  | 0.7111 | -1.419 | 4.015 | 3.3603 | 3.3472 | 1.0441 | 10.7185 | 14.2094 | 14.7896 | 11.0078 | -0.0001 | -0.0024 | 0.0006 | 0.0036 | 0.0013 | -0.0007 | -0.0101 | -0.0136 | 0.0103 | -360.1342 | 17.409 | -360.485 | 17.6944 | -360.8327 | 18.1543 | -360.8727 | 17.5096 | -352.6383 | 18.7333 | -352.709 | 16.8505
12:08 | 2896 | 32.9742 | 198.6995 | 444.6349 | 450.2504 | -18.1445 | -44.7076 | 8.2344 | 5.0005 | -1.0955 | -2.4573 | 1.0404 | -2.4624 | 7.8717 | 1.5753 | 0.6029 | 0.6453 | 0.9534 | 0.7246 | -130.8603 | -4.6509 | 3.2582 | 0.5196 | -5.4067 | -3.8143 | 2.4665 |  | 0.7767 | -1.4673 | 4.0144 | 3.3638 | 3.3482 | 1.0431 | 10.7544 | 14.2397 | 14.7978 | 11.0663 | 0 | -0.0027 | 0.0006 | 0.0039 | 0.0005 | -0.0001 | 0.0221 | 0.0007 | 0.0108 | -360.1404 | 17.3802 | -360.4327 | 17.6779 | -360.8143 | 18.1707 | -360.8697 | 17.5198 | -352.6537 | 18.7066 | -352.6506 | 16.832
12:08 | 2897 | 32.9963 | 198.7637 | 444.6753 | 450.2686 | -18.2199 | -44.735 | 8.2995 | 4.9679 | -1.1299 | -2.3748 | 0.9051 | -2.4842 | 7.8275 | 1.5593 | 0.6021 | 0.6469 | 0.9512 | 0.724 | -130.8109 | -4.7735 | 3.261 | 0.5918 | -5.2948 | -3.7816 | 2.5084 |  | 0.741 | -1.4951 | 4.016 | 3.3647 | 3.3479 | 1.0444 | 10.7624 | 14.2364 | 14.8132 | 11.0507 | 0.0005 | -0.0029 | 0.0006 | 0.0038 | 0.0005 | -0.0006 | 0.0125 | -0.0067 | -0.0035 | -360.2204 | 17.4254 | -360.4881 | 17.6882 | -360.8204 | 18.1728 | -360.9127 | 17.5527 | -352.7275 | 18.7497 | -352.6875 | 16.8279
12:08 | 2898 | 33.0869 | 198.6967 | 444.7485 | 450.308 | -18.2908 | -44.836 | 8.1517 | 4.9293 | -1.0996 | -2.2773 | 0.9641 | -2.5029 | 7.8038 | 1.5522 | 0.6025 | 0.6423 | 0.9498 | 0.7233 | -130.8614 | -4.7331 | 3.2673 | 0.5789 | -5.2737 | -3.8594 | 2.4613 |  | 0.7416 | -1.3292 | 4.0166 | 3.3626 | 3.3486 | 1.044 | 10.7404 | 14.2374 | 14.8251 | 11.0406 | 0 | -0.003 | 0.0012 | 0.0044 | 0.0009 | -0.0004 | 0.0046 | 0.0011 | -0.0093 | -360.1527 | 17.4131 | -360.4789 | 17.7046 | -360.8204 | 18.1502 | -360.8389 | 17.5116 | -352.6721 | 18.7312 | -352.6783 | 16.8443
12:08 | 2899 | 33.0085 | 198.6868 | 444.6415 | 450.2024 | -18.2755 | -44.8872 | 8.0822 | 4.9839 | -1.028 | -2.2564 | 1.0382 | -2.4344 | 7.8216 | 1.615 | 0.6026 | 0.6479 | 0.9566 | 0.7237 | -130.9333 | -4.7511 | 3.2222 | 0.5594 | -5.2663 | -3.8035 | 2.457 |  | 0.6587 | -1.4705 | 4.0154 | 3.3667 | 3.3517 | 1.0435 | 10.7498 | 14.2465 | 14.7865 | 11.033 | 0 | -0.0022 | 0.0009 | 0.0042 | 0.0007 | -0.0008 | 0.0174 | -0.0045 | 0.0027 | -360.1065 | 17.3925 | -360.4727 | 17.7046 | -360.8481 | 18.1748 | -360.8635 | 17.4931 | -352.629 | 18.7189 | -352.6721 | 16.834
12:08 | 2900 | 33.0756 | 198.7828 | 444.7001 | 450.2853 | -18.3468 | -44.916 | 8.1039 | 4.9812 | -1.0684 | -2.3399 | 0.9721 | -2.4243 | 7.8737 | 1.5879 | 0.6018 | 0.6448 | 0.9479 | 0.7203 | -130.8784 | -4.7335 | 3.3008 | 0.6146 | -5.3574 | -3.7713 | 2.483 |  | 0.735 | -1.5124 | 4.0152 | 3.3675 | 3.3539 | 1.0432 | 10.7372 | 14.2391 | 14.782 | 11.0331 | -0.0004 | -0.0028 | 0.0005 | 0.0031 | 0.0008 | -0.0007 | 0.0105 | -0.003 | -0.0098 | -360.1773 | 17.411 | -360.4819 | 17.7169 | -360.8389 | 18.1912 | -360.9435 | 17.5486 | -352.6906 | 18.723 | -352.6937 | 16.8402
12:08 | 2901 | 33.09 | 198.794 | 444.712 | 450.348 | -18.2909 | -44.9739 | 8.0989 | 5.0161 | -1.0936 | -2.3674 | 0.8923 | -2.4512 | 7.8743 | 1.6213 | 0.6022 | 0.6478 | 0.9525 | 0.7203 | -130.8518 | -4.7176 | 3.2975 | 0.7255 | -5.3175 | -3.8337 | 2.4723 |  | 0.8504 | -1.5497 | 4.0164 | 3.3625 | 3.3485 | 1.0439 | 10.6841 | 14.2087 | 14.7322 | 11.0155 | -0.0001 | -0.0033 | 0.0007 | 0.0036 | 0.0004 | -0.0008 | 0.0081 | -0.0014 | -0.0095 | -360.1527 | 17.4192 | -360.4727 | 17.7026 | -360.7927 | 18.1502 | -360.885 | 17.526 | -352.706 | 18.7538 | -352.7152 | 16.8299
12:08 | 2902 | 33.0252 | 198.7341 | 444.7165 | 450.2699 | -18.3627 | -45.0178 | 8.0668 | 5.0381 | -1.1056 | -2.2441 | 0.8955 | -2.5208 | 7.8893 | 1.5298 | 0.6019 | 0.6471 | 0.9518 | 0.7224 | -130.8563 | -4.7325 | 3.3747 | 0.7171 | -5.3204 | -3.8417 | 2.583 |  | 0.7401 | -1.5716 | 4.0152 | 3.3667 | 3.3471 | 1.044 | 10.7072 | 14.1626 | 14.7448 | 11.0035 | 0.0003 | -0.0029 | 0.0007 | 0.0034 | 0.0008 | -0.0009 | 0.0025 | -0.016 | -0.007 | -360.1527 | 17.3905 | -360.4942 | 17.7252 | -360.8235 | 18.1399 | -360.8266 | 17.4911 | -352.6075 | 18.7169 | -352.6906 | 16.8628
12:08 | 2903 | 33.0218 | 198.606 | 444.4766 | 450.2027 | -18.2814 | -44.8417 | 8.1627 | 5.0625 | -1.0346 | -2.2668 | 0.9422 | -2.4765 | 7.8636 | 1.5573 | 0.6014 | 0.6475 | 0.9521 | 0.7208 | -130.9239 | -4.7102 | 3.3214 | 0.7261 | -5.1928 | -3.8089 | 2.6041 |  | 0.7529 | -1.4434 | 4.0146 | 3.3633 | 3.3491 | 1.0443 | 10.691 | 14.1927 | 14.7462 | 11.0219 | -0.0002 | -0.0027 | 0.0005 | 0.0037 | 0.0008 | -0.0004 | 0.0098 | -0.0162 | 0.0066 | -360.1435 | 17.4172 | -360.5066 | 17.7334 | -360.8789 | 18.2015 | -360.8912 | 17.5157 | -352.6813 | 18.7436 | -352.6783 | 16.8566
12:08 | 2904 | 33.0573 | 198.6703 | 444.569 | 450.2787 | -18.269 | -44.7948 | 8.0811 | 5.0177 | -1.0385 | -2.3703 | 0.9865 | -2.4371 | 7.8711 | 1.5425 | 0.6028 | 0.6472 | 0.953 | 0.722 | -130.9125 | -4.7234 | 3.399 | 0.7935 | -5.1713 | -3.7782 | 2.5955 |  | 0.7519 | -1.5024 | 4.014 | 3.3632 | 3.353 | 1.0448 | 10.737 | 14.2337 | 14.8141 | 11.0666 | -0.0003 | -0.0029 | 0.0011 | 0.0041 | 0.0013 | -0.0006 | 0.0108 | -0.0159 | -0.0001 | -360.1896 | 17.4028 | -360.4666 | 17.6985 | -360.8174 | 18.1769 | -360.9097 | 17.5424 | -352.6844 | 18.7395 | -352.6937 | 16.8279
12:08 | 2905 | 33.1061 | 198.6721 | 444.5992 | 450.1946 | -18.2284 | -44.8121 | 8.1457 | 4.9645 | -1.1275 | -2.3742 | 0.9026 | -2.416 | 7.9202 | 1.6408 | 0.6026 | 0.6504 | 0.9519 | 0.7226 | -130.9057 | -4.7454 | 3.4077 | 0.7102 | -5.2776 | -3.8051 | 2.6027 |  | 0.7651 | -1.5379 | 4.0152 | 3.3628 | 3.3475 | 1.0443 | 10.7347 | 14.2721 | 14.8251 | 11.029 | 0.0004 | -0.0029 | 0.001 | 0.0039 | 0.0007 | -0.0001 | 0.0045 | -0.0183 | -0.0181 | -360.1681 | 17.4233 | -360.4912 | 17.6902 | -360.7773 | 18.1317 | -360.8174 | 17.5096 | -352.6783 | 18.7518 | -352.6967 | 16.8156
12:08 | 2906 | 33.0764 | 198.7637 | 444.611 | 450.2337 | -18.2621 | -44.8804 | 8.1371 | 4.9705 | -1.1365 | -2.3505 | 0.8933 | -2.4988 | 7.9551 | 1.626 | 0.6035 | 0.6493 | 0.9544 | 0.7234 | -130.8398 | -4.7467 | 3.4752 | 0.7494 | -5.2802 | -3.7772 | 2.5462 |  | 0.8288 | -1.5223 | 4.0139 | 3.3599 | 3.3469 | 1.0432 | 10.7648 | 14.221 | 14.8011 | 11.0771 | 0 | -0.0031 | 0.0003 | 0.0038 | 0.0013 | -0.0004 | -0.0016 | -0.008 | -0.0238 | -360.165 | 17.4233 | -360.5312 | 17.7313 | -360.8543 | 18.1625 | -360.8604 | 17.5239 | -352.6352 | 18.7353 | -352.7121 | 16.8566
12:08 | 2907 | 33.0225 | 198.7141 | 444.6025 | 450.2504 | -18.28 | -44.9763 | 8.1122 | 5.0235 | -1.0829 | -2.3037 | 0.9408 | -2.5308 | 7.9266 | 1.6241 | 0.6021 | 0.6461 | 0.9531 | 0.723 | -130.8308 | -4.7221 | 3.379 | 0.5126 | -5.2538 | -3.8682 | 2.5168 |  | 0.8429 | -1.4715 | 4.015 | 3.3631 | 3.3465 | 1.0442 | 10.7522 | 14.2428 | 14.7929 | 11.0417 | -0.0003 | -0.0027 | 0.0009 | 0.0038 | 0.0004 | -0.0004 | -0.0029 | -0.0147 | -0.0242 | -360.1958 | 17.3946 | -360.4696 | 17.7149 | -360.8574 | 18.1953 | -360.9004 | 17.5363 | -352.7152 | 18.7312 | -352.6844 | 16.8484
12:08 | 2908 | 33.0951 | 198.7183 | 444.5426 | 450.1792 | -18.3687 | -44.9729 | 8.0092 | 5.0289 | -1.0554 | -2.203 | 0.9957 | -2.4433 | 7.8937 | 1.6665 | 0.6031 | 0.6458 | 0.9512 | 0.7223 | -130.8505 | -4.7174 | 3.3259 | 0.4936 | -5.2862 | -3.8705 | 2.5783 |  | 0.7501 | -1.3979 | 4.0158 | 3.3621 | 3.3496 | 1.043 | 10.7521 | 14.2429 | 14.8229 | 11.0587 | -0.0004 | -0.0026 | 0.0007 | 0.0037 | 0.0007 | -0.0005 | 0.0159 | -0.0206 | 0.0084 | -360.1988 | 17.4028 | -360.4573 | 17.6718 | -360.7743 | 18.1461 | -360.882 | 17.5342 | -352.7213 | 18.7312 | -352.6537 | 16.8156
12:08 | 2909 | 33.1109 | 198.7192 | 444.5881 | 450.1854 | -18.3224 | -44.9539 | 8.0735 | 5.0536 | -1.0351 | -2.0929 | 0.9391 | -2.4139 | 7.9026 | 1.6939 | 0.6029 | 0.6478 | 0.9521 | 0.7216 | -130.865 | -4.8077 | 3.4084 | 0.479 | -5.2858 | -3.7083 | 2.6442 |  | 0.8231 | -1.4039 | 4.0139 | 3.3604 | 3.3493 | 1.0429 | 10.7059 | 14.1964 | 14.7745 | 11.0132 | -0.0001 | -0.0031 | 0.0008 | 0.0041 | 0.0006 | -0.0007 | 0.0136 | 0.0029 | -0.0101 | -360.1773 | 17.4274 | -360.4912 | 17.7108 | -360.8358 | 18.1461 | -360.8574 | 17.5198 | -352.6813 | 18.7477 | -352.6998 | 16.832
12:08 | 2910 | 33.0641 | 198.7465 | 444.6108 | 450.2032 | -18.3426 | -44.8951 | 8.0429 | 5.0578 | -1.0796 | -2.2446 | 0.9136 | -2.4249 | 7.8811 | 1.5786 | 0.603 | 0.649 | 0.9513 | 0.7222 | -130.8897 | -4.8173 | 3.38 | 0.5403 | -5.3339 | -3.7124 | 2.5863 |  | 0.8939 | -1.4337 | 4.0164 | 3.3646 | 3.349 | 1.0441 | 10.7059 | 14.1965 | 14.7813 | 11.0417 | 0 | -0.0032 | 0.0013 | 0.0037 | 0.0008 | -0.0005 | 0.0189 | -0.0179 | -0.0073 | -360.1404 | 17.4151 | -360.5066 | 17.7395 | -360.8543 | 18.1974 | -360.8912 | 17.5219 | -352.666 | 18.7497 | -352.7121 | 16.8587
12:08 | 2911 | 33.0819 | 198.7624 | 444.6392 | 450.1991 | -18.4055 | -44.9666 | 8.0693 | 5.0308 | -1.0251 | -2.2755 | 0.9725 | -2.4113 | 7.8587 | 1.6101 | 0.602 | 0.6457 | 0.9529 | 0.7208 | -130.8535 | -4.7444 | 3.3626 | 0.5245 | -5.2844 | -3.7411 | 2.5673 |  | 0.8666 | -1.4458 | 4.0149 | 3.3596 | 3.3473 | 1.0435 | 10.7082 | 14.2045 | 14.7425 | 11.0327 | -0.0003 | -0.0027 | 0.001 | 0.0038 | 0.0011 | -0.0009 | 0.0104 | -0.0091 | -0.0121 | -360.1711 | 17.372 | -360.4112 | 17.6985 | -360.8081 | 18.1748 | -360.885 | 17.5321 | -352.6721 | 18.7148 | -352.6537 | 16.8176
12:08 | 2912 | 33.0344 | 198.8185 | 444.7203 | 450.3168 | -18.3373 | -44.839 | 8.0722 | 5.0686 | -1.1006 | -2.2948 | 0.9247 | -2.4429 | 7.9802 | 1.7434 | 0.6029 | 0.6491 | 0.9538 | 0.7218 | -130.8948 | -4.7397 | 3.3277 | 0.452 | -5.2863 | -3.8232 | 2.5669 |  | 0.8563 | -1.4397 | 4.0137 | 3.3612 | 3.3459 | 1.0435 | 10.7279 | 14.2243 | 14.7973 | 11.0407 | -0.0005 | -0.0029 | 0.0007 | 0.0039 | 0.0005 | -0.0005 | 0.0086 | -0.0048 | -0.0244 | -360.1558 | 17.4151 | -360.4727 | 17.68 | -360.7897 | 18.1563 | -360.9066 | 17.5383 | -352.6444 | 18.7374 | -352.6629 | 16.8074
12:08 | 2913 | 33.0288 | 198.7959 | 444.6244 | 450.2434 | -18.3198 | -44.9036 | 8.0956 | 5.009 | -1.1153 | -2.3039 | 0.9802 | -2.4057 | 7.9572 | 1.7018 | 0.6031 | 0.6494 | 0.953 | 0.7218 | -130.8598 | -4.7772 | 3.3412 | 0.4346 | -5.3395 | -3.823 | 2.5648 |  | 0.9087 | -1.295 | 4.0153 | 3.3617 | 3.3482 | 1.0447 | 10.744 | 14.2291 | 14.8328 | 11.0388 | -0.0002 | -0.0027 | 0.0006 | 0.0039 | 0.001 | -0.0005 | 0.0058 | -0.0095 | -0.0043 | -360.1927 | 17.4356 | -360.5404 | 17.7436 | -360.8604 | 18.1666 | -360.8943 | 17.5321 | -352.6813 | 18.7661 | -352.7275 | 16.8587
12:08 | 2914 | 33.1037 | 198.7876 | 444.5694 | 450.1507 | -18.3546 | -44.8459 | 8.1041 | 5.026 | -1.0015 | -2.2648 | 1.0203 | -2.4558 | 7.8932 | 1.6183 | 0.6029 | 0.6472 | 0.9499 | 0.7206 | -131.0269 | -4.8726 | 3.2693 | 0.3846 | -5.2638 | -3.8735 | 2.5395 |  | 0.8829 | -1.2379 | 4.014 | 3.3632 | 3.3485 | 1.0432 | 10.7694 | 14.2548 | 14.8193 | 11.0753 | 0.0003 | -0.0031 | 0.0004 | 0.0033 | 0.0006 | -0.0002 | -0.007 | -0.0169 | -0.0336 | -360.0942 | 17.374 | -360.4635 | 17.7231 | -360.8635 | 18.1728 | -360.882 | 17.5055 | -352.6321 | 18.7251 | -352.6967 | 16.8505
12:08 | 2915 | 33.0518 | 198.734 | 444.4844 | 450.1821 | -18.3506 | -44.7337 | 8.2107 | 5.0032 | -0.977 | -2.2131 | 1.0435 | -2.5022 | 7.956 | 1.6747 | 0.6033 | 0.6473 | 0.951 | 0.7227 | -130.9357 | -4.7522 | 3.3132 | 0.5703 | -5.2354 | -3.8573 | 2.5559 |  | 0.8781 | -1.2969 | 4.0143 | 3.3635 | 3.3484 | 1.0436 | 10.721 | 14.2056 | 14.7775 | 11.0515 | -0.0002 | -0.0031 | 0.0006 | 0.0035 | 0.001 | -0.0005 | 0.0049 | -0.0019 | -0.0188 | -360.1404 | 17.3802 | -360.4481 | 17.6985 | -360.842 | 18.183 | -360.8727 | 17.5219 | -352.6352 | 18.7087 | -352.6321 | 16.8299
12:08 | 2916 | 33.173 | 198.7639 | 444.5816 | 450.244 | -18.2483 | -44.7644 | 8.2799 | 4.9837 | -0.9467 | -2.1455 | 1.0709 | -2.4892 | 7.9039 | 1.5623 | 0.6031 | 0.646 | 0.9527 | 0.7227 | -130.9506 | -4.7719 | 3.3855 | 0.639 | -5.208 | -3.8455 | 2.5804 |  | 0.853 | -1.402 | 4.0143 | 3.3681 | 3.3489 | 1.0444 | 10.7613 | 14.2351 | 14.8339 | 11.05 | -0.0003 | -0.0025 | 0.0011 | 0.003 | 0.0007 | 0 | 0.0194 | -0.0078 | -0.0084 | -360.2419 | 17.4418 | -360.4696 | 17.7026 | -360.8143 | 18.1707 | -360.885 | 17.5568 | -352.7275 | 18.76 | -352.6967 | 16.8381
12:08 | 2917 | 33.2075 | 198.7973 | 444.6329 | 450.2264 | -18.2185 | -44.7775 | 8.2221 | 5.0268 | -0.9477 | -2.2438 | 1.0328 | -2.5037 | 7.9525 | 1.665 | 0.6029 | 0.646 | 0.9524 | 0.7225 | -130.8443 | -4.7505 | 3.4159 | 0.5569 | -5.3195 | -3.8667 | 2.5519 |  | 0.8832 | -1.4106 | 4.0149 | 3.3624 | 3.3484 | 1.0433 | 10.7338 | 14.2124 | 14.7721 | 11.0414 | -0.0003 | -0.0027 | 0.0004 | 0.0035 | 0.0007 | -0.0006 | 0.0045 | -0.0124 | -0.0236 | -360.165 | 17.4254 | -360.5004 | 17.719 | -360.8204 | 18.1563 | -360.8327 | 17.4993 | -352.6783 | 18.7477 | -352.7337 | 16.8566
12:08 | 2918 | 33.1674 | 198.8385 | 444.7478 | 450.2513 | -18.2422 | -44.8015 | 8.26 | 4.9576 | -1.0094 | -2.1694 | 1.0871 | -2.3757 | 7.9311 | 1.6601 | 0.6022 | 0.6462 | 0.9506 | 0.7228 | -130.9169 | -4.7431 | 3.374 | 0.6027 | -5.3269 | -3.9161 | 2.4762 |  | 0.8636 | -1.3795 | 4.0157 | 3.3677 | 3.3507 | 1.0447 | 10.7151 | 14.2232 | 14.8086 | 11.0565 | 0.0001 | -0.0031 | 0.0011 | 0.0039 | 0.0006 | -0.0004 | -0.0016 | -0.0051 | -0.013 | -360.1127 | 17.4069 | -360.4912 | 17.7354 | -360.8481 | 18.1687 | -360.8604 | 17.5034 | -352.6598 | 18.7456 | -352.7029 | 16.8443
12:08 | 2919 | 33.116 | 198.7905 | 444.7201 | 450.1829 | -18.2629 | -44.7974 | 8.2976 | 4.9279 | -1.0014 | -2.2477 | 0.9917 | -2.3734 | 7.9802 | 1.6743 | 0.6025 | 0.6421 | 0.9524 | 0.7222 | -130.9218 | -4.7763 | 3.325 | 0.6369 | -5.2991 | -3.8534 | 2.5155 |  | 0.9247 | -1.414 | 4.014 | 3.3633 | 3.347 | 1.0438 | 10.7358 | 14.2154 | 14.7964 | 11.0478 | 0.0004 | -0.0029 | 0.0008 | 0.0039 | 0.0008 | -0.0006 | -0.0002 | -0.0059 | 0.0051 | -360.2081 | 17.4007 | -360.4604 | 17.7108 | -360.842 | 18.1994 | -360.9527 | 17.5424 | -352.6752 | 18.7497 | -352.666 | 16.8279
12:08 | 2920 | 33.1763 | 198.7495 | 444.7837 | 450.2899 | -18.2359 | -44.8311 | 8.3667 | 5.0468 | -0.9408 | -2.156 | 1.1009 | -2.4555 | 7.8551 | 1.5815 | 0.6011 | 0.641 | 0.9524 | 0.7226 | -130.8176 | -4.7208 | 3.3696 | 0.6966 | -5.3368 | -3.8263 | 2.5178 |  | 0.8065 | -1.514 | 4.0147 | 3.3647 | 3.3501 | 1.0435 | 10.7163 | 14.2358 | 14.7858 | 11.0407 | -0.0004 | -0.0028 | 0.0003 | 0.0039 | 0.0008 | -0.0009 | 0.0051 | -0.0057 | 0.0042 | -360.2019 | 17.4172 | -360.4666 | 17.6738 | -360.7712 | 18.1358 | -360.8481 | 17.5301 | -352.6844 | 18.7477 | -352.6967 | 16.8012
12:08 | 2921 | 33.167 | 198.7727 | 444.7404 | 450.3216 | -18.1863 | -44.9057 | 8.362 | 4.9249 | -1.0277 | -2.2174 | 0.9758 | -2.4083 | 7.9196 | 1.6119 | 0.6011 | 0.6449 | 0.9563 | 0.7223 | -130.8281 | -4.6631 | 3.4156 | 0.6805 | -5.2152 | -3.8062 | 2.5552 |  | 0.8621 | -1.4098 | 4.0145 | 3.3657 | 3.3495 | 1.0457 | 10.7554 | 14.2412 | 14.8186 | 11.0666 | 0.0003 | -0.0021 | 0.0007 | 0.0042 | 0.0009 | -0.0002 | 0.0118 | 0.0044 | -0.0256 | -360.2111 | 17.4418 | -360.5004 | 17.7087 | -360.8389 | 18.1481 | -360.845 | 17.528 | -352.6875 | 18.76 | -352.7213 | 16.8217
12:08 | 2922 | 33.1948 | 198.8766 | 444.7767 | 450.3319 | -18.1755 | -44.8901 | 8.3213 | 4.9792 | -0.9954 | -2.241 | 1.0164 | -2.3821 | 7.872 | 1.5936 | 0.6016 | 0.6449 | 0.9517 | 0.7215 | -130.8675 | -4.7332 | 3.3519 | 0.643 | -5.2137 | -3.812 | 2.5075 |  | 0.7964 | -1.39 | 4.0128 | 3.3653 | 3.3468 | 1.0422 | 10.7509 | 14.2592 | 14.8053 | 11.0803 | 0.0003 | -0.003 | 0.0003 | 0.0034 | 0.0004 | -0.0009 | 0.0128 | -0.0209 | -0.0103 | -360.1619 | 17.4048 | -360.4973 | 17.7354 | -360.8543 | 18.1871 | -360.8727 | 17.5198 | -352.6506 | 18.7477 | -352.7121 | 16.8464
12:08 | 2923 | 33.1612 | 198.8935 | 444.7942 | 450.2881 | -18.1906 | -45.0042 | 8.3561 | 4.9836 | -1.0002 | -2.1872 | 1.0004 | -2.4832 | 7.835 | 1.5013 | 0.6024 | 0.6455 | 0.9529 | 0.7218 | -130.844 | -4.7995 | 3.3035 | 0.5654 | -5.2549 | -3.8232 | 2.4957 |  | 0.8701 | -1.4382 | 4.0141 | 3.3627 | 3.345 | 1.0453 | 10.7221 | 14.23 | 14.8089 | 11.058 | 0.0004 | -0.0026 | 0.0002 | 0.0037 | 0.0007 | 0 | 0.0147 | -0.014 | 0.0168 | -360.1342 | 17.3782 | -360.3989 | 17.6759 | -360.7743 | 18.183 | -360.9158 | 17.5219 | -352.666 | 18.7087 | -352.6321 | 16.795
12:08 | 2924 | 33.2391 | 198.914 | 444.7308 | 450.3001 | -18.2141 | -44.9765 | 8.357 | 5.0519 | -1.0893 | -2.1817 | 1.0133 | -2.5197 | 7.8803 | 1.5335 | 0.604 | 0.6488 | 0.9514 | 0.7241 | -130.896 | -4.8194 | 3.3138 | 0.6205 | -5.2584 | -3.8189 | 2.4885 |  | 0.8306 | -1.3616 | 4.0148 | 3.3678 | 3.3464 | 1.0455 | 10.7279 | 14.1953 | 14.7568 | 11.0233 | -0.0004 | -0.0027 | 0.001 | 0.0036 | 0.0008 | -0.0005 | 0.0097 | -0.0144 | -0.0076 | -360.2173 | 17.4213 | -360.4789 | 17.6923 | -360.7897 | 18.1748 | -360.9066 | 17.5445 | -352.6998 | 18.7477 | -352.6752 | 16.8115
12:08 | 2925 | 33.1782 | 198.7454 | 444.6927 | 450.2267 | -18.2437 | -44.9517 | 8.3421 | 5.0609 | -1.0695 | -2.1628 | 0.9864 | -2.474 | 7.872 | 1.6316 | 0.6025 | 0.6472 | 0.9494 | 0.7232 | -130.8808 | -4.7765 | 3.3399 | 0.6656 | -5.2474 | -3.7778 | 2.5845 |  | 0.9246 | -1.3348 | 4.013 | 3.3626 | 3.3454 | 1.0439 | 10.7407 | 14.2136 | 14.7792 | 11.0309 | -0.0006 | -0.0025 | 0.0008 | 0.0037 | 0.0006 | -0.0004 | -0.004 | -0.0071 | -0.0272 | -360.1588 | 17.4274 | -360.5004 | 17.721 | -360.8666 | 18.1563 | -360.8512 | 17.5239 | -352.6937 | 18.7579 | -352.7521 | 16.8443
12:08 | 2926 | 33.2831 | 198.8238 | 444.7345 | 450.2642 | -18.1277 | -45.0165 | 8.3445 | 5.0318 | -1.1501 | -2.2475 | 0.9436 | -2.516 | 7.9473 | 1.6227 | 0.6022 | 0.6483 | 0.951 | 0.7215 | -130.8866 | -4.7936 | 3.3088 | 0.6463 | -5.2039 | -3.8296 | 2.5952 |  | 0.8253 | -1.4889 | 4.013 | 3.3652 | 3.3447 | 1.0435 | 10.7012 | 14.2093 | 14.7943 | 11.0197 | 0 | -0.0029 | 0.0009 | 0.0039 | 0.001 | -0.0007 | -0.0049 | -0.0117 | -0.0289 | -360.0973 | 17.3802 | -360.4727 | 17.7128 | -360.8666 | 18.1625 | -360.8512 | 17.4972 | -352.6106 | 18.6963 | -352.6475 | 16.8381
12:08 | 2927 | 33.2998 | 198.9171 | 444.8205 | 450.3057 | -18.1464 | -44.8991 | 8.3945 | 5.042 | -1.0453 | -2.2749 | 1.0784 | -2.5194 | 7.9695 | 1.5803 | 0.6022 | 0.649 | 0.9545 | 0.723 | -130.7843 | -4.7882 | 3.3828 | 0.691 | -5.1222 | -3.702 | 2.5688 |  | 0.8685 | -1.3609 | 4.0146 | 3.3635 | 3.3445 | 1.0454 | 10.7118 | 14.2019 | 14.755 | 11.0371 | 0 | -0.0035 | 0.0006 | 0.0035 | 0.0003 | -0.0008 | 0.0034 | -0.0098 | 0.0028 | -360.1681 | 17.4028 | -360.4481 | 17.7046 | -360.8574 | 18.1851 | -360.9035 | 17.5342 | -352.6752 | 18.7271 | -352.6937 | 16.8258
12:09 | 2928 | 33.2262 | 198.8139 | 444.7281 | 450.2238 | -18.096 | -44.8924 | 8.3959 | 5.0933 | -1.137 | -2.1998 | 1.108 | -2.4951 | 7.9073 | 1.5285 | 0.6028 | 0.6448 | 0.9509 | 0.7229 | -130.7985 | -4.7196 | 3.3494 | 0.6489 | -5.2049 | -3.7674 | 2.5341 |  | 0.8172 | -1.3722 | 4.0138 | 3.3662 | 3.3494 | 1.0443 | 10.744 | 14.2174 | 14.7855 | 11.0565 | -0.0003 | -0.0028 | 0.0006 | 0.0038 | 0.0012 | -0.0002 | 0.0117 | -0.0004 | -0.0252 | -360.2235 | 17.4315 | -360.4912 | 17.6902 | -360.8143 | 18.1584 | -360.8727 | 17.5301 | -352.7244 | 18.7518 | -352.6906 | 16.8217
12:09 | 2929 | 33.2155 | 198.8462 | 444.7128 | 450.2238 | -18.0859 | -44.9247 | 8.3682 | 5.1282 | -1.0918 | -2.2856 | 1.1198 | -2.5142 | 7.8342 | 1.5367 | 0.6023 | 0.6465 | 0.9542 | 0.7217 | -130.8621 | -4.7318 | 3.4046 | 0.7094 | -5.1478 | -3.7887 | 2.581 |  | 0.8629 | -1.3818 | 4.0147 | 3.3627 | 3.35 | 1.0437 | 10.7694 | 14.2374 | 14.7845 | 11.0348 | -0.0002 | -0.0026 | 0.0012 | 0.0039 | 0.0009 | -0.0005 | 0.0046 | 0.0018 | 0.0016 | -360.1342 | 17.4151 | -360.5127 | 17.7149 | -360.8174 | 18.1379 | -360.7927 | 17.4952 | -352.6537 | 18.7436 | -352.6967 | 16.8361
12:09 | 2930 | 33.2015 | 198.8272 | 444.7847 | 450.2479 | -18.1215 | -44.8729 | 8.3357 | 5.0305 | -1.0855 | -2.3728 | 0.9757 | -2.4901 | 7.9361 | 1.6241 | 0.602 | 0.6457 | 0.9535 | 0.7225 | -130.96 | -4.8424 | 3.3611 | 0.6609 | -5.0524 | -3.7626 | 2.5581 |  | 0.8417 | -1.3065 | 4.0152 | 3.3652 | 3.3493 | 1.0447 | 10.7579 | 14.2544 | 14.845 | 11.0648 | 0 | -0.0029 | 0 | 0.0031 | 0.0003 | -0.0006 | 0.0218 | -0.0082 | -0.0055 | -360.1588 | 17.4192 | -360.5281 | 17.7334 | -360.8697 | 18.1871 | -360.9004 | 17.5198 | -352.6629 | 18.7477 | -352.7183 | 16.8443
12:09 | 2931 | 33.3305 | 198.8296 | 444.8007 | 450.3506 | -18.207 | -44.806 | 8.3787 | 5.0111 | -1.1073 | -2.375 | 1.0063 | -2.5144 | 7.9382 | 1.6552 | 0.6036 | 0.6441 | 0.9518 | 0.7202 | -130.9569 | -4.727 | 3.3511 | 0.6336 | -5.1926 | -3.691 | 2.5836 |  | 0.8388 | -1.2796 | 4.0143 | 3.3638 | 3.3452 | 1.0438 | 10.7221 | 14.2243 | 14.7916 | 11.0638 | 0.0002 | -0.003 | 0.0003 | 0.0037 | 0.0012 | -0.0005 | 0.0094 | -0.0141 | -0.0239 | -360.1527 | 17.3925 | -360.445 | 17.7046 | -360.8266 | 18.1789 | -360.9035 | 17.5404 | -352.6967 | 18.721 | -352.6721 | 16.8279
12:09 | 2932 | 33.3394 | 198.8543 | 444.7882 | 450.3615 | -18.1469 | -44.8454 | 8.4581 | 5.1722 | -1.0577 | -2.2731 | 1.0688 | -2.4442 | 7.929 | 1.6292 | 0.6021 | 0.6451 | 0.9518 | 0.7213 | -130.9636 | -4.758 | 3.3602 | 0.6136 | -5.2083 | -3.6545 | 2.5741 |  | 0.917 | -1.3029 | 4.0142 | 3.3647 | 3.3468 | 1.0445 | 10.7302 | 14.2438 | 14.8048 | 11.0432 | -0.0003 | -0.0033 | 0.0013 | 0.0037 | 0.0002 | -0.0006 | 0.01 | 0 | 0.0072 | -360.205 | 17.4131 | -360.4204 | 17.6656 | -360.7558 | 18.142 | -360.8543 | 17.5383 | -352.669 | 18.7374 | -352.6629 | 16.795
12:09 | 2933 | 33.2973 | 198.9172 | 444.8744 | 450.3296 | -18.1274 | -44.8909 | 8.4763 | 5.1563 | -1.0283 | -2.28 | 1.0545 | -2.4988 | 7.8588 | 1.6052 | 0.6036 | 0.6431 | 0.9533 | 0.7209 | -130.8984 | -4.8013 | 3.4047 | 0.6958 | -5.2118 | -3.5711 | 2.5788 |  | 0.9027 | -1.3022 | 4.0157 | 3.3641 | 3.3485 | 1.0448 | 10.7404 | 14.2317 | 14.8077 | 11.0637 | -0.0003 | -0.0026 | 0.0011 | 0.0038 | 0.0006 | -0.0007 | 0.0019 | 0.0004 | -0.0339 | -360.1958 | 17.4254 | -360.4973 | 17.7395 | -360.8481 | 18.1728 | -360.8789 | 17.526 | -352.7244 | 18.7641 | -352.6998 | 16.8423
12:09 | 2934 | 33.3846 | 198.9127 | 444.8752 | 450.3713 | -18.0153 | -44.7772 | 8.5036 | 5.1692 | -1.0339 | -2.2137 | 0.9777 | -2.5565 | 7.8715 | 1.6116 | 0.6037 | 0.6438 | 0.952 | 0.7234 | -130.9603 | -4.7741 | 3.3306 | 0.5897 | -5.2347 | -3.603 | 2.5807 |  | 0.8625 | -1.3093 | 4.0144 | 3.366 | 3.3522 | 1.0456 | 10.7138 | 14.2281 | 14.7862 | 11.0547 | -0.0004 | -0.0033 | 0.0011 | 0.0043 | 0.0008 | -0.0003 | 0.011 | -0.0053 | -0.0102 | -360.1342 | 17.3946 | -360.4727 | 17.7169 | -360.8481 | 18.1871 | -360.8974 | 17.5137 | -352.6444 | 18.7333 | -352.6844 | 16.8299
12:09 | 2935 | 33.3312 | 198.8606 | 444.9006 | 450.3334 | -18.1713 | -44.8913 | 8.4244 | 5.1595 | -1.023 | -2.2893 | 0.9596 | -2.631 | 7.8412 | 1.6484 | 0.6021 | 0.6433 | 0.9514 | 0.7219 | -130.8061 | -4.6587 | 3.388 | 0.5698 | -5.2361 | -3.7284 | 2.5657 |  | 0.8211 | -1.2746 | 4.0143 | 3.3616 | 3.3491 | 1.045 | 10.736 | 14.2149 | 14.7932 | 11.0374 | 0.0001 | -0.0033 | 0.0009 | 0.0036 | 0.0011 | -0.0005 | -0.0042 | -0.0057 | -0.0108 | -360.1773 | 17.3987 | -360.4512 | 17.6964 | -360.7835 | 18.183 | -360.8943 | 17.5321 | -352.6506 | 18.7271 | -352.666 | 16.7971
12:09 | 2936 | 33.3925 | 198.9628 | 444.9574 | 450.3512 | -18.1497 | -44.8804 | 8.3935 | 5.1024 | -1.0124 | -2.2685 | 0.9922 | -2.5599 | 8.0021 | 1.7217 | 0.6034 | 0.6461 | 0.9532 | 0.7208 | -130.8362 | -4.7245 | 3.4896 | 0.5651 | -5.312 | -3.7576 | 2.5801 |  | 0.9129 | -1.3112 | 4.0139 | 3.3687 | 3.3499 | 1.0444 | 10.7163 | 14.2185 | 14.7684 | 11.0638 | -0.0001 | -0.0033 | 0.0004 | 0.0035 | 0.0006 | -0.0004 | -0.0085 | -0.0017 | -0.0065 | -360.2235 | 17.4336 | -360.5189 | 17.7334 | -360.8481 | 18.1645 | -360.8697 | 17.5404 | -352.6967 | 18.7682 | -352.7244 | 16.8299
12:09 | 2937 | 33.3696 | 198.9102 | 444.8847 | 450.3054 | -18.1631 | -44.9514 | 8.4221 | 5.1486 | -0.9793 | -2.2756 | 0.9611 | -2.5555 | 7.977 | 1.5178 | 0.603 | 0.6473 | 0.9559 | 0.7205 | -130.8321 | -4.7839 | 3.4901 | 0.6027 | -5.2786 | -3.6334 | 2.5435 |  | 0.8917 | -1.2804 | 4.0161 | 3.3651 | 3.3517 | 1.0455 | 10.737 | 14.2337 | 14.8141 | 11.0377 | -0.0002 | -0.0024 | 0.0007 | 0.004 | 0.0005 | -0.0006 | 0.0032 | -0.0109 | -0.011 | -360.1096 | 17.3966 | -360.4758 | 17.7169 | -360.7989 | 18.1604 | -360.8297 | 17.4972 | -352.6321 | 18.7333 | -352.6844 | 16.8258
12:09 | 2938 | 33.3379 | 198.7851 | 444.8624 | 450.2675 | -18.1396 | -44.856 | 8.3597 | 5.062 | -1.0369 | -2.249 | 0.8674 | -2.4618 | 7.884 | 1.62 | 0.6035 | 0.6441 | 0.9532 | 0.7196 | -130.9024 | -4.7998 | 3.4109 | 0.6046 | -5.2988 | -3.6858 | 2.5943 |  | 0.9722 | -1.1459 | 4.0151 | 3.3659 | 3.3472 | 1.046 | 10.7128 | 14.2151 | 14.8117 | 11.0313 | -0.0003 | -0.0028 | 0.0005 | 0.0037 | 0.0008 | -0.0001 | 0.0014 | -0.0071 | 0.006 | -360.1958 | 17.4007 | -360.4327 | 17.7108 | -360.8112 | 18.1625 | -360.8666 | 17.526 | -352.6444 | 18.7251 | -352.6813 | 16.8156
12:09 | 2939 | 33.3826 | 198.7339 | 444.7562 | 450.1279 | -18.1156 | -44.856 | 8.3808 | 5.0182 | -1.1037 | -2.3636 | 0.9157 | -2.4064 | 7.9582 | 1.5964 | 0.6045 | 0.6483 | 0.9522 | 0.7221 | -130.8284 | -4.7356 | 3.3362 | 0.5376 | -5.2829 | -3.6185 | 2.5918 |  | 0.9508 | -1.3068 | 4.0143 | 3.3661 | 3.3489 | 1.045 | 10.7014 | 14.1915 | 14.8027 | 11.0382 | 0.0001 | -0.0033 | 0.0008 | 0.0038 | 0.0005 | -0.0007 | 0.0058 | -0.0059 | -0.0325 | -360.1865 | 17.4315 | -360.5004 | 17.7231 | -360.8512 | 18.181 | -360.885 | 17.5342 | -352.6998 | 18.76 | -352.706 | 16.8258
12:09 | 2940 | 33.4253 | 198.7683 | 444.804 | 450.1672 | -18.1811 | -44.8558 | 8.3111 | 5.0911 | -0.9464 | -2.2318 | 1.0079 | -2.4848 | 7.8965 | 1.6548 | 0.6043 | 0.6454 | 0.9542 | 0.7211 | -130.8675 | -4.7563 | 3.2406 | 0.4145 | -5.2906 | -3.66 | 2.5973 |  | 0.9271 | -1.2429 | 4.012 | 3.3631 | 3.3486 | 1.0452 | 10.7347 | 14.2315 | 14.8356 | 11.0468 | 0 | -0.0029 | 0.0013 | 0.004 | 0.0003 | -0.0003 | 0.0038 | 0.001 | -0.0284 | -360.1158 | 17.3987 | -360.4604 | 17.6985 | -360.7866 | 18.1584 | -360.8635 | 17.5075 | -352.6537 | 18.7395 | -352.6906 | 16.8156
12:09 | 2941 | 33.3733 | 198.7338 | 444.8636 | 450.1555 | -18.1771 | -44.7953 | 8.3811 | 5.1257 | -0.9948 | -2.3288 | 0.8892 | -2.3708 | 7.9634 | 1.6462 | 0.6032 | 0.6414 | 0.9512 | 0.7204 | -130.8586 | -4.7405 | 3.2367 | 0.4284 | -5.261 | -3.5761 | 2.5534 |  | 0.9664 | -1.1935 | 4.0138 | 3.3671 | 3.3486 | 1.0455 | 10.744 | 14.2523 | 14.8444 | 11.0446 | -0.0002 | -0.0027 | 0.0007 | 0.0034 | 0.0004 | -0.0004 | 0.0183 | -0.0109 | -0.0072 | -360.1527 | 17.4151 | -360.4789 | 17.7108 | -360.8112 | 18.1707 | -360.8574 | 17.5219 | -352.6444 | 18.7436 | -352.666 | 16.8115
12:09 | 2942 | 33.3094 | 198.806 | 444.8047 | 450.1857 | -18.1346 | -44.7657 | 8.3671 | 5.1657 | -1.0673 | -2.3158 | 0.9582 | -2.4011 | 7.9307 | 1.7028 | 0.6035 | 0.6472 | 0.9543 | 0.7206 | -130.7824 | -4.9147 | 3.2799 | 0.4846 | -5.3206 | -3.7126 | 2.5945 |  | 0.8598 | -1.1451 | 4.0128 | 3.3636 | 3.3488 | 1.0451 | 10.7497 | 14.2468 | 14.8234 | 11.0727 | -0.0001 | -0.0024 | 0.0007 | 0.0038 | 0.0012 | -0.0008 | -0.0013 | -0.0038 | -0.0048 | -360.1619 | 17.4315 | -360.525 | 17.7313 | -360.8358 | 18.181 | -360.8974 | 17.5363 | -352.666 | 18.7497 | -352.7275 | 16.8402
12:09 | 2943 | 33.3299 | 198.89 | 444.8825 | 450.1883 | -18.1421 | -44.7837 | 8.3617 | 5.0653 | -1.0719 | -2.4302 | 0.9029 | -2.4177 | 7.9307 | 1.5862 | 0.6031 | 0.6436 | 0.9505 | 0.7209 | -130.7569 | -4.797 | 3.3392 | 0.592 | -5.2572 | -3.6495 | 2.6507 |  | 0.8794 | -1.2157 | 4.0128 | 3.3638 | 3.3482 | 1.0428 | 10.7567 | 14.2188 | 14.8168 | 11.0457 | 0.0002 | -0.0029 | 0.001 | 0.0039 | 0.0005 | -0.0002 | 0.0102 | -0.009 | -0.0092 | -360.1311 | 17.3987 | -360.4635 | 17.7026 | -360.7989 | 18.1604 | -360.8758 | 17.5219 | -352.6475 | 18.7271 | -352.6752 | 16.8115
12:09 | 2944 | 33.3741 | 198.9119 | 444.7189 | 450.2277 | -18.0366 | -44.7692 | 8.428 | 5.0815 | -1.0453 | -2.3342 | 0.9566 | -2.4982 | 7.955 | 1.6017 | 0.6043 | 0.6484 | 0.9522 | 0.721 | -130.7551 | -4.8751 | 3.4173 | 0.5993 | -5.2319 | -3.657 | 2.5994 |  | 0.867 | -1.2438 | 4.0131 | 3.3636 | 3.3505 | 1.0445 | 10.7395 | 14.2413 | 14.7779 | 11.0472 | -0.0003 | -0.0034 | -0.0002 | 0.0031 | 0.0006 | -0.0011 | 0.0079 | -0.0117 | -0.0049 | -360.1588 | 17.409 | -360.4573 | 17.6923 | -360.7743 | 18.1502 | -360.8697 | 17.5198 | -352.669 | 18.7353 | -352.6937 | 16.8012
12:09 | 2945 | 33.4679 | 198.9088 | 444.775 | 450.2647 | -18.0059 | -44.7504 | 8.4811 | 5.0558 | -1.0052 | -2.2491 | 0.9598 | -2.4506 | 7.9883 | 1.6616 | 0.6034 | 0.6443 | 0.9519 | 0.7204 | -130.7306 | -4.864 | 3.5103 | 0.4093 | -5.2752 | -3.5636 | 2.6239 |  | 0.8448 | -1.3384 | 4.0117 | 3.3675 | 3.349 | 1.044 | 10.7439 | 14.2409 | 14.776 | 11.0616 | 0 | -0.0023 | 0.0004 | 0.0038 | 0.0004 | -0.0003 | 0.0126 | 0.0034 | -0.0209 | -360.1804 | 17.4295 | -360.5219 | 17.7416 | -360.8574 | 18.1748 | -360.8727 | 17.5342 | -352.7029 | 18.7538 | -352.7183 | 16.8361
12:09 | 2946 | 33.4311 | 198.8656 | 444.9433 | 450.3739 | -18.1187 | -44.73 | 8.3406 | 5.1345 | -1.0017 | -2.248 | 0.991 | -2.4037 | 7.8847 | 1.6832 | 0.6042 | 0.6417 | 0.954 | 0.7225 | -130.7858 | -5.0099 | 3.4322 | 0.2987 | -5.305 | -3.5268 | 2.6413 |  | 0.8994 | -1.4076 | 4.0129 | 3.3649 | 3.3506 | 1.0446 | 10.7254 | 14.2109 | 14.8104 | 11.0543 | 0 | -0.0024 | 0.0008 | 0.0039 | 0.0011 | -0.0004 | 0.0084 | -0.0021 | -0.0119 | -360.1527 | 17.411 | -360.4973 | 17.7272 | -360.8297 | 18.1851 | -360.885 | 17.5178 | -352.6413 | 18.7436 | -352.706 | 16.8299
12:09 | 2947 | 33.4328 | 198.9049 | 444.9143 | 450.3829 | -18.1147 | -44.7439 | 8.3968 | 5.125 | -1.0909 | -2.2139 | 0.9163 | -2.474 | 7.8953 | 1.6925 | 0.6038 | 0.6443 | 0.9524 | 0.7198 | -130.7637 | -4.8925 | 3.4278 | 0.3713 | -5.3012 | -3.6261 | 2.5904 |  | 0.8743 | -1.3574 | 4.0139 | 3.3641 | 3.3496 | 1.0441 | 10.6689 | 14.1826 | 14.7728 | 11.028 | 0.0004 | -0.0025 | 0.0006 | 0.0039 | 0.0008 | -0.0002 | 0.0165 | -0.0049 | -0.0026 | -360.1404 | 17.3802 | -360.4358 | 17.7128 | -360.805 | 18.181 | -360.8727 | 17.5239 | -352.6567 | 18.7066 | -352.6537 | 16.8012
12:09 | 2948 | 33.3579 | 198.8346 | 444.8454 | 450.3342 | -18.0871 | -44.6727 | 8.4147 | 5.1338 | -1.1111 | -2.1334 | 0.966 | -2.4533 | 7.968 | 1.6579 | 0.6029 | 0.6412 | 0.9505 | 0.7205 | -130.7453 | -4.772 | 3.424 | 0.3187 | -5.2907 | -3.6045 | 2.5836 |  | 0.9012 | -1.4265 | 4.0129 | 3.3652 | 3.3486 | 1.0456 | 10.722 | 14.2188 | 14.8053 | 11.0399 | 0.0003 | -0.0029 | 0.0013 | 0.0038 | 0.0011 | -0.0002 | 0.0122 | -0.0143 | 0.0012 | -360.2204 | 17.4418 | -360.4942 | 17.7313 | -360.802 | 18.1748 | -360.922 | 17.5424 | -352.6875 | 18.7538 | -352.706 | 16.8135
12:09 | 2949 | 33.3931 | 198.8682 | 444.9007 | 450.3671 | -18.0295 | -44.688 | 8.3137 | 5.0354 | -1.081 | -2.239 | 0.9625 | -2.4626 | 7.9038 | 1.7009 | 0.6042 | 0.6444 | 0.9551 | 0.7203 | -130.7639 | -4.8602 | 3.389 | 0.2952 | -5.2746 | -3.6348 | 2.5886 |  | 0.8491 | -1.3862 | 4.0137 | 3.3642 | 3.3496 | 1.0445 | 10.7325 | 14.2115 | 14.8018 | 11.0569 | -0.0006 | -0.003 | 0.0004 | 0.0034 | 0.001 | -0.0004 | 0.0136 | -0.0114 | -0.0045 | -360.1681 | 17.4213 | -360.4942 | 17.7477 | -360.8327 | 18.1502 | -360.8512 | 17.5239 | -352.6967 | 18.7456 | -352.7121 | 16.834
12:09 | 2950 | 33.5149 | 198.9037 | 444.9565 | 450.3946 | -18.0271 | -44.5964 | 8.3796 | 5.0615 | -1.0205 | -2.2028 | 0.9047 | -2.4733 | 7.9208 | 1.6314 | 0.6027 | 0.6418 | 0.9507 | 0.7205 | -130.7813 | -4.8997 | 3.3784 | 0.2797 | -5.2541 | -3.7089 | 2.6094 |  | 0.9539 | -1.4525 | 4.0139 | 3.3652 | 3.349 | 1.0445 | 10.7244 | 14.2382 | 14.7885 | 11.0486 | -0.0006 | -0.0027 | 0.0007 | 0.0035 | 0.0008 | -0.0005 | 0.0094 | 0.0114 | -0.0275 | -360.0911 | 17.4048 | -360.4912 | 17.7395 | -360.842 | 18.1707 | -360.845 | 17.4952 | -352.6198 | 18.7107 | -352.6629 | 16.832
12:09 | 2951 | 33.527 | 198.9229 | 444.8568 | 450.331 | -18.1749 | -44.7751 | 8.1852 | 5.1461 | -1.0049 | -2.2573 | 1.0115 | -2.4436 | 7.9611 | 1.6708 | 0.602 | 0.6427 | 0.9535 | 0.7207 | -130.7082 | -4.7908 | 3.5026 | 0.2601 | -5.2536 | -3.6607 | 2.5686 |  | 0.9211 | -1.4248 | 4.0135 | 3.365 | 3.3505 | 1.0458 | 10.7174 | 14.2082 | 14.8113 | 11.0414 | -0.0002 | -0.0028 | 0.0006 | 0.0039 | 0.0011 | -0.0006 | 0.0194 | -0.0089 | -0.0082 | -360.1711 | 17.4233 | -360.4758 | 17.7436 | -360.8512 | 18.1892 | -360.9404 | 17.5404 | -352.6783 | 18.7353 | -352.6906 | 16.8299
12:09 | 2952 | 33.4814 | 198.9283 | 444.9564 | 450.3616 | -18.1986 | -44.6693 | 8.1735 | 5.115 | -0.9893 | -2.3803 | 1.0441 | -2.4826 | 7.9545 | 1.68 | 0.602 | 0.646 | 0.9538 | 0.7203 | -130.6992 | -4.7356 | 3.5135 | 0.2694 | -5.2981 | -3.6777 | 2.5385 |  | 0.8575 | -1.3116 | 4.0143 | 3.3635 | 3.347 | 1.0436 | 10.7348 | 14.2486 | 14.8334 | 11.0706 | 0 | -0.0032 | 0.0002 | 0.0032 | 0.0005 | -0.0006 | 0.011 | 0.0022 | -0.0305 | -360.1865 | 17.4213 | -360.4666 | 17.6944 | -360.8081 | 18.1481 | -360.8543 | 17.5239 | -352.6998 | 18.7518 | -352.6967 | 16.8053
12:09 | 2953 | 33.4115 | 198.8659 | 444.9418 | 450.2977 | -18.1123 | -44.6468 | 8.3074 | 5.1021 | -0.9321 | -2.1996 | 1.0832 | -2.4866 | 8.0171 | 1.7153 | 0.6031 | 0.6441 | 0.9518 | 0.7225 | -130.6376 | -4.7146 | 3.4955 | 0.2815 | -5.2893 | -3.7204 | 2.5788 |  | 0.8324 | -1.3234 | 4.0139 | 3.3662 | 3.3491 | 1.045 | 10.728 | 14.2124 | 14.7836 | 11.0414 | -0.0001 | -0.003 | 0.0003 | 0.0041 | 0.0009 | -0.0009 | 0.0189 | -0.0125 | -0.0004 | -360.1311 | 17.4233 | -360.5312 | 17.7436 | -360.8543 | 18.1194 | -360.8174 | 17.5075 | -352.669 | 18.7456 | -352.7213 | 16.832
12:09 | 2954 | 33.528 | 198.9208 | 445.0367 | 450.3484 | -18.1493 | -44.714 | 8.251 | 5.0746 | -0.983 | -2.2389 | 1.074 | -2.4854 | 7.9911 | 1.672 | 0.6022 | 0.6421 | 0.9503 | 0.7233 | -130.7644 | -4.7358 | 3.4864 | 0.3662 | -5.2475 | -3.7237 | 2.5797 |  | 0.8262 | -1.3036 | 4.0139 | 3.3676 | 3.3482 | 1.0464 | 10.7243 | 14.2385 | 14.8138 | 11.0594 | -0.0001 | -0.0023 | 0.0008 | 0.0044 | 0.0004 | -0.0005 | 0.0252 | -0.0099 | -0.0283 | -360.1681 | 17.4151 | -360.5035 | 17.7436 | -360.8758 | 18.1707 | -360.9097 | 17.526 | -352.6413 | 18.7456 | -352.709 | 16.8443
12:09 | 2955 | 33.5343 | 198.8272 | 444.9079 | 450.3291 | -18.1711 | -44.7271 | 8.3423 | 5.1173 | -1.0084 | -2.2206 | 1.0379 | -2.4958 | 8.0056 | 1.6801 | 0.6032 | 0.6437 | 0.9523 | 0.7225 | -130.7712 | -4.6443 | 3.4246 | 0.5217 | -5.2058 | -3.6183 | 2.5313 |  | 0.8849 | -1.4326 | 4.0138 | 3.3639 | 3.3497 | 1.0458 | 10.7359 | 14.221 | 14.8185 | 11.0655 | -0.0003 | -0.003 | 0.0008 | 0.0037 | 0.0008 | -0.0008 | 0.016 | 0.0044 | -0.0167 | -360.1158 | 17.3884 | -360.4173 | 17.6964 | -360.7927 | 18.144 | -360.8727 | 17.5301 | -352.6875 | 18.7189 | -352.6413 | 16.8053
12:09 | 2956 | 33.5336 | 198.9007 | 445.0109 | 450.4087 | -18.2226 | -44.8718 | 8.2436 | 5.1229 | -0.962 | -2.2455 | 1.0852 | -2.5148 | 7.9865 | 1.6949 | 0.6017 | 0.6451 | 0.9584 | 0.7226 | -130.7845 | -4.6141 | 3.4538 | 0.5053 | -5.1919 | -3.6875 | 2.5484 |  | 0.8403 | -1.4459 | 4.0139 | 3.3633 | 3.3479 | 1.045 | 10.7463 | 14.2373 | 14.8066 | 11.0583 | 0.0003 | -0.003 | 0.001 | 0.004 | 0.0005 | -0.0003 | 0.0217 | -0.0013 | 0.0026 | -360.1958 | 17.4274 | -360.4819 | 17.7005 | -360.7773 | 18.1276 | -360.8697 | 17.5363 | -352.6967 | 18.7477 | -352.6998 | 16.795
12:09 | 2957 | 33.496 | 198.875 | 444.9286 | 450.37 | -18.2161 | -44.8721 | 8.1675 | 5.1193 | -0.9142 | -2.166 | 1.1053 | -2.3907 | 8.0257 | 1.7493 | 0.6048 | 0.6447 | 0.955 | 0.7225 | -130.8257 | -4.703 | 3.5056 | 0.4972 | -5.2305 | -3.6265 | 2.584 |  | 0.8813 | -1.3871 | 4.0147 | 3.3615 | 3.3475 | 1.0443 | 10.7544 | 14.257 | 14.8152 | 11.0489 | 0.0002 | -0.0027 | 0.0007 | 0.0036 | 0.001 | -0.0004 | 0.0206 | -0.0134 | -0.0265 | -360.2235 | 17.4397 | -360.5219 | 17.7293 | -360.8481 | 18.144 | -360.8758 | 17.5301 | -352.709 | 18.762 | -352.7183 | 16.8423
12:09 | 2958 | 33.5217 | 198.8903 | 444.9457 | 450.3431 | -18.2546 | -44.8544 | 8.2988 | 5.1493 | -0.9067 | -2.0929 | 1.087 | -2.4148 | 7.9962 | 1.7675 | 0.6016 | 0.6457 | 0.951 | 0.7223 | -130.7619 | -4.6861 | 3.4574 | 0.5389 | -5.1207 | -3.6428 | 2.5933 |  | 0.8126 | -1.4448 | 4.0129 | 3.363 | 3.3478 | 1.0448 | 10.7302 | 14.2612 | 14.8337 | 11.0779 | -0.0008 | -0.0033 | 0.0009 | 0.0037 | 0.0004 | -0.0006 | 0.0169 | -0.0063 | -0.0012 | -360.1281 | 17.3884 | -360.4512 | 17.7231 | -360.8204 | 18.1522 | -360.8481 | 17.5034 | -352.6352 | 18.7312 | -352.6844 | 16.8176
12:09 | 2959 | 33.5752 | 198.8753 | 444.9648 | 450.3411 | -18.2078 | -44.9636 | 8.2884 | 5.1449 | -0.9481 | -2.1963 | 1.0887 | -2.4946 | 8.0153 | 1.8241 | 0.603 | 0.6453 | 0.955 | 0.7218 | -130.8021 | -4.6526 | 3.526 | 0.5574 | -5.1539 | -3.637 | 2.587 |  | 0.8834 | -1.3363 | 4.0132 | 3.3663 | 3.3468 | 1.0447 | 10.7427 | 14.2573 | 14.7999 | 11.0828 | -0.0001 | -0.0023 | 0.0007 | 0.0039 | 0.001 | -0.0003 | 0.0179 | -0.0059 | -0.0143 | -360.1804 | 17.3946 | -360.4419 | 17.7108 | -360.8204 | 18.1769 | -360.9251 | 17.5445 | -352.669 | 18.723 | -352.6537 | 16.8074
12:09 | 2960 | 33.5403 | 198.9048 | 444.8962 | 450.4114 | -18.1109 | -44.8931 | 8.2615 | 5.1404 | -0.9531 | -2.2666 | 1.0094 | -2.4213 | 7.9845 | 1.7383 | 0.6035 | 0.6457 | 0.9545 | 0.722 | -130.8173 | -4.7508 | 3.5432 | 0.6065 | -5.2958 | -3.7586 | 2.5439 |  | 0.8707 | -1.487 | 4.0141 | 3.3669 | 3.3469 | 1.0444 | 10.7152 | 14.2231 | 14.8018 | 11.0569 | 0.0001 | -0.0032 | 0.0004 | 0.0038 | 0.0008 | -0.0005 | 0.0083 | -0.0048 | -0.0073 | -360.1681 | 17.4131 | -360.4573 | 17.7149 | -360.805 | 18.1563 | -360.9127 | 17.5588 | -352.7183 | 18.7477 | -352.669 | 16.8176
12:09 | 2961 | 33.5225 | 198.9103 | 444.9568 | 450.3529 | -18.1933 | -44.9265 | 8.221 | 5.1675 | -0.9418 | -2.2604 | 1.062 | -2.3989 | 8.107 | 1.7828 | 0.6052 | 0.6476 | 0.9527 | 0.7221 | -130.8475 | -4.7677 | 3.5297 | 0.6389 | -5.2423 | -3.6162 | 2.5456 |  | 0.8185 | -1.5059 | 4.0132 | 3.3668 | 3.3436 | 1.045 | 10.7139 | 14.2395 | 14.7909 | 11.032 | 0.0001 | -0.0031 | 0.0009 | 0.0042 | 0.0006 | -0.0004 | 0.0141 | -0.0085 | -0.0061 | -360.1465 | 17.4069 | -360.4666 | 17.7169 | -360.8112 | 18.1214 | -360.8204 | 17.5096 | -352.6352 | 18.7456 | -352.6783 | 16.8156
12:09 | 2962 | 33.4782 | 198.7898 | 444.8931 | 450.3781 | -18.1724 | -44.7649 | 8.3118 | 5.1717 | -0.9023 | -2.101 | 1.0473 | -2.3616 | 8.0737 | 1.796 | 0.604 | 0.6459 | 0.9524 | 0.721 | -130.7862 | -4.6607 | 3.5358 | 0.591 | -5.0975 | -3.496 | 2.6169 |  | 0.813 | -1.2974 | 4.014 | 3.366 | 3.3483 | 1.0451 | 10.6816 | 14.2474 | 14.8031 | 11.0638 | -0.0001 | -0.0027 | 0.0005 | 0.0039 | 0.0006 | -0.001 | 0.0126 | 0.0034 | -0.0135 | -360.1558 | 17.4172 | -360.5189 | 17.7559 | -360.8881 | 18.1687 | -360.8543 | 17.5219 | -352.6783 | 18.7456 | -352.7152 | 16.8464
12:09 | 2963 | 33.504 | 198.8774 | 444.7841 | 450.3322 | -18.1302 | -44.9109 | 8.3744 | 5.1599 | -0.9568 | -2.2139 | 0.9621 | -2.407 | 7.9747 | 1.804 | 0.603 | 0.6458 | 0.9531 | 0.7225 | -130.8059 | -4.6403 | 3.5071 | 0.6206 | -5.1486 | -3.6405 | 2.5509 |  | 0.7362 | -1.3828 | 4.0139 | 3.3639 | 3.35 | 1.0451 | 10.7602 | 14.2395 | 14.8025 | 11.0666 | -0.0001 | -0.0026 | 0.0004 | 0.0035 | 0.0005 | -0.0001 | -0.0046 | -0.004 | -0.024 | -360.1311 | 17.3925 | -360.4758 | 17.7231 | -360.8389 | 18.181 | -360.8881 | 17.5301 | -352.6383 | 18.7271 | -352.6721 | 16.8258
12:09 | 2964 | 33.4357 | 198.846 | 444.7918 | 450.3776 | -18.1111 | -44.772 | 8.4831 | 5.1938 | -0.8718 | -2.171 | 0.9827 | -2.364 | 7.9777 | 1.7604 | 0.6041 | 0.6442 | 0.9542 | 0.7211 | -130.8107 | -4.6609 | 3.4902 | 0.6244 | -5.1804 | -3.5652 | 2.6062 |  | 0.7745 | -1.3337 | 4.0143 | 3.3648 | 3.3485 | 1.0459 | 10.7369 | 14.2225 | 14.8336 | 11.0774 | 0.0005 | -0.0027 | 0.0007 | 0.004 | 0.0008 | -0.001 | 0.004 | 0.0008 | -0.0148 | -360.1835 | 17.4151 | -360.4542 | 17.6902 | -360.7743 | 18.1337 | -360.8666 | 17.5445 | -352.6721 | 18.7271 | -352.6567 | 16.7909
12:09 | 2965 | 33.618 | 198.8596 | 444.8562 | 450.4212 | -18.1077 | -44.7959 | 8.4116 | 5.0753 | -0.9406 | -2.1827 | 1.0302 | -2.4134 | 8.0896 | 1.7634 | 0.6023 | 0.6487 | 0.9524 | 0.7207 | -130.8493 | -4.654 | 3.4139 | 0.6575 | -5.1748 | -3.5863 | 2.5709 |  | 0.8733 | -1.3926 | 4.0146 | 3.366 | 3.3472 | 1.0455 | 10.7405 | 14.272 | 14.8124 | 11.0525 | 0.0002 | -0.0027 | 0.001 | 0.0039 | 0.0004 | -0.0003 | 0.0021 | -0.01 | -0.0071 | -360.1988 | 17.4644 | -360.5435 | 17.7477 | -360.8389 | 18.1296 | -360.8727 | 17.5465 | -352.7121 | 18.7764 | -352.7367 | 16.832
12:09 | 2966 | 33.5067 | 198.9219 | 444.9173 | 450.392 | -18.1806 | -44.8448 | 8.2936 | 5.1465 | -0.9074 | -2.1936 | 1.0067 | -2.4098 | 8.0465 | 1.8071 | 0.6037 | 0.6443 | 0.9522 | 0.7209 | -130.7949 | -4.558 | 3.4417 | 0.6432 | -5.1364 | -3.6782 | 2.5815 |  | 0.8915 | -1.3249 | 4.0139 | 3.3663 | 3.3517 | 1.0457 | 10.7405 | 14.2082 | 14.794 | 11.0645 | -0.0001 | -0.0025 | 0.0011 | 0.0041 | 0.0009 | -0.0008 | 0.0102 | 0.007 | 0.0093 | -360.1496 | 17.4131 | -360.485 | 17.7375 | -360.8297 | 18.1296 | -360.8358 | 17.5116 | -352.6383 | 18.7333 | -352.6752 | 16.8279
12:09 | 2967 | 33.5103 | 198.8052 | 444.9013 | 450.2383 | -18.131 | -44.8472 | 8.307 | 5.1676 | -0.901 | -2.0822 | 1.1206 | -2.3661 | 8.0719 | 1.7595 | 0.6038 | 0.6436 | 0.9502 | 0.721 | -130.776 | -4.6127 | 3.5017 | 0.6464 | -5.2398 | -3.6865 | 2.5142 |  | 0.8253 | -1.3091 | 4.0132 | 3.3659 | 3.3484 | 1.0449 | 10.7001 | 14.2253 | 14.7456 | 11.0479 | -0.0005 | -0.0028 | 0.0004 | 0.0038 | 0.0002 | -0.0008 | 0.0185 | -0.009 | 0.002 | -360.1588 | 17.4007 | -360.4696 | 17.7231 | -360.8266 | 18.1666 | -360.8943 | 17.528 | -352.6506 | 18.7066 | -352.6906 | 16.8135
12:09 | 2968 | 33.5083 | 198.897 | 444.9364 | 450.2462 | -18.1685 | -44.8166 | 8.3189 | 5.1696 | -0.9234 | -2.2287 | 1.05 | -2.3706 | 8.1274 | 1.7721 | 0.6035 | 0.6457 | 0.9513 | 0.7216 | -130.7916 | -4.5405 | 3.4907 | 0.5844 | -5.224 | -3.6131 | 2.5946 |  | 0.8552 | -1.3441 | 4.0138 | 3.3634 | 3.3465 | 1.0447 | 10.7382 | 14.2234 | 14.7923 | 11.0562 | 0.0003 | -0.0022 | 0.0008 | 0.0037 | 0.0005 | -0.0007 | 0.0188 | -0.0058 | 0.0032 | -360.2111 | 17.4192 | -360.445 | 17.7026 | -360.7958 | 18.1625 | -360.9251 | 17.565 | -352.7306 | 18.7374 | -352.6444 | 16.795
12:09 | 2969 | 33.549 | 198.9448 | 444.8908 | 450.3873 | -18.1141 | -44.8574 | 8.309 | 5.1547 | -0.9203 | -2.1503 | 1.0645 | -2.3795 | 8.1273 | 1.765 | 0.6021 | 0.6483 | 0.9502 | 0.7213 | -130.8295 | -4.6062 | 3.4523 | 0.6506 | -5.2084 | -3.747 | 2.5775 |  | 0.9143 | -1.4431 | 4.013 | 3.3604 | 3.3477 | 1.0454 | 10.7082 | 14.2105 | 14.7899 | 11.0439 | 0.0002 | -0.0033 | 0.0007 | 0.0043 | 0.0012 | -0.0005 | 0.0139 | -0.0183 | -0.0006 | -360.2019 | 17.4233 | -360.4481 | 17.6882 | -360.7712 | 18.1296 | -360.8697 | 17.5445 | -352.6629 | 18.7312 | -352.6537 | 16.7848
12:09 | 2970 | 33.4616 | 198.8404 | 444.8175 | 450.365 | -18.1551 | -44.8545 | 8.3755 | 5.2073 | -0.8888 | -2.2224 | 1.0284 | -2.4344 | 8.1118 | 1.7427 | 0.6037 | 0.6438 | 0.9491 | 0.7224 | -130.8877 | -4.5842 | 3.4104 | 0.6736 | -5.2349 | -3.6584 | 2.6483 |  | 0.9335 | -1.3837 | 4.0131 | 3.3632 | 3.3517 | 1.0461 | 10.7163 | 14.2185 | 14.7916 | 11.0522 | -0.0002 | -0.0031 | 0.0006 | 0.004 | 0.001 | -0.0004 | 0.0104 | -0.0007 | -0.0182 | -360.1711 | 17.4397 | -360.5189 | 17.7477 | -360.8574 | 18.1502 | -360.8758 | 17.5383 | -352.6721 | 18.7538 | -352.7429 | 16.8402
12:09 | 2971 | 33.4377 | 198.8458 | 444.87 | 450.2954 | -18.1568 | -44.9034 | 8.2706 | 5.1677 | -0.8761 | -2.2191 | 1.0071 | -2.3874 | 8.1096 | 1.7218 | 0.6032 | 0.6449 | 0.9531 | 0.7223 | -130.8666 | -4.6258 | 3.4965 | 0.6442 | -5.2922 | -3.5909 | 2.6328 |  | 0.9544 | -1.3245 | 4.013 | 3.3639 | 3.3483 | 1.0463 | 10.7325 | 14.2231 | 14.796 | 11.0396 | -0.0005 | -0.0025 | 0.0005 | 0.0034 | 0.001 | -0.0004 | 0.0031 | -0.0086 | -0.0073 | -360.0881 | 17.3782 | -360.4389 | 17.7313 | -360.845 | 18.1584 | -360.8666 | 17.5137 | -352.6475 | 18.6984 | -352.666 | 16.8156
12:09 | 2972 | 33.5397 | 198.8735 | 444.9052 | 450.3606 | -18.189 | -44.9012 | 8.2926 | 5.169 | -0.9009 | -2.1526 | 1.0543 | -2.3906 | 8.142 | 1.8143 | 0.6031 | 0.646 | 0.9537 | 0.7211 | -130.8072 | -4.6314 | 3.4652 | 0.699 | -5.2364 | -3.5729 | 2.6937 |  | 0.9801 | -1.3028 | 4.0124 | 3.3657 | 3.3467 | 1.0467 | 10.6991 | 14.2238 | 14.8057 | 11.0129 | -0.0004 | -0.003 | 0.0008 | 0.0038 | 0.0003 | -0.0007 | 0.0138 | -0.0079 | 0.0051 | -360.1588 | 17.4007 | -360.4573 | 17.721 | -360.8574 | 18.1687 | -360.882 | 17.5424 | -352.6875 | 18.7251 | -352.666 | 16.795
12:09 | 2973 | 33.5402 | 198.8206 | 444.8324 | 450.4357 | -18.1622 | -44.7977 | 8.2411 | 5.1613 | -0.8487 | -2.2578 | 0.999 | -2.3831 | 8.1548 | 1.8158 | 0.6038 | 0.6416 | 0.9509 | 0.7223 | -130.8508 | -4.5942 | 3.5522 | 0.5971 | -5.2912 | -3.624 | 2.6511 |  | 0.9967 | -1.235 | 4.0128 | 3.3659 | 3.3466 | 1.0465 | 10.729 | 14.2429 | 14.7882 | 11.0298 | 0.0003 | -0.0029 | 0.0006 | 0.0035 | 0.001 | -0.0005 | 0.0117 | -0.0054 | -0.0175 | -360.2235 | 17.4295 | -360.4727 | 17.7067 | -360.802 | 18.1399 | -360.8697 | 17.5486 | -352.7183 | 18.7456 | -352.7121 | 16.793
12:09 | 2974 | 33.5449 | 198.8498 | 444.9337 | 450.3835 | -18.1414 | -44.7868 | 8.2891 | 5.1621 | -0.8602 | -2.3165 | 1.01 | -2.3209 | 8.1248 | 1.7189 | 0.6038 | 0.643 | 0.9519 | 0.7225 | -130.9261 | -4.6347 | 3.521 | 0.5736 | -5.1726 | -3.7052 | 2.7167 |  | 1.0203 | -1.2121 | 4.0139 | 3.3665 | 3.3515 | 1.0467 | 10.7186 | 14.2266 | 14.7943 | 11.0313 | 0 | -0.0032 | 0.0006 | 0.0038 | 0.0008 | -0.0002 | 0.0004 | -0.0125 | -0.0133 | -360.1465 | 17.4418 | -360.5158 | 17.7252 | -360.8266 | 18.1214 | -360.8327 | 17.5157 | -352.6598 | 18.7456 | -352.7029 | 16.8032
12:09 | 2975 | 33.5712 | 198.873 | 444.9067 | 450.4384 | -18.1161 | -44.8606 | 8.1972 | 5.1914 | -0.9544 | -2.1772 | 1.0684 | -2.3232 | 8.0594 | 1.8268 | 0.6031 | 0.6462 | 0.9502 | 0.7227 | -130.8707 | -4.65 | 3.4616 | 0.5486 | -5.198 | -3.6211 | 2.659 |  | 0.9553 | -1.3565 | 4.0129 | 3.3666 | 3.3508 | 1.0466 | 10.7394 | 14.2474 | 14.8205 | 11.0695 | -0.0007 | -0.0029 | 0.0007 | 0.004 | 0.001 | -0.0007 | 0.0108 | -0.0135 | -0.0088 | -360.165 | 17.4315 | -360.5158 | 17.7375 | -360.8481 | 18.1604 | -360.8543 | 17.5383 | -352.6721 | 18.7374 | -352.7583 | 16.8299
12:09 | 2976 | 33.555 | 198.8306 | 444.7877 | 450.3396 | -18.1183 | -44.8998 | 8.2808 | 5.1836 | -0.987 | -2.2463 | 0.9878 | -2.4068 | 8.0407 | 1.8392 | 0.6024 | 0.644 | 0.9484 | 0.7223 | -130.905 | -4.538 | 3.4339 | 0.5467 | -5.1098 | -3.6263 | 2.6855 |  | 1.0467 | -1.2678 | 4.0144 | 3.3646 | 3.3519 | 1.0452 | 10.7369 | 14.2515 | 14.8636 | 11.0713 | -0.0002 | -0.0026 | 0.0007 | 0.0038 | 0.0005 | -0.0004 | 0.0158 | -0.0015 | 0.0013 | -360.1558 | 17.3843 | -360.4112 | 17.6964 | -360.7866 | 18.1543 | -360.8666 | 17.5363 | -352.6413 | 18.7004 | -352.6506 | 16.7889
12:09 | 2977 | 33.6341 | 198.8735 | 444.8707 | 450.3448 | -18.1786 | -44.9029 | 8.243 | 5.1064 | -0.9746 | -2.192 | 0.9681 | -2.3836 | 8.1014 | 1.8666 | 0.6017 | 0.6421 | 0.9479 | 0.7222 | -130.9241 | -4.4771 | 3.386 | 0.3921 | -5.0399 | -3.6042 | 2.7104 |  | 0.9921 | -1.2687 | 4.0147 | 3.3657 | 3.3501 | 1.0456 | 10.7232 | 14.2198 | 14.8056 | 11.0818 | -0.0004 | -0.0034 | 0.0003 | 0.0036 | 0.0009 | -0.0008 | 0.0087 | 0.0079 | 0.001 | -360.2542 | 17.4295 | -360.485 | 17.6944 | -360.8143 | 18.1522 | -360.9158 | 17.5712 | -352.7521 | 18.7456 | -352.6844 | 16.7909
12:09 | 2978 | 33.599 | 198.9198 | 444.8834 | 450.3813 | -18.1745 | -44.8084 | 8.1683 | 5.0681 | -0.9613 | -2.0667 | 0.9617 | -2.3422 | 8.0497 | 1.8599 | 0.6025 | 0.6485 | 0.951 | 0.7224 | -130.887 | -4.4897 | 3.3551 | 0.5374 | -5.0773 | -3.6613 | 2.6836 |  | 1.0134 | -1.2271 | 4.0152 | 3.3675 | 3.3513 | 1.0462 | 10.7278 | 14.2128 | 14.7984 | 11.0865 | 0.0003 | -0.0029 | 0.0009 | 0.0042 | 0.0011 | -0.0001 | -0.0048 | -0.0064 | -0.0199 | -360.1681 | 17.4233 | -360.4819 | 17.6964 | -360.7897 | 18.1317 | -360.845 | 17.528 | -352.706 | 18.7477 | -352.6998 | 16.7909
12:09 | 2979 | 33.5935 | 198.9627 | 444.7969 | 450.2857 | -18.1746 | -44.9158 | 8.1232 | 5.0314 | -0.9253 | -2.0944 | 0.9853 | -2.2521 | 8.1172 | 1.7751 | 0.6023 | 0.6429 | 0.9494 | 0.7221 | -130.8039 | -4.4473 | 3.3546 | 0.6482 | -5.0929 | -3.4776 | 2.6645 |  | 0.9947 | -1.3079 | 4.0145 | 3.3694 | 3.3477 | 1.0468 | 10.7439 | 14.2468 | 14.8234 | 11.0612 | -0.0003 | -0.003 | 0.0003 | 0.0036 | 0.0007 | -0.0003 | -0.0026 | -0.0103 | -0.0166 | -360.1527 | 17.4069 | -360.4912 | 17.7272 | -360.8543 | 18.1481 | -360.8481 | 17.5239 | -352.6444 | 18.7333 | -352.7213 | 16.8135
12:09 | 2980 | 33.5306 | 198.7903 | 444.8094 | 450.2889 | -18.1015 | -44.8298 | 8.2419 | 5.1074 | -0.9012 | -2.1661 | 0.9826 | -2.2589 | 8.1564 | 1.7632 | 0.6037 | 0.6404 | 0.9515 | 0.7219 | -130.8442 | -4.3752 | 3.4742 | 0.5524 | -5.1471 | -3.6341 | 2.6947 |  | 0.9877 | -1.349 | 4.0135 | 3.3685 | 3.3495 | 1.0453 | 10.7221 | 14.2125 | 14.7673 | 11.0584 | -0.0002 | -0.0026 | 0.0009 | 0.0036 | 0.0005 | -0.0007 | 0.0111 | -0.0022 | 0.0043 | -360.1558 | 17.3946 | -360.4512 | 17.7272 | -360.8481 | 18.183 | -360.9404 | 17.5445 | -352.669 | 18.7128 | -352.6721 | 16.8176
12:09 | 2981 | 33.592 | 198.8028 | 444.8101 | 450.3322 | -18.1285 | -44.9715 | 8.2861 | 5.04 | -0.9746 | -2.1549 | 0.9937 | -2.3523 | 8.1197 | 1.782 | 0.6035 | 0.6453 | 0.9509 | 0.7228 | -130.8859 | -4.4408 | 3.4118 | 0.6118 | -5.086 | -3.5659 | 2.7386 |  | 0.9581 | -1.3936 | 4.0138 | 3.3667 | 3.3484 | 1.0458 | 10.7081 | 14.2395 | 14.7794 | 11.0377 | 0 | -0.003 | 0.0009 | 0.0037 | 0.0006 | -0.0001 | 0.0087 | -0.0115 | -0.0035 | -360.1835 | 17.3905 | -360.4142 | 17.682 | -360.7897 | 18.142 | -360.8789 | 17.5321 | -352.6721 | 18.7087 | -352.6444 | 16.7848
12:09 | 2982 | 33.6074 | 198.8734 | 444.8202 | 450.2869 | -18.1034 | -44.8645 | 8.2828 | 5.0987 | -0.9047 | -2.0642 | 1.0377 | -2.345 | 8.0598 | 1.6889 | 0.6044 | 0.6441 | 0.9532 | 0.7234 | -130.8365 | -4.4283 | 3.4581 | 0.5416 | -5.1357 | -3.545 | 2.7242 |  | 0.9271 | -1.3582 | 4.0117 | 3.3683 | 3.3486 | 1.0465 | 10.7313 | 14.222 | 14.813 | 11.0728 | -0.0001 | -0.003 | 0.0005 | 0.0038 | 0.0011 | -0.0005 | 0.0189 | -0.0138 | -0.0184 | -360.2296 | 17.4521 | -360.5035 | 17.721 | -360.8297 | 18.1399 | -360.8727 | 17.5486 | -352.7306 | 18.7661 | -352.7398 | 16.8135
12:09 | 2983 | 33.6721 | 198.9852 | 444.888 | 450.4131 | -18.1678 | -44.9443 | 8.17 | 5.0849 | -0.9316 | -2.2273 | 0.9825 | -2.3683 | 8.0409 | 1.7579 | 0.6039 | 0.6415 | 0.9526 | 0.7221 | -130.8817 | -4.4304 | 3.4482 | 0.6199 | -5.0926 | -3.6125 | 2.8118 |  | 0.8946 | -1.3338 | 4.0129 | 3.3697 | 3.3498 | 1.0471 | 10.7128 | 14.2441 | 14.7606 | 11.0251 | -0.0001 | -0.0028 | 0.0009 | 0.004 | 0.0007 | -0.0002 | 0.0029 | -0.0125 | -0.0141 | -360.1558 | 17.4172 | -360.5096 | 17.7252 | -360.8235 | 18.1399 | -360.8297 | 17.4952 | -352.6752 | 18.7415 | -352.6998 | 16.8156
12:09 | 2984 | 33.6984 | 198.7986 | 444.9131 | 450.4309 | -18.2356 | -45.0265 | 8.2753 | 5.0936 | -0.9133 | -2.1807 | 0.9202 | -2.3585 | 8.073 | 1.6696 | 0.6038 | 0.6413 | 0.9505 | 0.7206 | -130.8779 | -4.364 | 3.4828 | 0.6484 | -5.1032 | -3.5497 | 2.7638 |  | 0.9533 | -1.2902 | 4.0129 | 3.3637 | 3.3502 | 1.0455 | 10.7231 | 14.2317 | 14.8193 | 11.0753 | -0.0003 | -0.0026 | 0.0005 | 0.0038 | 0.0013 | -0.0006 | 0.0231 | -0.0046 | -0.0209 | -360.1927 | 17.4172 | -360.4942 | 17.7334 | -360.8635 | 18.1584 | -360.8697 | 17.5198 | -352.626 | 18.7374 | -352.709 | 16.8197
12:09 | 2985 | 33.637 | 198.8367 | 445.0248 | 450.4512 | -18.1317 | -45.0135 | 8.3652 | 5.0568 | -0.986 | -2.2017 | 0.9522 | -2.2623 | 8.0788 | 1.821 | 0.6039 | 0.641 | 0.9475 | 0.7217 | -130.8925 | -4.3807 | 3.5787 | 0.5984 | -5.177 | -3.5992 | 2.6911 |  | 0.9258 | -1.365 | 4.0135 | 3.3675 | 3.3471 | 1.0456 | 10.7232 | 14.214 | 14.8229 | 11.0529 | 0.0001 | -0.0026 | 0.0001 | 0.0036 | 0.0006 | -0.0003 | 0.0262 | -0.0014 | 0.0003 | -360.2019 | 17.4048 | -360.4358 | 17.7046 | -360.7897 | 18.1645 | -360.885 | 17.5609 | -352.706 | 18.7374 | -352.666 | 16.8032
12:09 | 2986 | 33.676 | 198.8844 | 444.9598 | 450.4179 | -18.1094 | -44.9661 | 8.2744 | 5.0138 | -0.9794 | -2.2532 | 0.9591 | -2.3516 | 8.0204 | 1.8684 | 0.6036 | 0.6429 | 0.9475 | 0.7215 | -130.799 | -4.3937 | 3.5236 | 0.6167 | -5.1371 | -3.5905 | 2.7566 |  | 0.905 | -1.366 | 4.013 | 3.3667 | 3.3494 | 1.0461 | 10.7267 | 14.2117 | 14.7912 | 11.0161 | 0.0001 | -0.0031 | 0.001 | 0.0044 | 0.0007 | -0.001 | 0.0097 | 0.0019 | -0.0119 | -360.1773 | 17.4233 | -360.4573 | 17.6759 | -360.7804 | 18.1317 | -360.8604 | 17.5465 | -352.6967 | 18.7333 | -352.6937 | 16.7724
12:09 | 2987 | 33.6196 | 198.8636 | 444.9482 | 450.4068 | -18.1787 | -44.9882 | 8.279 | 5.0709 | -1.0292 | -2.1413 | 0.9956 | -2.4021 | 8.0902 | 1.7957 | 0.6045 | 0.6436 | 0.9503 | 0.723 | -130.8242 | -4.3513 | 3.4394 | 0.7104 | -4.9983 | -3.573 | 2.793 |  | 0.8609 | -1.3858 | 4.0123 | 3.3647 | 3.3473 | 1.046 | 10.7267 | 14.2289 | 14.7902 | 11.0049 | -0.0001 | -0.0028 | 0.0007 | 0.0038 | 0.0004 | -0.0003 | 0.0054 | -0.008 | -0.0071 | -360.245 | 17.4439 | -360.5158 | 17.7087 | -360.8204 | 18.1481 | -360.8727 | 17.5486 | -352.7213 | 18.7559 | -352.7213 | 16.8053
12:10 | 2988 | 33.6988 | 198.8879 | 444.9772 | 450.3857 | -18.163 | -44.9714 | 8.382 | 4.9897 | -1.0807 | -2.0398 | 1.0065 | -2.2771 | 8.2536 | 1.8282 | 0.602 | 0.6418 | 0.9514 | 0.7238 | -130.8227 | -4.2882 | 3.4801 | 0.6728 | -5.0915 | -3.5547 | 2.8016 |  | 0.9442 | -1.2949 | 4.0137 | 3.3645 | 3.3481 | 1.0471 | 10.7001 | 14.1848 | 14.7629 | 11.0363 | -0.0001 | -0.0022 | 0.0008 | 0.0035 | 0.0008 | -0.0007 | 0.0275 | 0.0027 | 0.0046 | -360.1158 | 17.4028 | -360.4696 | 17.7067 | -360.8297 | 18.1481 | -360.8389 | 17.5096 | -352.6567 | 18.7148 | -352.6875 | 16.8053
12:10 | 2989 | 33.6683 | 198.9637 | 444.8992 | 450.413 | -18.2457 | -44.895 | 8.3395 | 5.0081 | -0.9996 | -2.0687 | 1.01 | -2.3271 | 8.1173 | 1.8463 | 0.6036 | 0.6444 | 0.9518 | 0.7232 | -130.7806 | -4.3146 | 3.5164 | 0.7486 | -5.0571 | -3.5649 | 2.761 |  | 0.9988 | -1.3592 | 4.013 | 3.3629 | 3.3499 | 1.0466 | 10.7093 | 14.2174 | 14.7507 | 11.0276 | -0.0001 | -0.0029 | 0.0017 | 0.0043 | 0.001 | -0.0005 | 0.0058 | -0.0164 | -0.0024 | -360.1773 | 17.3966 | -360.4542 | 17.721 | -360.842 | 18.1871 | -360.9281 | 17.5383 | -352.669 | 18.723 | -352.6537 | 16.793
12:10 | 2990 | 33.6428 | 198.9553 | 444.9526 | 450.4525 | -18.1059 | -44.8803 | 8.4696 | 5.1674 | -0.9445 | -2.0423 | 0.987 | -2.2473 | 8.1327 | 1.8286 | 0.6042 | 0.6448 | 0.9488 | 0.723 | -130.8425 | -4.2884 | 3.5567 | 0.8456 | -5.1092 | -3.6239 | 2.7219 |  | 0.9187 | -1.4344 | 4.0143 | 3.3668 | 3.3476 | 1.0462 | 10.7474 | 14.2501 | 14.7906 | 11.0767 | 0.0006 | -0.0027 | 0.0009 | 0.0038 | 0.0008 | -0.0001 | -0.0016 | 0.0011 | 0.0018 | -360.1619 | 17.4028 | -360.4389 | 17.7005 | -360.8389 | 18.1604 | -360.8881 | 17.5568 | -352.6844 | 18.7169 | -352.666 | 16.7971
12:10 | 2991 | 33.7279 | 198.8427 | 444.9856 | 450.4449 | -18.0731 | -44.8657 | 8.5472 | 5.1063 | -0.8723 | -2.0921 | 1.0174 | -2.3101 | 8.1071 | 1.7828 | 0.6015 | 0.6457 | 0.9478 | 0.7219 | -130.9137 | -4.3478 | 3.5365 | 0.8093 | -5.1219 | -3.6225 | 2.743 |  | 0.9591 | -1.4145 | 4.0134 | 3.3691 | 3.3517 | 1.0464 | 10.729 | 14.2197 | 14.764 | 11.0244 | 0 | -0.003 | 0.001 | 0.004 | 0.0006 | -0.0007 | -0.0038 | -0.0116 | -0.0035 | -360.2019 | 17.4233 | -360.485 | 17.6964 | -360.7773 | 18.1255 | -360.8543 | 17.526 | -352.6813 | 18.7312 | -352.7029 | 16.793
12:10 | 2992 | 33.7326 | 198.8889 | 444.9599 | 450.4422 | -18.1778 | -44.8155 | 8.6156 | 5.1178 | -0.8167 | -2.0872 | 0.9662 | -2.4415 | 8.0381 | 1.7997 | 0.6036 | 0.6427 | 0.9475 | 0.7239 | -130.8482 | -4.332 | 3.5126 | 0.8043 | -5.1063 | -3.4864 | 2.6992 |  | 0.943 | -1.3438 | 4.0143 | 3.3638 | 3.3511 | 1.0457 | 10.7301 | 14.2327 | 14.8369 | 11.0478 | -0.0004 | -0.0027 | 0.0008 | 0.0039 | 0.0011 | -0.0001 | 0.0056 | -0.0011 | 0.0009 | -360.1835 | 17.4315 | -360.5312 | 17.7518 | -360.8727 | 18.1563 | -360.8635 | 17.526 | -352.6598 | 18.7497 | -352.7337 | 16.8381
12:10 | 2993 | 33.7138 | 198.8864 | 445.0024 | 450.4836 | -18.1846 | -44.7917 | 8.6716 | 5.0895 | -0.8622 | -2.0625 | 0.9826 | -2.4021 | 8.115 | 1.7572 | 0.6033 | 0.6429 | 0.9491 | 0.7224 | -130.8235 | -4.4163 | 3.4571 | 0.7671 | -5.122 | -3.6301 | 2.7245 |  | 0.9275 | -1.3768 | 4.0135 | 3.3654 | 3.348 | 1.0474 | 10.7545 | 14.2392 | 14.7888 | 11.0616 | -0.0005 | -0.0029 | -0.0001 | 0.0033 | 0.001 | -0.0007 | -0.0011 | -0.0173 | -0.0096 | -360.1311 | 17.3946 | -360.4573 | 17.719 | -360.8327 | 18.1502 | -360.845 | 17.5157 | -352.6229 | 18.7128 | -352.6967 | 16.8217
12:10 | 2994 | 33.7705 | 198.9273 | 444.9628 | 450.4951 | -18.1342 | -44.7366 | 8.4595 | 5.1118 | -0.8676 | -2.0617 | 0.9461 | -2.3517 | 8.0527 | 1.8528 | 0.6032 | 0.6434 | 0.9466 | 0.7229 | -130.822 | -4.4253 | 3.4691 | 0.7587 | -5.1208 | -3.5229 | 2.762 |  | 0.8953 | -1.321 | 4.0145 | 3.3639 | 3.3493 | 1.0462 | 10.7152 | 14.2287 | 14.8123 | 11.0515 | -0.0002 | -0.0032 | 0.0006 | 0.0037 | 0.0008 | -0.0004 | 0.0101 | -0.0053 | 0.0043 | -360.1558 | 17.3966 | -360.4542 | 17.6985 | -360.8174 | 18.1522 | -360.882 | 17.5465 | -352.6875 | 18.7107 | -352.6537 | 16.8012
12:10 | 2995 | 33.6372 | 198.9422 | 444.9128 | 450.5464 | -18.19 | -44.7917 | 8.4518 | 5.068 | -0.8342 | -2.0618 | 0.9531 | -2.3904 | 8.036 | 1.8508 | 0.6031 | 0.6459 | 0.9503 | 0.7234 | -130.8807 | -4.4035 | 3.4948 | 0.8254 | -5.1044 | -3.4579 | 2.8127 |  | 0.9662 | -1.322 | 4.013 | 3.3667 | 3.3517 | 1.0473 | 10.7244 | 14.238 | 14.7874 | 11.0028 | -0.0001 | -0.0031 | 0.0008 | 0.0038 | 0.0009 | -0.0009 | 0.0114 | 0.0019 | -0.0067 | -360.2173 | 17.4439 | -360.4973 | 17.7005 | -360.8174 | 18.1358 | -360.8666 | 17.5588 | -352.7213 | 18.7579 | -352.7152 | 16.8094
12:10 | 2996 | 33.6913 | 198.9145 | 444.9993 | 450.5149 | -18.1352 | -44.7319 | 8.4807 | 5.1166 | -0.6964 | -2.0387 | 1.0218 | -2.4136 | 8.094 | 1.9263 | 0.6026 | 0.6448 | 0.9512 | 0.7227 | -130.8539 | -4.5066 | 3.5101 | 0.836 | -5.1153 | -3.496 | 2.7546 |  | 0.9975 | -1.3154 | 4.0146 | 3.3673 | 3.3482 | 1.0471 | 10.7095 | 14.217 | 14.7939 | 11.0403 | -0.0004 | -0.003 | 0.0009 | 0.0035 | 0.0002 | -0.0002 | -0.0024 | -0.0063 | 0.0074 | -360.2019 | 17.4192 | -360.4542 | 17.7087 | -360.8327 | 18.1132 | -360.8481 | 17.5363 | -352.6752 | 18.7271 | -352.6813 | 16.8053
12:10 | 2997 | 33.7408 | 198.8796 | 445.0107 | 450.5325 | -18.1051 | -44.6112 | 8.5342 | 5.1543 | -0.6289 | -2.0721 | 1.0285 | -2.3504 | 8.1388 | 1.9658 | 0.6028 | 0.6449 | 0.9543 | 0.7233 | -130.8768 | -4.4143 | 3.5462 | 0.8138 | -5.0732 | -3.5488 | 2.7883 |  | 1.0089 | -1.2919 | 4.0141 | 3.3656 | 3.3519 | 1.0457 | 10.737 | 14.2281 | 14.763 | 11.0605 | -0.0002 | -0.0025 | 0.001 | 0.0038 | 0.0006 | -0.0006 | 0.017 | -0.0144 | -0.0095 | -360.1588 | 17.4254 | -360.5035 | 17.7231 | -360.8666 | 18.1687 | -360.8943 | 17.5383 | -352.6198 | 18.7312 | -352.6967 | 16.8135
12:10 | 2998 | 33.7584 | 198.8853 | 444.9286 | 450.5032 | -18.0563 | -44.5587 | 8.582 | 5.2505 | -0.6466 | -1.9975 | 1.1087 | -2.2236 | 8.1817 | 1.9983 | 0.6025 | 0.6445 | 0.9524 | 0.723 | -130.7558 | -4.4255 | 3.4379 | 0.7523 | -5.0975 | -3.5677 | 2.7265 |  | 0.9989 | -1.2646 | 4.0136 | 3.3675 | 3.3511 | 1.0458 | 10.7509 | 14.242 | 14.8121 | 11.0626 | 0.0001 | -0.0033 | 0.001 | 0.0037 | 0.0008 | -0.0002 | 0.0097 | -0.007 | -0.0084 | -360.1896 | 17.3987 | -360.4142 | 17.6964 | -360.805 | 18.1625 | -360.9127 | 17.5506 | -352.6937 | 18.7169 | -352.629 | 16.7991
12:10 | 2999 | 33.703 | 198.8806 | 445.0456 | 450.5343 | -18.0728 | -44.6231 | 8.5818 | 5.3626 | -0.607 | -1.8223 | 1.1416 | -2.2497 | 8.1606 | 1.842 | 0.6031 | 0.6437 | 0.9483 | 0.722 | -130.7855 | -4.3498 | 3.4486 | 0.8535 | -5.0305 | -3.5497 | 2.7729 |  | 1.0184 | -1.2621 | 4.0148 | 3.3646 | 3.3489 | 1.0461 | 10.7498 | 14.2637 | 14.8086 | 11.0854 | -0.0001 | -0.0032 | 0.0005 | 0.0033 | 0.0005 | -0.0004 | 0.001 | 0.0001 | -0.0231 | -360.1742 | 17.3925 | -360.445 | 17.6861 | -360.7773 | 18.1543 | -360.8881 | 17.5383 | -352.6721 | 18.7087 | -352.6198 | 16.7745
12:10 | 3000 | 33.6789 | 198.902 | 444.9287 | 450.4068 | -17.9986 | -44.5125 | 8.6864 | 5.3454 | -0.6697 | -2.0543 | 1.0466 | -2.2889 | 8.1829 | 1.9336 | 0.6031 | 0.6427 | 0.9504 | 0.7224 | -130.7138 | -4.3725 | 3.5861 | 0.8124 | -5.0884 | -3.5644 | 2.808 |  | 1.0383 | -1.2889 | 4.0145 | 3.3688 | 3.3474 | 1.0465 | 10.7404 | 14.2432 | 14.8424 | 11.0926 | -0.0001 | -0.0024 | 0.0005 | 0.0039 | 0.0005 | -0.0011 | 0.0113 | -0.0243 | -0.0076 | -360.2758 | 17.4459 | -360.4881 | 17.719 | -360.8543 | 18.1625 | -360.8943 | 17.5486 | -352.6998 | 18.76 | -352.706 | 16.8032
12:10 | 3001 | 33.7378 | 198.9365 | 445.1029 | 450.4087 | -18.0941 | -44.4408 | 8.7006 | 5.2053 | -0.8515 | -2.1602 | 0.9218 | -2.2906 | 8.1353 | 2.0032 | 0.6037 | 0.6435 | 0.95 | 0.7234 | -130.7599 | -4.3642 | 3.5574 | 0.8119 | -5.0763 | -3.5207 | 2.7409 |  | 0.9679 | -1.4219 | 4.0131 | 3.3659 | 3.3487 | 1.0467 | 10.7578 | 14.2431 | 14.8587 | 11.0988 | -0.0009 | -0.0031 | 0.0001 | 0.0035 | 0.0009 | -0.0001 | 0.0055 | -0.0108 | -0.0124 | -360.1311 | 17.4007 | -360.4635 | 17.7272 | -360.8389 | 18.1235 | -360.845 | 17.5239 | -352.6044 | 18.7169 | -352.706 | 16.8217
12:10 | 3002 | 33.6912 | 198.8769 | 445.0634 | 450.4049 | -18.0817 | -44.5499 | 8.6423 | 5.277 | -0.7617 | -2.0991 | 1.0006 | -2.372 | 8.1451 | 1.9354 | 0.6029 | 0.641 | 0.9497 | 0.7221 | -130.7528 | -4.3262 | 3.5465 | 0.6842 | -5.0923 | -3.6188 | 2.7105 |  | 0.9765 | -1.2912 | 4.0137 | 3.3687 | 3.3455 | 1.0463 | 10.7012 | 14.2382 | 14.7943 | 11.0717 | 0.0002 | -0.0028 | 0.0006 | 0.0041 | 0.0007 | -0.0012 | 0.0192 | -0.0138 | -0.0172 | -360.125 | 17.411 | -360.4635 | 17.7169 | -360.8604 | 18.1645 | -360.8789 | 17.5239 | -352.6537 | 18.7251 | -352.6783 | 16.8074
12:10 | 3003 | 33.7647 | 198.9254 | 445.0336 | 450.4782 | -18.0834 | -44.5064 | 8.5768 | 5.3423 | -0.8258 | -2.0701 | 1.0238 | -2.4579 | 8.0103 | 1.8632 | 0.6047 | 0.6441 | 0.9498 | 0.7221 | -130.7405 | -4.3707 | 3.5217 | 0.6641 | -5.0615 | -3.5511 | 2.7528 |  | 0.8728 | -1.2658 | 4.014 | 3.3687 | 3.3493 | 1.0461 | 10.7243 | 14.2327 | 14.8138 | 11.0478 | 0.0003 | -0.003 | 0.0011 | 0.0041 | 0.0005 | -0.0002 | 0.009 | -0.0045 | -0.0078 | -360.205 | 17.4295 | -360.4666 | 17.7067 | -360.842 | 18.1481 | -360.9035 | 17.5712 | -352.6875 | 18.7395 | -352.6875 | 16.8115
12:10 | 3004 | 33.8057 | 198.9656 | 445.0676 | 450.559 | -18.0695 | -44.5034 | 8.6308 | 5.4065 | -0.819 | -2.0137 | 1.0344 | -2.3907 | 8.1589 | 1.9835 | 0.6038 | 0.6438 | 0.9501 | 0.7215 | -130.7259 | -4.39 | 3.4696 | 0.7901 | -5.058 | -3.5616 | 2.7517 |  | 0.9236 | -1.2952 | 4.0137 | 3.3669 | 3.3521 | 1.0466 | 10.7198 | 14.2102 | 14.7935 | 11.01 | -0.0002 | -0.0027 | 0.0005 | 0.0038 | 0.0007 | -0.0007 | 0.0133 | 0.0026 | -0.0011 | -360.2019 | 17.4172 | -360.485 | 17.7026 | -360.7958 | 18.1029 | -360.8758 | 17.5239 | -352.669 | 18.7436 | -352.706 | 16.7827
12:10 | 3005 | 33.8412 | 198.9271 | 445.1752 | 450.556 | -18.1287 | -44.5731 | 8.6063 | 5.3666 | -0.852 | -1.9531 | 1.0774 | -2.3671 | 8.1625 | 1.9411 | 0.6023 | 0.6439 | 0.9541 | 0.7208 | -130.6838 | -4.4654 | 3.5052 | 0.6631 | -5.0411 | -3.5703 | 2.7352 |  | 0.9299 | -1.3357 | 4.0131 | 3.3676 | 3.3467 | 1.0464 | 10.692 | 14.2059 | 14.7739 | 11.0334 | 0.0002 | -0.0025 | 0.0012 | 0.0042 | 0.0003 | -0.0004 | 0.0068 | -0.0023 | 0.0076 | -360.1927 | 17.4295 | -360.5343 | 17.7231 | -360.8635 | 18.1317 | -360.9066 | 17.5445 | -352.6875 | 18.7538 | -352.749 | 16.8156
12:10 | 3006 | 33.8841 | 199.0208 | 445.1403 | 450.4776 | -18.1522 | -44.5291 | 8.5803 | 5.3928 | -0.8804 | -1.9006 | 1.0544 | -2.3716 | 8.166 | 1.9179 | 0.6028 | 0.6443 | 0.9529 | 0.722 | -130.7985 | -4.4027 | 3.4489 | 0.8583 | -5.1306 | -3.7572 | 2.6881 |  | 1.0457 | -1.2711 | 4.0135 | 3.3673 | 3.3459 | 1.0469 | 10.7451 | 14.2594 | 14.8295 | 11.0684 | -0.0002 | -0.0028 | 0.001 | 0.0039 | 0.0011 | -0.0001 | 0.0046 | -0.0074 | -0.0052 | -360.1865 | 17.3884 | -360.4204 | 17.7005 | -360.8112 | 18.1194 | -360.8758 | 17.5363 | -352.6475 | 18.7066 | -352.6721 | 16.8074
12:10 | 3007 | 33.8277 | 198.9345 | 445.1297 | 450.5486 | -18.0465 | -44.4437 | 8.6745 | 5.3822 | -0.8479 | -1.899 | 1.0881 | -2.3903 | 8.221 | 1.9087 | 0.6029 | 0.6477 | 0.953 | 0.7206 | -130.7289 | -4.318 | 3.4854 | 0.8161 | -5.0884 | -3.6368 | 2.7063 |  | 0.9959 | -1.2791 | 4.014 | 3.3687 | 3.3467 | 1.0456 | 10.7498 | 14.2059 | 14.8086 | 11.0623 | 0.0006 | -0.0028 | 0.0004 | 0.0035 | 0.0007 | -0.0005 | 0.0019 | -0.0156 | -0.0116 | -360.1988 | 17.4213 | -360.4542 | 17.682 | -360.7835 | 18.1276 | -360.8881 | 17.5445 | -352.6475 | 18.7271 | -352.6752 | 16.7807
12:10 | 3008 | 33.8273 | 198.9551 | 445.0341 | 450.5689 | -17.9982 | -44.5992 | 8.6281 | 5.3001 | -0.9034 | -1.8851 | 1.1097 | -2.4523 | 8.1736 | 1.9907 | 0.6038 | 0.6484 | 0.9527 | 0.7223 | -130.7634 | -4.4479 | 3.5088 | 0.8111 | -4.9427 | -3.4149 | 2.8465 |  | 0.9803 | -1.211 | 4.0125 | 3.3678 | 3.35 | 1.0454 | 10.721 | 14.2229 | 14.7775 | 11.0457 | -0.0002 | -0.003 | 0.0004 | 0.0035 | 0.0009 | -0.0008 | 0.025 | -0.0185 | -0.026 | -360.1865 | 17.4233 | -360.4635 | 17.719 | -360.8266 | 18.1214 | -360.8666 | 17.5629 | -352.7152 | 18.7415 | -352.7029 | 16.8176
12:10 | 3009 | 33.8039 | 198.955 | 444.9976 | 450.584 | -17.9697 | -44.5596 | 8.7737 | 5.3902 | -0.868 | -1.9333 | 1.1399 | -2.416 | 8.1653 | 1.9296 | 0.6037 | 0.6496 | 0.9539 | 0.7226 | -130.7132 | -4.432 | 3.5747 | 0.8223 | -4.9074 | -3.5451 | 2.8301 |  | 0.9505 | -1.2428 | 4.0133 | 3.3667 | 3.3445 | 1.0444 | 10.7313 | 14.2627 | 14.8199 | 11.0724 | -0.0004 | -0.0021 | 0.0005 | 0.0039 | 0.0004 | -0.0006 | 0.0276 | -0.0016 | 0.0019 | -360.1558 | 17.4069 | -360.4266 | 17.6902 | -360.7804 | 18.1214 | -360.8574 | 17.5321 | -352.6413 | 18.7169 | -352.6721 | 16.795
12:10 | 3010 | 33.7588 | 198.9563 | 445.0779 | 450.4662 | -17.9528 | -44.4121 | 8.7827 | 5.3723 | -0.8824 | -1.8555 | 1.1907 | -2.3405 | 8.2537 | 2.0193 | 0.6032 | 0.6461 | 0.9532 | 0.7216 | -130.765 | -4.4377 | 3.5552 | 0.8356 | -4.9683 | -3.4217 | 2.8129 |  | 1.0426 | -1.2546 | 4.0138 | 3.3684 | 3.3489 | 1.0461 | 10.7129 | 14.209 | 14.7748 | 11.032 | -0.0003 | -0.003 | 0.0002 | 0.0036 | 0.0004 | -0.0007 | -0.008 | -0.0048 | -0.0107 | -360.1896 | 17.4151 | -360.5066 | 17.721 | -360.8481 | 18.1255 | -360.885 | 17.565 | -352.6567 | 18.7292 | -352.6875 | 16.8094
12:10 | 3011 | 33.8 | 199.0626 | 445.1281 | 450.5227 | -18.0213 | -44.4919 | 8.6813 | 5.4557 | -0.8157 | -1.8021 | 1.1398 | -2.3831 | 8.2581 | 2.059 | 0.605 | 0.6486 | 0.955 | 0.7219 | -130.7822 | -4.4625 | 3.5844 | 0.6716 | -5.0006 | -3.5257 | 2.7715 |  | 0.9863 | -1.3203 | 4.0116 | 3.3671 | 3.3475 | 1.0464 | 10.707 | 14.2093 | 14.7538 | 11.0313 | 0.0004 | -0.0025 | 0.001 | 0.004 | 0.001 | -0.0007 | 0.0234 | -0.0079 | -0.0156 | -360.1404 | 17.3946 | -360.4542 | 17.7128 | -360.8081 | 18.1214 | -360.8912 | 17.5506 | -352.6198 | 18.7251 | -352.6844 | 16.8012
12:10 | 3012 | 33.9088 | 199.0466 | 445.0622 | 450.5299 | -18.0466 | -44.4377 | 8.6675 | 5.3933 | -0.8147 | -1.9751 | 1.1241 | -2.4493 | 8.1705 | 2.0587 | 0.604 | 0.6418 | 0.954 | 0.7213 | -130.7435 | -4.4521 | 3.5317 | 0.6906 | -5.0627 | -3.4742 | 2.7877 |  | 0.9883 | -1.1797 | 4.0121 | 3.371 | 3.3474 | 1.0462 | 10.737 | 14.2106 | 14.8025 | 11.0262 | 0.0001 | -0.0031 | 0.0007 | 0.0037 | 0.0005 | 0 | 0.0067 | -0.003 | 0.011 | -360.1742 | 17.3987 | -360.4512 | 17.6985 | -360.7989 | 18.1132 | -360.8666 | 17.5527 | -352.6413 | 18.7169 | -352.669 | 16.793
12:10 | 3013 | 33.7676 | 198.9587 | 445.0314 | 450.5129 | -17.9903 | -44.474 | 8.6427 | 5.3568 | -0.7413 | -1.9418 | 1.1077 | -2.4242 | 8.2023 | 1.9451 | 0.6039 | 0.6397 | 0.952 | 0.7225 | -130.6679 | -4.4019 | 3.6283 | 0.6726 | -5.137 | -3.5001 | 2.781 |  | 0.9495 | -1.2723 | 4.0129 | 3.3649 | 3.3467 | 1.0464 | 10.7348 | 14.2429 | 14.8113 | 11.0702 | -0.0002 | -0.0029 | 0.0005 | 0.0034 | 0.0007 | -0.0008 | 0.0038 | -0.0022 | -0.0023 | -360.2111 | 17.4459 | -360.5096 | 17.7149 | -360.842 | 18.1276 | -360.8758 | 17.5629 | -352.7244 | 18.7477 | -352.6906 | 16.8115
12:10 | 3014 | 33.8159 | 199.045 | 445.1278 | 450.5767 | -18.0551 | -44.4134 | 8.5866 | 5.3763 | -0.7417 | -1.9562 | 1.0574 | -2.379 | 8.1543 | 1.9068 | 0.6032 | 0.646 | 0.9534 | 0.7226 | -130.6152 | -4.4264 | 3.4705 | 0.5959 | -5.1587 | -3.5006 | 2.8278 |  | 0.9921 | -1.3157 | 4.0137 | 3.3677 | 3.3458 | 1.0459 | 10.7219 | 14.2536 | 14.8121 | 11.0395 | -0.0001 | -0.0025 | 0.001 | 0.0037 | 0.0006 | 0.0001 | 0.001 | -0.0046 | -0.0185 | -360.1219 | 17.4069 | -360.4789 | 17.7231 | -360.805 | 18.0865 | -360.8574 | 17.5342 | -352.6413 | 18.7189 | -352.6937 | 16.8115
12:10 | 3015 | 33.8675 | 198.942 | 445.1703 | 450.5698 | -18.0196 | -44.4005 | 8.654 | 5.3445 | -0.7232 | -1.9845 | 1.0994 | -2.4088 | 8.1907 | 1.9931 | 0.6033 | 0.6478 | 0.954 | 0.7227 | -130.6979 | -4.3587 | 3.5633 | 0.563 | -5.1108 | -3.531 | 2.8843 |  | 1.067 | -1.2599 | 4.0139 | 3.367 | 3.3477 | 1.0469 | 10.7279 | 14.2241 | 14.8021 | 11.041 | 0 | -0.0033 | 0 | 0.0033 | 0.0009 | -0.0005 | 0.0047 | -0.0168 | -0.0152 | -360.1773 | 17.4151 | -360.4942 | 17.7272 | -360.8574 | 18.1317 | -360.8974 | 17.5404 | -352.6475 | 18.7189 | -352.6813 | 16.8053
12:10 | 3016 | 33.848 | 198.995 | 445.1265 | 450.4905 | -17.992 | -44.3493 | 8.5945 | 5.4456 | -0.6684 | -2.008 | 1.1521 | -2.3342 | 8.1259 | 1.9608 | 0.6033 | 0.6457 | 0.9517 | 0.7229 | -130.6774 | -4.3822 | 3.6598 | 0.58 | -5.15 | -3.4989 | 2.7544 |  | 1.0351 | -1.2688 | 4.0139 | 3.3715 | 3.3484 | 1.0464 | 10.7221 | 14.2243 | 14.7858 | 11.0176 | 0.0002 | -0.003 | 0.0008 | 0.0039 | 0.0003 | -0.0005 | 0.0122 | 0.0007 | -0.0118 | -360.2142 | 17.3966 | -360.4512 | 17.7046 | -360.8112 | 18.1194 | -360.9097 | 17.5691 | -352.6844 | 18.7045 | -352.6752 | 16.8053
12:10 | 3017 | 33.815 | 199.0734 | 445.1156 | 450.4914 | -18.0694 | -44.3623 | 8.5599 | 5.4553 | -0.6874 | -2.0863 | 1.1776 | -2.3018 | 8.0475 | 1.9659 | 0.602 | 0.6447 | 0.9508 | 0.7227 | -130.7023 | -4.3559 | 3.6244 | 0.5755 | -5.1402 | -3.4558 | 2.7681 |  | 0.9948 | -1.3243 | 4.0144 | 3.3712 | 3.3487 | 1.0455 | 10.7451 | 14.2247 | 14.7832 | 11.0222 | -0.0003 | -0.0023 | 0.0011 | 0.0044 | 0.001 | -0.0006 | 0.0187 | 0.0125 | -0.0016 | -360.2265 | 17.4315 | -360.4666 | 17.6861 | -360.7927 | 18.1029 | -360.8512 | 17.565 | -352.6937 | 18.7312 | -352.6567 | 16.7848
12:10 | 3018 | 33.9188 | 198.9677 | 445.0788 | 450.5274 | -18.0322 | -44.3577 | 8.5546 | 5.417 | -0.6852 | -2.0405 | 1.0919 | -2.3723 | 8.1216 | 2.0465 | 0.6037 | 0.6438 | 0.9529 | 0.7225 | -130.6738 | -4.3674 | 3.5991 | 0.5593 | -5.1709 | -3.605 | 2.7626 |  | 1.0396 | -1.3158 | 4.0135 | 3.3696 | 3.3477 | 1.0444 | 10.7141 | 14.2216 | 14.7693 | 11.0219 | -0.0008 | -0.0031 | 0.0008 | 0.004 | 0.0006 | -0.0005 | -0.0003 | -0.0058 | -0.0074 | -360.2173 | 17.4295 | -360.5096 | 17.7354 | -360.8635 | 18.1255 | -360.845 | 17.5568 | -352.6998 | 18.7374 | -352.7213 | 16.8217
12:10 | 3019 | 33.9082 | 199.0423 | 445.1266 | 450.4772 | -17.9517 | -44.2525 | 8.5192 | 5.4149 | -0.7227 | -2.1051 | 1.1466 | -2.3367 | 8.1249 | 2.0095 | 0.603 | 0.6447 | 0.9555 | 0.7225 | -130.6655 | -4.3959 | 3.5842 | 0.5987 | -5.1418 | -3.4839 | 2.7683 |  | 1.0102 | -1.3132 | 4.0142 | 3.369 | 3.3487 | 1.0462 | 10.6918 | 14.2235 | 14.7702 | 11.0442 | 0.0002 | -0.0028 | 0.0012 | 0.0042 | 0.0009 | -0.0002 | 0.0027 | 0.0023 | -0.0268 | -360.1004 | 17.3823 | -360.4389 | 17.7128 | -360.805 | 18.1337 | -360.8697 | 17.526 | -352.6136 | 18.6984 | -352.6567 | 16.8135
12:10 | 3020 | 33.9012 | 199.0649 | 445.1362 | 450.5474 | -17.9497 | -44.3315 | 8.4805 | 5.3904 | -0.751 | -2.1285 | 1.143 | -2.4149 | 8.1314 | 2.1042 | 0.6028 | 0.6465 | 0.9531 | 0.7228 | -130.6827 | -4.3956 | 3.6295 | 0.6168 | -5.1017 | -3.5669 | 2.8112 |  | 1.0238 | -1.3391 | 4.0133 | 3.366 | 3.3485 | 1.0457 | 10.7313 | 14.2395 | 14.8025 | 11.0782 | -0.0001 | -0.0036 | 0.0009 | 0.0035 | 0.0009 | -0.0007 | 0.0111 | -0.0107 | 0.0024 | -360.205 | 17.411 | -360.4327 | 17.7067 | -360.8481 | 18.1502 | -360.9281 | 17.5835 | -352.6875 | 18.7025 | -352.6383 | 16.793
12:10 | 3021 | 33.8758 | 199.0491 | 445.1272 | 450.507 | -17.9054 | -44.2852 | 8.5857 | 5.4323 | -0.6645 | -2.0019 | 1.1651 | -2.348 | 8.1555 | 2.091 | 0.6022 | 0.647 | 0.9496 | 0.7222 | -130.5701 | -4.2787 | 3.5772 | 0.4979 | -5.1193 | -3.54 | 2.7651 |  | 1.0387 | -1.3596 | 4.0125 | 3.3674 | 3.3472 | 1.0452 | 10.737 | 14.2511 | 14.8025 | 11.0609 | -0.0002 | -0.0026 | 0.0007 | 0.0035 | 0.0002 | -0.0003 | 0.001 | 0.0016 | -0.0029 | -360.1681 | 17.4131 | -360.4819 | 17.7067 | -360.7773 | 18.1173 | -360.8974 | 17.5712 | -352.7121 | 18.723 | -352.6998 | 16.7991
12:10 | 3022 | 33.8892 | 199.0855 | 445.0392 | 450.5267 | -17.8988 | -44.2759 | 8.5752 | 5.4302 | -0.6925 | -2.1095 | 1.0817 | -2.3595 | 8.1873 | 2.1595 | 0.6024 | 0.6455 | 0.9509 | 0.7231 | -130.5407 | -4.2813 | 3.5704 | 0.5516 | -5.0134 | -3.5155 | 2.8181 |  | 1.0645 | -1.3725 | 4.0125 | 3.3644 | 3.347 | 1.0466 | 10.73 | 14.2444 | 14.8091 | 11.0821 | -0.0004 | -0.0027 | 0.0007 | 0.0036 | 0.0008 | -0.0007 | 0.0135 | -0.0107 | -0.0202 | -360.1527 | 17.4131 | -360.4942 | 17.7231 | -360.8481 | 18.0968 | -360.8235 | 17.5198 | -352.6013 | 18.7148 | -352.7275 | 16.8115
12:10 | 3023 | 33.9341 | 199.0809 | 445.1899 | 450.5698 | -17.8678 | -44.3355 | 8.5491 | 5.4355 | -0.7003 | -2.0834 | 1.0295 | -2.3003 | 8.2298 | 2.0888 | 0.6035 | 0.6418 | 0.9527 | 0.724 | -130.6179 | -4.3125 | 3.4818 | 0.5798 | -5.0223 | -3.5315 | 2.7511 |  | 1.1331 | -1.2623 | 4.0123 | 3.367 | 3.3504 | 1.0466 | 10.7312 | 14.2455 | 14.7978 | 11.0778 | 0.0001 | -0.0028 | 0.0002 | 0.0034 | 0.0006 | -0.0002 | 0.0228 | 0.005 | -0.0055 | -360.1496 | 17.409 | -360.5066 | 17.7518 | -360.9097 | 18.1502 | -360.8912 | 17.5404 | -352.6567 | 18.7128 | -352.706 | 16.834
12:10 | 3024 | 33.9608 | 199.0785 | 445.1922 | 450.5742 | -17.8965 | -44.3588 | 8.6106 | 5.3523 | -0.7703 | -2.2126 | 1.077 | -2.3334 | 8.1978 | 2.0651 | 0.6035 | 0.6397 | 0.9524 | 0.722 | -130.5629 | -4.3426 | 3.5916 | 0.6534 | -5.0134 | -3.5217 | 2.7973 |  | 1.0721 | -1.3165 | 4.0138 | 3.3628 | 3.3488 | 1.0478 | 10.6804 | 14.2289 | 14.7555 | 11.0569 | 0.0004 | -0.0031 | 0.0008 | 0.0044 | 0.0012 | -0.0005 | 0.0099 | -0.0086 | 0.0027 | -360.1835 | 17.3987 | -360.4173 | 17.7005 | -360.8297 | 18.1317 | -360.8943 | 17.5527 | -352.6721 | 18.7066 | -352.6444 | 16.7991
12:10 | 3025 | 33.927 | 199.0703 | 445.1525 | 450.5052 | -17.837 | -44.2597 | 8.6556 | 5.4384 | -0.6887 | -2.1671 | 1.0921 | -2.2339 | 8.2404 | 2.03 | 0.6035 | 0.6455 | 0.9524 | 0.7222 | -130.5459 | -4.3177 | 3.6069 | 0.6436 | -5.1232 | -3.5676 | 2.8309 |  | 1.0979 | -1.2184 | 4.013 | 3.3673 | 3.3482 | 1.046 | 10.7462 | 14.2317 | 14.7787 | 11.0464 | -0.0001 | -0.0029 | 0.0008 | 0.0039 | 0.0007 | -0.0005 | 0.0164 | -0.0039 | -0.005 | -360.2019 | 17.4254 | -360.4912 | 17.6944 | -360.7804 | 18.0968 | -360.845 | 17.5609 | -352.6783 | 18.7353 | -352.6998 | 16.7786
12:10 | 3026 | 33.9841 | 199.1014 | 445.1651 | 450.4658 | -17.9263 | -44.2734 | 8.6244 | 5.4526 | -0.6994 | -2.1299 | 1.0462 | -2.2265 | 8.2036 | 1.9912 | 0.6039 | 0.6441 | 0.9472 | 0.7218 | -130.6202 | -4.3273 | 3.6243 | 0.7146 | -4.914 | -3.4909 | 2.8634 |  | 1.1561 | -1.2006 | 4.0124 | 3.3672 | 3.3467 | 1.0464 | 10.7244 | 14.2266 | 14.8059 | 11.0659 | -0.0004 | -0.0024 | 0.0005 | 0.0038 | 0.0008 | -0.0009 | 0.0127 | -0.011 | 0.0035 | -360.1896 | 17.4521 | -360.5496 | 17.7272 | -360.8512 | 18.1132 | -360.842 | 17.5486 | -352.6783 | 18.7497 | -352.7644 | 16.8238
12:10 | 3027 | 33.9867 | 199.1863 | 445.3349 | 450.5793 | -17.8952 | -44.2414 | 8.7997 | 5.3904 | -0.7621 | -2.1202 | 1.0525 | -2.2539 | 8.2177 | 2.0251 | 0.603 | 0.6454 | 0.9519 | 0.7218 | -130.623 | -4.327 | 3.6276 | 0.6083 | -4.984 | -3.5658 | 2.7273 |  | 1.1344 | -1.2043 | 4.0129 | 3.3669 | 3.3505 | 1.0469 | 10.6896 | 14.2152 | 14.7838 | 11.054 | 0.0001 | -0.0027 | 0.0015 | 0.0041 | 0.0007 | -0.0003 | 0.0168 | -0.0118 | 0.0125 | -360.1373 | 17.3843 | -360.4512 | 17.7128 | -360.802 | 18.105 | -360.845 | 17.5404 | -352.589 | 18.6943 | -352.669 | 16.8094
12:10 | 3028 | 33.903 | 199.0782 | 445.2339 | 450.4933 | -17.9521 | -44.3655 | 8.6767 | 5.4155 | -0.6836 | -2.0138 | 1.0661 | -2.2815 | 8.1726 | 2.0842 | 0.6036 | 0.6476 | 0.9537 | 0.7228 | -130.6284 | -4.3861 | 3.5798 | 0.826 | -4.9611 | -3.4997 | 2.7543 |  | 1.0935 | -1.2168 | 4.0146 | 3.3682 | 3.3475 | 1.0469 | 10.7336 | 14.2361 | 14.8168 | 11.0572 | 0.0002 | -0.003 | 0.0008 | 0.0036 | 0.001 | -0.0006 | 0.0133 | -0.0123 | 0.012 | -360.1558 | 17.4028 | -360.4358 | 17.7046 | -360.8266 | 18.144 | -360.9158 | 17.5732 | -352.7029 | 18.7025 | -352.6567 | 16.795
12:10 | 3029 | 33.9103 | 198.9678 | 445.2094 | 450.5002 | -18.0434 | -44.6102 | 8.7247 | 5.3579 | -0.6706 | -2.0689 | 1.0194 | -2.1824 | 8.164 | 2.1038 | 0.6028 | 0.6443 | 0.952 | 0.724 | -130.6127 | -4.3435 | 3.6198 | 0.7834 | -5.0462 | -3.5608 | 2.7606 |  | 1.1469 | -1.1831 | 4.0137 | 3.3655 | 3.3507 | 1.0454 | 10.7337 | 14.2358 | 14.7684 | 11.0176 | -0.0002 | -0.0029 | 0.0006 | 0.0035 | 0.001 | -0.0002 | 0.0114 | -0.0051 | -0.0161 | -360.1527 | 17.4131 | -360.4512 | 17.6779 | -360.7835 | 18.1194 | -360.8943 | 17.5732 | -352.706 | 18.723 | -352.6783 | 16.7889
12:10 | 3030 | 33.9333 | 198.9785 | 445.1302 | 450.4847 | -17.9998 | -44.4916 | 8.5753 | 5.4181 | -0.7144 | -1.9896 | 1.0804 | -2.2617 | 8.1023 | 2.1276 | 0.6033 | 0.6422 | 0.9478 | 0.7232 | -130.5967 | -4.3942 | 3.6335 | 0.8576 | -5.0457 | -3.5488 | 2.8071 |  | 1.1435 | -1.1844 | 4.0122 | 3.3628 | 3.3463 | 1.0454 | 10.714 | 14.2392 | 14.7772 | 11.0558 | -0.0003 | -0.0026 | 0.0007 | 0.0039 | 0.0006 | -0.0004 | 0.0134 | -0.0021 | 0.0024 | -360.1773 | 17.4172 | -360.4666 | 17.7046 | -360.8266 | 18.1112 | -360.842 | 17.5445 | -352.6567 | 18.7169 | -352.6537 | 16.795
12:10 | 3031 | 33.9375 | 198.9967 | 445.2246 | 450.4405 | -18.0669 | -44.3908 | 8.5439 | 5.4131 | -0.6643 | -2.0496 | 1.1359 | -2.2162 | 8.1837 | 2.1436 | 0.6045 | 0.641 | 0.9533 | 0.7235 | -130.6359 | -4.284 | 3.6504 | 0.8079 | -5.1443 | -3.6385 | 2.7905 |  | 1.1179 | -1.0983 | 4.0138 | 3.3648 | 3.3465 | 1.046 | 10.7382 | 14.2232 | 14.8144 | 11.0681 | 0 | -0.0027 | 0.0006 | 0.0038 | 0.0009 | -0.0004 | 0.0189 | -0.0089 | -0.0185 | -360.1527 | 17.4131 | -360.5158 | 17.7498 | -360.8943 | 18.1399 | -360.885 | 17.5506 | -352.6506 | 18.723 | -352.7521 | 16.8361
12:10 | 3032 | 33.9274 | 198.978 | 445.1868 | 450.5059 | -18.06 | -44.4627 | 8.6866 | 5.4514 | -0.6469 | -1.9484 | 1.112 | -2.2159 | 8.1768 | 2.0968 | 0.6019 | 0.6425 | 0.9568 | 0.7238 | -130.6562 | -4.3407 | 3.7053 | 0.7226 | -5.1179 | -3.5846 | 2.7995 |  | 1.1006 | -1.1327 | 4.0126 | 3.3628 | 3.3474 | 1.0452 | 10.7429 | 14.222 | 14.7899 | 11.0612 | -0.0001 | -0.0032 | 0.0004 | 0.004 | 0.0006 | -0.0004 | -0.0073 | -0.0118 | -0.0157 | -360.1342 | 17.3782 | -360.4481 | 17.6944 | -360.7866 | 18.1214 | -360.8758 | 17.5445 | -352.6198 | 18.6902 | -352.6475 | 16.7971
12:10 | 3033 | 33.9387 | 199.0347 | 445.2304 | 450.5821 | -17.9682 | -44.5014 | 8.6761 | 5.3644 | -0.7265 | -2.0648 | 1.0343 | -2.2698 | 8.1417 | 2.1137 | 0.6035 | 0.6431 | 0.9547 | 0.7256 | -130.7024 | -4.4088 | 3.6733 | 0.7202 | -5.1608 | -3.6826 | 2.7296 |  | 1.0464 | -1.1475 | 4.0136 | 3.3669 | 3.346 | 1.0458 | 10.7174 | 14.2139 | 14.7987 | 11.0533 | 0.0004 | -0.0028 | 0.0008 | 0.0042 | 0.0007 | -0.0011 | 0.0078 | -0.0128 | 0.009 | -360.2111 | 17.4274 | -360.4973 | 17.7067 | -360.8081 | 18.1153 | -360.8758 | 17.5609 | -352.6875 | 18.7271 | -352.6721 | 16.7909
12:10 | 3034 | 33.961 | 199.036 | 445.2039 | 450.5799 | -17.8296 | -44.394 | 8.5929 | 5.4329 | -0.7516 | -2 | 1.0089 | -2.1155 | 8.2421 | 2.1125 | 0.6035 | 0.6394 | 0.9556 | 0.7226 | -130.6915 | -4.2202 | 3.7107 | 0.843 | -5.1544 | -3.5811 | 2.7869 |  | 1.0622 | -1.1439 | 4.0134 | 3.3645 | 3.3497 | 1.0443 | 10.7325 | 14.2463 | 14.8028 | 11.0219 | -0.0002 | -0.0026 | 0.0008 | 0.0041 | 0.0004 | -0.0003 | 0.0019 | -0.0096 | -0.0087 | -360.1588 | 17.4192 | -360.5066 | 17.7272 | -360.805 | 18.1153 | -360.882 | 17.5486 | -352.6752 | 18.721 | -352.7306 | 16.8217
12:10 | 3035 | 33.9524 | 199.0428 | 445.2114 | 450.5846 | -17.7927 | -44.4119 | 8.6543 | 5.4595 | -0.6528 | -1.9003 | 1.0705 | -2.0271 | 8.1904 | 2.175 | 0.6036 | 0.6395 | 0.9534 | 0.725 | -130.6923 | -4.3398 | 3.8031 | 0.7958 | -5.1251 | -3.5436 | 2.7373 |  | 1.1186 | -1.2024 | 4.0132 | 3.3713 | 3.3508 | 1.046 | 10.7382 | 14.2696 | 14.8097 | 11.0504 | -0.0004 | -0.0024 | 0.0006 | 0.0038 | 0.0005 | -0.0011 | 0.0047 | -0.0024 | -0.0252 | -360.1558 | 17.4048 | -360.4512 | 17.6985 | -360.8081 | 18.1255 | -360.842 | 17.5465 | -352.6229 | 18.7128 | -352.6598 | 16.8012
12:10 | 3036 | 34.0873 | 199.1741 | 445.3322 | 450.7199 | -17.8429 | -44.3781 | 8.6719 | 5.481 | -0.6258 | -1.8278 | 1.1217 | -2.0886 | 8.2684 | 2.2338 | 0.6039 | 0.6403 | 0.9505 | 0.7253 | -130.6817 | -4.2238 | 3.8106 | 0.8636 | -5.1424 | -3.7176 | 2.8586 |  | 1.1355 | -1.2057 | 4.0124 | 3.3681 | 3.3474 | 1.0453 | 10.7163 | 14.2243 | 14.7916 | 11.0176 | 0.0001 | -0.0031 | 0.0006 | 0.0037 | 0.0005 | -0.0004 | 0.0094 | -0.0092 | 0.009 | -360.2019 | 17.4131 | -360.5066 | 17.7252 | -360.802 | 18.1276 | -360.9004 | 17.5609 | -352.6506 | 18.721 | -352.706 | 16.8197
12:10 | 3037 | 34.0944 | 199.0994 | 445.3299 | 450.6101 | -17.8478 | -44.3857 | 8.6442 | 5.4201 | -0.5437 | -1.9395 | 1.118 | -2.1315 | 8.3463 | 2.2405 | 0.6041 | 0.641 | 0.9556 | 0.7257 | -130.7055 | -4.2712 | 3.8491 | 0.8479 | -5.0467 | -3.5237 | 2.8434 |  | 1.1738 | -1.1888 | 4.0129 | 3.3667 | 3.3475 | 1.0476 | 10.7278 | 14.2302 | 14.7868 | 11.0634 | 0.0001 | -0.0032 | 0.0007 | 0.004 | 0.001 | -0.0005 | 0.0106 | -0.0108 | 0.0047 | -360.1219 | 17.4007 | -360.4173 | 17.6882 | -360.8266 | 18.1153 | -360.882 | 17.5424 | -352.6475 | 18.7004 | -352.6352 | 16.7889
12:10 | 3038 | 34.0491 | 199.1073 | 445.2219 | 450.5555 | -17.7802 | -44.2654 | 8.6541 | 5.4731 | -0.5771 | -1.8886 | 1.2174 | -2.1444 | 8.2616 | 2.2546 | 0.6036 | 0.6433 | 0.9521 | 0.7236 | -130.6875 | -4.2403 | 3.8114 | 0.7918 | -5.1462 | -3.537 | 2.8024 |  | 1.1851 | -1.2546 | 4.0148 | 3.3672 | 3.3478 | 1.0477 | 10.7266 | 14.2465 | 14.8328 | 11.0446 | -0.0002 | -0.0025 | 0.001 | 0.0039 | 0.0009 | -0.0003 | 0.0033 | -0.0077 | -0.0227 | -360.1865 | 17.4315 | -360.4942 | 17.7108 | -360.8235 | 18.1399 | -360.922 | 17.5753 | -352.7121 | 18.7312 | -352.7029 | 16.8032
12:10 | 3039 | 34.1189 | 199.1367 | 445.2237 | 450.5865 | -17.8462 | -44.2613 | 8.6779 | 5.4548 | -0.5629 | -1.8527 | 1.2133 | -2.1225 | 8.3724 | 2.2808 | 0.606 | 0.6447 | 0.9545 | 0.7256 | -130.6404 | -4.1568 | 3.8702 | 0.837 | -5.1127 | -3.5852 | 2.7912 |  | 1.1911 | -1.1266 | 4.0138 | 3.3643 | 3.3479 | 1.046 | 10.7048 | 14.2357 | 14.7731 | 11.0237 | -0.0006 | -0.0029 | 0.0008 | 0.004 | 0.0007 | -0.0003 | 0.0182 | -0.0155 | 0.0066 | -360.1588 | 17.4069 | -360.4635 | 17.7005 | -360.802 | 18.105 | -360.8297 | 17.5404 | -352.6475 | 18.7025 | -352.6629 | 16.7991
12:10 | 3040 | 34.0025 | 199.1294 | 445.261 | 450.5911 | -17.8067 | -44.2517 | 8.6716 | 5.4751 | -0.6576 | -1.8997 | 1.2771 | -2.1661 | 8.3386 | 2.1725 | 0.6035 | 0.6419 | 0.9518 | 0.725 | -130.6617 | -4.1495 | 3.8442 | 0.7785 | -5.2437 | -3.613 | 2.7481 |  | 1.1612 | -1.2472 | 4.0138 | 3.3671 | 3.3485 | 1.0461 | 10.759 | 14.2501 | 14.8369 | 11.0594 | 0 | -0.003 | 0.0011 | 0.0041 | 0.0009 | -0.0006 | -0.0002 | -0.0026 | -0.0243 | -360.1711 | 17.4131 | -360.5312 | 17.7293 | -360.8327 | 18.1481 | -360.8974 | 17.5424 | -352.6167 | 18.7128 | -352.7244 | 16.8176
12:10 | 3041 | 34.1119 | 199.1508 | 445.3068 | 450.6129 | -17.861 | -44.2078 | 8.6382 | 5.5503 | -0.6411 | -2.0188 | 1.2495 | -2.1607 | 8.2976 | 2.2058 | 0.6035 | 0.6432 | 0.9511 | 0.7244 | -130.6502 | -4.194 | 3.9243 | 0.7496 | -5.1575 | -3.6319 | 2.8064 |  | 1.1702 | -1.1121 | 4.0123 | 3.3659 | 3.3502 | 1.0476 | 10.6967 | 14.2044 | 14.7878 | 11.0389 | 0 | -0.0034 | 0.0006 | 0.0038 | 0.0007 | -0.0003 | -0.001 | -0.0117 | -0.0052 | -360.1742 | 17.3782 | -360.4327 | 17.7128 | -360.845 | 18.1255 | -360.882 | 17.5404 | -352.666 | 18.6881 | -352.6383 | 16.8074
12:10 | 3042 | 34.0518 | 199.1012 | 445.2495 | 450.6001 | -17.8387 | -44.2528 | 8.7109 | 5.5655 | -0.6412 | -1.9948 | 1.1585 | -2.068 | 8.3428 | 2.2135 | 0.6039 | 0.6437 | 0.9492 | 0.7244 | -130.6779 | -4.2605 | 3.8347 | 0.7191 | -5.0616 | -3.6017 | 2.7566 |  | 1.2341 | -1.1683 | 4.0117 | 3.3655 | 3.3508 | 1.0482 | 10.7255 | 14.2452 | 14.7899 | 11.0497 | -0.0003 | -0.0028 | 0.0007 | 0.0041 | 0.001 | -0.0003 | -0.0046 | -0.0123 | -0.0086 | -360.1896 | 17.4192 | -360.4666 | 17.6985 | -360.7989 | 18.1255 | -360.885 | 17.565 | -352.709 | 18.7251 | -352.666 | 16.7848
12:10 | 3043 | 34.0432 | 199.1645 | 445.2286 | 450.5229 | -17.935 | -44.4063 | 8.6695 | 5.4418 | -0.6687 | -2.0293 | 1.0734 | -2.1156 | 8.3686 | 2.2295 | 0.6047 | 0.6429 | 0.9504 | 0.7251 | -130.684 | -4.3005 | 3.8053 | 0.8094 | -4.9895 | -3.665 | 2.9147 |  | 1.1572 | -1.2813 | 4.0124 | 3.3648 | 3.3483 | 1.0471 | 10.7186 | 14.2208 | 14.7711 | 11.0197 | -0.0003 | -0.0028 | 0.0006 | 0.0041 | 0.0007 | -0.0001 | -0.0042 | -0.0075 | -0.0043 | -360.1988 | 17.4295 | -360.5066 | 17.7272 | -360.8081 | 18.105 | -360.8481 | 17.5363 | -352.6752 | 18.7436 | -352.7183 | 16.8217
12:10 | 3044 | 33.9726 | 199.1036 | 445.1201 | 450.4156 | -17.8622 | -44.3842 | 8.6789 | 5.3622 | -0.6574 | -2.0768 | 1.0872 | -2.114 | 8.3475 | 2.1792 | 0.6035 | 0.6433 | 0.9521 | 0.7263 | -130.7004 | -4.2326 | 3.8148 | 0.7756 | -5.0437 | -3.5206 | 2.8051 |  | 1.1103 | -1.2459 | 4.0141 | 3.3682 | 3.3491 | 1.0483 | 10.736 | 14.244 | 14.8174 | 11.0313 | -0.0003 | -0.0032 | 0.0008 | 0.0036 | 0.001 | -0.0008 | 0.013 | -0.0171 | -0.0058 | -360.125 | 17.409 | -360.5035 | 17.7334 | -360.8389 | 18.1153 | -360.8789 | 17.5219 | -352.6198 | 18.7148 | -352.706 | 16.8115
12:10 | 3045 | 34.0613 | 199.164 | 445.2455 | 450.627 | -17.8316 | -44.3532 | 8.7311 | 5.3541 | -0.627 | -1.9728 | 1.1303 | -2.0842 | 8.3559 | 2.2078 | 0.6046 | 0.6411 | 0.9552 | 0.7246 | -130.7259 | -4.2866 | 3.6874 | 0.7304 | -5.1012 | -3.597 | 2.8381 |  | 1.0964 | -1.3444 | 4.0132 | 3.3647 | 3.3493 | 1.0472 | 10.7774 | 14.2747 | 14.8289 | 11.0713 | 0.0002 | -0.0029 | 0.0012 | 0.004 | 0.0009 | 0.0001 | 0.0066 | -0.015 | -0.0206 | -360.1742 | 17.3966 | -360.4542 | 17.7149 | -360.8266 | 18.1399 | -360.9251 | 17.5712 | -352.706 | 18.7189 | -352.6629 | 16.8012
12:10 | 3046 | 34.1554 | 199.2697 | 445.1993 | 450.6682 | -17.8625 | -44.3393 | 8.7329 | 5.4493 | -0.5726 | -1.9768 | 1.2228 | -2.1636 | 8.2914 | 2.1176 | 0.6022 | 0.6418 | 0.9529 | 0.7253 | -130.6642 | -4.1853 | 3.7569 | 0.9124 | -5.0514 | -3.5264 | 2.9084 |  | 1.1267 | -1.2431 | 4.0124 | 3.3639 | 3.3479 | 1.0466 | 10.751 | 14.23 | 14.7916 | 11.0522 | -0.0003 | -0.003 | 0.0009 | 0.0036 | 0.0008 | -0.0009 | 0.0234 | -0.014 | -0.0057 | -360.2142 | 17.4151 | -360.4266 | 17.6759 | -360.7835 | 18.0927 | -360.8604 | 17.5671 | -352.7029 | 18.7312 | -352.6506 | 16.7683
12:10 | 3047 | 34.1398 | 199.2487 | 445.2446 | 450.653 | -17.8455 | -44.3024 | 8.7417 | 5.5083 | -0.5535 | -2.0065 | 1.1473 | -2.2156 | 8.2175 | 2.0203 | 0.6036 | 0.6424 | 0.9505 | 0.7256 | -130.6721 | -4.1577 | 3.7243 | 0.9108 | -5.0391 | -3.5974 | 2.9092 |  | 1.1573 | -1.1892 | 4.0139 | 3.3648 | 3.3477 | 1.0463 | 10.7288 | 14.2492 | 14.8377 | 11.0633 | -0.0001 | -0.0024 | 0.0008 | 0.004 | 0.0009 | -0.0003 | 0.0238 | 0.0004 | 0.0047 | -360.2388 | 17.4439 | -360.5281 | 17.7272 | -360.802 | 18.1132 | -360.8697 | 17.5629 | -352.706 | 18.7538 | -352.706 | 16.8074
12:11 | 3048 | 34.1116 | 199.2577 | 445.2801 | 450.6125 | -17.9528 | -44.3368 | 8.7383 | 5.4115 | -0.6015 | -2.0369 | 1.1246 | -2.1914 | 8.3276 | 2.0363 | 0.6033 | 0.6406 | 0.9559 | 0.7246 | -130.6178 | -4.1185 | 3.8319 | 0.8988 | -5.1133 | -3.7358 | 2.9338 |  | 1.197 | -1.17 | 4.0136 | 3.3678 | 3.3494 | 1.0471 | 10.7474 | 14.2501 | 14.7733 | 11.0478 | 0.0001 | -0.0025 | 0.0005 | 0.0039 | 0.0007 | -0.0008 | 0.0133 | -0.0075 | 0.0016 | -360.0911 | 17.3925 | -360.4481 | 17.7026 | -360.8204 | 18.1194 | -360.8512 | 17.5178 | -352.629 | 18.6984 | -352.6752 | 16.8094
12:11 | 3049 | 34.0532 | 199.1738 | 445.2319 | 450.5796 | -17.9594 | -44.4164 | 8.6737 | 5.4659 | -0.6056 | -2.0254 | 1.1681 | -2.1423 | 8.3549 | 2.0594 | 0.6033 | 0.6429 | 0.9538 | 0.7265 | -130.6528 | -4.0713 | 3.7388 | 0.8587 | -5.1932 | -3.5639 | 2.8977 |  | 1.2551 | -1.2036 | 4.0136 | 3.3658 | 3.3503 | 1.046 | 10.7128 | 14.2208 | 14.8001 | 11.0486 | 0 | -0.0032 | 0.0008 | 0.0038 | 0.0008 | -0.0004 | 0.0112 | -0.0119 | 0.0079 | -360.1496 | 17.3966 | -360.4327 | 17.7087 | -360.8543 | 18.1625 | -360.9435 | 17.5671 | -352.6352 | 18.6984 | -352.6629 | 16.8012
12:11 | 3050 | 34.0547 | 199.1775 | 445.2447 | 450.5813 | -17.8585 | -44.3971 | 8.8007 | 5.5137 | -0.5693 | -1.893 | 1.1791 | -2.1626 | 8.3012 | 2.143 | 0.6051 | 0.6421 | 0.954 | 0.7234 | -130.7081 | -4.0337 | 3.7693 | 0.8352 | -5.1985 | -3.4825 | 2.9204 |  | 1.1749 | -1.2608 | 4.0132 | 3.3645 | 3.3469 | 1.0475 | 10.7058 | 14.214 | 14.7708 | 11.0182 | 0.0003 | -0.0028 | 0.0009 | 0.0038 | 0.0008 | -0.0005 | 0.0149 | -0.0132 | -0.0184 | -360.1558 | 17.3884 | -360.4419 | 17.6902 | -360.7958 | 18.1276 | -360.8912 | 17.5568 | -352.6906 | 18.7066 | -352.6598 | 16.7889
12:11 | 3051 | 34.0329 | 199.1505 | 445.1323 | 450.6707 | -18.0007 | -44.582 | 8.6526 | 5.4658 | -0.5963 | -1.9862 | 1.1024 | -2.2353 | 8.2979 | 2.091 | 0.6039 | 0.6443 | 0.9558 | 0.7246 | -130.6561 | -3.9947 | 3.7269 | 0.8103 | -5.1189 | -3.5491 | 2.916 |  | 1.2059 | -1.0752 | 4.0132 | 3.3645 | 3.3457 | 1.0466 | 10.721 | 14.2171 | 14.7775 | 11.0573 | -0.0004 | -0.0028 | 0.0006 | 0.0035 | 0.0009 | -0.0004 | 0.0097 | 0.0028 | -0.0324 | -360.165 | 17.4233 | -360.4758 | 17.6964 | -360.8112 | 18.0988 | -360.8574 | 17.5424 | -352.6506 | 18.7271 | -352.666 | 16.7868
12:11 | 3052 | 34.0079 | 199.1609 | 445.2105 | 450.6259 | -18.0464 | -44.5307 | 8.6252 | 5.5136 | -0.5427 | -2.0614 | 1.1353 | -2.2582 | 8.2426 | 2.064 | 0.6042 | 0.6428 | 0.9562 | 0.7246 | -130.6683 | -3.9901 | 3.8069 | 0.8448 | -5.1441 | -3.7915 | 2.8864 |  | 1.2439 | -1.0586 | 4.0119 | 3.3662 | 3.3501 | 1.0471 | 10.7186 | 14.2151 | 14.7711 | 11.037 | -0.0003 | -0.0024 | 0.001 | 0.0038 | 0.0009 | 0 | 0.0065 | -0.0092 | 0.006 | -360.165 | 17.4274 | -360.5343 | 17.7252 | -360.885 | 18.1194 | -360.8543 | 17.5527 | -352.669 | 18.7395 | -352.7552 | 16.8299
12:11 | 3053 | 34.0573 | 199.0978 | 445.1589 | 450.6385 | -18.0468 | -44.4449 | 8.6637 | 5.4938 | -0.7099 | -1.9289 | 1.0765 | -2.148 | 8.4108 | 2.1914 | 0.6034 | 0.6459 | 0.9562 | 0.7258 | -130.696 | -4.1789 | 3.7045 | 0.8304 | -5.1671 | -3.637 | 2.8607 |  | 1.2017 | -1.1823 | 4.0138 | 3.365 | 3.3495 | 1.0468 | 10.7232 | 14.214 | 14.7998 | 11.0471 | 0.0001 | -0.0033 | 0.0006 | 0.0037 | 0.0013 | -0.0005 | 0.0201 | -0.0117 | 0.0074 | -360.1435 | 17.3946 | -360.4542 | 17.6841 | -360.7989 | 18.1153 | -360.8604 | 17.526 | -352.6198 | 18.7148 | -352.6752 | 16.7971
12:11 | 3054 | 34.035 | 199.0925 | 445.163 | 450.5886 | -18.1156 | -44.4023 | 8.6056 | 5.5127 | -0.6043 | -1.9644 | 1.1926 | -2.2216 | 8.338 | 2.051 | 0.6054 | 0.6438 | 0.9584 | 0.7256 | -130.6389 | -4.0831 | 3.817 | 0.7536 | -5.1116 | -3.535 | 2.9751 |  | 1.0775 | -1.1538 | 4.0141 | 3.366 | 3.3509 | 1.0496 | 10.751 | 14.2475 | 14.8042 | 11.0692 | 0.0003 | -0.0025 | 0.001 | 0.0041 | 0.0006 | -0.0003 | 0.0019 | -0.0013 | 0.0019 | -360.1958 | 17.4254 | -360.4912 | 17.6861 | -360.8112 | 18.1296 | -360.9097 | 17.5835 | -352.6937 | 18.721 | -352.6783 | 16.793
12:11 | 3055 | 34.0411 | 199.1758 | 445.1438 | 450.6774 | -18.0795 | -44.5134 | 8.6155 | 5.4898 | -0.5971 | -1.9846 | 1.0497 | -2.2001 | 8.2898 | 1.9424 | 0.6042 | 0.6452 | 0.9565 | 0.7242 | -130.6658 | -4.092 | 3.7299 | 0.6523 | -5.1891 | -3.5308 | 2.8923 |  | 1.1087 | -1.2051 | 4.0132 | 3.3645 | 3.3472 | 1.0476 | 10.7462 | 14.2432 | 14.7961 | 11.0695 | -0.0004 | -0.0029 | 0.0009 | 0.0039 | 0.0012 | -0.0006 | 0.0032 | -0.0142 | -0.0056 | -360.1835 | 17.411 | -360.4512 | 17.6923 | -360.8266 | 18.0824 | -360.8112 | 17.5568 | -352.6567 | 18.7169 | -352.6783 | 16.7909
12:11 | 3056 | 34.0435 | 199.1895 | 445.1119 | 450.615 | -18.11 | -44.3693 | 8.6914 | 5.4723 | -0.6257 | -2.0782 | 1.1117 | -2.3221 | 8.2976 | 2.0469 | 0.6034 | 0.6441 | 0.9549 | 0.7242 | -130.5572 | -4.1212 | 3.8874 | 0.666 | -5.2378 | -3.5182 | 2.8666 |  | 1.2051 | -1.1328 | 4.0122 | 3.3668 | 3.3471 | 1.0461 | 10.7221 | 14.2183 | 14.7905 | 11.0699 | -0.0002 | -0.0029 | 0 | 0.0039 | 0.0006 | -0.0004 | 0.0102 | -0.0052 | -0.0122 | -360.1773 | 17.4274 | -360.4912 | 17.7026 | -360.8481 | 18.1153 | -360.8974 | 17.5588 | -352.6598 | 18.7292 | -352.6998 | 16.7971
12:11 | 3057 | 34.1235 | 199.1351 | 445.1197 | 450.6109 | -18.0629 | -44.3682 | 8.64 | 5.4274 | -0.7103 | -2.1411 | 1.0959 | -2.2556 | 8.3001 | 2.0738 | 0.6038 | 0.643 | 0.9534 | 0.7241 | -130.7269 | -4.0946 | 3.8757 | 0.638 | -5.1106 | -3.4661 | 2.8587 |  | 1.0873 | -1.1731 | 4.0134 | 3.3666 | 3.3517 | 1.0482 | 10.7382 | 14.229 | 14.7912 | 11.0392 | 0 | -0.0031 | 0.0005 | 0.0035 | 0.0008 | -0.0005 | 0.0155 | 0.0007 | -0.0136 | -360.1558 | 17.3946 | -360.4296 | 17.6841 | -360.802 | 18.1029 | -360.885 | 17.5506 | -352.6537 | 18.7066 | -352.6721 | 16.8094
12:11 | 3058 | 34.1268 | 199.1805 | 445.2958 | 450.7365 | -18.0949 | -44.3322 | 8.6222 | 5.4493 | -0.7119 | -2.1008 | 1.0863 | -2.3461 | 8.2289 | 1.9939 | 0.6045 | 0.6419 | 0.9566 | 0.7241 | -130.6308 | -4.0635 | 3.8761 | 0.6476 | -5.0184 | -3.4875 | 2.8129 |  | 1.1488 | -1.2617 | 4.0133 | 3.3685 | 3.3505 | 1.0474 | 10.7372 | 14.2044 | 14.7646 | 11.0389 | 0.0001 | -0.0031 | 0.0005 | 0.0033 | 0.0007 | -0.0011 | 0.0163 | -0.0092 | -0.0185 | -360.1711 | 17.4192 | -360.4573 | 17.6902 | -360.8204 | 18.1029 | -360.8697 | 17.5445 | -352.6537 | 18.7066 | -352.6967 | 16.8012
12:11 | 3059 | 34.2304 | 199.3216 | 445.2634 | 450.7234 | -18.0308 | -44.3723 | 8.7025 | 5.4997 | -0.6944 | -2.0147 | 1.1406 | -2.1904 | 8.3382 | 2.0751 | 0.6057 | 0.6458 | 0.9551 | 0.7255 | -130.6416 | -4.1326 | 3.8108 | 0.6159 | -4.9516 | -3.5292 | 2.8772 |  | 1.116 | -1.1329 | 4.0119 | 3.3676 | 3.3488 | 1.0467 | 10.7197 | 14.2278 | 14.7667 | 11.0266 | -0.0004 | -0.0031 | 0.0008 | 0.0036 | 0.0007 | -0.0002 | 0.0055 | 0.0027 | -0.0195 | -360.165 | 17.3905 | -360.4512 | 17.7026 | -360.7989 | 18.1071 | -360.8697 | 17.5527 | -352.6506 | 18.7087 | -352.669 | 16.8135
12:11 | 3060 | 34.2486 | 199.3563 | 445.3154 | 450.6616 | -17.9942 | -44.4095 | 8.6923 | 5.4406 | -0.6305 | -1.7079 | 1.1684 | -2.2199 | 8.4193 | 2.022 | 0.6049 | 0.6424 | 0.9546 | 0.7259 | -130.7244 | -4.1443 | 3.7877 | 0.67 | -4.8945 | -3.537 | 2.9098 |  | 1.1387 | -1.138 | 4.0137 | 3.3667 | 3.3489 | 1.0471 | 10.7208 | 14.2465 | 14.7981 | 11.0388 | -0.0001 | -0.0025 | 0.0014 | 0.0043 | 0.0006 | -0.0005 | 0.0117 | -0.0074 | 0.0114 | -360.205 | 17.4151 | -360.4696 | 17.68 | -360.7866 | 18.1029 | -360.8974 | 17.5547 | -352.6506 | 18.7128 | -352.6598 | 16.7971
12:11 | 3061 | 34.1915 | 199.2441 | 445.2755 | 450.6571 | -17.9855 | -44.286 | 8.678 | 5.4445 | -0.6705 | -2.0237 | 1.1423 | -2.167 | 8.3702 | 2.0694 | 0.6059 | 0.6426 | 0.9564 | 0.7247 | -130.7168 | -4.2427 | 3.8299 | 0.7535 | -4.9333 | -3.5612 | 2.879 |  | 1.1751 | -1.2 | 4.0132 | 3.3655 | 3.3479 | 1.0472 | 10.7393 | 14.265 | 14.7879 | 11.0746 | -0.0002 | -0.0033 | 0.0008 | 0.0037 | 0.0005 | -0.0002 | -0.0033 | -0.0095 | -0.0187 | -360.1958 | 17.4233 | -360.5035 | 17.7128 | -360.8358 | 18.1009 | -360.8758 | 17.5588 | -352.6783 | 18.7251 | -352.7367 | 16.8258
12:11 | 3062 | 34.1861 | 199.2358 | 445.3067 | 450.6321 | -17.9776 | -44.2498 | 8.6401 | 5.3977 | -0.7499 | -1.9941 | 1.1507 | -2.1235 | 8.4006 | 2.0978 | 0.6057 | 0.6452 | 0.9585 | 0.7262 | -130.7294 | -4.194 | 3.822 | 0.9083 | -4.9378 | -3.5624 | 2.9095 |  | 1.1315 | -1.2115 | 4.0142 | 3.3711 | 3.3504 | 1.048 | 10.7243 | 14.2558 | 14.808 | 11.0594 | 0.0001 | -0.0032 | 0.001 | 0.0042 | 0.0009 | -0.0006 | 0.0104 | -0.0042 | -0.0038 | -360.1158 | 17.411 | -360.4819 | 17.6902 | -360.8143 | 18.0845 | -360.8389 | 17.5342 | -352.6075 | 18.7107 | -352.6937 | 16.8094
12:11 | 3063 | 34.1408 | 199.1551 | 445.2245 | 450.6626 | -18.0335 | -44.3144 | 8.6769 | 5.4272 | -0.6981 | -2.062 | 1.142 | -2.2079 | 8.3836 | 2.0178 | 0.6053 | 0.6455 | 0.9577 | 0.7251 | -130.7341 | -4.0554 | 3.7597 | 0.8203 | -4.9313 | -3.5732 | 2.8737 |  | 1.1283 | -1.2335 | 4.0141 | 3.3678 | 3.3498 | 1.0472 | 10.7509 | 14.2594 | 14.8295 | 11.08 | -0.0003 | -0.0029 | 0.0007 | 0.0035 | 0.0005 | -0.0002 | 0.0207 | -0.0008 | 0.0051 | -360.2296 | 17.409 | -360.4512 | 17.7128 | -360.842 | 18.1276 | -360.8789 | 17.5629 | -352.669 | 18.7169 | -352.6721 | 16.8053
12:11 | 3064 | 34.1555 | 199.2554 | 445.3643 | 450.68 | -17.9712 | -44.1673 | 8.7458 | 5.4303 | -0.6695 | -1.9507 | 1.1979 | -2.1887 | 8.3821 | 1.9864 | 0.6053 | 0.6455 | 0.956 | 0.7239 | -130.7023 | -4.1039 | 3.7273 | 0.8503 | -4.8829 | -3.5066 | 2.9363 |  | 1.251 | -1.1618 | 4.0131 | 3.3693 | 3.3465 | 1.047 | 10.7452 | 14.2533 | 14.81 | 11.0692 | -0.0003 | -0.0023 | 0.0003 | 0.0036 | 0.0011 | -0.0007 | 0.0078 | -0.0165 | -0.0056 | -360.1619 | 17.3925 | -360.4235 | 17.6697 | -360.7712 | 18.1009 | -360.8974 | 17.5753 | -352.6875 | 18.7025 | -352.6475 | 16.7909
12:11 | 3065 | 34.1224 | 199.2751 | 445.3544 | 450.6545 | -18.0023 | -44.1836 | 8.711 | 5.4534 | -0.6659 | -2.0114 | 1.1694 | -2.164 | 8.4307 | 2.0104 | 0.6042 | 0.648 | 0.9592 | 0.723 | -130.6621 | -4.1012 | 3.866 | 0.8254 | -4.9699 | -3.4913 | 2.8891 |  | 1.2366 | -1.0521 | 4.0127 | 3.3673 | 3.3498 | 1.048 | 10.721 | 14.2171 | 14.7428 | 11.04 | -0.0005 | -0.0034 | 0.0004 | 0.0037 | 0.0005 | -0.0002 | -0.0004 | -0.0083 | -0.015 | -360.2235 | 17.4356 | -360.4727 | 17.6841 | -360.7897 | 18.0927 | -360.8512 | 17.5712 | -352.6998 | 18.7333 | -352.6906 | 16.7889
12:11 | 3066 | 34.1547 | 199.2233 | 445.2687 | 450.6293 | -17.817 | -44.0555 | 8.9056 | 5.4833 | -0.615 | -2.0264 | 1.1103 | -2.1217 | 8.4764 | 2.1387 | 0.6039 | 0.6436 | 0.9552 | 0.7249 | -130.6702 | -4.126 | 3.7253 | 0.7791 | -4.9347 | -3.4578 | 2.9393 |  | 1.2477 | -1.0843 | 4.0137 | 3.367 | 3.3485 | 1.0476 | 10.7117 | 14.2369 | 14.7687 | 11.0594 | 0.0001 | -0.0031 | 0 | 0.0034 | 0.0008 | -0.0009 | -0.0078 | -0.0112 | 0.0046 | -360.1465 | 17.411 | -360.4973 | 17.7169 | -360.8727 | 18.1029 | -360.8543 | 17.5547 | -352.6906 | 18.7189 | -352.709 | 16.8238
12:11 | 3067 | 34.2193 | 199.2184 | 445.2454 | 450.5735 | -17.8322 | -44.1447 | 8.8927 | 5.3962 | -0.602 | -2.0246 | 1.1746 | -2.1731 | 8.4159 | 2.1906 | 0.6057 | 0.6426 | 0.9584 | 0.7246 | -130.6425 | -4.1062 | 3.7993 | 0.6341 | -4.8581 | -3.4488 | 2.9659 |  | 1.2475 | -1.0479 | 4.0145 | 3.3636 | 3.3498 | 1.0475 | 10.7313 | 14.222 | 14.8015 | 11.0381 | 0.0002 | -0.0028 | 0.0007 | 0.0035 | 0.0006 | -0.0005 | 0.0095 | -0.01 | -0.0115 | -360.1158 | 17.3761 | -360.4389 | 17.6902 | -360.8204 | 18.1194 | -360.882 | 17.5424 | -352.6444 | 18.6737 | -352.626 | 16.7991
12:11 | 3068 | 34.2982 | 199.24 | 445.3492 | 450.62 | -17.7902 | -44.1657 | 8.8793 | 5.4438 | -0.506 | -2.0731 | 1.1702 | -2.1425 | 8.3314 | 2.1197 | 0.6045 | 0.6437 | 0.9554 | 0.7265 | -130.6387 | -4.0225 | 3.647 | 0.7767 | -4.8402 | -3.4291 | 2.9937 |  | 1.2183 | -1.117 | 4.0133 | 3.3671 | 3.3467 | 1.0477 | 10.7498 | 14.2465 | 14.8212 | 11.0504 | -0.0003 | -0.0024 | 0.0013 | 0.0045 | 0.0007 | -0.0009 | 0.0166 | -0.0112 | -0.0078 | -360.2296 | 17.4028 | -360.4573 | 17.6923 | -360.8389 | 18.1276 | -360.9466 | 17.5753 | -352.6813 | 18.7066 | -352.6752 | 16.8053
12:11 | 3069 | 34.2414 | 199.212 | 445.3562 | 450.6497 | -17.7456 | -44.1977 | 8.8723 | 5.4302 | -0.5383 | -1.92 | 1.167 | -2.0847 | 8.3754 | 2.1403 | 0.6057 | 0.6476 | 0.9576 | 0.7259 | -130.7291 | -4.0268 | 3.7905 | 0.7344 | -4.9011 | -3.4575 | 3.0009 |  | 1.1672 | -1.1827 | 4.0128 | 3.3718 | 3.3517 | 1.0477 | 10.752 | 14.2549 | 14.8261 | 11.0922 | 0.0002 | -0.0024 | 0.0015 | 0.0042 | 0.0012 | -0.0001 | 0.0171 | -0.0026 | -0.0052 | -360.2019 | 17.4007 | -360.4727 | 17.682 | -360.7897 | 18.0886 | -360.842 | 17.5486 | -352.6629 | 18.7004 | -352.6475 | 16.7909
12:11 | 3070 | 34.2703 | 199.2939 | 445.3564 | 450.6353 | -17.7489 | -44.269 | 8.8503 | 5.4949 | -0.5268 | -1.9046 | 1.1106 | -2.0697 | 8.4728 | 2.1296 | 0.6059 | 0.6434 | 0.9553 | 0.7244 | -130.7301 | -3.97 | 3.7169 | 0.69 | -4.9515 | -3.4159 | 2.9461 |  | 1.2197 | -1.0919 | 4.013 | 3.3679 | 3.3438 | 1.0489 | 10.7705 | 14.2676 | 14.8322 | 11.0648 | 0.0003 | -0.0029 | 0.0007 | 0.0039 | 0.0008 | -0.0003 | 0.0145 | -0.0007 | -0.0056 | -360.1588 | 17.4274 | -360.5435 | 17.7354 | -360.8912 | 18.0968 | -360.8574 | 17.5404 | -352.6537 | 18.7312 | -352.7367 | 16.8381
12:11 | 3071 | 34.2185 | 199.1702 | 445.335 | 450.5818 | -17.86 | -44.3101 | 8.7888 | 5.5135 | -0.5642 | -1.9684 | 1.0568 | -2.0487 | 8.541 | 2.246 | 0.6059 | 0.6425 | 0.9563 | 0.7253 | -130.7671 | -4.0364 | 3.7088 | 0.6694 | -4.8772 | -3.4604 | 2.9404 |  | 1.1541 | -1.0332 | 4.0129 | 3.3681 | 3.3481 | 1.048 | 10.7543 | 14.2573 | 14.8173 | 11.0771 | 0.0004 | -0.0028 | 0.0007 | 0.0036 | 0.0009 | -0.0008 | -0.002 | 0.0043 | -0.0091 | -360.0942 | 17.4069 | -360.4912 | 17.7067 | -360.8266 | 18.1029 | -360.8697 | 17.5301 | -352.629 | 18.6963 | -352.6813 | 16.8279
12:11 | 3072 | 34.0667 | 199.1555 | 445.3534 | 450.6751 | -17.8817 | -44.2186 | 8.7376 | 5.5141 | -0.5162 | -1.9698 | 1.0586 | -2.1215 | 8.3809 | 2.2101 | 0.6046 | 0.6405 | 0.9528 | 0.7237 | -130.7819 | -4.0674 | 3.6834 | 0.6097 | -4.8774 | -3.4229 | 2.919 |  | 1.1139 | -1.0895 | 4.0133 | 3.3696 | 3.3516 | 1.0476 | 10.7555 | 14.2582 | 14.8165 | 11.0616 | -0.0002 | -0.0028 | 0.0002 | 0.0036 | 0.0007 | 0 | 0.0113 | -0.0078 | -0.0174 | -360.1773 | 17.3987 | -360.4235 | 17.6902 | -360.8112 | 18.1091 | -360.922 | 17.5773 | -352.666 | 18.6881 | -352.6383 | 16.795
12:11 | 3073 | 34.0876 | 199.2297 | 445.2529 | 450.7389 | -17.9028 | -44.3108 | 8.7373 | 5.5609 | -0.4234 | -1.8148 | 1.0931 | -2.169 | 8.4778 | 2.1577 | 0.6042 | 0.6407 | 0.9553 | 0.7242 | -130.7554 | -4.0587 | 3.7392 | 0.6489 | -4.8236 | -3.4632 | 2.8982 |  | 1.1618 | -1.0736 | 4.0134 | 3.3664 | 3.3484 | 1.0464 | 10.7072 | 14.2204 | 14.8085 | 11.0093 | -0.0003 | -0.003 | 0.0004 | 0.0038 | 0.0002 | -0.0012 | 0.009 | 0.0021 | -0.0173 | -360.2265 | 17.4295 | -360.4758 | 17.6902 | -360.7773 | 18.0906 | -360.8727 | 17.5732 | -352.7367 | 18.7312 | -352.7121 | 16.8115
12:11 | 3074 | 34.1626 | 199.216 | 445.3875 | 450.7408 | -17.8115 | -44.1936 | 8.807 | 5.5268 | -0.4804 | -1.8575 | 1.2107 | -2.1746 | 8.4223 | 2.2282 | 0.6057 | 0.6404 | 0.9588 | 0.7236 | -130.7415 | -4.0432 | 3.7449 | 0.578 | -4.7289 | -3.4579 | 2.8456 |  | 1.1638 | -1.064 | 4.0134 | 3.3689 | 3.3504 | 1.0474 | 10.7164 | 14.201 | 14.7558 | 11.0295 | 0.0004 | -0.0027 | 0.0009 | 0.0042 | 0.0002 | -0.0004 | 0.0094 | -0.0045 | -0.019 | -360.2142 | 17.4151 | -360.4635 | 17.6902 | -360.8081 | 18.0824 | -360.845 | 17.565 | -352.6783 | 18.7066 | -352.6629 | 16.8115
12:11 | 3075 | 34.2296 | 199.32 | 445.4643 | 450.8496 | -17.7845 | -44.108 | 8.8247 | 5.6399 | -0.4518 | -1.7298 | 1.2773 | -2.1832 | 8.4375 | 2.1315 | 0.6043 | 0.6433 | 0.9583 | 0.7234 | -130.7083 | -4.0503 | 3.7105 | 0.5265 | -4.6972 | -3.4211 | 2.8523 |  | 1.2232 | -1.1462 | 4.0147 | 3.365 | 3.3478 | 1.0481 | 10.7094 | 14.2345 | 14.7544 | 11.04 | 0.0002 | -0.0029 | 0.0008 | 0.0037 | 0.0011 | -0.0006 | 0.0059 | 0.0033 | -0.0124 | -360.1496 | 17.4048 | -360.4973 | 17.7128 | -360.8481 | 18.1173 | -360.9127 | 17.5527 | -352.6567 | 18.7045 | -352.7213 | 16.832
12:11 | 3076 | 34.1991 | 199.279 | 445.3934 | 450.7884 | -17.8242 | -44.1709 | 8.7887 | 5.417 | -0.5607 | -1.8218 | 1.1889 | -2.1129 | 8.498 | 2.202 | 0.6037 | 0.6454 | 0.9565 | 0.7236 | -130.7097 | -4.0138 | 3.7553 | 0.4551 | -4.7539 | -3.384 | 2.8809 |  | 1.105 | -1.1746 | 4.0147 | 3.3671 | 3.3519 | 1.0477 | 10.728 | 14.2124 | 14.7547 | 11.0183 | 0 | -0.0029 | 0.0015 | 0.0039 | 0.0005 | -0.0005 | 0.0122 | -0.0023 | -0.0155 | -360.1281 | 17.374 | -360.4266 | 17.6779 | -360.7804 | 18.1173 | -360.8943 | 17.5547 | -352.6198 | 18.6779 | -352.629 | 16.793
12:11 | 3077 | 34.1497 | 199.2353 | 445.3478 | 450.7254 | -17.7809 | -44.1315 | 8.7427 | 5.4257 | -0.4902 | -1.7291 | 1.1637 | -2.1166 | 8.5064 | 2.2159 | 0.6049 | 0.6416 | 0.9591 | 0.7236 | -130.761 | -4.1065 | 3.6969 | 0.4629 | -4.8235 | -3.4699 | 2.8762 |  | 1.1677 | -1.0222 | 4.0133 | 3.3671 | 3.3482 | 1.0476 | 10.7658 | 14.2573 | 14.8115 | 11.0713 | 0 | -0.0025 | 0.0009 | 0.0037 | 0.0011 | -0.0007 | 0.0161 | -0.0032 | -0.0211 | -360.2235 | 17.4254 | -360.4758 | 17.7067 | -360.8297 | 18.1112 | -360.9066 | 17.5732 | -352.6875 | 18.721 | -352.6967 | 16.8238
12:11 | 3078 | 34.3255 | 199.1975 | 445.3351 | 450.7408 | -17.8211 | -44.1202 | 8.8286 | 5.5143 | -0.4666 | -1.8293 | 1.1622 | -2.0838 | 8.4633 | 2.183 | 0.6049 | 0.6419 | 0.9568 | 0.7255 | -130.6859 | -4.1734 | 3.8503 | 0.4222 | -4.8184 | -3.3827 | 2.9754 |  | 1.2057 | -1.1353 | 4.013 | 3.3654 | 3.3459 | 1.0473 | 10.7556 | 14.2174 | 14.826 | 11.0623 | 0 | -0.0028 | 0.0001 | 0.0034 | 0.0007 | -0.0004 | 0.0185 | -0.0129 | 0.0163 | -360.1711 | 17.3987 | -360.4881 | 17.7067 | -360.802 | 18.0845 | -360.885 | 17.5506 | -352.6475 | 18.7025 | -352.709 | 16.8258
12:11 | 3079 | 34.2858 | 199.2225 | 445.2643 | 450.8063 | -17.748 | -44.1061 | 8.8386 | 5.479 | -0.5314 | -1.7516 | 1.1599 | -2.1421 | 8.4864 | 2.2042 | 0.6057 | 0.6437 | 0.9598 | 0.7264 | -130.6516 | -4.1739 | 3.7841 | 0.3614 | -4.8706 | -3.476 | 2.8992 |  | 1.1725 | -1.0556 | 4.014 | 3.367 | 3.3491 | 1.0483 | 10.7625 | 14.265 | 14.8168 | 11.0688 | 0.0001 | -0.0031 | 0.0006 | 0.0037 | 0.0006 | -0.0004 | 0.0124 | -0.0111 | -0.0054 | -360.1865 | 17.409 | -360.4635 | 17.6985 | -360.8327 | 18.1091 | -360.8727 | 17.5445 | -352.6321 | 18.7087 | -352.666 | 16.8115
12:11 | 3080 | 34.335 | 199.1781 | 445.3819 | 450.8027 | -17.8426 | -44.0386 | 8.789 | 5.4604 | -0.4565 | -1.7665 | 1.2047 | -2.0697 | 8.5165 | 2.3259 | 0.6041 | 0.6434 | 0.9584 | 0.7244 | -130.6934 | -4.1383 | 3.89 | 0.4536 | -4.8473 | -3.435 | 2.8606 |  | 1.2326 | -1.0314 | 4.0145 | 3.3669 | 3.3494 | 1.0476 | 10.7717 | 14.2455 | 14.8152 | 11.0836 | -0.0005 | -0.003 | -0.0001 | 0.0037 | 0.0009 | -0.0005 | 0.0007 | -0.0091 | -0.0219 | -360.1896 | 17.4213 | -360.4942 | 17.7231 | -360.8574 | 18.0968 | -360.8789 | 17.5712 | -352.6752 | 18.721 | -352.7213 | 16.8279
12:11 | 3081 | 34.2667 | 199.3158 | 445.4227 | 450.8001 | -17.7828 | -44.0712 | 8.8489 | 5.4525 | -0.4033 | -1.8504 | 1.2628 | -2.132 | 8.4313 | 2.2847 | 0.6035 | 0.6415 | 0.955 | 0.7238 | -130.6555 | -4.177 | 3.8743 | 0.3555 | -4.8108 | -3.3942 | 2.9434 |  | 1.1952 | -1.0432 | 4.014 | 3.3704 | 3.3517 | 1.0466 | 10.7487 | 14.2103 | 14.7888 | 11.0269 | -0.0003 | -0.0023 | 0.0004 | 0.0037 | 0 | -0.0006 | 0.0078 | -0.0008 | -0.0002 | -360.1373 | 17.3925 | -360.445 | 17.682 | -360.7989 | 18.0947 | -360.842 | 17.5363 | -352.6229 | 18.6922 | -352.6475 | 16.8032
12:11 | 3082 | 34.2295 | 199.2524 | 445.4254 | 450.7774 | -17.7525 | -44.0796 | 8.7898 | 5.4231 | -0.4908 | -1.8837 | 1.2409 | -2.1701 | 8.4374 | 2.2854 | 0.6036 | 0.6431 | 0.9581 | 0.7238 | -130.7662 | -4.1953 | 3.8146 | 0.4745 | -4.764 | -3.3356 | 2.9458 |  | 1.2648 | -1.1038 | 4.0134 | 3.3684 | 3.3527 | 1.0469 | 10.7371 | 14.222 | 14.8015 | 11.0555 | -0.0001 | -0.0031 | 0.0009 | 0.0039 | 0.0013 | -0.0006 | 0.0149 | 0.0085 | -0.0081 | -360.1988 | 17.4131 | -360.4819 | 17.7169 | -360.845 | 18.105 | -360.9004 | 17.5732 | -352.6537 | 18.6963 | -352.669 | 16.8135
12:11 | 3083 | 34.277 | 199.3542 | 445.4685 | 450.853 | -17.7818 | -44.1848 | 8.8811 | 5.4115 | -0.4953 | -1.8593 | 1.2068 | -2.1254 | 8.4685 | 2.2966 | 0.6053 | 0.6437 | 0.9562 | 0.7231 | -130.6642 | -4.0412 | 3.8242 | 0.5202 | -4.956 | -3.4455 | 2.88 |  | 1.1645 | -1.0638 | 4.0118 | 3.3665 | 3.3501 | 1.0472 | 10.7302 | 14.2324 | 14.8117 | 11.0313 | 0.0001 | -0.0032 | 0.0009 | 0.0039 | 0.0007 | -0.0004 | 0.023 | -0.0089 | -0.0239 | -360.1896 | 17.4356 | -360.5189 | 17.7108 | -360.8235 | 18.105 | -360.9281 | 17.5794 | -352.6813 | 18.723 | -352.709 | 16.8176
12:11 | 3084 | 34.3272 | 199.3667 | 445.4406 | 450.735 | -17.7829 | -44.0572 | 8.9528 | 5.348 | -0.591 | -1.8857 | 1.1695 | -2.0456 | 8.519 | 2.2337 | 0.6047 | 0.6448 | 0.957 | 0.7235 | -130.6739 | -4.1035 | 3.7812 | 0.4817 | -4.9998 | -3.443 | 2.9145 |  | 1.2251 | -1.0136 | 4.012 | 3.3696 | 3.3504 | 1.0473 | 10.7256 | 14.2275 | 14.7704 | 11.01 | -0.0002 | -0.0031 | 0.0013 | 0.0045 | 0.001 | -0.0008 | 0.0226 | -0.0071 | -0.0098 | -360.1742 | 17.4069 | -360.4419 | 17.6923 | -360.8174 | 18.066 | -360.8327 | 17.5506 | -352.6813 | 18.7128 | -352.6629 | 16.8012
12:11 | 3085 | 34.379 | 199.3342 | 445.5368 | 450.8079 | -17.7539 | -44.1264 | 8.9145 | 5.3284 | -0.4984 | -1.9426 | 1.0866 | -2.0821 | 8.5079 | 2.338 | 0.6046 | 0.6458 | 0.957 | 0.7231 | -130.641 | -4.1051 | 3.8 | 0.5344 | -4.9277 | -3.4683 | 2.8929 |  | 1.185 | -1.1086 | 4.0121 | 3.3648 | 3.3465 | 1.0469 | 10.715 | 14.2351 | 14.7876 | 11.0673 | -0.0004 | -0.0028 | 0.001 | 0.004 | 0.001 | 0.0001 | 0.0162 | -0.0003 | -0.0092 | -360.1681 | 17.4172 | -360.485 | 17.7375 | -360.8666 | 18.0947 | -360.885 | 17.5568 | -352.6444 | 18.7189 | -352.7029 | 16.8197
12:11 | 3086 | 34.3114 | 199.2429 | 445.3 | 450.8521 | -17.7472 | -44.0754 | 8.8458 | 5.3855 | -0.4446 | -1.8962 | 1.1545 | -2.0886 | 8.5255 | 2.342 | 0.6055 | 0.6454 | 0.9547 | 0.7249 | -130.6524 | -4.0606 | 3.8574 | 0.5335 | -4.9218 | -3.5076 | 2.9219 |  | 1.1892 | -1.1607 | 4.0123 | 3.3674 | 3.3471 | 1.0475 | 10.767 | 14.2641 | 14.8234 | 11.0496 | -0.0001 | -0.0026 | 0.0007 | 0.0036 | 0.0013 | -0.0005 | -0.0009 | -0.0154 | -0.0268 | -360.1527 | 17.3864 | -360.4419 | 17.6923 | -360.7989 | 18.1214 | -360.8943 | 17.5527 | -352.6598 | 18.6902 | -352.6475 | 16.8135
12:11 | 3087 | 34.32 | 199.2803 | 445.3973 | 450.7878 | -17.7883 | -44.0735 | 8.8255 | 5.3991 | -0.4608 | -1.9371 | 1.1271 | -2.1567 | 8.4842 | 2.2762 | 0.6041 | 0.6454 | 0.9584 | 0.7243 | -130.5697 | -3.9995 | 3.8947 | 0.5341 | -4.9113 | -3.4246 | 2.8781 |  | 1.2041 | -1.0799 | 4.0127 | 3.3662 | 3.3497 | 1.0471 | 10.7325 | 14.2404 | 14.8018 | 11.0396 | -0.0003 | -0.0033 | 0.0007 | 0.004 | 0.0003 | 0 | 0.018 | -0.0117 | -0.016 | -360.205 | 17.3966 | -360.4081 | 17.6779 | -360.8081 | 18.1009 | -360.9066 | 17.5671 | -352.6721 | 18.6922 | -352.6106 | 16.7827
12:11 | 3088 | 34.4369 | 199.3067 | 445.4756 | 450.9174 | -17.8346 | -44.0646 | 8.8475 | 5.3959 | -0.4558 | -2.0975 | 1.1717 | -2.0957 | 8.4963 | 2.2692 | 0.6046 | 0.6448 | 0.9547 | 0.7241 | -130.6271 | -4.0857 | 3.8616 | 0.5718 | -4.899 | -3.4115 | 2.9377 |  | 1.2179 | -1.1362 | 4.0126 | 3.3655 | 3.3517 | 1.0475 | 10.73 | 14.2504 | 14.8506 | 11.076 | 0.0004 | -0.0027 | 0.001 | 0.0043 | 0.001 | -0.0007 | 0.0212 | -0.0101 | 0.007 | -360.2358 | 17.4254 | -360.5004 | 17.7128 | -360.7958 | 18.1029 | -360.9004 | 17.5732 | -352.6906 | 18.7292 | -352.7121 | 16.8176
12:11 | 3089 | 34.3116 | 199.3582 | 445.4802 | 450.8636 | -17.7731 | -44.0322 | 8.8405 | 5.3983 | -0.4846 | -1.9752 | 1.1564 | -2.1041 | 8.4775 | 2.3275 | 0.6045 | 0.6452 | 0.956 | 0.7245 | -130.6166 | -4.0831 | 3.8601 | 0.5258 | -5.0001 | -3.5123 | 2.8696 |  | 1.2638 | -1.0599 | 4.0136 | 3.3671 | 3.3486 | 1.0476 | 10.7499 | 14.2462 | 14.8365 | 11.0973 | -0.0007 | -0.0029 | 0.0004 | 0.0036 | 0.0007 | -0.0003 | 0.0117 | -0.0029 | -0.0036 | -360.125 | 17.4048 | -360.4789 | 17.7149 | -360.842 | 18.0701 | -360.8297 | 17.528 | -352.629 | 18.7066 | -352.6906 | 16.8217
12:11 | 3090 | 34.4096 | 199.3477 | 445.5058 | 450.778 | -17.7001 | -44.0296 | 8.8444 | 5.3995 | -0.555 | -1.8725 | 1.1646 | -2.0952 | 8.4897 | 2.3544 | 0.6036 | 0.6474 | 0.9553 | 0.724 | -130.5475 | -4.0006 | 3.9397 | 0.6296 | -4.9582 | -3.5333 | 2.9287 |  | 1.3158 | -1.0803 | 4.0125 | 3.3683 | 3.3496 | 1.0478 | 10.7036 | 14.2231 | 14.7555 | 11.0454 | -0.0006 | -0.003 | 0.0008 | 0.0037 | 0.0008 | -0.0005 | 0.0105 | -0.0095 | -0.0193 | -360.1711 | 17.4069 | -360.4635 | 17.7395 | -360.9004 | 18.1337 | -360.9035 | 17.5506 | -352.6383 | 18.6984 | -352.7306 | 16.8361
12:11 | 3091 | 34.3727 | 199.3529 | 445.5477 | 450.8521 | -17.7438 | -43.9093 | 8.9118 | 5.4571 | -0.4014 | -1.8354 | 1.0944 | -1.9976 | 8.4736 | 2.3348 | 0.6048 | 0.6495 | 0.9544 | 0.7247 | -130.5252 | -4.0702 | 3.9413 | 0.8322 | -4.9686 | -3.588 | 2.9238 |  | 1.274 | -1.0361 | 4.012 | 3.3664 | 3.3493 | 1.0475 | 10.7475 | 14.2383 | 14.8069 | 11.0598 | 0.0004 | -0.003 | 0.0008 | 0.0039 | 0.001 | -0.0008 | 0.0123 | -0.0074 | 0.0031 | -360.1588 | 17.3987 | -360.4358 | 17.6923 | -360.8327 | 18.1029 | -360.8912 | 17.5547 | -352.6629 | 18.6943 | -352.629 | 16.8115
12:11 | 3092 | 34.4362 | 199.3447 | 445.5003 | 450.8689 | -17.711 | -44.0036 | 8.9786 | 5.5493 | -0.3854 | -1.9122 | 1.1025 | -2.1187 | 8.4161 | 2.3127 | 0.6044 | 0.6474 | 0.9542 | 0.7242 | -130.4778 | -3.9599 | 3.967 | 0.8581 | -4.9595 | -3.4667 | 2.887 |  | 1.3252 | -1.1257 | 4.0129 | 3.3651 | 3.3485 | 1.0479 | 10.7579 | 14.2487 | 14.8229 | 11.0414 | 0 | -0.0031 | 0.001 | 0.0037 | 0.0005 | -0.0001 | 0.0152 | -0.0127 | -0.0165 | -360.245 | 17.4295 | -360.4727 | 17.6944 | -360.7897 | 18.0845 | -360.8758 | 17.5671 | -352.6998 | 18.721 | -352.6752 | 16.7868
12:11 | 3093 | 34.4478 | 199.3126 | 445.5848 | 450.869 | -17.8137 | -44.0044 | 8.9807 | 5.5167 | -0.4577 | -1.7693 | 1.0689 | -2.1099 | 8.4684 | 2.3974 | 0.605 | 0.6475 | 0.9546 | 0.7256 | -130.5563 | -4.0091 | 3.9564 | 0.9328 | -4.8748 | -3.4227 | 2.926 |  | 1.2826 | -1.044 | 4.0131 | 3.3672 | 3.3528 | 1.0481 | 10.7347 | 14.2431 | 14.7893 | 11.041 | -0.0001 | -0.0026 | 0.0008 | 0.0035 | 0.0007 | -0.0011 | 0.0123 | 0.0017 | -0.0123 | -360.1896 | 17.4356 | -360.5373 | 17.7313 | -360.8297 | 18.0824 | -360.8481 | 17.5609 | -352.6906 | 18.7497 | -352.7275 | 16.8279
12:11 | 3094 | 34.5664 | 199.3409 | 445.5731 | 450.8122 | -17.6737 | -43.9757 | 8.8731 | 5.5055 | -0.383 | -1.913 | 0.9499 | -2.069 | 8.4495 | 2.312 | 0.6036 | 0.6449 | 0.9565 | 0.7274 | -130.586 | -4.0283 | 3.8431 | 0.8988 | -4.9276 | -3.4135 | 2.9371 |  | 1.2422 | -1.1456 | 4.0143 | 3.3656 | 3.3472 | 1.0481 | 10.7232 | 14.2486 | 14.7871 | 11.0475 | -0.0001 | -0.0027 | 0.0004 | 0.0034 | 0.0004 | -0.0005 | 0.0082 | -0.0136 | -0.0132 | -360.1373 | 17.4007 | -360.4727 | 17.7087 | -360.8204 | 18.0865 | -360.8697 | 17.5321 | -352.6229 | 18.6902 | -352.6875 | 16.8197
12:11 | 3095 | 34.4808 | 199.2708 | 445.4367 | 450.7659 | -17.6669 | -44.1425 | 8.9088 | 5.5814 | -0.3641 | -1.8404 | 1.037 | -2.1007 | 8.399 | 2.3238 | 0.6034 | 0.6425 | 0.9542 | 0.727 | -130.5205 | -4.0429 | 3.866 | 0.8787 | -4.8727 | -3.4193 | 2.9783 |  | 1.3589 | -1.0641 | 4.0129 | 3.3673 | 3.3463 | 1.0469 | 10.7462 | 14.2548 | 14.8135 | 11.0637 | 0.0004 | -0.0026 | 0.0007 | 0.004 | 0.0013 | -0.0002 | 0.0021 | -0.0143 | -0.0154 | -360.1742 | 17.409 | -360.4389 | 17.719 | -360.8604 | 18.1235 | -360.9127 | 17.5773 | -352.666 | 18.6902 | -352.6629 | 16.8156
12:11 | 3096 | 34.5253 | 199.3437 | 445.541 | 450.8603 | -17.725 | -44.0367 | 8.8686 | 5.5338 | -0.4227 | -1.9606 | 0.9623 | -2.0835 | 8.4084 | 2.3079 | 0.6033 | 0.6456 | 0.9548 | 0.7258 | -130.5647 | -4.0625 | 3.8284 | 0.748 | -4.9553 | -3.3982 | 2.9837 |  | 1.2858 | -1.1087 | 4.012 | 3.3643 | 3.3498 | 1.0476 | 10.7568 | 14.2302 | 14.7752 | 11.0634 | 0 | -0.0031 | 0.0007 | 0.0038 | 0.0009 | -0.0002 | 0.0095 | -0.0122 | -0.0123 | -360.1927 | 17.4069 | -360.445 | 17.6964 | -360.762 | 18.1009 | -360.9004 | 17.5773 | -352.6844 | 18.7025 | -352.6537 | 16.7889
12:11 | 3097 | 34.5412 | 199.433 | 445.533 | 450.8943 | -17.75 | -44.0924 | 8.819 | 5.6079 | -0.4337 | -1.9172 | 0.8978 | -2.0054 | 8.4578 | 2.3501 | 0.6032 | 0.6447 | 0.9536 | 0.726 | -130.6133 | -4.0498 | 3.8239 | 0.6641 | -4.8817 | -3.398 | 2.9579 |  | 1.3631 | -1.1418 | 4.0145 | 3.3664 | 3.3509 | 1.0474 | 10.7292 | 14.2192 | 14.7782 | 11.0371 | -0.0004 | -0.0027 | 0.0002 | 0.004 | 0.0013 | -0.0002 | 0.0187 | -0.01 | -0.0165 | -360.1558 | 17.4151 | -360.4635 | 17.6923 | -360.7804 | 18.0906 | -360.8666 | 17.5486 | -352.666 | 18.7148 | -352.6783 | 16.8012
12:11 | 3098 | 34.502 | 199.3963 | 445.6116 | 450.9835 | -17.6855 | -44.0054 | 8.985 | 5.654 | -0.5147 | -1.8217 | 0.9697 | -2.0361 | 8.4545 | 2.3844 | 0.605 | 0.6464 | 0.9549 | 0.7253 | -130.5815 | -4.0072 | 3.8219 | 0.5964 | -4.932 | -3.4248 | 2.9499 |  | 1.2403 | -1.147 | 4.0128 | 3.3649 | 3.3512 | 1.0483 | 10.7417 | 14.2326 | 14.8011 | 11.0309 | -0.0001 | -0.0025 | 0.0014 | 0.0046 | 0.0008 | -0.0002 | 0.012 | -0.0091 | -0.002 | -360.1465 | 17.4172 | -360.5189 | 17.7334 | -360.9127 | 18.1132 | -360.8974 | 17.5609 | -352.6444 | 18.7087 | -352.7244 | 16.8402
12:11 | 3099 | 34.5108 | 199.338 | 445.6766 | 450.8445 | -17.7481 | -44.0146 | 8.8787 | 5.4972 | -0.4769 | -1.8433 | 0.9741 | -2.0363 | 8.4943 | 2.5096 | 0.6038 | 0.6431 | 0.9534 | 0.7255 | -130.5337 | -3.9264 | 3.9173 | 0.6535 | -4.8854 | -3.4696 | 2.9742 |  | 1.286 | -1.0784 | 4.0137 | 3.3674 | 3.3492 | 1.0484 | 10.7315 | 14.233 | 14.7683 | 11.0339 | -0.0003 | -0.0031 | 0.0005 | 0.0036 | 0.001 | -0.0007 | 0.0135 | -0.0091 | -0.0042 | -360.1496 | 17.3782 | -360.4389 | 17.6882 | -360.8143 | 18.1029 | -360.8697 | 17.5568 | -352.6167 | 18.6758 | -352.6598 | 16.8197
12:11 | 3100 | 34.4147 | 199.3388 | 445.5796 | 450.8197 | -17.7149 | -44.0006 | 8.939 | 5.5488 | -0.3208 | -1.7897 | 1.0168 | -2.0384 | 8.4691 | 2.4108 | 0.6037 | 0.6476 | 0.9529 | 0.7263 | -130.5598 | -3.9784 | 3.8384 | 0.8122 | -4.9076 | -3.3784 | 2.967 |  | 1.2802 | -1.0488 | 4.012 | 3.3644 | 3.3486 | 1.0487 | 10.7451 | 14.2592 | 14.8284 | 11.0515 | 0.0011 | -0.0023 | 0.001 | 0.0035 | 0.001 | -0.0002 | 0.0197 | -0.012 | 0.0028 | -360.2204 | 17.4356 | -360.4819 | 17.6718 | -360.8204 | 18.0947 | -360.8574 | 17.5609 | -352.6844 | 18.7148 | -352.666 | 16.7991
12:11 | 3101 | 34.5218 | 199.3316 | 445.598 | 450.8602 | -17.6981 | -43.8783 | 8.9764 | 5.5518 | -0.3766 | -1.7786 | 1.0177 | -2.0886 | 8.472 | 2.4835 | 0.6034 | 0.6451 | 0.9534 | 0.7261 | -130.5858 | -3.9892 | 3.7733 | 0.8299 | -4.9431 | -3.3821 | 2.991 |  | 1.2465 | -1.124 | 4.0125 | 3.3682 | 3.35 | 1.0474 | 10.7233 | 14.2194 | 14.7908 | 11.0714 | -0.0001 | -0.003 | 0.0006 | 0.0036 | 0.0002 | -0.0011 | -0.0005 | -0.0048 | -0.0245 | -360.1742 | 17.4254 | -360.5066 | 17.7046 | -360.8389 | 18.1029 | -360.8697 | 17.5712 | -352.6813 | 18.723 | -352.7275 | 16.834
12:11 | 3102 | 34.4503 | 199.3288 | 445.6437 | 450.8906 | -17.7869 | -43.9299 | 8.9094 | 5.4967 | -0.434 | -1.6364 | 1.0088 | -2.0575 | 8.4927 | 2.3938 | 0.6028 | 0.6438 | 0.9545 | 0.7254 | -130.54 | -4.0037 | 3.7901 | 0.8629 | -4.8608 | -3.2996 | 3.0094 |  | 1.2074 | -1.1049 | 4.0132 | 3.363 | 3.347 | 1.0488 | 10.7487 | 14.2741 | 14.8072 | 11.0612 | -0.0002 | -0.0025 | 0.0004 | 0.0034 | 0.0005 | -0.0008 | -0.0033 | -0.0092 | 0.0045 | -360.1219 | 17.409 | -360.445 | 17.6738 | -360.8143 | 18.0968 | -360.8481 | 17.5404 | -352.6444 | 18.7025 | -352.666 | 16.8032
12:11 | 3103 | 34.4528 | 199.3383 | 445.5242 | 450.9207 | -17.693 | -43.9187 | 9.0235 | 5.5505 | -0.3934 | -1.6486 | 1.0561 | -2.0713 | 8.4448 | 2.4393 | 0.6033 | 0.6434 | 0.9524 | 0.7244 | -130.5429 | -4.0218 | 3.833 | 0.9413 | -4.9274 | -3.3039 | 3.0247 |  | 1.1988 | -1.1004 | 4.0138 | 3.3653 | 3.3513 | 1.0481 | 10.7393 | 14.2478 | 14.8005 | 11.0626 | 0.0001 | -0.0027 | 0.0005 | 0.004 | 0.0007 | -0.0002 | 0.0106 | -0.0171 | -0.0057 | -360.1835 | 17.4315 | -360.4881 | 17.6985 | -360.8389 | 18.1071 | -360.9004 | 17.5712 | -352.6567 | 18.7107 | -352.6967 | 16.834
12:11 | 3104 | 34.5042 | 199.343 | 445.4412 | 450.8596 | -17.7121 | -43.9818 | 8.9925 | 5.4967 | -0.4971 | -1.6091 | 1.078 | -2.0721 | 8.5558 | 2.5135 | 0.6041 | 0.6424 | 0.9562 | 0.7258 | -130.6 | -4.083 | 3.8298 | 0.8333 | -4.8849 | -3.3822 | 3.0018 |  | 1.2333 | -1.1147 | 4.0147 | 3.3645 | 3.3491 | 1.0484 | 10.7637 | 14.237 | 14.8219 | 11.0533 | -0.0002 | -0.003 | 0.0005 | 0.004 | 0.0011 | -0.0007 | 0.0098 | -0.0233 | 0.008 | -360.1588 | 17.4007 | -360.4635 | 17.6882 | -360.8143 | 18.0927 | -360.8697 | 17.5588 | -352.6629 | 18.7066 | -352.6813 | 16.8238
12:11 | 3105 | 34.484 | 199.3925 | 445.5406 | 450.8121 | -17.7467 | -44.08 | 9.0137 | 5.426 | -0.4924 | -1.6471 | 0.9912 | -2.0553 | 8.5075 | 2.4531 | 0.6037 | 0.648 | 0.9577 | 0.7264 | -130.6357 | -4.1196 | 3.8147 | 0.7394 | -4.936 | -3.5137 | 3.0248 |  | 1.2443 | -1.0346 | 4.0129 | 3.3645 | 3.3468 | 1.0483 | 10.7278 | 14.2535 | 14.8226 | 11.0688 | 0.0001 | -0.0028 | 0.0006 | 0.004 | 0.0006 | -0.0004 | -0.0008 | 0.0011 | -0.0083 | -360.165 | 17.411 | -360.4542 | 17.6759 | -360.7989 | 18.0968 | -360.882 | 17.5691 | -352.6567 | 18.7045 | -352.6537 | 16.793
12:11 | 3106 | 34.5887 | 199.3463 | 445.7451 | 450.8933 | -17.7968 | -44.1542 | 8.8652 | 5.4113 | -0.5015 | -1.8657 | 1.0415 | -2.0599 | 8.4884 | 2.4678 | 0.6035 | 0.6461 | 0.9569 | 0.7262 | -130.6125 | -4.0194 | 3.8908 | 0.7262 | -4.9782 | -3.4493 | 2.9347 |  | 1.1515 | -1.1965 | 4.0139 | 3.3636 | 3.3479 | 1.0482 | 10.7313 | 14.2683 | 14.842 | 11.0555 | -0.0006 | -0.003 | 0.0007 | 0.0037 | 0.0012 | -0.0006 | 0.0145 | -0.0008 | 0.0043 | -360.2512 | 17.4315 | -360.5096 | 17.6944 | -360.8143 | 18.1029 | -360.8758 | 17.5691 | -352.6906 | 18.7312 | -352.7275 | 16.8156
12:11 | 3107 | 34.5891 | 199.3188 | 445.6812 | 450.847 | -17.8408 | -44.297 | 8.859 | 5.4981 | -0.4757 | -1.7057 | 1.0524 | -2.1149 | 8.5365 | 2.569 | 0.6043 | 0.6471 | 0.953 | 0.7261 | -130.6999 | -4.0944 | 3.82 | 0.8317 | -4.9564 | -3.4153 | 3.0081 |  | 1.2121 | -1.1763 | 4.0135 | 3.3662 | 3.3485 | 1.0487 | 10.7245 | 14.2204 | 14.7969 | 11.0497 | -0.0003 | -0.0031 | 0.0005 | 0.0034 | 0.0004 | -0.0005 | 0.0131 | -0.0186 | -0.0016 | -360.1188 | 17.3966 | -360.4819 | 17.6882 | -360.7835 | 18.0927 | -360.8297 | 17.5363 | -352.6167 | 18.6963 | -352.7029 | 16.8217
12:12 | 3108 | 34.5806 | 199.4021 | 445.6624 | 450.8771 | -17.7989 | -44.2262 | 8.7707 | 5.4787 | -0.5048 | -1.7327 | 1.0902 | -2.0604 | 8.5396 | 2.6298 | 0.6058 | 0.645 | 0.9533 | 0.7261 | -130.6835 | -4.0623 | 3.8601 | 0.7978 | -4.9179 | -3.4023 | 2.9903 |  | 1.2254 | -1.1484 | 4.0138 | 3.3618 | 3.347 | 1.0484 | 10.7429 | 14.2045 | 14.7946 | 11.0385 | -0.0001 | -0.0034 | 0.0007 | 0.0037 | 0.0009 | -0.0005 | 0.0063 | -0.0138 | -0.0081 | -360.1835 | 17.3987 | -360.4419 | 17.6861 | -360.8512 | 18.1276 | -360.9035 | 17.5547 | -352.6567 | 18.6902 | -352.6537 | 16.8135
12:12 | 3109 | 34.5706 | 199.4013 | 445.6254 | 450.9957 | -17.8094 | -44.1666 | 8.8581 | 5.3645 | -0.5013 | -1.8279 | 1.0413 | -2.1449 | 8.4607 | 2.467 | 0.6048 | 0.6425 | 0.9537 | 0.7256 | -130.5939 | -3.8748 | 4.0007 | 0.8052 | -4.9114 | -3.3985 | 2.8583 |  | 1.2707 | -1.1588 | 4.0125 | 3.3641 | 3.3455 | 1.0489 | 10.7083 | 14.2217 | 14.7878 | 11.0678 | -0.0001 | -0.003 | 0.0006 | 0.0034 | 0.0005 | -0.0004 | 0.022 | -0.0021 | 0.0103 | -360.1588 | 17.3987 | -360.4481 | 17.6738 | -360.7743 | 18.1153 | -360.9158 | 17.5794 | -352.7213 | 18.6943 | -352.6998 | 16.8176
12:12 | 3110 | 34.6522 | 199.4183 | 445.7186 | 450.9904 | -17.7088 | -44.1639 | 8.8839 | 5.417 | -0.4338 | -1.8507 | 1.0868 | -2.1016 | 8.4362 | 2.4259 | 0.6057 | 0.6432 | 0.9534 | 0.725 | -130.5583 | -3.8915 | 4.0208 | 0.7737 | -4.9841 | -3.3225 | 2.9084 |  | 1.303 | -1.1131 | 4.0147 | 3.3666 | 3.3485 | 1.0479 | 10.7348 | 14.2312 | 14.7929 | 11.0186 | -0.0009 | -0.0031 | 0.0009 | 0.0039 | 0.0011 | -0.0004 | -0.0004 | -0.0079 | -0.0079 | -360.1435 | 17.4172 | -360.4635 | 17.6697 | -360.7835 | 18.068 | -360.8297 | 17.5445 | -352.6629 | 18.7107 | -352.666 | 16.8032
12:12 | 3111 | 34.6722 | 199.4099 | 445.622 | 451.0121 | -17.7526 | -44.3088 | 8.8709 | 5.4104 | -0.5104 | -1.8124 | 1.0619 | -2.1798 | 8.4778 | 2.3838 | 0.6038 | 0.6465 | 0.9503 | 0.7246 | -130.6694 | -4.03 | 3.9312 | 0.8325 | -4.9375 | -3.4394 | 2.9016 |  | 1.26 | -1.144 | 4.0149 | 3.3664 | 3.3507 | 1.0483 | 10.744 | 14.2754 | 14.8328 | 11.0793 | -0.0003 | -0.0027 | 0.001 | 0.004 | 0.001 | -0.0004 | -0.0011 | -0.0147 | -0.0151 | -360.1404 | 17.4233 | -360.5281 | 17.721 | -360.8758 | 18.1071 | -360.8512 | 17.5383 | -352.6844 | 18.7107 | -352.7121 | 16.8546
12:12 | 3112 | 34.6648 | 199.3623 | 445.6928 | 450.9949 | -17.7866 | -44.2909 | 8.8226 | 5.3941 | -0.4018 | -1.7795 | 1.1355 | -2.1002 | 8.4874 | 2.4237 | 0.6035 | 0.6431 | 0.9528 | 0.7258 | -130.6584 | -3.9452 | 3.9638 | 0.825 | -4.8723 | -3.4232 | 2.9161 |  | 1.2687 | -1.1188 | 4.0145 | 3.3673 | 3.3491 | 1.0487 | 10.7717 | 14.2919 | 14.851 | 11.0774 | 0.0003 | -0.0026 | 0.0009 | 0.0037 | 0.0007 | -0.0002 | 0.0042 | -0.0045 | -0.0295 | -360.1096 | 17.3823 | -360.4327 | 17.68 | -360.8297 | 18.105 | -360.845 | 17.5239 | -352.629 | 18.6779 | -352.669 | 16.8197
12:12 | 3113 | 34.5788 | 199.4273 | 445.6337 | 450.9593 | -17.7565 | -44.2885 | 8.8039 | 5.4759 | -0.3023 | -1.8233 | 1.1492 | -2.1064 | 8.4245 | 2.4881 | 0.6037 | 0.6431 | 0.9514 | 0.7251 | -130.6189 | -3.8752 | 3.9718 | 0.9167 | -4.8479 | -3.4164 | 2.8895 |  | 1.2635 | -1.1428 | 4.0134 | 3.3684 | 3.347 | 1.0467 | 10.7487 | 14.2105 | 14.7783 | 11.0439 | -0.0001 | -0.0031 | 0.0004 | 0.0037 | 0.0007 | -0.0006 | 0.0149 | -0.0138 | -0.004 | -360.2173 | 17.4192 | -360.4727 | 17.6718 | -360.802 | 18.1112 | -360.9435 | 17.5773 | -352.7183 | 18.7128 | -352.6813 | 16.8053
12:12 | 3114 | 34.6862 | 199.5117 | 445.6449 | 450.9778 | -17.7851 | -44.1584 | 8.8518 | 5.4582 | -0.409 | -1.7895 | 1.1244 | -2.1598 | 8.464 | 2.4106 | 0.6035 | 0.6409 | 0.9541 | 0.7258 | -130.6477 | -3.8409 | 3.9721 | 0.9146 | -4.8586 | -3.3888 | 2.9395 |  | 1.2781 | -1.1415 | 4.0134 | 3.3685 | 3.3461 | 1.0483 | 10.7475 | 14.2383 | 14.8011 | 11.0713 | -0.0003 | -0.0026 | 0.0007 | 0.0036 | 0.0004 | -0.0003 | 0.0057 | -0.0076 | 0.0032 | -360.2512 | 17.4377 | -360.4573 | 17.6615 | -360.7835 | 18.0578 | -360.8481 | 17.565 | -352.6906 | 18.7251 | -352.706 | 16.7971
12:12 | 3115 | 34.6869 | 199.4617 | 445.6656 | 450.9374 | -17.7036 | -44.1427 | 8.8974 | 5.5356 | -0.3547 | -1.7506 | 1.1695 | -2.0327 | 8.4727 | 2.3575 | 0.6038 | 0.647 | 0.955 | 0.7255 | -130.6362 | -3.8554 | 4.0224 | 0.8685 | -4.9064 | -3.3184 | 2.9596 |  | 1.2186 | -1.084 | 4.0142 | 3.3678 | 3.3497 | 1.0493 | 10.7601 | 14.257 | 14.8209 | 11.0836 | -0.0004 | -0.0027 | 0.0005 | 0.0034 | 0.0005 | -0.0007 | -0.0027 | -0.0158 | -0.0119 | -360.1896 | 17.4192 | -360.4973 | 17.7087 | -360.8327 | 18.0927 | -360.8512 | 17.5424 | -352.6506 | 18.721 | -352.706 | 16.8217
12:12 | 3116 | 34.6911 | 199.4841 | 445.7385 | 450.9652 | -17.7603 | -44.1393 | 8.8069 | 5.4928 | -0.3024 | -1.7479 | 1.2005 | -2.0871 | 8.5533 | 2.3506 | 0.6055 | 0.647 | 0.9556 | 0.7256 | -130.5885 | -3.8204 | 3.9812 | 0.7293 | -4.9191 | -3.3821 | 2.9142 |  | 1.2492 | -0.9761 | 4.013 | 3.3662 | 3.3465 | 1.0481 | 10.7325 | 14.2348 | 14.7797 | 11.0854 | -0.0002 | -0.0031 | 0.0011 | 0.0041 | 0.0007 | -0.0004 | 0 | -0.0038 | -0.0143 | -360.1281 | 17.4048 | -360.4542 | 17.6902 | -360.8358 | 18.1296 | -360.8789 | 17.5486 | -352.6629 | 18.6902 | -352.6813 | 16.8217
12:12 | 3117 | 34.718 | 199.4719 | 445.8067 | 450.9238 | -17.6959 | -44.1168 | 8.8142 | 5.5615 | -0.3643 | -1.7554 | 1.2187 | -2.0815 | 8.4828 | 2.3289 | 0.6044 | 0.6495 | 0.9546 | 0.7274 | -130.5908 | -3.9464 | 4.027 | 0.7853 | -4.9184 | -3.4107 | 2.9781 |  | 1.2533 | -0.9606 | 4.0143 | 3.3678 | 3.3523 | 1.0486 | 10.7209 | 14.2404 | 14.7612 | 11.0454 | 0.0003 | -0.003 | 0.0008 | 0.0038 | 0.0008 | -0.001 | 0.0195 | -0.0039 | -0.0073 | -360.1711 | 17.3823 | -360.4204 | 17.6636 | -360.7897 | 18.1112 | -360.8974 | 17.5629 | -352.666 | 18.6758 | -352.6321 | 16.7991
12:12 | 3118 | 34.7337 | 199.5241 | 445.8396 | 450.9271 | -17.6799 | -44.1386 | 8.8111 | 5.4552 | -0.3804 | -1.711 | 1.161 | -2.1309 | 8.4859 | 2.2392 | 0.6051 | 0.6504 | 0.9552 | 0.728 | -130.6225 | -4.1394 | 3.89 | 0.8074 | -4.9493 | -3.405 | 2.9746 |  | 1.3581 | -0.8748 | 4.0155 | 3.3664 | 3.3535 | 1.0492 | 10.7244 | 14.2555 | 14.7769 | 11.0428 | -0.0003 | -0.0029 | 0.0009 | 0.0035 | 0.0005 | -0.0004 | 0.0136 | -0.006 | -0.017 | -360.2081 | 17.4336 | -360.5035 | 17.6882 | -360.7958 | 18.1112 | -360.8881 | 17.5588 | -352.6967 | 18.7312 | -352.7213 | 16.8135
12:12 | 3119 | 34.7279 | 199.4565 | 445.7564 | 450.8653 | -17.754 | -44.0451 | 8.9402 | 5.3841 | -0.3462 | -1.7359 | 1.1403 | -2.0513 | 8.5318 | 2.3771 | 0.6064 | 0.6508 | 0.9555 | 0.7266 | -130.576 | -3.9758 | 3.9041 | 0.8033 | -4.8583 | -3.3749 | 2.904 |  | 1.2961 | -0.948 | 4.0149 | 3.3696 | 3.35 | 1.0484 | 10.7267 | 14.2463 | 14.7912 | 11.0681 | 0 | -0.0021 | 0.0007 | 0.0043 | 0.0009 | -0.0004 | 0.0202 | -0.0022 | -0.004 | -360.1127 | 17.4048 | -360.485 | 17.7067 | -360.8297 | 18.0763 | -360.8143 | 17.5239 | -352.626 | 18.7025 | -352.6875 | 16.832
12:12 | 3120 | 34.6301 | 199.4744 | 445.8046 | 450.9166 | -17.7126 | -44.074 | 9.0167 | 5.4386 | -0.3885 | -1.7553 | 1.1623 | -2.0481 | 8.4935 | 2.3205 | 0.604 | 0.6487 | 0.9555 | 0.7261 | -130.6158 | -4.1101 | 3.8275 | 0.8758 | -4.8132 | -3.353 | 3.0295 |  | 1.282 | -0.9398 | 4.0145 | 3.3654 | 3.3463 | 1.0473 | 10.7637 | 14.2544 | 14.8103 | 11.0648 | 0 | -0.0029 | 0.0005 | 0.0039 | 0.001 | 0.0001 | 0.02 | 0.0035 | -0.0226 | -360.1619 | 17.4131 | -360.4696 | 17.6985 | -360.8389 | 18.1091 | -360.8789 | 17.5671 | -352.6506 | 18.6861 | -352.6567 | 16.8176
12:12 | 3121 | 34.6525 | 199.428 | 445.7536 | 450.9145 | -17.7071 | -43.992 | 8.9784 | 5.4529 | -0.3244 | -1.7093 | 1.1053 | -2.1017 | 8.4633 | 2.3863 | 0.6046 | 0.6496 | 0.9542 | 0.727 | -130.6034 | -3.9526 | 3.8446 | 0.9932 | -4.8136 | -3.2749 | 3.1377 |  | 1.3128 | -0.8786 | 4.0142 | 3.3623 | 3.3481 | 1.0479 | 10.7335 | 14.2189 | 14.8121 | 11.0742 | 0.0006 | -0.0024 | 0.0005 | 0.0037 | 0.0005 | -0.0004 | 0.011 | -0.026 | -0.0091 | -360.1681 | 17.4151 | -360.4881 | 17.6882 | -360.8143 | 18.1091 | -360.8789 | 17.5527 | -352.6844 | 18.721 | -352.6967 | 16.8238
12:12 | 3122 | 34.703 | 199.4065 | 445.7005 | 451.06 | -17.79 | -44.0358 | 8.8722 | 5.542 | -0.3506 | -1.7943 | 1.1026 | -2.0424 | 8.5521 | 2.3934 | 0.6057 | 0.6473 | 0.9564 | 0.7266 | -130.6294 | -3.9573 | 3.8179 | 0.8473 | -4.8039 | -3.3356 | 3.0346 |  | 1.2804 | -0.9643 | 4.0134 | 3.368 | 3.3492 | 1.0484 | 10.7291 | 14.2369 | 14.7745 | 11.0941 | -0.0001 | -0.0029 | 0.0003 | 0.0038 | 0.0006 | -0.0006 | 0.0169 | 0.0011 | -0.0204 | -360.1558 | 17.4048 | -360.4789 | 17.6759 | -360.7989 | 18.0845 | -360.8666 | 17.5486 | -352.6352 | 18.7004 | -352.6844 | 16.8135
12:12 | 3123 | 34.6981 | 199.4166 | 445.7287 | 451.0974 | -17.7422 | -44.084 | 8.7973 | 5.5345 | -0.3738 | -1.8449 | 1.0634 | -2.0402 | 8.498 | 2.3156 | 0.6049 | 0.6471 | 0.957 | 0.7255 | -130.6178 | -3.8553 | 3.8173 | 0.8487 | -4.83 | -3.3619 | 3.0144 |  | 1.3164 | -0.999 | 4.0138 | 3.3677 | 3.3478 | 1.0482 | 10.7579 | 14.2603 | 14.7882 | 11.0876 | -0.0007 | -0.0027 | 0.001 | 0.0039 | 0.0008 | -0.0002 | -0.0038 | -0.0011 | -0.0176 | -360.2235 | 17.4356 | -360.5004 | 17.7046 | -360.8389 | 18.105 | -360.8727 | 17.5671 | -352.706 | 18.7333 | -352.7152 | 16.8381
12:12 | 3124 | 34.6947 | 199.5279 | 445.8388 | 451.1169 | -17.6941 | -43.9553 | 8.8487 | 5.4587 | -0.4027 | -1.7958 | 1.0019 | -2.126 | 8.4022 | 2.2795 | 0.6041 | 0.6477 | 0.9518 | 0.7253 | -130.5318 | -3.9352 | 3.9177 | 0.8077 | -4.9132 | -3.3987 | 2.9415 |  | 1.359 | -0.9393 | 4.0135 | 3.3672 | 3.3469 | 1.0485 | 10.7012 | 14.244 | 14.7711 | 11.0544 | -0.0002 | -0.003 | 0.0006 | 0.0038 | 0.0009 | -0.0011 | 0.0136 | -0.0147 | 0.0091 | -360.1188 | 17.3925 | -360.4635 | 17.6841 | -360.7989 | 18.0804 | -360.8297 | 17.5424 | -352.626 | 18.6984 | -352.6783 | 16.832
12:12 | 3125 | 34.6809 | 199.4136 | 445.7193 | 451.004 | -17.6628 | -44.0238 | 8.8984 | 5.4614 | -0.3524 | -1.7692 | 1.009 | -2.1224 | 8.5124 | 2.3852 | 0.6052 | 0.6488 | 0.9558 | 0.7262 | -130.548 | -3.8864 | 3.8732 | 0.9337 | -4.8537 | -3.4236 | 2.9796 |  | 1.2546 | -1.0549 | 4.0139 | 3.3703 | 3.3495 | 1.0461 | 10.7244 | 14.2612 | 14.7527 | 11.0432 | 0.0001 | -0.0033 | 0.0012 | 0.0041 | 0.0004 | -0.0001 | 0.0078 | -0.0092 | 0.0084 | -360.1865 | 17.4048 | -360.4604 | 17.6985 | -360.8604 | 18.1214 | -360.9035 | 17.5732 | -352.6844 | 18.7025 | -352.6475 | 16.8238
12:12 | 3126 | 34.638 | 199.3652 | 445.7586 | 450.9703 | -17.6928 | -44.0114 | 8.8002 | 5.6213 | -0.3181 | -1.6844 | 1.103 | -2.1217 | 8.5185 | 2.3466 | 0.6047 | 0.6494 | 0.9541 | 0.7277 | -130.5611 | -3.9454 | 3.9003 | 0.9193 | -4.849 | -3.3852 | 3.0102 |  | 1.2066 | -1.0229 | 4.0134 | 3.3655 | 3.3478 | 1.0481 | 10.737 | 14.228 | 14.8257 | 11.0435 | 0 | -0.0029 | 0.0008 | 0.0039 | 0.001 | -0.001 | 0.015 | -0.0045 | -0.0056 | -360.1865 | 17.4151 | -360.4696 | 17.6697 | -360.7773 | 18.0968 | -360.8974 | 17.5753 | -352.709 | 18.7169 | -352.6783 | 16.8053
12:12 | 3127 | 34.6537 | 199.334 | 445.7577 | 450.9672 | -17.7604 | -44.0698 | 8.7826 | 5.5825 | -0.3983 | -1.7511 | 1.1528 | -2.1302 | 8.5172 | 2.2826 | 0.6057 | 0.646 | 0.9542 | 0.7277 | -130.499 | -3.9994 | 3.8582 | 0.9279 | -5.0089 | -3.3666 | 2.9914 |  | 1.2755 | -1.014 | 4.0123 | 3.3662 | 3.3489 | 1.0484 | 10.7361 | 14.2495 | 14.7922 | 11.0725 | -0.0006 | -0.003 | 0.0004 | 0.0037 | 0.0005 | -0.0002 | 0.0021 | 0.0011 | -0.0141 | -360.1711 | 17.4336 | -360.4942 | 17.6964 | -360.8266 | 18.0783 | -360.8512 | 17.5404 | -352.6844 | 18.7148 | -352.6998 | 16.834
12:12 | 3128 | 34.7286 | 199.4249 | 445.7614 | 450.9525 | -17.7166 | -44.0425 | 8.8102 | 5.6233 | -0.3334 | -1.6179 | 1.1608 | -2.1272 | 8.5384 | 2.3526 | 0.6038 | 0.6447 | 0.958 | 0.7267 | -130.6067 | -3.8991 | 3.8521 | 0.7688 | -4.8802 | -3.3485 | 2.9924 |  | 1.2207 | -1.1144 | 4.0134 | 3.3644 | 3.3514 | 1.0489 | 10.7556 | 14.2754 | 14.8502 | 11.0793 | -0.0002 | -0.0026 | 0.0008 | 0.0042 | 0.0006 | -0.0006 | 0.0321 | -0.002 | -0.0051 | -360.1435 | 17.4069 | -360.4881 | 17.719 | -360.885 | 18.1296 | -360.8697 | 17.5445 | -352.6567 | 18.7045 | -352.7121 | 16.8607
12:12 | 3129 | 34.7731 | 199.4102 | 445.6634 | 450.9197 | -17.6958 | -44.0142 | 8.8851 | 5.6393 | -0.3464 | -1.7351 | 1.102 | -2.1247 | 8.5382 | 2.371 | 0.6058 | 0.6455 | 0.9551 | 0.7252 | -130.4861 | -3.8293 | 3.9512 | 0.7606 | -4.9351 | -3.3779 | 3.0127 |  | 1.326 | -1.0397 | 4.0136 | 3.3671 | 3.3531 | 1.0494 | 10.7555 | 14.264 | 14.7934 | 11.102 | 0.0002 | -0.0031 | 0.0007 | 0.0037 | 0.0006 | -0.0003 | 0.0062 | -0.0022 | -0.0178 | -360.1342 | 17.3699 | -360.405 | 17.6759 | -360.7927 | 18.1153 | -360.8881 | 17.5404 | -352.6352 | 18.6799 | -352.629 | 16.8156
12:12 | 3130 | 34.7 | 199.3888 | 445.7179 | 450.9548 | -17.7581 | -44.0636 | 8.8646 | 5.5577 | -0.3124 | -1.7117 | 1.0923 | -2.1236 | 8.4644 | 2.3874 | 0.6044 | 0.646 | 0.9557 | 0.726 | -130.445 | -3.8322 | 3.9083 | 0.7446 | -4.9354 | -3.4539 | 2.9609 |  | 1.2936 | -1.065 | 4.0121 | 3.3665 | 3.349 | 1.0486 | 10.7614 | 14.2462 | 14.8075 | 11.0742 | -0.0004 | -0.0033 | 0.0007 | 0.0037 | 0.0012 | 0 | -0.0083 | 0.0023 | -0.0191 | -360.2142 | 17.4439 | -360.4942 | 17.6902 | -360.842 | 18.0988 | -360.8912 | 17.5896 | -352.7152 | 18.7312 | -352.6906 | 16.8258
12:12 | 3131 | 34.6538 | 199.4301 | 445.7195 | 450.9685 | -17.7143 | -44.1166 | 8.8037 | 5.6603 | -0.2693 | -1.5311 | 1.109 | -1.9872 | 8.507 | 2.4735 | 0.6048 | 0.6465 | 0.9569 | 0.7265 | -130.4953 | -3.772 | 3.806 | 0.7897 | -4.9203 | -3.3423 | 3.0184 |  | 1.3627 | -0.954 | 4.0146 | 3.3694 | 3.3497 | 1.05 | 10.7589 | 14.2618 | 14.8438 | 11.0532 | -0.0002 | -0.0025 | 0.0013 | 0.0039 | 0.0006 | -0.0006 | 0.0078 | -0.013 | -0.0074 | -360.1742 | 17.4336 | -360.5035 | 17.7005 | -360.8266 | 18.0701 | -360.8297 | 17.5321 | -352.669 | 18.7251 | -352.7121 | 16.8402
12:12 | 3132 | 34.6586 | 199.399 | 445.6365 | 450.8827 | -17.698 | -44.0505 | 8.9481 | 5.6253 | -0.3258 | -1.6479 | 0.9625 | -2.0926 | 8.5761 | 2.3582 | 0.6046 | 0.6459 | 0.9567 | 0.7247 | -130.3636 | -3.7646 | 3.8948 | 0.7937 | -4.9156 | -3.3149 | 2.9838 |  | 1.273 | -1.0799 | 4.0147 | 3.3655 | 3.3452 | 1.0479 | 10.743 | 14.2275 | 14.8051 | 11.062 | -0.0008 | -0.0033 | 0.0006 | 0.0032 | 0.0004 | -0.0006 | 0.01 | -0.0033 | -0.0232 | -360.1342 | 17.4213 | -360.4819 | 17.7067 | -360.8358 | 18.0906 | -360.8758 | 17.5301 | -352.6537 | 18.7107 | -352.7029 | 16.8402
12:12 | 3133 | 34.7474 | 199.5189 | 445.607 | 450.9795 | -17.6754 | -44.1589 | 8.9215 | 5.6443 | -0.3061 | -1.6261 | 1.0185 | -2.0808 | 8.5969 | 2.4923 | 0.6049 | 0.6459 | 0.9545 | 0.7259 | -130.5083 | -3.7442 | 3.9325 | 0.846 | -4.9107 | -3.388 | 2.9178 |  | 1.292 | -1.0742 | 4.0144 | 3.3678 | 3.35 | 1.0483 | 10.7231 | 14.2373 | 14.8008 | 11.0583 | 0.0001 | -0.0029 | 0.0012 | 0.0041 | 0.0013 | -0.0005 | 0.0268 | -0.0196 | 0.0203 | -360.1742 | 17.409 | -360.4696 | 17.6902 | -360.8174 | 18.1255 | -360.9158 | 17.5671 | -352.6813 | 18.7066 | -352.666 | 16.834
12:12 | 3134 | 34.7115 | 199.5082 | 445.7266 | 450.9883 | -17.7488 | -44.0218 | 8.9324 | 5.6692 | -0.2745 | -1.5214 | 1.0686 | -2.2108 | 8.4215 | 2.4219 | 0.6037 | 0.6441 | 0.9554 | 0.7258 | -130.5257 | -3.7793 | 3.9203 | 0.8489 | -4.9248 | -3.3307 | 3.0223 |  | 1.2844 | -1.0923 | 4.0132 | 3.3643 | 3.3502 | 1.0494 | 10.7405 | 14.2489 | 14.8471 | 11.0756 | 0.0002 | -0.0033 | 0.0008 | 0.0038 | 0.0007 | -0.0003 | 0.0142 | 0.0019 | 0.0031 | -360.1927 | 17.4048 | -360.4296 | 17.6533 | -360.7497 | 18.0804 | -360.8758 | 17.5671 | -352.6967 | 18.6963 | -352.6629 | 16.8074
12:12 | 3135 | 34.792 | 199.5477 | 445.7856 | 451.0767 | -17.8071 | -44.0864 | 8.9322 | 5.6697 | -0.2573 | -1.5317 | 1.1176 | -2.1404 | 8.4612 | 2.3661 | 0.6037 | 0.6455 | 0.9558 | 0.7267 | -130.5021 | -3.7013 | 3.9103 | 0.7457 | -4.9795 | -3.4066 | 2.9625 |  | 1.2704 | -1.1114 | 4.0136 | 3.3661 | 3.3509 | 1.0497 | 10.7568 | 14.2764 | 14.81 | 11.0749 | -0.0001 | -0.0026 | 0.0004 | 0.0038 | 0.0005 | -0.0009 | -0.0014 | -0.0036 | -0.0172 | -360.1773 | 17.4336 | -360.5158 | 17.7067 | -360.8327 | 18.1071 | -360.8635 | 17.5465 | -352.6813 | 18.7312 | -352.7029 | 16.8402
12:12 | 3136 | 34.7955 | 199.5358 | 445.8861 | 451.0236 | -17.7987 | -44.0093 | 8.9397 | 5.6609 | -0.2714 | -1.6904 | 1.0683 | -2.1108 | 8.5518 | 2.4344 | 0.6049 | 0.6468 | 0.9568 | 0.727 | -130.5601 | -3.7796 | 3.8507 | 0.7498 | -4.9151 | -3.3912 | 2.883 |  | 1.3224 | -1.0883 | 4.0133 | 3.3678 | 3.3497 | 1.0488 | 10.7313 | 14.2567 | 14.7609 | 11.0612 | -0.0004 | -0.0025 | 0.0005 | 0.0038 | 0.0008 | -0.0002 | 0.012 | -0.0164 | 0.002 | -360.1742 | 17.3946 | -360.4604 | 17.6964 | -360.8512 | 18.1153 | -360.8881 | 17.5568 | -352.6537 | 18.7025 | -352.6813 | 16.8279
12:12 | 3137 | 34.7123 | 199.5306 | 445.7642 | 451.07 | -17.7051 | -43.9301 | 8.9269 | 5.7722 | -0.1442 | -1.6236 | 1.0539 | -2.2233 | 8.5794 | 2.5024 | 0.6031 | 0.6471 | 0.9557 | 0.7263 | -130.5373 | -3.6259 | 3.8548 | 0.754 | -4.8191 | -3.4101 | 2.9382 |  | 1.2973 | -1.1005 | 4.0135 | 3.366 | 3.3466 | 1.0492 | 10.7475 | 14.2498 | 14.8174 | 11.0544 | -0.0002 | -0.003 | 0.0004 | 0.0035 | 0.0008 | -0.0009 | 0.0046 | 0.0075 | 0.0042 | -360.1311 | 17.3987 | -360.4481 | 17.6738 | -360.802 | 18.1009 | -360.8881 | 17.5486 | -352.6321 | 18.6984 | -352.6629 | 16.8135
12:12 | 3138 | 34.733 | 199.5412 | 445.7884 | 451.0796 | -17.6746 | -43.9785 | 8.972 | 5.7289 | -0.2437 | -1.6162 | 1.0918 | -2.1653 | 8.5849 | 2.4948 | 0.604 | 0.6447 | 0.9508 | 0.7267 | -130.5945 | -3.6012 | 3.8527 | 0.8108 | -4.7199 | -3.2869 | 3.0334 |  | 1.3328 | -1.1127 | 4.0138 | 3.3657 | 3.3472 | 1.0492 | 10.759 | 14.2499 | 14.7606 | 11.0367 | 0.0004 | -0.0027 | 0.0007 | 0.0039 | 0.0006 | -0.0002 | 0.008 | -0.0008 | 0.0008 | -360.1681 | 17.4254 | -360.4666 | 17.7087 | -360.8389 | 18.1091 | -360.9066 | 17.5732 | -352.6844 | 18.7128 | -352.7029 | 16.832
12:12 | 3139 | 34.7615 | 199.4577 | 445.8054 | 451.0808 | -17.7176 | -43.9963 | 8.9882 | 5.7145 | -0.2919 | -1.7741 | 0.9967 | -2.1102 | 8.5124 | 2.4484 | 0.6046 | 0.6465 | 0.9528 | 0.7249 | -130.6005 | -3.6053 | 3.8963 | 0.8057 | -4.8073 | -3.2986 | 2.9482 |  | 1.4525 | -0.9799 | 4.013 | 3.3648 | 3.3471 | 1.049 | 10.7533 | 14.2268 | 14.8011 | 11.0655 | -0.0003 | -0.003 | 0.0011 | 0.0041 | 0.0006 | -0.001 | 0.0162 | -0.0232 | -0.0143 | -360.165 | 17.4007 | -360.4481 | 17.6759 | -360.7989 | 18.0947 | -360.8512 | 17.5445 | -352.666 | 18.7045 | -352.6629 | 16.8176
12:12 | 3140 | 34.737 | 199.4921 | 445.757 | 451.1169 | -17.7078 | -43.9476 | 9.0269 | 5.6782 | -0.2873 | -1.7675 | 1.0465 | -2.102 | 8.5624 | 2.4626 | 0.6045 | 0.6454 | 0.9532 | 0.7242 | -130.6343 | -3.5459 | 3.897 | 0.9208 | -4.8704 | -3.3553 | 2.974 |  | 1.3474 | -1.0156 | 4.0129 | 3.365 | 3.3517 | 1.048 | 10.751 | 14.2416 | 14.8031 | 11.0349 | -0.0003 | -0.0022 | 0.0012 | 0.004 | 0.0007 | -0.0006 | -0.0032 | 0.0067 | -0.0055 | -360.1865 | 17.4274 | -360.5312 | 17.7272 | -360.882 | 18.1071 | -360.8574 | 17.5486 | -352.6598 | 18.7128 | -352.7306 | 16.8402
12:12 | 3141 | 34.7217 | 199.4818 | 445.7701 | 451.0618 | -17.7053 | -43.9808 | 8.9645 | 5.7253 | -0.4193 | -1.6336 | 1.0244 | -2.1578 | 9.2616 | 2.4798 | 0.6049 | 0.6436 | 0.9537 | 0.7258 | -130.6202 | -3.5825 | 3.9663 | 0.8544 | -4.8509 | -3.3621 | 3.0254 |  | 1.4177 | -1.0368 | 4.0131 | 3.3657 | 3.3446 | 1.0496 | 10.7463 | 14.2198 | 14.794 | 11.0471 | 0.0001 | -0.0028 | 0.0003 | 0.0033 | 0.0009 | -0.0005 | 0.0009 | -0.0015 | -0.0197 | -360.1558 | 17.4069 | -360.4419 | 17.6985 | -360.845 | 18.1153 | -360.8574 | 17.5342 | -352.666 | 18.7025 | -352.6629 | 16.8361
12:12 | 3142 | 34.8033 | 199.5656 | 445.8362 | 451.1097 | -17.704 | -44.0647 | 8.8171 | 5.7604 | -0.5323 | -1.4883 | 1.1105 | -1.9876 | 9.4649 | 2.5726 | 0.6046 | 0.6435 | 0.9536 | 0.7238 | -130.4947 | -3.466 | 4.0666 | 0.9079 | -4.9384 | -3.4759 | 2.9948 |  | 1.3909 | -1.0481 | 4.0116 | 3.3685 | 3.3476 | 1.0483 | 10.7337 | 14.2243 | 14.7973 | 11.0638 | 0.0002 | -0.0033 | 0.0008 | 0.0036 | 0.0011 | -0.0006 | 0.0121 | -0.0155 | -0.0274 | -360.1927 | 17.4131 | -360.4542 | 17.682 | -360.7927 | 18.0906 | -360.9004 | 17.5691 | -352.6629 | 18.7045 | -352.6567 | 16.8053
12:12 | 3143 | 34.7648 | 199.4953 | 445.7458 | 451.0023 | -17.7063 | -44.1469 | 8.7873 | 5.7019 | -0.591 | -1.2452 | 1.0616 | -2.134 | 9.3865 | 2.4969 | 0.6035 | 0.6449 | 0.9549 | 0.7247 | -130.6203 | -3.5457 | 4.0222 | 0.9372 | -5.0344 | -3.4832 | 2.9773 |  | 1.3815 | -0.9987 | 4.0129 | 3.3686 | 3.3502 | 1.0484 | 10.7024 | 14.2219 | 14.7599 | 11.0212 | 0 | -0.0025 | 0.0003 | 0.0037 | 0.0007 | -0.0002 | 0.0082 | -0.0079 | -0.0072 | -360.205 | 17.4562 | -360.5189 | 17.7046 | -360.8481 | 18.0845 | -360.8574 | 17.5609 | -352.7244 | 18.7559 | -352.7244 | 16.8258
12:12 | 3144 | 34.7863 | 199.5164 | 445.7243 | 451.0134 | -17.6834 | -44.112 | 8.942 | 5.6253 | -0.6918 | -1.3806 | 0.9878 | -2.165 | 9.4297 | 2.6098 | 0.605 | 0.6468 | 0.9526 | 0.7267 | -130.6693 | -3.7437 | 3.9887 | 0.9869 | -4.9621 | -3.4569 | 2.9946 |  | 1.4356 | -1.0057 | 4.0139 | 3.3663 | 3.3483 | 1.048 | 10.743 | 14.2332 | 14.7983 | 11.0566 | -0.0006 | -0.0027 | 0.001 | 0.0043 | 0.0013 | -0.0008 | 0.0037 | -0.0156 | 0.0014 | -360.1281 | 17.4069 | -360.4789 | 17.7005 | -360.8358 | 18.0804 | -360.8297 | 17.5383 | -352.6413 | 18.7107 | -352.6752 | 16.8279
12:12 | 3145 | 34.7916 | 199.5258 | 445.8251 | 451.076 | -17.7331 | -44.1301 | 9.0247 | 5.552 | -0.6505 | -1.3268 | 0.9289 | -2.124 | 9.4382 | 2.5705 | 0.6055 | 0.6441 | 0.9544 | 0.7262 | -130.6458 | -3.6113 | 3.9828 | 0.9813 | -4.9528 | -3.3861 | 3.0109 |  | 1.4972 | -1.0739 | 4.0128 | 3.3674 | 3.3463 | 1.0472 | 10.7209 | 14.2578 | 14.7786 | 11.0627 | 0.0001 | -0.0026 | 0.0009 | 0.004 | 0.0004 | -0.0003 | 0.0107 | -0.0103 | 0.004 | -360.1711 | 17.409 | -360.4542 | 17.6923 | -360.8574 | 18.1379 | -360.9127 | 17.5609 | -352.6844 | 18.7004 | -352.6906 | 16.832
12:12 | 3146 | 34.8927 | 199.5696 | 445.8551 | 451.1162 | -17.7008 | -44.1172 | 9.0161 | 5.5671 | -0.7411 | -1.425 | 1.06 | -2.0654 | 9.4892 | 2.6193 | 0.6038 | 0.644 | 0.9514 | 0.7259 | -130.6219 | -3.7119 | 4.0252 | 0.9772 | -5.0518 | -3.4207 | 2.991 |  | 1.4384 | -0.9884 | 4.0131 | 3.3686 | 3.3461 | 1.0492 | 10.7682 | 14.2652 | 14.7774 | 11.0626 | 0.0001 | -0.0031 | 0.0005 | 0.0037 | 0.0009 | -0.0004 | 0.0167 | -0.009 | -0.0121 | -360.2204 | 17.3946 | -360.4142 | 17.6594 | -360.7866 | 18.0968 | -360.9004 | 17.5712 | -352.6721 | 18.6922 | -352.6444 | 16.7909
12:12 | 3147 | 34.9253 | 199.5536 | 445.8831 | 451.0488 | -17.7906 | -44.1028 | 8.8484 | 5.4866 | -0.7869 | -1.4159 | 1.0148 | -2.1259 | 9.5587 | 2.6392 | 0.6038 | 0.6486 | 0.9525 | 0.7267 | -130.618 | -3.675 | 4.0329 | 0.919 | -5.0889 | -3.4257 | 3.0479 |  | 1.366 | -1.0143 | 4.014 | 3.3641 | 3.3493 | 1.0487 | 10.7521 | 14.2429 | 14.8287 | 11.076 | -0.0001 | -0.003 | 0.0013 | 0.0042 | 0.0005 | -0.0001 | 0.013 | -0.0133 | -0.0087 | -360.1988 | 17.4439 | -360.5096 | 17.7026 | -360.7989 | 18.1071 | -360.8912 | 17.5732 | -352.7029 | 18.723 | -352.7213 | 16.8238
12:12 | 3148 | 34.8186 | 199.4929 | 445.9031 | 451.0695 | -17.8311 | -43.982 | 8.9679 | 5.4883 | -0.8449 | -1.4463 | 1.0151 | -2.1583 | 9.581 | 2.6553 | 0.6031 | 0.6481 | 0.9525 | 0.7254 | -130.5878 | -3.7022 | 4.0532 | 0.9739 | -5.0529 | -3.5496 | 2.9556 |  | 1.351 | -0.9955 | 4.0148 | 3.3663 | 3.3487 | 1.0498 | 10.7439 | 14.2466 | 14.7992 | 11.0442 | -0.0003 | -0.0025 | 0.001 | 0.0037 | 0.001 | -0.0003 | 0.0215 | -0.0129 | 0.0024 | -360.1373 | 17.411 | -360.4789 | 17.7169 | -360.8604 | 18.0927 | -360.845 | 17.5239 | -352.6413 | 18.7128 | -352.7244 | 16.8505
12:12 | 3149 | 34.8541 | 199.4691 | 445.8747 | 451.1429 | -17.8416 | -44.0851 | 8.9447 | 5.3874 | -0.7582 | -1.5491 | 1.101 | -2.1281 | 9.5497 | 2.5331 | 0.603 | 0.6485 | 0.9549 | 0.7262 | -130.6169 | -3.7082 | 4.0076 | 1.0733 | -4.9408 | -3.3147 | 3.0538 |  | 1.386 | -1.0295 | 4.0135 | 3.3683 | 3.3474 | 1.0492 | 10.7718 | 14.2627 | 14.8257 | 11.1013 | -0.0004 | -0.0028 | 0.0005 | 0.0036 | 0.0009 | -0.0005 | 0.0089 | -0.0049 | -0.0133 | -360.1588 | 17.409 | -360.5066 | 17.7169 | -360.8974 | 18.1379 | -360.8789 | 17.5383 | -352.6352 | 18.7066 | -352.6844 | 16.8525
12:12 | 3150 | 34.8496 | 199.4796 | 445.9225 | 451.0595 | -17.7374 | -44.028 | 8.9132 | 5.4079 | -0.6621 | -1.5633 | 1.1268 | -2.1146 | 9.5881 | 2.6916 | 0.6034 | 0.6505 | 0.9533 | 0.7269 | -130.6162 | -3.7701 | 4.0318 | 1.1024 | -4.8567 | -3.3359 | 3.1573 |  | 1.3543 | -1.0405 | 4.0139 | 3.367 | 3.3496 | 1.0493 | 10.7647 | 14.2502 | 14.8206 | 11.0706 | 0.0004 | -0.0027 | 0.0007 | 0.004 | 0.001 | -0.0001 | 0.0373 | -0.0149 | 0.0073 | -360.1804 | 17.3987 | -360.4481 | 17.6759 | -360.8204 | 18.1029 | -360.9127 | 17.5527 | -352.666 | 18.7025 | -352.6537 | 16.8279
12:12 | 3151 | 34.8434 | 199.5551 | 445.8684 | 451.0743 | -17.7355 | -44.1449 | 8.9429 | 5.4074 | -0.6165 | -1.594 | 1.0831 | -2.1031 | 9.5978 | 2.6837 | 0.6029 | 0.6483 | 0.9557 | 0.7263 | -130.6778 | -3.7676 | 4.0493 | 1.0655 | -4.8928 | -3.2638 | 3.0509 |  | 1.3628 | -1.038 | 4.0149 | 3.3675 | 3.348 | 1.0509 | 10.7313 | 14.2452 | 14.7667 | 11.0612 | 0 | -0.0035 | 0.0003 | 0.0034 | 0.0011 | -0.0008 | 0.0144 | -0.0076 | -0.0029 | -360.2327 | 17.4336 | -360.4973 | 17.6656 | -360.7958 | 18.0763 | -360.882 | 17.5609 | -352.7029 | 18.7415 | -352.7121 | 16.7971
12:12 | 3152 | 34.8084 | 199.4573 | 445.9332 | 451.0672 | -17.7436 | -44.1125 | 8.9484 | 5.404 | -0.5784 | -1.6402 | 1.0821 | -2.1492 | 9.53 | 2.6037 | 0.6037 | 0.6488 | 0.9548 | 0.727 | -130.7057 | -3.6886 | 4.0809 | 1.0255 | -4.8437 | -3.2162 | 3.1118 |  | 1.3449 | -1.0876 | 4.0142 | 3.3664 | 3.3494 | 1.0509 | 10.7255 | 14.222 | 14.7725 | 11.0555 | -0.0004 | -0.0029 | 0.0006 | 0.0039 | 0.0006 | -0.0004 | 0.0112 | 0.0008 | -0.0312 | -360.1742 | 17.4254 | -360.5096 | 17.6944 | -360.8358 | 18.0824 | -360.8666 | 17.5506 | -352.6967 | 18.7353 | -352.7244 | 16.8361
12:12 | 3153 | 34.8685 | 199.4734 | 445.8969 | 450.9969 | -17.8077 | -44.1573 | 8.8586 | 5.3643 | -0.5787 | -1.6707 | 0.9333 | -2.0253 | 9.5356 | 2.6424 | 0.6037 | 0.6462 | 0.9576 | 0.728 | -130.7229 | -3.7515 | 4.0921 | 0.8368 | -4.7666 | -3.2258 | 3.1027 |  | 1.3867 | -1.0659 | 4.014 | 3.3656 | 3.346 | 1.0493 | 10.7383 | 14.2346 | 14.796 | 11.0338 | -0.0005 | -0.003 | 0.0009 | 0.0041 | 0.0006 | -0.0005 | 0.0065 | -0.0014 | -0.0204 | -360.1588 | 17.3823 | -360.4358 | 17.6779 | -360.8512 | 18.1091 | -360.8758 | 17.5445 | -352.6167 | 18.6861 | -352.6598 | 16.8176
12:12 | 3154 | 34.8301 | 199.4773 | 445.9082 | 451.066 | -17.7386 | -44.1273 | 8.974 | 5.4404 | -0.5529 | -1.5617 | 0.9862 | -2.002 | 9.6102 | 2.6996 | 0.6038 | 0.6491 | 0.9531 | 0.7258 | -130.6325 | -3.5943 | 4.1074 | 0.9126 | -4.8455 | -3.1523 | 3.1207 |  | 1.2904 | -0.9869 | 4.0131 | 3.3662 | 3.3508 | 1.0501 | 10.7406 | 14.2428 | 14.7987 | 11.0417 | 0.0001 | -0.0034 | 0.0006 | 0.0038 | 0.0003 | -0.0005 | -0.0051 | -0.0223 | -0.0168 | -360.2235 | 17.4274 | -360.4881 | 17.682 | -360.8543 | 18.1194 | -360.8974 | 17.5691 | -352.709 | 18.7353 | -352.6906 | 16.8217
12:12 | 3155 | 34.8202 | 199.4891 | 445.9009 | 451.008 | -17.7525 | -44.0536 | 9.0296 | 5.4757 | -0.468 | -1.6254 | 1.0947 | -2.0721 | 9.5939 | 2.6351 | 0.6052 | 0.6457 | 0.9554 | 0.7269 | -130.6965 | -3.4612 | 4.025 | 0.903 | -4.8826 | -3.255 | 3.1009 |  | 1.2731 | -1.1128 | 4.0125 | 3.3663 | 3.3499 | 1.0498 | 10.7474 | 14.2386 | 14.7801 | 11.0475 | 0.0001 | -0.0029 | 0.0013 | 0.0044 | 0.0011 | -0.0003 | -0.0036 | -0.0006 | -0.0168 | -360.1588 | 17.4007 | -360.4296 | 17.6656 | -360.762 | 18.0927 | -360.8512 | 17.5404 | -352.6106 | 18.6984 | -352.6783 | 16.8217
12:12 | 3156 | 34.8074 | 199.5121 | 445.8947 | 450.9874 | -17.7505 | -44.0247 | 9.1128 | 5.3841 | -0.5477 | -1.6492 | 1.0736 | -1.9876 | 9.6416 | 2.56 | 0.6044 | 0.6464 | 0.9542 | 0.7279 | -130.6796 | -3.5802 | 4.1194 | 0.8164 | -4.8133 | -3.1989 | 3.0889 |  | 1.2771 | -1.0359 | 4.0148 | 3.3644 | 3.3468 | 1.05 | 10.7601 | 14.2456 | 14.8452 | 11.0659 | 0 | -0.0027 | 0.001 | 0.004 | 0.0004 | -0.0001 | 0.0094 | 0.0033 | 0.0098 | -360.1988 | 17.4213 | -360.5066 | 17.6944 | -360.8235 | 18.1194 | -360.8943 | 17.5609 | -352.6475 | 18.7292 | -352.7029 | 16.8258
12:12 | 3157 | 34.8673 | 199.6257 | 446.0038 | 451.0168 | -17.7096 | -44.0277 | 9.1309 | 5.4406 | -0.541 | -1.6822 | 1.1766 | -2.1477 | 9.4644 | 2.5091 | 0.6066 | 0.6468 | 0.9596 | 0.7254 | -130.6411 | -3.559 | 4.1486 | 0.897 | -4.8822 | -3.3344 | 3.0766 |  | 1.3198 | -1.0828 | 4.0136 | 3.3664 | 3.3489 | 1.0496 | 10.7764 | 14.2616 | 14.8485 | 11.1114 | -0.0003 | -0.0026 | 0.0006 | 0.0039 | 0.0011 | -0.0008 | 0.0314 | -0.0125 | 0.0153 | -360.1127 | 17.3946 | -360.4542 | 17.68 | -360.7989 | 18.1132 | -360.8574 | 17.5363 | -352.6136 | 18.7025 | -352.6813 | 16.8402
12:12 | 3158 | 34.9176 | 199.6863 | 446.0373 | 451.0765 | -17.6799 | -44.0335 | 9.0598 | 5.5104 | -0.5499 | -1.7445 | 1.1785 | -2.1146 | 9.5312 | 2.5009 | 0.6062 | 0.6471 | 0.957 | 0.7274 | -130.6189 | -3.5726 | 4.0943 | 0.953 | -4.7195 | -3.2408 | 3.12 |  | 1.252 | -1.0491 | 4.0125 | 3.3652 | 3.3482 | 1.0486 | 10.7359 | 14.2557 | 14.8127 | 11.054 | 0 | -0.0027 | 0.0009 | 0.0038 | 0.0006 | -0.0002 | -0.0003 | -0.0113 | -0.0244 | -360.1558 | 17.4007 | -360.4604 | 17.682 | -360.8543 | 18.144 | -360.885 | 17.5671 | -352.6752 | 18.7087 | -352.6598 | 16.8279
12:12 | 3159 | 34.9572 | 199.5689 | 445.9985 | 451.1445 | -17.6578 | -43.9352 | 9.1024 | 5.4696 | -0.5886 | -1.7345 | 1.1655 | -2.1964 | 9.5395 | 2.48 | 0.6027 | 0.6471 | 0.9524 | 0.725 | -130.6879 | -3.6791 | 4.0797 | 0.9544 | -4.6481 | -3.1442 | 3.1473 |  | 1.2703 | -1.1236 | 4.0138 | 3.3647 | 3.3449 | 1.0498 | 10.729 | 14.2544 | 14.7871 | 11.0533 | -0.0001 | -0.0033 | 0.0005 | 0.0036 | 0.0007 | -0.0009 | 0.009 | -0.0207 | -0.0012 | -360.1681 | 17.411 | -360.4666 | 17.6553 | -360.7835 | 18.1214 | -360.882 | 17.5527 | -352.6783 | 18.7251 | -352.7029 | 16.8115
12:12 | 3160 | 34.9788 | 199.6108 | 446.0457 | 451.173 | -17.5904 | -43.9481 | 8.9816 | 5.4769 | -0.5305 | -1.8108 | 1.1796 | -2.2164 | 9.5205 | 2.4353 | 0.6061 | 0.6468 | 0.9563 | 0.7247 | -130.6392 | -3.5857 | 4.1159 | 0.974 | -4.6443 | -3.2025 | 3.211 |  | 1.4029 | -1.1266 | 4.0138 | 3.3646 | 3.3471 | 1.0497 | 10.7152 | 14.2345 | 14.766 | 11.0573 | -0.0001 | -0.0029 | 0.0007 | 0.004 | 0.0008 | -0.0007 | 0.0102 | -0.015 | -0.0108 | -360.1619 | 17.4315 | -360.5343 | 17.6841 | -360.8358 | 18.1091 | -360.8204 | 17.5363 | -352.6752 | 18.7271 | -352.7398 | 16.8443
12:12 | 3161 | 34.9676 | 199.5637 | 446.1334 | 451.0985 | -17.6369 | -43.9122 | 9.1345 | 5.527 | -0.5245 | -1.8569 | 1.2492 | -2.0459 | 9.5647 | 2.6091 | 0.6043 | 0.6459 | 0.9554 | 0.7255 | -130.6115 | -3.586 | 4.208 | 0.9539 | -4.6182 | -3.1606 | 3.1126 |  | 1.4343 | -1.027 | 4.0131 | 3.3626 | 3.3476 | 1.05 | 10.7301 | 14.2152 | 14.7722 | 11.0598 | -0.0005 | -0.0027 | 0.0013 | 0.0045 | 0.0009 | -0.0002 | 0.004 | -0.0179 | -0.0108 | -360.1373 | 17.3987 | -360.4819 | 17.6964 | -360.842 | 18.1235 | -360.882 | 17.5424 | -352.669 | 18.721 | -352.6967 | 16.8443
12:12 | 3162 | 34.936 | 199.4141 | 446.0543 | 451.0598 | -17.6676 | -43.9059 | 8.9422 | 5.5235 | -0.5547 | -1.8826 | 1.1987 | -2.1043 | 9.5761 | 2.7044 | 0.605 | 0.6453 | 0.9538 | 0.7247 | -130.6324 | -3.6223 | 4.0341 | 0.978 | -4.6893 | -3.1435 | 3.1927 |  | 1.3789 | -1.0316 | 4.0133 | 3.363 | 3.3481 | 1.0488 | 10.7256 | 14.2161 | 14.783 | 11.0558 | 0.0002 | -0.0027 | 0.0006 | 0.0037 | 0.0005 | -0.0011 | 0.0136 | 0.0062 | -0.0084 | -360.1865 | 17.3925 | -360.4081 | 17.6451 | -360.8143 | 18.1296 | -360.8974 | 17.5568 | -352.6967 | 18.6922 | -352.6229 | 16.8012
12:12 | 3163 | 35.0047 | 199.4758 | 446.0721 | 451.11 | -17.6718 | -43.9293 | 9.0258 | 5.5249 | -0.4214 | -1.8214 | 1.1592 | -2.1863 | 9.6733 | 2.6397 | 0.6039 | 0.6487 | 0.9576 | 0.7274 | -130.5548 | -3.5772 | 4.0872 | 1.0744 | -4.6776 | -3.1217 | 3.2163 |  | 1.3929 | -0.9058 | 4.0144 | 3.3679 | 3.3506 | 1.0506 | 10.7416 | 14.2501 | 14.7848 | 11.071 | 0 | -0.0033 | 0.0007 | 0.0039 | 0.0006 | 0 | -0.0004 | -0.011 | -0.006 | -360.2358 | 17.4295 | -360.4696 | 17.6615 | -360.8112 | 18.1153 | -360.8912 | 17.5671 | -352.7152 | 18.7333 | -352.6937 | 16.8156
12:12 | 3164 | 34.9414 | 199.5222 | 446.104 | 451.0145 | -17.6925 | -43.9928 | 9.0208 | 5.5466 | -0.4259 | -1.7836 | 1.1938 | -2.08 | 9.558 | 2.7103 | 0.6044 | 0.6472 | 0.9548 | 0.7248 | -130.6518 | -3.6953 | 3.9805 | 1.0042 | -4.6957 | -3.1358 | 3.1264 |  | 1.386 | -0.9086 | 4.014 | 3.3663 | 3.35 | 1.0507 | 10.737 | 14.2512 | 14.8152 | 11.0836 | 0.0001 | -0.0025 | 0.001 | 0.004 | 0.0013 | -0.0004 | 0.0056 | -0.0149 | -0.0212 | -360.1127 | 17.4274 | -360.4727 | 17.6656 | -360.8174 | 18.1132 | -360.8481 | 17.526 | -352.6598 | 18.723 | -352.669 | 16.8217
12:12 | 3165 | 34.9655 | 199.5347 | 446.0408 | 451.1021 | -17.6852 | -43.9687 | 9.0549 | 5.5373 | -0.4279 | -1.7709 | 1.1577 | -2.126 | 9.554 | 2.6589 | 0.6052 | 0.6461 | 0.9583 | 0.7275 | -130.5641 | -3.5849 | 4.0407 | 1.0501 | -4.745 | -3.2314 | 3.1924 |  | 1.4037 | -0.9194 | 4.0148 | 3.3685 | 3.3533 | 1.0507 | 10.7384 | 14.217 | 14.7823 | 11.0634 | -0.0005 | -0.0029 | 0 | 0.0032 | 0.0006 | -0.0001 | 0.0024 | -0.0068 | -0.0168 | -360.1435 | 17.3946 | -360.4758 | 17.7026 | -360.8666 | 18.1563 | -360.922 | 17.526 | -352.6321 | 18.7087 | -352.6967 | 16.8484
12:12 | 3166 | 34.8999 | 199.4088 | 445.9501 | 450.9971 | -17.6063 | -44.0395 | 8.9795 | 5.5881 | -0.3906 | -1.7443 | 1.2087 | -2.1324 | 9.552 | 2.6773 | 0.605 | 0.6529 | 0.9578 | 0.7258 | -130.5719 | -3.6312 | 4.0173 | 1.1067 | -4.715 | -3.1822 | 3.2119 |  | 1.3552 | -0.9514 | 4.0126 | 3.3682 | 3.3519 | 1.0501 | 10.7417 | 14.2615 | 14.8185 | 11.054 | -0.0004 | -0.0027 | 0.001 | 0.004 | 0.001 | -0.0007 | 0.0159 | -0.0165 | -0.0062 | -360.1588 | 17.3843 | -360.4142 | 17.6553 | -360.8081 | 18.1379 | -360.882 | 17.5301 | -352.6383 | 18.684 | -352.6352 | 16.8156
12:12 | 3167 | 35.0155 | 199.4941 | 446.006 | 451.1469 | -17.6781 | -44.0783 | 8.9608 | 5.6107 | -0.3019 | -1.8289 | 1.1108 | -2.205 | 9.4939 | 2.7152 | 0.6043 | 0.6512 | 0.9596 | 0.7289 | -130.5008 | -3.6181 | 4.131 | 1.1413 | -4.7129 | -3.2271 | 3.2345 |  | 1.3176 | -0.9873 | 4.013 | 3.3684 | 3.3465 | 1.0506 | 10.7314 | 14.1988 | 14.7772 | 11.0327 | 0.0002 | -0.0029 | 0.0006 | 0.0037 | 0.0004 | -0.0003 | 0.0295 | -0.0183 | -0.0038 | -360.1958 | 17.4192 | -360.4696 | 17.6574 | -360.8235 | 18.1255 | -360.8974 | 17.5629 | -352.7029 | 18.7353 | -352.6813 | 16.8217
12:13 | 3168 | 34.9951 | 199.5146 | 446.0822 | 451.1167 | -17.6926 | -44.0747 | 9.106 | 5.5772 | -0.2396 | -1.8435 | 1.1149 | -2.1406 | 9.5834 | 2.7419 | 0.6054 | 0.6485 | 0.9554 | 0.7281 | -130.5275 | -3.6374 | 4.0289 | 1.1185 | -4.7682 | -3.2244 | 3.1268 |  | 1.3483 | -0.9955 | 4.0122 | 3.3639 | 3.3445 | 1.0512 | 10.7141 | 14.2216 | 14.7867 | 11.045 | 0 | -0.0033 | 0.0005 | 0.0042 | 0.001 | -0.0006 | -0.0058 | -0.0153 | -0.005 | -360.1742 | 17.4254 | -360.4727 | 17.6574 | -360.805 | 18.0968 | -360.8235 | 17.5219 | -352.6598 | 18.7312 | -352.6752 | 16.8176
12:13 | 3169 | 34.9592 | 199.5274 | 445.9897 | 451.0693 | -17.667 | -44.0144 | 9.1054 | 5.5547 | -0.2442 | -1.8062 | 1.0863 | -2.1506 | 9.5762 | 2.6644 | 0.6057 | 0.6523 | 0.9594 | 0.7279 | -130.573 | -3.7399 | 3.9988 | 1.1254 | -4.8281 | -3.2011 | 3.1804 |  | 1.4599 | -1.0142 | 4.0134 | 3.3634 | 3.351 | 1.0506 | 10.722 | 14.2244 | 14.7984 | 11.0576 | -0.0004 | -0.0026 | 0.0011 | 0.0044 | 0.0009 | -0.0004 | 0.0248 | -0.0072 | -0.0299 | -360.1896 | 17.4254 | -360.5158 | 17.6902 | -360.8604 | 18.1173 | -360.8912 | 17.5424 | -352.6813 | 18.7353 | -352.7429 | 16.8381
12:13 | 3170 | 34.9569 | 199.5026 | 445.9263 | 451.0969 | -17.7747 | -44.019 | 9.0676 | 5.6438 | -0.2786 | -1.8017 | 1.1054 | -2.1924 | 9.5447 | 2.6937 | 0.6063 | 0.6474 | 0.9556 | 0.7273 | -130.5145 | -3.6451 | 4.0093 | 1.028 | -4.9088 | -3.2008 | 3.0822 |  | 1.4404 | -1.0687 | 4.0136 | 3.3623 | 3.3539 | 1.0498 | 10.7544 | 14.2337 | 14.8083 | 11.0551 | -0.0002 | -0.0028 | 0.0009 | 0.004 | 0.0005 | -0.0004 | 0.0146 | -0.0061 | -0.0021 | -360.1527 | 17.3823 | -360.4266 | 17.6348 | -360.765 | 18.1235 | -360.8727 | 17.5465 | -352.6537 | 18.6943 | -352.6475 | 16.8012
12:13 | 3171 | 34.9933 | 199.5247 | 446.0079 | 451.1451 | -17.7272 | -44.0137 | 9.0661 | 5.7309 | -0.3949 | -1.8147 | 1.0923 | -2.1256 | 9.6402 | 2.6852 | 0.6052 | 0.6453 | 0.9553 | 0.7273 | -130.5247 | -3.602 | 4.0037 | 1.0802 | -4.8426 | -3.1409 | 3.035 |  | 1.4168 | -0.9351 | 4.0127 | 3.3622 | 3.3493 | 1.0488 | 10.7555 | 14.2584 | 14.8118 | 11.0612 | 0.0003 | -0.0031 | 0.0012 | 0.004 | 0.0009 | -0.0006 | 0.008 | -0.0154 | 0.0081 | -360.2111 | 17.4254 | -360.4512 | 17.6677 | -360.8266 | 18.1358 | -360.8881 | 17.5506 | -352.7183 | 18.7415 | -352.666 | 16.8176
12:13 | 3172 | 34.919 | 199.4693 | 446.1107 | 451.1858 | -17.7843 | -44.0253 | 8.9974 | 5.7052 | -0.2877 | -1.7568 | 1.0384 | -2.1689 | 9.5796 | 2.6791 | 0.6049 | 0.6501 | 0.9562 | 0.7279 | -130.5271 | -3.6216 | 3.9778 | 0.858 | -4.7048 | -3.1122 | 3.0771 |  | 1.4748 | -1.0853 | 4.0136 | 3.3606 | 3.3451 | 1.0495 | 10.7681 | 14.2828 | 14.8548 | 11.1197 | 0 | -0.003 | 0.0013 | 0.0043 | 0.0009 | -0.0004 | 0.0166 | -0.0089 | 0.0067 | -360.1619 | 17.3905 | -360.4727 | 17.6636 | -360.802 | 18.1317 | -360.8604 | 17.5342 | -352.6352 | 18.721 | -352.669 | 16.834
12:13 | 3173 | 34.9691 | 199.4377 | 445.9731 | 451.076 | -17.758 | -44.0438 | 9.0992 | 5.7365 | -0.3492 | -1.6747 | 1.1068 | -2.1593 | 9.6031 | 2.7393 | 0.6065 | 0.6506 | 0.9553 | 0.7254 | -130.5397 | -3.5771 | 4.03 | 0.8074 | -4.7057 | -3.2187 | 3.1029 |  | 1.4807 | -1.0435 | 4.0124 | 3.3609 | 3.3448 | 1.0498 | 10.7706 | 14.2673 | 14.859 | 11.0771 | -0.0004 | -0.0028 | 0.0004 | 0.0033 | 0.0009 | -0.0008 | 0.0332 | -0.0087 | 0.0109 | -360.1865 | 17.411 | -360.485 | 17.6656 | -360.802 | 18.1317 | -360.8574 | 17.5383 | -352.6413 | 18.7271 | -352.6567 | 16.8361
12:13 | 3174 | 34.9158 | 199.3496 | 446.0217 | 450.9995 | -17.77 | -44.0494 | 9.1156 | 5.6822 | -0.3887 | -1.7614 | 1.1565 | -2.2037 | 9.5157 | 2.7818 | 0.6058 | 0.6493 | 0.9541 | 0.7275 | -130.445 | -3.5722 | 4.0662 | 0.8669 | -4.7131 | -3.2768 | 2.987 |  | 1.5336 | -0.8851 | 4.0132 | 3.3649 | 3.3486 | 1.0509 | 10.7404 | 14.2549 | 14.7798 | 11.0576 | -0.0001 | -0.0024 | 0.0013 | 0.0039 | 0.0004 | -0.0005 | 0.0029 | 0.002 | -0.0168 | -360.1496 | 17.4131 | -360.4512 | 17.6738 | -360.842 | 18.1296 | -360.8912 | 17.5404 | -352.6567 | 18.7189 | -352.6813 | 16.8423
12:13 | 3175 | 35.0534 | 199.4171 | 446.0791 | 451.0991 | -17.5914 | -44.0241 | 9.1022 | 5.6757 | -0.4306 | -1.8195 | 1.1171 | -2.2508 | 9.494 | 2.6569 | 0.6055 | 0.6471 | 0.9572 | 0.7253 | -130.4176 | -3.5502 | 4.0686 | 0.8908 | -4.7583 | -3.2525 | 3.0329 |  | 1.4807 | -1.0407 | 4.0127 | 3.3633 | 3.3505 | 1.05 | 10.7406 | 14.2542 | 14.8092 | 11.071 | -0.0005 | -0.0033 | 0.0004 | 0.0038 | 0.001 | -0.0007 | 0.0073 | -0.015 | 0.0004 | -360.1281 | 17.3925 | -360.4573 | 17.6574 | -360.8112 | 18.1255 | -360.8758 | 17.5465 | -352.6537 | 18.6963 | -352.6598 | 16.834
12:13 | 3176 | 35.0899 | 199.5467 | 446.0757 | 451.1349 | -17.5972 | -43.8814 | 9.1546 | 5.6945 | -0.3732 | -1.8064 | 1.1404 | -2.2463 | 9.4983 | 2.6763 | 0.6043 | 0.6488 | 0.9551 | 0.7257 | -130.4554 | -3.5764 | 4.0536 | 0.896 | -4.695 | -3.1679 | 3.041 |  | 1.4371 | -1.093 | 4.0122 | 3.3624 | 3.3497 | 1.0508 | 10.7475 | 14.2094 | 14.8185 | 11.0713 | 0 | -0.0032 | 0.0008 | 0.0041 | 0.0007 | -0.0004 | 0.0094 | -0.0185 | -0.0149 | -360.1865 | 17.4274 | -360.4881 | 17.6615 | -360.8143 | 18.144 | -360.9066 | 17.5506 | -352.706 | 18.7395 | -352.706 | 16.8361
12:13 | 3177 | 35.0905 | 199.5157 | 446.061 | 451.1546 | -17.6409 | -43.9299 | 9.1574 | 5.6388 | -0.2238 | -1.7 | 1.1856 | -2.317 | 9.5152 | 2.7538 | 0.604 | 0.6476 | 0.9563 | 0.7265 | -130.4776 | -3.6367 | 4.0183 | 0.8955 | -4.7588 | -3.1501 | 3.0147 |  | 1.4439 | -1.0424 | 4.0144 | 3.3652 | 3.3514 | 1.0501 | 10.7267 | 14.2173 | 14.7844 | 11.0569 | 0.0002 | -0.0028 | 0.001 | 0.0043 | 0.0011 | -0.0009 | 0.0291 | -0.0251 | -0.0083 | -360.1773 | 17.4192 | -360.4789 | 17.6677 | -360.802 | 18.0906 | -360.8266 | 17.526 | -352.6444 | 18.7271 | -352.6967 | 16.8443
12:13 | 3178 | 35.0854 | 199.5328 | 446.1518 | 451.1211 | -17.6811 | -44.0415 | 9.0389 | 5.6781 | -0.151 | -1.6793 | 1.2617 | -2.3193 | 9.5516 | 2.6983 | 0.6042 | 0.6534 | 0.9578 | 0.7276 | -130.4152 | -3.6653 | 4.1221 | 0.7868 | -4.691 | -3.1807 | 3.088 |  | 1.5213 | -1.0643 | 4.0115 | 3.3634 | 3.344 | 1.0496 | 10.7301 | 14.2383 | 14.8011 | 11.054 | -0.0003 | -0.0028 | 0.0005 | 0.0037 | 0.0006 | 0 | 0.0229 | 0.0033 | -0.0234 | -360.1527 | 17.4213 | -360.525 | 17.6902 | -360.8543 | 18.142 | -360.9312 | 17.5363 | -352.6752 | 18.7353 | -352.7152 | 16.8525
12:13 | 3179 | 35.0303 | 199.5323 | 446.2356 | 451.1114 | -17.6726 | -43.9967 | 9.0866 | 5.6506 | -0.1546 | -1.6767 | 1.1669 | -2.1901 | 9.6327 | 2.7339 | 0.605 | 0.6518 | 0.9587 | 0.7277 | -130.4178 | -3.7216 | 4.1295 | 0.8555 | -4.643 | -3.2296 | 3.0469 |  | 1.4712 | -1.0045 | 4.014 | 3.3618 | 3.3461 | 1.0499 | 10.744 | 14.2232 | 14.7855 | 11.0739 | 0.0003 | -0.0029 | 0.0006 | 0.0037 | 0.001 | -0.0006 | -0.0065 | 0.0047 | -0.0156 | -360.165 | 17.3802 | -360.4204 | 17.6471 | -360.7989 | 18.1296 | -360.8974 | 17.5527 | -352.6721 | 18.6963 | -352.6413 | 16.8299
12:13 | 3180 | 35.026 | 199.537 | 446.078 | 451.1426 | -17.6678 | -44.0484 | 8.9762 | 5.7038 | -0.2345 | -1.6896 | 1.2028 | -2.2537 | 9.4954 | 2.6736 | 0.6054 | 0.6467 | 0.956 | 0.7264 | -130.4301 | -3.5901 | 4.1365 | 0.934 | -4.7169 | -3.1513 | 3.0798 |  | 1.5012 | -0.9656 | 4.0129 | 3.3624 | 3.3488 | 1.0494 | 10.7695 | 14.2428 | 14.8392 | 11.0706 | 0.0001 | -0.0031 | 0.0011 | 0.004 | 0.0005 | -0.0005 | 0.0345 | 0 | -0.0278 | -360.2204 | 17.4336 | -360.4481 | 17.643 | -360.7989 | 18.105 | -360.885 | 17.5629 | -352.7244 | 18.7292 | -352.6598 | 16.8156
12:13 | 3181 | 35.0888 | 199.6248 | 446.1284 | 451.117 | -17.7429 | -43.9875 | 9.0394 | 5.7079 | -0.1687 | -1.6259 | 1.2656 | -2.2416 | 9.558 | 2.6842 | 0.6062 | 0.6451 | 0.9565 | 0.7275 | -130.401 | -3.7033 | 4.1054 | 0.9384 | -4.7902 | -3.1844 | 3.0997 |  | 1.5244 | -1.0245 | 4.0142 | 3.3663 | 3.3506 | 1.0504 | 10.7913 | 14.2711 | 14.8247 | 11.0969 | 0 | -0.0026 | 0.0009 | 0.0038 | 0.001 | -0.0002 | 0.0156 | -0.0176 | -0.011 | -360.1558 | 17.4315 | -360.4912 | 17.68 | -360.842 | 18.1194 | -360.882 | 17.5527 | -352.7183 | 18.7415 | -352.7367 | 16.8505
12:13 | 3182 | 35.1144 | 199.5152 | 446.0792 | 451.104 | -17.705 | -43.9373 | 9.0542 | 5.6555 | -0.3254 | -1.7557 | 1.2061 | -2.2513 | 9.6546 | 2.7382 | 0.6054 | 0.6428 | 0.9578 | 0.7266 | -130.5402 | -3.6909 | 4.1318 | 0.8649 | -4.8082 | -3.2206 | 3.0742 |  | 1.5102 | -0.9479 | 4.0137 | 3.3643 | 3.3497 | 1.0492 | 10.7302 | 14.2382 | 14.8174 | 11.0428 | -0.0006 | -0.0028 | 0.0005 | 0.0038 | 0.0003 | -0.0011 | 0.0121 | 0.0016 | -0.0038 | -360.1188 | 17.3843 | -360.4481 | 17.6615 | -360.8327 | 18.1235 | -360.8543 | 17.5157 | -352.5952 | 18.6902 | -352.6506 | 16.8505
12:13 | 3183 | 35.1014 | 199.5028 | 446.0891 | 451.037 | -17.6466 | -44.048 | 9.026 | 5.7465 | -0.2462 | -1.6544 | 1.273 | -2.1937 | 9.6226 | 2.755 | 0.6047 | 0.6449 | 0.9567 | 0.7271 | -130.545 | -3.6653 | 4.1129 | 0.8454 | -4.7808 | -3.2375 | 3.0601 |  | 1.5804 | -0.9022 | 4.0124 | 3.3637 | 3.3487 | 1.0502 | 10.7405 | 14.2662 | 14.7777 | 11.0814 | -0.0001 | -0.0026 | 0.0006 | 0.0039 | 0.0003 | -0.0007 | 0.0064 | -0.0027 | -0.0108 | -360.1835 | 17.3905 | -360.4389 | 17.6697 | -360.842 | 18.1604 | -360.9558 | 17.5568 | -352.6721 | 18.7087 | -352.6506 | 16.8381
12:13 | 3184 | 35.1657 | 199.5793 | 446.1342 | 451.0887 | -17.6671 | -44.1658 | 8.9256 | 5.7292 | -0.2847 | -1.6077 | 1.1854 | -2.2147 | 9.6119 | 2.7574 | 0.6057 | 0.6466 | 0.9573 | 0.7251 | -130.5114 | -3.6037 | 4.172 | 1.0401 | -4.7575 | -3.1796 | 3.0038 |  | 1.4645 | -0.9323 | 4.0134 | 3.3674 | 3.3475 | 1.0507 | 10.7464 | 14.2081 | 14.7871 | 11.0648 | 0.0005 | -0.003 | 0.0008 | 0.0038 | 0.001 | -0.0009 | 0.0279 | -0.0066 | -0.0075 | -360.165 | 17.3946 | -360.4173 | 17.6471 | -360.7866 | 18.1255 | -360.8974 | 17.5547 | -352.6967 | 18.7189 | -352.6598 | 16.8279
12:13 | 3185 | 35.1178 | 199.5074 | 446.0303 | 451.0574 | -17.5786 | -44.0798 | 8.988 | 5.7267 | -0.202 | -1.6253 | 1.1791 | -2.2313 | 9.5144 | 2.6399 | 0.6046 | 0.6484 | 0.9582 | 0.7262 | -130.5001 | -3.5364 | 4.1514 | 1.004 | -4.7839 | -3.3014 | 2.9904 |  | 1.5326 | -0.9771 | 4.0117 | 3.3632 | 3.3477 | 1.0488 | 10.7118 | 14.2194 | 14.7561 | 11.0714 | -0.0002 | -0.003 | 0.0002 | 0.0034 | 0.0005 | -0.0003 | 0.0001 | -0.0137 | -0.0299 | -360.205 | 17.411 | -360.4973 | 17.6594 | -360.8174 | 18.1071 | -360.842 | 17.5301 | -352.6598 | 18.7374 | -352.7029 | 16.8381
12:13 | 3186 | 35.1064 | 199.5571 | 446.1913 | 451.1484 | -17.5238 | -43.9837 | 9.1088 | 5.7216 | -0.2986 | -1.6578 | 1.0643 | -2.2887 | 9.4544 | 2.6393 | 0.6047 | 0.6483 | 0.9559 | 0.7264 | -130.4775 | -3.5157 | 4.1837 | 1.0454 | -4.8 | -3.2543 | 3.0492 |  | 1.6239 | -0.9581 | 4.015 | 3.3646 | 3.3476 | 1.05 | 10.7578 | 14.2492 | 14.7972 | 11.0633 | 0.0001 | -0.002 | 0.0009 | 0.0036 | 0.0014 | -0.0003 | 0.0117 | 0.0092 | -0.008 | -360.1527 | 17.411 | -360.5066 | 17.7087 | -360.882 | 18.1337 | -360.8666 | 17.5178 | -352.6537 | 18.7333 | -352.7183 | 16.8833
12:13 | 3187 | 35.0623 | 199.527 | 446.1869 | 451.1075 | -17.5543 | -43.9809 | 9.1109 | 5.7078 | -0.3021 | -1.5128 | 1.2273 | -2.2357 | 9.5488 | 2.6363 | 0.606 | 0.6507 | 0.9573 | 0.7265 | -130.5244 | -3.4997 | 4.186 | 1.014 | -4.8341 | -3.3243 | 2.996 |  | 1.5856 | -0.924 | 4.0128 | 3.3662 | 3.3475 | 1.0498 | 10.7637 | 14.237 | 14.7698 | 11.0533 | -0.0001 | -0.003 | 0.0006 | 0.0036 | 0.0006 | -0.0002 | 0.004 | -0.0063 | -0.0148 | -360.125 | 17.3761 | -360.4358 | 17.6512 | -360.8235 | 18.1214 | -360.882 | 17.5198 | -352.6013 | 18.7025 | -352.6567 | 16.8361
12:13 | 3188 | 35.1428 | 199.4901 | 446.1616 | 451.1769 | -17.5961 | -44.0052 | 9.0448 | 5.5974 | -0.3553 | -1.7498 | 1.2124 | -2.1884 | 9.6106 | 2.664 | 0.6066 | 0.648 | 0.9542 | 0.7276 | -130.5853 | -3.5114 | 4.0766 | 0.9595 | -4.8063 | -3.1172 | 3.0713 |  | 1.4452 | -1.0289 | 4.013 | 3.3656 | 3.3516 | 1.0516 | 10.7487 | 14.2163 | 14.8188 | 11.0381 | 0.0002 | -0.003 | 0.001 | 0.004 | 0.0013 | -0.0004 | -0.0028 | -0.016 | -0.0118 | -360.1742 | 17.4233 | -360.4666 | 17.6718 | -360.7958 | 18.1276 | -360.922 | 17.5629 | -352.6998 | 18.7292 | -352.6629 | 16.8279
12:13 | 3189 | 35.0994 | 199.5045 | 446.1665 | 451.1595 | -17.5854 | -43.8888 | 9.1215 | 5.5014 | -0.3213 | -1.7649 | 1.2045 | -2.2072 | 9.5978 | 2.7123 | 0.606 | 0.6464 | 0.9544 | 0.7279 | -130.5595 | -3.581 | 4.028 | 0.801 | -4.8344 | -3.2045 | 3.0817 |  | 1.5006 | -0.9518 | 4.0124 | 3.363 | 3.3484 | 1.0506 | 10.7625 | 14.236 | 14.7984 | 11.0865 | 0.0001 | -0.0031 | 0.0006 | 0.0034 | 0.0001 | -0.0006 | 0.0035 | -0.0113 | -0.0143 | -360.205 | 17.4274 | -360.4758 | 17.6615 | -360.7989 | 18.1091 | -360.8758 | 17.5568 | -352.7183 | 18.7477 | -352.706 | 16.8423
12:13 | 3190 | 35.098 | 199.5625 | 446.2255 | 451.2127 | -17.6471 | -43.8689 | 9.0663 | 5.5392 | -0.3726 | -1.803 | 1.2178 | -2.1338 | 9.6214 | 2.6982 | 0.6053 | 0.6487 | 0.9533 | 0.7263 | -130.4444 | -3.5081 | 4.1285 | 0.8824 | -4.759 | -3.1633 | 3.01 |  | 1.4579 | -1.0083 | 4.0135 | 3.3662 | 3.3501 | 1.0499 | 10.721 | 14.2518 | 14.8181 | 11.0457 | -0.0006 | -0.0028 | 0.0008 | 0.0039 | 0.0008 | -0.0006 | 0.0187 | 0.0035 | -0.0246 | -360.1773 | 17.3946 | -360.4912 | 17.6738 | -360.8297 | 18.1009 | -360.8512 | 17.5239 | -352.6383 | 18.7169 | -352.6906 | 16.8505
12:13 | 3191 | 35.1266 | 199.545 | 446.1818 | 451.1181 | -17.5913 | -43.8665 | 9.1048 | 5.5371 | -0.3237 | -1.6937 | 1.1567 | -2.1692 | 9.631 | 2.6281 | 0.6058 | 0.6453 | 0.9564 | 0.7269 | -130.4981 | -3.5907 | 4.138 | 0.7016 | -4.7753 | -3.2477 | 2.9719 |  | 1.5543 | -0.9705 | 4.0123 | 3.3642 | 3.3512 | 1.0517 | 10.7405 | 14.2547 | 14.7545 | 11.0814 | 0 | -0.0029 | 0.0009 | 0.004 | 0.0009 | -0.0004 | -0.0007 | -0.0083 | -0.0028 | -360.1927 | 17.411 | -360.4727 | 17.68 | -360.885 | 18.1625 | -360.922 | 17.5465 | -352.6444 | 18.7128 | -352.6783 | 16.8587
12:13 | 3192 | 35.1323 | 199.5012 | 446.2583 | 451.0106 | -17.4984 | -43.8326 | 9.105 | 5.5165 | -0.427 | -1.765 | 1.1483 | -2.2623 | 9.6142 | 2.601 | 0.6045 | 0.6497 | 0.9543 | 0.7271 | -130.455 | -3.5441 | 4.1904 | 0.9005 | -4.7835 | -3.2305 | 3.0387 |  | 1.5292 | -0.9461 | 4.013 | 3.3638 | 3.3484 | 1.0503 | 10.7406 | 14.237 | 14.8392 | 11.0648 | -0.0004 | -0.0033 | 0.0006 | 0.0038 | 0.0008 | -0.0005 | -0.0008 | 0.0017 | -0.0017 | -360.1742 | 17.3987 | -360.4419 | 17.6492 | -360.7773 | 18.1235 | -360.8666 | 17.5424 | -352.6598 | 18.721 | -352.6567 | 16.832
12:13 | 3193 | 35.1236 | 199.6025 | 446.2615 | 451.1013 | -17.6015 | -43.8621 | 9.0648 | 5.5741 | -0.3489 | -1.6012 | 1.192 | -2.1291 | 9.6159 | 2.7016 | 0.605 | 0.6493 | 0.9553 | 0.7284 | -130.4708 | -3.48 | 4.2784 | 0.8357 | -4.7679 | -3.2098 | 3.0603 |  | 1.548 | -0.9888 | 4.0123 | 3.3644 | 3.3487 | 1.0491 | 10.7106 | 14.201 | 14.7847 | 11.041 | 0 | -0.0029 | 0.0003 | 0.0039 | 0.0008 | -0.0009 | 0.018 | 0.0024 | -0.0083 | -360.1342 | 17.4048 | -360.4942 | 17.6677 | -360.7958 | 18.1071 | -360.8389 | 17.5239 | -352.6106 | 18.723 | -352.6875 | 16.8464
12:13 | 3194 | 35.1752 | 199.621 | 446.2467 | 451.1985 | -17.6531 | -43.8421 | 9.121 | 5.6021 | -0.2896 | -1.552 | 1.2359 | -2.1572 | 9.6076 | 2.74 | 0.6058 | 0.6496 | 0.9607 | 0.729 | -130.5362 | -3.5859 | 4.1492 | 0.7103 | -4.7577 | -3.2007 | 3.0226 |  | 1.4858 | -0.9788 | 4.0142 | 3.3641 | 3.3481 | 1.0506 | 10.7832 | 14.263 | 14.8625 | 11.089 | -0.0002 | -0.0029 | 0.0005 | 0.0035 | 0.0005 | -0.0005 | 0.019 | -0.0014 | -0.0095 | -360.1804 | 17.4151 | -360.4912 | 17.6923 | -360.8789 | 18.1399 | -360.882 | 17.5506 | -352.6475 | 18.7271 | -352.7275 | 16.8566
12:13 | 3195 | 35.1606 | 199.642 | 446.255 | 451.188 | -17.6381 | -43.8124 | 9.0744 | 5.5877 | -0.3434 | -1.6093 | 1.2227 | -2.083 | 9.6116 | 2.7718 | 0.6055 | 0.647 | 0.9586 | 0.728 | -130.5627 | -3.4971 | 4.2041 | 0.8371 | -4.7619 | -3.2325 | 3.0382 |  | 1.5011 | -1.0262 | 4.0127 | 3.3658 | 3.3504 | 1.0493 | 10.7486 | 14.2742 | 14.8546 | 11.0955 | -0.0003 | -0.0025 | 0.0007 | 0.0039 | 0.0008 | -0.0008 | 0.0068 | -0.0072 | -0.0157 | -360.1619 | 17.3987 | -360.4696 | 17.6718 | -360.802 | 18.1337 | -360.882 | 17.5465 | -352.666 | 18.7169 | -352.669 | 16.8587
12:13 | 3196 | 35.2698 | 199.6253 | 446.3157 | 451.1871 | -17.6722 | -43.9816 | 9.0086 | 5.6099 | -0.2951 | -1.5303 | 1.2587 | -2.1001 | 9.6626 | 2.6811 | 0.6035 | 0.6461 | 0.9559 | 0.726 | -130.5485 | -3.4373 | 4.2258 | 0.8431 | -4.7668 | -3.1651 | 3.0498 |  | 1.5114 | -0.9552 | 4.0121 | 3.3628 | 3.3512 | 1.0492 | 10.7544 | 14.2684 | 14.7909 | 11.0666 | -0.0001 | -0.0033 | 0.0011 | 0.0043 | 0.0008 | 0 | 0.0116 | -0.0006 | -0.0204 | -360.1404 | 17.3946 | -360.4358 | 17.6533 | -360.8235 | 18.1173 | -360.8481 | 17.5342 | -352.5921 | 18.7025 | -352.6567 | 16.8279
12:13 | 3197 | 35.2014 | 199.5172 | 446.258 | 451.1445 | -17.6773 | -44.0337 | 9.0004 | 5.5674 | -0.3011 | -1.5934 | 1.1878 | -1.9804 | 9.6445 | 2.6967 | 0.6055 | 0.6482 | 0.9561 | 0.7265 | -130.5101 | -3.3685 | 4.2319 | 0.9907 | -4.6743 | -3.1829 | 3.1347 |  | 1.4872 | -0.8332 | 4.0131 | 3.3679 | 3.3483 | 1.0485 | 10.7624 | 14.2653 | 14.8247 | 11.1316 | 0.0004 | -0.003 | 0.0006 | 0.0035 | 0.001 | -0.0005 | 0.0021 | 0.0027 | -0.0322 | -360.2204 | 17.4254 | -360.5004 | 17.6841 | -360.8112 | 18.1358 | -360.8758 | 17.5547 | -352.6783 | 18.7271 | -352.6629 | 16.8464
12:13 | 3198 | 35.21 | 199.5033 | 446.2213 | 451.1548 | -17.635 | -44.0444 | 8.98 | 5.616 | -0.3237 | -1.5011 | 1.1538 | -1.9758 | 9.7463 | 2.7611 | 0.6053 | 0.6499 | 0.9573 | 0.7275 | -130.435 | -3.4345 | 4.2887 | 1.0541 | -4.6214 | -3.1951 | 3.2231 |  | 1.5719 | -0.9638 | 4.0131 | 3.3654 | 3.3466 | 1.0493 | 10.7533 | 14.273 | 14.7838 | 11.1002 | -0.0003 | -0.0023 | 0.0002 | 0.0036 | 0.0006 | 0 | 0.0141 | -0.0141 | -0.0121 | -360.1804 | 17.4233 | -360.5035 | 17.6882 | -360.842 | 18.1379 | -360.8881 | 17.5445 | -352.6998 | 18.7353 | -352.7121 | 16.8628
12:13 | 3199 | 35.1737 | 199.5695 | 446.234 | 451.1707 | -17.7953 | -44.1317 | 8.8432 | 5.6939 | -0.2338 | -1.4558 | 1.2149 | -2.0079 | 9.6672 | 2.7011 | 0.6053 | 0.646 | 0.9526 | 0.7276 | -130.4217 | -3.4564 | 4.1692 | 0.8595 | -4.6939 | -3.1738 | 3.1158 |  | 1.5583 | -0.9635 | 4.0122 | 3.3651 | 3.3462 | 1.0497 | 10.7174 | 14.2487 | 14.7766 | 11.0587 | -0.0004 | -0.0029 | 0.0008 | 0.0041 | 0.0012 | -0.0005 | 0.0086 | -0.0079 | -0.0146 | -360.1435 | 17.4069 | -360.4727 | 17.6553 | -360.8174 | 18.1194 | -360.842 | 17.5157 | -352.5952 | 18.7087 | -352.7121 | 16.8423
12:13 | 3200 | 35.2237 | 199.5745 | 446.3429 | 451.2332 | -17.7854 | -44.0653 | 8.8152 | 5.6314 | -0.178 | -1.5015 | 1.2065 | -2.023 | 9.6704 | 2.7818 | 0.6044 | 0.6507 | 0.954 | 0.7269 | -130.4379 | -3.4992 | 4.1967 | 0.8935 | -4.7549 | -3.179 | 3.0852 |  | 1.5083 | -0.925 | 4.0124 | 3.3631 | 3.3489 | 1.0504 | 10.7289 | 14.2432 | 14.7787 | 11.0522 | 0 | -0.0029 | 0.0005 | 0.004 | 0.0009 | -0.0003 | -0.0003 | -0.0048 | -0.0143 | -360.1804 | 17.3925 | -360.4389 | 17.6574 | -360.842 | 18.1317 | -360.885 | 17.5486 | -352.6813 | 18.7087 | -352.6506 | 16.834
12:13 | 3201 | 35.2123 | 199.6072 | 446.3716 | 451.2443 | -17.715 | -44.029 | 8.9396 | 5.6605 | -0.1213 | -1.4502 | 1.1758 | -2.0676 | 9.6749 | 2.8232 | 0.6065 | 0.649 | 0.9562 | 0.7261 | -130.4332 | -3.5473 | 4.2666 | 0.887 | -4.821 | -3.136 | 3.1477 |  | 1.5352 | -0.8501 | 4.0138 | 3.3669 | 3.3469 | 1.0517 | 10.7152 | 14.2462 | 14.767 | 11.0396 | 0 | -0.0032 | 0.0006 | 0.0036 | 0.0009 | -0.0004 | 0.009 | -0.0107 | -0.0151 | -360.2081 | 17.4377 | -360.5004 | 17.6759 | -360.7866 | 18.1235 | -360.9127 | 17.5609 | -352.6967 | 18.7497 | -352.7183 | 16.8381
12:13 | 3202 | 35.2433 | 199.5976 | 446.3056 | 451.2029 | -17.664 | -44.1449 | 8.9339 | 5.6913 | -0.0995 | -1.4171 | 1.2456 | -2.0291 | 9.6991 | 2.8221 | 0.6051 | 0.6475 | 0.9561 | 0.7265 | -130.4143 | -3.5107 | 4.3091 | 0.8774 | -4.8154 | -3.1752 | 3.0964 |  | 1.4471 | -0.9295 | 4.0126 | 3.3651 | 3.3483 | 1.0503 | 10.744 | 14.2348 | 14.7855 | 11.045 | -0.0003 | -0.0027 | 0.0013 | 0.0041 | 0.001 | -0.0005 | 0.007 | -0.0011 | 0.0019 | -360.1773 | 17.4069 | -360.4542 | 17.6533 | -360.7804 | 18.0906 | -360.8174 | 17.5383 | -352.6967 | 18.7312 | -352.6783 | 16.8443
12:13 | 3203 | 35.2536 | 199.6091 | 446.3999 | 451.1925 | -17.7258 | -44.1056 | 8.9401 | 5.6068 | -0.2635 | -1.492 | 1.1791 | -2.0291 | 9.7209 | 2.8358 | 0.6066 | 0.6515 | 0.9544 | 0.7282 | -130.3944 | -3.4584 | 4.2501 | 0.9577 | -4.8119 | -3.1307 | 3.1452 |  | 1.4478 | -1.008 | 4.0115 | 3.3694 | 3.3498 | 1.0512 | 10.7255 | 14.2509 | 14.7841 | 11.0728 | 0 | -0.0027 | 0.0011 | 0.0039 | 0.0003 | -0.0002 | 0.0101 | -0.0036 | -0.0181 | -360.1404 | 17.4069 | -360.5035 | 17.6759 | -360.8389 | 18.1255 | -360.8789 | 17.528 | -352.6537 | 18.721 | -352.7029 | 16.8525
12:13 | 3204 | 35.2887 | 199.7489 | 446.3786 | 451.2431 | -17.7281 | -44.223 | 8.9002 | 5.6614 | -0.2048 | -1.4436 | 1.2049 | -2.0022 | 9.818 | 2.8084 | 0.606 | 0.6485 | 0.9553 | 0.7265 | -130.3949 | -3.4539 | 4.2162 | 0.9725 | -4.7808 | -3.1093 | 3.1632 |  | 1.4681 | -0.9213 | 4.0129 | 3.3674 | 3.3476 | 1.0508 | 10.7452 | 14.2532 | 14.7973 | 11.0638 | -0.0001 | -0.0029 | 0.0012 | 0.0038 | 0.001 | -0.0008 | 0.0233 | -0.008 | -0.0057 | -360.1711 | 17.3946 | -360.4358 | 17.6697 | -360.8574 | 18.1563 | -360.922 | 17.5527 | -352.6752 | 18.723 | -352.669 | 16.8464
12:13 | 3205 | 35.2972 | 199.7404 | 446.3949 | 451.2194 | -17.7709 | -44.2092 | 9.0058 | 5.6654 | -0.1805 | -1.4456 | 1.241 | -1.9318 | 9.8277 | 2.7982 | 0.6063 | 0.6482 | 0.9537 | 0.7262 | -130.4533 | -3.5419 | 4.279 | 0.9349 | -4.857 | -3.0842 | 3.158 |  | 1.5189 | -0.9475 | 4.0122 | 3.3652 | 3.3501 | 1.0496 | 10.7648 | 14.2501 | 14.808 | 11.0825 | 0.0003 | -0.0029 | 0.001 | 0.0039 | 0.0009 | 0 | 0.0061 | -0.0058 | -0.0123 | -360.1773 | 17.4007 | -360.3989 | 17.6225 | -360.7866 | 18.1235 | -360.9035 | 17.5527 | -352.7029 | 18.7066 | -352.6413 | 16.8135
12:13 | 3206 | 35.2438 | 199.6847 | 446.4249 | 451.1907 | -17.7086 | -44.3224 | 9.0913 | 5.6534 | -0.0745 | -1.435 | 1.2257 | -1.9292 | 9.7395 | 2.7178 | 0.6045 | 0.6479 | 0.956 | 0.7271 | -130.4764 | -3.4707 | 4.3436 | 0.9933 | -4.7348 | -3.1622 | 3.1704 |  | 1.6213 | -0.8557 | 4.0119 | 3.365 | 3.3515 | 1.0498 | 10.7671 | 14.2523 | 14.7981 | 11.0908 | 0.0001 | -0.0028 | 0.0007 | 0.0037 | 0.0012 | -0.0006 | 0.0247 | -0.0152 | -0.0192 | -360.2019 | 17.4192 | -360.4912 | 17.6533 | -360.7866 | 18.1358 | -360.8666 | 17.528 | -352.6844 | 18.721 | -352.6752 | 16.8299
12:13 | 3207 | 35.2685 | 199.7317 | 446.3699 | 451.1524 | -17.7365 | -44.2781 | 9.0899 | 5.7474 | -0.0659 | -1.4591 | 1.3318 | -1.9926 | 9.7468 | 2.7518 | 0.6054 | 0.6489 | 0.9578 | 0.7271 | -130.5232 | -3.5033 | 4.2749 | 0.9191 | -4.7296 | -3.0524 | 3.1886 |  | 1.5241 | -0.9611 | 4.0133 | 3.364 | 3.3524 | 1.0497 | 10.7406 | 14.2312 | 14.8161 | 11.036 | -0.0003 | -0.0024 | 0.0009 | 0.004 | 0.0004 | -0.0007 | 0.0106 | -0.017 | 0.0051 | -360.1404 | 17.4233 | -360.5066 | 17.719 | -360.8881 | 18.1563 | -360.8512 | 17.5383 | -352.6598 | 18.7292 | -352.7429 | 16.8772
12:13 | 3208 | 35.2855 | 199.7619 | 446.4552 | 451.2714 | -17.5668 | -44.1115 | 9.1277 | 5.7027 | -0.1373 | -1.5221 | 1.2794 | -1.9918 | 9.7657 | 2.6279 | 0.6037 | 0.6489 | 0.9601 | 0.7272 | -130.4836 | -3.4167 | 4.2683 | 0.9268 | -4.7527 | -3.1344 | 3.1537 |  | 1.4708 | -0.9378 | 4.0119 | 3.3643 | 3.3502 | 1.0515 | 10.7313 | 14.2394 | 14.7957 | 11.0728 | -0.0002 | -0.0027 | 0.0005 | 0.0036 | 0.0007 | -0.0007 | 0.0145 | -0.0098 | -0.0067 | -360.1004 | 17.3782 | -360.4235 | 17.6738 | -360.8358 | 18.1625 | -360.8727 | 17.526 | -352.6075 | 18.6861 | -352.6383 | 16.8423
12:13 | 3209 | 35.2229 | 199.779 | 446.4903 | 451.263 | -17.5987 | -44.0136 | 9.0553 | 5.731 | -0.1421 | -1.5169 | 1.2675 | -1.9484 | 9.6984 | 2.6352 | 0.6041 | 0.6496 | 0.9608 | 0.7283 | -130.4511 | -3.5285 | 4.2988 | 0.9566 | -4.7755 | -3.17 | 3.1682 |  | 1.4567 | -0.991 | 4.0122 | 3.3654 | 3.3499 | 1.0501 | 10.7291 | 14.2137 | 14.7745 | 11.0652 | 0 | -0.0032 | 0.0005 | 0.0037 | 0.0006 | -0.0003 | 0.0216 | -0.0083 | 0.0056 | -360.2019 | 17.4048 | -360.445 | 17.6594 | -360.8266 | 18.1666 | -360.9066 | 17.5506 | -352.6844 | 18.721 | -352.6567 | 16.832
12:13 | 3210 | 35.1841 | 199.6897 | 446.4706 | 451.1942 | -17.546 | -43.9504 | 9.1582 | 5.7848 | -0.1381 | -1.4737 | 1.2972 | -2.0615 | 9.6938 | 2.6558 | 0.6052 | 0.6508 | 0.9589 | 0.7268 | -130.3902 | -3.3677 | 4.3305 | 0.9571 | -4.6714 | -3.1486 | 3.1818 |  | 1.4888 | -1.0268 | 4.0121 | 3.3639 | 3.3477 | 1.0509 | 10.722 | 14.2533 | 14.81 | 11.0518 | -0.0002 | -0.0032 | 0.0012 | 0.0039 | 0.0009 | -0.0008 | 0.0069 | -0.0016 | -0.0152 | -360.2142 | 17.4439 | -360.5004 | 17.6738 | -360.8204 | 18.1563 | -360.9035 | 17.5691 | -352.6998 | 18.7436 | -352.7152 | 16.8381
12:13 | 3211 | 35.2257 | 199.6867 | 446.3459 | 451.2714 | -17.5876 | -43.9876 | 9.0383 | 5.7727 | -0.1725 | -1.483 | 1.4444 | -2.1039 | 9.5582 | 2.5308 | 0.6055 | 0.6474 | 0.9587 | 0.727 | -130.298 | -3.4061 | 4.288 | 1.0473 | -4.5968 | -2.9794 | 3.2499 |  | 1.4348 | -0.9746 | 4.011 | 3.3644 | 3.3475 | 1.0509 | 10.7475 | 14.2383 | 14.8069 | 11.0655 | -0.0003 | -0.0028 | 0.0009 | 0.0037 | 0.0007 | -0.0002 | 0.0039 | -0.0088 | -0.0081 | -360.1619 | 17.4131 | -360.4912 | 17.6738 | -360.8174 | 18.1358 | -360.8204 | 17.5013 | -352.6537 | 18.7333 | -352.709 | 16.8566
12:13 | 3212 | 35.2857 | 199.7671 | 446.51 | 451.2618 | -17.4623 | -43.9424 | 9.043 | 5.8208 | -0.0788 | -1.4593 | 1.5499 | -2.0397 | 9.7375 | 2.6821 | 0.6043 | 0.6484 | 0.96 | 0.7283 | -130.3404 | -3.46 | 4.2706 | 1.0688 | -4.6012 | -2.9625 | 3.3395 |  | 1.5242 | -0.9951 | 4.0142 | 3.3653 | 3.347 | 1.0491 | 10.7336 | 14.236 | 14.8042 | 11.0403 | -0.0003 | -0.0027 | 0.001 | 0.0039 | 0.0007 | -0.0002 | 0.0083 | -0.0057 | -0.0143 | -360.165 | 17.4151 | -360.5189 | 17.6902 | -360.8481 | 18.1522 | -360.8635 | 17.5137 | -352.629 | 18.7189 | -352.6937 | 16.8484
12:13 | 3213 | 35.2658 | 199.6951 | 446.3741 | 451.2179 | -17.4734 | -43.9602 | 9.1367 | 5.7776 | -0.1217 | -1.5372 | 1.5873 | -2.0679 | 9.6815 | 2.6393 | 0.6057 | 0.6475 | 0.9569 | 0.7275 | -130.3309 | -3.4275 | 4.2797 | 1.0367 | -4.6068 | -3.0103 | 3.3209 |  | 1.4764 | -0.9101 | 4.0118 | 3.3646 | 3.3492 | 1.0501 | 10.7348 | 14.2429 | 14.7998 | 11.076 | 0.0002 | -0.0033 | 0.001 | 0.0047 | 0.0008 | -0.0002 | 0.0137 | -0.0071 | 0.0049 | -360.1835 | 17.4028 | -360.4635 | 17.6759 | -360.842 | 18.1851 | -360.8974 | 17.5465 | -352.6567 | 18.7148 | -352.6875 | 16.8443
12:13 | 3214 | 35.2406 | 199.6663 | 446.3471 | 451.2434 | -17.5365 | -43.975 | 9.0773 | 5.8034 | -0.106 | -1.5104 | 1.4572 | -2.0809 | 9.7083 | 2.6074 | 0.6065 | 0.6481 | 0.9559 | 0.7276 | -130.307 | -3.3598 | 4.2553 | 1.0324 | -4.5992 | -3.1001 | 3.3001 |  | 1.5328 | -0.9224 | 4.0114 | 3.3607 | 3.3467 | 1.0505 | 10.744 | 14.2232 | 14.8028 | 11.0508 | 0 | -0.003 | 0.0005 | 0.0036 | 0.0003 | -0.0004 | 0.0103 | -0.0067 | -0.0071 | -360.1435 | 17.3925 | -360.4173 | 17.6286 | -360.762 | 18.1379 | -360.885 | 17.5383 | -352.7121 | 18.7169 | -352.6444 | 16.8176
12:13 | 3215 | 35.2803 | 199.7081 | 446.4526 | 451.1647 | -17.4732 | -43.8962 | 9.1415 | 5.763 | -0.1629 | -1.6071 | 1.4609 | -2.1008 | 9.6912 | 2.5519 | 0.6065 | 0.6458 | 0.9589 | 0.7285 | -130.2889 | -3.4167 | 4.2479 | 1.0709 | -4.5984 | -3.15 | 3.2502 |  | 1.477 | -1.0533 | 4.0119 | 3.3628 | 3.3479 | 1.0507 | 10.7602 | 14.2395 | 14.7678 | 11.0782 | 0 | -0.0028 | 0.0007 | 0.0038 | 0.0009 | -0.001 | 0.003 | -0.007 | -0.0123 | -360.205 | 17.4356 | -360.4881 | 17.6553 | -360.8204 | 18.1379 | -360.8604 | 17.5424 | -352.7213 | 18.7436 | -352.6937 | 16.8258
12:13 | 3216 | 35.3844 | 199.7812 | 446.346 | 451.2554 | -17.4611 | -43.8467 | 9.0472 | 5.7513 | -0.1177 | -1.6154 | 1.4923 | -2.0473 | 9.6916 | 2.6475 | 0.6056 | 0.644 | 0.9534 | 0.7284 | -130.3183 | -3.415 | 4.2339 | 1.0582 | -4.6252 | -3.1553 | 3.24 |  | 1.4725 | -1.0416 | 4.0122 | 3.3633 | 3.3469 | 1.0509 | 10.7394 | 14.2302 | 14.8216 | 11.0461 | -0.0007 | -0.0028 | 0.001 | 0.004 | 0.0008 | -0.0002 | 0.0105 | -0.0063 | -0.0072 | -360.2111 | 17.4233 | -360.5004 | 17.6841 | -360.8481 | 18.1543 | -360.8697 | 17.5465 | -352.7121 | 18.7374 | -352.7152 | 16.8587
12:13 | 3217 | 35.4241 | 199.7565 | 446.4058 | 451.2431 | -17.438 | -43.8944 | 9.2247 | 5.7343 | -0.0731 | -1.6554 | 1.445 | -2.1524 | 9.6591 | 2.6522 | 0.6048 | 0.6455 | 0.957 | 0.7271 | -130.3504 | -3.4102 | 4.1511 | 0.9534 | -4.6303 | -3.0505 | 3.2764 |  | 1.5498 | -1.021 | 4.0125 | 3.3634 | 3.3486 | 1.0512 | 10.7232 | 14.2197 | 14.7987 | 11.0706 | 0.0002 | -0.0029 | 0.0006 | 0.0037 | 0.0013 | -0.0008 | 0.0103 | 0.0027 | 0.0094 | -360.1404 | 17.3884 | -360.4542 | 17.6574 | -360.802 | 18.1604 | -360.8574 | 17.4993 | -352.6321 | 18.7148 | -352.7029 | 16.8464
12:13 | 3218 | 35.4038 | 199.7532 | 446.4066 | 451.2837 | -17.5982 | -44.0709 | 9.0952 | 5.7513 | -0.0506 | -1.5863 | 1.4846 | -2.1632 | 9.6904 | 2.6062 | 0.6054 | 0.6429 | 0.9567 | 0.7277 | -130.4129 | -3.5183 | 4.1228 | 1.0407 | -4.6656 | -3.075 | 3.2584 |  | 1.4625 | -1.0393 | 4.0104 | 3.3634 | 3.3467 | 1.0499 | 10.7382 | 14.2521 | 14.7855 | 11.0392 | 0.0001 | -0.0031 | 0.0012 | 0.0045 | 0.0007 | 0 | 0.0072 | -0.0085 | 0.0168 | -360.1681 | 17.3925 | -360.4266 | 17.6553 | -360.8358 | 18.1728 | -360.8881 | 17.5198 | -352.6475 | 18.7045 | -352.6413 | 16.8217
12:13 | 3219 | 35.363 | 199.7337 | 446.3127 | 451.184 | -17.6427 | -44.0031 | 9.0039 | 5.7815 | -0.0364 | -1.5608 | 1.477 | -2.1368 | 9.7219 | 2.6514 | 0.6051 | 0.648 | 0.9549 | 0.7284 | -130.4445 | -3.5547 | 4.1572 | 1.0543 | -4.7514 | -3.0569 | 3.1988 |  | 1.4637 | -0.9148 | 4.0119 | 3.3631 | 3.3518 | 1.0502 | 10.7509 | 14.2478 | 14.8179 | 11.08 | -0.0001 | -0.003 | 0.001 | 0.004 | 0.0011 | -0.0002 | 0.0004 | -0.0157 | -0.0041 | -360.2173 | 17.4151 | -360.4727 | 17.6636 | -360.8327 | 18.1748 | -360.9281 | 17.5527 | -352.7121 | 18.7271 | -352.7029 | 16.8505
12:13 | 3220 | 35.3104 | 199.6683 | 446.3845 | 451.2096 | -17.6796 | -44.089 | 8.975 | 5.7778 | -0.1063 | -1.5166 | 1.5179 | -2.1311 | 9.7236 | 2.6392 | 0.6062 | 0.6466 | 0.9555 | 0.7277 | -130.4418 | -3.537 | 4.2234 | 1.0514 | -4.7166 | -3.1229 | 3.2532 |  | 1.5231 | -0.9287 | 4.0113 | 3.3631 | 3.3479 | 1.051 | 10.7614 | 14.2463 | 14.8202 | 11.0854 | 0 | -0.0027 | 0.0002 | 0.0034 | 0.0007 | -0.0006 | 0.0166 | -0.01 | -0.0045 | -360.1896 | 17.4192 | -360.4635 | 17.6636 | -360.8143 | 18.1337 | -360.8604 | 17.5404 | -352.6752 | 18.7415 | -352.706 | 16.8423
12:13 | 3221 | 35.2897 | 199.6817 | 446.3193 | 451.2268 | -17.6976 | -44.1099 | 8.9734 | 5.765 | -0.0353 | -1.3295 | 1.5294 | -2.0833 | 9.7686 | 2.6596 | 0.6057 | 0.6459 | 0.9539 | 0.7259 | -130.3982 | -3.4486 | 4.2571 | 0.9438 | -4.7137 | -3.0952 | 3.1975 |  | 1.442 | -0.9435 | 4.011 | 3.3618 | 3.3503 | 1.0509 | 10.7659 | 14.2397 | 14.8152 | 11.072 | -0.0002 | -0.0026 | 0.0005 | 0.0037 | 0.0011 | 0.0001 | 0.0207 | -0.0068 | -0.0102 | -360.1065 | 17.4028 | -360.4635 | 17.6636 | -360.8174 | 18.1461 | -360.8635 | 17.5034 | -352.6044 | 18.7292 | -352.6321 | 16.832
12:13 | 3222 | 35.3183 | 199.6735 | 446.4193 | 451.2454 | -17.6538 | -43.9858 | 9.1084 | 5.8295 | -0.1325 | -1.4046 | 1.4542 | -2.0554 | 9.7676 | 2.6432 | 0.6059 | 0.6504 | 0.9558 | 0.7258 | -130.3174 | -3.4773 | 4.2742 | 0.9465 | -4.6268 | -2.9935 | 3.2033 |  | 1.6041 | -0.8614 | 4.0119 | 3.3643 | 3.3459 | 1.0507 | 10.766 | 14.2627 | 14.8488 | 11.0897 | 0.0003 | -0.003 | 0.0003 | 0.0033 | 0.0006 | -0.0006 | 0.0182 | -0.0128 | -0.0148 | -360.1681 | 17.411 | -360.4881 | 17.68 | -360.8543 | 18.1645 | -360.8697 | 17.5321 | -352.6844 | 18.7292 | -352.669 | 16.8464
12:13 | 3223 | 35.3521 | 199.7221 | 446.4529 | 451.1641 | -17.5723 | -43.9898 | 9.1034 | 5.833 | -0.142 | -1.3673 | 1.5486 | -2.038 | 9.8255 | 2.7759 | 0.6075 | 0.6488 | 0.9562 | 0.7272 | -130.3416 | -3.4831 | 4.1837 | 1.0308 | -4.5731 | -3.0217 | 3.2939 |  | 1.5234 | -0.9398 | 4.0118 | 3.3647 | 3.3491 | 1.0508 | 10.7176 | 14.2077 | 14.7897 | 11.0429 | -0.0004 | -0.0032 | 0.0003 | 0.0035 | 0.0006 | -0.0005 | 0.0066 | -0.0054 | 0.0048 | -360.1958 | 17.4233 | -360.4973 | 17.6594 | -360.8174 | 18.1666 | -360.9035 | 17.5445 | -352.6752 | 18.7415 | -352.7152 | 16.832
12:13 | 3224 | 35.2943 | 199.6955 | 446.3327 | 451.2497 | -17.6144 | -43.9994 | 9.1123 | 5.9383 | -0.0237 | -1.4792 | 1.5501 | -2.1015 | 9.7367 | 2.6251 | 0.6064 | 0.646 | 0.9544 | 0.7278 | -130.2114 | -3.3504 | 4.2725 | 1.0306 | -4.6365 | -3.065 | 3.2434 |  | 1.573 | -0.8975 | 4.012 | 3.3612 | 3.3469 | 1.0503 | 10.7162 | 14.2246 | 14.7821 | 11.0515 | 0 | -0.0023 | 0.0014 | 0.0041 | 0.0015 | -0.0005 | -0.002 | -0.0098 | -0.0224 | -360.1096 | 17.3946 | -360.4419 | 17.6553 | -360.7927 | 18.1379 | -360.8604 | 17.5116 | -352.6475 | 18.7251 | -352.6567 | 16.832
12:13 | 3225 | 35.2976 | 199.7222 | 446.3382 | 451.2647 | -17.6594 | -43.9809 | 9.1383 | 5.8157 | -0.1089 | -1.6273 | 1.4808 | -2.1056 | 9.7403 | 2.7095 | 0.6058 | 0.647 | 0.9548 | 0.7256 | -130.2652 | -3.4546 | 4.1844 | 1.016 | -4.6243 | -3.0254 | 3.2618 |  | 1.5894 | -0.8906 | 4.0105 | 3.3638 | 3.3472 | 1.0501 | 10.7292 | 14.2134 | 14.8071 | 11.0198 | -0.0004 | -0.003 | 0.0005 | 0.0037 | 0.0006 | -0.0004 | 0.0055 | -0.0143 | -0.0125 | -360.1835 | 17.4028 | -360.4758 | 17.6636 | -360.7989 | 18.1481 | -360.9035 | 17.5219 | -352.6383 | 18.7436 | -352.6906 | 16.8299
12:13 | 3226 | 35.2245 | 199.6327 | 446.3814 | 451.2842 | -17.5703 | -43.904 | 9.2015 | 5.7543 | -0.1468 | -1.7159 | 1.4357 | -2.0957 | 9.7343 | 2.7184 | 0.6064 | 0.6475 | 0.9557 | 0.7276 | -130.2916 | -3.3608 | 4.2442 | 0.9569 | -4.5289 | -3.0772 | 3.2475 |  | 1.6406 | -0.8441 | 4.0116 | 3.3632 | 3.3491 | 1.0514 | 10.7405 | 14.2314 | 14.7998 | 11.0529 | 0.0002 | -0.0028 | 0.0012 | 0.0043 | 0.001 | -0.0008 | 0.0234 | 0.0021 | 0.0165 | -360.2173 | 17.4295 | -360.4819 | 17.68 | -360.8481 | 18.1666 | -360.9127 | 17.5445 | -352.6998 | 18.7436 | -352.706 | 16.8566
12:13 | 3227 | 35.2698 | 199.7479 | 446.3539 | 451.1955 | -17.5073 | -43.7753 | 9.1389 | 5.6945 | -0.1198 | -1.7368 | 1.4373 | -2.106 | 9.696 | 2.6579 | 0.6049 | 0.6453 | 0.9532 | 0.7288 | -130.2714 | -3.4438 | 4.2303 | 0.8546 | -4.6181 | -3.0571 | 3.2659 |  | 1.6555 | -0.9371 | 4.0119 | 3.3646 | 3.3542 | 1.0499 | 10.7878 | 14.2794 | 14.8343 | 11.1045 | 0.0002 | -0.0027 | 0.001 | 0.0044 | 0.0008 | -0.0002 | 0.0124 | -0.0195 | -0.0349 | -360.2019 | 17.3987 | -360.4666 | 17.6677 | -360.7989 | 18.1481 | -360.8666 | 17.5198 | -352.666 | 18.7271 | -352.7121 | 16.8505
12:14 | 3228 | 35.2435 | 199.7714 | 446.3961 | 451.3025 | -17.4602 | -43.8243 | 9.2262 | 5.6558 | -0.231 | -1.6903 | 1.4076 | -2.1166 | 9.7401 | 2.6282 | 0.6061 | 0.6479 | 0.9531 | 0.728 | -130.3513 | -3.3474 | 4.2818 | 0.7736 | -4.5137 | -3.0312 | 3.254 |  | 1.6069 | -0.9207 | 4.0117 | 3.3661 | 3.3526 | 1.0509 | 10.7637 | 14.2776 | 14.8403 | 11.0934 | -0.0004 | -0.0027 | 0.0004 | 0.0033 | 0.0008 | -0.001 | 0.0224 | -0.0027 | 0.0094 | -360.1188 | 17.3966 | -360.4389 | 17.6574 | -360.8266 | 18.144 | -360.845 | 17.5137 | -352.6352 | 18.721 | -352.6444 | 16.8279
12:14 | 3229 | 35.3949 | 199.7853 | 446.445 | 451.3444 | -17.4554 | -43.7326 | 9.3262 | 5.692 | -0.1134 | -1.6852 | 1.5398 | -2.1451 | 9.7237 | 2.6649 | 0.6059 | 0.6458 | 0.9551 | 0.7268 | -130.3213 | -3.2924 | 4.2763 | 0.8256 | -4.5159 | -2.9197 | 3.2793 |  | 1.6465 | -0.9463 | 4.01 | 3.3629 | 3.3459 | 1.0514 | 10.7509 | 14.2592 | 14.8053 | 11.0688 | -0.0002 | -0.0025 | 0.0007 | 0.0035 | 0.0008 | 0 | 0.0239 | 0.0046 | -0.0088 | -360.1896 | 17.411 | -360.4819 | 17.6697 | -360.842 | 18.1625 | -360.8881 | 17.5568 | -352.666 | 18.7271 | -352.6875 | 16.8361
12:14 | 3230 | 35.3866 | 199.7703 | 446.4423 | 451.3453 | -17.428 | -43.7299 | 9.3598 | 5.7332 | -0.0511 | -1.718 | 1.5194 | -2.1282 | 9.7016 | 2.6349 | 0.6051 | 0.6476 | 0.9552 | 0.7277 | -130.3463 | -3.3244 | 4.3009 | 0.8617 | -4.5042 | -3.059 | 3.2389 |  | 1.5431 | -0.8894 | 4.0111 | 3.3638 | 3.3518 | 1.0504 | 10.7418 | 14.2668 | 14.798 | 11.0378 | 0.0001 | -0.003 | 0.0001 | 0.0032 | 0.0002 | -0.001 | 0.0254 | -0.0089 | -0.0003 | -360.1742 | 17.4254 | -360.4696 | 17.6492 | -360.7989 | 18.1522 | -360.9066 | 17.5321 | -352.6967 | 18.7559 | -352.6844 | 16.8217
12:14 | 3231 | 35.4344 | 199.8375 | 446.4635 | 451.3259 | -17.4649 | -43.7881 | 9.2528 | 5.7875 | -0.0276 | -1.6649 | 1.482 | -2.0698 | 9.7559 | 2.6032 | 0.6052 | 0.6498 | 0.954 | 0.728 | -130.3177 | -3.3227 | 4.3667 | 0.9414 | -4.5735 | -3.1362 | 3.2187 |  | 1.5617 | -0.9265 | 4.0124 | 3.3637 | 3.3491 | 1.0513 | 10.721 | 14.2345 | 14.7486 | 11.0284 | -0.0001 | -0.003 | 0.0007 | 0.004 | 0.0005 | -0.0005 | 0.0118 | 0.0037 | -0.0055 | -360.1465 | 17.4028 | -360.4419 | 17.6677 | -360.8112 | 18.1379 | -360.8327 | 17.5116 | -352.6167 | 18.7271 | -352.6752 | 16.8402
12:14 | 3232 | 35.387 | 199.8383 | 446.5162 | 451.2418 | -17.4408 | -43.7643 | 9.2231 | 5.7483 | -0.0637 | -1.7225 | 1.4822 | -2.0402 | 9.7538 | 2.6909 | 0.6051 | 0.6467 | 0.9489 | 0.7278 | -130.3548 | -3.3414 | 4.3393 | 1.0402 | -4.6161 | -3.0627 | 3.2634 |  | 1.5913 | -0.8866 | 4.0121 | 3.3622 | 3.351 | 1.0507 | 10.7382 | 14.2174 | 14.7681 | 11.0219 | -0.0003 | -0.0027 | 0.0013 | 0.0042 | 0.0007 | -0.0005 | 0.0253 | -0.0041 | 0.0088 | -360.1558 | 17.4131 | -360.4942 | 17.6718 | -360.8327 | 18.1912 | -360.9158 | 17.5342 | -352.6598 | 18.7353 | -352.6752 | 16.8443
12:14 | 3233 | 35.4443 | 199.866 | 446.5336 | 451.278 | -17.4049 | -43.6271 | 9.2809 | 5.8089 | -0.0196 | -1.6698 | 1.5086 | -2.0123 | 9.7298 | 2.6659 | 0.6054 | 0.646 | 0.9578 | 0.7278 | -130.3888 | -3.1957 | 4.3411 | 0.9427 | -4.5798 | -2.9368 | 3.3284 |  | 1.543 | -0.9599 | 4.0107 | 3.3616 | 3.3461 | 1.0513 | 10.7291 | 14.2309 | 14.8082 | 11.0598 | -0.0006 | -0.0028 | 0.0007 | 0.004 | 0.001 | -0.0008 | 0.0049 | -0.0084 | -0.0153 | -360.1558 | 17.3905 | -360.4296 | 17.6615 | -360.845 | 18.1645 | -360.9097 | 17.5404 | -352.669 | 18.7128 | -352.6598 | 16.8443
12:14 | 3234 | 35.4321 | 199.8224 | 446.5057 | 451.191 | -17.4847 | -43.7103 | 9.1455 | 5.8331 | -0.043 | -1.7311 | 1.5049 | -2.0448 | 9.7678 | 2.7095 | 0.6064 | 0.6497 | 0.9575 | 0.7268 | -130.3966 | -3.2827 | 4.2961 | 0.9318 | -4.4854 | -2.9817 | 3.2551 |  | 1.6205 | -0.8743 | 4.0118 | 3.362 | 3.3456 | 1.0498 | 10.7393 | 14.2361 | 14.8342 | 11.0341 | 0.0001 | -0.0031 | 0.0008 | 0.0038 | 0.0009 | -0.0003 | 0.0128 | 0.0122 | -0.0058 | -360.1681 | 17.4028 | -360.4789 | 17.6369 | -360.7743 | 18.1399 | -360.8697 | 17.5239 | -352.666 | 18.7333 | -352.6598 | 16.8197
12:14 | 3235 | 35.5508 | 199.8753 | 446.4752 | 451.2393 | -17.6024 | -43.8404 | 9.0542 | 5.8515 | 0.1209 | -1.738 | 1.4921 | -2.1157 | 9.7454 | 2.6787 | 0.6056 | 0.6499 | 0.9555 | 0.7257 | -130.3628 | -3.2546 | 4.355 | 0.9546 | -4.5182 | -3.051 | 3.3001 |  | 1.5248 | -0.8087 | 4.0136 | 3.3646 | 3.349 | 1.0512 | 10.737 | 14.2628 | 14.8441 | 11.0894 | -0.0002 | -0.0032 | 0.0008 | 0.0038 | 0.0008 | -0.0006 | 0.0078 | -0.0073 | -0.0148 | -360.1896 | 17.4418 | -360.525 | 17.6902 | -360.8635 | 18.142 | -360.8327 | 17.5301 | -352.6937 | 18.762 | -352.7183 | 16.8607
12:14 | 3236 | 35.4503 | 199.8547 | 446.5885 | 451.2497 | -17.554 | -43.7569 | 9.1078 | 5.8612 | 0.007 | -1.6632 | 1.5166 | -2.0116 | 9.8135 | 2.7164 | 0.604 | 0.6498 | 0.957 | 0.7259 | -130.4448 | -3.3423 | 4.2287 | 1.0553 | -4.5337 | -3.0267 | 3.2913 |  | 1.5867 | -0.7835 | 4.012 | 3.3599 | 3.3522 | 1.0498 | 10.7452 | 14.2418 | 14.8331 | 11.0865 | -0.0003 | -0.0026 | 0.0001 | 0.0033 | 0.0006 | 0 | 0.0248 | 0.0049 | -0.0082 | -360.1127 | 17.3946 | -360.4789 | 17.6841 | -360.8327 | 18.144 | -360.8574 | 17.4972 | -352.6198 | 18.7271 | -352.709 | 16.8669
12:14 | 3237 | 35.4788 | 199.8498 | 446.5355 | 451.294 | -17.6168 | -43.8134 | 9.0864 | 5.7591 | 0.0712 | -1.5607 | 1.4746 | -1.9761 | 9.7775 | 2.7203 | 0.6069 | 0.6523 | 0.9578 | 0.7289 | -130.4139 | -3.3556 | 4.1853 | 1.0649 | -4.5708 | -3.0202 | 3.3616 |  | 1.5681 | -0.8928 | 4.0113 | 3.364 | 3.3494 | 1.0515 | 10.7417 | 14.2557 | 14.8127 | 11.0713 | -0.0005 | -0.0028 | 0.0006 | 0.0037 | 0.0009 | -0.0005 | 0.0129 | -0.0052 | -0.0048 | -360.1465 | 17.3905 | -360.445 | 17.6553 | -360.8297 | 18.1666 | -360.882 | 17.5157 | -352.6629 | 18.7148 | -352.6629 | 16.8402
12:14 | 3238 | 35.4773 | 199.8237 | 446.4866 | 451.2667 | -17.5315 | -43.8474 | 9.0744 | 5.7199 | 0.1225 | -1.5476 | 1.5042 | -2.0369 | 9.8146 | 2.6716 | 0.605 | 0.6471 | 0.9553 | 0.7278 | -130.3104 | -3.2177 | 4.3021 | 1.0595 | -4.6564 | -2.9608 | 3.3967 |  | 1.567 | -0.8625 | 4.0119 | 3.3612 | 3.3508 | 1.0516 | 10.729 | 14.2428 | 14.8219 | 11.0706 | -0.0002 | -0.003 | 0.0006 | 0.0038 | 0.0004 | 0 | 0.001 | -0.0093 | 0.01 | -360.2296 | 17.4172 | -360.4758 | 17.6553 | -360.7927 | 18.1563 | -360.9343 | 17.5609 | -352.7244 | 18.7538 | -352.6783 | 16.8464
12:14 | 3239 | 35.5218 | 199.8559 | 446.5359 | 451.2679 | -17.6182 | -43.9063 | 9.1131 | 5.7877 | 0.0914 | -1.4722 | 1.4494 | -1.8849 | 9.8691 | 2.7308 | 0.606 | 0.6483 | 0.9551 | 0.7275 | -130.3494 | -3.2587 | 4.2423 | 0.9855 | -4.6286 | -2.9955 | 3.2973 |  | 1.6645 | -0.8655 | 4.0121 | 3.3613 | 3.3485 | 1.0517 | 10.7279 | 14.2647 | 14.8031 | 11.0407 | 0.0001 | -0.0035 | 0.0009 | 0.004 | 0.0009 | -0.0009 | 0.0085 | 0.0111 | -0.0128 | -360.1588 | 17.4192 | -360.4881 | 17.6471 | -360.7743 | 18.1132 | -360.8204 | 17.5219 | -352.6752 | 18.7497 | -352.669 | 16.832
12:14 | 3240 | 35.5299 | 199.749 | 446.5524 | 451.2315 | -17.6706 | -43.9839 | 9.0893 | 5.8307 | 0.0287 | -1.4885 | 1.448 | -1.9817 | 9.8779 | 2.6505 | 0.6057 | 0.6451 | 0.9554 | 0.727 | -130.2725 | -3.1665 | 4.2917 | 1.0961 | -4.6201 | -2.9261 | 3.3402 |  | 1.6822 | -0.8139 | 4.0119 | 3.3621 | 3.3453 | 1.0507 | 10.7013 | 14.2091 | 14.7469 | 11.0374 | 0 | -0.0027 | 0.001 | 0.004 | 0.0008 | -0.0006 | 0.0139 | -0.0193 | -0.0007 | -360.1773 | 17.4172 | -360.4912 | 17.68 | -360.8481 | 18.142 | -360.8235 | 17.5178 | -352.6506 | 18.7456 | -352.6937 | 16.8464
12:14 | 3241 | 35.5837 | 199.7883 | 446.5437 | 451.2264 | -17.6039 | -43.9354 | 9.035 | 5.7762 | 0.0644 | -1.4658 | 1.4724 | -2.0932 | 9.8187 | 2.5575 | 0.6066 | 0.651 | 0.9565 | 0.7287 | -130.3821 | -3.2443 | 4.35 | 1.0201 | -4.6943 | -2.9264 | 3.3276 |  | 1.6672 | -0.885 | 4.0118 | 3.3635 | 3.3497 | 1.0515 | 10.7486 | 14.2337 | 14.8025 | 11.084 | -0.0003 | -0.0022 | 0.0006 | 0.004 | 0.001 | -0.0004 | 0.0273 | -0.0079 | 0.003 | -360.1773 | 17.3987 | -360.4512 | 17.6944 | -360.8697 | 18.1871 | -360.8789 | 17.5342 | -352.6475 | 18.7312 | -352.6844 | 16.8607
12:14 | 3242 | 35.5785 | 199.8065 | 446.5145 | 451.227 | -17.6684 | -44.0031 | 9.0551 | 5.8028 | -0.0526 | -1.5309 | 1.4107 | -2.1132 | 9.8447 | 2.5536 | 0.6055 | 0.651 | 0.9589 | 0.7269 | -130.3113 | -3.2499 | 4.3414 | 1.0662 | -4.648 | -2.8274 | 3.3789 |  | 1.6082 | -0.9371 | 4.0125 | 3.3652 | 3.3529 | 1.0525 | 10.7417 | 14.2615 | 14.8011 | 11.0424 | -0.0001 | -0.003 | 0.0009 | 0.0039 | 0.0007 | -0.0008 | 0.011 | -0.0081 | 0.0021 | -360.1865 | 17.3925 | -360.3865 | 17.6225 | -360.7835 | 18.1481 | -360.9066 | 17.5404 | -352.666 | 18.7189 | -352.6383 | 16.8094
12:14 | 3243 | 35.5565 | 199.7749 | 446.4902 | 451.1876 | -17.7062 | -44.0152 | 9.0218 | 5.8671 | -0.0394 | -1.5052 | 1.4361 | -2.0038 | 9.8322 | 2.5931 | 0.6058 | 0.6485 | 0.9554 | 0.7273 | -130.3668 | -3.3161 | 4.2818 | 1.0418 | -4.6721 | -3.0167 | 3.3909 |  | 1.6553 | -0.9553 | 4.0098 | 3.3645 | 3.346 | 1.0496 | 10.7623 | 14.2481 | 14.849 | 11.0619 | 0.0004 | -0.0026 | 0.0009 | 0.0041 | 0.0009 | 0 | 0.0259 | -0.0116 | 0.0056 | -360.1496 | 17.409 | -360.4819 | 17.6492 | -360.7497 | 18.142 | -360.8574 | 17.5301 | -352.6752 | 18.7436 | -352.6506 | 16.8197
12:14 | 3244 | 35.5153 | 199.7581 | 446.5557 | 451.1965 | -17.6263 | -43.9235 | 9.0207 | 5.8232 | -0.0229 | -1.4775 | 1.4413 | -2.0888 | 9.7698 | 2.5951 | 0.6054 | 0.6482 | 0.9556 | 0.7276 | -130.3592 | -3.3527 | 4.2424 | 1.1079 | -4.5492 | -3.0088 | 3.3601 |  | 1.6288 | -0.8884 | 4.0107 | 3.3627 | 3.3516 | 1.0511 | 10.7533 | 14.2557 | 14.8301 | 11.0771 | 0 | -0.0029 | 0.0002 | 0.0034 | 0.0008 | -0.0005 | 0.0137 | -0.0033 | -0.0043 | -360.1711 | 17.4315 | -360.5219 | 17.6985 | -360.8635 | 18.1461 | -360.885 | 17.5219 | -352.669 | 18.762 | -352.746 | 16.8689
12:14 | 3245 | 35.4737 | 199.6789 | 446.5034 | 451.2435 | -17.6691 | -44.0143 | 9.0214 | 5.7995 | -0.1934 | -1.5456 | 1.3955 | -2.0387 | 9.8942 | 2.608 | 0.6067 | 0.6522 | 0.9552 | 0.7273 | -130.3253 | -3.2717 | 4.4218 | 1.1356 | -4.5106 | -2.9476 | 3.4306 |  | 1.5816 | -0.9178 | 4.0121 | 3.3641 | 3.3448 | 1.0516 | 10.7486 | 14.2395 | 14.7967 | 11.0724 | -0.0001 | -0.0024 | 0.0011 | 0.004 | 0.0004 | -0.0004 | 0.0064 | -0.0052 | -0.0016 | -360.1188 | 17.3782 | -360.4542 | 17.6738 | -360.8512 | 18.1687 | -360.9035 | 17.5137 | -352.6413 | 18.7169 | -352.6321 | 16.8587
12:14 | 3246 | 35.6076 | 199.7201 | 446.5276 | 451.2578 | -17.6696 | -44.0203 | 9.0405 | 5.8743 | -0.0889 | -1.5525 | 1.5174 | -2.1249 | 9.8486 | 2.642 | 0.6065 | 0.6498 | 0.9558 | 0.7259 | -130.2843 | -3.2898 | 4.3195 | 1.1447 | -4.6398 | -3.0981 | 3.29 |  | 1.6818 | -0.8677 | 4.0111 | 3.3642 | 3.3498 | 1.0513 | 10.7417 | 14.2266 | 14.8059 | 11.0486 | 0 | -0.0027 | 0.0008 | 0.0037 | 0.0009 | -0.0006 | 0.011 | 0.0031 | -0.0083 | -360.0881 | 17.372 | -360.4327 | 17.643 | -360.7958 | 18.1584 | -360.8789 | 17.5239 | -352.6229 | 18.7066 | -352.6413 | 16.832
12:14 | 3247 | 35.526 | 199.6906 | 446.4509 | 451.2145 | -17.738 | -44.1205 | 9.0136 | 5.9537 | -0.0895 | -1.6303 | 1.5379 | -2.1464 | 9.8268 | 2.6522 | 0.6067 | 0.6489 | 0.9534 | 0.7271 | -130.2799 | -3.3245 | 4.2429 | 1.204 | -4.5252 | -2.9735 | 3.3474 |  | 1.6803 | -0.8712 | 4.0123 | 3.3653 | 3.3499 | 1.0513 | 10.7326 | 14.2461 | 14.8181 | 11.0515 | 0 | -0.0032 | 0.0007 | 0.0038 | 0 | -0.0009 | 0.0082 | -0.005 | 0.0008 | -360.2296 | 17.4356 | -360.5004 | 17.6574 | -360.8204 | 18.144 | -360.8789 | 17.5629 | -352.6937 | 18.7477 | -352.7244 | 16.834
12:14 | 3248 | 35.5206 | 199.7154 | 446.5254 | 451.1487 | -17.6934 | -44.1415 | 9.0133 | 5.9667 | -0.1111 | -1.5786 | 1.5511 | -2.0143 | 9.7793 | 2.6548 | 0.6061 | 0.6489 | 0.9553 | 0.7257 | -130.3332 | -3.2574 | 4.3112 | 1.2349 | -4.5549 | -2.9423 | 3.3464 |  | 1.6205 | -0.8602 | 4.0111 | 3.3674 | 3.3486 | 1.0493 | 10.7186 | 14.2034 | 14.7585 | 11.049 | 0.0001 | -0.0029 | 0.0007 | 0.004 | 0.001 | -0.0008 | -0.0006 | -0.0112 | -0.016 | -360.1619 | 17.4254 | -360.5127 | 17.6841 | -360.8389 | 18.142 | -360.8543 | 17.5178 | -352.6475 | 18.7395 | -352.749 | 16.8854
12:14 | 3249 | 35.5473 | 199.7315 | 446.5342 | 451.1501 | -17.6453 | -43.9814 | 9.1831 | 5.8749 | -0.1808 | -1.6036 | 1.6217 | -1.9543 | 9.8933 | 2.635 | 0.6067 | 0.6511 | 0.9582 | 0.7259 | -130.3296 | -3.236 | 4.247 | 1.1857 | -4.6425 | -3.0069 | 3.2352 |  | 1.6391 | -0.8382 | 4.0112 | 3.3651 | 3.3459 | 1.0494 | 10.7556 | 14.2406 | 14.8144 | 11.0623 | -0.0003 | -0.0026 | 0.0005 | 0.0038 | 0.0002 | -0.0003 | 0.0132 | -0.0143 | 0.0084 | -360.1342 | 17.3823 | -360.4604 | 17.6553 | -360.845 | 18.1461 | -360.8358 | 17.5034 | -352.629 | 18.7189 | -352.6629 | 16.8587
12:14 | 3250 | 35.5366 | 199.8342 | 446.6502 | 451.1582 | -17.6575 | -44.0154 | 9.1629 | 5.9435 | -0.1744 | -1.5886 | 1.639 | -2.0034 | 9.8836 | 2.6023 | 0.6056 | 0.6504 | 0.9573 | 0.7271 | -130.3736 | -3.2973 | 4.1907 | 1.1222 | -4.616 | -2.9236 | 3.2577 |  | 1.7091 | -0.7687 | 4.0123 | 3.3678 | 3.3495 | 1.0509 | 10.7324 | 14.2176 | 14.8328 | 11.0562 | 0.0001 | -0.0024 | 0.0013 | 0.004 | 0.0009 | -0.0011 | 0.0117 | -0.0063 | -0.0076 | -360.1896 | 17.3905 | -360.4542 | 17.6512 | -360.8327 | 18.1687 | -360.8974 | 17.5486 | -352.6629 | 18.7189 | -352.6444 | 16.8258
12:14 | 3251 | 35.6531 | 199.8282 | 446.5683 | 451.116 | -17.736 | -43.9802 | 9.0159 | 5.9771 | -0.0956 | -1.6241 | 1.6724 | -2.0479 | 9.8369 | 2.6745 | 0.6058 | 0.6463 | 0.9566 | 0.7268 | -130.3948 | -3.2907 | 4.1986 | 1.1793 | -4.7392 | -3.0739 | 3.3067 |  | 1.6511 | -0.7798 | 4.0104 | 3.3655 | 3.3485 | 1.049 | 10.7267 | 14.2059 | 14.7912 | 11.045 | 0.0001 | -0.0029 | 0.001 | 0.0038 | 0.0008 | -0.0001 | 0.0204 | -0.0015 | 0.0124 | -360.2388 | 17.4356 | -360.525 | 17.6574 | -360.8112 | 18.1502 | -360.885 | 17.5445 | -352.7244 | 18.7661 | -352.7275 | 16.8546
12:14 | 3252 | 35.6158 | 199.784 | 446.6223 | 451.1429 | -17.7624 | -43.9933 | 9.0504 | 5.9009 | -0.1357 | -1.5652 | 1.6617 | -2.0777 | 9.7245 | 2.6105 | 0.6053 | 0.6496 | 0.9564 | 0.726 | -130.2573 | -3.2304 | 4.2553 | 1.3126 | -4.6232 | -2.9701 | 3.3193 |  | 1.7283 | -0.8357 | 4.0111 | 3.3648 | 3.3501 | 1.0516 | 10.7486 | 14.2744 | 14.8267 | 11.0778 | 0.0005 | -0.0025 | 0.0006 | 0.0035 | 0.0005 | -0.0006 | 0.0066 | -0.0178 | -0.0031 | -360.1681 | 17.4069 | -360.4635 | 17.6677 | -360.8174 | 18.1153 | -360.8543 | 17.5178 | -352.6598 | 18.7333 | -352.706 | 16.8525
12:14 | 3253 | 35.6023 | 199.7853 | 446.5663 | 451.1047 | -17.6993 | -43.942 | 9.193 | 5.8306 | -0.1794 | -1.7409 | 1.6305 | -2.0804 | 9.806 | 2.6975 | 0.6068 | 0.6509 | 0.9555 | 0.7259 | -130.3042 | -3.2065 | 4.2969 | 1.3406 | -4.5956 | -3.0143 | 3.3022 |  | 1.6093 | -0.8982 | 4.0121 | 3.364 | 3.3487 | 1.0512 | 10.744 | 14.2754 | 14.7981 | 11.0619 | -0.0003 | -0.0025 | 0.001 | 0.004 | 0.0004 | -0.0005 | 0.0263 | -0.0084 | 0.0034 | -360.1465 | 17.4028 | -360.4666 | 17.6636 | -360.8543 | 18.1687 | -360.8697 | 17.5219 | -352.6106 | 18.7169 | -352.6567 | 16.8505
12:14 | 3254 | 35.5673 | 199.8227 | 446.5978 | 451.0879 | -17.6467 | -43.9118 | 9.151 | 5.84 | -0.1754 | -1.618 | 1.5894 | -2.1259 | 9.8441 | 2.712 | 0.6064 | 0.6503 | 0.9558 | 0.7257 | -130.244 | -3.168 | 4.3006 | 1.3704 | -4.5849 | -2.8793 | 3.3634 |  | 1.6651 | -0.8292 | 4.0129 | 3.3682 | 3.3552 | 1.0518 | 10.7313 | 14.2336 | 14.7957 | 11.0612 | -0.0004 | -0.0027 | 0.0007 | 0.004 | 0.0009 | -0.0001 | 0.0364 | -0.0081 | 0.0023 | -360.2204 | 17.4007 | -360.4419 | 17.6656 | -360.8543 | 18.1666 | -360.922 | 17.565 | -352.706 | 18.7271 | -352.666 | 16.8443
12:14 | 3255 | 35.4781 | 199.8338 | 446.5577 | 451.0085 | -17.5404 | -43.8983 | 9.1928 | 5.88 | -0.0672 | -1.6147 | 1.6246 | -2.0668 | 9.8129 | 2.6472 | 0.6067 | 0.6514 | 0.9589 | 0.727 | -130.332 | -3.2803 | 4.2795 | 1.412 | -4.5177 | -2.9476 | 3.4107 |  | 1.7265 | -0.8563 | 4.0103 | 3.3646 | 3.3484 | 1.0496 | 10.7613 | 14.2291 | 14.8097 | 11.0793 | 0.0003 | -0.003 | 0.0008 | 0.004 | 0.0011 | -0.0005 | -0.0036 | -0.0073 | 0.0032 | -360.1927 | 17.4007 | -360.4389 | 17.6389 | -360.762 | 18.1399 | -360.885 | 17.526 | -352.626 | 18.7333 | -352.6321 | 16.8176
12:14 | 3256 | 35.6559 | 199.7916 | 446.6744 | 451.1446 | -17.5367 | -43.7851 | 9.1501 | 5.776 | -0.0981 | -1.5632 | 1.6171 | -2.104 | 9.8735 | 2.7344 | 0.6062 | 0.6452 | 0.9549 | 0.7261 | -130.2845 | -3.2621 | 4.264 | 1.2812 | -4.4287 | -3.0739 | 3.4043 |  | 1.6259 | -0.8998 | 4.0108 | 3.3677 | 3.353 | 1.0514 | 10.7072 | 14.2318 | 14.7727 | 11.0328 | -0.0002 | -0.0033 | 0.0001 | 0.0033 | 0.0004 | -0.0004 | 0.0076 | -0.0038 | -0.0183 | -360.1619 | 17.4172 | -360.5066 | 17.6923 | -360.8512 | 18.142 | -360.8481 | 17.5157 | -352.6567 | 18.7436 | -352.6906 | 16.8566
12:14 | 3257 | 35.6079 | 199.8552 | 446.6055 | 451.0982 | -17.567 | -43.7993 | 9.2084 | 5.8001 | -0.0309 | -1.6761 | 1.6291 | -2.1903 | 9.7868 | 2.6697 | 0.6056 | 0.6488 | 0.9557 | 0.7267 | -130.2824 | -3.1809 | 4.2628 | 1.2486 | -4.4873 | -2.9241 | 3.3993 |  | 1.5889 | -0.8646 | 4.0108 | 3.3626 | 3.3508 | 1.0511 | 10.7613 | 14.2291 | 14.7865 | 11.0619 | -0.0002 | -0.0029 | 0.0006 | 0.0037 | 0.001 | -0.0005 | 0.0059 | -0.0116 | -0.0039 | -360.1373 | 17.3966 | -360.4727 | 17.6902 | -360.8604 | 18.1851 | -360.9004 | 17.5321 | -352.6444 | 18.723 | -352.6875 | 16.8628
12:14 | 3258 | 35.6215 | 199.8367 | 446.5508 | 451.0441 | -17.534 | -43.6945 | 9.1706 | 5.6276 | -0.0688 | -1.605 | 1.6208 | -2.1501 | 9.8321 | 2.7808 | 0.6066 | 0.647 | 0.9562 | 0.7278 | -130.3293 | -3.2428 | 4.1984 | 1.2554 | -4.5249 | -2.9181 | 3.4038 |  | 1.635 | -0.7625 | 4.0106 | 3.3628 | 3.3502 | 1.0521 | 10.7533 | 14.2324 | 14.8232 | 11.0775 | -0.0003 | -0.0026 | 0.0005 | 0.0041 | 0.0002 | -0.0004 | 0.009 | -0.0177 | -0.0124 | -360.1435 | 17.3905 | -360.4419 | 17.6512 | -360.7712 | 18.1584 | -360.8697 | 17.526 | -352.626 | 18.7025 | -352.6383 | 16.8361
12:14 | 3259 | 35.6385 | 199.7584 | 446.5477 | 451.0725 | -17.5534 | -43.7793 | 9.1305 | 5.7019 | -0.0141 | -1.5796 | 1.6927 | -2.2639 | 9.775 | 2.7073 | 0.607 | 0.649 | 0.9528 | 0.7263 | -130.2544 | -3.1491 | 4.2614 | 1.2672 | -4.5912 | -2.9334 | 3.3647 |  | 1.6093 | -0.8127 | 4.0094 | 3.3643 | 3.3466 | 1.0501 | 10.7393 | 14.2361 | 14.8053 | 11.0399 | -0.0002 | -0.0032 | 0.0009 | 0.0037 | 0.001 | -0.0005 | 0.0081 | 0.0021 | 0.0153 | -360.2019 | 17.4274 | -360.5219 | 17.6964 | -360.8574 | 18.1625 | -360.8881 | 17.5465 | -352.6906 | 18.7497 | -352.7029 | 16.8546
12:14 | 3260 | 35.7145 | 199.8926 | 446.6037 | 451.0564 | -17.5521 | -43.8417 | 9.1289 | 5.8489 | -0.1314 | -1.5147 | 1.643 | -2.2668 | 9.7506 | 2.6983 | 0.6068 | 0.646 | 0.9569 | 0.7266 | -130.216 | -3.1408 | 4.2639 | 1.3412 | -4.5696 | -3.0201 | 3.4284 |  | 1.5771 | -0.7515 | 4.0102 | 3.366 | 3.3492 | 1.0513 | 10.7612 | 14.2526 | 14.835 | 11.0785 | 0.0002 | -0.0031 | 0.0009 | 0.004 | 0.0008 | -0.0003 | 0.0043 | -0.0098 | -0.0004 | -360.1096 | 17.4131 | -360.4727 | 17.6636 | -360.7989 | 18.1604 | -360.8543 | 17.5116 | -352.6413 | 18.7251 | -352.6906 | 16.8628
12:14 | 3261 | 35.6851 | 199.8222 | 446.6085 | 451.0209 | -17.4897 | -43.6472 | 9.1456 | 5.7937 | -0.1463 | -1.6969 | 1.5442 | -2.181 | 9.7764 | 2.7008 | 0.6066 | 0.6486 | 0.9534 | 0.7263 | -130.2846 | -3.2224 | 4.2869 | 1.3822 | -4.5385 | -2.8421 | 3.5057 |  | 1.5992 | -0.768 | 4.0109 | 3.3679 | 3.3483 | 1.0519 | 10.7579 | 14.2254 | 14.7987 | 11.0533 | -0.0005 | -0.003 | 0.0008 | 0.0037 | 0.0008 | -0.0003 | 0.0294 | -0.006 | -0.0096 | -360.165 | 17.3925 | -360.4666 | 17.682 | -360.8327 | 18.1666 | -360.8974 | 17.5321 | -352.6598 | 18.7128 | -352.6721 | 16.8525
12:14 | 3262 | 35.5771 | 199.7722 | 446.5614 | 450.9816 | -17.5141 | -43.6311 | 9.2203 | 5.7921 | -0.1619 | -1.7352 | 1.5344 | -2.0658 | 9.7823 | 2.7407 | 0.6073 | 0.6465 | 0.9543 | 0.7258 | -130.2311 | -3.1708 | 4.2538 | 1.3175 | -4.589 | -2.8557 | 3.4619 |  | 1.5911 | -0.7826 | 4.0106 | 3.3674 | 3.3467 | 1.051 | 10.7555 | 14.2698 | 14.8281 | 11.0904 | -0.0001 | -0.0027 | 0.0008 | 0.0042 | 0.0006 | -0.0003 | 0.0134 | -0.0104 | 0.0055 | -360.1711 | 17.409 | -360.4819 | 17.6738 | -360.7866 | 18.181 | -360.9004 | 17.5527 | -352.6537 | 18.7251 | -352.669 | 16.8443
12:14 | 3263 | 35.6456 | 199.8261 | 446.5156 | 450.9472 | -17.5009 | -43.6559 | 9.3645 | 5.8639 | -0.1191 | -1.6497 | 1.5809 | -2.0221 | 9.7881 | 2.8275 | 0.6084 | 0.6488 | 0.959 | 0.7265 | -130.3465 | -3.1779 | 4.2195 | 1.123 | -4.556 | -2.8157 | 3.4596 |  | 1.5657 | -0.8961 | 4.0103 | 3.363 | 3.3482 | 1.0494 | 10.7405 | 14.2372 | 14.8171 | 11.0529 | -0.0002 | -0.0033 | 0.0006 | 0.004 | 0.0008 | -0.0005 | 0.0012 | -0.0007 | -0.0186 | -360.165 | 17.4028 | -360.4573 | 17.6492 | -360.7989 | 18.1522 | -360.8358 | 17.526 | -352.6567 | 18.7251 | -352.6321 | 16.834
12:14 | 3264 | 35.6686 | 199.7949 | 446.5732 | 450.9353 | -17.4689 | -43.6797 | 9.3266 | 5.8819 | -0.1109 | -1.5839 | 1.5252 | -2.0078 | 9.8716 | 2.7423 | 0.607 | 0.649 | 0.9572 | 0.7258 | -130.2453 | -3.039 | 4.2905 | 1.0422 | -4.5169 | -2.7771 | 3.3924 |  | 1.6469 | -0.7738 | 4.0103 | 3.3655 | 3.3469 | 1.0499 | 10.7267 | 14.2462 | 14.7728 | 11.0685 | 0.0002 | -0.003 | 0.0004 | 0.0039 | 0.0006 | -0.0009 | 0.0258 | -0.0168 | -0.0097 | -360.1927 | 17.4295 | -360.4973 | 17.6985 | -360.8204 | 18.1707 | -360.9158 | 17.5239 | -352.6321 | 18.7497 | -352.7121 | 16.8669
12:14 | 3265 | 35.6798 | 199.9304 | 446.6188 | 450.9925 | -17.5336 | -43.5996 | 9.3322 | 5.8701 | -0.0855 | -1.6044 | 1.5552 | -1.982 | 9.9023 | 2.7771 | 0.6067 | 0.6504 | 0.957 | 0.7266 | -130.2687 | -3.1338 | 4.2574 | 1.0579 | -4.5787 | -2.8323 | 3.3651 |  | 1.6071 | -0.8281 | 4.0114 | 3.3687 | 3.3459 | 1.0508 | 10.7162 | 14.2303 | 14.7647 | 11.0688 | 0.0004 | -0.0026 | 0.0004 | 0.0033 | 0.0002 | -0.0008 | 0.012 | -0.0046 | -0.0059 | -360.1527 | 17.3905 | -360.4419 | 17.6594 | -360.8112 | 18.1748 | -360.845 | 17.5178 | -352.6106 | 18.7107 | -352.6506 | 16.8361
12:14 | 3266 | 35.7269 | 199.9405 | 446.5854 | 451.0461 | -17.446 | -43.7498 | 9.3777 | 5.9479 | -0.1272 | -1.6451 | 1.5394 | -1.9918 | 9.8581 | 2.8514 | 0.6073 | 0.6491 | 0.9549 | 0.7269 | -130.3134 | -3.2268 | 4.1958 | 0.9754 | -4.6232 | -2.9505 | 3.3005 |  | 1.6824 | -0.8058 | 4.0107 | 3.3663 | 3.3494 | 1.0509 | 10.7197 | 14.2278 | 14.7957 | 11.0323 | -0.0001 | -0.0026 | 0.0008 | 0.0044 | 0.0008 | -0.0007 | -0.0067 | -0.0053 | 0.0115 | -360.1527 | 17.4007 | -360.5004 | 17.6923 | -360.8204 | 18.1851 | -360.922 | 17.5404 | -352.6413 | 18.7292 | -352.6937 | 16.8587
12:14 | 3267 | 35.6351 | 199.8553 | 446.6452 | 450.9593 | -17.507 | -43.6827 | 9.4025 | 5.8891 | -0.0774 | -1.5208 | 1.4653 | -2.0203 | 9.8884 | 2.8484 | 0.6075 | 0.6461 | 0.9534 | 0.7274 | -130.2825 | -3.1931 | 4.2595 | 0.9664 | -4.6421 | -2.9626 | 3.2053 |  | 1.6769 | -0.8104 | 4.0104 | 3.3674 | 3.3515 | 1.0525 | 10.7705 | 14.2504 | 14.8333 | 11.0875 | 0.0001 | -0.0024 | 0.001 | 0.0041 | 0.0009 | 0.0001 | 0.0089 | -0.0157 | -0.0061 | -360.1835 | 17.4028 | -360.4327 | 17.6636 | -360.7989 | 18.1604 | -360.8727 | 17.5219 | -352.6598 | 18.721 | -352.6844 | 16.8361
12:14 | 3268 | 35.6553 | 199.8478 | 446.6817 | 450.9285 | -17.4316 | -43.6201 | 9.3919 | 5.9422 | -0.0173 | -1.5445 | 1.4968 | -2.0048 | 9.8612 | 2.8704 | 0.6064 | 0.6503 | 0.9583 | 0.7265 | -130.2468 | -3.2001 | 4.1862 | 1.0249 | -4.6247 | -2.8392 | 3.2547 |  | 1.7004 | -0.8209 | 4.0101 | 3.3651 | 3.3483 | 1.0528 | 10.7717 | 14.2745 | 14.8046 | 11.0774 | 0.0003 | -0.003 | 0.0007 | 0.0037 | 0.0008 | -0.0008 | 0.0082 | -0.0086 | 0.0003 | -360.1896 | 17.3966 | -360.4696 | 17.6779 | -360.8174 | 18.1584 | -360.8574 | 17.5157 | -352.626 | 18.7271 | -352.6875 | 16.8525
12:14 | 3269 | 35.6855 | 199.7853 | 446.6122 | 450.9064 | -17.3839 | -43.7136 | 9.4194 | 5.9156 | -0.0404 | -1.4976 | 1.5026 | -2.0431 | 9.9242 | 2.869 | 0.6072 | 0.6481 | 0.9583 | 0.7248 | -130.302 | -3.193 | 4.2502 | 1.0242 | -4.5727 | -2.8453 | 3.2673 |  | 1.658 | -0.7452 | 4.0108 | 3.3631 | 3.3489 | 1.0519 | 10.7612 | 14.2641 | 14.8292 | 11.0785 | 0.0003 | -0.0025 | 0.0009 | 0.0041 | 0.0006 | 0.0003 | -0.0031 | -0.0119 | -0.0176 | -360.1681 | 17.4213 | -360.4973 | 17.6841 | -360.8604 | 18.1871 | -360.8758 | 17.5178 | -352.6783 | 18.7456 | -352.706 | 16.8689
12:14 | 3270 | 35.7078 | 199.892 | 446.623 | 450.9101 | -17.3249 | -43.7062 | 9.4054 | 5.9357 | 0.0163 | -1.4415 | 1.4982 | -2.0987 | 9.9535 | 2.8618 | 0.6084 | 0.6494 | 0.96 | 0.7277 | -130.2124 | -3.2434 | 4.2297 | 1.0394 | -4.6226 | -2.9205 | 3.2721 |  | 1.7236 | -0.7423 | 4.0121 | 3.3633 | 3.348 | 1.0521 | 10.722 | 14.2475 | 14.7695 | 11.0518 | -0.0004 | -0.0026 | 0.0008 | 0.0038 | 0.0008 | -0.0013 | 0.0148 | 0.0053 | -0.0075 | -360.1435 | 17.3884 | -360.4512 | 17.6656 | -360.8081 | 18.1666 | -360.8512 | 17.5219 | -352.6229 | 18.7128 | -352.666 | 16.8423
12:14 | 3271 | 35.6744 | 199.9333 | 446.6971 | 450.8644 | -17.3513 | -43.6899 | 9.518 | 5.9595 | 0.0678 | -1.4724 | 1.5723 | -2.0455 | 9.9199 | 2.8512 | 0.6069 | 0.6514 | 0.9573 | 0.7251 | -130.2848 | -3.2948 | 4.1836 | 0.9406 | -4.5988 | -3.0103 | 3.1844 |  | 1.7468 | -0.7703 | 4.0118 | 3.3638 | 3.3504 | 1.0517 | 10.7522 | 14.2542 | 14.8034 | 11.0768 | -0.0005 | -0.0029 | 0.0003 | 0.0037 | 0.0004 | -0.0001 | 0.0112 | -0.0149 | -0.0216 | -360.1896 | 17.409 | -360.4912 | 17.6718 | -360.7958 | 18.1666 | -360.9035 | 17.5219 | -352.6413 | 18.7395 | -352.6813 | 16.8464
12:14 | 3272 | 35.756 | 199.8814 | 446.7147 | 450.8811 | -17.381 | -43.6696 | 9.4962 | 5.9232 | 0.0997 | -1.3993 | 1.5781 | -2.0872 | 9.8405 | 2.9012 | 0.6052 | 0.6474 | 0.9559 | 0.7252 | -130.2575 | -3.2755 | 4.2281 | 0.9917 | -4.5821 | -3.0815 | 3.2461 |  | 1.7516 | -0.7859 | 4.0107 | 3.3655 | 3.3465 | 1.0508 | 10.7395 | 14.2241 | 14.8021 | 11.0468 | 0.0003 | -0.0032 | 0.0007 | 0.0038 | 0.001 | -0.0005 | 0.0074 | -0.0103 | -0.0158 | -360.1958 | 17.409 | -360.4635 | 17.6738 | -360.8297 | 18.1687 | -360.8943 | 17.5321 | -352.6967 | 18.7436 | -352.6783 | 16.8566
12:14 | 3273 | 35.7378 | 199.9014 | 446.7303 | 450.9143 | -17.4506 | -43.621 | 9.3563 | 5.9955 | 0.1351 | -1.5102 | 1.4639 | -2.0759 | 9.8279 | 2.8382 | 0.6074 | 0.6471 | 0.9557 | 0.7262 | -130.2381 | -3.255 | 4.283 | 0.9243 | -4.5578 | -3.0234 | 3.2754 |  | 1.6798 | -0.8381 | 4.0115 | 3.3651 | 3.3523 | 1.0518 | 10.7291 | 14.2195 | 14.7861 | 11.0363 | -0.0001 | -0.0032 | 0.001 | 0.004 | 0.0011 | -0.0005 | 0.013 | -0.0177 | -0.003 | -360.1435 | 17.3946 | -360.4389 | 17.6574 | -360.7743 | 18.1502 | -360.8481 | 17.5157 | -352.626 | 18.7292 | -352.6537 | 16.8423
12:14 | 3274 | 35.7282 | 199.9074 | 446.6661 | 450.8127 | -17.4672 | -43.632 | 9.3902 | 5.8557 | 0.0935 | -1.5401 | 1.5277 | -2.0565 | 9.9426 | 2.9256 | 0.6074 | 0.6457 | 0.9544 | 0.7272 | -130.2474 | -3.3055 | 4.2533 | 0.8781 | -4.569 | -2.999 | 3.2691 |  | 1.7317 | -0.8058 | 4.0115 | 3.3683 | 3.3534 | 1.0517 | 10.737 | 14.2106 | 14.762 | 11.0724 | 0.0003 | -0.0022 | 0.001 | 0.0037 | 0.0009 | -0.0004 | 0.0085 | -0.0118 | -0.0031 | -360.2019 | 17.4048 | -360.4912 | 17.6759 | -360.8235 | 18.183 | -360.8789 | 17.5239 | -352.6906 | 18.7436 | -352.6813 | 16.8402
12:14 | 3275 | 35.7151 | 199.8022 | 446.6921 | 450.7056 | -17.4323 | -43.797 | 9.291 | 5.851 | 0.0901 | -1.519 | 1.5447 | -2.0977 | 10.0156 | 2.9502 | 0.6072 | 0.6494 | 0.9564 | 0.7258 | -130.3229 | -3.2218 | 4.3006 | 0.8633 | -4.5443 | -2.9914 | 3.3342 |  | 1.7062 | -0.7963 | 4.0124 | 3.3651 | 3.351 | 1.0517 | 10.7382 | 14.2521 | 14.8086 | 11.0912 | -0.0004 | -0.0027 | 0.0007 | 0.004 | 0.0012 | -0.001 | 0.0129 | -0.0054 | -0.0091 | -360.1896 | 17.411 | -360.4819 | 17.6882 | -360.8512 | 18.1789 | -360.9127 | 17.5363 | -352.6844 | 18.7374 | -352.6998 | 16.8546
12:14 | 3276 | 35.6761 | 199.8402 | 446.7118 | 450.7429 | -17.4532 | -43.7334 | 9.2911 | 5.8913 | 0.1469 | -1.4274 | 1.603 | -1.9647 | 9.9204 | 2.8861 | 0.606 | 0.6496 | 0.9548 | 0.7261 | -130.2968 | -3.1548 | 4.354 | 0.8872 | -4.527 | -3.0039 | 3.3842 |  | 1.6876 | -0.8493 | 4.0122 | 3.3641 | 3.3501 | 1.0527 | 10.7625 | 14.265 | 14.8458 | 11.0919 | 0 | -0.0031 | 0.0008 | 0.0038 | 0.0006 | -0.0004 | 0.0175 | 0.0071 | -0.0282 | -360.1588 | 17.3905 | -360.4266 | 17.6553 | -360.7712 | 18.1666 | -360.8512 | 17.5137 | -352.6383 | 18.723 | -352.6567 | 16.8279
12:14 | 3277 | 35.6186 | 199.9293 | 446.7383 | 450.8269 | -17.4432 | -43.8028 | 9.3933 | 5.9284 | 0.2076 | -1.3747 | 1.6185 | -2.0567 | 9.8588 | 2.8476 | 0.6065 | 0.65 | 0.9566 | 0.7272 | -130.285 | -3.1728 | 4.4066 | 0.8037 | -4.5978 | -3.118 | 3.2797 |  | 1.6109 | -0.8243 | 4.0125 | 3.3658 | 3.3538 | 1.0517 | 10.7683 | 14.2419 | 14.811 | 11.0688 | 0.0003 | -0.003 | 0.0007 | 0.0042 | 0.0007 | -0.0006 | 0.0127 | 0.0013 | -0.0098 | -360.205 | 17.4069 | -360.4881 | 17.68 | -360.8266 | 18.1769 | -360.885 | 17.5239 | -352.6475 | 18.7415 | -352.669 | 16.8381
12:14 | 3278 | 35.7058 | 199.8636 | 446.7522 | 450.8455 | -17.4729 | -43.7002 | 9.3561 | 5.9612 | 0.1259 | -1.4394 | 1.6435 | -1.9977 | 9.9641 | 2.9105 | 0.6068 | 0.6508 | 0.9572 | 0.7262 | -130.2785 | -3.127 | 4.4155 | 0.9787 | -4.5883 | -2.9991 | 3.3416 |  | 1.6876 | -0.7797 | 4.0114 | 3.3661 | 3.3503 | 1.0525 | 10.7475 | 14.2729 | 14.8174 | 11.0717 | -0.0004 | -0.003 | 0.0008 | 0.0038 | 0.0001 | -0.0005 | -0.0036 | 0.0054 | -0.0106 | -360.2081 | 17.4151 | -360.4942 | 17.682 | -360.7989 | 18.1769 | -360.9035 | 17.528 | -352.6444 | 18.7538 | -352.7429 | 16.8525
12:14 | 3279 | 35.74 | 199.8863 | 446.7531 | 450.8552 | -17.4454 | -43.6143 | 9.4071 | 5.9386 | 0.1167 | -1.3982 | 1.5575 | -1.9869 | 10.0006 | 2.9416 | 0.6091 | 0.6495 | 0.9572 | 0.7267 | -130.2593 | -3.1816 | 4.39 | 0.9949 | -4.5804 | -2.9732 | 3.3 |  | 1.7444 | -0.7666 | 4.011 | 3.3661 | 3.3501 | 1.0513 | 10.7302 | 14.2208 | 14.8232 | 11.0659 | -0.0003 | -0.0026 | 0.0004 | 0.0036 | 0.0008 | -0.0007 | 0.0162 | -0.0128 | 0.0056 | -360.1281 | 17.3843 | -360.445 | 17.6553 | -360.7958 | 18.1584 | -360.8327 | 17.5137 | -352.6044 | 18.7087 | -352.6413 | 16.8402
12:14 | 3280 | 35.7634 | 199.9499 | 446.6869 | 450.7984 | -17.4311 | -43.6938 | 9.4093 | 5.9926 | 0.1347 | -1.4552 | 1.6176 | -1.9892 | 10.0044 | 2.8782 | 0.606 | 0.6484 | 0.955 | 0.7259 | -130.2516 | -3.1946 | 4.4321 | 1.0394 | -4.5241 | -2.993 | 3.3162 |  | 1.713 | -0.797 | 4.0098 | 3.3644 | 3.3514 | 1.0513 | 10.7292 | 14.2134 | 14.7666 | 11.0487 | -0.0001 | -0.0035 | 0.0003 | 0.0036 | 0.0004 | -0.0006 | 0.0103 | -0.0266 | -0.0044 | -360.1681 | 17.4151 | -360.4635 | 17.6697 | -360.8174 | 18.1748 | -360.8666 | 17.5301 | -352.6413 | 18.7374 | -352.6506 | 16.834
12:14 | 3281 | 35.6208 | 199.957 | 446.7074 | 450.7853 | -17.4219 | -43.6658 | 9.4273 | 5.9745 | 0.1349 | -1.4949 | 1.6388 | -1.9707 | 10.0518 | 2.8648 | 0.606 | 0.6456 | 0.9594 | 0.7254 | -130.3169 | -3.1876 | 4.4801 | 1.0545 | -4.5591 | -3.0319 | 3.3339 |  | 1.5584 | -0.8951 | 4.011 | 3.3652 | 3.3489 | 1.0525 | 10.7338 | 14.2297 | 14.7894 | 11.0183 | -0.0001 | -0.0032 | 0.0008 | 0.0039 | 0.001 | -0.0005 | 0.0132 | -0.0114 | 0.0039 | -360.2111 | 17.4213 | -360.4666 | 17.682 | -360.842 | 18.1851 | -360.8758 | 17.5363 | -352.6998 | 18.7518 | -352.6937 | 16.8505
12:14 | 3282 | 35.7442 | 199.9821 | 446.7516 | 450.7603 | -17.4661 | -43.6993 | 9.4176 | 6.0196 | 0.1865 | -1.5109 | 1.6735 | -2.0375 | 9.9995 | 2.9286 | 0.6071 | 0.647 | 0.9591 | 0.7272 | -130.3544 | -3.1845 | 4.4382 | 1.2014 | -4.579 | -2.9567 | 3.4117 |  | 1.6228 | -0.8215 | 4.0118 | 3.3662 | 3.3502 | 1.0527 | 10.7556 | 14.2349 | 14.8155 | 11.0908 | -0.0005 | -0.0031 | 0.0005 | 0.0036 | 0.001 | 0.0001 | 0.0203 | 0.0041 | -0.0078 | -360.1342 | 17.3946 | -360.4727 | 17.6636 | -360.7835 | 18.1481 | -360.8481 | 17.5075 | -352.6537 | 18.7271 | -352.6537 | 16.8361
12:14 | 3283 | 35.6804 | 199.9715 | 446.7263 | 450.7871 | -17.5108 | -43.6783 | 9.3696 | 5.9714 | 0.1465 | -1.4046 | 1.7113 | -1.9809 | 9.9601 | 2.9068 | 0.6078 | 0.6484 | 0.9581 | 0.7277 | -130.3716 | -3.2628 | 4.468 | 1.0412 | -4.6168 | -2.9809 | 3.2893 |  | 1.5628 | -0.8379 | 4.0122 | 3.3615 | 3.3493 | 1.0533 | 10.7349 | 14.2022 | 14.7513 | 11.0421 | -0.0003 | -0.0027 | 0.001 | 0.0041 | 0.0005 | -0.0007 | 0.0133 | -0.0122 | 0.0062 | -360.1588 | 17.4192 | -360.4973 | 17.68 | -360.8481 | 18.183 | -360.8758 | 17.5137 | -352.6783 | 18.7497 | -352.6998 | 16.8402
12:14 | 3284 | 35.7342 | 199.9621 | 446.7651 | 450.8053 | -17.3528 | -43.663 | 9.3027 | 6.053 | 0.2533 | -1.4401 | 1.6693 | -2.0187 | 9.9622 | 2.7831 | 0.6072 | 0.6485 | 0.9587 | 0.7267 | -130.2718 | -3.1965 | 4.4372 | 1.0806 | -4.5634 | -3.016 | 3.3867 |  | 1.725 | -0.8686 | 4.0119 | 3.3656 | 3.349 | 1.0514 | 10.7611 | 14.2934 | 14.8255 | 11.1182 | 0.0003 | -0.0028 | 0.001 | 0.0038 | 0.0009 | -0.0003 | 0.0108 | -0.0064 | -0.0082 | -360.1835 | 17.4069 | -360.4789 | 17.68 | -360.8174 | 18.1748 | -360.9158 | 17.5363 | -352.6813 | 18.7271 | -352.6875 | 16.8546
12:14 | 3285 | 35.6731 | 199.9704 | 446.8273 | 450.7448 | -17.4292 | -43.7928 | 9.4145 | 6.0079 | 0.2228 | -1.59 | 1.69 | -1.8997 | 10.015 | 2.8762 | 0.6061 | 0.6486 | 0.9597 | 0.7269 | -130.2953 | -3.1725 | 4.4354 | 1.0567 | -4.579 | -2.9601 | 3.3726 |  | 1.6859 | -0.8189 | 4.0127 | 3.3674 | 3.3489 | 1.052 | 10.7856 | 14.2825 | 14.8584 | 11.1031 | 0 | -0.0032 | 0.0005 | 0.0039 | 0.0005 | -0.0005 | 0.0106 | -0.0115 | -0.0153 | -360.1435 | 17.4007 | -360.4327 | 17.6369 | -360.762 | 18.1666 | -360.8481 | 17.5178 | -352.6752 | 18.7251 | -352.6537 | 16.8197
12:14 | 3286 | 35.655 | 200.0645 | 446.8147 | 450.7872 | -17.4597 | -43.8317 | 9.3647 | 6.0617 | 0.2795 | -1.5467 | 1.6857 | -1.9303 | 10.0104 | 2.8646 | 0.6068 | 0.6459 | 0.9556 | 0.7262 | -130.193 | -3.239 | 4.388 | 0.9715 | -4.6928 | -3.0077 | 3.3566 |  | 1.6744 | -0.8713 | 4.0117 | 3.3682 | 3.3506 | 1.0524 | 10.7729 | 14.2581 | 14.8444 | 11.085 | 0 | -0.0028 | 0.0007 | 0.0038 | 0.0011 | -0.0005 | 0.0013 | -0.0187 | -0.0184 | -360.2173 | 17.4192 | -360.4819 | 17.682 | -360.842 | 18.1707 | -360.8635 | 17.5424 | -352.6875 | 18.7518 | -352.6906 | 16.8402
12:14 | 3287 | 35.6734 | 200.0299 | 446.7674 | 450.7729 | -17.4282 | -43.7438 | 9.3083 | 5.9914 | 0.1998 | -1.6184 | 1.6779 | -1.9181 | 10.068 | 2.905 | 0.6086 | 0.65 | 0.9569 | 0.7275 | -130.2404 | -3.2417 | 4.3321 | 0.7699 | -4.7357 | -2.9726 | 3.3265 |  | 1.6653 | -0.8253 | 4.0115 | 3.3617 | 3.35 | 1.0532 | 10.767 | 14.2585 | 14.8476 | 11.0955 | 0 | -0.0023 | 0.0003 | 0.0037 | 0.0012 | 0.0002 | 0.0116 | -0.0128 | -0.0129 | -360.1619 | 17.411 | -360.4912 | 17.6718 | -360.8297 | 18.1728 | -360.882 | 17.5116 | -352.6567 | 18.7497 | -352.6906 | 16.8525
12:15 | 3288 | 35.7612 | 200.0254 | 446.8442 | 450.7746 | -17.3876 | -43.7151 | 9.2852 | 6.0852 | 0.2427 | -1.4231 | 1.7345 | -1.8352 | 10.0444 | 2.8509 | 0.6083 | 0.6481 | 0.9588 | 0.7295 | -130.337 | -3.2611 | 4.3162 | 0.8499 | -4.6793 | -2.9737 | 3.2814 |  | 1.6935 | -0.7876 | 4.0094 | 3.365 | 3.3505 | 1.0526 | 10.7268 | 14.2518 | 14.8065 | 11.0573 | -0.0005 | -0.003 | 0.0007 | 0.0038 | 0.0008 | -0.0008 | 0.0156 | -0.0042 | 0.0188 | -360.1496 | 17.374 | -360.4358 | 17.6636 | -360.802 | 18.1543 | -360.8574 | 17.5116 | -352.6136 | 18.7189 | -352.6198 | 16.8258
12:15 | 3289 | 35.7326 | 199.9235 | 446.7991 | 450.7055 | -17.4851 | -43.7525 | 9.252 | 6.0766 | 0.2683 | -1.5249 | 1.7432 | -1.8969 | 10.1024 | 2.9981 | 0.607 | 0.6482 | 0.9562 | 0.726 | -130.275 | -3.2025 | 4.3851 | 0.984 | -4.5823 | -2.9912 | 3.3532 |  | 1.6813 | -0.7747 | 4.0117 | 3.3682 | 3.354 | 1.0526 | 10.751 | 14.2186 | 14.7984 | 11.0749 | 0.0004 | -0.0031 | 0.0011 | 0.004 | 0.0005 | -0.0002 | 0.0061 | -0.0184 | -0.0347 | -360.1681 | 17.4213 | -360.4881 | 17.6677 | -360.8081 | 18.1789 | -360.9004 | 17.5404 | -352.6813 | 18.7395 | -352.6629 | 16.8279
12:15 | 3290 | 35.7227 | 199.9091 | 446.8371 | 450.7069 | -17.5759 | -43.6796 | 9.2093 | 5.9932 | 0.1905 | -1.5302 | 1.649 | -1.9245 | 10.0748 | 3.0781 | 0.6073 | 0.6483 | 0.9614 | 0.7284 | -130.1559 | -3.157 | 4.4322 | 1.0451 | -4.5579 | -2.9621 | 3.424 |  | 1.6453 | -0.7594 | 4.0124 | 3.3658 | 3.3502 | 1.0527 | 10.7289 | 14.2431 | 14.8008 | 11.0294 | -0.0001 | -0.0032 | 0.001 | 0.0042 | 0.0013 | -0.0006 | 0.0168 | 0.0021 | -0.0113 | -360.2081 | 17.4069 | -360.5004 | 17.6759 | -360.8174 | 18.1563 | -360.8789 | 17.5301 | -352.669 | 18.7436 | -352.7029 | 16.8423
12:15 | 3291 | 35.7622 | 199.947 | 446.781 | 450.7082 | -17.584 | -43.6695 | 9.2846 | 5.9781 | 0.2022 | -1.5534 | 1.6564 | -1.8308 | 10.0513 | 3.0615 | 0.6062 | 0.6474 | 0.9591 | 0.7269 | -130.2058 | -3.1855 | 4.3406 | 1.165 | -4.5633 | -2.8978 | 3.4367 |  | 1.5701 | -0.8531 | 4.0123 | 3.3672 | 3.3516 | 1.0518 | 10.7197 | 14.2163 | 14.7841 | 11.0323 | -0.0001 | -0.0025 | 0.0006 | 0.0039 | 0.0003 | -0.0004 | 0.0201 | -0.0023 | -0.025 | -360.1127 | 17.3905 | -360.4573 | 17.6759 | -360.802 | 18.1604 | -360.845 | 17.4972 | -352.6167 | 18.7189 | -352.6537 | 16.8443
12:15 | 3292 | 35.7501 | 199.9455 | 446.808 | 450.7605 | -17.4536 | -43.6271 | 9.1692 | 5.9737 | 0.2248 | -1.5328 | 1.6684 | -1.7437 | 10.0241 | 3.0582 | 0.6061 | 0.6482 | 0.9598 | 0.7273 | -130.1978 | -3.2608 | 4.3329 | 1.1799 | -4.5837 | -2.9205 | 3.3707 |  | 1.708 | -0.789 | 4.0109 | 3.3659 | 3.3495 | 1.052 | 10.7254 | 14.2281 | 14.7862 | 11.0431 | -0.0001 | -0.0026 | 0.0009 | 0.0038 | 0.0014 | -0.0004 | 0.0233 | -0.0077 | -0.0091 | -360.1804 | 17.4069 | -360.4604 | 17.7005 | -360.8574 | 18.1789 | -360.8789 | 17.5301 | -352.6537 | 18.7312 | -352.7029 | 16.8464
12:15 | 3293 | 35.8027 | 199.9964 | 446.8827 | 450.7594 | -17.3839 | -43.5651 | 9.249 | 6.0133 | 0.2185 | -1.5215 | 1.6098 | -1.9125 | 9.9427 | 3.0985 | 0.6078 | 0.6486 | 0.9597 | 0.7277 | -130.1626 | -3.2466 | 4.4452 | 1.1257 | -4.5323 | -2.8025 | 3.3776 |  | 1.7298 | -0.8816 | 4.0124 | 3.3646 | 3.3505 | 1.0517 | 10.7348 | 14.2717 | 14.7929 | 11.0648 | 0.0002 | -0.0027 | 0 | 0.0032 | 0.0007 | -0.0003 | 0.0059 | -0.0145 | -0.0209 | -360.205 | 17.4172 | -360.4573 | 17.6718 | -360.8081 | 18.181 | -360.9004 | 17.5424 | -352.6629 | 18.7538 | -352.6844 | 16.8361
12:15 | 3294 | 35.8076 | 200.1232 | 446.9183 | 450.8179 | -17.3399 | -43.4841 | 9.3173 | 6.0264 | 0.2157 | -1.4056 | 1.582 | -1.9747 | 9.9744 | 3.0433 | 0.6074 | 0.6507 | 0.9596 | 0.7259 | -130.2175 | -3.1491 | 4.473 | 1.1656 | -4.6203 | -2.8668 | 3.3671 |  | 1.7832 | -0.7475 | 4.0124 | 3.3653 | 3.3515 | 1.0527 | 10.7579 | 14.2544 | 14.8219 | 11.0706 | 0.0003 | -0.0031 | 0.0008 | 0.0042 | 0.0009 | -0.0004 | 0.0142 | -0.0078 | -0.0079 | -360.1465 | 17.3966 | -360.4512 | 17.6656 | -360.762 | 18.144 | -360.8297 | 17.5096 | -352.6444 | 18.7374 | -352.666 | 16.8258
12:15 | 3295 | 35.7585 | 199.9438 | 446.8059 | 450.7471 | -17.3656 | -43.5823 | 9.2626 | 6.0593 | 0.2208 | -1.4696 | 1.5533 | -1.8727 | 9.961 | 3.0937 | 0.6066 | 0.649 | 0.9581 | 0.7265 | -130.2172 | -3.2176 | 4.3968 | 1.1691 | -4.548 | -2.752 | 3.4884 |  | 1.7759 | -0.85 | 4.01 | 3.3656 | 3.3502 | 1.0537 | 10.7277 | 14.2883 | 14.8005 | 11.08 | -0.0001 | -0.0021 | 0.0013 | 0.0043 | 0.0007 | -0.0004 | 0.0191 | 0.0007 | 0.0078 | -360.1496 | 17.4192 | -360.4696 | 17.6779 | -360.8112 | 18.1666 | -360.8543 | 17.5157 | -352.6321 | 18.7497 | -352.6906 | 16.8423
12:15 | 3296 | 35.772 | 200.0058 | 446.7974 | 450.7421 | -17.4778 | -43.5857 | 9.2672 | 6.0624 | 0.1539 | -1.4602 | 1.65 | -1.7753 | 9.9617 | 3.0737 | 0.6068 | 0.6482 | 0.957 | 0.727 | -130.1724 | -3.0928 | 4.3869 | 1.1466 | -4.5652 | -2.826 | 3.362 |  | 1.687 | -0.8268 | 4.0124 | 3.3672 | 3.3489 | 1.0535 | 10.7706 | 14.2441 | 14.8243 | 11.0655 | -0.0002 | -0.0028 | 0.0006 | 0.004 | 0.0007 | -0.0002 | 0.0016 | -0.0093 | -0.0065 | -360.205 | 17.4028 | -360.4512 | 17.6902 | -360.845 | 18.183 | -360.885 | 17.5445 | -352.6475 | 18.7374 | -352.6906 | 16.8525
12:15 | 3297 | 35.752 | 200.0278 | 446.797 | 450.7367 | -17.4303 | -43.6264 | 9.2679 | 6.0591 | 0.1414 | -1.3948 | 1.6416 | -1.8989 | 9.9467 | 3.0534 | 0.6061 | 0.6476 | 0.9586 | 0.7266 | -130.2205 | -3.0012 | 4.4789 | 1.1232 | -4.6552 | -2.8825 | 3.4225 |  | 1.6614 | -0.7771 | 4.0129 | 3.3676 | 3.3521 | 1.0527 | 10.7059 | 14.208 | 14.7745 | 11.019 | -0.0004 | -0.0031 | 0.001 | 0.0037 | 0.0011 | -0.0007 | 0.008 | -0.0157 | -0.0022 | -360.1404 | 17.3946 | -360.4389 | 17.643 | -360.7743 | 18.1584 | -360.8604 | 17.528 | -352.6629 | 18.7169 | -352.6752 | 16.8258
12:15 | 3298 | 35.7874 | 199.9413 | 446.7441 | 450.7168 | -17.4614 | -43.7302 | 9.3387 | 6.117 | 0.1487 | -1.3678 | 1.5306 | -1.8943 | 9.9643 | 3.0008 | 0.6065 | 0.6504 | 0.958 | 0.7272 | -130.1903 | -3.0949 | 4.494 | 0.9818 | -4.6468 | -2.8822 | 3.4415 |  | 1.69 | -0.8679 | 4.0115 | 3.3638 | 3.3532 | 1.0547 | 10.7544 | 14.2628 | 14.8673 | 11.0836 | 0.0002 | -0.0029 | 0.001 | 0.0036 | 0.0003 | -0.0007 | 0.0116 | -0.019 | -0.0173 | -360.2019 | 17.4131 | -360.4604 | 17.6594 | -360.8235 | 18.1563 | -360.8358 | 17.528 | -352.6567 | 18.7395 | -352.6383 | 16.8279
12:15 | 3299 | 35.7472 | 199.9018 | 446.8171 | 450.6219 | -17.4027 | -43.715 | 9.2895 | 6.045 | 0.1038 | -1.4559 | 1.445 | -1.8457 | 10.0169 | 3.0137 | 0.6068 | 0.6503 | 0.9534 | 0.726 | -130.175 | -3.0633 | 4.5836 | 1.0116 | -4.6473 | -2.9592 | 3.3611 |  | 1.6671 | -0.8031 | 4.012 | 3.3655 | 3.3511 | 1.0536 | 10.7614 | 14.2635 | 14.8133 | 11.0627 | -0.0005 | -0.0033 | 0.0004 | 0.0034 | 0.0011 | -0.0005 | 0.0189 | -0.012 | -0.0202 | -360.1865 | 17.4172 | -360.5127 | 17.6923 | -360.8204 | 18.1851 | -360.8881 | 17.526 | -352.6629 | 18.7538 | -352.709 | 16.8587
12:15 | 3300 | 35.8101 | 199.932 | 446.8747 | 450.741 | -17.4131 | -43.6326 | 9.3938 | 5.9974 | 0.1422 | -1.4265 | 1.486 | -1.9909 | 9.9543 | 2.9055 | 0.6065 | 0.6534 | 0.9589 | 0.7273 | -130.1187 | -3.0425 | 4.5786 | 1.0681 | -4.5576 | -2.9603 | 3.4652 |  | 1.6989 | -0.7633 | 4.0114 | 3.3668 | 3.3504 | 1.0542 | 10.7498 | 14.2523 | 14.8155 | 11.0793 | -0.0002 | -0.0026 | 0.0007 | 0.0036 | 0.0005 | -0.0004 | -0.0032 | -0.0057 | -0.0171 | -360.1588 | 17.3905 | -360.445 | 17.6718 | -360.7989 | 18.1707 | -360.845 | 17.5055 | -352.6321 | 18.723 | -352.6598 | 16.8361
12:15 | 3301 | 35.8662 | 200.0452 | 446.9583 | 450.7842 | -17.5865 | -43.7411 | 9.2721 | 6.0089 | 0.1439 | -1.4747 | 1.5133 | -1.8765 | 9.9794 | 3.0591 | 0.6074 | 0.6514 | 0.9566 | 0.7287 | -130.1421 | -3.0934 | 4.5398 | 0.9681 | -4.5368 | -2.8757 | 3.4695 |  | 1.6257 | -0.8835 | 4.0123 | 3.3654 | 3.3525 | 1.0541 | 10.7579 | 14.2372 | 14.8403 | 11.0876 | 0.0001 | -0.003 | 0.0003 | 0.0034 | 0.0011 | -0.0008 | 0.0089 | -0.0058 | 0.0084 | -360.1404 | 17.3966 | -360.4481 | 17.6718 | -360.7804 | 18.1728 | -360.8758 | 17.5116 | -352.6167 | 18.7333 | -352.6444 | 16.8258
12:15 | 3302 | 35.8679 | 199.9838 | 446.9172 | 450.8264 | -17.564 | -43.8088 | 9.2561 | 6.0117 | 0.232 | -1.4498 | 1.5173 | -1.8653 | 10.0784 | 3.0767 | 0.6061 | 0.6508 | 0.9582 | 0.7276 | -130.176 | -3.0806 | 4.504 | 0.8669 | -4.4495 | -2.8657 | 3.4805 |  | 1.6665 | -0.8649 | 4.0123 | 3.3675 | 3.3513 | 1.0537 | 10.7511 | 14.253 | 14.7789 | 11.0641 | -0.0003 | -0.0035 | 0.0005 | 0.0038 | 0.0003 | -0.0002 | 0.0103 | 0.0007 | -0.0086 | -360.2296 | 17.4233 | -360.4942 | 17.6985 | -360.8297 | 18.1933 | -360.8974 | 17.5363 | -352.666 | 18.76 | -352.6783 | 16.8464
12:15 | 3303 | 35.8089 | 199.9539 | 446.8099 | 450.7944 | -17.5644 | -43.786 | 9.2904 | 6.0134 | 0.2014 | -1.4091 | 1.4531 | -1.9395 | 10.0114 | 2.9804 | 0.608 | 0.6517 | 0.9599 | 0.7297 | -130.1326 | -3.0017 | 4.6134 | 0.8441 | -4.3744 | -2.8429 | 3.505 |  | 1.5436 | -0.9126 | 4.0113 | 3.3694 | 3.3508 | 1.0516 | 10.7694 | 14.2142 | 14.8182 | 11.0583 | 0.0001 | -0.0028 | 0.001 | 0.0042 | 0.0011 | -0.0005 | 0.0234 | -0.0168 | 0.0159 | -360.1742 | 17.409 | -360.4973 | 17.6985 | -360.7989 | 18.1769 | -360.8758 | 17.5219 | -352.669 | 18.7497 | -352.7306 | 16.8525
12:15 | 3304 | 35.8633 | 200.0177 | 446.8023 | 450.7397 | -17.6067 | -43.6965 | 9.2542 | 6.0671 | 0.2328 | -1.3536 | 1.6318 | -1.9315 | 10.0106 | 3.0199 | 0.6069 | 0.6476 | 0.9598 | 0.7261 | -130.1207 | -3.0015 | 4.5846 | 0.8404 | -4.3665 | -2.7708 | 3.5352 |  | 1.4741 | -0.918 | 4.011 | 3.3636 | 3.3528 | 1.0519 | 10.7326 | 14.1997 | 14.8054 | 11.0403 | -0.001 | -0.003 | 0.0003 | 0.0035 | 0.0009 | -0.0001 | 0.0058 | -0.0157 | -0.0219 | -360.1619 | 17.3905 | -360.4142 | 17.6718 | -360.7712 | 18.1625 | -360.845 | 17.5178 | -352.6383 | 18.721 | -352.6413 | 16.8361
12:15 | 3305 | 35.8642 | 199.8939 | 446.78 | 450.7219 | -17.6013 | -43.7166 | 9.2618 | 6.1034 | 0.2111 | -1.4314 | 1.5591 | -1.9558 | 10.0327 | 3.0606 | 0.6063 | 0.6486 | 0.9569 | 0.7289 | -130.0701 | -2.9344 | 4.5409 | 0.7733 | -4.3803 | -2.7763 | 3.5542 |  | 1.5814 | -0.871 | 4.0131 | 3.3633 | 3.35 | 1.0529 | 10.759 | 14.2268 | 14.8127 | 11.0598 | 0.0001 | -0.0026 | 0.001 | 0.0042 | 0.0008 | -0.0003 | 0.009 | -0.0011 | 0.0058 | -360.1342 | 17.4028 | -360.4604 | 17.68 | -360.8081 | 18.183 | -360.8727 | 17.5198 | -352.6321 | 18.7353 | -352.6813 | 16.832
12:15 | 3306 | 35.8281 | 199.9272 | 446.8069 | 450.7192 | -17.5757 | -43.6215 | 9.2801 | 6.1433 | 0.2822 | -1.353 | 1.5706 | -1.8725 | 9.9416 | 2.9527 | 0.6054 | 0.6521 | 0.9594 | 0.7276 | -130.0848 | -2.9736 | 4.5018 | 0.8138 | -4.3287 | -2.7953 | 3.5761 |  | 1.5355 | -0.8566 | 4.0118 | 3.3651 | 3.352 | 1.0515 | 10.7475 | 14.2383 | 14.8417 | 11.0598 | -0.0001 | -0.0033 | 0.0006 | 0.004 | 0.0009 | -0.0008 | 0.0149 | -0.0155 | -0.022 | -360.2142 | 17.4274 | -360.4696 | 17.7026 | -360.842 | 18.1974 | -360.8974 | 17.5342 | -352.6906 | 18.7518 | -352.6875 | 16.8587
12:15 | 3307 | 35.8057 | 199.9034 | 446.8255 | 450.7056 | -17.6135 | -43.6732 | 9.2839 | 6.1435 | 0.3209 | -1.448 | 1.5667 | -1.8828 | 10.0202 | 2.9357 | 0.6061 | 0.6498 | 0.9619 | 0.7288 | -130.0049 | -2.92 | 4.5906 | 0.8059 | -4.3044 | -2.7794 | 3.5137 |  | 1.5314 | -0.7866 | 4.0108 | 3.3658 | 3.3491 | 1.0507 | 10.7579 | 14.2312 | 14.8334 | 11.0706 | -0.0001 | -0.0031 | 0.0005 | 0.0033 | 0.0007 | -0.0002 | 0.0234 | -0.0062 | -0.0141 | -360.165 | 17.411 | -360.4542 | 17.6759 | -360.7927 | 18.1728 | -360.8604 | 17.5116 | -352.6506 | 18.7353 | -352.6875 | 16.8361
12:15 | 3308 | 35.8073 | 200.041 | 446.921 | 450.7628 | -17.5681 | -43.5833 | 9.2555 | 6.1462 | 0.4047 | -1.4215 | 1.5677 | -1.7487 | 9.9853 | 3.0105 | 0.6065 | 0.6488 | 0.9631 | 0.7275 | -130.0937 | -3.0029 | 4.5058 | 0.796 | -4.3288 | -2.8144 | 3.5097 |  | 1.4814 | -0.781 | 4.0122 | 3.365 | 3.3516 | 1.0513 | 10.707 | 14.2266 | 14.8117 | 11.0428 | 0 | -0.0025 | 0.0008 | 0.0038 | 0.001 | -0.0008 | 0.0229 | -0.0067 | -0.0066 | -360.1404 | 17.4131 | -360.4542 | 17.68 | -360.7958 | 18.1502 | -360.842 | 17.5075 | -352.6198 | 18.7271 | -352.6598 | 16.832
12:15 | 3309 | 35.9001 | 199.9527 | 446.8745 | 450.7629 | -17.6499 | -43.57 | 9.2164 | 6.1133 | 0.448 | -1.1631 | 1.6271 | -1.8508 | 9.946 | 2.9364 | 0.6069 | 0.6492 | 0.9597 | 0.7277 | -130.0607 | -3.0089 | 4.5712 | 0.9719 | -4.4671 | -2.8664 | 3.4935 |  | 1.5143 | -0.8659 | 4.0128 | 3.3673 | 3.3532 | 1.0515 | 10.7533 | 14.2555 | 14.7827 | 11.0428 | -0.0002 | -0.0026 | 0.0002 | 0.0035 | 0.0007 | -0.0002 | 0.0069 | -0.0175 | 0.0026 | -360.1896 | 17.4172 | -360.5158 | 17.7128 | -360.8389 | 18.183 | -360.9004 | 17.5363 | -352.6783 | 18.7374 | -352.6998 | 16.8587
12:15 | 3310 | 35.9267 | 199.9588 | 446.936 | 450.7134 | -17.65 | -43.6448 | 9.1728 | 6.1524 | 0.4104 | -1.2535 | 1.5953 | -1.9507 | 10.0219 | 2.8478 | 0.6076 | 0.6451 | 0.9562 | 0.7263 | -130.0065 | -2.9062 | 4.5834 | 0.9534 | -4.5047 | -2.8361 | 3.5419 |  | 1.5109 | -0.7248 | 4.0117 | 3.3651 | 3.3525 | 1.0531 | 10.7243 | 14.2327 | 14.7906 | 11.0478 | 0.0004 | -0.0029 | 0.0011 | 0.004 | 0.0012 | -0.0008 | 0.0054 | -0.0022 | -0.0078 | -360.1773 | 17.3925 | -360.4327 | 17.6841 | -360.8358 | 18.1666 | -360.8758 | 17.5219 | -352.6413 | 18.7415 | -352.6752 | 16.8402
12:15 | 3311 | 35.8859 | 199.9401 | 446.8633 | 450.7062 | -17.5716 | -43.5671 | 9.306 | 6.0954 | 0.3057 | -1.2731 | 1.574 | -1.8603 | 10.0643 | 2.9222 | 0.6064 | 0.6482 | 0.9586 | 0.7267 | -130.0345 | -2.9033 | 4.6333 | 0.9969 | -4.3555 | -2.8185 | 3.6128 |  | 1.5114 | -0.8071 | 4.0124 | 3.3652 | 3.3456 | 1.0524 | 10.7313 | 14.2452 | 14.8072 | 11.0728 | -0.0001 | -0.0033 | 0.0006 | 0.0042 | 0.0003 | -0.0004 | 0.0111 | -0.0018 | -0.0084 | -360.1465 | 17.3987 | -360.4481 | 17.6677 | -360.7712 | 18.1584 | -360.8574 | 17.5157 | -352.6506 | 18.7353 | -352.6506 | 16.8238
12:15 | 3312 | 35.8931 | 199.8837 | 446.7201 | 450.7809 | -17.5104 | -43.52 | 9.3742 | 6.0872 | 0.2135 | -1.4352 | 1.514 | -1.9148 | 10.0455 | 2.9333 | 0.6077 | 0.6505 | 0.9616 | 0.7275 | -129.9779 | -2.8914 | 4.6953 | 1.0656 | -4.4199 | -2.7908 | 3.5751 |  | 1.5077 | -0.7119 | 4.0121 | 3.3676 | 3.351 | 1.0538 | 10.7474 | 14.2501 | 14.8196 | 11.071 | -0.0001 | -0.0022 | 0.0005 | 0.0038 | 0.001 | -0.0005 | 0.0117 | -0.0101 | 0.0009 | -360.2173 | 17.4315 | -360.5004 | 17.6964 | -360.8235 | 18.183 | -360.8881 | 17.528 | -352.6752 | 18.762 | -352.6629 | 16.8381
12:15 | 3313 | 35.9629 | 199.9013 | 446.8263 | 450.8088 | -17.3931 | -43.4966 | 9.3399 | 6.1289 | 0.2767 | -1.1723 | 1.5804 | -1.9155 | 9.9096 | 2.9666 | 0.6078 | 0.6501 | 0.9587 | 0.7263 | -129.9838 | -2.869 | 4.7012 | 1.156 | -4.2998 | -2.7081 | 3.6679 |  | 1.4738 | -0.7479 | 4.0121 | 3.3697 | 3.3492 | 1.0535 | 10.7672 | 14.2406 | 14.7912 | 11.0623 | -0.0001 | -0.0027 | 0.0009 | 0.0041 | 0.0005 | -0.0003 | 0.0101 | -0.0119 | 0.0077 | -360.1804 | 17.4007 | -360.4758 | 17.7108 | -360.8174 | 18.1625 | -360.8789 | 17.5198 | -352.6383 | 18.7436 | -352.7029 | 16.8484
12:15 | 3314 | 35.9503 | 199.8543 | 446.8329 | 450.7994 | -17.4136 | -43.5846 | 9.3085 | 6.0664 | 0.2943 | -1.1699 | 1.5476 | -1.9456 | 9.9173 | 2.9569 | 0.6082 | 0.6516 | 0.9606 | 0.7261 | -129.9648 | -2.8279 | 4.6957 | 1.0749 | -4.262 | -2.7292 | 3.6997 |  | 1.4735 | -0.8519 | 4.0113 | 3.366 | 3.348 | 1.0521 | 10.7371 | 14.2335 | 14.7888 | 11.0501 | 0.0004 | -0.0033 | 0.0009 | 0.0037 | 0.0007 | -0.0006 | 0.0036 | -0.0037 | -0.0081 | -360.1527 | 17.3884 | -360.4296 | 17.6738 | -360.7897 | 18.1769 | -360.8666 | 17.4993 | -352.629 | 18.723 | -352.6413 | 16.8217
12:15 | 3315 | 35.9767 | 199.8776 | 446.793 | 450.7948 | -17.4036 | -43.5159 | 9.4087 | 5.9771 | 0.2836 | -1.2314 | 1.5397 | -1.8973 | 9.8975 | 2.9172 | 0.6073 | 0.651 | 0.9593 | 0.7268 | -129.9062 | -2.7979 | 4.6784 | 1.0288 | -4.2306 | -2.6664 | 3.6449 |  | 1.4883 | -0.9133 | 4.0119 | 3.3656 | 3.3491 | 1.0514 | 10.707 | 14.2613 | 14.7711 | 11.037 | 0.0004 | -0.0029 | 0.0005 | 0.0034 | 0.0009 | -0.0005 | 0.0168 | -0.0135 | -0.0155 | -360.1342 | 17.3987 | -360.4542 | 17.6902 | -360.8174 | 18.1769 | -360.8881 | 17.5342 | -352.6598 | 18.7312 | -352.6783 | 16.832
12:15 | 3316 | 35.9968 | 199.9704 | 446.8509 | 450.7844 | -17.3689 | -43.4533 | 9.4563 | 6.1029 | 0.2154 | -1.1616 | 1.5237 | -1.8203 | 10.004 | 2.9777 | 0.608 | 0.6488 | 0.9604 | 0.7252 | -130.0077 | -2.8247 | 4.6187 | 1.1402 | -4.3171 | -2.8612 | 3.6481 |  | 1.5144 | -0.7812 | 4.0105 | 3.3676 | 3.3474 | 1.0529 | 10.7465 | 14.2481 | 14.784 | 11.0718 | -0.0006 | -0.003 | 0.0006 | 0.004 | 0.0003 | -0.0005 | 0.016 | -0.0161 | -0.0086 | -360.2296 | 17.4295 | -360.5035 | 17.7026 | -360.8235 | 18.183 | -360.8727 | 17.5383 | -352.6844 | 18.762 | -352.7213 | 16.8505
12:15 | 3317 | 35.9443 | 199.9199 | 446.844 | 450.8598 | -17.4502 | -43.5666 | 9.3561 | 6.0988 | 0.2204 | -1.3389 | 1.5904 | -1.9063 | 9.9155 | 3.0014 | 0.6074 | 0.6495 | 0.9582 | 0.7271 | -130.0131 | -2.874 | 4.6218 | 1.1358 | -4.2593 | -2.7951 | 3.6331 |  | 1.5317 | -0.7672 | 4.0112 | 3.368 | 3.3489 | 1.0527 | 10.7348 | 14.2081 | 14.7871 | 11.0417 | 0.0002 | -0.0024 | 0.0008 | 0.0037 | 0.0008 | -0.0008 | 0.0088 | -0.0055 | -0.0182 | -360.1496 | 17.3987 | -360.4481 | 17.7067 | -360.802 | 18.1522 | -360.8574 | 17.5096 | -352.6321 | 18.7353 | -352.6906 | 16.8464
12:15 | 3318 | 35.9688 | 199.999 | 446.8205 | 450.8894 | -17.6296 | -43.5991 | 9.2304 | 6.1496 | 0.1817 | -1.3117 | 1.5365 | -1.8985 | 9.8294 | 3.0056 | 0.6066 | 0.6497 | 0.9574 | 0.7242 | -129.9095 | -2.772 | 4.631 | 1.0765 | -4.3103 | -2.8432 | 3.6294 |  | 1.4635 | -0.8327 | 4.0121 | 3.3664 | 3.3501 | 1.0543 | 10.7325 | 14.2406 | 14.826 | 11.0739 | 0.0002 | -0.0027 | 0.0007 | 0.0042 | 0.0007 | -0.0006 | 0.021 | -0.0086 | -0.0081 | -360.1127 | 17.3966 | -360.4666 | 17.6902 | -360.8266 | 18.1728 | -360.8266 | 17.4972 | -352.586 | 18.723 | -352.6537 | 16.8381
12:15 | 3319 | 35.9514 | 199.9853 | 446.7819 | 450.7902 | -17.5361 | -43.6652 | 9.2529 | 6.2058 | 0.1598 | -1.2721 | 1.5896 | -1.924 | 9.7751 | 2.9911 | 0.6055 | 0.6497 | 0.9595 | 0.7269 | -129.9381 | -2.7945 | 4.6718 | 1.0084 | -4.3821 | -2.7986 | 3.6258 |  | 1.5067 | -0.8087 | 4.012 | 3.3659 | 3.3474 | 1.0532 | 10.7452 | 14.2416 | 14.8205 | 11.0695 | -0.0001 | -0.0032 | 0.001 | 0.004 | 0.0006 | -0.0009 | 0.0266 | 0.0083 | -0.0105 | -360.1958 | 17.4151 | -360.4819 | 17.7128 | -360.8666 | 18.1912 | -360.8974 | 17.5465 | -352.6813 | 18.7538 | -352.6783 | 16.8443
12:15 | 3320 | 35.9549 | 200.0241 | 446.7929 | 450.8156 | -17.5838 | -43.7117 | 9.3136 | 6.1489 | 0.1198 | -1.2991 | 1.493 | -1.9715 | 9.7651 | 3.0074 | 0.6067 | 0.6526 | 0.9592 | 0.7253 | -130.0142 | -2.9048 | 4.6122 | 1.0111 | -4.3688 | -2.8709 | 3.5824 |  | 1.5003 | -0.7568 | 4.0113 | 3.3667 | 3.348 | 1.054 | 10.7578 | 14.249 | 14.8366 | 11.0695 | -0.0001 | -0.0029 | 0.0007 | 0.0039 | 0.0005 | -0.0003 | 0.0048 | -0.0042 | -0.0027 | -360.1835 | 17.4254 | -360.4727 | 17.6841 | -360.7927 | 18.1645 | -360.9035 | 17.5301 | -352.6813 | 18.7497 | -352.6967 | 16.834
12:15 | 3321 | 35.9683 | 200.0646 | 446.8362 | 450.8125 | -17.5176 | -43.6401 | 9.1934 | 6.1294 | 0.1136 | -1.347 | 1.6638 | -2.0014 | 9.8148 | 2.9459 | 0.605 | 0.6486 | 0.9593 | 0.7256 | -129.9388 | -2.8624 | 4.6517 | 1.036 | -4.3176 | -2.7879 | 3.6218 |  | 1.4301 | -0.7609 | 4.0124 | 3.3667 | 3.3508 | 1.0526 | 10.7845 | 14.2581 | 14.8444 | 11.0677 | -0.0007 | -0.0029 | 0.0007 | 0.0037 | 0.0008 | -0.0005 | 0.0082 | 0.0019 | -0.016 | -360.1404 | 17.4069 | -360.4727 | 17.6902 | -360.7927 | 18.144 | -360.8112 | 17.5013 | -352.6444 | 18.7374 | -352.6629 | 16.8361
12:15 | 3322 | 35.8604 | 200.0212 | 446.8071 | 450.6902 | -17.5856 | -43.6522 | 9.2687 | 6.1833 | 0.2152 | -1.2783 | 1.4868 | -2.0052 | 9.8503 | 3.0257 | 0.6053 | 0.6511 | 0.9569 | 0.7261 | -129.9528 | -2.8349 | 4.5486 | 1.0499 | -4.2962 | -2.7178 | 3.6497 |  | 1.5259 | -0.6505 | 4.0101 | 3.3654 | 3.3485 | 1.0524 | 10.759 | 14.2499 | 14.8243 | 11.054 | 0 | -0.003 | 0.0006 | 0.0036 | 0.0005 | -0.0001 | 0.0198 | -0.0025 | -0.0163 | -360.125 | 17.411 | -360.5004 | 17.7087 | -360.7958 | 18.1789 | -360.8758 | 17.5198 | -352.6444 | 18.7292 | -352.6875 | 16.8361
12:15 | 3323 | 35.8961 | 199.9251 | 446.7316 | 450.7562 | -17.628 | -43.6045 | 9.1524 | 6.189 | 0.2199 | -1.3665 | 1.4954 | -1.937 | 9.902 | 3.0507 | 0.6063 | 0.6464 | 0.9609 | 0.7276 | -129.9245 | -2.7954 | 4.6755 | 1.0057 | -4.2834 | -2.6822 | 3.7127 |  | 1.5344 | -0.7252 | 4.0105 | 3.3656 | 3.3488 | 1.0536 | 10.7314 | 14.2566 | 14.8062 | 11.0674 | 0 | -0.0032 | 0.0005 | 0.0036 | 0.0009 | -0.0006 | 0.0096 | -0.0077 | -0.014 | -360.2111 | 17.4069 | -360.4881 | 17.7169 | -360.8389 | 18.1953 | -360.882 | 17.5321 | -352.6967 | 18.7518 | -352.6906 | 16.8505
12:15 | 3324 | 35.9626 | 199.9881 | 446.8406 | 450.7853 | -17.6193 | -43.6231 | 9.245 | 6.1507 | 0.133 | -1.3535 | 1.5305 | -1.9264 | 9.9727 | 3.0106 | 0.6071 | 0.6481 | 0.9589 | 0.7274 | -129.9868 | -2.8253 | 4.6518 | 1.0181 | -4.3514 | -2.7843 | 3.6066 |  | 1.4512 | -0.7503 | 4.0111 | 3.366 | 3.3475 | 1.0529 | 10.729 | 14.2545 | 14.7998 | 11.0414 | 0 | -0.003 | 0.0011 | 0.004 | 0.0006 | -0.0003 | 0.0096 | -0.0103 | -0.0187 | -360.1588 | 17.4048 | -360.4573 | 17.6985 | -360.7743 | 18.1584 | -360.8789 | 17.5321 | -352.6875 | 18.7353 | -352.6721 | 16.832
12:15 | 3325 | 35.9579 | 199.9968 | 446.8579 | 450.8954 | -17.6872 | -43.6663 | 9.2543 | 6.1496 | 0.2026 | -1.3056 | 1.4931 | -1.9388 | 9.9063 | 2.9492 | 0.6057 | 0.6467 | 0.957 | 0.7272 | -129.9664 | -2.8012 | 4.7052 | 1.1031 | -4.377 | -2.7522 | 3.662 |  | 1.4757 | -0.7295 | 4.0111 | 3.3678 | 3.3475 | 1.0544 | 10.7279 | 14.2358 | 14.8089 | 11.0464 | -0.0005 | -0.0028 | 0.0008 | 0.0039 | 0.0008 | -0.0005 | 0.0008 | -0.0068 | -0.0073 | -360.1681 | 17.4048 | -360.4573 | 17.6944 | -360.7866 | 18.1563 | -360.8174 | 17.5137 | -352.6444 | 18.7292 | -352.6383 | 16.8176
12:15 | 3326 | 35.9334 | 199.9685 | 446.721 | 450.8178 | -17.6606 | -43.7087 | 9.1108 | 6.1497 | 0.1674 | -1.4172 | 1.5465 | -1.9016 | 9.9694 | 2.9566 | 0.6071 | 0.6474 | 0.9581 | 0.7269 | -129.9353 | -2.7728 | 4.6177 | 1.1037 | -4.347 | -2.787 | 3.5947 |  | 1.4917 | -0.8204 | 4.0109 | 3.3651 | 3.3452 | 1.0534 | 10.7452 | 14.2358 | 14.8031 | 11.0522 | 0 | -0.0031 | 0.001 | 0.004 | 0.001 | -0.0003 | 0.0007 | -0.0145 | -0.0307 | -360.1681 | 17.4131 | -360.4789 | 17.7252 | -360.8543 | 18.1769 | -360.8912 | 17.5239 | -352.6136 | 18.7456 | -352.6783 | 16.8258
12:15 | 3327 | 36.0517 | 200.0288 | 446.8985 | 450.8088 | -17.6485 | -43.7516 | 9.0995 | 6.1701 | 0.1277 | -1.3813 | 1.604 | -1.9065 | 9.9955 | 2.9708 | 0.607 | 0.6454 | 0.9581 | 0.728 | -129.9424 | -2.7188 | 4.6077 | 1.0879 | -4.4643 | -2.9134 | 3.5569 |  | 1.446 | -0.805 | 4.0092 | 3.3641 | 3.3444 | 1.0537 | 10.7301 | 14.221 | 14.8127 | 11.0482 | 0.0002 | -0.0032 | 0.0011 | 0.0047 | 0.0006 | 0.0002 | 0.0098 | -0.0124 | -0.0212 | -360.2296 | 17.4172 | -360.4819 | 17.7149 | -360.8327 | 18.1974 | -360.8943 | 17.5321 | -352.6783 | 18.7477 | -352.6783 | 16.832
12:15 | 3328 | 36.0191 | 199.9725 | 446.9056 | 450.7957 | -17.6174 | -43.6483 | 9.067 | 6.0283 | 0.0431 | -1.4679 | 1.5072 | -1.8975 | 9.9523 | 3.0341 | 0.6068 | 0.6476 | 0.9583 | 0.7269 | -129.9569 | -2.8579 | 4.7065 | 1.065 | -4.5013 | -2.9777 | 3.482 |  | 1.4526 | -0.7493 | 4.0099 | 3.3646 | 3.345 | 1.0542 | 10.7522 | 14.2833 | 14.8045 | 11.0822 | -0.0002 | -0.0032 | 0.0001 | 0.0037 | 0.0008 | -0.0009 | 0.0102 | -0.0055 | 0.0069 | -360.1896 | 17.3946 | -360.4419 | 17.6861 | -360.7835 | 18.1666 | -360.8697 | 17.5219 | -352.6444 | 18.7333 | -352.6567 | 16.8176
12:15 | 3329 | 36.0675 | 200.0576 | 446.8215 | 450.7882 | -17.6016 | -43.5105 | 9.048 | 6.0653 | 0.124 | -1.5732 | 1.5387 | -1.8469 | 9.9259 | 2.9325 | 0.6058 | 0.6481 | 0.9574 | 0.7283 | -129.9783 | -2.8117 | 4.702 | 0.9313 | -4.5251 | -2.9423 | 3.4978 |  | 1.5177 | -0.7963 | 4.0098 | 3.3671 | 3.3466 | 1.054 | 10.7821 | 14.2676 | 14.8438 | 11.0879 | -0.0003 | -0.0024 | 0.0008 | 0.0039 | 0.0004 | -0.0004 | 0.0116 | -0.0135 | -0.0197 | -360.1896 | 17.409 | -360.4512 | 17.6759 | -360.7773 | 18.1543 | -360.8327 | 17.5075 | -352.6321 | 18.7312 | -352.6598 | 16.8053
12:15 | 3330 | 36.0861 | 199.9587 | 446.9476 | 450.9047 | -17.5888 | -43.505 | 9.1585 | 6.1096 | 0.2394 | -1.4184 | 1.5397 | -1.7899 | 9.9389 | 2.9256 | 0.6069 | 0.649 | 0.954 | 0.7279 | -129.9733 | -2.8507 | 4.6999 | 0.622 | -4.5071 | -2.9209 | 3.4778 |  | 1.4663 | -0.839 | 4.0101 | 3.3625 | 3.3459 | 1.0545 | 10.7578 | 14.2547 | 14.8124 | 11.0352 | -0.0002 | -0.0025 | 0.0008 | 0.0036 | 0.001 | -0.0007 | -0.0025 | -0.0036 | -0.0308 | -360.2173 | 17.4151 | -360.4912 | 17.7046 | -360.8266 | 18.1728 | -360.8204 | 17.5219 | -352.6721 | 18.7415 | -352.6813 | 16.8217
12:15 | 3331 | 35.9902 | 200.0016 | 446.9471 | 450.8642 | -17.5846 | -43.6164 | 9.1536 | 6.0813 | 0.1613 | -1.3401 | 1.4871 | -1.8479 | 9.963 | 2.947 | 0.6064 | 0.6495 | 0.9537 | 0.7274 | -129.9082 | -2.7206 | 4.6853 | 1.0949 | -4.4912 | -2.9632 | 3.4554 |  | 1.5423 | -0.7855 | 4.012 | 3.3625 | 3.348 | 1.0537 | 10.7347 | 14.2547 | 14.795 | 11.0641 | 0 | -0.003 | 0.0005 | 0.0038 | 0.0006 | -0.0004 | 0.016 | -0.0114 | 0.0078 | -360.1804 | 17.4274 | -360.4881 | 17.7169 | -360.8358 | 18.2036 | -360.9066 | 17.528 | -352.6721 | 18.7579 | -352.7213 | 16.8299
12:15 | 3332 | 36.1071 | 200.0374 | 446.9158 | 450.8913 | -17.5532 | -43.5488 | 9.123 | 6.1026 | 0.2385 | -1.3452 | 1.5163 | -1.8399 | 9.9553 | 2.8877 | 0.6073 | 0.6481 | 0.9572 | 0.7274 | -129.9207 | -2.7259 | 4.7161 | 1.2302 | -4.454 | -2.8941 | 3.5371 |  | 1.4412 | -0.7197 | 4.0112 | 3.3653 | 3.3487 | 1.0547 | 10.729 | 14.2429 | 14.7708 | 11.024 | 0.0001 | -0.0029 | 0.0006 | 0.0038 | 0.0009 | -0.0005 | 0.0108 | -0.0009 | -0.0055 | -360.1988 | 17.4048 | -360.4296 | 17.7046 | -360.8297 | 18.1666 | -360.842 | 17.528 | -352.6567 | 18.7374 | -352.6998 | 16.8156
12:15 | 3333 | 36.1461 | 199.9224 | 447.0226 | 450.9374 | -17.5887 | -43.7242 | 9.2119 | 6.1564 | 0.2931 | -1.4089 | 1.5994 | -1.8363 | 9.9418 | 2.8824 | 0.6074 | 0.6459 | 0.9584 | 0.7274 | -129.8825 | -2.6374 | 4.6828 | 1.1252 | -4.4342 | -2.9335 | 3.4888 |  | 1.457 | -0.641 | 4.0107 | 3.3637 | 3.3453 | 1.0541 | 10.7533 | 14.2615 | 14.8011 | 11.0655 | -0.0004 | -0.0025 | 0.0008 | 0.004 | 0.0005 | -0.001 | 0.0082 | -0.0037 | -0.0051 | -360.1435 | 17.3987 | -360.4296 | 17.6861 | -360.7712 | 18.1584 | -360.8512 | 17.5137 | -352.6352 | 18.723 | -352.6721 | 16.8074
12:15 | 3334 | 36.1591 | 199.9257 | 447.0509 | 450.9485 | -17.5497 | -43.7472 | 9.2197 | 6.1788 | 0.2894 | -1.2464 | 1.5019 | -1.7739 | 9.9364 | 2.9348 | 0.6081 | 0.6467 | 0.9611 | 0.728 | -129.9615 | -2.7788 | 4.7987 | 1.1375 | -4.4662 | -2.8513 | 3.5125 |  | 1.4247 | -0.7991 | 4.0102 | 3.3639 | 3.3439 | 1.0539 | 10.7024 | 14.2392 | 14.7946 | 11.0501 | -0.0001 | -0.0027 | 0.0002 | 0.0039 | 0.0004 | -0.0007 | 0.0078 | -0.0203 | -0.0083 | -360.1465 | 17.4028 | -360.4542 | 17.6861 | -360.8266 | 18.1604 | -360.842 | 17.5178 | -352.6383 | 18.7271 | -352.6629 | 16.8115
12:15 | 3335 | 36.1217 | 200.0208 | 446.9696 | 450.9107 | -17.536 | -43.6846 | 9.1853 | 6.1097 | 0.2385 | -1.2915 | 1.4896 | -1.844 | 9.9433 | 3.0038 | 0.6066 | 0.6487 | 0.9593 | 0.7264 | -129.9524 | -2.7646 | 4.6865 | 1.0958 | -4.4048 | -2.8642 | 3.5724 |  | 1.4663 | -0.6869 | 4.0116 | 3.3648 | 3.3433 | 1.0538 | 10.7232 | 14.2429 | 14.7882 | 11.0471 | 0.0003 | -0.003 | 0.0005 | 0.0041 | 0.0009 | -0.0001 | 0.0106 | -0.0164 | -0.0361 | -360.1619 | 17.4274 | -360.4912 | 17.719 | -360.805 | 18.1851 | -360.885 | 17.5342 | -352.6475 | 18.7477 | -352.7152 | 16.8279
12:15 | 3336 | 36.1555 | 200.0495 | 446.9897 | 450.9031 | -17.4726 | -43.7484 | 9.2268 | 6.0918 | 0.135 | -1.1913 | 1.5077 | -1.8171 | 9.8735 | 3.0561 | 0.6074 | 0.648 | 0.9577 | 0.7245 | -129.8818 | -2.6717 | 4.7193 | 1.2278 | -4.3186 | -2.798 | 3.6243 |  | 1.5016 | -0.7761 | 4.0113 | 3.365 | 3.3477 | 1.0541 | 10.7337 | 14.2358 | 14.7626 | 11.0233 | 0.0002 | -0.0026 | 0.0001 | 0.0037 | 0.0004 | -0.0005 | 0.0045 | -0.005 | 0.0034 | -360.1773 | 17.4131 | -360.4819 | 17.7128 | -360.8235 | 18.181 | -360.9066 | 17.528 | -352.6752 | 18.7538 | -352.6937 | 16.8381
12:15 | 3337 | 36.1288 | 200.0631 | 446.9871 | 450.9618 | -17.5454 | -43.795 | 9.1253 | 6.0241 | 0.0614 | -1.2045 | 1.5373 | -1.8585 | 9.9556 | 2.9806 | 0.6075 | 0.6459 | 0.9593 | 0.7268 | -130.0137 | -2.716 | 4.6173 | 1.2104 | -4.33 | -2.8884 | 3.5531 |  | 1.546 | -0.6591 | 4.0099 | 3.3648 | 3.3473 | 1.0539 | 10.7475 | 14.2613 | 14.8001 | 11.0428 | -0.0003 | -0.0026 | 0.0007 | 0.004 | 0.0012 | -0.0002 | 0.0205 | -0.0067 | 0.0078 | -360.1281 | 17.3946 | -360.445 | 17.6964 | -360.7835 | 18.1461 | -360.8481 | 17.5137 | -352.6198 | 18.7353 | -352.6752 | 16.8258
12:15 | 3338 | 36.0346 | 200.034 | 446.8403 | 450.9884 | -17.4549 | -43.6721 | 9.2794 | 6.0568 | 0.0139 | -1.0991 | 1.6446 | -1.8824 | 9.8953 | 2.9301 | 0.6075 | 0.65 | 0.958 | 0.7278 | -130.0245 | -2.8365 | 4.5468 | 1.1959 | -4.2997 | -2.9596 | 3.545 |  | 1.4745 | -0.6951 | 4.0116 | 3.366 | 3.3457 | 1.0553 | 10.729 | 14.2429 | 14.794 | 11.0818 | -0.0002 | -0.0024 | 0.001 | 0.0042 | 0.0008 | -0.0003 | 0.0137 | -0.0108 | -0.0143 | -360.1558 | 17.4028 | -360.4296 | 17.682 | -360.7989 | 18.1625 | -360.8266 | 17.4993 | -352.6167 | 18.7353 | -352.669 | 16.8094
12:15 | 3339 | 36.0081 | 200.0155 | 446.9386 | 450.9617 | -17.5016 | -43.7727 | 9.2041 | 5.9903 | 0.0149 | -1.235 | 1.5977 | -1.9416 | 9.8345 | 2.8982 | 0.6077 | 0.6492 | 0.9556 | 0.7281 | -129.984 | -2.8525 | 4.5967 | 1.1854 | -4.2878 | -2.8133 | 3.5446 |  | 1.4754 | -0.7048 | 4.0091 | 3.3642 | 3.3462 | 1.0554 | 10.7465 | 14.2367 | 14.7966 | 11.054 | 0.0001 | -0.003 | 0.0008 | 0.0036 | 0.0012 | -0.0007 | 0.0021 | -0.023 | -0.0322 | -360.1835 | 17.4028 | -360.4666 | 17.7108 | -360.8297 | 18.181 | -360.8974 | 17.5383 | -352.6629 | 18.7374 | -352.6783 | 16.8238
12:15 | 3340 | 35.9676 | 199.9419 | 446.8374 | 450.9097 | -17.497 | -43.726 | 9.1257 | 5.9965 | -0.016 | -1.1638 | 1.6033 | -1.9342 | 9.9535 | 2.9271 | 0.6071 | 0.6517 | 0.954 | 0.7272 | -129.9859 | -2.795 | 4.5605 | 1.0893 | -4.2405 | -2.861 | 3.5207 |  | 1.6166 | -0.6118 | 4.0101 | 3.3632 | 3.3432 | 1.0542 | 10.7418 | 14.238 | 14.8106 | 11.0663 | 0 | -0.0035 | 0.0009 | 0.004 | 0.0004 | -0.0006 | 0.0007 | 0.0002 | -0.0311 | -360.2512 | 17.4315 | -360.485 | 17.6985 | -360.8235 | 18.1912 | -360.9066 | 17.5363 | -352.6967 | 18.7682 | -352.6998 | 16.8197
12:15 | 3341 | 36.1038 | 200.0194 | 446.9709 | 450.9727 | -17.5343 | -43.7846 | 9.2283 | 5.9938 | 0.0579 | -1.253 | 1.6415 | -1.9449 | 9.9722 | 2.9019 | 0.6074 | 0.6516 | 0.9566 | 0.7297 | -129.9912 | -2.8594 | 4.5719 | 1.0433 | -4.2382 | -2.9086 | 3.498 |  | 1.5896 | -0.692 | 4.0097 | 3.3656 | 3.3451 | 1.054 | 10.7267 | 14.2406 | 14.8028 | 11.0623 | -0.0002 | -0.0028 | 0.001 | 0.004 | 0.0009 | -0.001 | 0.0019 | -0.0206 | -0.0062 | -360.1958 | 17.409 | -360.485 | 17.6861 | -360.8174 | 18.1481 | -360.8697 | 17.5342 | -352.7029 | 18.7456 | -352.6813 | 16.8197
12:15 | 3342 | 36.085 | 200.041 | 446.9922 | 450.9948 | -17.4705 | -43.7365 | 9.2519 | 5.9482 | 0.1689 | -1.2383 | 1.7594 | -1.9416 | 9.9493 | 2.9629 | 0.6072 | 0.6487 | 0.9596 | 0.7288 | -129.8906 | -2.8113 | 4.5812 | 1.0369 | -4.2907 | -2.8758 | 3.5725 |  | 1.5746 | -0.6965 | 4.0093 | 3.3642 | 3.3477 | 1.0559 | 10.7094 | 14.2346 | 14.7844 | 11.0627 | -0.0005 | -0.0015 | 0.0004 | 0.004 | 0.0004 | -0.0003 | 0.0071 | -0.0008 | -0.0026 | -360.1188 | 17.4007 | -360.4542 | 17.682 | -360.7897 | 18.144 | -360.8543 | 17.5096 | -352.6198 | 18.7292 | -352.6752 | 16.8156
12:15 | 3343 | 36.0312 | 199.9533 | 446.8947 | 450.9637 | -17.4702 | -43.7688 | 9.1612 | 5.9734 | 0.1207 | -1.2343 | 1.6695 | -1.9629 | 9.9981 | 2.9535 | 0.608 | 0.6497 | 0.9603 | 0.7288 | -129.929 | -2.7594 | 4.6356 | 1.0881 | -4.3053 | -2.8096 | 3.5509 |  | 1.6262 | -0.6721 | 4.0116 | 3.3619 | 3.3442 | 1.0541 | 10.767 | 14.2352 | 14.8002 | 11.0901 | 0.0003 | -0.0028 | 0.0008 | 0.0039 | 0.0008 | -0.0007 | 0.0076 | 0.0082 | -0.0162 | -360.1588 | 17.3987 | -360.4789 | 17.7067 | -360.8081 | 18.1625 | -360.8543 | 17.5096 | -352.6444 | 18.7353 | -352.666 | 16.8197
12:15 | 3344 | 36.0934 | 200.0036 | 446.8798 | 450.945 | -17.4676 | -43.6452 | 9.1949 | 5.9082 | 0.1328 | -1.166 | 1.5187 | -1.883 | 10.03 | 2.9638 | 0.6073 | 0.6522 | 0.958 | 0.7292 | -129.9624 | -2.7422 | 4.6431 | 1.1407 | -4.2945 | -2.8314 | 3.5558 |  | 1.6183 | -0.5446 | 4.0099 | 3.3663 | 3.3477 | 1.0553 | 10.7452 | 14.23 | 14.8089 | 11.0638 | 0.0004 | -0.003 | 0.0006 | 0.0034 | 0.0004 | -0.0008 | 0.0033 | -0.0128 | -0.0131 | -360.1742 | 17.4151 | -360.4696 | 17.7087 | -360.8758 | 18.1994 | -360.9035 | 17.5404 | -352.6721 | 18.7333 | -352.6629 | 16.8217
12:15 | 3345 | 36.1296 | 200.0736 | 446.995 | 451.0188 | -17.5378 | -43.6324 | 9.1914 | 5.8982 | 0.1229 | -1.3179 | 1.582 | -1.9472 | 10.0075 | 2.9766 | 0.6076 | 0.6553 | 0.9589 | 0.7284 | -129.9599 | -2.6743 | 4.6584 | 1.1796 | -4.2493 | -2.7705 | 3.5559 |  | 1.6987 | -0.6402 | 4.0111 | 3.3667 | 3.3443 | 1.0534 | 10.76 | 14.2631 | 14.8578 | 11.1175 | -0.0003 | -0.0032 | 0.0007 | 0.0038 | 0.0008 | -0.0003 | 0.0183 | -0.0146 | 0.0006 | -360.205 | 17.4048 | -360.4512 | 17.68 | -360.7681 | 18.1707 | -360.9035 | 17.5445 | -352.6906 | 18.7333 | -352.669 | 16.8074
12:15 | 3346 | 36.1029 | 200.0498 | 446.8638 | 451.0035 | -17.5647 | -43.5898 | 9.2764 | 5.9344 | 0.1192 | -1.2625 | 1.6225 | -1.8854 | 10.0478 | 2.9723 | 0.6064 | 0.6514 | 0.9578 | 0.7275 | -129.9588 | -2.5511 | 4.7199 | 1.1934 | -4.248 | -2.8594 | 3.5576 |  | 1.6704 | -0.6403 | 4.0104 | 3.3649 | 3.3474 | 1.0553 | 10.7648 | 14.2732 | 14.808 | 11.0594 | -0.0003 | -0.0025 | 0.0006 | 0.0039 | 0.0005 | -0.0006 | 0.0077 | -0.0173 | 0.0001 | -360.1927 | 17.4131 | -360.4389 | 17.682 | -360.7773 | 18.1379 | -360.8204 | 17.5034 | -352.6475 | 18.7333 | -352.6721 | 16.8094
12:15 | 3347 | 36.2299 | 200.1476 | 447.0055 | 451.0569 | -17.5464 | -43.5993 | 9.3219 | 5.9137 | 0.0364 | -1.2154 | 1.6038 | -1.9133 | 9.9323 | 2.9611 | 0.6074 | 0.6501 | 0.9564 | 0.7283 | -129.956 | -2.5086 | 4.7908 | 1.1592 | -4.2375 | -2.9235 | 3.4825 |  | 1.7242 | -0.5571 | 4.0094 | 3.3621 | 3.3451 | 1.0539 | 10.7557 | 14.2231 | 14.796 | 11.0627 | -0.0005 | -0.0032 | 0.0007 | 0.0034 | 0.0005 | -0.0002 | 0.0211 | -0.0086 | -0.0251 | -360.1281 | 17.3966 | -360.4789 | 17.7169 | -360.8481 | 18.1769 | -360.8481 | 17.4952 | -352.6075 | 18.7292 | -352.6506 | 16.832
12:16 | 3348 | 36.2212 | 200.198 | 447.0401 | 451.07 | -17.5163 | -43.5148 | 9.26 | 5.9609 | 0.0565 | -1.3629 | 1.5727 | -1.8209 | 9.9664 | 2.8462 | 0.6074 | 0.6517 | 0.956 | 0.7274 | -129.9048 | -2.5003 | 4.7637 | 1.0602 | -4.2983 | -2.9333 | 3.4517 |  | 1.6271 | -0.6501 | 4.0105 | 3.3625 | 3.3465 | 1.0543 | 10.7093 | 14.2232 | 14.7797 | 11.045 | 0.0003 | -0.0031 | 0.001 | 0.0046 | 0.0014 | -0.0005 | 0.0055 | -0.0119 | -0.0063 | -360.1804 | 17.4007 | -360.4604 | 17.7046 | -360.8481 | 18.1974 | -360.9435 | 17.5424 | -352.6598 | 18.7312 | -352.6721 | 16.8197
12:16 | 3349 | 36.2697 | 200.2204 | 447.0533 | 451.1846 | -17.5423 | -43.6213 | 9.2314 | 5.9771 | 0.0923 | -1.4136 | 1.5128 | -1.8652 | 10.007 | 2.9371 | 0.6076 | 0.6512 | 0.9557 | 0.7289 | -129.9572 | -2.5145 | 4.7376 | 1.1351 | -4.3088 | -2.9079 | 3.5067 |  | 1.7104 | -0.4971 | 4.01 | 3.3687 | 3.3493 | 1.0546 | 10.7244 | 14.2266 | 14.8117 | 11.0544 | -0.0003 | -0.0033 | 0.0006 | 0.0038 | 0.0008 | 0 | 0.0047 | -0.0221 | -0.0067 | -360.205 | 17.4172 | -360.485 | 17.6882 | -360.7866 | 18.1625 | -360.9158 | 17.5424 | -352.7429 | 18.7497 | -352.6967 | 16.8238
12:16 | 3350 | 36.3239 | 200.1988 | 447.027 | 451.0751 | -17.6386 | -43.5829 | 9.1064 | 6.0402 | 0.1424 | -1.51 | 1.6218 | -1.8844 | 10.0738 | 2.9949 | 0.6056 | 0.6486 | 0.9571 | 0.7276 | -129.8747 | -2.4742 | 4.8493 | 1.2245 | -4.3744 | -2.881 | 3.5442 |  | 1.663 | -0.5583 | 4.0107 | 3.3658 | 3.348 | 1.0535 | 10.7163 | 14.23 | 14.7742 | 11.0349 | -0.0006 | -0.0028 | 0.0006 | 0.0039 | 0.0014 | -0.0004 | 0.0104 | -0.0158 | -0.0036 | -360.1404 | 17.4172 | -360.485 | 17.6902 | -360.7897 | 18.1379 | -360.7897 | 17.4993 | -352.6352 | 18.7415 | -352.6967 | 16.832
12:16 | 3351 | 36.2396 | 200.1846 | 446.976 | 451.0793 | -17.5739 | -43.6072 | 9.0784 | 5.9386 | 0.1327 | -1.5013 | 1.5621 | -1.8522 | 10.088 | 3.0207 | 0.6058 | 0.6479 | 0.9583 | 0.7292 | -129.9289 | -2.5496 | 4.8317 | 1.1706 | -4.4023 | -2.8844 | 3.5755 |  | 1.7042 | -0.5775 | 4.0109 | 3.3656 | 3.3481 | 1.0541 | 10.6886 | 14.202 | 14.785 | 11.0309 | 0.0001 | -0.0028 | 0.0004 | 0.0038 | 0.0004 | -0.0002 | 0.0152 | -0.0141 | -0.0033 | -360.1096 | 17.3843 | -360.4481 | 17.7108 | -360.8635 | 18.1666 | -360.8543 | 17.4931 | -352.6044 | 18.7169 | -352.666 | 16.832
12:16 | 3352 | 36.2465 | 200.2952 | 446.9459 | 451.0894 | -17.6185 | -43.7197 | 9.0503 | 5.9349 | 0.178 | -1.4749 | 1.5563 | -1.8772 | 10.0221 | 2.9645 | 0.6061 | 0.6487 | 0.9568 | 0.7269 | -129.9032 | -2.5098 | 4.7809 | 1.2051 | -4.3496 | -2.8334 | 3.5967 |  | 1.6418 | -0.5443 | 4.0115 | 3.3662 | 3.3488 | 1.0544 | 10.7521 | 14.2603 | 14.794 | 11.0645 | 0.0001 | -0.0031 | 0.001 | 0.0041 | 0.0008 | -0.0005 | 0.0113 | -0.0107 | 0.0077 | -360.1773 | 17.409 | -360.4604 | 17.7128 | -360.8512 | 18.1953 | -360.922 | 17.5445 | -352.6906 | 18.7333 | -352.669 | 16.8238
12:16 | 3353 | 36.2505 | 200.2331 | 446.9924 | 451.134 | -17.6001 | -43.6773 | 9.0785 | 5.9698 | 0.2067 | -1.3963 | 1.6085 | -1.9841 | 9.9391 | 2.8935 | 0.6051 | 0.649 | 0.9567 | 0.7298 | -129.8655 | -2.5299 | 4.8641 | 1.2621 | -4.2708 | -2.839 | 3.6331 |  | 1.6373 | -0.5819 | 4.0119 | 3.3659 | 3.345 | 1.0538 | 10.7693 | 14.2492 | 14.8493 | 11.0922 | 0.0004 | -0.0028 | 0.0012 | 0.0041 | 0.0007 | -0.0003 | 0.0186 | -0.0117 | 0.0037 | -360.2142 | 17.4254 | -360.5004 | 17.7046 | -360.7897 | 18.1645 | -360.9066 | 17.5424 | -352.7244 | 18.762 | -352.709 | 16.8176
12:16 | 3354 | 36.3051 | 200.157 | 446.9416 | 451.1194 | -17.5413 | -43.768 | 9.1012 | 5.9669 | 0.1855 | -1.4576 | 1.6556 | -2.0378 | 10.0492 | 2.9608 | 0.6057 | 0.6544 | 0.9545 | 0.7295 | -129.8665 | -2.5309 | 4.8056 | 1.2986 | -4.2416 | -2.8224 | 3.7166 |  | 1.6555 | -0.5386 | 4.011 | 3.3641 | 3.3479 | 1.0542 | 10.7394 | 14.2591 | 14.8042 | 11.0692 | -0.0003 | -0.0025 | 0.0011 | 0.0042 | 0.0009 | -0.0009 | 0.0033 | -0.0095 | 0.0013 | -360.1619 | 17.4131 | -360.4789 | 17.719 | -360.8266 | 18.1399 | -360.802 | 17.4952 | -352.6229 | 18.7518 | -352.6875 | 16.8279
12:16 | 3355 | 36.2963 | 200.1653 | 447.0156 | 451.1834 | -17.6553 | -43.7769 | 9.0835 | 6.0318 | 0.2703 | -1.4615 | 1.6563 | -1.8974 | 10.0493 | 2.9991 | 0.6056 | 0.647 | 0.9574 | 0.7293 | -129.9248 | -2.4437 | 4.7251 | 1.2292 | -4.2901 | -2.9367 | 3.6342 |  | 1.7601 | -0.5389 | 4.0118 | 3.3679 | 3.35 | 1.0544 | 10.7578 | 14.2547 | 14.8182 | 11.0641 | -0.0003 | -0.0026 | 0.0009 | 0.0037 | 0.001 | -0.0003 | 0.0228 | -0.0089 | -0.0026 | -360.125 | 17.3946 | -360.4696 | 17.7272 | -360.8327 | 18.1666 | -360.8174 | 17.4972 | -352.6167 | 18.7251 | -352.666 | 16.8279
12:16 | 3356 | 36.3023 | 200.095 | 446.8878 | 451.0765 | -17.5769 | -43.8007 | 9.1642 | 6.0238 | 0.186 | -1.446 | 1.6137 | -1.7573 | 10.1418 | 3.1341 | 0.6058 | 0.6496 | 0.9602 | 0.7283 | -129.8427 | -2.5024 | 4.708 | 1.3082 | -4.2045 | -2.849 | 3.6384 |  | 1.7086 | -0.5819 | 4.0107 | 3.3641 | 3.3466 | 1.0539 | 10.7556 | 14.2695 | 14.8318 | 11.0681 | 0.0001 | -0.0032 | 0.0005 | 0.0036 | 0.0004 | -0.0008 | 0.0007 | -0.014 | -0.0295 | -360.1681 | 17.409 | -360.4542 | 17.7149 | -360.8266 | 18.1974 | -360.9251 | 17.5445 | -352.6752 | 18.7292 | -352.669 | 16.8217
12:16 | 3357 | 36.351 | 200.1455 | 446.9861 | 451.1046 | -17.5365 | -43.7462 | 9.238 | 5.9774 | 0.2473 | -1.2559 | 1.6387 | -1.8908 | 10.0327 | 2.9746 | 0.6063 | 0.6503 | 0.9564 | 0.7277 | -129.8358 | -2.4479 | 4.7104 | 1.255 | -4.186 | -2.8199 | 3.646 |  | 1.6914 | -0.5639 | 4.0115 | 3.3641 | 3.3478 | 1.0555 | 10.7476 | 14.209 | 14.8269 | 11.0494 | 0.0002 | -0.003 | 0.0007 | 0.0041 | 0.0008 | -0.0007 | -0.0008 | -0.002 | -0.0091 | -360.2358 | 17.4356 | -360.5004 | 17.7149 | -360.7835 | 18.1604 | -360.8697 | 17.5506 | -352.7337 | 18.7703 | -352.7152 | 16.8217
12:16 | 3358 | 36.3447 | 200.1538 | 447.1037 | 451.1659 | -17.6059 | -43.6167 | 9.2002 | 6.0097 | 0.1501 | -1.4856 | 1.6327 | -1.7884 | 10.0546 | 3.069 | 0.6064 | 0.6486 | 0.9537 | 0.7278 | -129.8148 | -2.4385 | 4.7653 | 1.36 | -4.1798 | -2.7474 | 3.699 |  | 1.7237 | -0.6145 | 4.0113 | 3.3642 | 3.3479 | 1.0552 | 10.7279 | 14.23 | 14.7916 | 11.0349 | 0 | -0.0025 | 0.0002 | 0.0036 | 0.0005 | -0.0005 | 0.0022 | -0.0179 | 0.0005 | -360.2111 | 17.4131 | -360.4789 | 17.7128 | -360.7866 | 18.1317 | -360.802 | 17.4952 | -352.6506 | 18.7559 | -352.709 | 16.8299
12:16 | 3359 | 36.3301 | 200.0992 | 447.0231 | 451.0971 | -17.5682 | -43.6776 | 9.0745 | 6.0287 | 0.1691 | -1.5322 | 1.6362 | -1.7611 | 10.0485 | 3.0789 | 0.6067 | 0.6492 | 0.9572 | 0.7289 | -129.8854 | -2.4801 | 4.8756 | 1.4155 | -4.2098 | -2.7991 | 3.6591 |  | 1.7158 | -0.4855 | 4.0103 | 3.365 | 3.3438 | 1.0537 | 10.7059 | 14.2426 | 14.8034 | 11.071 | -0.0005 | -0.0028 | 0.0004 | 0.0041 | 0.0008 | -0.0009 | 0.0298 | -0.007 | -0.0176 | -360.1158 | 17.3802 | -360.4604 | 17.7231 | -360.7927 | 18.1461 | -360.8327 | 17.4952 | -352.5767 | 18.7169 | -352.6721 | 16.8238
12:16 | 3360 | 36.3451 | 200.1002 | 446.9506 | 451.1092 | -17.5849 | -43.6719 | 9.1568 | 6.0082 | 0.1583 | -1.565 | 1.6205 | -1.7695 | 10.1427 | 3.1732 | 0.6064 | 0.6471 | 0.9572 | 0.7276 | -129.7987 | -2.2921 | 4.9334 | 1.3562 | -4.263 | -2.777 | 3.6279 |  | 1.7126 | -0.5992 | 4.0109 | 3.363 | 3.3445 | 1.0541 | 10.7232 | 14.2256 | 14.7882 | 11.024 | 0.0002 | -0.0025 | 0.0012 | 0.0044 | 0.0005 | 0 | 0.0173 | 0.0062 | -0.025 | -360.2019 | 17.3946 | -360.4327 | 17.7026 | -360.805 | 18.1666 | -360.9066 | 17.5301 | -352.666 | 18.7169 | -352.626 | 16.8012
12:16 | 3361 | 36.4402 | 200.1645 | 446.9959 | 451.1209 | -17.5669 | -43.6739 | 9.1846 | 6.0696 | 0.2364 | -1.5276 | 1.7019 | -1.8017 | 10.0792 | 3.131 | 0.6063 | 0.6531 | 0.9584 | 0.7288 | -129.8553 | -2.3608 | 4.8389 | 1.3283 | -4.3305 | -2.7363 | 3.612 |  | 1.7085 | -0.5754 | 4.0109 | 3.3641 | 3.3467 | 1.0542 | 10.7209 | 14.2404 | 14.8133 | 11.0627 | 0 | -0.0032 | 0.0007 | 0.0037 | 0.0012 | -0.0006 | 0.0145 | -0.0172 | -0.0024 | -360.2265 | 17.4315 | -360.5004 | 17.7128 | -360.8204 | 18.142 | -360.882 | 17.5568 | -352.7121 | 18.762 | -352.709 | 16.8176
12:16 | 3362 | 36.4045 | 200.2282 | 447.1643 | 451.1323 | -17.6244 | -43.8113 | 9.1469 | 6.0293 | 0.2243 | -1.6438 | 1.6017 | -1.8695 | 10.1403 | 3.1403 | 0.6074 | 0.6508 | 0.9596 | 0.7297 | -129.8346 | -2.3437 | 4.832 | 1.4527 | -4.2626 | -2.642 | 3.6863 |  | 1.6846 | -0.5961 | 4.011 | 3.3635 | 3.3461 | 1.0549 | 10.7568 | 14.2649 | 14.8447 | 11.0461 | -0.0004 | -0.0028 | 0.0009 | 0.0043 | 0.0005 | 0.0001 | 0.0128 | -0.0053 | -0.0202 | -360.1619 | 17.4315 | -360.5066 | 17.719 | -360.8327 | 18.1337 | -360.8481 | 17.5157 | -352.6906 | 18.7518 | -352.7213 | 16.8361
12:16 | 3363 | 36.428 | 200.2172 | 447.0973 | 451.1569 | -17.5411 | -43.8044 | 9.1231 | 6.1457 | 0.328 | -1.5983 | 1.6321 | -1.8979 | 10.1165 | 3.0769 | 0.6069 | 0.649 | 0.9569 | 0.7295 | -129.8138 | -2.3573 | 4.9271 | 1.4795 | -4.2037 | -2.6844 | 3.7569 |  | 1.7225 | -0.5718 | 4.0105 | 3.3629 | 3.3469 | 1.0552 | 10.7266 | 14.2696 | 14.8212 | 11.085 | -0.0004 | -0.0026 | 0.0007 | 0.0037 | 0.001 | -0.0005 | 0.0029 | 0.0024 | 0.0059 | -360.0911 | 17.3761 | -360.4235 | 17.7108 | -360.8266 | 18.144 | -360.8666 | 17.5013 | -352.629 | 18.7107 | -352.6752 | 16.832
12:16 | 3364 | 36.4242 | 200.1461 | 447.1072 | 451.0877 | -17.5358 | -43.5489 | 9.1664 | 6.1478 | 0.3869 | -1.5475 | 1.6525 | -1.8193 | 10.1445 | 3.1432 | 0.6074 | 0.6534 | 0.9558 | 0.7299 | -129.6879 | -2.2387 | 4.9502 | 1.412 | -4.2117 | -2.6479 | 3.7552 |  | 1.7572 | -0.5281 | 4.0092 | 3.3639 | 3.3461 | 1.0556 | 10.7696 | 14.2426 | 14.8266 | 11.0768 | -0.0004 | -0.0031 | 0.0004 | 0.0034 | 0.0005 | -0.0008 | 0.005 | -0.0057 | -0.0166 | -360.1804 | 17.3843 | -360.3835 | 17.68 | -360.7773 | 18.1481 | -360.9004 | 17.5383 | -352.6629 | 18.7128 | -352.6075 | 16.7827
12:16 | 3365 | 36.4833 | 200.1763 | 447.0477 | 451.0689 | -17.5615 | -43.5527 | 9.1191 | 6.0596 | 0.3993 | -1.6026 | 1.6561 | -1.8198 | 10.1641 | 3.0586 | 0.6073 | 0.653 | 0.9529 | 0.7288 | -129.8583 | -2.3509 | 4.8922 | 1.414 | -4.1716 | -2.7177 | 3.6894 |  | 1.7785 | -0.5377 | 4.0104 | 3.3671 | 3.3473 | 1.0545 | 10.7315 | 14.2389 | 14.7809 | 11.0335 | 0 | -0.0032 | 0.0009 | 0.0042 | 0.0006 | -0.0009 | 0.004 | -0.0141 | 0.0101 | -360.2142 | 17.4233 | -360.4604 | 17.7005 | -360.7773 | 18.144 | -360.8912 | 17.5486 | -352.6844 | 18.7559 | -352.669 | 16.8032
12:16 | 3366 | 36.4871 | 200.0894 | 447.0563 | 451.0615 | -17.6474 | -43.6468 | 9.0349 | 6.1067 | 0.5361 | -1.3512 | 1.6622 | -1.7963 | 10.1511 | 2.9982 | 0.6081 | 0.6488 | 0.9555 | 0.7275 | -129.8936 | -2.3337 | 4.8488 | 1.459 | -4.1968 | -2.7066 | 3.6283 |  | 1.7391 | -0.5034 | 4.0103 | 3.3675 | 3.3485 | 1.0552 | 10.7533 | 14.2673 | 14.7838 | 11.0655 | -0.0001 | -0.003 | 0.0006 | 0.0038 | 0.0004 | -0.0007 | 0.0093 | 0.0016 | 0.0002 | -360.1804 | 17.4377 | -360.5158 | 17.7559 | -360.8758 | 18.1461 | -360.8666 | 17.5383 | -352.6844 | 18.7723 | -352.7337 | 16.8484
12:16 | 3367 | 36.5162 | 200.085 | 446.9895 | 451.061 | -17.5983 | -43.5325 | 9.0538 | 6.1179 | 0.4429 | -1.6038 | 1.6055 | -1.8069 | 10.1561 | 3.0332 | 0.6084 | 0.6506 | 0.9547 | 0.7276 | -129.7847 | -2.2669 | 4.9247 | 1.4083 | -4.1348 | -2.6749 | 3.6645 |  | 1.7734 | -0.5453 | 4.0097 | 3.3661 | 3.3479 | 1.0551 | 10.736 | 14.2324 | 14.7653 | 11.0601 | -0.0002 | -0.0025 | 0.0005 | 0.0037 | 0.0006 | -0.0004 | 0.005 | -0.0075 | -0.0303 | -360.1219 | 17.3843 | -360.4635 | 17.7252 | -360.8574 | 18.1687 | -360.9097 | 17.526 | -352.6352 | 18.7271 | -352.6783 | 16.832
12:16 | 3368 | 36.4261 | 200.0747 | 447.1099 | 451.1966 | -17.494 | -43.5461 | 9.0756 | 6.0994 | 0.4678 | -1.491 | 1.5753 | -1.8015 | 10.2521 | 3.1298 | 0.6087 | 0.6524 | 0.9577 | 0.7281 | -129.7102 | -2.2064 | 5.0322 | 1.3843 | -4.0355 | -2.6612 | 3.7574 |  | 1.7215 | -0.609 | 4.0102 | 3.3665 | 3.3492 | 1.0554 | 10.7497 | 14.2524 | 14.8397 | 11.0616 | 0 | -0.0029 | 0.0014 | 0.0044 | 0.0013 | -0.0002 | 0.0094 | -0.019 | -0.0214 | -360.1773 | 17.3782 | -360.4019 | 17.6882 | -360.7743 | 18.1481 | -360.8912 | 17.5321 | -352.6783 | 18.7045 | -352.6136 | 16.8032
12:16 | 3369 | 36.4122 | 200.081 | 447.0586 | 451.1416 | -17.5834 | -43.5434 | 9.1886 | 6.1577 | 0.403 | -1.3609 | 1.5979 | -1.8118 | 10.1961 | 3.0547 | 0.6092 | 0.6497 | 0.9594 | 0.7263 | -129.7115 | -2.298 | 4.9845 | 1.4115 | -4.0956 | -2.6385 | 3.7456 |  | 1.7257 | -0.6337 | 4.0107 | 3.3658 | 3.3503 | 1.0562 | 10.7475 | 14.2383 | 14.8301 | 11.0713 | 0.0004 | -0.003 | 0.001 | 0.0037 | 0.0004 | -0.0006 | 0.0033 | -0.013 | 0.0128 | -360.1681 | 17.4172 | -360.4635 | 17.6902 | -360.7743 | 18.1153 | -360.8143 | 17.5321 | -352.666 | 18.7415 | -352.6567 | 16.795
12:16 | 3370 | 36.3362 | 200.0233 | 447.0894 | 451.0523 | -17.5045 | -43.4631 | 9.1757 | 6.1765 | 0.4575 | -1.5042 | 1.5403 | -1.8576 | 10.1724 | 3.0742 | 0.6076 | 0.6463 | 0.9543 | 0.7279 | -129.7804 | -2.2136 | 5.0288 | 1.3457 | -4.1474 | -2.7372 | 3.6314 |  | 1.7842 | -0.5114 | 4.0093 | 3.3644 | 3.3493 | 1.0562 | 10.7533 | 14.2788 | 14.8301 | 11.0887 | -0.0001 | -0.0029 | 0.0003 | 0.0036 | 0.0011 | -0.0003 | 0.018 | -0.0113 | -0.0085 | -360.1558 | 17.4172 | -360.5096 | 17.7395 | -360.8758 | 18.1522 | -360.8389 | 17.5157 | -352.629 | 18.7271 | -352.709 | 16.8361
12:16 | 3371 | 36.3897 | 200.0828 | 447.0809 | 451.1322 | -17.5313 | -43.4813 | 9.1795 | 6.1836 | 0.4256 | -1.4914 | 1.5652 | -1.7488 | 10.2554 | 3.1704 | 0.6075 | 0.6538 | 0.9593 | 0.7278 | -129.866 | -2.2716 | 4.8993 | 1.4644 | -4.1215 | -2.5906 | 3.8294 |  | 1.7562 | -0.5384 | 4.0107 | 3.3671 | 3.3518 | 1.0543 | 10.7925 | 14.2664 | 14.8251 | 11.0868 | -0.0008 | -0.0029 | 0.0006 | 0.0038 | 0.0008 | -0.0002 | 0.0039 | 0.0067 | -0.0217 | -360.1527 | 17.4007 | -360.4727 | 17.7293 | -360.8727 | 18.183 | -360.9097 | 17.5383 | -352.6721 | 18.721 | -352.6906 | 16.832
12:16 | 3372 | 36.4404 | 200.0682 | 447.1482 | 451.2279 | -17.4884 | -43.425 | 9.2297 | 6.2081 | 0.5044 | -1.5333 | 1.5525 | -1.8241 | 10.1718 | 3.039 | 0.6075 | 0.6507 | 0.959 | 0.729 | -129.7766 | -2.4191 | 4.9278 | 1.4879 | -4.143 | -2.6073 | 3.7598 |  | 1.7453 | -0.6182 | 4.0105 | 3.3656 | 3.3498 | 1.0555 | 10.736 | 14.244 | 14.829 | 11.0428 | -0.0001 | -0.0028 | 0.0006 | 0.0037 | 0.0007 | -0.0008 | 0.0096 | 0.0003 | -0.0104 | -360.2296 | 17.4254 | -360.4512 | 17.7026 | -360.7989 | 18.1481 | -360.9097 | 17.565 | -352.7337 | 18.7456 | -352.6752 | 16.8094
12:16 | 3373 | 36.4322 | 200.109 | 447.1881 | 451.3061 | -17.51 | -43.4048 | 9.2568 | 6.1982 | 0.5182 | -1.4147 | 1.5454 | -1.7996 | 10.1509 | 3.0484 | 0.6081 | 0.6498 | 0.9589 | 0.7283 | -129.7309 | -2.296 | 4.99 | 1.4717 | -4.1578 | -2.6876 | 3.7156 |  | 1.7529 | -0.5492 | 4.0097 | 3.3628 | 3.3469 | 1.0544 | 10.7221 | 14.2358 | 14.7973 | 11.0695 | 0.0003 | -0.0032 | 0.0007 | 0.0043 | 0.0009 | 0.0002 | -0.0043 | -0.0071 | -0.005 | -360.1465 | 17.4151 | -360.5096 | 17.7169 | -360.8327 | 18.1214 | -360.7958 | 17.5055 | -352.6537 | 18.7436 | -352.6998 | 16.832
12:16 | 3374 | 36.4374 | 200.1049 | 447.1238 | 451.337 | -17.4644 | -43.4482 | 9.2527 | 6.2456 | 0.506 | -1.3211 | 1.5966 | -1.8138 | 10.0821 | 3.0556 | 0.6083 | 0.6506 | 0.9574 | 0.7302 | -129.7829 | -2.2189 | 4.9903 | 1.5153 | -4.1749 | -2.8031 | 3.7273 |  | 1.788 | -0.5739 | 4.0093 | 3.3654 | 3.3479 | 1.0566 | 10.736 | 14.2091 | 14.7759 | 11.0316 | -0.0002 | -0.0032 | 0.0008 | 0.0039 | 0.0006 | -0.0008 | 0.0166 | -0.0145 | -0.0062 | -360.0758 | 17.3843 | -360.4327 | 17.7169 | -360.8297 | 18.1337 | -360.802 | 17.5075 | -352.5921 | 18.7025 | -352.6537 | 16.8176
12:16 | 3375 | 36.4723 | 200.1204 | 447.191 | 451.332 | -17.3775 | -43.4641 | 9.4171 | 6.1674 | 0.4721 | -1.128 | 1.5597 | -1.8553 | 10.1575 | 3.0553 | 0.6089 | 0.6514 | 0.9575 | 0.7294 | -129.7538 | -2.2788 | 4.8504 | 1.3909 | -4.1912 | -2.7198 | 3.7354 |  | 1.7787 | -0.5768 | 4.0094 | 3.3667 | 3.3463 | 1.0542 | 10.7198 | 14.2277 | 14.783 | 11.0154 | -0.0003 | -0.0028 | 0.0003 | 0.0037 | 0.0005 | -0.0005 | 0.0039 | -0.0143 | -0.0011 | -360.1896 | 17.3905 | -360.4296 | 17.6882 | -360.805 | 18.1522 | -360.9127 | 17.5486 | -352.6813 | 18.7107 | -352.6321 | 16.7848
12:16 | 3376 | 36.4761 | 200.13 | 447.2307 | 451.3389 | -17.3322 | -43.4017 | 9.4822 | 6.2034 | 0.4772 | -1.024 | 1.6023 | -1.7692 | 10.1565 | 3.0843 | 0.607 | 0.6539 | 0.9598 | 0.7298 | -129.7845 | -2.3207 | 4.8677 | 1.3517 | -4.1896 | -2.7422 | 3.7146 |  | 1.8358 | -0.538 | 4.0099 | 3.3644 | 3.3521 | 1.0537 | 10.7451 | 14.2478 | 14.8353 | 11.0915 | -0.0001 | -0.0026 | 0.0015 | 0.0043 | 0.001 | -0.0005 | 0.0127 | -0.0103 | -0.0108 | -360.2327 | 17.4541 | -360.5343 | 17.7252 | -360.8266 | 18.1317 | -360.8635 | 17.5527 | -352.7152 | 18.7723 | -352.706 | 16.8258
12:16 | 3377 | 36.5176 | 200.1551 | 447.2833 | 451.3382 | -17.3289 | -43.2868 | 9.4879 | 6.3095 | 0.4764 | -1.0216 | 1.7211 | -1.7328 | 10.2162 | 3.2175 | 0.6073 | 0.6532 | 0.964 | 0.7316 | -129.708 | -2.3788 | 5.012 | 1.3151 | -4.1901 | -2.6915 | 3.7125 |  | 1.8442 | -0.5561 | 4.0099 | 3.362 | 3.3495 | 1.0551 | 10.7335 | 14.2422 | 14.8305 | 11.0969 | 0.0006 | -0.0027 | 0.0009 | 0.0036 | 0.0003 | -0.0008 | -0.0059 | 0.0022 | 0.0013 | -360.1558 | 17.4233 | -360.5158 | 17.7436 | -360.8727 | 18.1461 | -360.8635 | 17.5219 | -352.669 | 18.7456 | -352.7398 | 16.8484
12:16 | 3378 | 36.5098 | 200.1096 | 447.324 | 451.3128 | -17.3677 | -43.3037 | 9.4623 | 6.2448 | 0.5715 | -0.9992 | 1.6329 | -1.8066 | 10.1926 | 3.1323 | 0.6085 | 0.6493 | 0.9555 | 0.7291 | -129.6993 | -2.2995 | 4.9272 | 1.411 | -4.1572 | -2.6639 | 3.7521 |  | 1.8395 | -0.5425 | 4.0111 | 3.3629 | 3.3473 | 1.0557 | 10.7763 | 14.2733 | 14.8322 | 11.0995 | 0.0003 | -0.0031 | 0 | 0.0034 | 0.0009 | -0.0003 | -0.0074 | -0.0208 | -0.0178 | -360.1281 | 17.374 | -360.4235 | 17.7005 | -360.8143 | 18.1666 | -360.9189 | 17.5445 | -352.6537 | 18.7004 | -352.6598 | 16.8012
12:16 | 3379 | 36.4944 | 200.0784 | 447.2171 | 451.3162 | -17.4073 | -43.3263 | 9.5728 | 6.1637 | 0.6077 | -1.0453 | 1.5524 | -1.8063 | 10.1812 | 3.2199 | 0.6076 | 0.6499 | 0.954 | 0.7294 | -129.7244 | -2.2073 | 5.0465 | 1.3915 | -4.2014 | -2.6546 | 3.729 |  | 1.8535 | -0.4526 | 4.0108 | 3.3659 | 3.349 | 1.0556 | 10.7637 | 14.2429 | 14.7998 | 11.0702 | -0.0004 | -0.0026 | 0.0008 | 0.0037 | 0.0007 | -0.0007 | 0.0042 | -0.0164 | -0.0101 | -360.1804 | 17.411 | -360.4296 | 17.6738 | -360.7435 | 18.1235 | -360.8666 | 17.5465 | -352.6537 | 18.723 | -352.629 | 16.7745
12:16 | 3380 | 36.3961 | 200.042 | 447.1661 | 451.2963 | -17.4633 | -43.326 | 9.5003 | 6.0912 | 0.5679 | -1.0786 | 1.5631 | -1.7899 | 10.1592 | 3.2469 | 0.6058 | 0.6505 | 0.9541 | 0.7282 | -129.6183 | -2.1289 | 5.0835 | 1.3935 | -4.1806 | -2.672 | 3.7253 |  | 1.856 | -0.534 | 4.0111 | 3.363 | 3.3461 | 1.0545 | 10.7602 | 14.2452 | 14.842 | 11.0555 | -0.0004 | -0.0028 | 0.0002 | 0.0037 | 0.0008 | 0 | -0.0088 | -0.0054 | -0.0165 | -360.1896 | 17.4274 | -360.4881 | 17.7128 | -360.8112 | 18.1214 | -360.8297 | 17.528 | -352.6537 | 18.7436 | -352.7121 | 16.7971
12:16 | 3381 | 36.3642 | 200.2024 | 447.1427 | 451.2872 | -17.4975 | -43.3726 | 9.4554 | 6.2168 | 0.6506 | -0.9721 | 1.6006 | -1.8777 | 10.1368 | 3.171 | 0.6084 | 0.6505 | 0.9595 | 0.73 | -129.5945 | -2.1824 | 5.0578 | 1.3122 | -4.1724 | -2.682 | 3.7377 |  | 1.8688 | -0.5927 | 4.0109 | 3.3624 | 3.3521 | 1.0561 | 10.7175 | 14.2253 | 14.7977 | 11.0652 | 0.0001 | -0.0028 | 0.0003 | 0.0039 | 0.0013 | -0.0006 | 0.0151 | -0.0062 | -0.0074 | -360.1619 | 17.4069 | -360.4789 | 17.7436 | -360.8881 | 18.1769 | -360.8974 | 17.5342 | -352.6629 | 18.723 | -352.6998 | 16.8299
12:16 | 3382 | 36.5056 | 200.1977 | 447.2172 | 451.4136 | -17.4734 | -43.4207 | 9.4652 | 6.1953 | 0.6335 | -1.0151 | 1.6106 | -1.7439 | 10.1153 | 3.1412 | 0.6087 | 0.6523 | 0.9633 | 0.7301 | -129.6839 | -2.1651 | 5.0187 | 1.3499 | -4.1731 | -2.7774 | 3.6893 |  | 1.8494 | -0.501 | 4.01 | 3.3628 | 3.3473 | 1.0573 | 10.7303 | 14.2148 | 14.7922 | 11.0436 | 0 | -0.0032 | 0.0007 | 0.0037 | 0.0005 | -0.0005 | 0.0076 | -0.0139 | 0.0003 | -360.1896 | 17.409 | -360.4296 | 17.6964 | -360.7866 | 18.1625 | -360.9189 | 17.5671 | -352.6998 | 18.7251 | -352.6444 | 16.795
12:16 | 3383 | 36.5278 | 200.219 | 447.2445 | 451.4071 | -17.3445 | -43.4433 | 9.4661 | 6.3157 | 0.6988 | -0.929 | 1.6933 | -1.7189 | 10.1576 | 3.1309 | 0.6074 | 0.6511 | 0.9603 | 0.7311 | -129.5698 | -2.1676 | 4.9284 | 1.338 | -4.1638 | -2.6631 | 3.7582 |  | 1.8587 | -0.485 | 4.0084 | 3.3626 | 3.3453 | 1.0552 | 10.7072 | 14.2262 | 14.7738 | 11.0382 | -0.0005 | -0.0032 | 0.0002 | 0.0039 | 0.0007 | -0.0011 | 0.0024 | -0.0051 | -0.0099 | -360.2111 | 17.411 | -360.4358 | 17.68 | -360.7497 | 18.1173 | -360.8389 | 17.5424 | -352.6844 | 18.7374 | -352.6475 | 16.7889
12:16 | 3384 | 36.5006 | 200.2115 | 447.2589 | 451.3657 | -17.2678 | -43.2859 | 9.5658 | 6.3859 | 0.6867 | -0.8138 | 1.7161 | -1.6991 | 10.1841 | 3.1697 | 0.6077 | 0.6502 | 0.9569 | 0.7302 | -129.5624 | -2.091 | 5.0406 | 1.3906 | -4.1708 | -2.7142 | 3.766 |  | 1.9242 | -0.5391 | 4.0101 | 3.363 | 3.3493 | 1.0554 | 10.736 | 14.244 | 14.8001 | 11.0313 | -0.0003 | -0.0024 | 0.0011 | 0.0041 | 0.0002 | -0.0004 | 0.0062 | -0.0005 | -0.0013 | -360.1188 | 17.3884 | -360.4696 | 17.721 | -360.8143 | 18.1337 | -360.842 | 17.5034 | -352.6044 | 18.723 | -352.6875 | 16.8197
12:16 | 3385 | 36.6133 | 200.2812 | 447.3029 | 451.4672 | -17.3619 | -43.3681 | 9.4484 | 6.3594 | 0.7543 | -0.9028 | 1.718 | -1.8152 | 10.1253 | 3.0937 | 0.608 | 0.6496 | 0.9581 | 0.7296 | -129.5099 | -2.0109 | 5.1766 | 1.2441 | -4.2138 | -2.7368 | 3.6991 |  | 1.9616 | -0.4811 | 4.0115 | 3.3635 | 3.3505 | 1.0559 | 10.7556 | 14.2348 | 14.8433 | 11.0739 | 0.0001 | -0.0033 | 0.0008 | 0.0038 | 0.0009 | -0.0002 | 0.0204 | -0.0111 | -0.0101 | -360.1435 | 17.3864 | -360.4542 | 17.7149 | -360.8327 | 18.1851 | -360.9435 | 17.5445 | -352.6783 | 18.7107 | -352.6506 | 16.8032
12:16 | 3386 | 36.6334 | 200.1489 | 447.3035 | 451.4913 | -17.4123 | -43.4499 | 9.3338 | 6.3002 | 0.7733 | -0.9714 | 1.6924 | -1.7589 | 10.1388 | 3.1335 | 0.6082 | 0.6528 | 0.9569 | 0.7309 | -129.5955 | -2.0577 | 5.0332 | 1.3543 | -4.1818 | -2.6062 | 3.7166 |  | 2.0074 | -0.5062 | 4.0116 | 3.3623 | 3.3465 | 1.0559 | 10.7787 | 14.2581 | 14.8039 | 11.0908 | 0.0002 | -0.003 | 0.0003 | 0.0032 | 0.0005 | -0.0007 | 0.018 | -0.0081 | -0.0208 | -360.2204 | 17.4315 | -360.4727 | 17.7067 | -360.7866 | 18.1625 | -360.9251 | 17.5835 | -352.7306 | 18.7497 | -352.6721 | 16.7971
12:16 | 3387 | 36.6365 | 200.2272 | 447.2517 | 451.5359 | -17.386 | -43.4876 | 9.4218 | 6.3248 | 0.7376 | -0.9511 | 1.6483 | -1.9318 | 10.0574 | 3.0046 | 0.6087 | 0.6482 | 0.956 | 0.7297 | -129.5373 | -2.1333 | 5.0705 | 1.3613 | -4.1008 | -2.5907 | 3.7891 |  | 2.0173 | -0.5062 | 4.0117 | 3.3634 | 3.3494 | 1.0567 | 10.7521 | 14.2662 | 14.8298 | 11.093 | -0.0001 | -0.0028 | 0.0007 | 0.0038 | 0.0006 | -0.0002 | 0.0028 | -0.0044 | -0.0126 | -360.1865 | 17.4274 | -360.5004 | 17.7354 | -360.8574 | 18.1399 | -360.8143 | 17.5219 | -352.6629 | 18.7559 | -352.7306 | 16.832
12:16 | 3388 | 36.6413 | 200.3095 | 447.2936 | 451.6002 | -17.4269 | -43.5165 | 9.3103 | 6.4298 | 0.7131 | -1.0595 | 1.6475 | -1.8455 | 10.2178 | 3.0819 | 0.6084 | 0.6489 | 0.958 | 0.7296 | -129.5411 | -2.1784 | 5.0779 | 1.4158 | -4.0475 | -2.5866 | 3.8157 |  | 2.0387 | -0.4684 | 4.0119 | 3.3663 | 3.349 | 1.0561 | 10.7545 | 14.2625 | 14.8072 | 11.0843 | -0.0004 | -0.0024 | 0.0001 | 0.0034 | 0.0011 | -0.0003 | 0.0156 | -0.0025 | -0.02 | -360.0696 | 17.3576 | -360.4173 | 17.7128 | -360.8389 | 18.1666 | -360.8697 | 17.5034 | -352.6013 | 18.7025 | -352.6383 | 16.8115
12:16 | 3389 | 36.6382 | 200.2119 | 447.25 | 451.526 | -17.448 | -43.4887 | 9.3456 | 6.4578 | 0.7117 | -1.1231 | 1.6409 | -1.8122 | 10.0921 | 3.0765 | 0.6086 | 0.6488 | 0.9568 | 0.729 | -129.64 | -2.1202 | 5.01 | 1.333 | -4.1417 | -2.6962 | 3.7265 |  | 2.0387 | -0.458 | 4.0106 | 3.3648 | 3.3505 | 1.0569 | 10.7371 | 14.222 | 14.813 | 11.0555 | -0.0001 | -0.0026 | 0.0006 | 0.004 | 0.0003 | -0.0006 | 0.016 | -0.0021 | -0.0063 | -360.1558 | 17.3802 | -360.4019 | 17.6738 | -360.7435 | 18.1461 | -360.882 | 17.5424 | -352.6444 | 18.6984 | -352.6075 | 16.7786
12:16 | 3390 | 36.6179 | 200.2217 | 447.3182 | 451.5195 | -17.433 | -43.4669 | 9.3701 | 6.4378 | 0.6837 | -1.0956 | 1.6161 | -1.824 | 10.0431 | 3.0145 | 0.608 | 0.6481 | 0.9592 | 0.7288 | -129.5759 | -2.1427 | 5.0151 | 1.337 | -4.1372 | -2.6898 | 3.6688 |  | 2.0046 | -0.5481 | 4.0109 | 3.3642 | 3.3492 | 1.0549 | 10.7175 | 14.2311 | 14.7803 | 11.019 | -0.0002 | -0.0032 | 0.0008 | 0.0042 | 0.0012 | -0.0004 | -0.0007 | -0.0001 | 0.0097 | -360.2265 | 17.4315 | -360.4881 | 17.7087 | -360.8112 | 18.1235 | -360.8389 | 17.5198 | -352.6783 | 18.7518 | -352.6813 | 16.8012
12:16 | 3391 | 36.5753 | 200.3006 | 447.3637 | 451.564 | -17.4154 | -43.5044 | 9.327 | 6.3679 | 0.6133 | -1.1739 | 1.5714 | -1.7532 | 10.034 | 3.0113 | 0.6085 | 0.6484 | 0.9596 | 0.7299 | -129.5905 | -2.216 | 5.0716 | 1.2728 | -4.132 | -2.6194 | 3.7173 |  | 2.0052 | -0.531 | 4.0093 | 3.3644 | 3.3501 | 1.0561 | 10.7509 | 14.2246 | 14.7879 | 11.0457 | -0.0001 | -0.0029 | 0.0006 | 0.0036 | 0.001 | -0.0001 | 0.0119 | -0.0104 | -0.0107 | -360.1619 | 17.4151 | -360.5096 | 17.7477 | -360.9066 | 18.1687 | -360.8881 | 17.5137 | -352.6413 | 18.7251 | -352.7183 | 16.8381
12:16 | 3392 | 36.7222 | 200.2774 | 447.4067 | 451.4908 | -17.4412 | -43.4298 | 9.2582 | 6.4864 | 0.7013 | -1.032 | 1.6941 | -1.7746 | 10.0536 | 3.0613 | 0.6066 | 0.6487 | 0.9584 | 0.7292 | -129.5553 | -2.1794 | 5.0658 | 1.3104 | -4.1616 | -2.6904 | 3.688 |  | 2.0812 | -0.5379 | 4.0112 | 3.3673 | 3.352 | 1.0568 | 10.7336 | 14.2649 | 14.7868 | 11.0807 | -0.0006 | -0.003 | 0.0009 | 0.004 | 0.0012 | -0.0008 | 0.0132 | -0.003 | 0.0034 | -360.1773 | 17.4007 | -360.4481 | 17.7128 | -360.8604 | 18.1769 | -360.9158 | 17.5486 | -352.6906 | 18.7148 | -352.6783 | 16.8115
12:16 | 3393 | 36.6839 | 200.2901 | 447.3564 | 451.5114 | -17.3302 | -43.4024 | 9.3168 | 6.4196 | 0.6528 | -0.9653 | 1.7309 | -1.8102 | 10.1123 | 3.0498 | 0.6084 | 0.6492 | 0.9604 | 0.7295 | -129.5791 | -2.0671 | 5.0345 | 1.5292 | -4.1173 | -2.6485 | 3.7804 |  | 2.0852 | -0.3935 | 4.0112 | 3.3625 | 3.3502 | 1.0567 | 10.7474 | 14.256 | 14.8206 | 11.0764 | -0.0001 | -0.0026 | 0.0009 | 0.0038 | 0.0009 | 0.0003 | 0.012 | -0.0189 | -0.025 | -360.2081 | 17.4315 | -360.4819 | 17.6841 | -360.7773 | 18.1399 | -360.8666 | 17.5424 | -352.6967 | 18.7456 | -352.6752 | 16.7909
12:16 | 3394 | 36.706 | 200.2917 | 447.2914 | 451.5072 | -17.358 | -43.3574 | 9.3041 | 6.3999 | 0.6329 | -1.0114 | 1.6243 | -1.8191 | 10.0699 | 3.0253 | 0.6065 | 0.648 | 0.9558 | 0.7278 | -129.6048 | -2.077 | 5.0429 | 1.4787 | -4.1121 | -2.7747 | 3.7053 |  | 2.1133 | -0.4446 | 4.0122 | 3.3637 | 3.3502 | 1.0542 | 10.7625 | 14.2533 | 14.81 | 11.0403 | 0.0003 | -0.0033 | 0.0005 | 0.0034 | 0.0009 | -0.0008 | -0.0048 | -0.0179 | -0.0279 | -360.1311 | 17.4131 | -360.4912 | 17.719 | -360.8112 | 18.1255 | -360.8266 | 17.4993 | -352.626 | 18.7271 | -352.6875 | 16.8258
12:16 | 3395 | 36.6445 | 200.2199 | 447.295 | 451.4606 | -17.4156 | -43.4572 | 9.3273 | 6.377 | 0.5847 | -0.9744 | 1.6578 | -1.7767 | 10.0531 | 3.0587 | 0.6063 | 0.648 | 0.9549 | 0.7281 | -129.4847 | -2.0248 | 5.0179 | 1.4235 | -4.1031 | -2.6988 | 3.6511 |  | 2.1351 | -0.3685 | 4.0099 | 3.3622 | 3.3489 | 1.055 | 10.7683 | 14.2361 | 14.8053 | 11.0515 | 0.0002 | -0.0028 | 0.0009 | 0.0038 | 0.0006 | -0.0002 | 0.0036 | -0.0065 | -0.0282 | -360.1188 | 17.3864 | -360.4204 | 17.7005 | -360.8204 | 18.1543 | -360.8943 | 17.5116 | -352.629 | 18.7087 | -352.6198 | 16.7971
12:16 | 3396 | 36.6352 | 200.2058 | 447.2785 | 451.4385 | -17.3793 | -43.5193 | 9.2938 | 6.3577 | 0.4963 | -1.0655 | 1.5612 | -1.7775 | 10.1124 | 3.0693 | 0.6075 | 0.6476 | 0.96 | 0.728 | -129.598 | -2.0201 | 4.9896 | 1.3706 | -4.0757 | -2.7321 | 3.7264 |  | 2.1214 | -0.3265 | 4.0123 | 3.3645 | 3.3483 | 1.057 | 10.7601 | 14.2803 | 14.8162 | 11.0659 | -0.0003 | -0.0025 | 0.0008 | 0.0041 | 0.001 | -0.0003 | 0.0216 | -0.0096 | -0.0055 | -360.2081 | 17.4131 | -360.4942 | 17.6861 | -360.7743 | 18.1584 | -360.9066 | 17.5506 | -352.6844 | 18.7251 | -352.6752 | 16.7827
12:16 | 3397 | 36.6454 | 200.1875 | 447.2676 | 451.5748 | -17.3363 | -43.5344 | 9.3254 | 6.2545 | 0.4701 | -1.0271 | 1.5446 | -1.8418 | 10.0509 | 3.034 | 0.6085 | 0.6478 | 0.958 | 0.7277 | -129.5821 | -2.0229 | 5.0351 | 1.2798 | -4.1123 | -2.5615 | 3.7882 |  | 2.1905 | -0.3761 | 4.0108 | 3.3616 | 3.3501 | 1.0556 | 10.7315 | 14.2389 | 14.7867 | 11.0277 | -0.0005 | -0.0029 | 0.0004 | 0.0038 | 0.0006 | -0.0007 | 0.012 | -0.0206 | -0.0071 | -360.2142 | 17.45 | -360.5281 | 17.7375 | -360.8697 | 18.1296 | -360.8327 | 17.5486 | -352.6844 | 18.7497 | -352.7213 | 16.8279
12:16 | 3398 | 36.6726 | 200.1615 | 447.2426 | 451.474 | -17.3396 | -43.4996 | 9.4342 | 6.3077 | 0.4318 | -0.9612 | 1.5217 | -1.7844 | 10.1009 | 3.1432 | 0.6085 | 0.6503 | 0.961 | 0.7282 | -129.5464 | -2.0938 | 5.0424 | 1.2857 | -4.0428 | -2.604 | 3.7082 |  | 2.0767 | -0.3998 | 4.0115 | 3.3645 | 3.3462 | 1.0558 | 10.7751 | 14.2434 | 14.8319 | 11.0402 | 0.0005 | -0.0024 | 0.0013 | 0.0046 | 0.0005 | -0.0005 | 0.0105 | -0.0013 | -0.0073 | -360.1865 | 17.4151 | -360.4666 | 17.7149 | -360.8358 | 18.1666 | -360.8943 | 17.5363 | -352.6598 | 18.7271 | -352.7244 | 16.8197
12:16 | 3399 | 36.7012 | 200.2588 | 447.2329 | 451.4202 | -17.3615 | -43.6022 | 9.3509 | 6.3468 | 0.5445 | -0.9596 | 1.6383 | -1.8382 | 9.9641 | 3.0797 | 0.6092 | 0.6462 | 0.9575 | 0.7273 | -129.5289 | -2.121 | 4.9935 | 1.3297 | -4.1502 | -2.6505 | 3.6932 |  | 2.1235 | -0.4123 | 4.0103 | 3.3646 | 3.3497 | 1.0556 | 10.7348 | 14.1908 | 14.7756 | 11.0475 | 0.0003 | -0.0029 | 0.0004 | 0.0035 | 0.0011 | -0.0008 | 0.0087 | -0.0055 | -0.023 | -360.1835 | 17.3802 | -360.4235 | 17.6882 | -360.7927 | 18.1481 | -360.882 | 17.5506 | -352.6967 | 18.7087 | -352.6413 | 16.8074
12:16 | 3400 | 36.6826 | 200.2594 | 447.3226 | 451.4633 | -17.3201 | -43.5369 | 9.3523 | 6.3046 | 0.4707 | -0.9852 | 1.6675 | -1.8261 | 9.954 | 2.9858 | 0.61 | 0.649 | 0.9577 | 0.729 | -129.4961 | -2.1316 | 4.9886 | 1.3666 | -4.0642 | -2.5849 | 3.768 |  | 2.1053 | -0.4169 | 4.0115 | 3.3652 | 3.3485 | 1.0565 | 10.7383 | 14.2289 | 14.7786 | 11.0742 | -0.0002 | -0.0027 | 0.0009 | 0.0039 | 0.0008 | -0.0003 | 0.0171 | 0.0079 | -0.0002 | -360.1619 | 17.4151 | -360.4358 | 17.682 | -360.7681 | 18.1153 | -360.8204 | 17.5219 | -352.6444 | 18.723 | -352.6506 | 16.7971
12:16 | 3401 | 36.6539 | 200.3217 | 447.3405 | 451.5428 | -17.3107 | -43.5249 | 9.4117 | 6.2914 | 0.3582 | -0.9811 | 1.6718 | -1.8477 | 10.1344 | 3.0758 | 0.6083 | 0.6516 | 0.9534 | 0.7282 | -129.6039 | -2.1599 | 4.9342 | 1.3968 | -4.0132 | -2.6304 | 3.8165 |  | 2.1422 | -0.3708 | 4.0108 | 3.3616 | 3.3476 | 1.0555 | 10.7277 | 14.2422 | 14.8016 | 11.068 | 0.0002 | -0.0025 | 0.001 | 0.0035 | 0.0006 | -0.001 | -0.0076 | -0.0123 | -0.0006 | -360.1342 | 17.4069 | -360.4635 | 17.7128 | -360.8204 | 18.1337 | -360.8697 | 17.526 | -352.6352 | 18.7128 | -352.6813 | 16.8074
12:16 | 3402 | 36.5795 | 200.2238 | 447.2496 | 451.5766 | -17.3433 | -43.5953 | 9.3589 | 6.1957 | 0.2675 | -1.0921 | 1.6132 | -1.8566 | 10.1111 | 3.1524 | 0.6087 | 0.6483 | 0.9517 | 0.7284 | -129.636 | -2.0528 | 5.0313 | 1.5398 | -4.0233 | -2.511 | 3.8925 |  | 2.1212 | -0.4123 | 4.0118 | 3.3629 | 3.3465 | 1.0561 | 10.7719 | 14.2624 | 14.8467 | 11.0847 | -0.0001 | -0.0032 | 0.0002 | 0.0031 | 0.0001 | -0.0006 | 0.0133 | -0.0154 | -0.0102 | -360.2173 | 17.4172 | -360.4758 | 17.7087 | -360.8327 | 18.1625 | -360.8758 | 17.5486 | -352.6844 | 18.7333 | -352.6875 | 16.8074
12:16 | 3403 | 36.6379 | 200.3268 | 447.3818 | 451.6193 | -17.3563 | -43.5999 | 9.382 | 6.2555 | 0.2548 | -1.0784 | 1.6156 | -1.8719 | 10.1751 | 3.1971 | 0.6081 | 0.6499 | 0.9556 | 0.7274 | -129.5403 | -2.0093 | 5.0256 | 1.413 | -4.1142 | -2.6887 | 3.7499 |  | 2.1268 | -0.3894 | 4.0109 | 3.363 | 3.3492 | 1.0563 | 10.7186 | 14.2382 | 14.7653 | 11.0313 | 0.0007 | -0.0027 | 0.0012 | 0.004 | 0.0014 | -0.0005 | 0.0122 | -0.0111 | 0.0057 | -360.1588 | 17.4131 | -360.4758 | 17.7128 | -360.7989 | 18.1543 | -360.8758 | 17.5383 | -352.666 | 18.7292 | -352.6937 | 16.8156
12:16 | 3404 | 36.6914 | 200.3059 | 447.3252 | 451.6708 | -17.3982 | -43.5359 | 9.4209 | 6.2158 | 0.1915 | -1.2292 | 1.5499 | -1.8227 | 10.1178 | 3.1134 | 0.6071 | 0.6486 | 0.9549 | 0.7274 | -129.562 | -2.0235 | 5.103 | 1.3027 | -4.1636 | -2.6516 | 3.7236 |  | 2.1757 | -0.3562 | 4.0116 | 3.3661 | 3.3483 | 1.0559 | 10.7313 | 14.2509 | 14.8188 | 11.0439 | -0.0004 | -0.0027 | 0.0007 | 0.0039 | 0.0006 | -0.0001 | 0.0278 | 0.0038 | 0.0046 | -360.1404 | 17.3966 | -360.4389 | 17.6985 | -360.7804 | 18.1358 | -360.845 | 17.528 | -352.6198 | 18.7066 | -352.6567 | 16.7991
12:16 | 3405 | 36.5574 | 200.1944 | 447.3337 | 451.695 | -17.3598 | -43.4499 | 9.3762 | 6.1372 | 0.1446 | -1.2976 | 1.4975 | -1.8671 | 10.0325 | 3.0268 | 0.6076 | 0.6473 | 0.9514 | 0.7287 | -129.5013 | -2.115 | 5.0423 | 1.3568 | -4.1509 | -2.548 | 3.7874 |  | 2.1821 | -0.4914 | 4.0111 | 3.3662 | 3.3504 | 1.0559 | 10.7453 | 14.2646 | 14.8194 | 11.0526 | -0.0006 | -0.0028 | 0.0007 | 0.004 | 0.0005 | -0.0008 | 0.0259 | -0.0037 | 0.0101 | -360.125 | 17.4028 | -360.4389 | 17.6902 | -360.802 | 18.1502 | -360.8789 | 17.5219 | -352.6198 | 18.7169 | -352.6475 | 16.7971
12:16 | 3406 | 36.6484 | 200.3072 | 447.4253 | 451.681 | -17.4198 | -43.4519 | 9.4613 | 6.112 | 0.245 | -1.1354 | 1.4948 | -1.7495 | 10.1157 | 3.1639 | 0.608 | 0.649 | 0.9587 | 0.7315 | -129.5446 | -2.0901 | 5.0884 | 1.4939 | -4.106 | -2.6574 | 3.7963 |  | 2.0986 | -0.5293 | 4.0111 | 3.3679 | 3.3517 | 1.0562 | 10.7371 | 14.2336 | 14.7899 | 11.0381 | 0 | -0.0031 | 0.0013 | 0.0047 | 0.0011 | 0 | -0.0074 | -0.0089 | -0.019 | -360.2081 | 17.4213 | -360.5004 | 17.719 | -360.8143 | 18.1522 | -360.9066 | 17.5424 | -352.6721 | 18.7333 | -352.6967 | 16.8135
12:16 | 3407 | 36.6666 | 200.2935 | 447.3258 | 451.6555 | -17.3726 | -43.3986 | 9.381 | 6.198 | 0.3199 | -1.0072 | 1.5951 | -1.8479 | 10.1317 | 3.1637 | 0.6087 | 0.6486 | 0.9568 | 0.7307 | -129.6122 | -2.1409 | 4.9438 | 1.3927 | -4.1623 | -2.5794 | 3.7481 |  | 2.0906 | -0.4455 | 4.011 | 3.3642 | 3.3459 | 1.0559 | 10.7661 | 14.245 | 14.8178 | 11.0732 | -0.0001 | -0.003 | 0.0008 | 0.0036 | 0.0008 | -0.0007 | 0.0068 | -0.0041 | -0.0107 | -360.2019 | 17.411 | -360.5004 | 17.7169 | -360.8204 | 18.1604 | -360.8912 | 17.5363 | -352.6875 | 18.7292 | -352.6844 | 16.8258
12:17 | 3408 | 36.5937 | 200.3263 | 447.3478 | 451.6325 | -17.4426 | -43.4259 | 9.3257 | 6.2527 | 0.2972 | -1.0168 | 1.6059 | -1.852 | 10.1 | 3.152 | 0.6095 | 0.6483 | 0.9599 | 0.729 | -129.6399 | -2.1577 | 4.9327 | 1.4699 | -4.1684 | -2.5876 | 3.7235 |  | 2.1612 | -0.4607 | 4.0111 | 3.3645 | 3.3488 | 1.0561 | 10.729 | 14.2372 | 14.7824 | 11.0529 | 0.0001 | -0.0027 | 0.0007 | 0.0038 | 0.0011 | -0.0001 | -0.0023 | -0.0222 | -0.0171 | -360.125 | 17.3925 | -360.4389 | 17.6923 | -360.7804 | 18.1379 | -360.9066 | 17.5321 | -352.6352 | 18.7045 | -352.6475 | 16.8094
12:17 | 3409 | 36.649 | 200.2696 | 447.2404 | 451.5712 | -17.3886 | -43.3745 | 9.3205 | 6.1794 | 0.2572 | -1.0562 | 1.5791 | -1.8134 | 10.1927 | 3.2406 | 0.6083 | 0.6482 | 0.9584 | 0.7288 | -129.6104 | -2.2019 | 4.9672 | 1.4579 | -4.2008 | -2.5984 | 3.8138 |  | 2.1571 | -0.3592 | 4.0106 | 3.3645 | 3.3494 | 1.056 | 10.7163 | 14.2589 | 14.8147 | 11.0522 | -0.0006 | -0.0028 | 0.001 | 0.0041 | 0.0006 | -0.0004 | 0.002 | -0.0044 | -0.031 | -360.1773 | 17.3987 | -360.4327 | 17.7005 | -360.7927 | 18.1071 | -360.8327 | 17.5321 | -352.6629 | 18.7128 | -352.6721 | 16.793
12:17 | 3410 | 36.7225 | 200.3832 | 447.4141 | 451.7509 | -17.3631 | -43.332 | 9.397 | 6.1614 | 0.3426 | -1.0823 | 1.605 | -1.7539 | 10.1786 | 3.1639 | 0.607 | 0.6492 | 0.9637 | 0.7294 | -129.5232 | -2.1524 | 5.0637 | 1.4844 | -4.1106 | -2.5527 | 3.7809 |  | 2.2149 | -0.4243 | 4.0107 | 3.3654 | 3.3498 | 1.0577 | 10.7291 | 14.26 | 14.7803 | 11.0306 | -0.0002 | -0.0031 | 0.0006 | 0.0036 | 0.0009 | -0.0004 | 0.008 | -0.0089 | -0.0058 | -360.1927 | 17.4274 | -360.4973 | 17.7457 | -360.842 | 18.1276 | -360.8574 | 17.526 | -352.6752 | 18.7415 | -352.7029 | 16.8176
12:17 | 3411 | 36.6946 | 200.3317 | 447.3063 | 451.6098 | -17.3426 | -43.3133 | 9.4222 | 6.1731 | 0.4091 | -1.0565 | 1.5288 | -1.6924 | 10.2123 | 3.1556 | 0.6089 | 0.6463 | 0.9563 | 0.7279 | -129.526 | -2.0889 | 5.1089 | 1.4696 | -4.0917 | -2.6273 | 3.7856 |  | 2.2369 | -0.419 | 4.0113 | 3.3647 | 3.3481 | 1.0563 | 10.7555 | 14.2698 | 14.7992 | 11.0731 | 0.0003 | -0.0032 | 0.0009 | 0.0044 | 0.0007 | -0.0001 | 0.0043 | -0.0021 | -0.0018 | -360.1804 | 17.4069 | -360.4758 | 17.7334 | -360.842 | 18.1379 | -360.885 | 17.5424 | -352.6783 | 18.7271 | -352.6721 | 16.8299
12:17 | 3412 | 36.7643 | 200.3337 | 447.2792 | 451.7279 | -17.3636 | -43.3189 | 9.4036 | 6.2953 | 0.4745 | -1.1337 | 1.5712 | -1.7186 | 10.2078 | 3.1749 | 0.6079 | 0.6491 | 0.9582 | 0.7296 | -129.6071 | -2.1848 | 5.1203 | 1.3181 | -4.0858 | -2.6193 | 3.735 |  | 2.1981 | -0.4221 | 4.0099 | 3.361 | 3.3476 | 1.0569 | 10.7591 | 14.2151 | 14.8059 | 11.0833 | -0.0002 | -0.0028 | 0.0011 | 0.0039 | 0.0012 | -0.0006 | 0.0052 | -0.0201 | -0.0213 | -360.1711 | 17.411 | -360.4296 | 17.682 | -360.7804 | 18.1112 | -360.882 | 17.5301 | -352.6475 | 18.7251 | -352.6506 | 16.793
12:17 | 3413 | 36.6346 | 200.262 | 447.3321 | 451.6559 | -17.4155 | -43.2082 | 9.3339 | 6.2082 | 0.4211 | -1.1835 | 1.4985 | -1.8154 | 10.0598 | 3.0931 | 0.6071 | 0.6477 | 0.9557 | 0.7294 | -129.6225 | -2.088 | 5.108 | 1.2879 | -4.0662 | -2.5827 | 3.8319 |  | 2.2064 | -0.3798 | 4.0101 | 3.3633 | 3.3467 | 1.057 | 10.7416 | 14.2732 | 14.808 | 11.0536 | -0.0001 | -0.0024 | 0.0009 | 0.0039 | 0.0005 | -0.0003 | -0.0018 | 0.0069 | -0.0117 | -360.1558 | 17.409 | -360.4819 | 17.7087 | -360.7897 | 18.0947 | -360.8327 | 17.5137 | -352.6383 | 18.7251 | -352.6598 | 16.8094
12:17 | 3414 | 36.6924 | 200.3196 | 447.2598 | 451.7271 | -17.352 | -43.2147 | 9.4461 | 6.2334 | 0.4834 | -1.2312 | 1.559 | -1.8193 | 10.1107 | 3.0734 | 0.6096 | 0.65 | 0.9648 | 0.7286 | -129.5726 | -2.0224 | 5.1774 | 1.3345 | -4.112 | -2.6534 | 3.7306 |  | 2.1974 | -0.3403 | 4.0118 | 3.3655 | 3.3491 | 1.0572 | 10.7302 | 14.2324 | 14.8117 | 11.0313 | -0.0006 | -0.0031 | 0.0005 | 0.0038 | 0.0006 | -0.0012 | 0.0137 | 0.0023 | -0.0053 | -360.1465 | 17.4069 | -360.4573 | 17.719 | -360.845 | 18.1379 | -360.8974 | 17.5445 | -352.6598 | 18.7148 | -352.6875 | 16.8197
12:17 | 3415 | 36.6674 | 200.3723 | 447.3751 | 451.7046 | -17.3573 | -43.2293 | 9.4322 | 6.1978 | 0.4555 | -1.176 | 1.6611 | -1.7109 | 10.2135 | 3.1836 | 0.6087 | 0.6508 | 0.9609 | 0.7289 | -129.6641 | -1.9545 | 5.1676 | 1.3453 | -4.0326 | -2.5993 | 3.7889 |  | 2.196 | -0.4011 | 4.0114 | 3.3643 | 3.3491 | 1.0588 | 10.7382 | 14.2348 | 14.8144 | 11.045 | 0.0002 | -0.0029 | 0.0008 | 0.0038 | 0.0007 | -0.0003 | 0.0249 | -0.0027 | 0.0042 | -360.1835 | 17.4254 | -360.4666 | 17.7046 | -360.8204 | 18.1276 | -360.9004 | 17.5629 | -352.706 | 18.7333 | -352.666 | 16.8074
12:17 | 3416 | 36.7323 | 200.4207 | 447.3563 | 451.7689 | -17.4297 | -43.1277 | 9.4033 | 6.2173 | 0.4705 | -1.0434 | 1.6967 | -1.8086 | 10.1176 | 3.219 | 0.6083 | 0.6481 | 0.9581 | 0.7291 | -129.5205 | -1.9206 | 5.2012 | 1.2512 | -4.0239 | -2.603 | 3.7533 |  | 2.1489 | -0.4448 | 4.0092 | 3.3603 | 3.3463 | 1.057 | 10.736 | 14.2498 | 14.7885 | 11.0717 | -0.0003 | -0.0033 | 0.0006 | 0.0036 | 0.001 | -0.0005 | 0.0025 | -0.0013 | -0.0221 | -360.1865 | 17.4048 | -360.4789 | 17.7046 | -360.805 | 18.0906 | -360.842 | 17.5486 | -352.6937 | 18.7415 | -352.6844 | 16.7991
12:17 | 3417 | 36.6725 | 200.2611 | 447.2689 | 451.7496 | -17.3995 | -43.1837 | 9.4218 | 6.1819 | 0.4555 | -1.0294 | 1.5775 | -1.7362 | 10.1899 | 3.1449 | 0.6084 | 0.6526 | 0.956 | 0.7289 | -129.5824 | -2.0793 | 5.0877 | 1.315 | -4.1335 | -2.6333 | 3.6628 |  | 2.2016 | -0.4305 | 4.0111 | 3.3614 | 3.3467 | 1.0577 | 10.7417 | 14.2441 | 14.7954 | 11.0482 | -0.0004 | -0.0027 | 0.0011 | 0.0041 | 0.0008 | -0.0005 | 0.0037 | -0.0054 | -0.0327 | -360.1465 | 17.3823 | -360.4358 | 17.7087 | -360.7927 | 18.0988 | -360.8574 | 17.5219 | -352.5736 | 18.7107 | -352.6598 | 16.8094
12:17 | 3418 | 36.7475 | 200.3726 | 447.4169 | 451.8352 | -17.3245 | -43.192 | 9.4809 | 6.1442 | 0.3774 | -1.1197 | 1.6064 | -1.7965 | 10.1862 | 3.126 | 0.6092 | 0.6513 | 0.9562 | 0.7285 | -129.5048 | -1.9852 | 5.1394 | 1.4162 | -4.1918 | -2.5941 | 3.7246 |  | 2.2299 | -0.3644 | 4.0115 | 3.3619 | 3.3485 | 1.0587 | 10.7325 | 14.2463 | 14.8202 | 11.0796 | -0.0002 | -0.0025 | 0.0011 | 0.004 | 0.0007 | -0.0002 | 0.0159 | 0.0019 | -0.0034 | -360.1588 | 17.3864 | -360.4019 | 17.6964 | -360.8266 | 18.1194 | -360.8727 | 17.5527 | -352.6352 | 18.6922 | -352.6413 | 16.8032
12:17 | 3419 | 36.7811 | 200.3122 | 447.3947 | 451.788 | -17.3458 | -43.2442 | 9.4468 | 6.2152 | 0.3877 | -1.0987 | 1.7122 | -1.7631 | 10.1016 | 3.0941 | 0.6079 | 0.6505 | 0.9612 | 0.7293 | -129.5063 | -2.1777 | 5.1297 | 1.4232 | -4.1686 | -2.6113 | 3.7166 |  | 2.1636 | -0.3349 | 4.0108 | 3.3628 | 3.3474 | 1.0581 | 10.7544 | 14.2684 | 14.8199 | 11.084 | 0.0002 | -0.0031 | 0.0008 | 0.0041 | 0.0004 | -0.0009 | -0.0094 | 0.0016 | -0.0163 | -360.2265 | 17.4377 | -360.4758 | 17.6985 | -360.802 | 18.1132 | -360.9035 | 17.5691 | -352.7029 | 18.7374 | -352.669 | 16.7889
12:17 | 3420 | 36.8149 | 200.3771 | 447.4219 | 451.8782 | -17.3969 | -43.2909 | 9.441 | 6.2004 | 0.4145 | -1.2343 | 1.6804 | -1.7836 | 10.114 | 3.0813 | 0.6086 | 0.6485 | 0.9609 | 0.7288 | -129.51 | -2.0447 | 5.2359 | 1.4604 | -4.2325 | -2.5878 | 3.6681 |  | 2.2091 | -0.3797 | 4.0115 | 3.3614 | 3.3483 | 1.057 | 10.7347 | 14.2431 | 14.8182 | 11.0872 | 0.0005 | -0.0029 | 0.0007 | 0.004 | 0.0005 | -0.0001 | 0.006 | -0.01 | -0.0303 | -360.1835 | 17.4172 | -360.5219 | 17.7477 | -360.845 | 18.1153 | -360.8758 | 17.5568 | -352.6752 | 18.7415 | -352.7337 | 16.8443
12:17 | 3421 | 36.7329 | 200.3952 | 447.3403 | 451.8274 | -17.4763 | -43.3372 | 9.4227 | 6.1588 | 0.3459 | -1.3377 | 1.5699 | -1.7381 | 10.2292 | 3.1843 | 0.6083 | 0.6518 | 0.9612 | 0.7292 | -129.5551 | -2.0845 | 5.1593 | 1.3821 | -4.1717 | -2.612 | 3.7266 |  | 2.2273 | -0.3704 | 4.011 | 3.362 | 3.353 | 1.057 | 10.7591 | 14.2671 | 14.829 | 11.0659 | -0.0004 | -0.0027 | 0.0005 | 0.0038 | 0.0009 | -0.0005 | 0.0044 | -0.0061 | -0.0144 | -360.1435 | 17.3658 | -360.405 | 17.6923 | -360.805 | 18.1317 | -360.922 | 17.5547 | -352.6352 | 18.6881 | -352.589 | 16.7971
12:17 | 3422 | 36.858 | 200.4823 | 447.4384 | 451.8711 | -17.5072 | -43.2709 | 9.3897 | 6.1928 | 0.4956 | -1.2159 | 1.6956 | -1.7311 | 10.1311 | 3.086 | 0.6076 | 0.6522 | 0.9591 | 0.7297 | -129.6405 | -2.1409 | 5.1061 | 1.5334 | -4.1152 | -2.4364 | 3.7509 |  | 2.1678 | -0.2471 | 4.0107 | 3.3676 | 3.3507 | 1.0578 | 10.7623 | 14.2539 | 14.82 | 11.0619 | 0 | -0.0021 | 0.0009 | 0.0041 | 0.0007 | 0 | 0.0117 | 0.0021 | -0.0145 | -360.1835 | 17.4028 | -360.4296 | 17.682 | -360.7404 | 18.0886 | -360.8543 | 17.5609 | -352.6721 | 18.7169 | -352.6229 | 16.7724
12:17 | 3423 | 36.8044 | 200.3355 | 447.3507 | 451.821 | -17.3681 | -43.2696 | 9.4091 | 6.2595 | 0.5217 | -1.2703 | 1.6906 | -1.7003 | 10.1434 | 3.0745 | 0.6079 | 0.6506 | 0.957 | 0.7269 | -129.5525 | -2.0219 | 5.0698 | 1.4551 | -4.0517 | -2.5653 | 3.6843 |  | 2.2039 | -0.256 | 4.0115 | 3.3663 | 3.3522 | 1.057 | 10.7393 | 14.2419 | 14.7995 | 11.063 | 0.0004 | -0.0029 | 0.0003 | 0.0031 | 0.0007 | -0.0008 | 0.0099 | -0.0011 | -0.0121 | -360.165 | 17.4274 | -360.5281 | 17.7457 | -360.8697 | 18.1112 | -360.8481 | 17.5465 | -352.6598 | 18.7271 | -352.6937 | 16.8258
12:17 | 3424 | 36.8266 | 200.4041 | 447.4954 | 451.9299 | -17.4358 | -43.1712 | 9.4661 | 6.2333 | 0.5158 | -1.2714 | 1.7691 | -1.6234 | 10.2198 | 3.1922 | 0.6082 | 0.6553 | 0.9578 | 0.7278 | -129.5426 | -2.1337 | 5.1534 | 1.3235 | -4.0997 | -2.592 | 3.692 |  | 2.1392 | -0.4515 | 4.0109 | 3.3617 | 3.3471 | 1.0562 | 10.736 | 14.2266 | 14.8001 | 11.0775 | 0.0005 | -0.0028 | 0.0011 | 0.0041 | 0.0005 | -0.0004 | 0.0045 | -0.0048 | -0.0211 | -360.1681 | 17.3905 | -360.4358 | 17.721 | -360.842 | 18.1584 | -360.9281 | 17.5609 | -352.6475 | 18.7025 | -352.6598 | 16.8238
12:17 | 3425 | 36.7737 | 200.429 | 447.4156 | 451.8598 | -17.3671 | -43.3147 | 9.4233 | 6.2477 | 0.5864 | -1.2234 | 1.8635 | -1.7181 | 10.1919 | 3.1089 | 0.6088 | 0.6527 | 0.9587 | 0.7278 | -129.5509 | -2.004 | 5.2811 | 1.3661 | -4.1516 | -2.5765 | 3.7752 |  | 2.1129 | -0.3564 | 4.0106 | 3.3665 | 3.3479 | 1.0572 | 10.7093 | 14.2407 | 14.7865 | 11.033 | 0 | -0.003 | 0.0008 | 0.0041 | 0.0008 | -0.0007 | 0.012 | -0.0075 | -0.0001 | -360.1588 | 17.4048 | -360.4419 | 17.68 | -360.7527 | 18.105 | -360.8666 | 17.5547 | -352.6629 | 18.7148 | -352.669 | 16.7991
12:17 | 3426 | 36.6932 | 200.3231 | 447.3651 | 451.7886 | -17.3433 | -43.2514 | 9.5267 | 6.2607 | 0.5791 | -1.3044 | 1.8465 | -1.7599 | 10.1634 | 3.1089 | 0.6075 | 0.652 | 0.9584 | 0.7281 | -129.5982 | -1.9804 | 5.2224 | 1.4146 | -4.0803 | -2.5659 | 3.7241 |  | 2.1586 | -0.242 | 4.0112 | 3.3663 | 3.3471 | 1.056 | 10.767 | 14.2699 | 14.8465 | 11.0901 | -0.0002 | -0.0024 | 0.0008 | 0.0036 | 0.0008 | -0.0003 | -0.0026 | -0.0094 | -0.0231 | -360.1465 | 17.3966 | -360.4819 | 17.7313 | -360.8266 | 18.0968 | -360.8235 | 17.526 | -352.6352 | 18.7025 | -352.7029 | 16.8238
12:17 | 3427 | 36.7123 | 200.2993 | 447.3338 | 451.771 | -17.234 | -43.2069 | 9.5634 | 6.1975 | 0.5444 | -1.3547 | 1.8033 | -1.7132 | 10.2198 | 3.2295 | 0.6079 | 0.6506 | 0.9601 | 0.7287 | -129.5294 | -1.9967 | 5.2452 | 1.3693 | -4.0997 | -2.4839 | 3.7113 |  | 2.2018 | -0.2914 | 4.0099 | 3.3621 | 3.348 | 1.0562 | 10.7358 | 14.2211 | 14.7906 | 11.0478 | 0.0005 | -0.0023 | 0.0012 | 0.0043 | 0.0008 | -0.0006 | 0.0348 | -0.0082 | 0.0178 | -360.1711 | 17.4007 | -360.4542 | 17.721 | -360.8789 | 18.1502 | -360.8974 | 17.5629 | -352.6321 | 18.6943 | -352.666 | 16.8197
12:17 | 3428 | 36.7179 | 200.2948 | 447.4028 | 451.8043 | -17.2652 | -43.1665 | 9.5042 | 6.1434 | 0.5307 | -1.2287 | 1.8101 | -1.7435 | 10.1982 | 3.2704 | 0.61 | 0.6508 | 0.9593 | 0.7274 | -129.5441 | -1.9569 | 5.3045 | 1.4009 | -4.1022 | -2.552 | 3.6732 |  | 2.1667 | -0.3582 | 4.0101 | 3.3642 | 3.3479 | 1.0568 | 10.7314 | 14.2102 | 14.7878 | 11.0504 | 0.0001 | -0.0033 | 0.0003 | 0.0036 | 0.0005 | -0.0005 | 0.0032 | -0.0081 | -0.02 | -360.2142 | 17.4295 | -360.4727 | 17.7046 | -360.8143 | 18.105 | -360.8697 | 17.5753 | -352.6937 | 18.7415 | -352.6906 | 16.795
12:17 | 3429 | 36.6208 | 200.2174 | 447.3449 | 451.8129 | -17.2226 | -43.104 | 9.5235 | 6.1654 | 0.5666 | -1.3493 | 1.7991 | -1.6494 | 10.1699 | 3.2371 | 0.6079 | 0.6495 | 0.9587 | 0.7284 | -129.5422 | -1.947 | 5.2919 | 1.3635 | -4.1329 | -2.5291 | 3.6614 |  | 2.1522 | -0.2337 | 4.0107 | 3.3639 | 3.3478 | 1.0565 | 10.7174 | 14.2254 | 14.7871 | 11.0475 | 0 | -0.0027 | 0.0009 | 0.0039 | 0.0004 | -0.0008 | 0.0003 | -0.0044 | -0.0164 | -360.1034 | 17.4069 | -360.485 | 17.721 | -360.8081 | 18.0906 | -360.8112 | 17.5178 | -352.6229 | 18.7189 | -352.709 | 16.8176
12:17 | 3430 | 36.6485 | 200.2617 | 447.3279 | 451.8765 | -17.2685 | -43.0283 | 9.4536 | 6.1888 | 0.4239 | -1.2163 | 1.7906 | -1.7329 | 10.139 | 3.222 | 0.6083 | 0.6475 | 0.9565 | 0.728 | -129.6068 | -1.9523 | 5.2548 | 1.4285 | -4.0936 | -2.539 | 3.6048 |  | 2.146 | -0.3553 | 4.0116 | 3.3645 | 3.3481 | 1.0574 | 10.7245 | 14.1973 | 14.7969 | 11.0324 | -0.0003 | -0.0027 | 0.0004 | 0.004 | 0.0005 | -0.0012 | -0.0019 | 0.0042 | -0.0219 | -360.1158 | 17.3884 | -360.4296 | 17.7108 | -360.8174 | 18.1235 | -360.9004 | 17.5363 | -352.629 | 18.6922 | -352.6321 | 16.7991
12:17 | 3431 | 36.6817 | 200.3244 | 447.3245 | 451.8734 | -17.2278 | -43.0228 | 9.4972 | 6.1218 | 0.4353 | -1.2399 | 1.7772 | -1.6957 | 10.1707 | 3.2365 | 0.6083 | 0.65 | 0.9563 | 0.7276 | -129.6048 | -1.9965 | 5.2453 | 1.4298 | -4.0532 | -2.5239 | 3.6963 |  | 2.1409 | -0.3731 | 4.0094 | 3.3637 | 3.349 | 1.0553 | 10.7382 | 14.2001 | 14.797 | 11.045 | -0.0004 | -0.0029 | 0.0007 | 0.0035 | 0.0007 | -0.0002 | 0 | -0.005 | -0.0037 | -360.2327 | 17.4254 | -360.4727 | 17.7026 | -360.805 | 18.1214 | -360.9004 | 17.5896 | -352.7306 | 18.7353 | -352.6813 | 16.7889
12:17 | 3432 | 36.7114 | 200.3004 | 447.3994 | 451.8376 | -17.1901 | -43.0242 | 9.5877 | 6.2346 | 0.5098 | -1.1895 | 1.8362 | -1.6857 | 10.1538 | 3.106 | 0.606 | 0.6508 | 0.9573 | 0.7274 | -129.6226 | -2.0524 | 5.205 | 1.4167 | -4.0383 | -2.6057 | 3.6605 |  | 2.1111 | -0.3833 | 4.0099 | 3.3629 | 3.3464 | 1.0573 | 10.7255 | 14.2278 | 14.7957 | 11.0612 | 0.0001 | -0.0031 | 0.001 | 0.0041 | 0.0012 | -0.0007 | 0.0017 | -0.0077 | -0.0262 | -360.1773 | 17.4397 | -360.5096 | 17.7272 | -360.8481 | 18.0988 | -360.8266 | 17.5506 | -352.6752 | 18.7497 | -352.7398 | 16.8176
12:17 | 3433 | 36.7834 | 200.2713 | 447.377 | 451.8542 | -17.2169 | -42.9855 | 9.5683 | 6.3055 | 0.4902 | -1.2029 | 1.82 | -1.776 | 10.1323 | 2.9876 | 0.608 | 0.6523 | 0.9615 | 0.7291 | -129.5993 | -2.0431 | 5.2522 | 1.4717 | -4.0721 | -2.4846 | 3.7527 |  | 2.0944 | -0.3311 | 4.0112 | 3.3656 | 3.3466 | 1.0574 | 10.7706 | 14.2499 | 14.8359 | 11.0771 | -0.0005 | -0.0032 | 0.0011 | 0.0043 | 0.0007 | -0.0004 | 0.0293 | -0.0105 | 0.0012 | -360.1065 | 17.3699 | -360.4266 | 17.7046 | -360.7927 | 18.1153 | -360.8543 | 17.526 | -352.589 | 18.6799 | -352.6383 | 16.8074
12:17 | 3434 | 36.7413 | 200.2436 | 447.3565 | 451.8544 | -17.2016 | -43.0116 | 9.4655 | 6.3409 | 0.5075 | -1.1459 | 1.9095 | -1.745 | 10.1454 | 3.0605 | 0.6077 | 0.6517 | 0.9595 | 0.7297 | -129.524 | -1.9769 | 5.2435 | 1.4384 | -4.0332 | -2.4231 | 3.8079 |  | 2.1861 | -0.3448 | 4.0108 | 3.3668 | 3.3487 | 1.0575 | 10.7543 | 14.2631 | 14.8346 | 11.0771 | -0.0001 | -0.0026 | 0.0002 | 0.004 | 0.001 | -0.0004 | 0.0065 | -0.0106 | -0.0152 | -360.1988 | 17.4069 | -360.4173 | 17.6697 | -360.7866 | 18.1071 | -360.885 | 17.5814 | -352.7244 | 18.6984 | -352.6537 | 16.7724
12:17 | 3435 | 36.8072 | 200.3637 | 447.4514 | 451.9894 | -17.3552 | -43.1471 | 9.3357 | 6.3333 | 0.5462 | -1.1867 | 1.92 | -1.8379 | 10.0963 | 3.0614 | 0.6064 | 0.6542 | 0.9594 | 0.73 | -129.4881 | -1.982 | 5.2855 | 1.4585 | -3.9286 | -2.4315 | 3.8528 |  | 2.1377 | -0.4538 | 4.0108 | 3.3664 | 3.3459 | 1.0561 | 10.7625 | 14.2591 | 14.81 | 11.0749 | -0.0004 | -0.0032 | 0.0001 | 0.0034 | 0.0004 | -0.0005 | 0.0093 | 0.0037 | -0.0053 | -360.2019 | 17.448 | -360.5312 | 17.7252 | -360.8389 | 18.0968 | -360.8697 | 17.565 | -352.6998 | 18.7456 | -352.7244 | 16.8156
12:17 | 3436 | 36.7813 | 200.2969 | 447.3414 | 451.9297 | -17.3725 | -43.2063 | 9.4629 | 6.3254 | 0.5293 | -1.2028 | 1.8096 | -1.7465 | 10.2237 | 3.0511 | 0.6064 | 0.6535 | 0.9597 | 0.731 | -129.5581 | -1.9933 | 5.2735 | 1.4591 | -3.9935 | -2.5889 | 3.7808 |  | 2.1338 | -0.4833 | 4.0106 | 3.3612 | 3.3472 | 1.0568 | 10.7624 | 14.2478 | 14.8063 | 11.0453 | 0.0002 | -0.0032 | 0.0006 | 0.0042 | 0.0011 | -0.0002 | 0.0034 | -0.0004 | -0.0015 | -360.1188 | 17.3946 | -360.4696 | 17.7354 | -360.8327 | 18.1358 | -360.8789 | 17.5383 | -352.6475 | 18.7045 | -352.6783 | 16.8299
12:17 | 3437 | 36.8271 | 200.3628 | 447.3825 | 451.9638 | -17.3189 | -43.1716 | 9.467 | 6.4233 | 0.5245 | -1.0778 | 1.7039 | -1.8138 | 10.1988 | 3.0445 | 0.6089 | 0.6524 | 0.9604 | 0.7308 | -129.57 | -1.9606 | 5.3316 | 1.4718 | -4.063 | -2.5675 | 3.6912 |  | 2.1733 | -0.431 | 4.011 | 3.3661 | 3.351 | 1.0575 | 10.7441 | 14.2289 | 14.7902 | 11.0569 | 0 | -0.0032 | 0.0005 | 0.0037 | 0.0005 | -0.0004 | 0.0039 | -0.0083 | 0.0061 | -360.1619 | 17.3699 | -360.3742 | 17.6656 | -360.7927 | 18.1235 | -360.8666 | 17.5588 | -352.6444 | 18.6737 | -352.589 | 16.7683
12:17 | 3438 | 36.8313 | 200.2821 | 447.372 | 451.9557 | -17.2774 | -43.0856 | 9.5248 | 6.381 | 0.5875 | -1.1049 | 1.7807 | -1.9154 | 10.1517 | 3.1089 | 0.6067 | 0.6506 | 0.9628 | 0.7299 | -129.5593 | -2.0135 | 5.274 | 1.5603 | -4.0567 | -2.4522 | 3.7614 |  | 2.1165 | -0.3695 | 4.0104 | 3.3654 | 3.3482 | 1.0565 | 10.7164 | 14.2182 | 14.7894 | 11.0356 | -0.0003 | -0.0029 | 0.0006 | 0.0041 | 0.0008 | -0.0004 | 0.0134 | 0.0072 | -0.016 | -360.2111 | 17.4356 | -360.4973 | 17.7067 | -360.7897 | 18.1029 | -360.8881 | 17.5671 | -352.666 | 18.721 | -352.6783 | 16.7991
12:17 | 3439 | 36.8302 | 200.3746 | 447.4349 | 451.9567 | -17.2921 | -43.1995 | 9.5001 | 6.3776 | 0.4742 | -1.1594 | 1.7637 | -1.802 | 10.1029 | 3.1786 | 0.607 | 0.6494 | 0.9597 | 0.7275 | -129.6292 | -2.0928 | 5.1276 | 1.4749 | -4.0317 | -2.501 | 3.7203 |  | 2.1837 | -0.3098 | 4.0123 | 3.3636 | 3.3472 | 1.0551 | 10.7381 | 14.2584 | 14.7886 | 11.067 | -0.0001 | -0.0026 | 0.0011 | 0.004 | 0.0013 | -0.0002 | 0.0059 | -0.007 | -0.0172 | -360.1804 | 17.4172 | -360.5127 | 17.7642 | -360.885 | 18.1317 | -360.8697 | 17.5486 | -352.6567 | 18.7169 | -352.7337 | 16.8505
12:17 | 3440 | 36.9194 | 200.437 | 447.511 | 452.0677 | -17.2701 | -43.2651 | 9.4088 | 6.3559 | 0.5017 | -1.1048 | 1.7557 | -1.861 | 10.1103 | 3.146 | 0.6089 | 0.6516 | 0.9593 | 0.731 | -129.6457 | -2.0489 | 5.2153 | 1.3891 | -4.0581 | -2.515 | 3.7629 |  | 2.1366 | -0.4062 | 4.0119 | 3.3661 | 3.3477 | 1.0565 | 10.751 | 14.23 | 14.8031 | 11.0349 | 0.0003 | -0.0031 | 0.0008 | 0.0034 | 0.0003 | -0.0007 | 0.0197 | 0.0003 | -0.002 | -360.1373 | 17.372 | -360.3989 | 17.7046 | -360.8081 | 18.1296 | -360.9158 | 17.5609 | -352.6198 | 18.6717 | -352.6383 | 16.7991
12:17 | 3441 | 36.8514 | 200.3707 | 447.3986 | 451.9898 | -17.2586 | -43.3257 | 9.4062 | 6.3948 | 0.4909 | -1.0691 | 1.7299 | -1.7679 | 10.1253 | 3.156 | 0.6084 | 0.6501 | 0.958 | 0.7285 | -129.5855 | -1.9926 | 5.3657 | 1.3331 | -4.052 | -2.4553 | 3.7775 |  | 2.1942 | -0.3658 | 4.0104 | 3.3659 | 3.3497 | 1.057 | 10.7266 | 14.2407 | 14.7749 | 11.0446 | 0.0002 | -0.0029 | 0.0009 | 0.004 | 0.0013 | -0.0005 | -0.0002 | -0.0093 | 0.0097 | -360.1835 | 17.4131 | -360.4419 | 17.6861 | -360.7589 | 18.0865 | -360.8266 | 17.5527 | -352.669 | 18.7148 | -352.6352 | 16.7868
12:17 | 3442 | 36.8791 | 200.4467 | 447.4615 | 452.0381 | -17.2306 | -43.317 | 9.4166 | 6.3744 | 0.539 | -1.1787 | 1.6718 | -1.8052 | 10.1488 | 3.1427 | 0.6074 | 0.6478 | 0.9566 | 0.7294 | -129.5485 | -2.004 | 5.2716 | 1.3975 | -4.0303 | -2.4837 | 3.7508 |  | 2.1533 | -0.3847 | 4.0112 | 3.3684 | 3.3519 | 1.0572 | 10.7347 | 14.2431 | 14.8356 | 11.0468 | -0.0004 | -0.0027 | 0.0011 | 0.0038 | 0.0004 | -0.0003 | -0.0031 | -0.0183 | -0.0269 | -360.1404 | 17.4233 | -360.5189 | 17.7621 | -360.882 | 18.1194 | -360.8574 | 17.5301 | -352.6475 | 18.721 | -352.7521 | 16.8423
12:17 | 3443 | 36.864 | 200.4034 | 447.5202 | 452.0319 | -17.317 | -43.2786 | 9.2832 | 6.4057 | 0.6319 | -1.1501 | 1.745 | -1.8587 | 10.1364 | 3.1352 | 0.6057 | 0.6484 | 0.9591 | 0.7289 | -129.5397 | -1.963 | 5.259 | 1.3654 | -3.9854 | -2.5019 | 3.7596 |  | 2.1766 | -0.3727 | 4.0108 | 3.3642 | 3.346 | 1.0553 | 10.781 | 14.2662 | 14.8471 | 11.0699 | -0.0001 | -0.0026 | 0.0003 | 0.0037 | 0.0007 | -0.0007 | 0.0175 | -0.011 | -0.0106 | -360.1127 | 17.3946 | -360.4758 | 17.7313 | -360.842 | 18.1481 | -360.9035 | 17.5424 | -352.6413 | 18.7025 | -352.669 | 16.834
12:17 | 3444 | 36.8854 | 200.3546 | 447.5515 | 452.0226 | -17.3453 | -43.3492 | 9.3567 | 6.294 | 0.4718 | -1.2817 | 1.6732 | -1.7791 | 10.195 | 3.1633 | 0.6081 | 0.6489 | 0.9573 | 0.729 | -129.5688 | -1.9456 | 5.3757 | 1.407 | -3.9913 | -2.4279 | 3.7483 |  | 2.1723 | -0.3905 | 4.0113 | 3.3656 | 3.3489 | 1.0565 | 10.7279 | 14.2243 | 14.7916 | 11.0522 | 0.0004 | -0.0029 | 0.0003 | 0.0037 | 0.0007 | -0.0004 | 0.0212 | 0.0041 | -0.0111 | -360.1527 | 17.4069 | -360.4112 | 17.6759 | -360.7373 | 18.0988 | -360.8635 | 17.5588 | -352.6721 | 18.7066 | -352.6567 | 16.7786
12:17 | 3445 | 36.8971 | 200.3736 | 447.4214 | 451.9806 | -17.3412 | -43.2422 | 9.2733 | 6.2198 | 0.3044 | -1.3543 | 1.7009 | -1.8047 | 10.2106 | 3.2328 | 0.6072 | 0.6484 | 0.9599 | 0.7308 | -129.5066 | -1.9658 | 5.3979 | 1.428 | -3.9891 | -2.4549 | 3.7355 |  | 2.161 | -0.3602 | 4.0107 | 3.3658 | 3.3487 | 1.0577 | 10.7314 | 14.2392 | 14.8004 | 11.0616 | 0 | -0.0032 | 0.0007 | 0.0039 | 0.0011 | -0.0009 | 0.0099 | -0.0182 | 0.0002 | -360.1958 | 17.4356 | -360.5127 | 17.7313 | -360.8358 | 18.0927 | -360.8143 | 17.5404 | -352.6598 | 18.7251 | -352.7275 | 16.8176
12:17 | 3446 | 36.87 | 200.3482 | 447.5286 | 451.9878 | -17.3017 | -43.2112 | 9.2971 | 6.2531 | 0.3706 | -1.3389 | 1.7394 | -1.7878 | 10.2527 | 3.2099 | 0.6077 | 0.6478 | 0.9604 | 0.7305 | -129.6267 | -1.9921 | 5.3465 | 1.406 | -4.0222 | -2.5645 | 3.7904 |  | 2.2131 | -0.3739 | 4.012 | 3.3675 | 3.3493 | 1.058 | 10.7117 | 14.2311 | 14.7803 | 11.0306 | 0 | -0.0027 | 0.0008 | 0.0039 | 0.0007 | 0 | 0.0182 | -0.006 | -0.0134 | -360.1558 | 17.4151 | -360.4942 | 17.7395 | -360.8512 | 18.144 | -360.8666 | 17.5506 | -352.6567 | 18.7004 | -352.6967 | 16.8402
12:17 | 3447 | 36.873 | 200.3728 | 447.4684 | 451.9546 | -17.3082 | -43.2315 | 9.2469 | 6.2839 | 0.3185 | -1.113 | 1.799 | -1.7549 | 10.2092 | 3.1567 | 0.6066 | 0.6505 | 0.9579 | 0.7295 | -129.5527 | -2.0244 | 5.3424 | 1.4538 | -3.9128 | -2.4923 | 3.8412 |  | 2.2432 | -0.4319 | 4.011 | 3.3645 | 3.3475 | 1.0561 | 10.7429 | 14.2278 | 14.7841 | 11.0266 | -0.0003 | -0.0028 | 0.0013 | 0.0039 | 0.0007 | -0.0009 | 0.0007 | 0.0006 | -0.0172 | -360.1988 | 17.3925 | -360.405 | 17.6779 | -360.7835 | 18.1071 | -360.8912 | 17.5712 | -352.6752 | 18.6963 | -352.6229 | 16.7909
12:17 | 3448 | 36.9465 | 200.4853 | 447.4397 | 452.0106 | -17.3338 | -43.2497 | 9.2596 | 6.2968 | 0.4012 | -1.2102 | 1.7853 | -1.6943 | 10.2418 | 3.2009 | 0.6069 | 0.6483 | 0.9591 | 0.7279 | -129.5953 | -1.9418 | 5.2402 | 1.4222 | -3.9623 | -2.4659 | 3.8048 |  | 2.2012 | -0.4413 | 4.013 | 3.3649 | 3.3488 | 1.0572 | 10.7439 | 14.2524 | 14.8223 | 11.0847 | 0.0005 | -0.0022 | 0.0007 | 0.0037 | 0.0003 | -0.0005 | 0.0151 | -0.0074 | -0.0114 | -360.2296 | 17.4274 | -360.4758 | 17.6902 | -360.7804 | 18.0804 | -360.8174 | 17.5465 | -352.669 | 18.7251 | -352.6783 | 16.7991
12:17 | 3449 | 36.8774 | 200.4087 | 447.3951 | 452.0147 | -17.2631 | -43.1732 | 9.353 | 6.2453 | 0.3404 | -1.2609 | 1.8138 | -1.7003 | 10.1928 | 3.1251 | 0.6083 | 0.6507 | 0.9614 | 0.7298 | -129.5627 | -1.897 | 5.2407 | 1.467 | -3.9335 | -2.3822 | 3.8587 |  | 2.1903 | -0.4202 | 4.011 | 3.3669 | 3.349 | 1.0556 | 10.7267 | 14.2348 | 14.797 | 11.0161 | 0.0001 | -0.003 | 0.0011 | 0.0043 | 0.0004 | -0.0006 | 0.0076 | -0.0016 | -0.0045 | -360.1527 | 17.4295 | -360.4789 | 17.7539 | -360.885 | 18.1358 | -360.8789 | 17.5547 | -352.6598 | 18.7087 | -352.6813 | 16.834
12:17 | 3450 | 36.9184 | 200.4039 | 447.4438 | 451.9252 | -17.2804 | -43.2671 | 9.1964 | 6.2689 | 0.397 | -1.1529 | 1.8911 | -1.7357 | 10.2709 | 3.12 | 0.6082 | 0.6519 | 0.9605 | 0.7297 | -129.6107 | -1.9166 | 5.1838 | 1.3847 | -3.9573 | -2.3224 | 3.8125 |  | 2.2203 | -0.3917 | 4.0109 | 3.3665 | 3.35 | 1.057 | 10.774 | 14.271 | 14.87 | 11.0915 | -0.0001 | -0.0028 | 0.0008 | 0.0039 | 0.0009 | -0.0005 | 0.0132 | -0.0224 | -0.0163 | -360.1742 | 17.3864 | -360.4389 | 17.7067 | -360.8174 | 18.142 | -360.9312 | 17.5794 | -352.6906 | 18.6984 | -352.6475 | 16.7971
12:17 | 3451 | 36.8639 | 200.32 | 447.4791 | 452.0216 | -17.3122 | -43.3404 | 9.2181 | 6.2998 | 0.4811 | -1.0485 | 1.8917 | -1.7101 | 10.249 | 3.0977 | 0.6086 | 0.6499 | 0.96 | 0.7284 | -129.6288 | -1.977 | 5.2066 | 1.5107 | -3.8784 | -2.301 | 3.8306 |  | 2.236 | -0.3247 | 4.0109 | 3.3641 | 3.3522 | 1.0576 | 10.744 | 14.2581 | 14.8039 | 11.0966 | -0.0002 | -0.0026 | 0.0006 | 0.0036 | 0.0004 | -0.0003 | 0.0118 | 0.0046 | -0.0298 | -360.2081 | 17.3925 | -360.4173 | 17.6759 | -360.7466 | 18.0988 | -360.8635 | 17.5609 | -352.6506 | 18.7045 | -352.629 | 16.7745
12:17 | 3452 | 36.8471 | 200.3514 | 447.4537 | 451.9824 | -17.3471 | -43.4401 | 9.2293 | 6.2401 | 0.41 | -1.1447 | 1.8425 | -1.8367 | 10.2839 | 3.1118 | 0.6071 | 0.6477 | 0.9577 | 0.7298 | -129.6535 | -1.9068 | 5.1299 | 1.3853 | -3.9665 | -2.3812 | 3.8092 |  | 2.2327 | -0.3464 | 4.0105 | 3.3635 | 3.3432 | 1.0576 | 10.7245 | 14.2493 | 14.7911 | 11.0613 | -0.0003 | -0.0029 | 0.0002 | 0.0036 | 0.0004 | -0.001 | 0.0249 | -0.001 | -0.007 | -360.1711 | 17.4233 | -360.5096 | 17.7252 | -360.8481 | 18.1029 | -360.845 | 17.5301 | -352.629 | 18.721 | -352.6937 | 16.8135
12:17 | 3453 | 36.9226 | 200.4146 | 447.4793 | 451.9304 | -17.4295 | -43.4234 | 9.1694 | 6.2212 | 0.5203 | -1.0823 | 1.8164 | -1.6989 | 10.2617 | 3.156 | 0.6079 | 0.652 | 0.9616 | 0.7311 | -129.5574 | -1.8729 | 5.2087 | 1.4178 | -3.9563 | -2.3959 | 3.8154 |  | 2.2986 | -0.3842 | 4.01 | 3.3637 | 3.3477 | 1.0569 | 10.714 | 14.2219 | 14.8062 | 11.0385 | 0.0001 | -0.0032 | 0.0009 | 0.0038 | 0.0006 | -0.0002 | 0.0059 | -0.0131 | -0.0187 | -360.125 | 17.3987 | -360.4912 | 17.7272 | -360.882 | 18.1502 | -360.8974 | 17.5609 | -352.6413 | 18.6922 | -352.706 | 16.8299
12:17 | 3454 | 36.9086 | 200.4274 | 447.4285 | 451.9863 | -17.3604 | -43.327 | 9.2545 | 6.222 | 0.6394 | -1.1144 | 1.7942 | -1.6171 | 10.3059 | 3.2285 | 0.6084 | 0.6535 | 0.9611 | 0.7311 | -129.5973 | -1.8832 | 5.2017 | 1.4023 | -3.9697 | -2.3803 | 3.797 |  | 2.2907 | -0.3508 | 4.0106 | 3.3657 | 3.3454 | 1.0552 | 10.7142 | 14.2099 | 14.8088 | 11.0396 | -0.0006 | -0.0035 | 0.0008 | 0.0039 | 0.0011 | -0.0006 | 0.0134 | -0.0152 | -0.022 | -360.1742 | 17.3761 | -360.4204 | 17.6697 | -360.7897 | 18.1317 | -360.8727 | 17.5609 | -352.6721 | 18.684 | -352.626 | 16.8012
12:17 | 3455 | 36.8639 | 200.5628 | 447.5579 | 452.1046 | -17.352 | -43.3468 | 9.2155 | 6.187 | 0.6659 | -1.1446 | 1.7996 | -1.6663 | 10.3495 | 3.0892 | 0.6073 | 0.6496 | 0.9625 | 0.7303 | -129.6928 | -1.9338 | 5.1849 | 1.3217 | -3.9843 | -2.4239 | 3.7424 |  | 2.2721 | -0.4558 | 4.011 | 3.3663 | 3.3465 | 1.0563 | 10.7278 | 14.2244 | 14.8158 | 11.0576 | -0.0003 | -0.0029 | 0.0009 | 0.0038 | 0.0006 | -0.0005 | 0.001 | 0.0038 | -0.0176 | -360.1496 | 17.4131 | -360.4696 | 17.6738 | -360.7527 | 18.0906 | -360.8297 | 17.5527 | -352.6506 | 18.7128 | -352.666 | 16.793
12:17 | 3456 | 36.9235 | 200.4808 | 447.4573 | 452.0841 | -17.3372 | -43.3249 | 9.2059 | 6.1888 | 0.7048 | -1.2243 | 1.8082 | -1.7186 | 10.3492 | 3.0815 | 0.6092 | 0.6515 | 0.9602 | 0.7301 | -129.5662 | -1.9352 | 5.2711 | 1.2213 | -3.9513 | -2.3937 | 3.7715 |  | 2.2233 | -0.4793 | 4.0109 | 3.3645 | 3.3445 | 1.0564 | 10.7658 | 14.2805 | 14.8057 | 11.0886 | 0.0003 | -0.0025 | 0.0015 | 0.0041 | 0.0009 | -0.0007 | 0.017 | -0.0044 | -0.0136 | -360.1527 | 17.4192 | -360.5066 | 17.7375 | -360.8727 | 18.1296 | -360.8635 | 17.5424 | -352.6475 | 18.7189 | -352.7244 | 16.8443
12:17 | 3457 | 36.8761 | 200.4228 | 447.4631 | 452.12 | -17.2636 | -43.1316 | 9.2732 | 6.2819 | 0.619 | -1.1532 | 1.8274 | -1.7886 | 10.3548 | 3.0704 | 0.6083 | 0.6477 | 0.9547 | 0.7292 | -129.5727 | -1.8934 | 5.2699 | 1.2632 | -3.9763 | -2.4111 | 3.8134 |  | 2.2594 | -0.3735 | 4.0107 | 3.3668 | 3.3496 | 1.0564 | 10.7822 | 14.2499 | 14.8243 | 11.106 | 0.0001 | -0.0034 | 0.0007 | 0.0036 | 0.0005 | -0.0005 | 0.0144 | -0.0026 | -0.0126 | -360.1619 | 17.3905 | -360.4696 | 17.7108 | -360.845 | 18.1461 | -360.882 | 17.5506 | -352.669 | 18.6984 | -352.6752 | 16.834
12:17 | 3458 | 36.9079 | 200.4195 | 447.4796 | 452.1853 | -17.36 | -43.1677 | 9.1742 | 6.2529 | 0.5836 | -1.1012 | 1.8279 | -1.7833 | 10.2919 | 3.0094 | 0.6086 | 0.651 | 0.9582 | 0.7293 | -129.6592 | -1.9194 | 5.1518 | 1.336 | -4.0237 | -2.441 | 3.7338 |  | 2.3045 | -0.3149 | 4.0102 | 3.3659 | 3.3483 | 1.0582 | 10.7704 | 14.2736 | 14.8459 | 11.0756 | 0.0002 | -0.0026 | 0.0011 | 0.004 | 0.0012 | -0.0001 | 0.0137 | -0.0077 | 0.0058 | -360.1619 | 17.3946 | -360.4173 | 17.6574 | -360.762 | 18.1029 | -360.885 | 17.5609 | -352.6352 | 18.6963 | -352.6352 | 16.7766
12:17 | 3459 | 37.0068 | 200.4671 | 447.4745 | 452.1656 | -17.387 | -43.2032 | 9.2084 | 6.2448 | 0.5257 | -1.2419 | 2.0137 | -1.8952 | 10.2261 | 2.9492 | 0.6084 | 0.6466 | 0.9574 | 0.7305 | -129.6376 | -1.9559 | 5.209 | 1.419 | -3.952 | -2.3889 | 3.8554 |  | 2.2454 | -0.3207 | 4.0083 | 3.3641 | 3.3437 | 1.0573 | 10.7902 | 14.2931 | 14.8523 | 11.1247 | -0.0005 | -0.0028 | 0 | 0.0036 | 0.0006 | -0.0004 | 0.0333 | -0.0062 | -0.0119 | -360.1896 | 17.448 | -360.5158 | 17.7128 | -360.8327 | 18.0886 | -360.845 | 17.5506 | -352.6752 | 18.7374 | -352.7244 | 16.8156
12:17 | 3460 | 36.9638 | 200.3871 | 447.3888 | 452.1449 | -17.328 | -43.2741 | 9.308 | 6.2583 | 0.5972 | -1.0769 | 2.0368 | -1.8159 | 10.2859 | 3.0113 | 0.6085 | 0.649 | 0.9577 | 0.7294 | -129.6218 | -1.9582 | 5.1945 | 1.49 | -3.9426 | -2.3866 | 3.8171 |  | 2.2235 | -0.3459 | 4.0095 | 3.3644 | 3.3463 | 1.0577 | 10.7359 | 14.2499 | 14.8301 | 11.054 | -0.0001 | -0.0027 | 0.0006 | 0.0039 | 0.0006 | -0.0005 | 0.0242 | -0.0131 | 0.0035 | -360.1681 | 17.4131 | -360.5066 | 17.7272 | -360.882 | 18.1173 | -360.8697 | 17.5486 | -352.6506 | 18.7128 | -352.709 | 16.8464
12:17 | 3461 | 36.9431 | 200.3583 | 447.3997 | 452.2049 | -17.346 | -43.2195 | 9.279 | 6.1728 | 0.5716 | -1.1158 | 2.0017 | -1.7768 | 10.2925 | 3.0849 | 0.6084 | 0.6487 | 0.9584 | 0.73 | -129.6593 | -1.9803 | 5.2093 | 1.4809 | -4.0248 | -2.3553 | 3.7969 |  | 2.261 | -0.352 | 4.0098 | 3.3684 | 3.3437 | 1.0571 | 10.6943 | 14.2254 | 14.7929 | 11.0417 | 0.0001 | -0.0032 | 0.0008 | 0.004 | 0.0007 | -0.0005 | 0.0176 | -0.0082 | -0.0092 | -360.1373 | 17.374 | -360.3773 | 17.6759 | -360.7835 | 18.0968 | -360.8543 | 17.5588 | -352.6506 | 18.6696 | -352.6136 | 16.795
12:17 | 3462 | 36.9281 | 200.4123 | 447.5018 | 452.2522 | -17.3706 | -43.218 | 9.2148 | 6.2146 | 0.6241 | -1.1589 | 2.0325 | -1.7648 | 10.2649 | 3.0336 | 0.6092 | 0.6518 | 0.9597 | 0.7281 | -129.6179 | -1.913 | 5.2669 | 1.4881 | -4.0336 | -2.4208 | 3.8062 |  | 2.1776 | -0.4436 | 4.0091 | 3.369 | 3.3452 | 1.0575 | 10.7222 | 14.2413 | 14.8126 | 11.0819 | 0.0001 | -0.003 | 0.0003 | 0.0036 | 0.0003 | -0.0008 | 0.0194 | 0.0026 | -0.0039 | -360.2111 | 17.4254 | -360.4604 | 17.6656 | -360.802 | 18.0845 | -360.8758 | 17.5753 | -352.706 | 18.7169 | -352.6567 | 16.7868
12:17 | 3463 | 36.9872 | 200.4743 | 447.5899 | 452.3131 | -17.4219 | -43.2176 | 9.209 | 6.2058 | 0.5679 | -1.2866 | 1.9561 | -1.7878 | 10.2636 | 3.0474 | 0.6088 | 0.6479 | 0.9588 | 0.7275 | -129.6857 | -1.8686 | 5.276 | 1.5539 | -3.9349 | -2.3447 | 3.8583 |  | 2.26 | -0.3654 | 4.0101 | 3.3649 | 3.3482 | 1.0576 | 10.7117 | 14.2253 | 14.7919 | 11.019 | -0.0002 | -0.0027 | 0.0009 | 0.0041 | 0.0015 | -0.0006 | -0.0001 | -0.015 | -0.0104 | -360.205 | 17.4356 | -360.5066 | 17.7128 | -360.8512 | 18.1029 | -360.8512 | 17.5609 | -352.6937 | 18.7312 | -352.7152 | 16.832
12:17 | 3464 | 36.9537 | 200.4232 | 447.5309 | 452.2702 | -17.4636 | -43.2118 | 9.1768 | 6.2878 | 0.5634 | -1.3136 | 2.0655 | -1.777 | 10.2126 | 3.0827 | 0.6097 | 0.6524 | 0.9615 | 0.7281 | -129.7066 | -1.8312 | 5.227 | 1.3958 | -3.9217 | -2.3391 | 3.8751 |  | 2.2923 | -0.3486 | 4.0117 | 3.3706 | 3.3483 | 1.0564 | 10.7359 | 14.2499 | 14.8185 | 11.0424 | -0.0002 | -0.0028 | 0.001 | 0.0038 | 0.0011 | 0.0002 | 0.0126 | -0.0049 | -0.0297 | -360.1373 | 17.374 | -360.4419 | 17.7026 | -360.8204 | 18.1214 | -360.885 | 17.5321 | -352.626 | 18.6861 | -352.6567 | 16.8074
12:17 | 3465 | 36.9288 | 200.3985 | 447.5156 | 452.3117 | -17.4234 | -43.2987 | 9.2484 | 6.1611 | 0.5865 | -1.3748 | 1.994 | -1.6987 | 10.2641 | 3.1174 | 0.6092 | 0.6545 | 0.9602 | 0.7271 | -129.7141 | -1.8725 | 5.246 | 1.3654 | -3.9578 | -2.3404 | 3.8961 |  | 2.2304 | -0.3526 | 4.0097 | 3.3666 | 3.3441 | 1.0575 | 10.7671 | 14.2638 | 14.8386 | 11.0966 | 0.0001 | -0.0028 | 0.0008 | 0.0036 | 0.001 | -0.0009 | 0.0162 | -0.0074 | -0.0143 | -360.1896 | 17.3864 | -360.3958 | 17.6553 | -360.7958 | 18.1029 | -360.9066 | 17.5691 | -352.6352 | 18.6779 | -352.5952 | 16.7704
12:17 | 3466 | 36.9547 | 200.4265 | 447.4128 | 452.2372 | -17.4143 | -43.2211 | 9.3502 | 6.1934 | 0.6059 | -1.372 | 1.973 | -1.7567 | 10.2798 | 3.0806 | 0.6091 | 0.6515 | 0.9608 | 0.7286 | -129.727 | -1.8894 | 5.2379 | 1.4253 | -3.9182 | -2.3746 | 3.9138 |  | 2.2134 | -0.3038 | 4.0097 | 3.3643 | 3.3444 | 1.0577 | 10.7301 | 14.2674 | 14.8369 | 11.0941 | 0.0005 | -0.003 | 0.0009 | 0.0038 | 0.0006 | -0.0004 | 0.0079 | -0.0148 | -0.019 | -360.2265 | 17.4315 | -360.4758 | 17.6964 | -360.8204 | 18.1009 | -360.8912 | 17.5753 | -352.669 | 18.7271 | -352.7121 | 16.8094
12:17 | 3467 | 36.9591 | 200.4478 | 447.4584 | 452.2711 | -17.4023 | -43.2795 | 9.4467 | 6.2545 | 0.7035 | -1.3293 | 1.9241 | -1.8234 | 10.2539 | 3.0586 | 0.6081 | 0.6493 | 0.9589 | 0.7272 | -129.7227 | -1.9454 | 5.2021 | 1.328 | -3.9286 | -2.3604 | 3.9417 |  | 2.2066 | -0.3814 | 4.0104 | 3.3696 | 3.3455 | 1.0589 | 10.7601 | 14.2572 | 14.851 | 11.0601 | 0.0002 | -0.0024 | 0.0003 | 0.0034 | 0.0009 | -0.0006 | 0.0029 | 0.0018 | -0.0088 | -360.1804 | 17.4131 | -360.4912 | 17.7354 | -360.8881 | 18.1112 | -360.8635 | 17.5445 | -352.6444 | 18.721 | -352.7306 | 16.8525
12:18 | 3468 | 36.9855 | 200.4354 | 447.5202 | 452.2842 | -17.3681 | -43.2623 | 9.3771 | 6.0962 | 0.6088 | -1.4086 | 1.8212 | -1.7668 | 10.2086 | 3.0739 | 0.6086 | 0.6516 | 0.9599 | 0.7266 | -129.6625 | -1.8671 | 5.1688 | 1.249 | -3.9372 | -2.57 | 3.815 |  | 2.2146 | -0.4269 | 4.0112 | 3.3674 | 3.3424 | 1.0568 | 10.7221 | 14.2357 | 14.8079 | 11.0699 | -0.0003 | -0.0027 | 0.0006 | 0.0036 | 0.0005 | -0.0004 | -0.0032 | -0.0049 | -0.0055 | -360.0881 | 17.3638 | -360.4081 | 17.682 | -360.802 | 18.1235 | -360.9035 | 17.5486 | -352.6198 | 18.6696 | -352.6475 | 16.8032
12:18 | 3469 | 36.9344 | 200.3943 | 447.5224 | 452.2459 | -17.4458 | -43.2733 | 9.3709 | 6.1523 | 0.6682 | -1.3478 | 1.919 | -1.8056 | 10.2075 | 3.0202 | 0.608 | 0.6505 | 0.955 | 0.7275 | -129.625 | -1.8618 | 5.276 | 1.0996 | -3.9485 | -2.3932 | 3.8142 |  | 2.1833 | -0.4782 | 4.01 | 3.3672 | 3.346 | 1.0578 | 10.7128 | 14.2441 | 14.778 | 11.0482 | 0.0001 | -0.0027 | 0.001 | 0.0042 | 0.0005 | -0.0007 | -0.0021 | -0.0053 | -0.0062 | -360.2081 | 17.4069 | -360.4573 | 17.6841 | -360.762 | 18.0824 | -360.8574 | 17.5691 | -352.6444 | 18.7045 | -352.6506 | 16.7889
12:18 | 3470 | 36.9035 | 200.3627 | 447.477 | 452.2414 | -17.3657 | -43.2053 | 9.4121 | 6.2098 | 0.7892 | -1.2242 | 1.9611 | -1.8204 | 10.2368 | 3.0024 | 0.6087 | 0.6499 | 0.9577 | 0.7291 | -129.6886 | -1.8931 | 5.2614 | 1.1288 | -3.9286 | -2.3975 | 3.7764 |  | 2.1464 | -0.4827 | 4.0095 | 3.3669 | 3.3439 | 1.0582 | 10.737 | 14.2511 | 14.8257 | 11.084 | 0.0005 | -0.0026 | 0.0009 | 0.0039 | 0.0008 | -0.0006 | 0.0101 | -0.0153 | -0.0172 | -360.1927 | 17.4336 | -360.5343 | 17.7375 | -360.8574 | 18.1009 | -360.8543 | 17.5445 | -352.669 | 18.7333 | -352.7183 | 16.8402
12:18 | 3471 | 36.9826 | 200.3156 | 447.5177 | 452.2734 | -17.3562 | -43.1719 | 9.5633 | 6.2234 | 0.7878 | -1.2394 | 1.9878 | -1.6619 | 10.2384 | 3.1357 | 0.61 | 0.6517 | 0.962 | 0.7288 | -129.6083 | -1.8416 | 5.3005 | 1.2407 | -3.9814 | -2.317 | 3.823 |  | 2.2278 | -0.3808 | 4.0104 | 3.3685 | 3.3468 | 1.0589 | 10.7463 | 14.2604 | 14.8298 | 11.0699 | -0.0001 | -0.0028 | 0.001 | 0.0039 | 0.0006 | -0.0002 | 0.0174 | 0.0005 | -0.0183 | -360.1311 | 17.3905 | -360.4758 | 17.7169 | -360.8635 | 18.1214 | -360.8789 | 17.5404 | -352.6537 | 18.7004 | -352.6937 | 16.834
12:18 | 3472 | 36.9622 | 200.3393 | 447.4727 | 452.3257 | -17.3045 | -43.1935 | 9.4623 | 6.2209 | 0.7584 | -1.2894 | 1.8315 | -1.737 | 10.2365 | 3.1546 | 0.6086 | 0.649 | 0.9589 | 0.7289 | -129.5384 | -1.8284 | 5.3067 | 1.2572 | -4.0064 | -2.3923 | 3.9288 |  | 2.2147 | -0.445 | 4.0098 | 3.3672 | 3.3476 | 1.0583 | 10.7451 | 14.2592 | 14.8226 | 11.0688 | -0.0004 | -0.0026 | 0.0011 | 0.0039 | 0.001 | -0.0007 | 0.0145 | -0.0057 | -0.0128 | -360.1619 | 17.374 | -360.4112 | 17.6718 | -360.762 | 18.0988 | -360.8697 | 17.5609 | -352.6537 | 18.6758 | -352.6075 | 16.7848
12:18 | 3473 | 36.9633 | 200.4213 | 447.4751 | 452.3694 | -17.3284 | -43.1288 | 9.4574 | 6.236 | 0.5249 | -1.4033 | 1.7744 | -1.8401 | 10.209 | 3.0978 | 0.6076 | 0.6499 | 0.9594 | 0.7287 | -129.5521 | -1.778 | 5.3411 | 1.217 | -3.944 | -2.5892 | 3.8518 |  | 2.1468 | -0.4319 | 4.0112 | 3.3671 | 3.3452 | 1.0584 | 10.7221 | 14.2588 | 14.7963 | 11.0584 | -0.0002 | -0.0031 | 0.0002 | 0.0034 | 0.0007 | -0.0001 | 0.0061 | 0.0108 | -0.0135 | -360.2142 | 17.4295 | -360.4973 | 17.7005 | -360.8112 | 18.0701 | -360.8697 | 17.5568 | -352.6752 | 18.721 | -352.6937 | 16.7971
12:18 | 3474 | 37.082 | 200.3883 | 447.5151 | 452.382 | -17.389 | -43.2181 | 9.3731 | 6.189 | 0.3958 | -1.2927 | 1.8598 | -1.7528 | 10.2309 | 3.1692 | 0.6069 | 0.6501 | 0.9594 | 0.7286 | -129.6272 | -1.833 | 5.2699 | 1.2936 | -3.9074 | -2.4785 | 3.8259 |  | 2.3633 | -0.3228 | 4.0114 | 3.3672 | 3.3466 | 1.0584 | 10.7626 | 14.2416 | 14.8263 | 11.0638 | -0.0002 | -0.0033 | 0.0007 | 0.0035 | 0.0012 | -0.0005 | 0.0107 | -0.0065 | -0.0075 | -360.2142 | 17.4315 | -360.5558 | 17.7395 | -360.8789 | 18.1112 | -360.845 | 17.5527 | -352.669 | 18.7189 | -352.7429 | 16.8402
12:18 | 3475 | 37.0177 | 200.3991 | 447.4302 | 452.3509 | -17.3765 | -43.1813 | 9.3779 | 6.2056 | 0.3671 | -1.2108 | 1.8672 | -1.7536 | 10.3007 | 3.1804 | 0.6064 | 0.6481 | 0.9589 | 0.7292 | -129.6338 | -1.8678 | 5.1367 | 1.4902 | -3.8899 | -2.4395 | 3.8008 |  | 2.2498 | -0.3657 | 4.0108 | 3.3637 | 3.3453 | 1.0581 | 10.7429 | 14.2509 | 14.8072 | 11.0555 | -0.0002 | -0.003 | 0.0007 | 0.0039 | 0.0007 | -0.0001 | 0.0198 | 0.0036 | -0.0211 | -360.1619 | 17.3946 | -360.4327 | 17.6944 | -360.845 | 18.1317 | -360.9066 | 17.5773 | -352.6721 | 18.6779 | -352.6537 | 16.8156
12:18 | 3476 | 37.0441 | 200.3999 | 447.4497 | 452.2712 | -17.3925 | -43.1892 | 9.4084 | 6.2031 | 0.4052 | -1.1993 | 1.81 | -1.7119 | 10.2434 | 3.1164 | 0.6083 | 0.6496 | 0.961 | 0.7305 | -129.6358 | -1.9668 | 5.149 | 1.5669 | -3.9498 | -2.5307 | 3.8091 |  | 2.3114 | -0.3891 | 4.0099 | 3.3663 | 3.3432 | 1.0578 | 10.7417 | 14.2555 | 14.8232 | 11.0717 | -0.0007 | -0.0029 | 0.0008 | 0.0043 | 0.0011 | -0.0003 | 0.0222 | -0.0108 | 0.0129 | -360.1711 | 17.4007 | -360.4173 | 17.6738 | -360.7404 | 18.0721 | -360.8543 | 17.5609 | -352.6967 | 18.7066 | -352.6629 | 16.7868
12:18 | 3477 | 37.0972 | 200.4691 | 447.4575 | 452.3392 | -17.4125 | -43.2097 | 9.3582 | 6.1394 | 0.4156 | -1.2732 | 1.7681 | -1.7763 | 10.2913 | 3.1619 | 0.6093 | 0.6493 | 0.9611 | 0.7297 | -129.6097 | -1.9119 | 5.3104 | 1.5173 | -3.8912 | -2.4641 | 3.8104 |  | 2.1718 | -0.2528 | 4.0089 | 3.3669 | 3.3432 | 1.0576 | 10.7185 | 14.2327 | 14.7964 | 11.071 | -0.0003 | -0.0026 | 0.0012 | 0.0042 | 0.0009 | 0 | 0.0184 | -0.0004 | 0.0049 | -360.1804 | 17.411 | -360.4881 | 17.7087 | -360.8081 | 18.0824 | -360.8081 | 17.5404 | -352.6198 | 18.7128 | -352.6998 | 16.8176
12:18 | 3478 | 37.0412 | 200.466 | 447.3861 | 452.3657 | -17.4201 | -43.1684 | 9.3272 | 6.1862 | 0.465 | -1.3176 | 1.8514 | -1.6652 | 10.2552 | 3.1277 | 0.6084 | 0.65 | 0.9632 | 0.7278 | -129.5968 | -1.899 | 5.2837 | 1.4888 | -3.8627 | -2.3377 | 3.8256 |  | 2.2221 | -0.3809 | 4.01 | 3.3621 | 3.3434 | 1.058 | 10.7683 | 14.2649 | 14.8505 | 11.0807 | 0 | -0.0035 | 0.001 | 0.0039 | 0.0007 | -0.0004 | 0.008 | 0.0039 | -0.0225 | -360.165 | 17.4069 | -360.4819 | 17.7272 | -360.8512 | 18.1379 | -360.9189 | 17.5527 | -352.6321 | 18.7004 | -352.706 | 16.834
12:18 | 3479 | 37.0433 | 200.4376 | 447.5206 | 452.2946 | -17.3961 | -43.0857 | 9.43 | 6.2636 | 0.562 | -1.2703 | 1.7691 | -1.7394 | 10.2261 | 3.1269 | 0.6076 | 0.65 | 0.9607 | 0.7299 | -129.6115 | -1.9014 | 5.2101 | 1.4611 | -3.8833 | -2.3454 | 3.7812 |  | 2.1995 | -0.3773 | 4.0108 | 3.3673 | 3.3466 | 1.0578 | 10.7405 | 14.2661 | 14.8056 | 11.024 | -0.0003 | -0.003 | 0.0009 | 0.004 | 0.0006 | -0.0003 | 0.0233 | -0.0155 | -0.0068 | -360.2111 | 17.3966 | -360.4481 | 17.6882 | -360.8174 | 18.1153 | -360.9343 | 17.5937 | -352.7121 | 18.6963 | -352.6506 | 16.8053
12:18 | 3480 | 37.1422 | 200.4644 | 447.5257 | 452.3952 | -17.2838 | -43.1114 | 9.5607 | 6.2766 | 0.5747 | -1.2931 | 1.8342 | -1.7282 | 10.1417 | 3.1587 | 0.6094 | 0.65 | 0.9602 | 0.7297 | -129.6194 | -1.9488 | 5.2593 | 1.4637 | -4.0097 | -2.4095 | 3.817 |  | 2.2302 | -0.4364 | 4.01 | 3.3638 | 3.3444 | 1.0574 | 10.7404 | 14.2779 | 14.8656 | 11.0753 | -0.0004 | -0.0032 | 0.0008 | 0.0038 | 0.0006 | -0.0007 | 0.0221 | -0.006 | 0.0144 | -360.1435 | 17.4213 | -360.4481 | 17.6738 | -360.7804 | 18.0968 | -360.8543 | 17.5527 | -352.6783 | 18.7128 | -352.6967 | 16.8074
12:18 | 3481 | 37.1223 | 200.3931 | 447.5022 | 452.4072 | -17.3437 | -43.0584 | 9.5383 | 6.3968 | 0.5806 | -1.2904 | 1.9373 | -1.7357 | 10.1927 | 3.1416 | 0.6068 | 0.6493 | 0.9593 | 0.7281 | -129.5066 | -1.9184 | 5.3334 | 1.4809 | -3.9237 | -2.3245 | 3.804 |  | 2.3315 | -0.3387 | 4.0111 | 3.3637 | 3.3464 | 1.0585 | 10.7383 | 14.252 | 14.8596 | 11.08 | 0 | -0.0029 | 0.0002 | 0.0032 | 0.001 | -0.0004 | 0.0152 | -0.0063 | -0.0111 | -360.1311 | 17.3925 | -360.4635 | 17.7046 | -360.7958 | 18.0906 | -360.845 | 17.5321 | -352.5736 | 18.6902 | -352.6598 | 16.834
12:18 | 3482 | 37.0718 | 200.4617 | 447.6386 | 452.3489 | -17.3354 | -43.0708 | 9.4567 | 6.3403 | 0.6562 | -1.2412 | 1.9013 | -1.7507 | 10.2397 | 3.0861 | 0.6071 | 0.644 | 0.9582 | 0.728 | -129.5415 | -1.8753 | 5.2881 | 1.6143 | -3.9701 | -2.3512 | 3.8227 |  | 2.2883 | -0.3968 | 4.0092 | 3.3651 | 3.3469 | 1.0574 | 10.7624 | 14.2652 | 14.8642 | 11.08 | 0.0003 | -0.0028 | 0.0011 | 0.004 | 0.0006 | -0.0005 | 0.0117 | 0.0047 | -0.009 | -360.1619 | 17.3925 | -360.4266 | 17.7005 | -360.842 | 18.1194 | -360.8943 | 17.5547 | -352.6413 | 18.6737 | -352.6106 | 16.8074
12:18 | 3483 | 37.0709 | 200.3957 | 447.4618 | 452.3564 | -17.2404 | -43.166 | 9.436 | 6.3196 | 0.5651 | -1.1922 | 1.8987 | -1.7512 | 10.2643 | 3.0577 | 0.6084 | 0.6456 | 0.9593 | 0.7281 | -129.4557 | -1.7921 | 5.312 | 1.6331 | -3.9776 | -2.3218 | 3.8679 |  | 2.2199 | -0.3281 | 4.0106 | 3.3631 | 3.3459 | 1.0598 | 10.7498 | 14.2521 | 14.826 | 11.0739 | 0.0002 | -0.003 | 0.0005 | 0.0042 | 0.001 | -0.0005 | 0.0205 | -0.0002 | -0.0195 | -360.2327 | 17.4377 | -360.5004 | 17.7005 | -360.8143 | 18.105 | -360.8912 | 17.5794 | -352.6813 | 18.721 | -352.6813 | 16.8197
12:18 | 3484 | 37.092 | 200.4478 | 447.5221 | 452.3951 | -17.1885 | -43.1063 | 9.5437 | 6.3612 | 0.6781 | -1.1721 | 1.9097 | -1.6911 | 10.3433 | 3.1916 | 0.6099 | 0.6492 | 0.9619 | 0.7279 | -129.4641 | -1.8188 | 5.3056 | 1.553 | -3.9716 | -2.2522 | 3.8527 |  | 2.2654 | -0.2471 | 4.0122 | 3.3635 | 3.3463 | 1.0598 | 10.7441 | 14.2346 | 14.8018 | 11.0511 | -0.0002 | -0.0027 | 0.0008 | 0.0042 | 0.0007 | 0 | 0.0067 | 0.0003 | -0.0011 | -360.1804 | 17.4131 | -360.5035 | 17.7334 | -360.8512 | 18.1071 | -360.8666 | 17.5506 | -352.6721 | 18.721 | -352.7244 | 16.8484
12:18 | 3485 | 37.0727 | 200.3978 | 447.5418 | 452.371 | -17.3244 | -43.2029 | 9.4884 | 6.3137 | 0.699 | -1.1719 | 1.8332 | -1.7222 | 10.3216 | 3.1703 | 0.6086 | 0.6497 | 0.9612 | 0.7303 | -129.5256 | -1.7469 | 5.3859 | 1.4335 | -3.9557 | -2.2948 | 3.8616 |  | 2.2359 | -0.4056 | 4.011 | 3.3669 | 3.3447 | 1.0594 | 10.7463 | 14.2373 | 14.8124 | 11.0468 | -0.0002 | -0.0025 | 0.0011 | 0.0042 | 0.0011 | -0.0005 | 0.0025 | 0.0013 | 0.0021 | -360.1681 | 17.3761 | -360.4266 | 17.7046 | -360.8204 | 18.1009 | -360.8881 | 17.5527 | -352.6475 | 18.6779 | -352.6475 | 16.8217
12:18 | 3486 | 37.1193 | 200.5206 | 447.4782 | 452.3591 | -17.3304 | -43.093 | 9.4902 | 6.3204 | 0.7302 | -1.0581 | 1.9522 | -1.6924 | 10.3451 | 3.2568 | 0.6085 | 0.6499 | 0.9581 | 0.7305 | -129.5568 | -1.8894 | 5.3535 | 1.4261 | -4.077 | -2.2971 | 3.8714 |  | 2.3353 | -0.3241 | 4.0104 | 3.3608 | 3.3474 | 1.0582 | 10.7267 | 14.2348 | 14.8144 | 11.0565 | 0.0001 | -0.003 | 0.0005 | 0.0036 | 0.0007 | 0 | -0.0089 | -0.0063 | -0.0258 | -360.1588 | 17.411 | -360.4204 | 17.6759 | -360.7589 | 18.0721 | -360.8327 | 17.5547 | -352.6413 | 18.7004 | -352.6413 | 16.793
12:18 | 3487 | 37.074 | 200.3834 | 447.5739 | 452.3638 | -17.2609 | -43.1394 | 9.5143 | 6.3113 | 0.7678 | -1.1459 | 1.9429 | -1.6254 | 10.2726 | 3.1323 | 0.6092 | 0.6536 | 0.96 | 0.7295 | -129.5281 | -1.829 | 5.3496 | 1.503 | -4.0198 | -2.3255 | 3.8348 |  | 2.2305 | -0.3011 | 4.0103 | 3.3648 | 3.3483 | 1.059 | 10.7545 | 14.2394 | 14.8015 | 11.0612 | 0.0005 | -0.0029 | 0.001 | 0.0039 | 0.0012 | -0.0006 | 0.0054 | -0.0145 | -0.0163 | -360.1527 | 17.411 | -360.4942 | 17.7108 | -360.8327 | 18.105 | -360.8543 | 17.5465 | -352.6229 | 18.7066 | -352.6721 | 16.8238
12:18 | 3488 | 37.167 | 200.5176 | 447.5071 | 452.4441 | -17.2448 | -43.2519 | 9.5119 | 6.3133 | 0.7185 | -1.0656 | 1.9387 | -1.7215 | 10.3443 | 3.1621 | 0.6074 | 0.65 | 0.9622 | 0.7304 | -129.5378 | -1.7003 | 5.3719 | 1.5193 | -3.969 | -2.316 | 3.8486 |  | 2.2238 | -0.3396 | 4.0111 | 3.3648 | 3.3445 | 1.0592 | 10.7199 | 14.2157 | 14.7972 | 11.0627 | -0.0003 | -0.0027 | 0.0005 | 0.0034 | 0.0003 | -0.0007 | 0.0137 | -0.012 | 0.002 | -360.1742 | 17.4172 | -360.4666 | 17.721 | -360.8543 | 18.1358 | -360.9158 | 17.5773 | -352.6844 | 18.7066 | -352.6813 | 16.8443
12:18 | 3489 | 37.057 | 200.4822 | 447.4247 | 452.4456 | -17.2507 | -43.2806 | 9.4331 | 6.4184 | 0.7825 | -1.0909 | 1.91 | -1.8378 | 10.3055 | 3.0847 | 0.6076 | 0.6502 | 0.9597 | 0.7304 | -129.5073 | -1.8115 | 5.3787 | 1.5321 | -3.97 | -2.3169 | 3.8075 |  | 2.1542 | -0.3114 | 4.0109 | 3.3639 | 3.3426 | 1.0585 | 10.7278 | 14.2649 | 14.8158 | 11.0865 | 0 | -0.0023 | -0.0002 | 0.0028 | 0.0005 | -0.0006 | 0.0129 | -0.0178 | 0.0038 | -360.2019 | 17.4048 | -360.4389 | 17.6964 | -360.7927 | 18.1071 | -360.882 | 17.5629 | -352.6537 | 18.7087 | -352.6844 | 16.8094
12:18 | 3490 | 37.0705 | 200.3976 | 447.5137 | 452.3426 | -17.249 | -43.2394 | 9.4768 | 6.4471 | 0.7234 | -1.2209 | 1.9163 | -1.7281 | 10.2557 | 3.1119 | 0.6059 | 0.6554 | 0.9627 | 0.7307 | -129.5206 | -1.747 | 5.4399 | 1.5171 | -3.9493 | -2.2537 | 3.857 |  | 2.2139 | -0.2181 | 4.0112 | 3.362 | 3.3456 | 1.0575 | 10.7232 | 14.2254 | 14.8219 | 11.0475 | 0.0001 | -0.003 | 0.0007 | 0.0043 | 0.0007 | -0.0014 | 0.011 | -0.0134 | 0.0008 | -360.1711 | 17.4028 | -360.4696 | 17.6985 | -360.7558 | 18.0886 | -360.8512 | 17.5445 | -352.6198 | 18.7004 | -352.6598 | 16.8115
12:18 | 3491 | 37.0922 | 200.4354 | 447.4678 | 452.399 | -17.3016 | -43.1617 | 9.4273 | 6.4606 | 0.7504 | -1.0077 | 1.8649 | -1.7111 | 10.1895 | 3.0836 | 0.6069 | 0.6478 | 0.9618 | 0.7309 | -129.5687 | -1.8524 | 5.406 | 1.4877 | -4.0552 | -2.3363 | 3.8165 |  | 2.1548 | -0.2535 | 4.0112 | 3.3619 | 3.344 | 1.057 | 10.7394 | 14.2244 | 14.8216 | 11.0692 | 0.0004 | -0.0026 | 0.0007 | 0.0041 | 0.0006 | -0.0002 | 0.0082 | -0.0137 | -0.002 | -360.1342 | 17.3966 | -360.4635 | 17.7087 | -360.8081 | 18.0988 | -360.8543 | 17.5486 | -352.6198 | 18.7004 | -352.669 | 16.8094
12:18 | 3492 | 37.1951 | 200.4835 | 447.5718 | 452.469 | -17.3185 | -43.1363 | 9.4326 | 6.5193 | 0.7745 | -1.023 | 1.9039 | -1.6704 | 10.2684 | 3.1098 | 0.607 | 0.6512 | 0.9605 | 0.7311 | -129.5061 | -1.8395 | 5.4422 | 1.4568 | -3.9818 | -2.3533 | 3.8094 |  | 2.3163 | -0.2065 | 4.0111 | 3.3621 | 3.3445 | 1.0573 | 10.7451 | 14.2592 | 14.8284 | 11.0688 | 0.0002 | -0.0027 | 0.0006 | 0.004 | 0.0011 | -0.0003 | 0.0001 | -0.0064 | -0.0103 | -360.2481 | 17.4151 | -360.4942 | 17.719 | -360.8358 | 18.1194 | -360.9404 | 17.5712 | -352.6506 | 18.7169 | -352.666 | 16.8258
12:18 | 3493 | 37.1524 | 200.4531 | 447.5894 | 452.3921 | -17.3428 | -43.2346 | 9.3838 | 6.5188 | 0.7222 | -0.8891 | 1.9221 | -1.6891 | 10.3229 | 3.1269 | 0.608 | 0.6504 | 0.9605 | 0.7316 | -129.5218 | -1.9432 | 5.458 | 1.5271 | -3.8826 | -2.3341 | 3.8572 |  | 2.2729 | -0.3482 | 4.0118 | 3.363 | 3.3452 | 1.0584 | 10.7348 | 14.2312 | 14.8045 | 11.088 | -0.0004 | -0.0025 | 0.0004 | 0.0036 | 0.0006 | -0.0003 | 0.0048 | -0.0062 | -0.003 | -360.2111 | 17.411 | -360.4912 | 17.7128 | -360.8358 | 18.0988 | -360.8974 | 17.5732 | -352.666 | 18.7189 | -352.7152 | 16.8299
12:18 | 3494 | 37.1507 | 200.5292 | 447.5377 | 452.4277 | -17.1634 | -42.9325 | 9.4403 | 6.4567 | 0.632 | -0.9631 | 1.9151 | -1.7187 | 10.3324 | 3.1743 | 0.6076 | 0.6518 | 0.9614 | 0.7308 | -129.5001 | -1.8675 | 5.4488 | 1.594 | -3.8136 | -2.3765 | 3.9688 |  | 2.2587 | -0.3289 | 4.0105 | 3.3666 | 3.3473 | 1.0597 | 10.7382 | 14.2523 | 14.8444 | 11.085 | 0 | -0.0029 | 0.0006 | 0.0035 | 0.0008 | -0.0008 | -0.0028 | -0.0171 | -0.0292 | -360.0973 | 17.4007 | -360.445 | 17.6985 | -360.7989 | 18.0906 | -360.8297 | 17.5342 | -352.6321 | 18.7025 | -352.669 | 16.8074
12:18 | 3495 | 37.2209 | 200.5093 | 447.5772 | 452.4727 | -17.2422 | -42.9483 | 9.5017 | 6.4668 | 0.5387 | -0.9362 | 1.943 | -1.6656 | 10.2889 | 3.148 | 0.6085 | 0.6503 | 0.9595 | 0.73 | -129.4625 | -1.8529 | 5.4906 | 1.4265 | -3.7979 | -2.4766 | 3.9484 |  | 2.2402 | -0.3547 | 4.0099 | 3.3607 | 3.3461 | 1.0599 | 10.7141 | 14.2332 | 14.7867 | 11.0624 | 0.0001 | -0.0033 | 0.0005 | 0.0034 | 0.0003 | -0.0003 | 0.0227 | 0.0063 | 0.0068 | -360.1527 | 17.3884 | -360.4542 | 17.6964 | -360.7558 | 18.0906 | -360.8481 | 17.5486 | -352.629 | 18.6861 | -352.6321 | 16.793
12:18 | 3496 | 37.1602 | 200.5587 | 447.5345 | 452.4541 | -17.3056 | -43.0095 | 9.5146 | 6.4139 | 0.4464 | -1.0107 | 1.8425 | -1.6171 | 10.3324 | 3.1893 | 0.6092 | 0.653 | 0.9622 | 0.7311 | -129.5163 | -1.9593 | 5.3685 | 1.3636 | -3.7838 | -2.2218 | 4.0972 |  | 2.2566 | -0.3865 | 4.0094 | 3.3604 | 3.3463 | 1.0604 | 10.7187 | 14.2148 | 14.8095 | 11.0551 | -0.0002 | -0.0029 | 0.0011 | 0.0041 | 0.0012 | -0.0008 | 0.0147 | -0.0071 | 0.0017 | -360.2111 | 17.4233 | -360.4789 | 17.7026 | -360.8358 | 18.0968 | -360.8635 | 17.5588 | -352.6537 | 18.7045 | -352.6629 | 16.8135
12:18 | 3497 | 37.0999 | 200.4193 | 447.5246 | 452.4279 | -17.2665 | -42.9741 | 9.6088 | 6.4088 | 0.4234 | -0.9462 | 1.9644 | -1.7921 | 10.3047 | 3.1317 | 0.6103 | 0.65 | 0.9619 | 0.7311 | -129.4644 | -1.848 | 5.3753 | 1.3847 | -3.7254 | -2.2917 | 4.0106 |  | 2.2997 | -0.2877 | 4.0103 | 3.3644 | 3.3463 | 1.0597 | 10.7338 | 14.2413 | 14.801 | 11.0819 | -0.0005 | -0.0026 | 0.0008 | 0.0039 | 0.0006 | -0.0003 | 0.0229 | -0.0013 | 0.0155 | -360.1927 | 17.4233 | -360.5158 | 17.7272 | -360.842 | 18.1173 | -360.8789 | 17.565 | -352.6875 | 18.7333 | -352.7121 | 16.8279
12:18 | 3498 | 37.0856 | 200.444 | 447.4609 | 452.441 | -17.2802 | -42.9646 | 9.5639 | 6.4389 | 0.4012 | -0.9009 | 1.9317 | -1.6823 | 10.2631 | 3.0693 | 0.6085 | 0.6486 | 0.9593 | 0.7301 | -129.5857 | -1.879 | 5.2922 | 1.4306 | -3.7405 | -2.2134 | 3.9854 |  | 2.2321 | -0.1904 | 4.0109 | 3.3647 | 3.346 | 1.0595 | 10.7371 | 14.2394 | 14.8362 | 11.067 | -0.0002 | -0.0029 | 0.001 | 0.0042 | 0.0012 | -0.0002 | 0.0137 | -0.0148 | -0.0046 | -360.1158 | 17.4007 | -360.4758 | 17.7067 | -360.8143 | 18.1029 | -360.9004 | 17.5609 | -352.6444 | 18.6984 | -352.6998 | 16.8258
12:18 | 3499 | 37.1183 | 200.5572 | 447.5693 | 452.4596 | -17.2098 | -42.9757 | 9.6687 | 6.3672 | 0.3961 | -0.9764 | 1.8855 | -1.7479 | 10.2876 | 3.1169 | 0.6083 | 0.6488 | 0.959 | 0.7292 | -129.5696 | -1.963 | 5.2481 | 1.4965 | -3.7356 | -2.2739 | 4.0439 |  | 2.2633 | -0.275 | 4.0109 | 3.3656 | 3.3434 | 1.0582 | 10.7324 | 14.2524 | 14.857 | 11.102 | 0.0002 | -0.003 | 0.0004 | 0.004 | 0.0006 | 0.0001 | 0.0254 | -0.0092 | -0.0058 | -360.1496 | 17.3884 | -360.4235 | 17.6944 | -360.765 | 18.0947 | -360.8604 | 17.5465 | -352.6198 | 18.6943 | -352.6075 | 16.7868
12:18 | 3500 | 37.0931 | 200.6182 | 447.5198 | 452.5114 | -17.149 | -42.951 | 9.7244 | 6.3485 | 0.4941 | -0.9673 | 1.9199 | -1.729 | 10.2689 | 3.1882 | 0.6094 | 0.6539 | 0.9598 | 0.7319 | -129.5632 | -1.8039 | 5.333 | 1.4681 | -3.7714 | -2.1691 | 4.0123 |  | 2.2681 | -0.2613 | 4.0122 | 3.3657 | 3.3481 | 1.0595 | 10.7429 | 14.2452 | 14.8246 | 11.1017 | 0 | -0.0032 | 0.0003 | 0.0035 | 0.0006 | -0.0007 | 0.0189 | -0.0106 | -0.0015 | -360.1619 | 17.4069 | -360.4881 | 17.7087 | -360.7773 | 18.0988 | -360.8604 | 17.5568 | -352.6136 | 18.7025 | -352.669 | 16.8074
12:18 | 3501 | 37.1038 | 200.5474 | 447.5191 | 452.4654 | -17.1801 | -42.9297 | 9.7444 | 6.4617 | 0.4205 | -0.87 | 1.8749 | -1.7491 | 10.2722 | 3.0592 | 0.6087 | 0.6524 | 0.961 | 0.7314 | -129.5847 | -1.7967 | 5.376 | 1.4991 | -3.8325 | -2.2762 | 3.9759 |  | 2.2642 | -0.2425 | 4.011 | 3.365 | 3.3458 | 1.0599 | 10.7659 | 14.2572 | 14.8799 | 11.089 | -0.0002 | -0.0025 | 0.001 | 0.0042 | 0.0008 | -0.0002 | 0.0246 | -0.0074 | -0.0117 | -360.2019 | 17.4192 | -360.4942 | 17.7313 | -360.8574 | 18.1235 | -360.8758 | 17.5712 | -352.6752 | 18.7271 | -352.6783 | 16.8279
12:18 | 3502 | 37.1118 | 200.5049 | 447.5491 | 452.4301 | -17.1588 | -43.0782 | 9.7228 | 6.4277 | 0.3945 | -1.0652 | 1.79 | -1.659 | 10.3673 | 3.1026 | 0.6095 | 0.6557 | 0.9617 | 0.7318 | -129.5894 | -1.7785 | 5.4484 | 1.5008 | -3.8365 | -2.2612 | 3.916 |  | 2.3266 | -0.3081 | 4.0095 | 3.3638 | 3.3478 | 1.0594 | 10.737 | 14.2337 | 14.8025 | 11.0666 | -0.0004 | -0.0028 | 0.0006 | 0.0034 | 0.0009 | -0.0003 | 0.0095 | -0.0181 | -0.0247 | -360.1958 | 17.4028 | -360.4696 | 17.7026 | -360.8266 | 18.1132 | -360.9004 | 17.565 | -352.6629 | 18.7087 | -352.6752 | 16.8156
12:18 | 3503 | 37.2126 | 200.5874 | 447.6391 | 452.384 | -17.2164 | -42.9919 | 9.7782 | 6.393 | 0.3866 | -1.0697 | 1.8119 | -1.7349 | 10.3671 | 3.1213 | 0.6087 | 0.6526 | 0.9595 | 0.7296 | -129.6743 | -1.7507 | 5.4506 | 1.5186 | -3.8207 | -2.4331 | 3.9308 |  | 2.2943 | -0.2138 | 4.0105 | 3.3655 | 3.3475 | 1.0586 | 10.7856 | 14.2594 | 14.8932 | 11.0857 | 0 | -0.0031 | 0.001 | 0.004 | 0.0011 | -0.0005 | 0.0151 | -0.0094 | 0.0111 | -360.1681 | 17.3925 | -360.4204 | 17.682 | -360.7866 | 18.0824 | -360.8174 | 17.5465 | -352.629 | 18.7025 | -352.6352 | 16.8053
12:18 | 3504 | 37.2003 | 200.5807 | 447.6446 | 452.5132 | -17.1147 | -42.8799 | 9.8298 | 6.4569 | 0.4731 | -1.0501 | 1.8968 | -1.7139 | 10.3404 | 3.1647 | 0.6103 | 0.6539 | 0.9623 | 0.7302 | -129.6176 | -1.7324 | 5.3789 | 1.541 | -3.8599 | -2.2657 | 3.9089 |  | 2.2151 | -0.3374 | 4.0099 | 3.3626 | 3.3426 | 1.0583 | 10.7082 | 14.2452 | 14.8072 | 11.0555 | 0.0003 | -0.0028 | 0.0011 | 0.0038 | 0.0001 | -0.0005 | 0.0046 | -0.0128 | -0.0159 | -360.1619 | 17.4048 | -360.4604 | 17.6861 | -360.8081 | 18.0968 | -360.8358 | 17.5383 | -352.6136 | 18.7004 | -352.6721 | 16.8053
12:18 | 3505 | 37.1499 | 200.5019 | 447.502 | 452.4521 | -17.2304 | -42.8718 | 9.7769 | 6.4557 | 0.5228 | -1.1023 | 1.9249 | -1.6726 | 10.2894 | 3.0313 | 0.6091 | 0.6536 | 0.9639 | 0.731 | -129.6616 | -1.8711 | 5.4775 | 1.613 | -3.787 | -2.3259 | 3.974 |  | 2.3287 | -0.3623 | 4.01 | 3.3635 | 3.3457 | 1.0583 | 10.7475 | 14.2557 | 14.8127 | 11.0367 | -0.0004 | -0.0025 | 0.0009 | 0.0039 | 0.0011 | -0.0007 | 0.004 | -0.0091 | -0.0211 | -360.1865 | 17.4172 | -360.4789 | 17.7005 | -360.8389 | 18.1173 | -360.885 | 17.5753 | -352.6537 | 18.7148 | -352.6844 | 16.8176
12:18 | 3506 | 37.2052 | 200.5289 | 447.6137 | 452.4511 | -17.148 | -42.8974 | 9.8671 | 6.4394 | 0.5229 | -1.0762 | 1.8389 | -1.7974 | 10.2165 | 3.0587 | 0.6081 | 0.6509 | 0.963 | 0.7315 | -129.6688 | -1.882 | 5.4031 | 1.5671 | -3.7821 | -2.2491 | 3.9806 |  | 2.2864 | -0.3656 | 4.0107 | 3.3643 | 3.3479 | 1.0594 | 10.7233 | 14.2195 | 14.7803 | 11.0479 | -0.0001 | -0.0029 | 0.0005 | 0.0039 | 0.0002 | -0.0005 | 0.0114 | -0.0032 | 0.0047 | -360.1958 | 17.411 | -360.4789 | 17.682 | -360.8389 | 18.1071 | -360.9035 | 17.5712 | -352.709 | 18.7292 | -352.6813 | 16.8156
12:18 | 3507 | 37.2147 | 200.4748 | 447.5245 | 452.5541 | -17.1612 | -42.8344 | 9.7834 | 6.391 | 0.5439 | -1.1364 | 1.8715 | -1.6933 | 10.2662 | 3.0928 | 0.6101 | 0.6481 | 0.9614 | 0.7298 | -129.6517 | -1.8831 | 5.3878 | 1.4477 | -3.823 | -2.386 | 3.8648 |  | 2.2529 | -0.3037 | 4.0106 | 3.3638 | 3.3465 | 1.0592 | 10.7 | 14.2256 | 14.7998 | 11.0356 | 0.0001 | -0.003 | 0.0007 | 0.0038 | 0.0009 | -0.0007 | 0.0161 | -0.0006 | 0.0053 | -360.125 | 17.3987 | -360.445 | 17.6636 | -360.7712 | 18.0865 | -360.8235 | 17.5342 | -352.6321 | 18.7025 | -352.6629 | 16.8094
12:18 | 3508 | 37.2409 | 200.5347 | 447.5726 | 452.5536 | -17.1059 | -42.7459 | 9.8139 | 6.353 | 0.5087 | -1.0903 | 2.0072 | -1.7713 | 10.2777 | 2.9913 | 0.6076 | 0.6495 | 0.9603 | 0.7302 | -129.6582 | -1.8047 | 5.3936 | 1.3969 | -3.8216 | -2.2989 | 3.9107 |  | 2.3301 | -0.2709 | 4.0107 | 3.3635 | 3.3493 | 1.0599 | 10.7624 | 14.2594 | 14.8526 | 11.0857 | 0.0002 | -0.0028 | 0.0005 | 0.0039 | 0.0006 | -0.0004 | 0.0235 | -0.0015 | 0.0044 | -360.1465 | 17.4028 | -360.4727 | 17.6718 | -360.8204 | 18.1091 | -360.8881 | 17.5588 | -352.6383 | 18.6943 | -352.666 | 16.8074
12:18 | 3509 | 37.1942 | 200.5279 | 447.5656 | 452.5499 | -17.0303 | -42.7333 | 9.8307 | 6.3233 | 0.526 | -1.0012 | 1.9554 | -1.7975 | 10.3043 | 3.0345 | 0.6075 | 0.6482 | 0.9628 | 0.7307 | -129.6564 | -1.869 | 5.4511 | 1.2844 | -3.8615 | -2.3768 | 3.851 |  | 2.3419 | -0.2795 | 4.0106 | 3.3637 | 3.3469 | 1.0593 | 10.7326 | 14.2112 | 14.7881 | 11.0519 | -0.0004 | -0.0031 | 0.0006 | 0.0037 | 0.0007 | -0.0004 | 0.0156 | -0.0088 | -0.0128 | -360.165 | 17.4233 | -360.5127 | 17.6759 | -360.8174 | 18.1235 | -360.8758 | 17.5691 | -352.706 | 18.7169 | -352.706 | 16.8238
12:18 | 3510 | 37.1273 | 200.5687 | 447.5956 | 452.4482 | -17.1251 | -42.7495 | 9.839 | 6.4218 | 0.5268 | -0.9241 | 2.0177 | -1.7496 | 10.325 | 3.0927 | 0.61 | 0.6517 | 0.9622 | 0.7297 | -129.6832 | -1.9201 | 5.3702 | 1.347 | -3.8279 | -2.3277 | 3.8864 |  | 2.3519 | -0.3173 | 4.0099 | 3.3617 | 3.342 | 1.0586 | 10.7624 | 14.2478 | 14.8642 | 11.0569 | -0.0004 | -0.0023 | 0.0004 | 0.0037 | 0.0007 | -0.0002 | 0.0049 | 0.0014 | -0.015 | -360.1988 | 17.4151 | -360.4942 | 17.6738 | -360.8174 | 18.1071 | -360.882 | 17.5588 | -352.6537 | 18.7251 | -352.7029 | 16.8299
12:18 | 3511 | 37.1534 | 200.48 | 447.5793 | 452.543 | -17.1694 | -42.8405 | 9.7308 | 6.4523 | 0.5742 | -1.0165 | 1.9624 | -1.7857 | 10.3499 | 3.1449 | 0.6094 | 0.6508 | 0.9616 | 0.7316 | -129.7248 | -1.9184 | 5.3902 | 1.416 | -3.8701 | -2.3068 | 3.9419 |  | 2.2841 | -0.4081 | 4.0103 | 3.3639 | 3.3432 | 1.0593 | 10.7578 | 14.2662 | 14.8356 | 11.0872 | 0 | -0.003 | 0.0008 | 0.0038 | 0.0003 | -0.0005 | 0.0235 | -0.0081 | -0.0123 | -360.1158 | 17.3782 | -360.4204 | 17.6697 | -360.7958 | 18.0947 | -360.8297 | 17.5445 | -352.6198 | 18.6799 | -352.6475 | 16.8176
12:18 | 3512 | 37.191 | 200.5348 | 447.5084 | 452.5344 | -17.1207 | -42.821 | 9.7044 | 6.4647 | 0.6334 | -0.7303 | 1.9712 | -1.7564 | 10.3369 | 3.136 | 0.6096 | 0.6511 | 0.9601 | 0.7318 | -129.6542 | -1.8883 | 5.3121 | 1.4122 | -3.8714 | -2.299 | 3.903 |  | 2.2977 | -0.4917 | 4.0099 | 3.3611 | 3.3441 | 1.0587 | 10.7337 | 14.2185 | 14.78 | 11.0638 | 0.0001 | -0.0031 | 0.0011 | 0.0042 | 0.0011 | -0.0004 | 0.0158 | -0.0187 | -0.0098 | -360.1804 | 17.4048 | -360.4481 | 17.643 | -360.7773 | 18.0968 | -360.8512 | 17.5547 | -352.6106 | 18.6922 | -352.6229 | 16.7868
12:18 | 3513 | 37.1725 | 200.5268 | 447.5603 | 452.5587 | -17.0914 | -42.8701 | 9.7279 | 6.4521 | 0.5896 | -0.9741 | 1.996 | -1.7176 | 10.354 | 3.1459 | 0.6102 | 0.6545 | 0.963 | 0.7333 | -129.6288 | -1.9324 | 5.352 | 1.445 | -3.8097 | -2.3044 | 3.909 |  | 2.2971 | -0.4307 | 4.0103 | 3.362 | 3.3436 | 1.0594 | 10.7439 | 14.2466 | 14.8107 | 11.0731 | 0.0005 | -0.0023 | 0.0008 | 0.0036 | 0.0006 | -0.0007 | 0.0173 | -0.0011 | -0.0082 | -360.1958 | 17.4213 | -360.4727 | 17.6861 | -360.8204 | 18.1091 | -360.842 | 17.5671 | -352.6413 | 18.7189 | -352.709 | 16.8156
12:18 | 3514 | 37.2263 | 200.546 | 447.6206 | 452.5483 | -17.1365 | -42.8766 | 9.7055 | 6.4685 | 0.6722 | -0.9592 | 2.013 | -1.7753 | 10.3286 | 3.1946 | 0.6084 | 0.649 | 0.9639 | 0.7307 | -129.7112 | -1.8271 | 5.4155 | 1.3929 | -3.7816 | -2.3661 | 3.9393 |  | 2.2277 | -0.4269 | 4.0116 | 3.3614 | 3.3474 | 1.0606 | 10.7371 | 14.2277 | 14.8293 | 11.0674 | -0.0005 | -0.0027 | 0.0004 | 0.0036 | 0.0011 | -0.0004 | 0.01 | 0.0023 | -0.0331 | -360.1465 | 17.4151 | -360.5035 | 17.7046 | -360.8789 | 18.1296 | -360.8697 | 17.565 | -352.6875 | 18.7189 | -352.706 | 16.8299
12:18 | 3515 | 37.1322 | 200.601 | 447.5461 | 452.5279 | -17.1561 | -42.8138 | 9.8095 | 6.4665 | 0.656 | -0.973 | 2.0181 | -1.7631 | 10.3529 | 3.2039 | 0.6099 | 0.6521 | 0.962 | 0.73 | -129.668 | -1.9026 | 5.3947 | 1.4635 | -3.8376 | -2.3002 | 3.9744 |  | 2.2202 | -0.4197 | 4.0094 | 3.3617 | 3.3463 | 1.0595 | 10.729 | 14.2372 | 14.8171 | 11.076 | 0.0001 | -0.0029 | 0.0009 | 0.0041 | 0.0006 | -0.0007 | 0.0116 | -0.0091 | -0.0093 | -360.1711 | 17.3925 | -360.445 | 17.6553 | -360.7589 | 18.1235 | -360.8912 | 17.5568 | -352.6598 | 18.7066 | -352.6598 | 16.8032
12:18 | 3516 | 37.1648 | 200.479 | 447.6017 | 452.5432 | -17.1766 | -42.8365 | 9.7187 | 6.483 | 0.7359 | -1.0159 | 1.9935 | -1.6806 | 10.3549 | 3.2319 | 0.609 | 0.6481 | 0.9595 | 0.7294 | -129.7199 | -1.8211 | 5.3623 | 1.4696 | -3.7295 | -2.4462 | 3.9072 |  | 2.1794 | -0.3764 | 4.0108 | 3.3624 | 3.347 | 1.0609 | 10.7232 | 14.2254 | 14.7929 | 11.0764 | 0 | -0.0032 | 0.0002 | 0.0033 | 0.0009 | -0.0007 | -0.0042 | -0.0107 | -0.0235 | -360.1588 | 17.3905 | -360.4358 | 17.6615 | -360.7712 | 18.0865 | -360.8266 | 17.5363 | -352.6413 | 18.6984 | -352.6475 | 16.795
12:18 | 3517 | 37.3192 | 200.4954 | 447.5775 | 452.6392 | -17.1641 | -42.7943 | 9.6813 | 6.5594 | 0.7884 | -0.973 | 1.9617 | -1.635 | 10.3802 | 3.2258 | 0.6099 | 0.6485 | 0.9609 | 0.7291 | -129.7394 | -1.8256 | 5.3017 | 1.5151 | -3.8483 | -2.3087 | 3.8785 |  | 2.2668 | -0.2819 | 4.0106 | 3.3612 | 3.3464 | 1.0602 | 10.759 | 14.2732 | 14.8369 | 11.0594 | -0.0005 | -0.0031 | 0.0007 | 0.004 | 0.0007 | -0.0002 | 0.007 | -0.0069 | 0.0022 | -360.165 | 17.409 | -360.4727 | 17.682 | -360.8389 | 18.1091 | -360.8604 | 17.5404 | -352.6106 | 18.7087 | -352.669 | 16.8135
12:18 | 3518 | 37.2763 | 200.5522 | 447.5249 | 452.5941 | -17.1981 | -42.8726 | 9.6856 | 6.5776 | 0.7771 | -1.0142 | 2.0908 | -1.6683 | 10.3887 | 3.1757 | 0.6093 | 0.6481 | 0.9609 | 0.7307 | -129.7266 | -1.8072 | 5.3239 | 1.5111 | -3.8318 | -2.3219 | 3.889 |  | 2.232 | -0.2477 | 4.0105 | 3.3626 | 3.3476 | 1.0583 | 10.7289 | 14.2373 | 14.8066 | 11.0699 | -0.0003 | -0.0024 | 0.001 | 0.0041 | 0.001 | -0.0007 | 0.0237 | -0.0052 | -0.0003 | -360.1742 | 17.4007 | -360.4696 | 17.682 | -360.8727 | 18.142 | -360.922 | 17.565 | -352.6598 | 18.7107 | -352.6721 | 16.8258
12:18 | 3519 | 37.2982 | 200.4897 | 447.5889 | 452.5498 | -17.1186 | -42.8279 | 9.7451 | 6.6086 | 0.869 | -0.9315 | 2.1772 | -1.7794 | 10.4133 | 3.1412 | 0.6104 | 0.6471 | 0.9623 | 0.7301 | -129.6467 | -1.7402 | 5.3927 | 1.4657 | -3.8929 | -2.3022 | 3.8765 |  | 2.2341 | -0.3801 | 4.0098 | 3.3635 | 3.3435 | 1.0592 | 10.736 | 14.2498 | 14.8348 | 11.0717 | -0.0005 | -0.003 | 0.0008 | 0.0037 | 0.0004 | -0.0001 | 0.0242 | -0.0113 | -0.0033 | -360.1988 | 17.4172 | -360.4881 | 17.6656 | -360.7927 | 18.1132 | -360.9097 | 17.5671 | -352.6813 | 18.7189 | -352.6752 | 16.8197
12:18 | 3520 | 37.2641 | 200.5418 | 447.584 | 452.602 | -17.0594 | -42.8485 | 9.8096 | 6.4752 | 0.7639 | -0.9885 | 2.142 | -1.7663 | 10.3572 | 3.1733 | 0.6099 | 0.6448 | 0.9599 | 0.73 | -129.7234 | -1.8991 | 5.3319 | 1.3255 | -3.8164 | -2.2992 | 3.9339 |  | 2.2653 | -0.4011 | 4.0094 | 3.3639 | 3.3475 | 1.0584 | 10.7117 | 14.2428 | 14.8103 | 11.0591 | 0.0001 | -0.003 | 0.0013 | 0.0042 | 0.0009 | -0.0008 | 0.0304 | -0.0068 | -0.001 | -360.1311 | 17.3946 | -360.4481 | 17.6677 | -360.7989 | 18.0721 | -360.8143 | 17.5301 | -352.6567 | 18.7025 | -352.6629 | 16.8258
12:18 | 3521 | 37.273 | 200.5664 | 447.5663 | 452.6626 | -17.1492 | -42.9153 | 9.8866 | 6.463 | 0.6913 | -1.02 | 2.0867 | -1.7508 | 10.4106 | 3.2424 | 0.6092 | 0.6486 | 0.9608 | 0.7305 | -129.7152 | -1.8621 | 5.3156 | 1.2513 | -3.8369 | -2.2913 | 3.9321 |  | 2.2414 | -0.4235 | 4.0109 | 3.3616 | 3.3403 | 1.059 | 10.7394 | 14.2243 | 14.7973 | 11.058 | 0.0001 | -0.0033 | 0.0006 | 0.0033 | 0.0006 | -0.0004 | 0.0155 | -0.01 | 0.0026 | -360.0911 | 17.3699 | -360.4296 | 17.6738 | -360.7773 | 18.1173 | -360.8727 | 17.5096 | -352.5736 | 18.6779 | -352.6352 | 16.8238
12:18 | 3522 | 37.2944 | 200.6406 | 447.6075 | 452.7013 | -17.1185 | -42.8577 | 9.8692 | 6.4688 | 0.6575 | -1.0768 | 2.1005 | -1.7067 | 10.4272 | 3.1945 | 0.6081 | 0.6469 | 0.9602 | 0.7317 | -129.6717 | -1.7874 | 5.3455 | 1.293 | -3.8782 | -2.3146 | 3.8527 |  | 2.2937 | -0.3399 | 4.0102 | 3.3644 | 3.3429 | 1.0597 | 10.7405 | 14.2487 | 14.8403 | 11.0645 | -0.0003 | -0.0029 | 0.0003 | 0.0038 | 0.0011 | -0.0005 | 0.0103 | -0.0088 | -0.0012 | -360.2204 | 17.411 | -360.4481 | 17.6677 | -360.842 | 18.1235 | -360.9035 | 17.5691 | -352.6967 | 18.6984 | -352.666 | 16.8053
12:18 | 3523 | 37.2412 | 200.5564 | 447.6199 | 452.701 | -17.1634 | -42.9002 | 9.8727 | 6.5341 | 0.7431 | -1.1678 | 2.1088 | -1.8095 | 10.4119 | 3.1118 | 0.6092 | 0.6513 | 0.9589 | 0.7305 | -129.6762 | -1.8997 | 5.4188 | 1.3712 | -3.8504 | -2.3333 | 3.8967 |  | 2.2669 | -0.3825 | 4.0105 | 3.3623 | 3.3454 | 1.0597 | 10.7198 | 14.2103 | 14.8004 | 11.0616 | -0.0003 | -0.0033 | 0.0007 | 0.004 | 0.0009 | -0.0007 | 0.0076 | -0.022 | -0.0125 | -360.2235 | 17.4377 | -360.5189 | 17.6964 | -360.8512 | 18.1029 | -360.845 | 17.5465 | -352.7121 | 18.7538 | -352.7121 | 16.832
12:18 | 3524 | 37.2235 | 200.4921 | 447.5041 | 452.6389 | -17.1792 | -43.0653 | 9.7738 | 6.5323 | 0.789 | -0.9833 | 2.1647 | -1.7341 | 10.3227 | 3.1957 | 0.6086 | 0.6513 | 0.9612 | 0.7319 | -129.6936 | -1.7647 | 5.295 | 1.3975 | -3.8223 | -2.4433 | 3.8275 |  | 2.2418 | -0.4041 | 4.0095 | 3.3634 | 3.3433 | 1.0587 | 10.7291 | 14.2311 | 14.8208 | 11.0421 | 0.0001 | -0.0031 | 0.0003 | 0.0031 | 0.0005 | -0.0007 | -0.0001 | -0.0137 | -0.0099 | -360.0911 | 17.3864 | -360.4666 | 17.682 | -360.8389 | 18.1214 | -360.8512 | 17.5178 | -352.6075 | 18.6984 | -352.6813 | 16.8279
12:18 | 3525 | 37.2394 | 200.5187 | 447.6431 | 452.7151 | -17.2427 | -43.1682 | 9.6875 | 6.5379 | 0.6946 | -0.9838 | 2.1604 | -1.8257 | 10.2736 | 3.2054 | 0.6101 | 0.6522 | 0.9624 | 0.7299 | -129.6349 | -1.7622 | 5.3775 | 1.3466 | -3.8615 | -2.262 | 3.822 |  | 2.237 | -0.4276 | 4.0101 | 3.3653 | 3.3444 | 1.0594 | 10.7463 | 14.272 | 14.8356 | 11.0641 | -0.0008 | -0.003 | 0.0009 | 0.004 | 0.001 | -0.0007 | 0.0095 | -0.0055 | 0.0052 | -360.1835 | 17.3802 | -360.4081 | 17.6451 | -360.7712 | 18.0947 | -360.8789 | 17.5609 | -352.6413 | 18.6922 | -352.5952 | 16.7786
12:18 | 3526 | 37.2532 | 200.551 | 447.6607 | 452.7092 | -17.2577 | -43.205 | 9.6379 | 6.5739 | 0.6775 | -0.9072 | 2.1144 | -1.7603 | 10.2626 | 3.1624 | 0.6084 | 0.6492 | 0.9607 | 0.7302 | -129.6675 | -1.8274 | 5.2594 | 1.2848 | -3.8977 | -2.3557 | 3.8714 |  | 2.2557 | -0.4116 | 4.0107 | 3.3628 | 3.3453 | 1.0593 | 10.7358 | 14.2732 | 14.7906 | 11.0478 | -0.0001 | -0.0027 | 0.0014 | 0.0041 | 0.0004 | -0.0003 | 0.0133 | -0.017 | -0.0073 | -360.2327 | 17.4439 | -360.5066 | 17.68 | -360.8235 | 18.0947 | -360.8297 | 17.5445 | -352.6752 | 18.7436 | -352.7306 | 16.8135
12:18 | 3527 | 37.2546 | 200.5176 | 447.6539 | 452.7292 | -17.2083 | -43.1237 | 9.7596 | 6.5385 | 0.6962 | -1.0806 | 2.0988 | -1.8036 | 10.1998 | 3.1256 | 0.6085 | 0.6507 | 0.9576 | 0.729 | -129.7269 | -1.8551 | 5.34 | 1.1898 | -3.7986 | -2.1616 | 3.9476 |  | 2.1972 | -0.4222 | 4.0096 | 3.3672 | 3.3425 | 1.0592 | 10.7589 | 14.2735 | 14.8449 | 11.0875 | -0.0003 | -0.0025 | 0.0008 | 0.0036 | 0.0009 | -0.0007 | 0.0134 | -0.0119 | -0.0181 | -360.1558 | 17.411 | -360.5096 | 17.7046 | -360.8881 | 18.1296 | -360.8758 | 17.5383 | -352.6475 | 18.723 | -352.7152 | 16.8484
12:19 | 3528 | 37.2011 | 200.4692 | 447.6227 | 452.7362 | -17.1723 | -43.1481 | 9.7759 | 6.4963 | 0.6181 | -1.1071 | 2.076 | -1.8019 | 10.3328 | 3.1741 | 0.6097 | 0.6509 | 0.9625 | 0.7307 | -129.6676 | -1.8105 | 5.3291 | 1.2245 | -3.7546 | -2.3132 | 3.9362 |  | 2.2431 | -0.4049 | 4.0093 | 3.3639 | 3.3459 | 1.0597 | 10.7648 | 14.2443 | 14.8138 | 11.0825 | 0.0002 | -0.0031 | 0.0013 | 0.004 | 0.0005 | -0.0004 | -0.0101 | -0.0195 | -0.0029 | -360.1558 | 17.3597 | -360.3958 | 17.641 | -360.7435 | 18.1091 | -360.885 | 17.5527 | -352.669 | 18.6922 | -352.626 | 16.7991
12:19 | 3529 | 37.2431 | 200.6014 | 447.6527 | 452.7022 | -17.2469 | -43.2433 | 9.7303 | 6.4787 | 0.6519 | -1.0371 | 2.1331 | -1.7375 | 10.3426 | 3.2042 | 0.6099 | 0.649 | 0.9598 | 0.7303 | -129.697 | -1.7864 | 5.4188 | 1.2533 | -3.7907 | -2.2837 | 3.8742 |  | 2.2492 | -0.3855 | 4.0107 | 3.3642 | 3.3459 | 1.0595 | 10.744 | 14.229 | 14.826 | 11.0508 | 0.0002 | -0.003 | 0.0005 | 0.0034 | 0.0009 | -0.0004 | 0.005 | -0.0079 | 0.0058 | -360.2173 | 17.4295 | -360.4819 | 17.6656 | -360.7773 | 18.0804 | -360.8297 | 17.5424 | -352.6629 | 18.7374 | -352.6783 | 16.8012
12:19 | 3530 | 37.2184 | 200.5375 | 447.691 | 452.6877 | -17.2901 | -43.1427 | 9.6217 | 6.4796 | 0.6759 | -1.1956 | 2.1593 | -1.749 | 10.2969 | 3.1923 | 0.6086 | 0.6495 | 0.9571 | 0.7305 | -129.6105 | -1.8555 | 5.4068 | 1.1315 | -3.8698 | -2.3268 | 3.8502 |  | 2.317 | -0.3473 | 4.0095 | 3.3623 | 3.3419 | 1.0592 | 10.7405 | 14.2256 | 14.8229 | 11.0818 | 0.0001 | -0.0026 | 0.0005 | 0.0036 | 0.001 | 0 | 0.0218 | -0.0124 | 0.0135 | -360.1865 | 17.4192 | -360.5281 | 17.7169 | -360.8789 | 18.1235 | -360.8789 | 17.5424 | -352.6413 | 18.7148 | -352.6937 | 16.8484
12:19 | 3531 | 37.2689 | 200.4777 | 447.7112 | 452.7408 | -17.2086 | -43.1116 | 9.6225 | 6.5191 | 0.7588 | -1.2535 | 2.045 | -1.7052 | 10.2573 | 3.1324 | 0.6092 | 0.6524 | 0.9578 | 0.7311 | -129.6278 | -1.8054 | 5.3897 | 1.1628 | -3.7499 | -2.3316 | 3.9239 |  | 2.2588 | -0.4709 | 4.0098 | 3.3624 | 3.3458 | 1.0586 | 10.7119 | 14.2074 | 14.805 | 11.0436 | -0.0006 | -0.0031 | 0.0004 | 0.0034 | 0.0004 | -0.0013 | -0.0033 | -0.0118 | -0.0198 | -360.1865 | 17.3946 | -360.4235 | 17.6574 | -360.8204 | 18.1358 | -360.9189 | 17.5773 | -352.706 | 18.7045 | -352.666 | 16.8135
12:19 | 3532 | 37.27 | 200.4801 | 447.5812 | 452.6056 | -17.2428 | -43.0631 | 9.6344 | 6.44 | 0.7383 | -1.1627 | 2.1076 | -1.7353 | 10.3045 | 3.2099 | 0.6093 | 0.6515 | 0.9576 | 0.7304 | -129.746 | -1.7442 | 5.418 | 1.1563 | -3.7193 | -2.4309 | 3.8982 |  | 2.2268 | -0.4288 | 4.0085 | 3.3638 | 3.3476 | 1.058 | 10.7036 | 14.2057 | 14.7728 | 11.0454 | 0.0004 | -0.0029 | 0.0003 | 0.0031 | 0.001 | -0.0007 | 0.0055 | -0.0061 | -0.0297 | -360.205 | 17.4048 | -360.4112 | 17.6328 | -360.762 | 18.0845 | -360.8697 | 17.5506 | -352.6629 | 18.7087 | -352.6567 | 16.795
12:19 | 3533 | 37.3565 | 200.5413 | 447.6357 | 452.6874 | -17.2101 | -43.0432 | 9.6347 | 6.3713 | 0.7693 | -1.1247 | 2.105 | -1.7014 | 10.388 | 3.2461 | 0.6092 | 0.6506 | 0.9603 | 0.7294 | -129.7007 | -1.7328 | 5.3841 | 1.1267 | -3.6976 | -2.2653 | 3.918 |  | 2.2775 | -0.3908 | 4.0119 | 3.3625 | 3.3433 | 1.0591 | 10.7268 | 14.2171 | 14.8239 | 11.0862 | 0 | -0.0032 | 0.0003 | 0.0035 | 0.0007 | -0.0005 | 0.008 | 0.0036 | -0.0111 | -360.165 | 17.411 | -360.5066 | 17.7026 | -360.845 | 18.0947 | -360.845 | 17.526 | -352.6229 | 18.7148 | -352.6906 | 16.8402
12:19 | 3534 | 37.2905 | 200.5181 | 447.7728 | 452.688 | -17.1448 | -42.9218 | 9.7133 | 6.4203 | 0.7114 | -1.0506 | 2.0227 | -1.6625 | 10.4121 | 3.2013 | 0.6093 | 0.6481 | 0.9566 | 0.7301 | -129.7089 | -1.862 | 5.3344 | 1.2679 | -3.6373 | -2.2589 | 3.9915 |  | 2.3719 | -0.426 | 4.0124 | 3.364 | 3.3432 | 1.059 | 10.7486 | 14.2627 | 14.7967 | 11.0609 | 0.0001 | -0.0026 | 0.0015 | 0.0042 | 0.001 | -0.0004 | 0.02 | -0.0043 | -0.0089 | -360.1588 | 17.3905 | -360.4635 | 17.6964 | -360.8881 | 18.1563 | -360.9497 | 17.5609 | -352.6537 | 18.6984 | -352.6752 | 16.8423
12:19 | 3535 | 37.3636 | 200.6038 | 447.7493 | 452.7198 | -17.2829 | -43.0028 | 9.6579 | 6.4326 | 0.7148 | -1.0347 | 2.0742 | -1.7402 | 10.3703 | 3.1979 | 0.6108 | 0.6449 | 0.9619 | 0.7287 | -129.6214 | -1.7871 | 5.3196 | 1.2885 | -3.5927 | -2.2861 | 4.0432 |  | 2.3233 | -0.44 | 4.0112 | 3.3622 | 3.3442 | 1.0599 | 10.7669 | 14.2297 | 14.866 | 11.0951 | -0.0003 | -0.0026 | 0.0012 | 0.004 | 0.0011 | 0.0001 | 0.0057 | -0.0044 | -0.001 | -360.1619 | 17.3946 | -360.4204 | 17.6553 | -360.7743 | 18.1029 | -360.885 | 17.5671 | -352.7029 | 18.7025 | -352.6567 | 16.8217
12:19 | 3536 | 37.3539 | 200.5571 | 447.6784 | 452.694 | -17.1579 | -43.0642 | 9.6459 | 6.492 | 0.8136 | -0.9591 | 2.1259 | -1.703 | 10.4433 | 3.2433 | 0.6082 | 0.6486 | 0.9595 | 0.7307 | -129.685 | -1.7615 | 5.3716 | 1.2817 | -3.5825 | -2.2173 | 4.0387 |  | 2.2761 | -0.4665 | 4.011 | 3.3644 | 3.3419 | 1.0583 | 10.7856 | 14.3055 | 14.8342 | 11.0861 | -0.0002 | -0.0027 | 0.0007 | 0.0036 | 0.0007 | -0.0005 | 0.0053 | 0.0033 | -0.0011 | -360.1311 | 17.4151 | -360.4881 | 17.68 | -360.8297 | 18.0701 | -360.7958 | 17.5178 | -352.626 | 18.7128 | -352.709 | 16.8402
12:19 | 3537 | 37.3522 | 200.5174 | 447.6944 | 452.7903 | -17.1728 | -43.0537 | 9.5918 | 6.474 | 0.8557 | -0.9605 | 2.1642 | -1.7263 | 10.3501 | 3.2522 | 0.6084 | 0.6465 | 0.9617 | 0.7293 | -129.679 | -1.7379 | 5.3605 | 1.3001 | -3.5304 | -2.1747 | 4.0697 |  | 2.3446 | -0.3637 | 4.0108 | 3.3641 | 3.347 | 1.0586 | 10.7545 | 14.2394 | 14.8362 | 11.0728 | 0.0001 | -0.0032 | 0.0008 | 0.0036 | 0.0006 | 0 | 0.0189 | -0.0027 | -0.0107 | -360.1619 | 17.3864 | -360.4604 | 17.6964 | -360.8604 | 18.1358 | -360.882 | 17.5363 | -352.6506 | 18.6922 | -352.6506 | 16.8587
12:19 | 3538 | 37.3105 | 200.4918 | 447.7062 | 452.8189 | -17.1542 | -43.0753 | 9.5946 | 6.5455 | 0.8662 | -0.9375 | 2.0944 | -1.6693 | 10.4415 | 3.262 | 0.6073 | 0.6461 | 0.961 | 0.7312 | -129.6901 | -1.7753 | 5.3662 | 1.437 | -3.6358 | -2.1776 | 4.0062 |  | 2.3813 | -0.3631 | 4.0107 | 3.3625 | 3.3421 | 1.0606 | 10.7464 | 14.26 | 14.8266 | 11.0479 | -0.0003 | -0.003 | 0.0002 | 0.0038 | 0.0005 | -0.0009 | 0.0057 | -0.017 | -0.003 | -360.2204 | 17.4028 | -360.4542 | 17.6615 | -360.8266 | 18.1276 | -360.8943 | 17.5773 | -352.7121 | 18.7148 | -352.6783 | 16.8361
12:19 | 3539 | 37.4038 | 200.508 | 447.6445 | 452.808 | -17.1666 | -43.0822 | 9.604 | 6.6035 | 0.8246 | -0.9638 | 2.1437 | -1.7575 | 10.3594 | 3.1613 | 0.609 | 0.6502 | 0.9607 | 0.7297 | -129.5989 | -1.7873 | 5.5288 | 1.3758 | -3.8153 | -2.2003 | 4.0554 |  | 2.2694 | -0.3836 | 4.0099 | 3.3587 | 3.3441 | 1.0593 | 10.736 | 14.2207 | 14.8048 | 11.0605 | -0.0004 | -0.0027 | 0.0005 | 0.0041 | 0.0005 | -0.0004 | 0.0048 | -0.0061 | 0.0007 | -360.1773 | 17.4274 | -360.4635 | 17.6738 | -360.7897 | 18.0865 | -360.8143 | 17.5342 | -352.6629 | 18.721 | -352.6875 | 16.8279
12:19 | 3540 | 37.3807 | 200.5601 | 447.6406 | 452.7779 | -17.1954 | -43.1027 | 9.4592 | 6.5457 | 0.8614 | -1.1075 | 2.0817 | -1.8152 | 10.3013 | 3.1359 | 0.6102 | 0.6491 | 0.9598 | 0.7323 | -129.5504 | -1.7654 | 5.4483 | 1.3492 | -3.7629 | -2.1382 | 4.0393 |  | 2.3536 | -0.2821 | 4.0108 | 3.3606 | 3.3424 | 1.0587 | 10.6932 | 14.2068 | 14.75 | 11.0584 | -0.0002 | -0.0032 | 0.0009 | 0.0041 | 0.0015 | -0.0008 | 0.0112 | -0.0039 | -0.0205 | -360.1619 | 17.409 | -360.4881 | 17.6944 | -360.885 | 18.1194 | -360.8789 | 17.5342 | -352.6136 | 18.7087 | -352.7213 | 16.8484
12:19 | 3541 | 37.379 | 200.5672 | 447.7939 | 452.8506 | -17.2109 | -43.0549 | 9.3633 | 6.5457 | 0.8483 | -1.1505 | 2.0611 | -1.8005 | 10.3199 | 3.213 | 0.6095 | 0.6496 | 0.9596 | 0.7312 | -129.6069 | -1.8007 | 5.3889 | 1.4046 | -3.7523 | -2.1476 | 4.0591 |  | 2.2683 | -0.338 | 4.0108 | 3.3635 | 3.3417 | 1.0593 | 10.7245 | 14.2206 | 14.7806 | 11.0494 | 0 | -0.0034 | 0.0006 | 0.0037 | 0.0009 | -0.0001 | 0.0064 | -0.0058 | -0.0021 | -360.1958 | 17.3946 | -360.4481 | 17.6738 | -360.8266 | 18.1379 | -360.922 | 17.5732 | -352.6906 | 18.7066 | -352.6537 | 16.8279
12:19 | 3542 | 37.4013 | 200.5894 | 447.7724 | 452.8064 | -17.2325 | -43.0309 | 9.3936 | 6.519 | 0.8756 | -1.1479 | 2.0384 | -1.8247 | 10.3316 | 3.2473 | 0.6091 | 0.646 | 0.9615 | 0.7306 | -129.5641 | -1.8294 | 5.3949 | 1.4147 | -3.8042 | -2.1369 | 4.0248 |  | 2.2354 | -0.362 | 4.0107 | 3.3666 | 3.3445 | 1.0582 | 10.7173 | 14.2431 | 14.8124 | 11.0756 | 0.0002 | -0.0028 | 0.0017 | 0.0042 | 0.001 | -0.0002 | 0.0051 | -0.0063 | -0.013 | -360.1773 | 17.4172 | -360.4327 | 17.6492 | -360.7804 | 18.0742 | -360.8543 | 17.5486 | -352.6752 | 18.7251 | -352.7121 | 16.8094
12:19 | 3543 | 37.3969 | 200.5163 | 447.6977 | 452.8536 | -17.32 | -43.1739 | 9.3915 | 6.5274 | 0.8938 | -1.0258 | 2.0574 | -1.7947 | 10.3071 | 3.2427 | 0.6103 | 0.6511 | 0.9585 | 0.7309 | -129.5828 | -1.7729 | 5.3347 | 1.3628 | -3.7443 | -2.0749 | 4.0596 |  | 2.3079 | -0.3815 | 4.0109 | 3.3613 | 3.3422 | 1.0601 | 10.7637 | 14.2487 | 14.8345 | 11.0702 | -0.0007 | -0.0027 | 0.0006 | 0.0036 | 0.0007 | -0.0006 | 0.014 | -0.0097 | 0.0045 | -360.1342 | 17.4007 | -360.4758 | 17.682 | -360.8235 | 18.0865 | -360.8266 | 17.5239 | -352.6229 | 18.7045 | -352.6813 | 16.8381
12:19 | 3544 | 37.415 | 200.4843 | 447.7323 | 452.8044 | -17.2097 | -43.0946 | 9.5273 | 6.5121 | 0.8401 | -1.1844 | 2.0687 | -1.7624 | 10.3068 | 3.3244 | 0.6086 | 0.65 | 0.9585 | 0.7296 | -129.5628 | -1.8498 | 5.5196 | 1.3686 | -3.7329 | -2.0844 | 3.9919 |  | 2.2682 | -0.3856 | 4.0094 | 3.365 | 3.3478 | 1.0594 | 10.7671 | 14.2756 | 14.8397 | 11.0847 | -0.0001 | -0.0026 | 0.0006 | 0.0036 | 0.001 | 0.0002 | 0.0064 | -0.0075 | -0.0061 | -360.2019 | 17.4007 | -360.4666 | 17.6882 | -360.8758 | 18.1563 | -360.9004 | 17.5568 | -352.6352 | 18.6943 | -352.6598 | 16.8402
12:19 | 3545 | 37.2964 | 200.5169 | 447.6369 | 452.8418 | -17.2432 | -43.0799 | 9.5182 | 6.5376 | 0.8555 | -1.1351 | 2.0452 | -1.7292 | 10.275 | 3.3452 | 0.6106 | 0.6514 | 0.9564 | 0.7303 | -129.5486 | -1.7481 | 5.4165 | 1.3106 | -3.7989 | -2.1468 | 3.9622 |  | 2.2898 | -0.388 | 4.0092 | 3.3652 | 3.3482 | 1.0592 | 10.7509 | 14.271 | 14.87 | 11.0857 | 0.0001 | -0.0031 | 0.0006 | 0.0038 | 0.001 | -0.0007 | -0.0031 | -0.0166 | -0.0244 | -360.1711 | 17.4007 | -360.4358 | 17.641 | -360.7681 | 18.1071 | -360.8881 | 17.5773 | -352.6875 | 18.7087 | -352.6537 | 16.8135
12:19 | 3546 | 37.3039 | 200.473 | 447.7483 | 452.8031 | -17.3229 | -43.1007 | 9.4869 | 6.5878 | 0.822 | -1.1549 | 2.0218 | -1.6556 | 10.4122 | 3.3782 | 0.6079 | 0.6478 | 0.961 | 0.73 | -129.5738 | -1.7904 | 5.4137 | 1.2501 | -3.9201 | -2.1371 | 3.9638 |  | 2.3264 | -0.3095 | 4.01 | 3.3645 | 3.3449 | 1.0582 | 10.7372 | 14.2333 | 14.8225 | 11.0966 | -0.0002 | -0.0028 | 0 | 0.0036 | 0.0006 | -0.0003 | 0.0261 | -0.013 | 0.0034 | -360.1527 | 17.4172 | -360.4635 | 17.6533 | -360.8204 | 18.0927 | -360.7958 | 17.5321 | -352.6444 | 18.7025 | -352.6506 | 16.8258
12:19 | 3547 | 37.3924 | 200.5376 | 447.7571 | 452.7772 | -17.2292 | -43.094 | 9.5944 | 6.5868 | 0.8845 | -1.0729 | 2.0213 | -1.579 | 10.4384 | 3.4023 | 0.6091 | 0.6491 | 0.9639 | 0.7308 | -129.5537 | -1.8853 | 5.3603 | 1.2722 | -3.8661 | -2.2095 | 3.9317 |  | 2.2353 | -0.2513 | 4.0101 | 3.3656 | 3.3436 | 1.0586 | 10.7245 | 14.2206 | 14.7806 | 11.0494 | -0.0002 | -0.0026 | 0.0006 | 0.004 | 0.0007 | -0.0009 | 0.0068 | -0.0067 | -0.0189 | -360.1404 | 17.4069 | -360.5096 | 17.6985 | -360.882 | 18.1317 | -360.8758 | 17.5404 | -352.626 | 18.7045 | -352.6937 | 16.8587
12:19 | 3548 | 37.3698 | 200.5954 | 447.7111 | 452.7682 | -17.2627 | -42.9715 | 9.5893 | 6.4892 | 0.8987 | -0.9402 | 1.9802 | -1.6696 | 10.3191 | 3.3911 | 0.609 | 0.6491 | 0.9594 | 0.7297 | -129.563 | -1.774 | 5.3681 | 1.2705 | -3.7766 | -2.2471 | 3.8783 |  | 2.2745 | -0.3304 | 4.0115 | 3.3647 | 3.3452 | 1.0602 | 10.7337 | 14.2474 | 14.7973 | 11.0638 | -0.0003 | -0.0024 | 0.0009 | 0.0043 | 0.0006 | -0.0002 | 0.0149 | -0.01 | -0.0145 | -360.1865 | 17.3802 | -360.4419 | 17.6718 | -360.845 | 18.1194 | -360.885 | 17.5671 | -352.666 | 18.6881 | -352.666 | 16.8402
12:19 | 3549 | 37.4161 | 200.5144 | 447.6466 | 452.8839 | -17.3329 | -43.0238 | 9.5078 | 6.5708 | 0.9087 | -0.9399 | 2.0609 | -1.5593 | 10.3838 | 3.408 | 0.6109 | 0.6491 | 0.9593 | 0.7292 | -129.5698 | -1.7764 | 5.3402 | 1.3027 | -3.7836 | -2.2455 | 3.8355 |  | 2.3041 | -0.2471 | 4.0106 | 3.3623 | 3.3427 | 1.0592 | 10.7325 | 14.252 | 14.8249 | 11.0742 | 0.0002 | -0.003 | 0.0007 | 0.0039 | 0.001 | -0.0008 | -0.0067 | 0.005 | -0.0178 | -360.1435 | 17.4048 | -360.4266 | 17.6369 | -360.7743 | 18.0824 | -360.8543 | 17.5445 | -352.6567 | 18.7107 | -352.6475 | 16.8115
12:19 | 3550 | 37.3481 | 200.4916 | 447.7513 | 452.8244 | -17.2761 | -43.0711 | 9.5989 | 6.6458 | 0.8544 | -0.9521 | 2.1548 | -1.6779 | 10.3839 | 3.3598 | 0.6096 | 0.6514 | 0.9584 | 0.7302 | -129.604 | -1.7785 | 5.3338 | 1.3107 | -3.8103 | -2.2993 | 3.8499 |  | 2.2735 | -0.4363 | 4.0103 | 3.3606 | 3.3427 | 1.0594 | 10.7428 | 14.2512 | 14.8094 | 11.0663 | 0.0002 | -0.0031 | 0.0017 | 0.0045 | 0.0005 | -0.0003 | 0.0005 | 0.0082 | 0.0011 | -360.165 | 17.409 | -360.4942 | 17.7005 | -360.8697 | 18.1029 | -360.8635 | 17.5465 | -352.6567 | 18.7128 | -352.6906 | 16.8525
12:19 | 3551 | 37.342 | 200.5101 | 447.6604 | 452.7719 | -17.3333 | -43.0724 | 9.562 | 6.5466 | 0.8124 | -1.026 | 2.038 | -1.7911 | 10.3253 | 3.3073 | 0.61 | 0.6505 | 0.9585 | 0.7312 | -129.5219 | -1.7628 | 5.3445 | 1.3951 | -3.7874 | -2.2287 | 3.9275 |  | 2.3159 | -0.2929 | 4.0107 | 3.365 | 3.3459 | 1.0589 | 10.7612 | 14.2759 | 14.865 | 11.0897 | -0.0001 | -0.0023 | 0.0008 | 0.0042 | 0.0008 | -0.0007 | 0.0013 | -0.0066 | 0 | -360.1773 | 17.4048 | -360.4758 | 17.6861 | -360.8666 | 18.1399 | -360.882 | 17.5506 | -352.6721 | 18.723 | -352.709 | 16.8505
12:19 | 3552 | 37.3456 | 200.5311 | 447.5261 | 452.8087 | -17.2816 | -43.0643 | 9.5756 | 6.5653 | 0.8825 | -0.9263 | 2.1884 | -1.7828 | 10.3337 | 3.2889 | 0.6089 | 0.649 | 0.954 | 0.7304 | -129.5096 | -1.7795 | 5.4242 | 1.4789 | -3.8222 | -2.2361 | 3.9096 |  | 2.3095 | -0.2783 | 4.0112 | 3.3575 | 3.3459 | 1.0574 | 10.7498 | 14.2406 | 14.8376 | 11.0912 | -0.0002 | -0.0027 | 0.0001 | 0.0034 | 0.0007 | -0.0002 | 0.0197 | -0.0023 | -0.016 | -360.1619 | 17.3905 | -360.4235 | 17.6533 | -360.7773 | 18.1009 | -360.8912 | 17.5588 | -352.6413 | 18.7004 | -352.6475 | 16.8135
12:19 | 3553 | 37.441 | 200.5867 | 447.6458 | 452.8178 | -17.264 | -43.0861 | 9.5588 | 6.5803 | 0.8491 | -0.8914 | 2.177 | -1.8085 | 10.4459 | 3.38 | 0.6087 | 0.6513 | 0.9563 | 0.73 | -129.5233 | -1.7685 | 5.4116 | 1.5656 | -3.8399 | -2.208 | 3.8881 |  | 2.2724 | -0.3071 | 4.0103 | 3.3626 | 3.3442 | 1.0594 | 10.7313 | 14.228 | 14.8141 | 11.0666 | 0 | -0.0028 | 0.0006 | 0.0036 | 0.0006 | -0.0004 | 0.0034 | -0.0105 | -0.0089 | -360.1404 | 17.4233 | -360.4666 | 17.6656 | -360.8081 | 18.0886 | -360.8266 | 17.5404 | -352.6598 | 18.7087 | -352.6813 | 16.8299
12:19 | 3554 | 37.2982 | 200.6307 | 447.5935 | 452.8403 | -17.3357 | -43.0669 | 9.5385 | 6.5327 | 0.6343 | -1.0813 | 2.0842 | -1.7811 | 10.4665 | 3.3273 | 0.6088 | 0.6504 | 0.9538 | 0.7295 | -129.5918 | -1.833 | 5.5083 | 1.4302 | -3.8518 | -2.3503 | 3.8836 |  | 2.3729 | -0.2553 | 4.0097 | 3.3631 | 3.3445 | 1.059 | 10.7187 | 14.2206 | 14.8095 | 11.0436 | 0 | -0.0034 | 0.0007 | 0.0039 | 0.0008 | -0.0004 | -0.0005 | 0.0026 | -0.0135 | -360.1988 | 17.4131 | -360.5127 | 17.7005 | -360.8389 | 18.1358 | -360.8789 | 17.5527 | -352.6598 | 18.721 | -352.7152 | 16.8505
12:19 | 3555 | 37.2786 | 200.6198 | 447.5592 | 452.8136 | -17.2722 | -43.01 | 9.6114 | 6.4855 | 0.656 | -1.0371 | 2.0781 | -1.7166 | 10.4329 | 3.3378 | 0.6098 | 0.6508 | 0.9553 | 0.7303 | -129.587 | -1.8123 | 5.4978 | 1.2939 | -3.8349 | -2.2883 | 3.8925 |  | 2.3108 | -0.2309 | 4.0111 | 3.3636 | 3.3429 | 1.0595 | 10.7187 | 14.2321 | 14.7748 | 11.0551 | -0.0003 | -0.0029 | 0.0007 | 0.0039 | 0.0006 | -0.0005 | 0.0196 | -0.0125 | 0.0024 | -360.1711 | 17.3802 | -360.4389 | 17.6512 | -360.8174 | 18.1214 | -360.882 | 17.5588 | -352.6321 | 18.6943 | -352.6444 | 16.8361
12:19 | 3556 | 37.3328 | 200.6359 | 447.5892 | 452.7781 | -17.2786 | -42.9903 | 9.6012 | 6.5006 | 0.7309 | -1.0139 | 2.1298 | -1.8065 | 10.4321 | 3.3064 | 0.6089 | 0.6521 | 0.9575 | 0.7309 | -129.5143 | -1.7052 | 5.4884 | 1.3739 | -3.7672 | -2.2218 | 3.9783 |  | 2.363 | -0.2716 | 4.0118 | 3.3652 | 3.3457 | 1.0603 | 10.7002 | 14.2136 | 14.7792 | 11.0598 | 0.0001 | -0.0026 | 0.001 | 0.0039 | 0.0008 | -0.001 | 0.03 | -0.002 | -0.0025 | -360.1527 | 17.3884 | -360.4419 | 17.6369 | -360.7466 | 18.0865 | -360.8481 | 17.5383 | -352.6321 | 18.6984 | -352.666 | 16.8238
12:19 | 3557 | 37.3637 | 200.6708 | 447.5955 | 452.7992 | -17.307 | -43.0799 | 9.5239 | 6.505 | 0.7376 | -0.9651 | 2.109 | -1.7589 | 10.3668 | 3.3401 | 0.6098 | 0.6473 | 0.9564 | 0.7303 | -129.5228 | -1.7651 | 5.451 | 1.3188 | -3.7963 | -2.2156 | 3.931 |  | 2.4151 | -0.1953 | 4.0101 | 3.3628 | 3.3439 | 1.0598 | 10.7326 | 14.2171 | 14.7891 | 11.0111 | -0.0002 | -0.0031 | 0.0007 | 0.0035 | 0.0003 | -0.0005 | 0.0044 | -0.0066 | 0.0057 | -360.1988 | 17.411 | -360.4666 | 17.6841 | -360.8481 | 18.1071 | -360.8697 | 17.5568 | -352.6383 | 18.7087 | -352.6721 | 16.8443
12:19 | 3558 | 37.3659 | 200.6587 | 447.6036 | 452.7921 | -17.2356 | -43.0591 | 9.6191 | 6.6342 | 0.8514 | -0.9555 | 2.2026 | -1.7251 | 10.3942 | 3.1927 | 0.6098 | 0.6503 | 0.955 | 0.7302 | -129.52 | -1.7936 | 5.3884 | 1.4578 | -3.8701 | -2.1188 | 3.885 |  | 2.4022 | -0.1924 | 4.0102 | 3.3645 | 3.3454 | 1.06 | 10.737 | 14.2569 | 14.8546 | 11.0666 | 0.0003 | -0.0033 | 0.0011 | 0.0036 | 0.0009 | -0.0008 | 0.0204 | -0.0101 | 0.0083 | -360.2081 | 17.4131 | -360.4789 | 17.6636 | -360.8389 | 18.1235 | -360.9004 | 17.565 | -352.6783 | 18.723 | -352.6813 | 16.8381
12:19 | 3559 | 37.3658 | 200.5662 | 447.63 | 452.7587 | -17.2289 | -43.0127 | 9.6267 | 6.516 | 0.7705 | -0.925 | 2.0805 | -1.7958 | 10.3718 | 3.2403 | 0.6094 | 0.6509 | 0.9569 | 0.7297 | -129.5333 | -1.8747 | 5.3251 | 1.4578 | -3.845 | -2.1905 | 3.8536 |  | 2.2997 | -0.1878 | 4.0104 | 3.3661 | 3.3447 | 1.0593 | 10.7533 | 14.2383 | 14.8011 | 11.0829 | -0.0002 | -0.003 | 0.0009 | 0.0038 | 0.0007 | 0.0001 | -0.0001 | -0.0153 | -0.0251 | -360.1435 | 17.3843 | -360.4512 | 17.6389 | -360.7958 | 18.105 | -360.8604 | 17.5445 | -352.6413 | 18.7025 | -352.669 | 16.8279
12:19 | 3560 | 37.3364 | 200.5705 | 447.7025 | 452.783 | -17.2517 | -42.9932 | 9.6356 | 6.5706 | 0.7856 | -1.0077 | 2.0585 | -1.8036 | 10.3663 | 3.2563 | 0.6087 | 0.6526 | 0.9583 | 0.7321 | -129.5787 | -1.7392 | 5.32 | 1.5022 | -3.8056 | -2.1914 | 3.8783 |  | 2.3422 | -0.2601 | 4.0106 | 3.3626 | 3.3463 | 1.0594 | 10.7683 | 14.2592 | 14.8342 | 11.0977 | -0.0006 | -0.0027 | 0.0004 | 0.0032 | 0.0012 | -0.0007 | 0.0278 | 0.0113 | -0.0088 | -360.1619 | 17.3946 | -360.4481 | 17.641 | -360.7989 | 18.1029 | -360.8389 | 17.5424 | -352.6475 | 18.7025 | -352.626 | 16.8238
12:19 | 3561 | 37.347 | 200.7269 | 447.6121 | 452.8058 | -17.2898 | -43.0407 | 9.604 | 6.6432 | 0.8716 | -0.9641 | 2.0956 | -1.778 | 10.4257 | 3.2598 | 0.6098 | 0.6532 | 0.9596 | 0.7315 | -129.6433 | -1.72 | 5.435 | 1.4569 | -3.8128 | -2.1685 | 3.879 |  | 2.3042 | -0.2928 | 4.0097 | 3.3642 | 3.3454 | 1.0593 | 10.7614 | 14.2463 | 14.8318 | 11.0681 | -0.0002 | -0.0029 | 0.0007 | 0.0038 | 0.0002 | -0.0005 | 0.015 | 0.0005 | -0.0194 | -360.1896 | 17.409 | -360.4881 | 17.6718 | -360.8481 | 18.1358 | -360.922 | 17.5712 | -352.6629 | 18.723 | -352.6752 | 16.8423
12:19 | 3562 | 37.3715 | 200.6461 | 447.6716 | 452.8252 | -17.3032 | -42.9207 | 9.627 | 6.6023 | 0.8227 | -1.018 | 2.0584 | -1.7291 | 10.4585 | 3.2544 | 0.6082 | 0.6495 | 0.9554 | 0.7303 | -129.7445 | -1.8309 | 5.307 | 1.3898 | -3.8326 | -2.2364 | 3.8006 |  | 2.2826 | -0.2711 | 4.0093 | 3.3637 | 3.3427 | 1.0594 | 10.7498 | 14.2753 | 14.8144 | 11.0565 | -0.0001 | -0.0032 | 0.0007 | 0.0042 | 0.0009 | -0.0004 | 0.0146 | -0.0072 | 0.0065 | -360.1865 | 17.3905 | -360.4604 | 17.6471 | -360.7958 | 18.1091 | -360.9004 | 17.5568 | -352.666 | 18.721 | -352.6629 | 16.8258
12:19 | 3563 | 37.38 | 200.598 | 447.6612 | 452.9005 | -17.3458 | -42.9367 | 9.6154 | 6.6424 | 0.7928 | -1.0843 | 2.1036 | -1.665 | 10.4726 | 3.2919 | 0.6108 | 0.6504 | 0.9562 | 0.7322 | -129.7536 | -1.7969 | 5.3553 | 1.3921 | -3.8024 | -2.2261 | 3.79 |  | 2.3521 | -0.2603 | 4.0115 | 3.3639 | 3.3455 | 1.0597 | 10.7152 | 14.2229 | 14.8065 | 11.0573 | -0.0002 | -0.003 | 0.0003 | 0.0037 | 0.0005 | -0.0008 | 0.0049 | -0.0047 | 0.0193 | -360.1465 | 17.4007 | -360.4666 | 17.6512 | -360.8112 | 18.1132 | -360.8697 | 17.5383 | -352.6106 | 18.7045 | -352.6813 | 16.8361
12:19 | 3564 | 37.3213 | 200.4815 | 447.6204 | 452.828 | -17.2784 | -42.9032 | 9.6137 | 6.6585 | 0.6954 | -0.9769 | 2.0825 | -1.7147 | 10.4356 | 3.2123 | 0.6093 | 0.6492 | 0.9568 | 0.7304 | -129.6946 | -1.7639 | 5.3881 | 1.3685 | -3.8358 | -2.2363 | 3.8562 |  | 2.3255 | -0.311 | 4.0095 | 3.3615 | 3.3429 | 1.0598 | 10.7476 | 14.2265 | 14.8106 | 11.049 | -0.0005 | -0.0031 | 0.0014 | 0.0042 | 0.0005 | -0.0006 | 0.0152 | -0.0063 | 0.0014 | -360.1865 | 17.4007 | -360.4758 | 17.6882 | -360.8297 | 18.1481 | -360.882 | 17.5547 | -352.6721 | 18.7148 | -352.6875 | 16.8402
12:19 | 3565 | 37.3665 | 200.6342 | 447.5482 | 452.8911 | -17.3485 | -42.8864 | 9.6428 | 6.7237 | 0.7957 | -0.8868 | 2.1136 | -1.6157 | 10.4374 | 3.3491 | 0.6101 | 0.6487 | 0.9542 | 0.7309 | -129.7032 | -1.8214 | 5.3584 | 1.3443 | -3.8522 | -2.2604 | 3.9479 |  | 2.305 | -0.3527 | 4.0106 | 3.3647 | 3.3447 | 1.0595 | 10.7163 | 14.2358 | 14.7858 | 11.0464 | -0.0003 | -0.003 | 0.0006 | 0.0035 | 0.0009 | -0.0008 | 0.0113 | -0.0091 | -0.0058 | -360.1773 | 17.4028 | -360.4604 | 17.6512 | -360.7989 | 18.1399 | -360.8727 | 17.5609 | -352.6629 | 18.721 | -352.6629 | 16.8279
12:19 | 3566 | 37.4015 | 200.609 | 447.4855 | 452.7886 | -17.3529 | -42.9875 | 9.593 | 6.6218 | 0.8193 | -1.0286 | 2.0455 | -1.6933 | 10.4226 | 3.2327 | 0.6102 | 0.6491 | 0.9579 | 0.7324 | -129.7536 | -1.7556 | 5.3111 | 1.1893 | -3.7166 | -2.2221 | 3.9226 |  | 2.4074 | -0.3794 | 4.0103 | 3.36 | 3.3422 | 1.0591 | 10.7278 | 14.2477 | 14.7937 | 11.0515 | 0.0001 | -0.0035 | 0.0009 | 0.0039 | 0.0007 | -0.0001 | 0.006 | -0.0046 | -0.0015 | -360.1435 | 17.3987 | -360.4727 | 17.6512 | -360.7804 | 18.0906 | -360.8143 | 17.528 | -352.6537 | 18.723 | -352.6844 | 16.8135
12:19 | 3567 | 37.4644 | 200.6343 | 447.6226 | 452.8115 | -17.2748 | -42.8361 | 9.6217 | 6.6245 | 0.8263 | -1.131 | 2.0183 | -1.6729 | 10.5125 | 3.2738 | 0.6111 | 0.6525 | 0.9586 | 0.7303 | -129.6985 | -1.801 | 5.3701 | 1.1358 | -3.7887 | -2.1704 | 3.9295 |  | 2.3332 | -0.3736 | 4.0106 | 3.3631 | 3.3464 | 1.0593 | 10.744 | 14.2406 | 14.8202 | 11.0392 | 0 | -0.0029 | 0.0008 | 0.0036 | 0.0011 | 0 | 0.0123 | 0.0039 | -0.007 | -360.2081 | 17.4131 | -360.4912 | 17.6779 | -360.8358 | 18.1399 | -360.8666 | 17.5363 | -352.6567 | 18.7189 | -352.706 | 16.8423
12:19 | 3568 | 37.5046 | 200.6474 | 447.5595 | 452.801 | -17.3056 | -42.8143 | 9.6511 | 6.6036 | 0.7519 | -1.1394 | 2.0067 | -1.7338 | 10.4181 | 3.2052 | 0.6109 | 0.6534 | 0.9604 | 0.7338 | -129.6327 | -1.7143 | 5.4209 | 1.166 | -3.7393 | -2.2141 | 3.9356 |  | 2.3348 | -0.3483 | 4.0098 | 3.3606 | 3.3426 | 1.0602 | 10.7508 | 14.2769 | 14.8711 | 11.1143 | -0.0002 | -0.0025 | 0.0004 | 0.0035 | 0.0006 | 0.0002 | 0.0055 | -0.0067 | 0.003 | -360.1958 | 17.4028 | -360.445 | 17.6636 | -360.8297 | 18.1502 | -360.9251 | 17.5671 | -352.6844 | 18.7087 | -352.6629 | 16.8361
12:19 | 3569 | 37.501 | 200.5999 | 447.599 | 452.7554 | -17.2087 | -42.7461 | 9.7471 | 6.5897 | 0.781 | -0.9852 | 2.0679 | -1.734 | 10.4247 | 3.1476 | 0.612 | 0.6526 | 0.9597 | 0.7314 | -129.5602 | -1.6327 | 5.4758 | 1.3013 | -3.7443 | -2.1852 | 3.9875 |  | 2.4207 | -0.367 | 4.0106 | 3.3666 | 3.3449 | 1.0611 | 10.744 | 14.2579 | 14.826 | 11.0681 | -0.0002 | -0.0028 | 0.0008 | 0.0038 | 0.001 | -0.0007 | 0.0004 | -0.0124 | -0.0147 | -360.1865 | 17.4007 | -360.4296 | 17.6204 | -360.765 | 18.1091 | -360.845 | 17.5342 | -352.6598 | 18.7107 | -352.6167 | 16.8012
12:19 | 3570 | 37.4757 | 200.669 | 447.6408 | 452.8132 | -17.0914 | -42.6775 | 9.7661 | 6.6155 | 0.7023 | -0.949 | 2.1175 | -1.8287 | 10.3729 | 3.1721 | 0.6106 | 0.6515 | 0.9581 | 0.7312 | -129.5929 | -1.5906 | 5.5398 | 1.4683 | -3.7235 | -2.1961 | 3.9782 |  | 2.4604 | -0.27 | 4.0095 | 3.363 | 3.3439 | 1.0595 | 10.7475 | 14.2673 | 14.7954 | 11.0655 | 0 | -0.0027 | 0.0006 | 0.0041 | 0.0008 | 0 | 0.0155 | -0.0082 | 0.0011 | -360.165 | 17.409 | -360.4881 | 17.6718 | -360.8081 | 18.1132 | -360.8297 | 17.5321 | -352.6352 | 18.7004 | -352.6875 | 16.8299
12:19 | 3571 | 37.4271 | 200.6392 | 447.6449 | 452.8883 | -17.1871 | -42.7428 | 9.744 | 6.6189 | 0.7116 | -1.0196 | 2.049 | -1.8147 | 10.3078 | 3.0622 | 0.6101 | 0.6495 | 0.9576 | 0.731 | -129.6136 | -1.6481 | 5.5159 | 1.5899 | -3.7261 | -2.1037 | 3.9746 |  | 2.4285 | -0.268 | 4.0104 | 3.3612 | 3.3417 | 1.0589 | 10.7302 | 14.244 | 14.8232 | 11.0601 | 0 | -0.0031 | 0.0006 | 0.0038 | 0.0008 | -0.0008 | 0.0131 | -0.0217 | -0.0203 | -360.1558 | 17.4007 | -360.4542 | 17.6738 | -360.8727 | 18.1707 | -360.9097 | 17.5424 | -352.6598 | 18.7045 | -352.6721 | 16.8566
12:19 | 3572 | 37.4174 | 200.6181 | 447.6878 | 452.809 | -17.1071 | -42.7986 | 9.6992 | 6.7141 | 0.6544 | -0.9108 | 2.1751 | -1.8238 | 10.3553 | 3.1541 | 0.6099 | 0.6499 | 0.9578 | 0.7316 | -129.6973 | -1.7747 | 5.4726 | 1.3838 | -3.8045 | -2.1577 | 3.9725 |  | 2.3621 | -0.3298 | 4.0106 | 3.3606 | 3.3413 | 1.0604 | 10.7648 | 14.2558 | 14.8311 | 11.0825 | 0 | -0.0025 | 0.001 | 0.0041 | 0.0006 | -0.0005 | 0.0253 | -0.0067 | -0.0009 | -360.1773 | 17.3884 | -360.4358 | 17.6204 | -360.7681 | 18.1214 | -360.8943 | 17.5506 | -352.6906 | 18.7066 | -352.6475 | 16.8053
12:19 | 3573 | 37.4445 | 200.5246 | 447.6539 | 452.892 | -17.1134 | -42.7295 | 9.8339 | 6.7724 | 0.7261 | -0.888 | 2.1798 | -1.8358 | 10.3546 | 3.3112 | 0.6101 | 0.6509 | 0.9588 | 0.7332 | -129.6932 | -1.7371 | 5.4907 | 1.3156 | -3.7565 | -2.1547 | 4.0438 |  | 2.3137 | -0.3641 | 4.0095 | 3.3645 | 3.3454 | 1.0601 | 10.7648 | 14.2501 | 14.8427 | 11.0883 | 0 | -0.0025 | 0.0007 | 0.0036 | 0.0008 | -0.0009 | 0.0147 | 0.0009 | -0.021 | -360.1773 | 17.4131 | -360.4727 | 17.6512 | -360.7804 | 18.1071 | -360.8543 | 17.5096 | -352.6475 | 18.7148 | -352.666 | 16.832
12:19 | 3574 | 37.4806 | 200.5837 | 447.6404 | 452.8646 | -17.1778 | -42.9692 | 9.6731 | 6.798 | 0.8132 | -0.8059 | 2.2423 | -1.7999 | 10.3671 | 3.2725 | 0.6107 | 0.6496 | 0.9593 | 0.7313 | -129.6985 | -1.8212 | 5.3983 | 1.356 | -3.7201 | -2.1126 | 3.99 |  | 2.3472 | -0.3061 | 4.0097 | 3.3623 | 3.3409 | 1.0592 | 10.7544 | 14.2453 | 14.8488 | 11.0897 | 0.0002 | -0.0031 | 0.0007 | 0.0035 | 0.0005 | -0.0005 | 0.0034 | -0.0067 | -0.0208 | -360.1527 | 17.3946 | -360.4758 | 17.6779 | -360.8912 | 18.1687 | -360.9035 | 17.5301 | -352.626 | 18.7025 | -352.6813 | 16.8423
12:19 | 3575 | 37.4083 | 200.6469 | 447.663 | 452.9169 | -17.1319 | -42.8556 | 9.6926 | 6.7362 | 0.7406 | -0.8572 | 2.1545 | -1.723 | 10.4492 | 3.3259 | 0.6092 | 0.65 | 0.9581 | 0.7315 | -129.6772 | -1.7075 | 5.4442 | 1.2632 | -3.766 | -2.0918 | 3.9075 |  | 2.4165 | -0.2714 | 4.0109 | 3.3614 | 3.3429 | 1.0609 | 10.7243 | 14.2616 | 14.8138 | 11.0767 | 0.0006 | -0.0027 | 0.0011 | 0.0041 | 0.0005 | -0.0003 | 0.0028 | 0.0005 | -0.0133 | -360.1711 | 17.3905 | -360.4235 | 17.641 | -360.8112 | 18.1358 | -360.9035 | 17.5588 | -352.6783 | 18.6984 | -352.6475 | 16.832
12:19 | 3576 | 37.4946 | 200.6517 | 447.6423 | 452.9125 | -17.1248 | -42.7618 | 9.7287 | 6.7479 | 0.7653 | -0.8138 | 2.233 | -1.7095 | 10.5085 | 3.3756 | 0.6096 | 0.6523 | 0.9572 | 0.7318 | -129.5435 | -1.7236 | 5.469 | 1.2644 | -3.7554 | -2.1771 | 3.9241 |  | 2.3814 | -0.3527 | 4.0099 | 3.3613 | 3.341 | 1.0607 | 10.7394 | 14.2416 | 14.8321 | 11.0522 | -0.0002 | -0.0027 | 0.0007 | 0.0041 | 0.0007 | -0.0006 | 0.0028 | 0.0002 | -0.0251 | -360.1958 | 17.4131 | -360.4881 | 17.6451 | -360.7804 | 18.0906 | -360.8204 | 17.5178 | -352.6383 | 18.7292 | -352.6813 | 16.8238
12:19 | 3577 | 37.4604 | 200.6554 | 447.6813 | 452.8282 | -17.1783 | -42.9328 | 9.8033 | 6.6907 | 0.7947 | -0.8958 | 2.236 | -1.8676 | 10.409 | 3.23 | 0.6091 | 0.6506 | 0.9566 | 0.7309 | -129.5019 | -1.6538 | 5.5782 | 1.3367 | -3.7017 | -2.2596 | 4.0209 |  | 2.4106 | -0.307 | 4.0074 | 3.3629 | 3.3421 | 1.0582 | 10.7347 | 14.2662 | 14.8124 | 11.0756 | -0.0002 | -0.0023 | 0.001 | 0.0044 | 0.0006 | -0.0001 | 0.0296 | 0.0019 | -0.0008 | -360.1127 | 17.4131 | -360.525 | 17.6985 | -360.8912 | 18.1379 | -360.8604 | 17.5219 | -352.6136 | 18.7271 | -352.7183 | 16.871
12:19 | 3578 | 37.471 | 200.7309 | 447.6351 | 452.8658 | -17.2149 | -42.9197 | 9.8064 | 6.6521 | 0.7762 | -0.8041 | 2.1914 | -1.8157 | 10.41 | 3.1934 | 0.6088 | 0.6513 | 0.9561 | 0.7322 | -129.5184 | -1.6298 | 5.5101 | 1.4871 | -3.7438 | -2.2104 | 4.0115 |  | 2.4002 | -0.3081 | 4.0084 | 3.3639 | 3.3461 | 1.0598 | 10.7302 | 14.2208 | 14.8117 | 11.037 | -0.0001 | -0.003 | 0.0009 | 0.0041 | 0.0011 | -0.0005 | 0.0135 | -0.0185 | -0.0005 | -360.1435 | 17.3802 | -360.4389 | 17.6471 | -360.8389 | 18.1502 | -360.9066 | 17.528 | -352.6598 | 18.7107 | -352.6444 | 16.8464
12:19 | 3579 | 37.5046 | 200.6552 | 447.6932 | 452.8187 | -17.1778 | -42.8612 | 9.8889 | 6.7264 | 0.8622 | -0.7433 | 2.2884 | -1.8152 | 10.4437 | 3.2318 | 0.6081 | 0.6536 | 0.9562 | 0.7315 | -129.5749 | -1.6703 | 5.5653 | 1.5378 | -3.6441 | -2.0836 | 4.0617 |  | 2.3406 | -0.2881 | 4.01 | 3.3606 | 3.3424 | 1.0592 | 10.7395 | 14.2299 | 14.8484 | 11.0468 | -0.0001 | -0.0033 | 0.0007 | 0.004 | 0.0006 | -0.0006 | 0.0146 | -0.0001 | -0.0125 | -360.2081 | 17.4151 | -360.4512 | 17.6307 | -360.765 | 18.0947 | -360.8327 | 17.5424 | -352.6444 | 18.7271 | -352.6629 | 16.8032
12:19 | 3580 | 37.5014 | 200.7697 | 447.635 | 452.8759 | -17.0904 | -42.8754 | 9.7593 | 6.7774 | 0.7713 | -0.9353 | 2.2373 | -1.8351 | 10.3987 | 3.1217 | 0.6081 | 0.6505 | 0.9553 | 0.7306 | -129.6412 | -1.7589 | 5.4446 | 1.4555 | -3.7103 | -2.2497 | 4.0156 |  | 2.3409 | -0.2587 | 4.0095 | 3.366 | 3.3432 | 1.059 | 10.729 | 14.2256 | 14.8113 | 11.076 | 0.0001 | -0.003 | 0.0006 | 0.0037 | 0.0013 | -0.0007 | 0.0054 | -0.0089 | 0.0084 | -360.1773 | 17.4295 | -360.5312 | 17.6985 | -360.8758 | 18.1194 | -360.8481 | 17.5301 | -352.6752 | 18.7415 | -352.7429 | 16.8689
12:19 | 3581 | 37.619 | 200.7737 | 447.7475 | 452.9297 | -17.1425 | -42.9002 | 9.7868 | 6.7935 | 0.7251 | -1.0666 | 2.1925 | -1.7256 | 10.5015 | 3.2308 | 0.6103 | 0.6519 | 0.9594 | 0.7302 | -129.587 | -1.6756 | 5.5336 | 1.403 | -3.7047 | -2.1628 | 3.9729 |  | 2.336 | -0.2467 | 4.0076 | 3.3633 | 3.3437 | 1.0598 | 10.7418 | 14.2438 | 14.8048 | 11.0259 | -0.0005 | -0.0027 | 0.0009 | 0.0036 | 0.0005 | -0.0003 | 0.0214 | -0.0087 | -0.0108 | -360.1773 | 17.3905 | -360.4573 | 17.6636 | -360.8358 | 18.1563 | -360.9158 | 17.5486 | -352.6567 | 18.7025 | -352.6567 | 16.8546
12:19 | 3582 | 37.5852 | 200.6377 | 447.694 | 452.9342 | -17.0856 | -42.8271 | 9.7693 | 6.736 | 0.6595 | -0.8778 | 2.2081 | -1.7062 | 10.4654 | 3.2438 | 0.61 | 0.6548 | 0.9576 | 0.7291 | -129.5867 | -1.7083 | 5.4924 | 1.4878 | -3.634 | -2.1564 | 4.0052 |  | 2.2926 | -0.367 | 4.0092 | 3.3678 | 3.3432 | 1.0604 | 10.7499 | 14.2404 | 14.8365 | 11.0685 | 0.0001 | -0.0028 | 0.0008 | 0.0036 | 0.0006 | -0.0008 | -0.0058 | -0.009 | -0.028 | -360.2019 | 17.4028 | -360.4481 | 17.6307 | -360.7527 | 18.1132 | -360.8666 | 17.5568 | -352.6783 | 18.7169 | -352.6537 | 16.8176
12:19 | 3583 | 37.6057 | 200.7173 | 447.6554 | 452.9489 | -17.0702 | -42.8409 | 9.7518 | 6.6991 | 0.6646 | -0.9116 | 2.1525 | -1.7145 | 10.4317 | 3.3512 | 0.6104 | 0.6526 | 0.954 | 0.73 | -129.5204 | -1.5824 | 5.4448 | 1.5193 | -3.6533 | -2.257 | 4.0647 |  | 2.2816 | -0.4286 | 4.0092 | 3.3646 | 3.3433 | 1.0608 | 10.7349 | 14.2253 | 14.8324 | 11.0594 | 0.0001 | -0.0035 | 0.0004 | 0.0036 | 0.0003 | -0.0002 | 0.0215 | -0.0059 | -0.0068 | -360.1988 | 17.4397 | -360.5066 | 17.6759 | -360.8327 | 18.1153 | -360.8481 | 17.5527 | -352.6844 | 18.7518 | -352.709 | 16.8566
12:19 | 3584 | 37.5494 | 200.7101 | 447.6785 | 452.9144 | -17.0875 | -42.8987 | 9.7803 | 6.7724 | 0.7437 | -0.8784 | 2.0989 | -1.7816 | 10.4685 | 3.2507 | 0.6097 | 0.6539 | 0.9572 | 0.7306 | -129.6385 | -1.6658 | 5.4889 | 1.4447 | -3.773 | -2.1704 | 4.0233 |  | 2.3496 | -0.3414 | 4.0092 | 3.3648 | 3.3439 | 1.0594 | 10.7672 | 14.2579 | 14.826 | 11.0739 | 0 | -0.0029 | 0.0008 | 0.0036 | 0.0004 | -0.0007 | -0.0076 | -0.0113 | -0.0042 | -360.1034 | 17.3843 | -360.4666 | 17.682 | -360.8358 | 18.1522 | -360.882 | 17.528 | -352.6629 | 18.7169 | -352.6967 | 16.8648
12:19 | 3585 | 37.5769 | 200.6911 | 447.6977 | 452.9223 | -17.0982 | -42.7261 | 9.7748 | 6.6941 | 0.8282 | -0.7874 | 2.1844 | -1.7774 | 10.5188 | 3.3103 | 0.61 | 0.6516 | 0.9593 | 0.7299 | -129.5951 | -1.663 | 5.478 | 1.5708 | -3.6264 | -2.0708 | 4.0616 |  | 2.3566 | -0.3249 | 4.0107 | 3.365 | 3.3447 | 1.0595 | 10.7786 | 14.2468 | 14.8407 | 11.0843 | 0 | -0.0023 | 0.0008 | 0.0043 | 0.0007 | -0.0005 | 0.0087 | 0.0007 | -0.0082 | -360.165 | 17.3761 | -360.405 | 17.6245 | -360.7835 | 18.1317 | -360.922 | 17.5547 | -352.6598 | 18.6963 | -352.6167 | 16.8053
12:19 | 3586 | 37.6172 | 200.6537 | 447.6983 | 452.8913 | -17.1087 | -42.7784 | 9.7615 | 6.6911 | 0.7818 | -0.8788 | 2.1031 | -1.6546 | 10.5186 | 3.2671 | 0.61 | 0.6532 | 0.9613 | 0.7317 | -129.5343 | -1.7353 | 5.4499 | 1.525 | -3.7046 | -2.1438 | 4.0492 |  | 2.2766 | -0.258 | 4.0096 | 3.3636 | 3.3436 | 1.0597 | 10.781 | 14.2836 | 14.8819 | 11.0988 | -0.0003 | -0.0031 | 0.0009 | 0.0039 | 0.0012 | -0.0002 | 0.0227 | -0.0048 | -0.0091 | -360.1988 | 17.4377 | -360.485 | 17.6718 | -360.8297 | 18.1296 | -360.8635 | 17.5506 | -352.6967 | 18.7477 | -352.709 | 16.8566
12:19 | 3587 | 37.5798 | 200.7408 | 447.7222 | 452.8878 | -17.0589 | -42.7478 | 9.8106 | 6.6779 | 0.8431 | -0.6721 | 2.2692 | -1.6179 | 10.5798 | 3.3056 | 0.61 | 0.6557 | 0.962 | 0.734 | -129.6798 | -1.7167 | 5.42 | 1.5635 | -3.769 | -2.1941 | 4.0082 |  | 2.3605 | -0.2628 | 4.0104 | 3.3662 | 3.3447 | 1.0613 | 10.7718 | 14.2452 | 14.8767 | 11.067 | 0.0001 | -0.0031 | 0.0009 | 0.0038 | 0.0006 | -0.0006 | 0.021 | -0.0089 | 0.0028 | -360.1096 | 17.3823 | -360.4635 | 17.6841 | -360.8574 | 18.1399 | -360.8143 | 17.5096 | -352.6321 | 18.7128 | -352.6906 | 16.8731
12:20 | 3588 | 37.6673 | 200.7031 | 447.8062 | 452.8899 | -17.0577 | -42.8438 | 9.8535 | 6.6787 | 0.8677 | -0.6899 | 2.2383 | -1.6727 | 10.5239 | 3.2924 | 0.6095 | 0.6536 | 0.9586 | 0.7305 | -129.567 | -1.7609 | 5.4361 | 1.3835 | -3.7052 | -2.1511 | 3.9863 |  | 2.3281 | -0.3091 | 4.0093 | 3.3606 | 3.3413 | 1.0602 | 10.7453 | 14.2241 | 14.831 | 11.0641 | -0.0003 | -0.0035 | 0.0006 | 0.0037 | 0.0001 | -0.0004 | 0.0052 | -0.0041 | 0.0182 | -360.1404 | 17.372 | -360.4173 | 17.6533 | -360.8143 | 18.1399 | -360.9066 | 17.5321 | -352.6383 | 18.6881 | -352.6229 | 16.8361
12:20 | 3589 | 37.6784 | 200.7569 | 447.7905 | 452.8655 | -17.0132 | -42.8148 | 9.8769 | 6.6522 | 0.8255 | -0.7805 | 2.1571 | -1.6619 | 10.5288 | 3.4083 | 0.6096 | 0.6511 | 0.9596 | 0.7323 | -129.5362 | -1.7343 | 5.446 | 1.4008 | -3.5663 | -2.2141 | 4.0824 |  | 2.3774 | -0.2644 | 4.0087 | 3.3651 | 3.3434 | 1.0603 | 10.7349 | 14.2194 | 14.8024 | 11.0483 | -0.0001 | -0.0025 | 0.0003 | 0.0031 | 0.0005 | -0.0009 | 0.0162 | -0.0099 | -0.0006 | -360.2942 | 17.4418 | -360.5035 | 17.6574 | -360.8204 | 18.1255 | -360.8789 | 17.5671 | -352.6998 | 18.7579 | -352.7183 | 16.8361
12:20 | 3590 | 37.6498 | 200.7919 | 447.7575 | 452.9509 | -17.0885 | -42.7415 | 9.8799 | 6.5971 | 0.8721 | -0.717 | 2.2024 | -1.6017 | 10.5261 | 3.3705 | 0.6103 | 0.6523 | 0.9602 | 0.7329 | -129.5429 | -1.668 | 5.3764 | 1.3633 | -3.5544 | -2.1361 | 4.0399 |  | 2.4376 | -0.2001 | 4.0102 | 3.3672 | 3.3431 | 1.0603 | 10.7174 | 14.2545 | 14.7882 | 11.0529 | 0 | -0.0026 | 0.0007 | 0.0038 | 0.0005 | -0.0003 | 0.0005 | -0.003 | 0.0019 | -360.125 | 17.4151 | -360.5096 | 17.6779 | -360.8327 | 18.105 | -360.7958 | 17.4993 | -352.626 | 18.7251 | -352.7121 | 16.8648
12:20 | 3591 | 37.7282 | 200.7774 | 447.8495 | 453.0614 | -17.1499 | -42.7695 | 9.8499 | 6.6289 | 0.9677 | -0.8091 | 2.2671 | -1.7261 | 10.5227 | 3.2822 | 0.6102 | 0.6495 | 0.9577 | 0.7325 | -129.5696 | -1.753 | 5.4541 | 1.3193 | -3.6167 | -2.0961 | 4.061 |  | 2.4213 | -0.2179 | 4.0107 | 3.3636 | 3.3442 | 1.0596 | 10.7475 | 14.2382 | 14.8464 | 11.089 | -0.0001 | -0.0032 | 0.001 | 0.0038 | 0.0012 | -0.0007 | 0.0076 | 0.0024 | -0.0213 | -360.1465 | 17.3925 | -360.4481 | 17.6553 | -360.842 | 18.1522 | -360.882 | 17.528 | -352.6413 | 18.7066 | -352.6229 | 16.8402
12:20 | 3592 | 37.7006 | 200.716 | 447.7197 | 452.949 | -17.1909 | -42.7532 | 9.8149 | 6.654 | 0.9213 | -0.7512 | 2.1607 | -1.6965 | 10.5353 | 3.2374 | 0.6095 | 0.6504 | 0.9573 | 0.7314 | -129.5771 | -1.6924 | 5.4392 | 1.3025 | -3.7221 | -2.08 | 4.0493 |  | 2.3358 | -0.3674 | 4.0076 | 3.3617 | 3.346 | 1.0602 | 10.7497 | 14.2466 | 14.7992 | 11.0731 | 0.0005 | -0.003 | 0.0009 | 0.0039 | 0.0003 | -0.0001 | 0.0062 | -0.0201 | -0.0117 | -360.2358 | 17.4233 | -360.4789 | 17.6451 | -360.7835 | 18.1296 | -360.9189 | 17.5773 | -352.7398 | 18.7415 | -352.6844 | 16.8381
12:20 | 3593 | 37.6206 | 200.6453 | 447.7098 | 452.8948 | -17.2341 | -42.872 | 9.7543 | 6.7079 | 0.8318 | -0.8516 | 2.1359 | -1.8107 | 10.4839 | 3.2133 | 0.6108 | 0.6496 | 0.9571 | 0.7318 | -129.5949 | -1.7891 | 5.4175 | 1.3219 | -3.6361 | -2.0526 | 4.0517 |  | 2.3611 | -0.2802 | 4.0095 | 3.3627 | 3.3462 | 1.0591 | 10.7659 | 14.263 | 14.8683 | 11.1121 | 0.0001 | -0.0025 | 0.0005 | 0.0042 | 0.0011 | -0.0005 | 0.0088 | -0.0023 | -0.0207 | -360.1711 | 17.4172 | -360.4727 | 17.6553 | -360.8081 | 18.1009 | -360.7927 | 17.5198 | -352.6537 | 18.7271 | -352.7152 | 16.8546
12:20 | 3594 | 37.6858 | 200.7909 | 447.837 | 452.9696 | -17.2409 | -42.7305 | 9.6715 | 6.678 | 0.8498 | -0.804 | 2.1606 | -1.7407 | 10.4589 | 3.2613 | 0.61 | 0.6515 | 0.9596 | 0.7322 | -129.6703 | -1.7517 | 5.389 | 1.3541 | -3.658 | -2.19 | 4.0402 |  | 2.3838 | -0.1646 | 4.0084 | 3.3631 | 3.3454 | 1.0614 | 10.7613 | 14.2581 | 14.8328 | 11.1024 | 0.0001 | -0.0022 | 0.0006 | 0.0039 | 0.0003 | -0.0006 | 0.0054 | -0.0137 | -0.0102 | -360.0942 | 17.3782 | -360.4666 | 17.6697 | -360.8297 | 18.1337 | -360.882 | 17.5116 | -352.6013 | 18.6963 | -352.6783 | 16.8587
12:20 | 3595 | 37.7116 | 200.7642 | 447.8244 | 452.9759 | -17.1542 | -42.604 | 9.7848 | 6.7627 | 0.8979 | -0.8016 | 2.2045 | -1.6981 | 10.4721 | 3.3102 | 0.6099 | 0.6502 | 0.9604 | 0.7316 | -129.5803 | -1.6751 | 5.4599 | 1.3557 | -3.5653 | -2.0841 | 4.1062 |  | 2.3466 | -0.2768 | 4.0107 | 3.3622 | 3.3448 | 1.0615 | 10.7313 | 14.2509 | 14.7899 | 11.0843 | 0.0002 | -0.0028 | 0.0007 | 0.0036 | 0.0007 | -0.0006 | -0.0005 | -0.0057 | -0.0123 | -360.2142 | 17.4048 | -360.4419 | 17.6512 | -360.8143 | 18.1543 | -360.922 | 17.5753 | -352.7337 | 18.7251 | -352.6383 | 16.834
12:20 | 3596 | 37.6813 | 200.7558 | 447.7888 | 453.0051 | -17.0999 | -42.6495 | 9.8461 | 6.7438 | 0.8446 | -0.8826 | 2.1975 | -1.7279 | 10.5365 | 3.2846 | 0.6102 | 0.6516 | 0.9615 | 0.7327 | -129.5923 | -1.6452 | 5.5235 | 1.4217 | -3.6088 | -2.0165 | 4.151 |  | 2.3913 | -0.2286 | 4.01 | 3.3602 | 3.3464 | 1.0604 | 10.7441 | 14.2345 | 14.8181 | 11.0573 | 0.0003 | -0.0025 | 0.0008 | 0.0041 | 0.0005 | -0.0009 | 0.0191 | -0.0037 | -0.0015 | -360.2265 | 17.4131 | -360.4573 | 17.6451 | -360.7743 | 18.1132 | -360.845 | 17.5547 | -352.6967 | 18.7395 | -352.706 | 16.8299
12:20 | 3597 | 37.6378 | 200.8639 | 447.839 | 453.0001 | -17.1199 | -42.6931 | 9.8907 | 6.7633 | 0.8843 | -0.7945 | 2.1842 | -1.5793 | 10.5445 | 3.2996 | 0.6083 | 0.6489 | 0.9618 | 0.7311 | -129.6194 | -1.714 | 5.5431 | 1.3727 | -3.6084 | -2.1523 | 4.0772 |  | 2.4748 | -0.2356 | 4.0096 | 3.3612 | 3.3411 | 1.0606 | 10.7162 | 14.2244 | 14.8042 | 11.0634 | -0.0003 | -0.0027 | 0.0015 | 0.0041 | 0.0006 | -0.0001 | 0.0165 | -0.0075 | -0.0028 | -360.1404 | 17.3884 | -360.4727 | 17.6697 | -360.8389 | 18.1235 | -360.8266 | 17.4993 | -352.5921 | 18.7004 | -352.6813 | 16.8607
12:20 | 3598 | 37.6004 | 200.8016 | 447.8261 | 452.9393 | -17.1349 | -42.7327 | 9.9126 | 6.7056 | 0.7995 | -0.7951 | 2.201 | -1.5359 | 10.5843 | 3.3802 | 0.6106 | 0.6492 | 0.9596 | 0.7325 | -129.5588 | -1.6886 | 5.5932 | 1.3697 | -3.6707 | -2.2072 | 4.1442 |  | 2.4671 | -0.2752 | 4.0096 | 3.3663 | 3.3438 | 1.0603 | 10.7417 | 14.244 | 14.8117 | 11.0717 | -0.0003 | -0.0025 | 0.0007 | 0.004 | 0.0015 | -0.0004 | -0.003 | -0.0146 | 0.0091 | -360.1096 | 17.3802 | -360.4419 | 17.6553 | -360.8297 | 18.1604 | -360.922 | 17.5506 | -352.6413 | 18.6902 | -352.6136 | 16.832
12:20 | 3599 | 37.6401 | 200.7771 | 447.7105 | 453.0078 | -17.1539 | -42.638 | 9.9311 | 6.6543 | 0.7274 | -0.7824 | 2.171 | -1.6628 | 10.5145 | 3.3199 | 0.6094 | 0.6492 | 0.9628 | 0.7325 | -129.5634 | -1.594 | 5.4462 | 1.4137 | -3.7028 | -1.9967 | 4.1046 |  | 2.3743 | -0.2153 | 4.0107 | 3.3651 | 3.3417 | 1.0617 | 10.7417 | 14.221 | 14.7664 | 11.0713 | 0.0005 | -0.0023 | 0.0011 | 0.0043 | 0.0006 | -0.0003 | 0.0091 | -0.0096 | 0.0116 | -360.2388 | 17.4192 | -360.4727 | 17.6677 | -360.8112 | 18.1358 | -360.9312 | 17.5712 | -352.706 | 18.7456 | -352.6875 | 16.8423
12:20 | 3600 | 37.6841 | 200.7869 | 447.7573 | 452.9616 | -17.2078 | -42.7742 | 9.9661 | 6.5955 | 0.7591 | -0.7234 | 2.0679 | -1.6162 | 10.4914 | 3.301 | 0.6093 | 0.6514 | 0.9616 | 0.732 | -129.6006 | -1.6963 | 5.4428 | 1.3085 | -3.7753 | -2.1467 | 4.079 |  | 2.4282 | -0.1756 | 4.0101 | 3.3606 | 3.3418 | 1.0601 | 10.7337 | 14.2416 | 14.8147 | 11.0695 | -0.0001 | -0.0034 | 0.0006 | 0.0037 | 0.0009 | -0.0001 | 0.0281 | -0.0054 | -0.0216 | -360.1773 | 17.4254 | -360.4912 | 17.6759 | -360.8389 | 18.1173 | -360.8358 | 17.5321 | -352.666 | 18.7374 | -352.7275 | 16.8587
12:20 | 3601 | 37.6201 | 200.7417 | 447.7941 | 452.9919 | -17.1905 | -42.6906 | 9.9274 | 6.6489 | 0.7912 | -0.7636 | 2.1534 | -1.7799 | 10.3973 | 3.2884 | 0.6088 | 0.6521 | 0.9602 | 0.7342 | -129.61 | -1.7423 | 5.4519 | 1.2188 | -3.7752 | -2.0957 | 4.052 |  | 2.4758 | -0.1903 | 4.0103 | 3.3589 | 3.3441 | 1.0599 | 10.7428 | 14.2511 | 14.8488 | 11.1129 | -0.0003 | -0.0029 | 0.0003 | 0.0039 | 0.0002 | -0.0006 | -0.0045 | -0.0064 | -0.0059 | -360.1034 | 17.3617 | -360.4235 | 17.6636 | -360.845 | 18.1358 | -360.8389 | 17.5116 | -352.5798 | 18.684 | -352.6383 | 16.8525
12:20 | 3602 | 37.6622 | 200.703 | 447.7496 | 453.0127 | -17.235 | -42.6521 | 9.8747 | 6.5978 | 0.7292 | -0.6718 | 2.2193 | -1.795 | 10.4253 | 3.329 | 0.6103 | 0.6511 | 0.956 | 0.7333 | -129.6081 | -1.6554 | 5.3971 | 1.4236 | -3.7695 | -2.0315 | 4.0562 |  | 2.4011 | -0.3159 | 4.0094 | 3.3605 | 3.3447 | 1.0599 | 10.7452 | 14.236 | 14.8216 | 11.0692 | -0.0003 | -0.0027 | 0.0007 | 0.004 | 0.0014 | 0 | 0.0057 | -0.0167 | -0.0123 | -360.1835 | 17.3946 | -360.4327 | 17.6512 | -360.8143 | 18.1317 | -360.9281 | 17.5547 | -352.6629 | 18.7087 | -352.6198 | 16.8238
12:20 | 3603 | 37.6057 | 200.6138 | 447.8131 | 452.9831 | -17.1358 | -42.6587 | 9.9017 | 6.6063 | 0.7967 | -0.6983 | 2.2396 | -1.7065 | 10.4666 | 3.3315 | 0.6094 | 0.6506 | 0.9575 | 0.7295 | -129.5845 | -1.625 | 5.4785 | 1.5028 | -3.7705 | -2.0559 | 4.0714 |  | 2.4076 | -0.2823 | 4.0086 | 3.365 | 3.3424 | 1.0615 | 10.7406 | 14.2428 | 14.8392 | 11.0937 | -0.0004 | -0.0031 | 0.0003 | 0.0034 | 0.0007 | -0.0005 | 0.0086 | -0.0134 | -0.0122 | -360.2481 | 17.4397 | -360.5189 | 17.6738 | -360.8266 | 18.1296 | -360.8789 | 17.5465 | -352.7275 | 18.7538 | -352.7152 | 16.8525
12:20 | 3604 | 37.7217 | 200.7762 | 447.8221 | 453.0511 | -17.1362 | -42.6129 | 9.8244 | 6.5954 | 0.6822 | -0.7437 | 2.1353 | -1.7 | 10.4636 | 3.3042 | 0.6096 | 0.6509 | 0.9596 | 0.7323 | -129.6376 | -1.4802 | 5.4781 | 1.5447 | -3.7167 | -2.0474 | 4.031 |  | 2.4458 | -0.2706 | 4.0105 | 3.3674 | 3.3443 | 1.0618 | 10.7349 | 14.208 | 14.8208 | 11.0883 | 0 | -0.0033 | 0.0002 | 0.0032 | 0.0009 | -0.0009 | 0.0011 | -0.004 | -0.0088 | -360.1342 | 17.4028 | -360.5281 | 17.6985 | -360.8266 | 18.1296 | -360.8358 | 17.5178 | -352.6567 | 18.7312 | -352.7306 | 16.8813
12:20 | 3605 | 37.6245 | 200.7184 | 447.7951 | 452.9824 | -17.2091 | -42.7345 | 9.7036 | 6.5227 | 0.606 | -0.7728 | 2.175 | -1.6231 | 10.4694 | 3.2789 | 0.61 | 0.6496 | 0.9647 | 0.7307 | -129.6999 | -1.5982 | 5.406 | 1.4678 | -3.6951 | -1.9998 | 3.9929 |  | 2.4232 | -0.3005 | 4.0096 | 3.367 | 3.3463 | 1.0617 | 10.737 | 14.2684 | 14.843 | 11.0955 | -0.0003 | -0.0031 | 0.0009 | 0.0036 | 0.0003 | -0.0003 | 0.0153 | -0.0137 | -0.0126 | -360.1065 | 17.3761 | -360.4081 | 17.6512 | -360.8143 | 18.1337 | -360.8604 | 17.5137 | -352.629 | 18.6963 | -352.629 | 16.834
12:20 | 3606 | 37.6101 | 200.7049 | 447.7431 | 453.1295 | -17.2541 | -42.7934 | 9.7304 | 6.5781 | 0.5676 | -0.6824 | 2.1756 | -1.5631 | 10.537 | 3.3182 | 0.6092 | 0.6483 | 0.9626 | 0.7318 | -129.6247 | -1.6233 | 5.4562 | 1.4977 | -3.7281 | -2.0706 | 3.9816 |  | 2.3744 | -0.2606 | 4.0083 | 3.3621 | 3.3428 | 1.0596 | 10.7568 | 14.2418 | 14.7984 | 11.0865 | -0.0005 | -0.0025 | 0.0006 | 0.0036 | 0.0007 | -0.0007 | 0.0035 | -0.006 | 0.0035 | -360.2388 | 17.3966 | -360.4419 | 17.643 | -360.7866 | 18.1255 | -360.922 | 17.5506 | -352.6998 | 18.7189 | -352.6721 | 16.8238
12:20 | 3607 | 37.6205 | 200.6794 | 447.8041 | 453.0202 | -17.2064 | -42.7323 | 9.7171 | 6.6575 | 0.6112 | -0.6931 | 2.2381 | -1.6754 | 10.4747 | 3.2535 | 0.611 | 0.6538 | 0.9599 | 0.733 | -129.653 | -1.6597 | 5.4234 | 1.544 | -3.623 | -2.1545 | 4.0676 |  | 2.4438 | -0.2697 | 4.0099 | 3.3634 | 3.3421 | 1.06 | 10.7059 | 14.2426 | 14.815 | 11.0537 | -0.0002 | -0.0033 | 0.0008 | 0.004 | 0.0008 | -0.0007 | 0.0141 | -0.0109 | 0.0104 | -360.2204 | 17.45 | -360.5343 | 17.6697 | -360.8235 | 18.1173 | -360.8727 | 17.5424 | -352.7121 | 18.762 | -352.7244 | 16.8587
12:20 | 3608 | 37.6257 | 200.8223 | 447.8514 | 453.0955 | -17.1285 | -42.7512 | 9.6588 | 6.8088 | 0.7184 | -0.8443 | 2.2812 | -1.6796 | 10.471 | 3.2606 | 0.61 | 0.6523 | 0.9624 | 0.7304 | -129.6234 | -1.7026 | 5.411 | 1.5831 | -3.5362 | -2.0918 | 4.0889 |  | 2.2917 | -0.2995 | 4.0082 | 3.3627 | 3.3429 | 1.0601 | 10.7462 | 14.2549 | 14.8493 | 11.1269 | 0.0004 | -0.003 | 0.0007 | 0.0041 | 0.0008 | -0.0001 | -0.0038 | 0.0026 | -0.0348 | -360.1034 | 17.3987 | -360.4573 | 17.6759 | -360.842 | 18.1091 | -360.842 | 17.5198 | -352.6321 | 18.7148 | -352.6967 | 16.8505
12:20 | 3609 | 37.607 | 200.7651 | 447.8034 | 453.0305 | -17.1227 | -42.716 | 9.699 | 6.7757 | 0.7134 | -0.8895 | 2.2898 | -1.6966 | 10.504 | 3.296 | 0.6078 | 0.6532 | 0.9617 | 0.7309 | -129.6226 | -1.6734 | 5.4913 | 1.4889 | -3.5483 | -2.1846 | 4.0657 |  | 2.4447 | -0.2644 | 4.0092 | 3.3644 | 3.3463 | 1.0611 | 10.7464 | 14.2369 | 14.8555 | 11.0768 | -0.0003 | -0.0035 | 0.0002 | 0.0038 | 0.0009 | -0.0007 | 0.0064 | -0.0007 | -0.0026 | -360.1373 | 17.3761 | -360.4204 | 17.6286 | -360.7989 | 18.1317 | -360.882 | 17.5424 | -352.6352 | 18.684 | -352.6136 | 16.8176
12:20 | 3610 | 37.623 | 200.7974 | 447.8581 | 452.9874 | -17.1625 | -42.6855 | 9.7308 | 6.8013 | 0.7064 | -0.9219 | 2.2733 | -1.6985 | 10.3939 | 3.2278 | 0.6092 | 0.6517 | 0.9642 | 0.7308 | -129.6096 | -1.6911 | 5.464 | 1.4214 | -3.6367 | -2.0696 | 4.0402 |  | 2.3965 | -0.2204 | 4.0099 | 3.3619 | 3.3459 | 1.0612 | 10.7441 | 14.2287 | 14.847 | 11.0746 | -0.0007 | -0.0031 | 0.0004 | 0.0038 | 0.0004 | -0.0004 | 0.0123 | -0.0057 | -0.0251 | -360.2481 | 17.4336 | -360.4789 | 17.6389 | -360.7866 | 18.1235 | -360.882 | 17.5671 | -352.7429 | 18.7436 | -352.6752 | 16.8176
12:20 | 3611 | 37.6096 | 200.7962 | 447.8447 | 453.03 | -17.0958 | -42.6155 | 9.7762 | 6.842 | 0.7823 | -0.906 | 2.2753 | -1.7098 | 10.4325 | 3.2262 | 0.6101 | 0.6549 | 0.9585 | 0.7308 | -129.5964 | -1.6904 | 5.4098 | 1.4426 | -3.6017 | -2.0991 | 4.021 |  | 2.4186 | -0.1458 | 4.0082 | 3.3613 | 3.3453 | 1.0617 | 10.7359 | 14.2499 | 14.8127 | 11.0771 | -0.0001 | -0.0025 | 0.0004 | 0.0036 | 0.0008 | -0.0007 | 0.0171 | -0.0076 | 0.0023 | -360.1835 | 17.4172 | -360.5158 | 17.6759 | -360.8512 | 18.142 | -360.8635 | 17.5445 | -352.6752 | 18.7333 | -352.7367 | 16.8689
12:20 | 3612 | 37.6751 | 200.7338 | 447.8336 | 452.989 | -17.103 | -42.7053 | 9.7237 | 6.787 | 0.9326 | -0.9332 | 2.2896 | -1.7248 | 10.3866 | 3.2782 | 0.609 | 0.6572 | 0.9607 | 0.7315 | -129.6729 | -1.6689 | 5.5954 | 1.5069 | -3.6352 | -2.0985 | 3.9524 |  | 2.4493 | -0.2875 | 4.0079 | 3.3631 | 3.3439 | 1.0605 | 10.7245 | 14.2146 | 14.8027 | 11.0613 | 0.0002 | -0.0033 | 0.0002 | 0.0034 | 0.0002 | -0.0005 | 0.0093 | -0.0186 | -0.0063 | -360.1219 | 17.3658 | -360.4173 | 17.6492 | -360.8081 | 18.1645 | -360.8943 | 17.5178 | -352.6013 | 18.6922 | -352.6229 | 16.8402
12:20 | 3613 | 37.6715 | 200.8032 | 447.9186 | 453.0696 | -16.9868 | -42.6434 | 9.7911 | 6.8442 | 0.9528 | -0.8971 | 2.3389 | -1.787 | 10.4099 | 3.265 | 0.6091 | 0.6514 | 0.9623 | 0.731 | -129.5401 | -1.6714 | 5.5151 | 1.4478 | -3.6212 | -2.1196 | 4.0395 |  | 2.4616 | -0.1395 | 4.0076 | 3.3637 | 3.3421 | 1.0614 | 10.7324 | 14.2293 | 14.8223 | 11.0616 | 0.0005 | -0.0028 | 0.0016 | 0.0043 | 0.0011 | -0.0007 | 0.0021 | 0 | 0.0004 | -360.205 | 17.4028 | -360.4296 | 17.6204 | -360.7989 | 18.1481 | -360.8881 | 17.5629 | -352.6752 | 18.7025 | -352.6383 | 16.8074
12:20 | 3614 | 37.6535 | 200.7482 | 447.891 | 453.0907 | -17.0249 | -42.7383 | 9.8344 | 6.8241 | 1.0358 | -0.9405 | 2.2844 | -1.7363 | 10.4376 | 3.3413 | 0.6079 | 0.6522 | 0.9572 | 0.7325 | -129.5853 | -1.6682 | 5.4833 | 1.5298 | -3.6301 | -2.3299 | 3.9745 |  | 2.4919 | -0.2102 | 4.0087 | 3.3622 | 3.3438 | 1.0617 | 10.7348 | 14.2314 | 14.8113 | 11.0587 | -0.0002 | -0.0028 | 0.0008 | 0.0035 | 0.0003 | -0.0005 | 0.0037 | -0.013 | -0.0185 | -360.1988 | 17.4397 | -360.5219 | 17.6779 | -360.8266 | 18.1543 | -360.8604 | 17.5506 | -352.6813 | 18.7682 | -352.709 | 16.8587
12:20 | 3615 | 37.7758 | 200.8062 | 447.9421 | 453.1473 | -17.0153 | -42.6241 | 9.8345 | 6.7575 | 1.0644 | -0.9706 | 2.3024 | -1.717 | 10.4471 | 3.3586 | 0.6082 | 0.6507 | 0.9594 | 0.7317 | -129.5594 | -1.631 | 5.4754 | 1.5826 | -3.6931 | -2.1662 | 3.9924 |  | 2.4166 | -0.1642 | 4.0082 | 3.3621 | 3.3432 | 1.0607 | 10.7509 | 14.2361 | 14.84 | 11.0399 | -0.0007 | -0.0028 | 0.0004 | 0.0037 | 0.001 | -0.0002 | 0.0102 | -0.0197 | -0.0177 | -360.085 | 17.3823 | -360.4635 | 17.682 | -360.8697 | 18.1707 | -360.8635 | 17.5178 | -352.6229 | 18.7087 | -352.7121 | 16.8689
12:20 | 3616 | 37.7386 | 200.7852 | 447.9042 | 453.0895 | -16.927 | -42.6466 | 9.8858 | 6.7161 | 1.0157 | -1.0238 | 2.3362 | -1.7799 | 10.4528 | 3.3087 | 0.6085 | 0.6532 | 0.9602 | 0.7321 | -129.4985 | -1.6469 | 5.4984 | 1.5642 | -3.6033 | -2.1863 | 4.0198 |  | 2.503 | -0.2144 | 4.0084 | 3.3602 | 3.3443 | 1.0605 | 10.7496 | 14.2701 | 14.8534 | 11.1013 | 0.0003 | -0.0025 | 0.001 | 0.0039 | 0.0009 | -0.0002 | 0.0225 | -0.0082 | -0.004 | -360.1465 | 17.3679 | -360.4112 | 17.6471 | -360.802 | 18.1666 | -360.8758 | 17.5301 | -352.6198 | 18.6902 | -352.5983 | 16.834
12:20 | 3617 | 37.7122 | 200.8105 | 447.8883 | 453.0874 | -16.9587 | -42.641 | 10.0183 | 6.6739 | 1.061 | -1.0128 | 2.3184 | -1.7132 | 10.4838 | 3.2343 | 0.6094 | 0.6492 | 0.9591 | 0.7318 | -129.5336 | -1.7339 | 5.4972 | 1.5804 | -3.7126 | -2.0882 | 4.0646 |  | 2.502 | -0.1627 | 4.0082 | 3.3648 | 3.3465 | 1.0614 | 10.7591 | 14.244 | 14.8348 | 11.0948 | 0.0002 | -0.003 | 0 | 0.0035 | 0.0006 | -0.0002 | 0.0225 | -0.0137 | -0.0044 | -360.2327 | 17.4397 | -360.4819 | 17.6574 | -360.8174 | 18.144 | -360.9066 | 17.5568 | -352.6875 | 18.7312 | -352.6721 | 16.832
12:20 | 3618 | 37.7665 | 200.8115 | 447.9246 | 453.0565 | -16.9952 | -42.695 | 9.9665 | 6.7223 | 1.0335 | -0.9946 | 2.26 | -1.826 | 10.4375 | 3.2615 | 0.6085 | 0.6547 | 0.9641 | 0.7314 | -129.6896 | -1.7523 | 5.345 | 1.5297 | -3.7058 | -2.2001 | 3.9552 |  | 2.4441 | -0.1962 | 4.0078 | 3.3641 | 3.3424 | 1.0624 | 10.759 | 14.221 | 14.8532 | 11.0829 | 0.0003 | -0.0028 | 0.0008 | 0.0038 | 0.0008 | -0.0008 | 0.005 | -0.0068 | -0.0089 | -360.1681 | 17.4213 | -360.5312 | 17.6985 | -360.8512 | 18.1502 | -360.8358 | 17.5096 | -352.6598 | 18.7436 | -352.746 | 16.8751
12:20 | 3619 | 37.6994 | 200.8472 | 447.8673 | 453.083 | -16.9868 | -42.6315 | 9.8868 | 6.6794 | 1.0527 | -0.9278 | 2.1904 | -1.7074 | 10.3601 | 3.3603 | 0.6088 | 0.656 | 0.9613 | 0.7325 | -129.6995 | -1.7612 | 5.421 | 1.5295 | -3.6423 | -2.0162 | 4.0039 |  | 2.5084 | -0.1613 | 4.0106 | 3.3624 | 3.3457 | 1.0617 | 10.7441 | 14.2346 | 14.8075 | 11.0685 | -0.0005 | -0.0028 | 0.001 | 0.004 | 0.0007 | -0.0004 | 0.0012 | -0.0103 | 0.0178 | -360.1219 | 17.3761 | -360.4512 | 17.6492 | -360.7897 | 18.1687 | -360.8358 | 17.5034 | -352.6013 | 18.6902 | -352.6383 | 16.8566
12:20 | 3620 | 37.6659 | 200.8175 | 447.914 | 453.0555 | -16.962 | -42.6809 | 9.9035 | 6.7258 | 1.0625 | -0.9617 | 2.1547 | -1.694 | 10.4245 | 3.4124 | 0.6086 | 0.6543 | 0.961 | 0.7315 | -129.5151 | -1.7559 | 5.3901 | 1.6026 | -3.7457 | -2.0987 | 3.9211 |  | 2.4869 | -0.1879 | 4.0091 | 3.3643 | 3.3436 | 1.061 | 10.7314 | 14.2333 | 14.782 | 11.062 | 0.0002 | -0.0025 | 0.0005 | 0.0036 | 0.001 | -0.0007 | 0.0181 | -0.0015 | -0.0104 | -360.1896 | 17.4028 | -360.4296 | 17.6369 | -360.7804 | 18.1563 | -360.882 | 17.5383 | -352.6537 | 18.7148 | -352.6321 | 16.8176
12:20 | 3621 | 37.7755 | 200.8047 | 447.8771 | 453.0252 | -16.9075 | -42.7153 | 9.9069 | 6.8051 | 1.0005 | -1.0022 | 2.1347 | -1.6818 | 10.3684 | 3.3822 | 0.6098 | 0.6527 | 0.9615 | 0.7308 | -129.548 | -1.7757 | 5.4622 | 1.4799 | -3.7522 | -2.0959 | 3.9523 |  | 2.5 | -0.1913 | 4.0094 | 3.3676 | 3.3467 | 1.0614 | 10.7382 | 14.2349 | 14.8097 | 11.0677 | 0.0001 | -0.003 | 0.0012 | 0.0041 | 0.0005 | -0.0006 | 0.001 | -0.009 | -0.0122 | -360.245 | 17.448 | -360.5435 | 17.6738 | -360.8266 | 18.1604 | -360.8604 | 17.528 | -352.7183 | 18.7579 | -352.7275 | 16.8628
12:20 | 3622 | 37.802 | 200.8534 | 447.8721 | 453.0137 | -16.8815 | -42.6764 | 9.9645 | 6.7144 | 1.0101 | -0.9283 | 2.148 | -1.6806 | 10.4644 | 3.4164 | 0.6106 | 0.6543 | 0.9648 | 0.7319 | -129.536 | -1.6723 | 5.4796 | 1.4833 | -3.7285 | -2.1135 | 3.9156 |  | 2.4382 | -0.1997 | 4.0101 | 3.3619 | 3.3396 | 1.0623 | 10.7614 | 14.2406 | 14.8549 | 11.0796 | -0.0004 | -0.0029 | 0.0008 | 0.0037 | 0.0009 | -0.0009 | 0.0154 | -0.0028 | -0.0197 | -360.1065 | 17.3925 | -360.4789 | 17.6861 | -360.8604 | 18.1543 | -360.8604 | 17.5055 | -352.6321 | 18.723 | -352.6967 | 16.8669
12:20 | 3623 | 37.8372 | 200.8549 | 447.9686 | 453.1642 | -16.9141 | -42.5935 | 9.9951 | 6.8008 | 0.9501 | -0.9014 | 2.2057 | -1.6623 | 10.4086 | 3.4363 | 0.6094 | 0.6526 | 0.963 | 0.7299 | -129.5474 | -1.76 | 5.4856 | 1.4425 | -3.7571 | -2.1613 | 3.983 |  | 2.4905 | -0.3011 | 4.0077 | 3.3636 | 3.3445 | 1.062 | 10.7301 | 14.2383 | 14.8359 | 11.0944 | -0.0001 | -0.0024 | 0.0006 | 0.0039 | 0.0009 | -0.0002 | 0.0074 | -0.0132 | -0.008 | -360.1496 | 17.372 | -360.3958 | 17.6328 | -360.7804 | 18.1584 | -360.8543 | 17.526 | -352.6044 | 18.6779 | -352.6044 | 16.8217
12:20 | 3624 | 37.8602 | 200.7721 | 447.9059 | 453.1395 | -16.973 | -42.6429 | 9.8986 | 6.7473 | 0.8672 | -0.8909 | 2.2612 | -1.5463 | 10.4489 | 3.4857 | 0.6088 | 0.6539 | 0.9601 | 0.731 | -129.5795 | -1.6669 | 5.4115 | 1.6161 | -3.6079 | -2.1006 | 4.0429 |  | 2.579 | -0.2362 | 4.0087 | 3.3659 | 3.3446 | 1.0622 | 10.7417 | 14.2499 | 14.8185 | 11.0771 | -0.0001 | -0.0027 | 0.0006 | 0.0037 | 0.0011 | -0.0005 | 0.0129 | -0.0025 | -0.011 | -360.2388 | 17.4192 | -360.4604 | 17.6266 | -360.7743 | 18.1481 | -360.8635 | 17.5424 | -352.7183 | 18.7312 | -352.6567 | 16.8176
12:20 | 3625 | 37.8155 | 200.6894 | 447.8935 | 453.1303 | -16.9297 | -42.743 | 10.0206 | 6.7894 | 0.9011 | -0.9562 | 2.1925 | -1.5898 | 10.507 | 3.5468 | 0.6091 | 0.6526 | 0.9596 | 0.7322 | -129.5584 | -1.6589 | 5.4521 | 1.6789 | -3.5838 | -2.1109 | 4.0411 |  | 2.5311 | -0.1371 | 4.0091 | 3.3648 | 3.3467 | 1.0625 | 10.7476 | 14.2727 | 14.8106 | 11.0663 | 0 | -0.0031 | 0 | 0.0033 | 0.0005 | 0.0001 | 0.0029 | -0.0081 | -0.0032 | -360.2235 | 17.4397 | -360.5312 | 17.68 | -360.8574 | 18.1625 | -360.8604 | 17.528 | -352.6783 | 18.7641 | -352.749 | 16.8546
12:20 | 3626 | 37.8634 | 200.7704 | 447.9303 | 453.1833 | -16.9671 | -42.7678 | 10.0694 | 6.7775 | 0.8546 | -0.9528 | 2.1635 | -1.5801 | 10.4643 | 3.472 | 0.6094 | 0.6546 | 0.9613 | 0.7333 | -129.6049 | -1.6292 | 5.4731 | 1.6389 | -3.6092 | -2.0791 | 4.0494 |  | 2.4939 | -0.1614 | 4.0095 | 3.3658 | 3.3457 | 1.0619 | 10.729 | 14.237 | 14.8334 | 11.0764 | -0.0001 | -0.0033 | 0.0004 | 0.0037 | 0.0006 | -0.0007 | -0.0003 | -0.0032 | -0.0081 | -360.1281 | 17.3761 | -360.4419 | 17.6574 | -360.8389 | 18.1707 | -360.882 | 17.5034 | -352.6044 | 18.721 | -352.6752 | 16.8669
12:20 | 3627 | 37.7929 | 200.7693 | 447.9426 | 453.1009 | -16.9988 | -42.802 | 9.9941 | 6.7664 | 0.8963 | -1.0134 | 2.1673 | -1.6099 | 10.4339 | 3.4856 | 0.6098 | 0.6508 | 0.9624 | 0.7323 | -129.5585 | -1.6471 | 5.4669 | 1.6647 | -3.6485 | -2.0525 | 4.0313 |  | 2.4818 | -0.1077 | 4.0092 | 3.3633 | 3.346 | 1.0619 | 10.7695 | 14.2254 | 14.8219 | 11.0764 | -0.0001 | -0.0024 | 0.0009 | 0.0041 | 0.0009 | -0.0005 | 0.0081 | -0.0056 | 0.0028 | -360.1281 | 17.3782 | -360.3835 | 17.6102 | -360.7712 | 18.1645 | -360.8912 | 17.528 | -352.6444 | 18.6902 | -352.6044 | 16.8176
12:20 | 3628 | 37.848 | 200.6914 | 447.8999 | 453.0216 | -16.975 | -42.8071 | 10 | 6.7761 | 0.9048 | -0.9616 | 2.2221 | -1.6868 | 10.4637 | 3.5088 | 0.6105 | 0.6516 | 0.9574 | 0.7337 | -129.5636 | -1.5378 | 5.4795 | 1.6955 | -3.6814 | -2.0064 | 4.0653 |  | 2.4269 | -0.108 | 4.0116 | 3.3658 | 3.3439 | 1.0632 | 10.7522 | 14.2486 | 14.8045 | 11.0706 | -0.0001 | -0.0027 | 0.0008 | 0.0036 | 0.0007 | -0.0004 | 0.0101 | 0.0051 | -0.016 | -360.2296 | 17.409 | -360.4573 | 17.6348 | -360.762 | 18.144 | -360.8789 | 17.5321 | -352.6844 | 18.7333 | -352.6813 | 16.8217
12:20 | 3629 | 37.7617 | 200.6548 | 447.727 | 453.061 | -17.0328 | -42.8205 | 9.9953 | 6.7768 | 0.9247 | -0.9578 | 2.1167 | -1.6557 | 10.4234 | 3.4886 | 0.6092 | 0.6543 | 0.962 | 0.7334 | -129.5881 | -1.6223 | 5.5127 | 1.654 | -3.607 | -1.9792 | 4.057 |  | 2.4643 | -0.1321 | 4.0098 | 3.3672 | 3.3424 | 1.0615 | 10.7383 | 14.2635 | 14.8075 | 11.08 | -0.0003 | -0.0036 | 0.0012 | 0.0042 | 0.001 | -0.0005 | 0.0165 | -0.0193 | -0.0237 | -360.1681 | 17.4254 | -360.5219 | 17.6841 | -360.885 | 18.1584 | -360.8543 | 17.5239 | -352.6567 | 18.7395 | -352.7337 | 16.8731
12:20 | 3630 | 37.802 | 200.7916 | 447.9359 | 453.0736 | -16.9663 | -42.682 | 9.9385 | 6.8251 | 0.8458 | -1.0911 | 2.1648 | -1.6339 | 10.4794 | 3.4014 | 0.6085 | 0.6545 | 0.9621 | 0.732 | -129.5799 | -1.6881 | 5.4273 | 1.6687 | -3.6601 | -2.1259 | 4.0533 |  | 2.4769 | -0.0993 | 4.0089 | 3.3631 | 3.3434 | 1.0626 | 10.7716 | 14.2573 | 14.8752 | 11.0886 | 0.0003 | -0.0026 | 0.0012 | 0.0042 | 0.0008 | -0.0001 | 0.0169 | -0.0056 | -0.0043 | -360.1096 | 17.3782 | -360.4481 | 17.6615 | -360.8666 | 18.1912 | -360.9281 | 17.5116 | -352.6537 | 18.7189 | -352.666 | 16.8648
12:20 | 3631 | 37.8097 | 200.7159 | 447.8077 | 453.0228 | -17.0327 | -42.7316 | 10.0946 | 6.8169 | 0.8951 | -0.9529 | 2.1744 | -1.6862 | 10.4138 | 3.2876 | 0.6096 | 0.6537 | 0.9606 | 0.7335 | -129.5159 | -1.6025 | 5.4541 | 1.6711 | -3.6218 | -2.0144 | 4.0792 |  | 2.5305 | -0.0659 | 4.0101 | 3.3659 | 3.3427 | 1.0622 | 10.7648 | 14.2557 | 14.8532 | 11.1175 | -0.0007 | -0.0032 | 0.0002 | 0.0033 | 0.0011 | -0.0011 | 0.0075 | -0.0047 | -0.0206 | -360.1558 | 17.3679 | -360.3927 | 17.6266 | -360.7558 | 18.1604 | -360.885 | 17.5178 | -352.6844 | 18.6984 | -352.629 | 16.8238
12:20 | 3632 | 37.7943 | 200.7887 | 447.8886 | 453.1079 | -17.0521 | -42.7669 | 9.9658 | 6.8306 | 0.8653 | -0.8971 | 2.233 | -1.6905 | 10.3632 | 3.3455 | 0.6094 | 0.6545 | 0.959 | 0.7324 | -129.5705 | -1.6341 | 5.2857 | 1.636 | -3.7006 | -1.9656 | 4.0972 |  | 2.5014 | -0.1653 | 4.011 | 3.3638 | 3.3443 | 1.0612 | 10.7579 | 14.2603 | 14.8345 | 11.0587 | -0.0004 | -0.0026 | 0.0005 | 0.0037 | 0.0003 | -0.0003 | 0.0036 | -0.0006 | -0.0181 | -360.2204 | 17.4151 | -360.4942 | 17.643 | -360.7927 | 18.1317 | -360.8389 | 17.5096 | -352.6598 | 18.7436 | -352.6629 | 16.834
12:20 | 3633 | 37.8137 | 200.754 | 447.9225 | 453.0357 | -16.9584 | -42.6599 | 10.0071 | 6.8398 | 0.7744 | -0.9254 | 2.2832 | -1.7021 | 10.3208 | 3.3971 | 0.6097 | 0.6532 | 0.9596 | 0.7305 | -129.4989 | -1.5801 | 5.3244 | 1.6734 | -3.6165 | -1.9804 | 4.1153 |  | 2.5589 | -0.035 | 4.0095 | 3.3666 | 3.3423 | 1.0615 | 10.7325 | 14.2232 | 14.8086 | 11.0623 | 0.0002 | -0.0029 | 0.0001 | 0.0033 | 0.0009 | -0.0006 | 0.0062 | -0.0041 | -0.0178 | -360.1896 | 17.4172 | -360.5158 | 17.6964 | -360.9066 | 18.1666 | -360.8881 | 17.5096 | -352.6537 | 18.7456 | -352.7121 | 16.8772
12:20 | 3634 | 37.8102 | 200.8134 | 447.957 | 453.1185 | -16.9499 | -42.5417 | 9.9211 | 6.8668 | 0.7136 | -0.8532 | 2.2675 | -1.6852 | 10.3496 | 3.5044 | 0.61 | 0.6503 | 0.9562 | 0.7305 | -129.5503 | -1.5679 | 5.4147 | 1.64 | -3.5627 | -2.0364 | 4.0212 |  | 2.4976 | -0.0535 | 4.0095 | 3.364 | 3.3456 | 1.0609 | 10.7418 | 14.2149 | 14.7932 | 11.049 | -0.0001 | -0.003 | 0.0008 | 0.0041 | 0.0004 | -0.0001 | 0.0186 | -0.0162 | -0.0123 | -360.1342 | 17.3905 | -360.4727 | 17.6697 | -360.8635 | 18.1769 | -360.8974 | 17.5178 | -352.6475 | 18.721 | -352.6721 | 16.8628
12:20 | 3635 | 37.8462 | 200.8444 | 447.9371 | 453.1739 | -17.0095 | -42.563 | 9.7601 | 6.8256 | 0.5945 | -0.9635 | 2.2479 | -1.7549 | 10.2836 | 3.4359 | 0.6096 | 0.6533 | 0.9611 | 0.7318 | -129.4572 | -1.656 | 5.3556 | 1.6438 | -3.5799 | -2.1047 | 4.0649 |  | 2.4279 | -0.1755 | 4.0087 | 3.3609 | 3.3457 | 1.061 | 10.6816 | 14.201 | 14.75 | 11.0295 | 0 | -0.0028 | 0.0009 | 0.0039 | 0.0009 | -0.0006 | -0.0022 | -0.0131 | 0.002 | -360.1711 | 17.3966 | -360.4296 | 17.6245 | -360.7712 | 18.1461 | -360.8389 | 17.528 | -352.6721 | 18.7045 | -352.626 | 16.8156
12:20 | 3636 | 37.9163 | 200.8223 | 447.9007 | 453.1773 | -17.0653 | -42.7331 | 9.7314 | 6.8192 | 0.6335 | -0.8817 | 2.301 | -1.6931 | 10.3608 | 3.5256 | 0.6086 | 0.6533 | 0.9622 | 0.7322 | -129.4859 | -1.6045 | 5.3886 | 1.622 | -3.5041 | -2.0391 | 4.1287 |  | 2.4731 | -0.158 | 4.0092 | 3.3654 | 3.342 | 1.0602 | 10.7267 | 14.2637 | 14.8202 | 11.0623 | -0.0002 | -0.0027 | 0.0009 | 0.0039 | 0.0006 | -0.0004 | 0.0061 | -0.0106 | -0.0059 | -360.1988 | 17.45 | -360.4942 | 17.6656 | -360.8204 | 18.1358 | -360.842 | 17.5178 | -352.6537 | 18.7436 | -352.6937 | 16.8443
12:20 | 3637 | 37.881 | 200.8494 | 447.882 | 453.1995 | -16.9974 | -42.6354 | 9.7922 | 6.8944 | 0.6619 | -0.9745 | 2.2123 | -1.6585 | 10.4077 | 3.51 | 0.6092 | 0.6497 | 0.9641 | 0.7324 | -129.4939 | -1.5038 | 5.3513 | 1.605 | -3.525 | -1.9815 | 4.09 |  | 2.5343 | -0.1335 | 4.009 | 3.3626 | 3.3438 | 1.0622 | 10.7498 | 14.2465 | 14.8212 | 11.0793 | 0 | -0.0025 | 0.0008 | 0.0039 | 0.0012 | -0.0003 | -0.0048 | -0.008 | -0.0005 | -360.1958 | 17.4213 | -360.5219 | 17.6944 | -360.8943 | 18.1666 | -360.8758 | 17.5301 | -352.6629 | 18.7456 | -352.7152 | 16.8751
12:20 | 3638 | 37.9171 | 200.7814 | 447.9413 | 453.2171 | -16.9917 | -42.5589 | 9.8291 | 6.9068 | 0.6545 | -0.8589 | 2.2488 | -1.7015 | 10.4036 | 3.5744 | 0.608 | 0.6523 | 0.9605 | 0.7317 | -129.569 | -1.5939 | 5.3268 | 1.62 | -3.5903 | -2.043 | 4.0078 |  | 2.4239 | -0.1654 | 4.0093 | 3.3607 | 3.3432 | 1.0615 | 10.7578 | 14.2373 | 14.8414 | 11.1103 | 0.0004 | -0.0029 | 0.001 | 0.0039 | 0.0008 | -0.0005 | -0.0021 | -0.0171 | -0.0213 | -360.1219 | 17.372 | -360.3958 | 17.6471 | -360.7897 | 18.1645 | -360.8727 | 17.5198 | -352.6444 | 18.7045 | -352.626 | 16.8484
12:20 | 3639 | 37.8693 | 200.8287 | 448.0261 | 453.1773 | -17.0665 | -42.6523 | 9.7404 | 6.7974 | 0.7216 | -0.9567 | 2.2173 | -1.6785 | 10.4232 | 3.5636 | 0.6095 | 0.652 | 0.9599 | 0.733 | -129.5102 | -1.5661 | 5.3466 | 1.6032 | -3.6572 | -2.0359 | 4.0486 |  | 2.4938 | -0.1705 | 4.0093 | 3.3618 | 3.3426 | 1.0616 | 10.759 | 14.2615 | 14.8243 | 11.1233 | -0.0001 | -0.0023 | 0.0001 | 0.0033 | 0.0004 | -0.0006 | 0.0055 | -0.0192 | -0.0174 | -360.205 | 17.3905 | -360.4358 | 17.6184 | -360.7435 | 18.1399 | -360.8727 | 17.5321 | -352.669 | 18.7169 | -352.6352 | 16.8156
12:20 | 3640 | 37.8273 | 200.8594 | 448.034 | 453.213 | -17.0717 | -42.6613 | 9.7916 | 6.7559 | 0.8014 | -0.9145 | 2.3021 | -1.6572 | 10.324 | 3.4469 | 0.6085 | 0.6561 | 0.962 | 0.7327 | -129.5557 | -1.6162 | 5.4651 | 1.6031 | -3.6012 | -2.0374 | 4.0944 |  | 2.4712 | -0.1894 | 4.0087 | 3.3606 | 3.3451 | 1.0623 | 10.7728 | 14.2699 | 14.8407 | 11.1074 | -0.0003 | -0.0024 | 0.001 | 0.004 | 0.001 | -0.0008 | -0.0082 | -0.0069 | -0.0174 | -360.1681 | 17.4377 | -360.4912 | 17.6636 | -360.8358 | 18.1604 | -360.8543 | 17.5383 | -352.706 | 18.7518 | -352.6875 | 16.8505
12:20 | 3641 | 37.8546 | 200.7937 | 448.0438 | 453.2615 | -17.1333 | -42.7276 | 9.7922 | 6.7511 | 0.8519 | -0.8222 | 2.2877 | -1.6921 | 10.379 | 3.3452 | 0.6092 | 0.6543 | 0.9575 | 0.7317 | -129.56 | -1.657 | 5.4466 | 1.5588 | -3.6745 | -2.0338 | 4.0104 |  | 2.3632 | -0.2072 | 4.0095 | 3.3651 | 3.3429 | 1.0603 | 10.7336 | 14.2533 | 14.81 | 11.0923 | 0.0002 | -0.0029 | 0.0005 | 0.0042 | 0.0008 | -0.0002 | 0.0148 | -0.0075 | -0.0114 | -360.1435 | 17.3966 | -360.5096 | 17.6759 | -360.845 | 18.1707 | -360.8697 | 17.5157 | -352.6352 | 18.7312 | -352.7275 | 16.8772
12:20 | 3642 | 37.7666 | 200.8119 | 447.9386 | 453.2254 | -17.1618 | -42.7172 | 9.7778 | 6.6517 | 0.8249 | -1.0633 | 2.244 | -1.7039 | 10.4983 | 3.4181 | 0.61 | 0.6533 | 0.9622 | 0.7329 | -129.5401 | -1.5435 | 5.4907 | 1.6154 | -3.6819 | -2.0568 | 4.0255 |  | 2.4793 | -0.1644 | 4.0102 | 3.3595 | 3.3438 | 1.0614 | 10.7174 | 14.237 | 14.8277 | 11.0764 | 0.0004 | -0.003 | 0.0004 | 0.0036 | 0.0009 | -0.001 | 0.0033 | 0.0002 | -0.0205 | -360.1311 | 17.3802 | -360.3989 | 17.6328 | -360.7989 | 18.1707 | -360.8881 | 17.5178 | -352.626 | 18.6861 | -352.5952 | 16.8238
12:20 | 3643 | 37.7906 | 200.8106 | 447.8817 | 453.1579 | -17.0814 | -42.6299 | 9.7736 | 6.6538 | 0.8143 | -1.1222 | 2.1267 | -1.7745 | 10.4311 | 3.2863 | 0.6085 | 0.6526 | 0.9613 | 0.7342 | -129.5762 | -1.4494 | 5.5091 | 1.6098 | -3.6091 | -1.9974 | 4.0397 |  | 2.4841 | -0.1765 | 4.0093 | 3.3647 | 3.3441 | 1.061 | 10.7371 | 14.2163 | 14.8188 | 11.0728 | -0.0001 | -0.0027 | 0.0008 | 0.0041 | 0.0006 | -0.0002 | 0.0141 | -0.0094 | -0.0149 | -360.1588 | 17.3925 | -360.4481 | 17.6348 | -360.7835 | 18.1604 | -360.8974 | 17.526 | -352.6413 | 18.7189 | -352.6537 | 16.8238
12:20 | 3644 | 37.8424 | 200.8183 | 447.8308 | 453.1488 | -17.1291 | -42.6792 | 9.7972 | 6.6344 | 0.7619 | -1.0985 | 2.1604 | -1.7396 | 10.4862 | 3.3129 | 0.6108 | 0.6513 | 0.9631 | 0.7335 | -129.5581 | -1.4764 | 5.5051 | 1.6181 | -3.6113 | -1.9651 | 4.0648 |  | 2.3713 | -0.1973 | 4.0091 | 3.3646 | 3.3424 | 1.0608 | 10.7394 | 14.236 | 14.8216 | 11.1096 | -0.0003 | -0.0027 | 0.001 | 0.0038 | 0.0014 | -0.0005 | 0.0145 | -0.0115 | -0.0103 | -360.2204 | 17.4295 | -360.5219 | 17.6841 | -360.8543 | 18.1604 | -360.8666 | 17.5363 | -352.6721 | 18.7415 | -352.7121 | 16.8628
12:20 | 3645 | 37.8984 | 200.8755 | 447.9824 | 453.1749 | -17.1447 | -42.7915 | 9.8465 | 6.6254 | 0.8925 | -0.8971 | 2.2917 | -1.6891 | 10.4808 | 3.4476 | 0.6094 | 0.6494 | 0.9597 | 0.7335 | -129.5531 | -1.5048 | 5.4659 | 1.6868 | -3.7063 | -1.9435 | 4.0347 |  | 2.436 | -0.2909 | 4.0095 | 3.3641 | 3.338 | 1.061 | 10.7291 | 14.2078 | 14.8255 | 11.054 | -0.0001 | -0.0033 | 0.0006 | 0.0038 | 0.0003 | -0.0007 | 0.0121 | -0.0079 | -0.0099 | -360.1096 | 17.3946 | -360.485 | 17.6656 | -360.8512 | 18.183 | -360.8543 | 17.5116 | -352.6383 | 18.7169 | -352.6783 | 16.8566
12:20 | 3646 | 37.9018 | 200.8127 | 448.0199 | 453.2432 | -17.0812 | -42.7364 | 9.8535 | 6.6394 | 0.9764 | -0.8379 | 2.2505 | -1.7004 | 10.404 | 3.4239 | 0.6103 | 0.6535 | 0.9634 | 0.7327 | -129.5024 | -1.5255 | 5.4976 | 1.7117 | -3.5939 | -1.9517 | 3.9871 |  | 2.444 | -0.2383 | 4.0091 | 3.3664 | 3.3407 | 1.0611 | 10.7474 | 14.2558 | 14.8138 | 11.0941 | 0.0002 | -0.0031 | 0.0011 | 0.004 | 0.0014 | -0.0002 | 0.0168 | 0.0009 | -0.0243 | -360.1281 | 17.3679 | -360.4142 | 17.6369 | -360.7897 | 18.1502 | -360.8727 | 17.5219 | -352.6198 | 18.7045 | -352.5983 | 16.8423
12:20 | 3647 | 37.8716 | 200.8756 | 447.9076 | 453.1897 | -17.0183 | -42.6851 | 9.8881 | 6.6428 | 0.916 | -0.8007 | 2.3374 | -1.6801 | 10.4874 | 3.4509 | 0.6099 | 0.6492 | 0.9582 | 0.7324 | -129.4608 | -1.5626 | 5.6215 | 1.7317 | -3.5958 | -1.9805 | 4.0502 |  | 2.4329 | -0.2635 | 4.0096 | 3.3671 | 3.345 | 1.0621 | 10.7303 | 14.2379 | 14.8153 | 11.0667 | -0.0002 | -0.0028 | 0.0003 | 0.0035 | 0.0003 | -0.0008 | 0.0162 | 0.0022 | 0.0044 | -360.205 | 17.4315 | -360.4789 | 17.6574 | -360.7927 | 18.1563 | -360.8727 | 17.526 | -352.6352 | 18.7415 | -352.6444 | 16.8299
12:21 | 3648 | 37.8595 | 200.8483 | 447.9756 | 453.1427 | -17.044 | -42.6556 | 9.8538 | 6.6965 | 1.0243 | -0.7754 | 2.3057 | -1.8075 | 10.4705 | 3.4249 | 0.6101 | 0.6534 | 0.9581 | 0.7322 | -129.4928 | -1.4617 | 5.5426 | 1.6137 | -3.6787 | -1.9423 | 4.0084 |  | 2.5209 | -0.1837 | 4.0106 | 3.3654 | 3.3436 | 1.0617 | 10.7579 | 14.237 | 14.8219 | 11.0995 | -0.0006 | -0.003 | 0.0007 | 0.0039 | 0.0014 | -0.0001 | 0.0068 | -0.01 | -0.028 | -360.1865 | 17.4131 | -360.525 | 17.6923 | -360.8481 | 18.1625 | -360.8604 | 17.5239 | -352.6813 | 18.7436 | -352.7275 | 16.8669
12:21 | 3649 | 37.8945 | 200.8713 | 447.9995 | 453.186 | -17.0609 | -42.7104 | 9.789 | 6.5659 | 0.9455 | -0.7933 | 2.249 | -1.8386 | 10.4109 | 3.3839 | 0.6095 | 0.6533 | 0.9627 | 0.7323 | -129.4586 | -1.5572 | 5.4845 | 1.6656 | -3.6463 | -2.0101 | 4.0994 |  | 2.4731 | -0.1444 | 4.0086 | 3.3673 | 3.3409 | 1.0603 | 10.759 | 14.2616 | 14.808 | 11.0883 | 0.0001 | -0.0027 | 0.0007 | 0.0039 | 0.0007 | -0.0006 | 0.0351 | -0.0008 | -0.0057 | -360.1773 | 17.3925 | -360.4481 | 17.6574 | -360.8327 | 18.1707 | -360.8697 | 17.5055 | -352.626 | 18.7169 | -352.6752 | 16.8525
12:21 | 3650 | 37.9417 | 200.8047 | 448.0918 | 453.251 | -16.9757 | -42.6833 | 9.8209 | 6.6254 | 0.9787 | -0.6464 | 2.2492 | -1.6987 | 10.5527 | 3.4207 | 0.6093 | 0.6546 | 0.9651 | 0.7324 | -129.4808 | -1.5611 | 5.4664 | 1.6628 | -3.6957 | -2.1468 | 3.9873 |  | 2.5258 | -0.1491 | 4.0094 | 3.3655 | 3.3441 | 1.0621 | 10.751 | 14.23 | 14.8205 | 11.0811 | -0.0001 | -0.0033 | 0.001 | 0.0043 | 0.0004 | -0.0005 | 0.006 | 0.0001 | -0.0062 | -360.1927 | 17.3884 | -360.4512 | 17.6369 | -360.7989 | 18.144 | -360.8697 | 17.5219 | -352.6198 | 18.7189 | -352.6167 | 16.834
12:21 | 3651 | 37.9499 | 200.8238 | 447.8379 | 453.1904 | -16.9373 | -42.7269 | 9.8557 | 6.7154 | 1.048 | -0.7399 | 2.26 | -1.753 | 10.4888 | 3.4412 | 0.6077 | 0.6487 | 0.9585 | 0.7317 | -129.4386 | -1.5382 | 5.4157 | 1.6723 | -3.7014 | -2.0482 | 3.9701 |  | 2.4395 | -0.1603 | 4.0103 | 3.3648 | 3.3455 | 1.0597 | 10.737 | 14.228 | 14.8488 | 11.0955 | 0.0003 | -0.0029 | 0.0012 | 0.0043 | 0.0011 | -0.0008 | -0.0043 | -0.0108 | -0.0308 | -360.1988 | 17.4192 | -360.485 | 17.6533 | -360.7927 | 18.1625 | -360.8666 | 17.5239 | -352.6629 | 18.7415 | -352.6813 | 16.8402
12:21 | 3652 | 37.9336 | 200.8323 | 447.9037 | 453.2284 | -16.9496 | -42.6506 | 9.9393 | 6.7986 | 1.1022 | -0.7177 | 2.342 | -1.6952 | 10.4988 | 3.4813 | 0.6094 | 0.6517 | 0.9605 | 0.7331 | -129.4604 | -1.529 | 5.4386 | 1.7555 | -3.5682 | -1.9296 | 4.058 |  | 2.4288 | -0.1779 | 4.01 | 3.3662 | 3.3433 | 1.0611 | 10.7671 | 14.2523 | 14.856 | 11.0966 | -0.0002 | -0.0028 | 0.001 | 0.0037 | 0.0005 | -0.0001 | 0.0188 | 0.0079 | -0.0064 | -360.1711 | 17.409 | -360.5066 | 17.682 | -360.8297 | 18.1789 | -360.9004 | 17.5342 | -352.6783 | 18.7477 | -352.6998 | 16.8546
12:21 | 3653 | 37.9276 | 200.8402 | 448.0066 | 453.2155 | -17.0297 | -42.576 | 9.8523 | 6.7426 | 1.0139 | -0.7502 | 2.3139 | -1.6225 | 10.4725 | 3.5545 | 0.6105 | 0.6511 | 0.9587 | 0.7332 | -129.3889 | -1.3914 | 5.4678 | 1.714 | -3.5741 | -1.9192 | 3.9964 |  | 2.4569 | -0.1179 | 4.0083 | 3.3631 | 3.3438 | 1.0617 | 10.7463 | 14.2487 | 14.8229 | 11.0587 | 0 | -0.0025 | 0.0009 | 0.0041 | 0.0007 | -0.0006 | -0.0007 | -0.0076 | 0.0117 | -360.1804 | 17.4048 | -360.4635 | 17.6471 | -360.8112 | 18.1625 | -360.8943 | 17.5239 | -352.6475 | 18.7333 | -352.669 | 16.8402
12:21 | 3654 | 37.8667 | 200.8212 | 447.9019 | 453.1884 | -17.045 | -42.5624 | 9.9142 | 6.6639 | 0.9784 | -0.7102 | 2.2816 | -1.7384 | 10.461 | 3.5226 | 0.6085 | 0.6519 | 0.9592 | 0.7306 | -129.4339 | -1.5332 | 5.5512 | 1.6341 | -3.5086 | -1.8652 | 4.0451 |  | 2.4459 | -0.1453 | 4.0092 | 3.3646 | 3.3437 | 1.0611 | 10.7231 | 14.2315 | 14.8124 | 11.0756 | 0.0004 | -0.0031 | 0.001 | 0.0038 | 0.0004 | -0.0006 | -0.0016 | -0.0009 | -0.0235 | -360.1742 | 17.3864 | -360.4327 | 17.6307 | -360.7589 | 18.1461 | -360.8604 | 17.5178 | -352.6229 | 18.7087 | -352.629 | 16.8423
12:21 | 3655 | 37.9303 | 200.9363 | 447.8545 | 453.2046 | -17.0557 | -42.5844 | 9.9013 | 6.6954 | 0.9929 | -0.8407 | 2.3269 | -1.7801 | 10.4388 | 3.4338 | 0.6087 | 0.653 | 0.9631 | 0.7311 | -129.4605 | -1.5503 | 5.5391 | 1.5434 | -3.4887 | -1.9146 | 4.0381 |  | 2.4698 | -0.055 | 4.0091 | 3.3623 | 3.3435 | 1.0602 | 10.7071 | 14.2438 | 14.7643 | 11.049 | -0.0003 | -0.0034 | 0.0003 | 0.0035 | 0.0011 | -0.0006 | 0.0174 | -0.0225 | -0.0075 | -360.1681 | 17.4131 | -360.4604 | 17.6369 | -360.7958 | 18.1645 | -360.8389 | 17.5075 | -352.6167 | 18.7292 | -352.6752 | 16.834
12:21 | 3656 | 37.9738 | 200.9011 | 447.8804 | 453.147 | -17.0523 | -42.6278 | 9.9787 | 6.6915 | 0.9862 | -0.768 | 2.3336 | -1.7775 | 10.4665 | 3.5183 | 0.6098 | 0.6531 | 0.9635 | 0.7309 | -129.4247 | -1.3769 | 5.474 | 1.6604 | -3.5025 | -1.9505 | 4.0378 |  | 2.5643 | -0.092 | 4.0088 | 3.3647 | 3.3423 | 1.0612 | 10.7382 | 14.2291 | 14.8212 | 11.0504 | -0.0002 | -0.0024 | 0.0003 | 0.0042 | 0.0006 | -0.0001 | 0.0149 | -0.012 | -0.0055 | -360.1865 | 17.411 | -360.5189 | 17.6882 | -360.8358 | 18.1769 | -360.9097 | 17.5342 | -352.6537 | 18.7436 | -352.6875 | 16.8505
12:21 | 3657 | 38.0144 | 200.8476 | 447.8822 | 453.1848 | -17.0929 | -42.5451 | 9.9763 | 6.7516 | 0.964 | -0.8114 | 2.3314 | -1.6442 | 10.479 | 3.4746 | 0.6075 | 0.6516 | 0.9587 | 0.7294 | -129.4008 | -1.2708 | 5.5156 | 1.5998 | -3.542 | -2.0138 | 4.0346 |  | 2.5189 | -0.1557 | 4.0082 | 3.3633 | 3.3439 | 1.061 | 10.7185 | 14.2499 | 14.8359 | 11.0829 | -0.0003 | -0.0028 | 0.0007 | 0.004 | 0.0006 | -0.0006 | 0.0034 | -0.0104 | -0.0141 | -360.1435 | 17.4007 | -360.4666 | 17.6574 | -360.8174 | 18.1748 | -360.8912 | 17.5239 | -352.709 | 18.7497 | -352.6844 | 16.834
12:21 | 3658 | 38.0391 | 200.9433 | 447.9192 | 453.141 | -16.9976 | -42.6331 | 9.9893 | 6.7071 | 1.0381 | -0.6673 | 2.3551 | -1.6998 | 10.4982 | 3.598 | 0.609 | 0.6503 | 0.9552 | 0.7312 | -129.4899 | -1.4521 | 5.5374 | 1.7048 | -3.4378 | -1.9567 | 4.1395 |  | 2.5002 | -0.0971 | 4.0095 | 3.3652 | 3.3416 | 1.0613 | 10.7487 | 14.245 | 14.8235 | 11.0963 | 0.0001 | -0.0032 | 0.0006 | 0.0039 | 0.0009 | -0.0001 | 0.0063 | -0.0102 | -0.0151 | -360.1681 | 17.3884 | -360.4389 | 17.6553 | -360.7712 | 18.1379 | -360.8266 | 17.5137 | -352.6321 | 18.721 | -352.629 | 16.8299
12:21 | 3659 | 38.001 | 200.8601 | 447.9428 | 453.0885 | -17.0252 | -42.564 | 10.0139 | 6.7489 | 1.1207 | -0.7917 | 2.342 | -1.6571 | 10.4478 | 3.5208 | 0.6097 | 0.6523 | 0.9563 | 0.7328 | -129.4392 | -1.4183 | 5.5321 | 1.6493 | -3.5465 | -2.0309 | 4.0828 |  | 2.4988 | -0.1106 | 4.0094 | 3.3644 | 3.3381 | 1.061 | 10.6932 | 14.201 | 14.8079 | 11.041 | 0.0002 | -0.0031 | 0.0005 | 0.0034 | 0.0005 | -0.0006 | 0.0314 | -0.0002 | -0.0031 | -360.1496 | 17.4131 | -360.4789 | 17.6677 | -360.8266 | 18.181 | -360.8635 | 17.5096 | -352.5952 | 18.7374 | -352.6967 | 16.8361
12:21 | 3660 | 37.9746 | 200.9254 | 448.0076 | 453.0627 | -16.9737 | -42.5889 | 9.9747 | 6.7772 | 1.0769 | -0.7076 | 2.4114 | -1.6217 | 10.4781 | 3.5521 | 0.6101 | 0.6561 | 0.9597 | 0.7314 | -129.4329 | -1.3631 | 5.6444 | 1.6303 | -3.5283 | -2.1469 | 4.1275 |  | 2.557 | -0.1354 | 4.0101 | 3.365 | 3.3455 | 1.0619 | 10.7694 | 14.2953 | 14.8829 | 11.1157 | -0.0005 | -0.0026 | 0.0008 | 0.0037 | 0.0008 | -0.0005 | 0.0217 | -0.0018 | -0.0187 | -360.2019 | 17.3987 | -360.4696 | 17.6902 | -360.8574 | 18.183 | -360.9004 | 17.5342 | -352.666 | 18.7333 | -352.6906 | 16.8566
12:21 | 3661 | 37.8919 | 200.8568 | 447.925 | 452.9958 | -17.0405 | -42.6384 | 9.9354 | 6.7543 | 1.0317 | -0.7508 | 2.3685 | -1.728 | 10.4367 | 3.4457 | 0.6106 | 0.6521 | 0.96 | 0.7316 | -129.4485 | -1.3625 | 5.6586 | 1.6217 | -3.5112 | -2.083 | 4.1049 |  | 2.5104 | -0.2374 | 4.0098 | 3.364 | 3.3443 | 1.062 | 10.7706 | 14.2674 | 14.8485 | 11.0594 | 0 | -0.0023 | 0.0008 | 0.0039 | 0.001 | 0 | 0.0178 | -0.0116 | -0.0073 | -360.165 | 17.4028 | -360.4512 | 17.6533 | -360.7897 | 18.1666 | -360.8912 | 17.526 | -352.6813 | 18.723 | -352.6598 | 16.8464
12:21 | 3662 | 37.9272 | 200.8523 | 447.9991 | 453.0496 | -16.9867 | -42.6747 | 9.9906 | 6.7886 | 0.9734 | -0.8061 | 2.3369 | -1.7066 | 10.3666 | 3.3768 | 0.6087 | 0.6541 | 0.9552 | 0.7315 | -129.4133 | -1.4883 | 5.5893 | 1.6527 | -3.6014 | -2.045 | 4.0195 |  | 2.4683 | -0.1789 | 4.0087 | 3.3655 | 3.3393 | 1.062 | 10.7498 | 14.2696 | 14.7981 | 11.0677 | 0.0001 | -0.0029 | 0.001 | 0.0036 | 0.0007 | -0.0012 | 0.0007 | 0.0046 | -0.0139 | -360.1342 | 17.3987 | -360.4512 | 17.6656 | -360.7897 | 18.142 | -360.8358 | 17.5096 | -352.666 | 18.723 | -352.6475 | 16.832
12:21 | 3663 | 37.928 | 200.8453 | 447.9758 | 452.9469 | -17.068 | -42.6487 | 9.9416 | 6.8712 | 0.9728 | -0.7696 | 2.3476 | -1.7188 | 10.455 | 3.5348 | 0.6094 | 0.6559 | 0.9573 | 0.7333 | -129.4701 | -1.4547 | 5.5585 | 1.5478 | -3.6009 | -2.0628 | 3.9913 |  | 2.5432 | -0.1601 | 4.0082 | 3.3645 | 3.3421 | 1.0616 | 10.7556 | 14.2812 | 14.827 | 11.0677 | 0.0002 | -0.0027 | 0.0007 | 0.0044 | 0.0007 | 0.0002 | 0.0093 | -0.011 | -0.0042 | -360.1804 | 17.4048 | -360.4789 | 17.6964 | -360.8512 | 18.1563 | -360.8481 | 17.5116 | -352.6352 | 18.7292 | -352.666 | 16.8607
12:21 | 3664 | 37.9494 | 200.8193 | 448.0181 | 453.0226 | -17.0462 | -42.6001 | 9.992 | 6.9552 | 0.9588 | -0.6858 | 2.3689 | -1.7092 | 10.4891 | 3.4804 | 0.6104 | 0.6551 | 0.958 | 0.7323 | -129.4017 | -1.403 | 5.6722 | 1.5506 | -3.5406 | -2.0101 | 4.0668 |  | 2.4789 | -0.1148 | 4.0083 | 3.3637 | 3.3404 | 1.061 | 10.7625 | 14.2419 | 14.8458 | 11.0515 | 0 | -0.003 | 0.0008 | 0.0041 | 0.0008 | -0.0008 | 0.0056 | -0.0112 | 0.0031 | -360.1773 | 17.4192 | -360.4758 | 17.6902 | -360.8512 | 18.2077 | -360.882 | 17.5137 | -352.6444 | 18.7374 | -352.6844 | 16.8607
12:21 | 3665 | 37.9423 | 200.9246 | 448.004 | 453.0355 | -17.0864 | -42.6283 | 9.9801 | 6.9022 | 0.9932 | -0.8934 | 2.4124 | -1.7017 | 10.5019 | 3.4732 | 0.6095 | 0.6551 | 0.9615 | 0.7323 | -129.4245 | -1.4716 | 5.5612 | 1.6557 | -3.5551 | -2.0297 | 3.984 |  | 2.4688 | -0.1874 | 4.0091 | 3.3622 | 3.3406 | 1.0613 | 10.7567 | 14.242 | 14.8295 | 11.0511 | 0.0001 | -0.002 | 0.0005 | 0.0037 | 0.0004 | -0.0002 | 0.0086 | -0.018 | -0.0182 | -360.165 | 17.4048 | -360.4235 | 17.6656 | -360.7989 | 18.1707 | -360.9097 | 17.5465 | -352.6352 | 18.7251 | -352.669 | 16.8381
12:21 | 3666 | 37.9563 | 200.8735 | 448.0387 | 453.1258 | -17.0302 | -42.6108 | 9.8611 | 6.8836 | 0.9678 | -0.8293 | 2.398 | -1.5998 | 10.4537 | 3.4607 | 0.6092 | 0.6522 | 0.9585 | 0.7325 | -129.4521 | -1.3376 | 5.6136 | 1.6379 | -3.5597 | -2.0271 | 4.085 |  | 2.5343 | -0.1221 | 4.0099 | 3.3614 | 3.3402 | 1.0602 | 10.7497 | 14.264 | 14.8165 | 11.0847 | 0.0001 | -0.0028 | 0.0011 | 0.0042 | 0.001 | -0.0007 | 0.0014 | -0.0031 | -0.013 | -360.2019 | 17.4172 | -360.4758 | 17.6615 | -360.7743 | 18.1543 | -360.7989 | 17.4972 | -352.6506 | 18.7395 | -352.6783 | 16.834
12:21 | 3667 | 37.9179 | 200.8521 | 448.0245 | 453.0638 | -16.9457 | -42.4804 | 9.8522 | 6.876 | 0.9862 | -0.7464 | 2.334 | -1.6699 | 10.4718 | 3.4694 | 0.6091 | 0.6539 | 0.9585 | 0.7322 | -129.5172 | -1.3715 | 5.5559 | 1.6878 | -3.5822 | -1.9633 | 4.0898 |  | 2.4752 | -0.1405 | 4.0104 | 3.3611 | 3.343 | 1.0596 | 10.714 | 14.2277 | 14.8062 | 11.0501 | 0.0001 | -0.0032 | 0.0005 | 0.0036 | 0.001 | -0.0002 | -0.0008 | -0.0139 | -0.0199 | -360.1404 | 17.4069 | -360.4973 | 17.6902 | -360.845 | 18.1728 | -360.842 | 17.5013 | -352.6321 | 18.7415 | -352.6844 | 16.8566
12:21 | 3668 | 37.909 | 200.8136 | 448.0645 | 453.0814 | -17.0247 | -42.6052 | 9.8933 | 6.8506 | 0.9032 | -0.7746 | 2.4002 | -1.5707 | 10.5702 | 3.6123 | 0.6104 | 0.654 | 0.9602 | 0.732 | -129.6018 | -1.3701 | 5.5898 | 1.6512 | -3.5073 | -2.063 | 4.0813 |  | 2.5065 | -0.0876 | 4.0097 | 3.3674 | 3.3436 | 1.0618 | 10.7197 | 14.2567 | 14.8188 | 11.0323 | -0.0001 | -0.0028 | 0.0004 | 0.0034 | 0.0009 | -0.0005 | 0.0086 | -0.0153 | -0.0034 | -360.1804 | 17.4028 | -360.4604 | 17.6841 | -360.8574 | 18.2036 | -360.9281 | 17.5465 | -352.666 | 18.7271 | -352.6506 | 16.8423
12:21 | 3669 | 38.006 | 200.8052 | 447.9414 | 453.008 | -17.0625 | -42.4919 | 9.9631 | 6.8218 | 0.9113 | -0.6726 | 2.4274 | -1.5383 | 10.5733 | 3.5186 | 0.6085 | 0.6532 | 0.9575 | 0.7318 | -129.5192 | -1.4501 | 5.5677 | 1.6779 | -3.5706 | -1.9344 | 4.131 |  | 2.5236 | -0.1644 | 4.0099 | 3.3676 | 3.3437 | 1.0607 | 10.7072 | 14.2146 | 14.7969 | 11.044 | -0.0005 | -0.0032 | 0.0004 | 0.0032 | 0.0009 | -0.0006 | -0.0065 | -0.0198 | 0.0091 | -360.2204 | 17.4233 | -360.4789 | 17.6533 | -360.7835 | 18.1666 | -360.9004 | 17.5383 | -352.709 | 18.7538 | -352.6629 | 16.8299
12:21 | 3670 | 38.0774 | 200.841 | 448.0103 | 453.0045 | -17.0613 | -42.4454 | 10.0368 | 6.8073 | 0.9544 | -0.6982 | 2.3931 | -1.6082 | 10.5173 | 3.5631 | 0.6105 | 0.6555 | 0.9576 | 0.7335 | -129.5508 | -1.4116 | 5.5775 | 1.6301 | -3.5575 | -1.9265 | 4.1114 |  | 2.5079 | -0.1388 | 4.0094 | 3.3653 | 3.3455 | 1.0611 | 10.7256 | 14.2335 | 14.7772 | 11.0501 | 0 | -0.003 | 0.0008 | 0.0037 | 0.0008 | -0.0006 | 0.0137 | -0.0062 | -0.0189 | -360.165 | 17.409 | -360.4604 | 17.6636 | -360.7897 | 18.1481 | -360.8204 | 17.4952 | -352.6537 | 18.7436 | -352.7029 | 16.834
12:21 | 3671 | 38.0094 | 200.8287 | 447.9316 | 452.9948 | -17.086 | -42.5495 | 9.9433 | 6.8654 | 1.0446 | -0.7133 | 2.4494 | -1.6274 | 10.6128 | 3.5834 | 0.6106 | 0.6553 | 0.959 | 0.7312 | -129.5697 | -1.3506 | 5.5916 | 1.658 | -3.5151 | -1.8294 | 4.1517 |  | 2.5894 | -0.0917 | 4.0093 | 3.3652 | 3.3446 | 1.0611 | 10.7255 | 14.2453 | 14.8257 | 11.1186 | 0.0002 | -0.003 | 0.0005 | 0.0039 | 0.0011 | -0.0006 | -0.0015 | -0.0118 | 0.0174 | -360.165 | 17.3925 | -360.4727 | 17.6902 | -360.8574 | 18.1789 | -360.9158 | 17.4972 | -352.586 | 18.721 | -352.6506 | 16.8443
12:21 | 3672 | 38.0339 | 200.8503 | 447.9259 | 452.9098 | -17.0392 | -42.5773 | 9.9946 | 6.8774 | 0.9786 | -0.9477 | 2.3968 | -1.5618 | 10.5393 | 3.4664 | 0.6105 | 0.6522 | 0.9557 | 0.7316 | -129.5438 | -1.4516 | 5.4955 | 1.6465 | -3.5435 | -1.9238 | 4.0923 |  | 2.4406 | -0.1195 | 4.0082 | 3.3605 | 3.3415 | 1.0618 | 10.7256 | 14.2333 | 14.8341 | 11.062 | -0.0003 | -0.0035 | 0.0007 | 0.0038 | 0.0001 | -0.0007 | 0.0221 | -0.0054 | -0.0341 | -360.2327 | 17.4007 | -360.4419 | 17.6615 | -360.8143 | 18.2097 | -360.922 | 17.5465 | -352.6998 | 18.7333 | -352.6567 | 16.8238
12:21 | 3673 | 38.0712 | 200.89 | 448.0045 | 452.9348 | -17.0437 | -42.6691 | 9.9547 | 6.8526 | 0.9724 | -0.9477 | 2.4542 | -1.6292 | 10.4451 | 3.5059 | 0.6098 | 0.6568 | 0.9614 | 0.732 | -129.4709 | -1.4424 | 5.4481 | 1.5725 | -3.586 | -1.962 | 4.1121 |  | 2.4791 | -0.0768 | 4.0087 | 3.3621 | 3.346 | 1.0615 | 10.7544 | 14.2395 | 14.843 | 11.0897 | -0.0003 | -0.0025 | 0.0004 | 0.0037 | 0.0007 | -0.0008 | 0.0148 | -0.0117 | -0.0216 | -360.2081 | 17.4131 | -360.4573 | 17.641 | -360.7681 | 18.1543 | -360.8635 | 17.528 | -352.666 | 18.7353 | -352.6598 | 16.8176
12:21 | 3674 | 38.0604 | 200.8521 | 448.0165 | 452.9096 | -16.9631 | -42.6616 | 9.9151 | 6.8346 | 0.9577 | -0.9239 | 2.3873 | -1.5892 | 10.5269 | 3.5674 | 0.6114 | 0.6569 | 0.9602 | 0.7304 | -129.5097 | -1.4335 | 5.5544 | 1.5756 | -3.5163 | -1.9343 | 4.106 |  | 2.5412 | -0.1026 | 4.007 | 3.361 | 3.3443 | 1.0617 | 10.7578 | 14.2721 | 14.8656 | 11.0984 | -0.0005 | -0.003 | 0.0008 | 0.0039 | 0.0007 | 0.0001 | 0.0109 | -0.0195 | -0.0295 | -360.1711 | 17.411 | -360.4604 | 17.6718 | -360.8266 | 18.1584 | -360.7989 | 17.4829 | -352.6229 | 18.7333 | -352.6721 | 16.8443
12:21 | 3675 | 37.9955 | 200.7212 | 447.9542 | 452.8564 | -16.9412 | -42.6337 | 9.8758 | 6.9204 | 0.9723 | -0.9413 | 2.453 | -1.6284 | 10.4829 | 3.5114 | 0.6099 | 0.654 | 0.9545 | 0.7314 | -129.5813 | -1.3811 | 5.5134 | 1.6406 | -3.5115 | -1.923 | 4.098 |  | 2.5459 | -0.0816 | 4.0091 | 3.3651 | 3.3446 | 1.0611 | 10.7511 | 14.253 | 14.8484 | 11.0873 | 0.0003 | -0.0032 | 0.0008 | 0.0034 | 0.0008 | -0.001 | 0.0208 | 0.0022 | -0.016 | -360.165 | 17.3884 | -360.4573 | 17.6923 | -360.8327 | 18.2097 | -360.9251 | 17.5219 | -352.6413 | 18.723 | -352.6413 | 16.8607
12:21 | 3676 | 38.0652 | 200.7842 | 447.8598 | 452.8949 | -16.9163 | -42.5866 | 9.9084 | 6.8773 | 0.916 | -0.9477 | 2.3533 | -1.6798 | 10.5298 | 3.5561 | 0.6094 | 0.6555 | 0.9592 | 0.7328 | -129.5322 | -1.4335 | 5.5928 | 1.6025 | -3.4526 | -1.8699 | 4.1328 |  | 2.5051 | -0.1345 | 4.009 | 3.3575 | 3.3427 | 1.0614 | 10.7567 | 14.242 | 14.8468 | 11.0915 | 0.0001 | -0.0032 | 0.0012 | 0.0038 | 0.0012 | 0.0003 | 0.0056 | -0.001 | -0.0101 | -360.1619 | 17.3802 | -360.445 | 17.6636 | -360.8204 | 18.1953 | -360.9035 | 17.5301 | -352.6783 | 18.7292 | -352.6383 | 16.8402
12:21 | 3677 | 37.9812 | 200.7996 | 447.8926 | 452.8293 | -16.9751 | -42.6783 | 9.9752 | 6.867 | 0.9123 | -0.9254 | 2.405 | -1.6574 | 10.4107 | 3.5237 | 0.6103 | 0.654 | 0.9566 | 0.7326 | -129.5099 | -1.4378 | 5.6175 | 1.6287 | -3.4338 | -1.9058 | 4.2108 |  | 2.4828 | -0.2238 | 4.0084 | 3.3614 | 3.3417 | 1.0606 | 10.7428 | 14.2627 | 14.8315 | 11.1071 | -0.0002 | -0.0025 | 0.001 | 0.0039 | 0.0009 | -0.0007 | 0.013 | -0.0101 | -0.0083 | -360.1742 | 17.409 | -360.485 | 17.6574 | -360.7743 | 18.1358 | -360.8174 | 17.5116 | -352.6475 | 18.7415 | -352.6721 | 16.8279
12:21 | 3678 | 38.0509 | 200.8448 | 447.9839 | 452.8461 | -17.0221 | -42.6966 | 9.9675 | 6.7998 | 0.9221 | -1.0767 | 2.394 | -1.6918 | 10.488 | 3.5553 | 0.6113 | 0.6534 | 0.9551 | 0.7319 | -129.4861 | -1.414 | 5.6012 | 1.6277 | -3.4928 | -1.9265 | 4.1901 |  | 2.4638 | -0.1955 | 4.0094 | 3.3637 | 3.3428 | 1.0622 | 10.7175 | 14.2369 | 14.8092 | 11.0594 | 0 | -0.0025 | 0.0008 | 0.0038 | 0.0004 | -0.0006 | 0.0216 | -0.0138 | -0.0132 | -360.165 | 17.4131 | -360.5127 | 17.7067 | -360.8727 | 18.1789 | -360.8358 | 17.5013 | -352.6567 | 18.7538 | -352.6937 | 16.8751
12:21 | 3679 | 38.0787 | 200.8341 | 448.0663 | 452.8464 | -17.0614 | -42.6792 | 9.8242 | 6.8492 | 0.9204 | -1.0061 | 2.3526 | -1.6681 | 10.4699 | 3.5685 | 0.6107 | 0.6554 | 0.9561 | 0.7324 | -129.5564 | -1.4147 | 5.4618 | 1.4421 | -3.4293 | -1.9616 | 4.0546 |  | 2.4565 | -0.124 | 4.0088 | 3.36 | 3.3408 | 1.0615 | 10.7601 | 14.2397 | 14.8094 | 11.0951 | 0.0003 | -0.0031 | 0.0005 | 0.0039 | 0.0011 | -0.0005 | 0.013 | -0.0122 | -0.0217 | -360.1311 | 17.4007 | -360.4696 | 17.6923 | -360.8697 | 18.1974 | -360.882 | 17.5075 | -352.6567 | 18.7353 | -352.6752 | 16.8669
12:21 | 3680 | 37.9952 | 200.7653 | 448.0014 | 452.9385 | -17.0269 | -42.6579 | 9.8803 | 6.8522 | 0.995 | -1.0464 | 2.3572 | -1.6747 | 10.463 | 3.5174 | 0.6118 | 0.6525 | 0.958 | 0.731 | -129.497 | -1.4804 | 5.5273 | 1.5137 | -3.3891 | -1.8498 | 4.1452 |  | 2.5127 | -0.1802 | 4.0081 | 3.3615 | 3.3426 | 1.0614 | 10.7626 | 14.2532 | 14.8147 | 11.0869 | 0.0004 | -0.0027 | 0.0002 | 0.0039 | 0.0005 | -0.0003 | 0.0159 | -0.0069 | -0.0032 | -360.2081 | 17.3884 | -360.4081 | 17.6348 | -360.7681 | 18.1645 | -360.8697 | 17.5301 | -352.6783 | 18.723 | -352.6413 | 16.8115
12:21 | 3681 | 38.0392 | 200.8684 | 448.0381 | 452.9251 | -17.1037 | -42.7751 | 9.7725 | 6.9299 | 1.0552 | -0.9954 | 2.4239 | -1.6425 | 10.4094 | 3.4173 | 0.6113 | 0.6545 | 0.9612 | 0.7304 | -129.4855 | -1.3814 | 5.5604 | 1.5135 | -3.4033 | -1.8222 | 4.2287 |  | 2.4761 | -0.1815 | 4.0077 | 3.3637 | 3.3412 | 1.0616 | 10.7405 | 14.2257 | 14.8298 | 11.0468 | -0.0002 | -0.0028 | 0.0012 | 0.0044 | 0.0011 | -0.0001 | -0.0071 | -0.0009 | -0.0005 | -360.1988 | 17.4336 | -360.5035 | 17.6718 | -360.802 | 18.144 | -360.8327 | 17.5178 | -352.6752 | 18.76 | -352.6998 | 16.8217
12:21 | 3682 | 38.0165 | 200.7608 | 447.967 | 452.8849 | -17.1546 | -42.8828 | 9.7692 | 7.0075 | 1.0948 | -0.9109 | 2.5187 | -1.661 | 10.4361 | 3.3586 | 0.6102 | 0.6572 | 0.9579 | 0.7293 | -129.5316 | -1.4222 | 5.4706 | 1.5249 | -3.5137 | -1.7798 | 4.0934 |  | 2.4976 | -0.2118 | 4.0079 | 3.3648 | 3.3393 | 1.0615 | 10.7509 | 14.2652 | 14.8237 | 11.0684 | -0.0002 | -0.0022 | 0.0007 | 0.0035 | 0.0012 | -0.0006 | -0.0052 | -0.0126 | -0.0309 | -360.1927 | 17.4274 | -360.525 | 17.6985 | -360.8666 | 18.1728 | -360.8574 | 17.5178 | -352.6598 | 18.76 | -352.7152 | 16.8566
12:21 | 3683 | 37.9397 | 200.7783 | 447.8941 | 452.8365 | -16.9778 | -42.6077 | 9.9088 | 6.9653 | 1.0144 | -0.9142 | 2.5335 | -1.6014 | 10.5222 | 3.512 | 0.6107 | 0.6556 | 0.9561 | 0.73 | -129.4792 | -1.3399 | 5.625 | 1.5668 | -3.3405 | -1.9033 | 4.1624 |  | 2.4873 | -0.241 | 4.0083 | 3.3651 | 3.3421 | 1.0618 | 10.7464 | 14.2369 | 14.8266 | 11.0999 | -0.0002 | -0.0031 | 0.001 | 0.0035 | 0.0002 | -0.0004 | 0.0149 | -0.003 | -0.0148 | -360.1588 | 17.3905 | -360.4419 | 17.6718 | -360.8358 | 18.1892 | -360.8758 | 17.5096 | -352.6506 | 18.7271 | -352.666 | 16.834
12:21 | 3684 | 38.0026 | 200.6881 | 447.9355 | 452.8596 | -16.9357 | -42.5806 | 9.8717 | 6.8847 | 1.0295 | -0.7969 | 2.4712 | -1.6751 | 10.4261 | 3.509 | 0.6108 | 0.6573 | 0.9531 | 0.7308 | -129.5197 | -1.484 | 5.6164 | 1.5529 | -3.4024 | -1.8578 | 4.1773 |  | 2.5296 | -0.2067 | 4.0079 | 3.3641 | 3.3403 | 1.0624 | 10.7348 | 14.2545 | 14.8113 | 11.076 | 0.0003 | -0.0032 | 0.001 | 0.0041 | 0.001 | -0.0008 | 0.0113 | -0.0059 | -0.0088 | -360.1958 | 17.3884 | -360.4327 | 17.6512 | -360.7835 | 18.1522 | -360.8697 | 17.528 | -352.6321 | 18.7189 | -352.6475 | 16.8053
12:21 | 3685 | 38.0425 | 200.7754 | 448.0034 | 452.8798 | -16.922 | -42.4734 | 9.86 | 6.8215 | 1.0312 | -0.9049 | 2.3516 | -1.6895 | 10.5501 | 3.4826 | 0.6096 | 0.656 | 0.9626 | 0.73 | -129.4648 | -1.3849 | 5.5354 | 1.6217 | -3.3835 | -1.8414 | 4.239 |  | 2.5354 | -0.1995 | 4.008 | 3.3618 | 3.3404 | 1.0615 | 10.7568 | 14.2358 | 14.8031 | 11.0464 | -0.0003 | -0.0028 | 0.0006 | 0.0034 | 0.0002 | -0.0005 | 0.0056 | -0.01 | -0.0045 | -360.2388 | 17.4397 | -360.4573 | 17.6738 | -360.8389 | 18.1666 | -360.842 | 17.5301 | -352.7029 | 18.762 | -352.6844 | 16.8156
12:21 | 3686 | 38.0211 | 200.7868 | 447.8492 | 452.772 | -16.9632 | -42.5417 | 9.9133 | 6.8177 | 0.9325 | -0.996 | 2.2433 | -1.7378 | 10.4816 | 3.4036 | 0.6102 | 0.6545 | 0.9593 | 0.7311 | -129.4253 | -1.3853 | 5.5531 | 1.68 | -3.3913 | -1.872 | 4.1924 |  | 2.4768 | -0.2414 | 4.0088 | 3.3635 | 3.3433 | 1.062 | 10.7083 | 14.1986 | 14.7935 | 11.0678 | -0.0005 | -0.0026 | 0.0006 | 0.0041 | 0.0014 | -0.0008 | 0.0107 | -0.0077 | -0.0219 | -360.1619 | 17.4131 | -360.5127 | 17.7026 | -360.8543 | 18.1728 | -360.8881 | 17.5239 | -352.6229 | 18.7477 | -352.7213 | 16.8484
12:21 | 3687 | 38.0127 | 200.8463 | 447.9179 | 452.7833 | -16.9662 | -42.624 | 9.7925 | 6.8654 | 1.0225 | -0.9449 | 2.2367 | -1.6899 | 10.5334 | 3.5466 | 0.6113 | 0.6546 | 0.9583 | 0.7304 | -129.4311 | -1.3313 | 5.6343 | 1.6216 | -3.4014 | -1.9848 | 4.1724 |  | 2.4973 | -0.1991 | 4.008 | 3.3618 | 3.3419 | 1.0623 | 10.7428 | 14.2397 | 14.8094 | 11.0605 | 0.0009 | -0.0021 | 0.0003 | 0.0039 | -0.0002 | -0.0008 | 0.0204 | -0.0207 | -0.0119 | -360.1281 | 17.3843 | -360.4266 | 17.6512 | -360.7927 | 18.183 | -360.8635 | 17.4993 | -352.629 | 18.7251 | -352.626 | 16.8156
12:21 | 3688 | 38.0381 | 200.8671 | 447.9614 | 452.8531 | -16.959 | -42.6599 | 9.774 | 6.8164 | 1.0953 | -0.8924 | 2.2517 | -1.7352 | 10.4927 | 3.5643 | 0.6086 | 0.6522 | 0.9563 | 0.7307 | -129.5166 | -1.3237 | 5.5523 | 1.7723 | -3.4618 | -1.908 | 4.1755 |  | 2.516 | -0.2274 | 4.0097 | 3.3627 | 3.3432 | 1.062 | 10.7683 | 14.2707 | 14.8505 | 11.0749 | 0.0003 | -0.0031 | 0.0005 | 0.0036 | 0.0012 | -0.0003 | 0.0062 | 0.001 | -0.0225 | -360.1619 | 17.4007 | -360.4358 | 17.6656 | -360.7773 | 18.1584 | -360.8635 | 17.5178 | -352.626 | 18.7271 | -352.666 | 16.8094
12:21 | 3689 | 38.0411 | 200.9018 | 448.015 | 452.9227 | -16.8746 | -42.5366 | 9.8393 | 6.8868 | 1.075 | -1.0249 | 2.1994 | -1.6072 | 10.4749 | 3.5139 | 0.6093 | 0.6524 | 0.9597 | 0.7318 | -129.5191 | -1.361 | 5.5586 | 1.758 | -3.4395 | -1.8649 | 4.1651 |  | 2.5215 | -0.3498 | 4.0089 | 3.3649 | 3.3455 | 1.0622 | 10.736 | 14.2496 | 14.8222 | 11.0605 | -0.0005 | -0.003 | 0.0007 | 0.0042 | 0.0009 | -0.0004 | 0.0104 | -0.0045 | -0.0204 | -360.205 | 17.4295 | -360.5004 | 17.6923 | -360.8389 | 18.183 | -360.8789 | 17.5198 | -352.6629 | 18.7559 | -352.6937 | 16.8361
12:21 | 3690 | 37.9868 | 200.8389 | 447.9968 | 452.8062 | -16.8538 | -42.5283 | 9.9546 | 6.7925 | 1.028 | -1.0426 | 2.2073 | -1.6514 | 10.5442 | 3.4687 | 0.6125 | 0.6584 | 0.9625 | 0.7325 | -129.454 | -1.2442 | 5.5824 | 1.6942 | -3.513 | -1.8467 | 4.1352 |  | 2.4954 | -0.1844 | 4.009 | 3.363 | 3.3416 | 1.063 | 10.7556 | 14.2174 | 14.797 | 11.0565 | -0.0001 | -0.0026 | 0.0006 | 0.0035 | 0.0006 | -0.0003 | 0.0155 | -0.0079 | 0.0073 | -360.1311 | 17.409 | -360.4758 | 17.6841 | -360.7958 | 18.181 | -360.9035 | 17.5178 | -352.6475 | 18.7395 | -352.6813 | 16.8381
12:21 | 3691 | 38.1406 | 200.9621 | 448.1161 | 452.9431 | -16.903 | -42.5362 | 9.8677 | 6.8876 | 1.1481 | -0.9282 | 2.363 | -1.5997 | 10.4999 | 3.3684 | 0.61 | 0.661 | 0.9607 | 0.7324 | -129.5096 | -1.3328 | 5.6241 | 1.7625 | -3.5515 | -1.9626 | 4.0759 |  | 2.5046 | -0.1112 | 4.0082 | 3.3595 | 3.3409 | 1.0628 | 10.7614 | 14.2462 | 14.8365 | 11.08 | -0.0005 | -0.003 | 0.0008 | 0.0036 | 0.0009 | -0.0003 | 0.014 | -0.0061 | -0.0051 | -360.125 | 17.3925 | -360.4142 | 17.6512 | -360.7681 | 18.1584 | -360.8481 | 17.5075 | -352.6537 | 18.7333 | -352.6506 | 16.8217
12:21 | 3692 | 38.1128 | 200.9449 | 448.0149 | 452.8754 | -16.9116 | -42.5653 | 9.8502 | 6.7767 | 1.1161 | -1.0596 | 2.3284 | -1.5263 | 10.4825 | 3.4708 | 0.6111 | 0.6592 | 0.9649 | 0.7323 | -129.4522 | -1.2861 | 5.6041 | 1.7355 | -3.442 | -1.9616 | 4.1055 |  | 2.5617 | -0.1149 | 4.0095 | 3.3612 | 3.3411 | 1.0623 | 10.6943 | 14.2486 | 14.7987 | 11.0591 | 0 | -0.0032 | 0.0012 | 0.0038 | 0.0005 | -0.0004 | 0.0196 | -0.0045 | -0.0119 | -360.1373 | 17.3966 | -360.4389 | 17.6636 | -360.7743 | 18.1645 | -360.8481 | 17.5116 | -352.5952 | 18.7251 | -352.6721 | 16.8217
12:21 | 3693 | 38.1034 | 200.9856 | 448.0248 | 452.8597 | -16.8538 | -42.5009 | 10.0973 | 6.8679 | 1.0585 | -1.0329 | 2.2955 | -1.5506 | 10.4685 | 3.4711 | 0.6119 | 0.6563 | 0.9618 | 0.7314 | -129.4809 | -1.3746 | 5.5288 | 1.7379 | -3.457 | -1.948 | 4.1302 |  | 2.5092 | -0.151 | 4.0085 | 3.3607 | 3.3422 | 1.0628 | 10.7511 | 14.2472 | 14.8136 | 11.0641 | -0.0001 | -0.0033 | 0.0008 | 0.0037 | 0.0009 | -0.0006 | 0.0099 | -0.0006 | 0.0026 | -360.1988 | 17.409 | -360.4696 | 17.68 | -360.8358 | 18.183 | -360.8697 | 17.5157 | -352.6721 | 18.7456 | -352.6752 | 16.8381
12:21 | 3694 | 38.1043 | 201.0255 | 448.0007 | 452.9032 | -16.8369 | -42.5379 | 10.0534 | 6.8758 | 1.1206 | -0.9262 | 2.334 | -1.4606 | 10.5764 | 3.5034 | 0.6109 | 0.6572 | 0.9613 | 0.733 | -129.459 | -1.4219 | 5.5907 | 1.7103 | -3.4594 | -1.8872 | 4.079 |  | 2.5125 | -0.0291 | 4.0088 | 3.3643 | 3.3406 | 1.063 | 10.7671 | 14.2754 | 14.8502 | 11.0677 | -0.0003 | -0.0027 | 0.0004 | 0.0039 | 0.0006 | -0.0005 | 0.0132 | -0.0124 | 0.0061 | -360.1681 | 17.4151 | -360.4789 | 17.6738 | -360.8235 | 18.1933 | -360.9035 | 17.528 | -352.669 | 18.7497 | -352.7244 | 16.8402
12:21 | 3695 | 38.106 | 201.0352 | 447.9525 | 452.9007 | -16.92 | -42.5482 | 9.9945 | 6.9104 | 1.1152 | -0.9941 | 2.3168 | -1.5442 | 10.5386 | 3.4505 | 0.6116 | 0.6598 | 0.9622 | 0.7317 | -129.4649 | -1.3322 | 5.6159 | 1.6791 | -3.4806 | -2.0347 | 4.1084 |  | 2.5414 | -0.1376 | 4.0086 | 3.3606 | 3.3372 | 1.0626 | 10.7383 | 14.2289 | 14.8018 | 11.0396 | -0.0005 | -0.0033 | 0.0007 | 0.004 | 0.0009 | -0.0007 | 0.0001 | 0.0017 | -0.0319 | -360.1527 | 17.4028 | -360.4512 | 17.6574 | -360.7897 | 18.1789 | -360.8697 | 17.5096 | -352.669 | 18.7436 | -352.666 | 16.8238
12:21 | 3696 | 38.0747 | 200.99 | 447.9963 | 452.8631 | -16.8829 | -42.536 | 9.9598 | 6.7768 | 1.0064 | -0.975 | 2.3941 | -1.6241 | 10.5404 | 3.4169 | 0.6124 | 0.6578 | 0.9612 | 0.7333 | -129.477 | -1.2621 | 5.584 | 1.6506 | -3.589 | -1.8556 | 4.0857 |  | 2.5287 | -0.1295 | 4.0098 | 3.3639 | 3.3401 | 1.0642 | 10.7463 | 14.2545 | 14.8345 | 11.0934 | 0.0002 | -0.003 | 0.0002 | 0.0038 | 0.0004 | -0.0004 | 0.0335 | -0.01 | -0.0065 | -360.1435 | 17.3905 | -360.4789 | 17.6553 | -360.7681 | 18.1604 | -360.8327 | 17.4911 | -352.6136 | 18.7312 | -352.6506 | 16.832
12:21 | 3697 | 38.2023 | 200.9833 | 448.0423 | 452.9141 | -16.9118 | -42.5138 | 9.9518 | 6.7655 | 1.0722 | -0.948 | 2.3781 | -1.6413 | 10.5624 | 3.3946 | 0.6139 | 0.6592 | 0.9606 | 0.7333 | -129.4634 | -1.2886 | 5.5663 | 1.7079 | -3.5091 | -2.0354 | 4.1439 |  | 2.539 | -0.1799 | 4.01 | 3.3658 | 3.3428 | 1.0622 | 10.7105 | 14.2475 | 14.7984 | 11.0749 | 0 | -0.0032 | 0.0007 | 0.0041 | 0.0011 | -0.0007 | 0.0298 | -0.0006 | -0.0178 | -360.1773 | 17.3884 | -360.4389 | 17.6677 | -360.7835 | 18.1707 | -360.8327 | 17.4931 | -352.6229 | 18.7333 | -352.6537 | 16.8197
12:21 | 3698 | 38.2282 | 201.0437 | 448.1836 | 452.9934 | -16.7244 | -42.3693 | 10.07 | 6.8147 | 1.1245 | -0.9562 | 2.4004 | -1.7007 | 10.4477 | 3.3516 | 0.6113 | 0.6574 | 0.9592 | 0.7309 | -129.4834 | -1.296 | 5.5522 | 1.718 | -3.4635 | -1.9087 | 4.1574 |  | 2.6573 | -0.1811 | 4.0093 | 3.3661 | 3.3446 | 1.0629 | 10.7475 | 14.2324 | 14.8001 | 11.0544 | -0.0009 | -0.0031 | 0.001 | 0.0037 | 0.0005 | -0.0002 | -0.0027 | -0.0079 | 0.0029 | -360.1988 | 17.4254 | -360.4881 | 17.6759 | -360.8204 | 18.1789 | -360.9004 | 17.5383 | -352.6629 | 18.7395 | -352.669 | 16.8217
12:21 | 3699 | 38.2395 | 200.9795 | 448.1001 | 452.9066 | -16.8695 | -42.4734 | 10.0956 | 6.7556 | 1.0372 | -0.8775 | 2.381 | -1.657 | 10.5025 | 3.4002 | 0.6108 | 0.6523 | 0.9616 | 0.7324 | -129.4443 | -1.3065 | 5.5274 | 1.5881 | -3.3782 | -1.9361 | 4.0913 |  | 2.625 | -0.1291 | 4.0084 | 3.3638 | 3.3411 | 1.063 | 10.7567 | 14.2592 | 14.8574 | 11.0688 | -0.0001 | -0.0026 | 0.0011 | 0.0042 | 0.0007 | -0.0008 | 0.0013 | 0.0016 | 0.0056 | -360.2173 | 17.4315 | -360.4942 | 17.682 | -360.8297 | 18.1707 | -360.8789 | 17.5321 | -352.6998 | 18.7579 | -352.6875 | 16.8381
12:21 | 3700 | 38.1801 | 200.9235 | 448.1674 | 452.821 | -16.828 | -42.5552 | 10.025 | 6.7557 | 1.0927 | -0.8466 | 2.4763 | -1.5641 | 10.5169 | 3.407 | 0.6109 | 0.6546 | 0.9593 | 0.731 | -129.3783 | -1.3547 | 5.5822 | 1.591 | -3.3822 | -1.9252 | 4.1216 |  | 2.6872 | -0.1063 | 4.0077 | 3.3648 | 3.3451 | 1.0624 | 10.7533 | 14.2498 | 14.829 | 11.0775 | 0.0001 | -0.0031 | 0.0014 | 0.004 | 0.0002 | -0.0007 | 0.0129 | -0.005 | 0.0023 | -360.1619 | 17.4028 | -360.485 | 17.6697 | -360.7989 | 18.1707 | -360.8327 | 17.4993 | -352.6567 | 18.7456 | -352.666 | 16.834
12:21 | 3701 | 38.1963 | 200.988 | 448.2469 | 452.8691 | -16.9345 | -42.6879 | 9.8485 | 6.799 | 1.1056 | -0.8482 | 2.4142 | -1.5656 | 10.548 | 3.4044 | 0.6096 | 0.6558 | 0.9592 | 0.7309 | -129.4404 | -1.2904 | 5.619 | 1.7562 | -3.3753 | -1.9044 | 4.1799 |  | 2.6408 | -0.0234 | 4.0091 | 3.3668 | 3.3438 | 1.0631 | 10.7717 | 14.2455 | 14.8094 | 11.0951 | 0.0002 | -0.0031 | 0.0013 | 0.004 | 0.0008 | -0.0003 | 0.004 | -0.0106 | -0.0124 | -360.1311 | 17.374 | -360.4112 | 17.6594 | -360.7989 | 18.1687 | -360.8481 | 17.5013 | -352.6044 | 18.7025 | -352.6229 | 16.8217
12:21 | 3702 | 38.1573 | 200.9207 | 448.0653 | 452.8017 | -16.9868 | -42.6145 | 9.926 | 6.897 | 1.1392 | -0.7485 | 2.4222 | -1.4496 | 10.5456 | 3.4384 | 0.611 | 0.655 | 0.9571 | 0.7321 | -129.4331 | -1.2271 | 5.5067 | 1.6457 | -3.4112 | -1.8516 | 4.0998 |  | 2.6488 | -0.0861 | 4.0101 | 3.3637 | 3.3459 | 1.0637 | 10.7428 | 14.2512 | 14.8267 | 11.072 | 0.0001 | -0.0027 | 0.0004 | 0.0037 | 0.0008 | -0.0006 | -0.0002 | -0.0056 | -0.0001 | -360.2111 | 17.4192 | -360.4635 | 17.641 | -360.7989 | 18.1748 | -360.8789 | 17.5342 | -352.6906 | 18.7333 | -352.6721 | 16.8094
12:21 | 3703 | 38.194 | 200.933 | 448.1161 | 452.8608 | -16.9324 | -42.7108 | 9.8656 | 6.8849 | 1.0851 | -0.6825 | 2.3698 | -1.4727 | 10.568 | 3.4484 | 0.6119 | 0.6564 | 0.9573 | 0.7316 | -129.3983 | -1.2265 | 5.6125 | 1.63 | -3.3094 | -1.8702 | 4.1238 |  | 2.6911 | -0.0287 | 4.0096 | 3.3628 | 3.3436 | 1.0617 | 10.7348 | 14.2429 | 14.8171 | 11.0818 | -0.0004 | -0.0027 | 0.0007 | 0.0037 | 0.0009 | -0.0003 | 0.0011 | -0.0182 | 0.002 | -360.1988 | 17.4418 | -360.4912 | 17.6779 | -360.8327 | 18.1748 | -360.8727 | 17.5363 | -352.6752 | 18.762 | -352.709 | 16.8361
12:21 | 3704 | 38.1447 | 200.9361 | 448.1216 | 452.8994 | -16.907 | -42.6153 | 9.8209 | 6.7836 | 1.0506 | -0.8368 | 2.4006 | -1.5658 | 10.5615 | 3.4204 | 0.6115 | 0.6597 | 0.9604 | 0.7316 | -129.3797 | -1.2409 | 5.643 | 1.6121 | -3.3553 | -1.838 | 4.1687 |  | 2.5554 | 0.0757 | 4.0083 | 3.3601 | 3.3418 | 1.0633 | 10.744 | 14.2407 | 14.827 | 11.0562 | 0.0004 | -0.0028 | 0.0001 | 0.0036 | 0.001 | -0.0005 | 0.0134 | -0.0082 | -0.0213 | -360.1619 | 17.409 | -360.5158 | 17.6964 | -360.8297 | 18.1892 | -360.885 | 17.5013 | -352.6537 | 18.7477 | -352.7121 | 16.8566
12:21 | 3705 | 38.2299 | 200.9229 | 448.0632 | 452.8796 | -16.9653 | -42.5428 | 9.9893 | 6.8806 | 1.0359 | -0.8006 | 2.359 | -1.4733 | 10.6233 | 3.4755 | 0.6115 | 0.6566 | 0.9586 | 0.7299 | -129.4723 | -1.2728 | 5.6197 | 1.6082 | -3.413 | -1.8985 | 4.1682 |  | 2.5876 | 0.0057 | 4.0095 | 3.3648 | 3.3452 | 1.0634 | 10.7153 | 14.2169 | 14.8275 | 11.0523 | 0.0001 | -0.0031 | 0.0005 | 0.0037 | 0.0003 | -0.0006 | 0.0136 | -0.0214 | -0.0024 | -360.1588 | 17.374 | -360.4019 | 17.6492 | -360.7958 | 18.1728 | -360.8789 | 17.5137 | -352.6229 | 18.7128 | -352.6044 | 16.8197
12:21 | 3706 | 38.2602 | 200.9111 | 448.0545 | 452.8559 | -17.0143 | -42.5365 | 10.0871 | 6.8957 | 1.0433 | -0.7256 | 2.4256 | -1.6018 | 10.5214 | 3.4065 | 0.61 | 0.6572 | 0.9595 | 0.7315 | -129.4455 | -1.2388 | 5.6367 | 1.5742 | -3.4543 | -1.9309 | 4.1447 |  | 2.5817 | 0.0215 | 4.0096 | 3.3635 | 3.3458 | 1.0632 | 10.7151 | 14.2463 | 14.8028 | 11.0392 | -0.0003 | -0.0026 | 0.0011 | 0.0039 | 0.0009 | -0.0006 | 0.0139 | 0.0019 | -0.0151 | -360.1835 | 17.3966 | -360.4419 | 17.643 | -360.7743 | 18.1645 | -360.8758 | 17.5157 | -352.6506 | 18.7333 | -352.6352 | 16.7971
12:21 | 3707 | 38.2441 | 200.9211 | 448.1126 | 452.8773 | -16.97 | -42.4811 | 9.9672 | 6.8931 | 1.0684 | -0.7416 | 2.4012 | -1.6042 | 10.4904 | 3.4495 | 0.612 | 0.6584 | 0.9581 | 0.7325 | -129.3897 | -1.3157 | 5.5192 | 1.5914 | -3.3916 | -1.9576 | 4.1405 |  | 2.6085 | -0.0817 | 4.0099 | 3.3663 | 3.3435 | 1.0644 | 10.7706 | 14.2326 | 14.7896 | 11.0655 | -0.0003 | -0.0026 | 0.0011 | 0.0038 | 0.0005 | -0.0004 | 0.027 | -0.0093 | 0.0058 | -360.1927 | 17.4254 | -360.5096 | 17.7108 | -360.8389 | 18.1666 | -360.8512 | 17.5096 | -352.6383 | 18.76 | -352.6967 | 16.8484
12:22 | 3708 | 38.2734 | 200.9508 | 448.1894 | 452.9037 | -16.9403 | -42.6637 | 10.0001 | 6.8718 | 1.1878 | -0.6836 | 2.4047 | -1.5614 | 10.5647 | 3.5609 | 0.6101 | 0.6594 | 0.9602 | 0.7319 | -129.4356 | -1.2276 | 5.6516 | 1.5793 | -3.4493 | -1.9811 | 4.1044 |  | 2.5391 | -0.0731 | 4.0096 | 3.3658 | 3.3444 | 1.0629 | 10.7313 | 14.2337 | 14.8141 | 11.0551 | 0.0003 | -0.0025 | 0.0015 | 0.0045 | 0.0008 | -0.0005 | 0.0155 | -0.0069 | 0.0025 | -360.1588 | 17.3987 | -360.4542 | 17.719 | -360.8666 | 18.2077 | -360.9004 | 17.5157 | -352.6721 | 18.7292 | -352.6752 | 16.8525
12:22 | 3709 | 38.2247 | 200.9105 | 448.2242 | 453.029 | -17.0704 | -42.7012 | 9.9417 | 6.8937 | 1.0744 | -0.7783 | 2.3355 | -1.5787 | 10.6126 | 3.507 | 0.6119 | 0.6557 | 0.96 | 0.7318 | -129.4679 | -1.1862 | 5.6171 | 1.5296 | -3.4737 | -1.9352 | 4.0935 |  | 2.5248 | -0.1235 | 4.0099 | 3.3631 | 3.3437 | 1.0622 | 10.7462 | 14.249 | 14.8772 | 11.1215 | 0.0004 | -0.0029 | 0.0009 | 0.0041 | 0.0007 | -0.0004 | 0.015 | -0.008 | 0.0163 | -360.1927 | 17.3843 | -360.4235 | 17.6697 | -360.7804 | 18.1728 | -360.8666 | 17.5239 | -352.6752 | 18.721 | -352.629 | 16.8115
12:22 | 3710 | 38.1952 | 200.8955 | 448.1652 | 452.9184 | -16.9345 | -42.5986 | 9.973 | 6.8881 | 1.064 | -0.7022 | 2.3385 | -1.592 | 10.5541 | 3.3678 | 0.611 | 0.6566 | 0.9571 | 0.7314 | -129.4746 | -1.178 | 5.5265 | 1.5449 | -3.5518 | -1.9194 | 4.1174 |  | 2.5435 | -0.1498 | 4.0087 | 3.3643 | 3.3438 | 1.0629 | 10.7798 | 14.2882 | 14.84 | 11.0919 | 0.0001 | -0.0026 | 0.0001 | 0.0034 | 0.0007 | -0.0005 | 0.0195 | -0.004 | -0.015 | -360.1773 | 17.411 | -360.4758 | 17.6882 | -360.8081 | 18.1522 | -360.8235 | 17.4993 | -352.6567 | 18.7518 | -352.6813 | 16.834
12:22 | 3711 | 38.2052 | 200.8295 | 448.1427 | 452.9596 | -17.0025 | -42.6533 | 9.9315 | 6.8907 | 1.0941 | -0.6601 | 2.4392 | -1.6007 | 10.5806 | 3.4472 | 0.6121 | 0.6591 | 0.9602 | 0.732 | -129.4908 | -1.1617 | 5.6163 | 1.563 | -3.4255 | -1.8227 | 4.1817 |  | 2.5787 | -0.0792 | 4.0104 | 3.3643 | 3.3441 | 1.0646 | 10.7474 | 14.2038 | 14.8254 | 11.0594 | -0.0002 | -0.0025 | 0.0011 | 0.004 | 0.001 | -0.0005 | -0.0051 | 0.0113 | -0.0008 | -360.1435 | 17.411 | -360.4942 | 17.719 | -360.9035 | 18.181 | -360.8635 | 17.4993 | -352.5983 | 18.7292 | -352.6752 | 16.8546
12:22 | 3712 | 38.1892 | 200.7837 | 448.0456 | 452.9316 | -17.0485 | -42.6545 | 9.9098 | 6.8722 | 0.9841 | -0.5724 | 2.4444 | -1.5958 | 10.5959 | 3.4543 | 0.6105 | 0.6624 | 0.9617 | 0.7319 | -129.5327 | -1.2874 | 5.4785 | 1.6541 | -3.4067 | -1.8707 | 4.2192 |  | 2.6718 | -0.096 | 4.0093 | 3.3635 | 3.3421 | 1.0634 | 10.7418 | 14.2149 | 14.799 | 11.0374 | -0.0003 | -0.0032 | 0 | 0.0033 | 0.0007 | -0.0004 | 0.0196 | -0.0031 | -0.0137 | -360.205 | 17.4048 | -360.4481 | 17.7108 | -360.8604 | 18.1953 | -360.9158 | 17.5424 | -352.666 | 18.7271 | -352.666 | 16.8361
12:22 | 3713 | 38.2012 | 200.8594 | 448.0531 | 452.8998 | -17.0655 | -42.5791 | 9.9446 | 6.8746 | 0.8675 | -0.6345 | 2.3679 | -1.5529 | 10.5166 | 3.4963 | 0.6104 | 0.6606 | 0.9587 | 0.7314 | -129.5028 | -1.284 | 5.5418 | 1.6268 | -3.4094 | -1.8656 | 4.2062 |  | 2.6634 | -0.1293 | 4.0083 | 3.3638 | 3.3404 | 1.0622 | 10.7234 | 14.2134 | 14.8013 | 11.0775 | 0 | -0.0033 | 0.0007 | 0.0039 | 0.001 | -0.0006 | 0.0145 | -0.0027 | -0.0242 | -360.245 | 17.4192 | -360.4789 | 17.6882 | -360.7989 | 18.1584 | -360.8666 | 17.5363 | -352.7029 | 18.7661 | -352.709 | 16.832
12:22 | 3714 | 38.2426 | 200.8576 | 448.0187 | 452.8686 | -17.0217 | -42.5145 | 10.0337 | 6.8208 | 0.8945 | -0.558 | 2.3414 | -1.6253 | 10.4768 | 3.4427 | 0.6112 | 0.6552 | 0.9603 | 0.7313 | -129.4669 | -1.24 | 5.4871 | 1.5307 | -3.4801 | -1.9212 | 4.0731 |  | 2.6336 | -0.0849 | 4.0096 | 3.3649 | 3.3453 | 1.0606 | 10.7267 | 14.2232 | 14.797 | 11.0623 | -0.0002 | -0.0028 | 0.0009 | 0.0039 | 0.0005 | -0.0003 | 0.0211 | -0.0079 | -0.0088 | -360.1311 | 17.4028 | -360.4942 | 17.7087 | -360.7989 | 18.144 | -360.7835 | 17.4705 | -352.6352 | 18.7395 | -352.7183 | 16.8566
12:22 | 3715 | 38.2387 | 200.7584 | 448.1205 | 452.9203 | -16.998 | -42.5336 | 10.0949 | 6.8993 | 0.9244 | -0.4918 | 2.3815 | -1.5211 | 10.5244 | 3.5137 | 0.6134 | 0.6584 | 0.9582 | 0.7309 | -129.5734 | -1.2394 | 5.4972 | 1.5382 | -3.4633 | -1.8827 | 4.1136 |  | 2.5504 | -0.0354 | 4.0101 | 3.3587 | 3.3406 | 1.062 | 10.7475 | 14.2613 | 14.8348 | 11.0717 | -0.0007 | -0.0028 | 0.0007 | 0.0036 | 0.001 | -0.0006 | 0.0084 | -0.0138 | 0.0012 | -360.1465 | 17.3864 | -360.445 | 17.6944 | -360.8174 | 18.1789 | -360.8697 | 17.4952 | -352.6106 | 18.7128 | -352.666 | 16.8217
12:22 | 3716 | 38.1501 | 200.7711 | 448.1403 | 453.0008 | -17.0143 | -42.5272 | 10.0392 | 6.8113 | 0.8658 | -0.6032 | 2.378 | -1.5551 | 10.5428 | 3.4953 | 0.6111 | 0.6569 | 0.9587 | 0.731 | -129.4915 | -1.2779 | 5.5472 | 1.5514 | -3.5203 | -1.834 | 4.259 |  | 2.6866 | -0.1469 | 4.0093 | 3.3634 | 3.3409 | 1.0623 | 10.7394 | 14.2418 | 14.8216 | 11.0634 | -0.0002 | -0.0028 | 0.0017 | 0.0045 | 0.0006 | 0.0001 | 0.0082 | 0.0026 | -0.0061 | -360.2481 | 17.4274 | -360.4727 | 17.6861 | -360.7897 | 18.1707 | -360.922 | 17.5527 | -352.6844 | 18.7559 | -352.6752 | 16.8115
12:22 | 3717 | 38.1807 | 200.8918 | 448.1037 | 452.9288 | -17.0573 | -42.4763 | 10.0697 | 6.9103 | 0.8808 | -0.5338 | 2.4152 | -1.5055 | 10.5084 | 3.5794 | 0.6115 | 0.6566 | 0.9545 | 0.7335 | -129.6055 | -1.2878 | 5.4639 | 1.4151 | -3.482 | -1.9355 | 4.2273 |  | 2.5865 | -0.1494 | 4.0085 | 3.3628 | 3.3423 | 1.0624 | 10.7683 | 14.265 | 14.8689 | 11.0977 | -0.0003 | -0.0032 | 0.0006 | 0.0037 | 0.0011 | -0.0006 | 0.0123 | -0.0098 | 0.0047 | -360.1927 | 17.4336 | -360.5343 | 17.7149 | -360.8174 | 18.1502 | -360.845 | 17.5137 | -352.6844 | 18.7785 | -352.7306 | 16.8587
12:22 | 3718 | 38.167 | 200.8552 | 448.0378 | 452.969 | -17.0499 | -42.5518 | 9.9832 | 6.944 | 1.0093 | -0.4415 | 2.3873 | -1.7171 | 10.5042 | 3.5261 | 0.6116 | 0.6601 | 0.9563 | 0.7329 | -129.5111 | -1.263 | 5.6005 | 1.373 | -3.5247 | -1.9378 | 4.2166 |  | 2.5677 | -0.2065 | 4.0088 | 3.364 | 3.3416 | 1.0625 | 10.7776 | 14.2742 | 14.8546 | 11.084 | 0 | -0.0031 | 0.0005 | 0.0037 | 0.0002 | -0.0001 | 0.0104 | -0.0155 | -0.0176 | -360.1065 | 17.374 | -360.445 | 17.7087 | -360.805 | 18.1584 | -360.8635 | 17.4911 | -352.6075 | 18.7148 | -352.6567 | 16.8381
12:22 | 3719 | 38.2289 | 200.9337 | 448.0761 | 452.9416 | -16.9575 | -42.4616 | 10.0352 | 6.974 | 0.9456 | -0.5415 | 2.4468 | -1.5875 | 10.5893 | 3.5417 | 0.611 | 0.6592 | 0.957 | 0.7315 | -129.4816 | -1.3045 | 5.5615 | 1.5538 | -3.5479 | -1.9694 | 4.186 |  | 2.5842 | -0.1926 | 4.0095 | 3.3663 | 3.346 | 1.0624 | 10.7475 | 14.2557 | 14.7896 | 11.0713 | -0.0003 | -0.0029 | 0.0006 | 0.0039 | 0.0009 | -0.0005 | 0.006 | -0.003 | -0.0013 | -360.1681 | 17.3946 | -360.4235 | 17.6656 | -360.7835 | 18.1728 | -360.8943 | 17.5404 | -352.6937 | 18.7128 | -352.6413 | 16.8032
12:22 | 3720 | 38.2506 | 200.9305 | 448.1147 | 452.9873 | -16.9579 | -42.5144 | 9.9579 | 6.9578 | 1.0145 | -0.6222 | 2.417 | -1.6084 | 10.5783 | 3.4243 | 0.6094 | 0.6566 | 0.9542 | 0.7324 | -129.4978 | -1.2515 | 5.5778 | 1.5401 | -3.4608 | -1.9638 | 4.1668 |  | 2.5568 | -0.1995 | 4.0095 | 3.3632 | 3.343 | 1.0634 | 10.7545 | 14.2336 | 14.8478 | 11.0323 | -0.0003 | -0.0027 | 0.0007 | 0.0038 | 0.0004 | -0.0005 | 0.0136 | -0.0007 | -0.0055 | -360.2573 | 17.4397 | -360.4973 | 17.7026 | -360.8204 | 18.1625 | -360.8635 | 17.5445 | -352.7367 | 18.7703 | -352.7152 | 16.8361
12:22 | 3721 | 38.3063 | 200.9698 | 448.061 | 453.1379 | -17.1039 | -42.5205 | 9.9448 | 6.978 | 1.0065 | -0.6007 | 2.4202 | -1.5354 | 10.6098 | 3.446 | 0.6119 | 0.6573 | 0.96 | 0.7338 | -129.5622 | -1.2077 | 5.7753 | 1.4662 | -3.4048 | -1.8617 | 4.2262 |  | 2.5956 | -0.1899 | 4.0101 | 3.3624 | 3.3408 | 1.0643 | 10.6978 | 14.2229 | 14.7949 | 11.0515 | 0.0003 | -0.0032 | 0.0007 | 0.0037 | 0.0007 | -0.0008 | 0.0086 | -0.0017 | 0.0103 | -360.1034 | 17.3884 | -360.4789 | 17.721 | -360.842 | 18.1645 | -360.8481 | 17.4931 | -352.6413 | 18.723 | -352.6844 | 16.8669
12:22 | 3722 | 38.2507 | 200.9384 | 448.1284 | 453.0788 | -17.078 | -42.5555 | 10.0374 | 6.9478 | 1.09 | -0.6077 | 2.4628 | -1.5273 | 10.5474 | 3.4963 | 0.6115 | 0.6544 | 0.9595 | 0.732 | -129.5367 | -1.224 | 5.6612 | 1.518 | -3.4654 | -1.9831 | 4.1415 |  | 2.5637 | -0.2376 | 4.0083 | 3.3652 | 3.3432 | 1.0638 | 10.7197 | 14.228 | 14.8083 | 11.1013 | 0.0003 | -0.003 | 0.0012 | 0.0039 | 0.0008 | -0.0007 | 0.0112 | -0.016 | -0.0113 | -360.1465 | 17.3699 | -360.4142 | 17.6841 | -360.7989 | 18.1851 | -360.8974 | 17.5219 | -352.6229 | 18.7107 | -352.5921 | 16.8115
12:22 | 3723 | 38.2897 | 200.9421 | 448.1128 | 453.1092 | -17.0355 | -42.5257 | 9.9744 | 6.9337 | 1.1002 | -0.4829 | 2.4031 | -1.5269 | 10.6708 | 3.5745 | 0.611 | 0.6554 | 0.9602 | 0.733 | -129.5456 | -1.0615 | 5.5859 | 1.5375 | -3.4203 | -1.8699 | 4.1642 |  | 2.5744 | -0.1435 | 4.0109 | 3.3643 | 3.3428 | 1.0629 | 10.7405 | 14.2661 | 14.8461 | 11.1107 | -0.0002 | -0.0026 | 0.001 | 0.004 | 0.001 | -0.0004 | 0.0053 | -0.0125 | -0.0053 | -360.2235 | 17.4254 | -360.4666 | 17.6985 | -360.7835 | 18.1604 | -360.9004 | 17.5424 | -352.6906 | 18.7579 | -352.6506 | 16.8238
12:22 | 3724 | 38.2144 | 200.9463 | 448.0293 | 453.0535 | -17.029 | -42.4559 | 10.0335 | 6.9123 | 1.122 | -0.6254 | 2.4856 | -1.5478 | 10.6594 | 3.4773 | 0.609 | 0.6556 | 0.954 | 0.7303 | -129.5505 | -1.1162 | 5.6009 | 1.6293 | -3.4489 | -1.8243 | 4.2116 |  | 2.5871 | -0.188 | 4.0117 | 3.3637 | 3.3447 | 1.0649 | 10.7579 | 14.2487 | 14.8171 | 11.0645 | -0.0002 | -0.0025 | 0.0006 | 0.0037 | 0.0007 | -0.0003 | 0.0227 | -0.0158 | 0.0011 | -360.1958 | 17.4131 | -360.5312 | 17.7375 | -360.8543 | 18.1604 | -360.8604 | 17.5096 | -352.6567 | 18.7518 | -352.7121 | 16.8628
12:22 | 3725 | 38.2628 | 200.9851 | 448.1347 | 453.1558 | -16.9809 | -42.4858 | 9.9467 | 6.957 | 1.0948 | -0.5096 | 2.4578 | -1.5109 | 10.6499 | 3.5071 | 0.6103 | 0.6579 | 0.9591 | 0.7335 | -129.6223 | -1.1808 | 5.5702 | 1.5986 | -3.4922 | -1.847 | 4.1905 |  | 2.5155 | -0.1627 | 4.01 | 3.367 | 3.3409 | 1.0627 | 10.7462 | 14.2548 | 14.8714 | 11.0753 | 0.0002 | -0.0028 | 0.0012 | 0.0043 | 0.001 | 0.0002 | 0.0189 | 0.0089 | -0.0065 | -360.0973 | 17.3617 | -360.4142 | 17.6861 | -360.8174 | 18.1892 | -360.882 | 17.5096 | -352.6136 | 18.6861 | -352.6167 | 16.8443
12:22 | 3726 | 38.2714 | 201.0187 | 448.1022 | 453.1981 | -17.0371 | -42.5023 | 10.0051 | 6.8797 | 1.0298 | -0.5647 | 2.4158 | -1.5401 | 10.5756 | 3.5255 | 0.6113 | 0.6573 | 0.961 | 0.734 | -129.5843 | -1.12 | 5.5682 | 1.6433 | -3.5221 | -1.837 | 4.1778 |  | 2.6048 | -0.1212 | 4.0085 | 3.3644 | 3.3417 | 1.0628 | 10.7522 | 14.2717 | 14.845 | 11.0591 | 0.0003 | -0.0031 | 0.0002 | 0.0034 | 0.0008 | -0.0005 | -0.0032 | -0.0045 | -0.0084 | -360.1681 | 17.4028 | -360.4389 | 17.68 | -360.7866 | 18.1604 | -360.8543 | 17.5301 | -352.6567 | 18.721 | -352.629 | 16.8115
12:22 | 3727 | 38.2972 | 200.9536 | 448.0643 | 453.1158 | -17.0408 | -42.5905 | 9.9917 | 6.9137 | 0.9891 | -0.5917 | 2.3739 | -1.5165 | 10.6252 | 3.5744 | 0.6102 | 0.6578 | 0.958 | 0.7336 | -129.4904 | -1.1032 | 5.6176 | 1.5838 | -3.4228 | -1.9376 | 4.163 |  | 2.6024 | -0.1657 | 4.0096 | 3.3662 | 3.3448 | 1.0623 | 10.736 | 14.2496 | 14.8048 | 11.0779 | -0.0002 | -0.0028 | 0.0007 | 0.0043 | 0.0002 | -0.0005 | 0.0391 | -0.0111 | -0.005 | -360.1835 | 17.4377 | -360.525 | 17.7252 | -360.882 | 18.1584 | -360.8081 | 17.5219 | -352.6598 | 18.7641 | -352.7429 | 16.8607
12:22 | 3728 | 38.283 | 200.9243 | 448.0593 | 453.1846 | -17.0983 | -42.5342 | 10.0425 | 7.0113 | 1.1074 | -0.4931 | 2.4771 | -1.5702 | 10.6303 | 3.4372 | 0.6104 | 0.6573 | 0.9547 | 0.732 | -129.517 | -1.0575 | 5.5986 | 1.5703 | -3.5025 | -1.984 | 4.1126 |  | 2.5772 | -0.1323 | 4.0094 | 3.3607 | 3.3465 | 1.0623 | 10.7118 | 14.2367 | 14.785 | 11.0598 | -0.0001 | -0.0025 | 0.0007 | 0.0038 | 0.0008 | -0.0011 | 0.0102 | -0.0011 | 0.0071 | -360.1496 | 17.3925 | -360.4819 | 17.7149 | -360.8512 | 18.1871 | -360.8789 | 17.5096 | -352.6444 | 18.7251 | -352.6844 | 16.871
12:22 | 3729 | 38.3709 | 201.0099 | 448.1265 | 453.1435 | -16.9521 | -42.3796 | 10.144 | 6.9367 | 1.1301 | -0.5742 | 2.4393 | -1.4788 | 10.713 | 3.4687 | 0.6107 | 0.6577 | 0.9581 | 0.7326 | -129.4945 | -1.0894 | 5.626 | 1.5267 | -3.58 | -2.0229 | 4.1002 |  | 2.5974 | -0.058 | 4.009 | 3.3609 | 3.3396 | 1.0605 | 10.721 | 14.2401 | 14.7996 | 11.075 | 0 | -0.003 | 0.0002 | 0.0037 | 0.0004 | -0.0006 | 0.0109 | -0.0062 | -0.0096 | -360.1619 | 17.3864 | -360.3896 | 17.6533 | -360.765 | 18.1625 | -360.8604 | 17.526 | -352.669 | 18.7169 | -352.6321 | 16.8094
12:22 | 3730 | 38.3422 | 201.0852 | 448.0974 | 453.2499 | -16.9741 | -42.4435 | 10.1326 | 6.8699 | 1.1359 | -0.49 | 2.4702 | -1.4754 | 10.7576 | 3.5574 | 0.6118 | 0.659 | 0.9609 | 0.7351 | -129.5093 | -1.035 | 5.6341 | 1.6855 | -3.486 | -1.8482 | 4.1244 |  | 2.6013 | -0.0349 | 4.0086 | 3.3667 | 3.3416 | 1.0632 | 10.7255 | 14.2047 | 14.7725 | 11.0497 | 0.0004 | -0.0025 | 0.0012 | 0.0044 | 0.0007 | -0.0008 | 0.0063 | -0.0164 | 0.0173 | -360.2081 | 17.4336 | -360.5035 | 17.6861 | -360.7866 | 18.1358 | -360.7958 | 17.5137 | -352.6506 | 18.7436 | -352.7029 | 16.8238
12:22 | 3731 | 38.2494 | 200.9964 | 448.0592 | 453.1865 | -16.9707 | -42.4173 | 10.1126 | 6.8734 | 1.114 | -0.5204 | 2.5115 | -1.5391 | 10.6505 | 3.516 | 0.6112 | 0.6573 | 0.9596 | 0.7323 | -129.5508 | -1.0823 | 5.6389 | 1.6253 | -3.502 | -2.0462 | 4.0773 |  | 2.5846 | -0.1254 | 4.0085 | 3.3639 | 3.3418 | 1.0626 | 10.7556 | 14.2232 | 14.8318 | 11.097 | 0 | -0.0029 | 0.0007 | 0.0037 | 0.0005 | -0.0003 | 0.0143 | 0.0027 | -0.0134 | -360.1465 | 17.4254 | -360.5158 | 17.7293 | -360.8974 | 18.1748 | -360.8543 | 17.5137 | -352.6567 | 18.7415 | -352.7521 | 16.8566
12:22 | 3732 | 38.1708 | 200.9746 | 448.0568 | 453.1861 | -16.9725 | -42.4811 | 10.1593 | 6.9324 | 1.1173 | -0.4264 | 2.468 | -1.5297 | 10.6658 | 3.4803 | 0.6104 | 0.6587 | 0.958 | 0.7326 | -129.4515 | -1.0906 | 5.6143 | 1.5468 | -3.4754 | -1.9232 | 4.1207 |  | 2.5629 | -0.0997 | 4.0092 | 3.3668 | 3.3425 | 1.0631 | 10.7301 | 14.2383 | 14.8127 | 11.1002 | -0.0006 | -0.0027 | 0.001 | 0.004 | 0.0009 | -0.0008 | 0.0131 | -0.0158 | -0.0054 | -360.165 | 17.3925 | -360.4296 | 17.6882 | -360.842 | 18.2036 | -360.9158 | 17.5424 | -352.6567 | 18.7169 | -352.6444 | 16.8258
12:22 | 3733 | 38.33 | 201.0487 | 448.0744 | 453.2227 | -17.0024 | -42.5919 | 10.117 | 6.8928 | 1.1289 | -0.5173 | 2.3658 | -1.6119 | 10.6827 | 3.4958 | 0.6092 | 0.6564 | 0.9558 | 0.7326 | -129.449 | -1.0866 | 5.6959 | 1.4637 | -3.4818 | -1.9856 | 4.0354 |  | 2.5795 | -0.1325 | 4.0096 | 3.3623 | 3.3407 | 1.0622 | 10.7682 | 14.2536 | 14.8758 | 11.0915 | -0.0002 | -0.0029 | 0.0009 | 0.0038 | 0.0008 | -0.0005 | -0.0017 | -0.024 | -0.0133 | -360.2111 | 17.4131 | -360.4389 | 17.6533 | -360.7466 | 18.1296 | -360.845 | 17.5321 | -352.709 | 18.7353 | -352.6506 | 16.7971
12:22 | 3734 | 38.3734 | 201.0209 | 447.9513 | 453.2652 | -16.9847 | -42.57 | 10.1045 | 6.9005 | 1.0802 | -0.5692 | 2.4648 | -1.5968 | 10.6219 | 3.3992 | 0.6107 | 0.656 | 0.957 | 0.7318 | -129.5018 | -1.1578 | 5.5886 | 1.4873 | -3.456 | -2.0443 | 4.0987 |  | 2.5729 | -0.1323 | 4.0079 | 3.3645 | 3.3425 | 1.063 | 10.7601 | 14.2628 | 14.8615 | 11.1009 | -0.0001 | -0.0032 | 0.0002 | 0.0038 | 0.0008 | -0.0003 | 0.0143 | -0.015 | -0.0135 | -360.1681 | 17.4151 | -360.4789 | 17.6861 | -360.8297 | 18.1399 | -360.8327 | 17.5034 | -352.6537 | 18.7353 | -352.6967 | 16.8258
12:22 | 3735 | 38.3344 | 201.0359 | 448.0576 | 453.3094 | -16.9289 | -42.5388 | 10.1278 | 6.9205 | 1.138 | -0.4399 | 2.4606 | -1.6445 | 10.6352 | 3.4654 | 0.6116 | 0.6577 | 0.9586 | 0.7333 | -129.4022 | -1.1258 | 5.6906 | 1.5543 | -3.5114 | -1.9459 | 4.119 |  | 2.5336 | -0.0874 | 4.0099 | 3.3617 | 3.3422 | 1.0632 | 10.7232 | 14.2544 | 14.7871 | 11.088 | -0.0001 | -0.003 | 0.0008 | 0.0041 | 0.0008 | -0.0004 | -0.0051 | -0.0017 | 0.0043 | -360.1742 | 17.3987 | -360.4604 | 17.7108 | -360.845 | 18.2036 | -360.9127 | 17.5219 | -352.6352 | 18.7148 | -352.6813 | 16.832
12:22 | 3736 | 38.2268 | 201.0279 | 447.9118 | 453.2911 | -16.8627 | -42.4578 | 10.2253 | 6.887 | 1.1597 | -0.5508 | 2.4458 | -1.684 | 10.6378 | 3.3999 | 0.6113 | 0.6595 | 0.9569 | 0.7332 | -129.4372 | -1.227 | 5.6301 | 1.6291 | -3.5805 | -1.9859 | 4.1642 |  | 2.6188 | -0.0473 | 4.0099 | 3.3666 | 3.344 | 1.0642 | 10.7176 | 14.2423 | 14.7955 | 11.0544 | -0.0004 | -0.0028 | 0.0005 | 0.0041 | 0.0003 | -0.0004 | 0.0057 | 0.0053 | -0.0064 | -360.2173 | 17.4007 | -360.4573 | 17.6697 | -360.7743 | 18.1666 | -360.9435 | 17.5588 | -352.7213 | 18.7353 | -352.6598 | 16.8012
12:22 | 3737 | 38.3506 | 201.1118 | 448.0826 | 453.3311 | -16.9181 | -42.4932 | 10.1221 | 6.8908 | 1.222 | -0.4212 | 2.5918 | -1.6444 | 10.6873 | 3.4675 | 0.6111 | 0.6575 | 0.9569 | 0.7333 | -129.3649 | -1.1911 | 5.7481 | 1.6061 | -3.5915 | -1.9022 | 4.1638 |  | 2.6036 | 0.0124 | 4.0097 | 3.3627 | 3.3436 | 1.0625 | 10.7174 | 14.2023 | 14.7871 | 11.088 | -0.0001 | -0.0029 | 0.0007 | 0.0035 | 0.0013 | -0.0003 | 0.0075 | -0.0059 | -0.0038 | -360.1435 | 17.411 | -360.4758 | 17.6697 | -360.7527 | 18.1502 | -360.8358 | 17.5116 | -352.6383 | 18.7353 | -352.6752 | 16.8156
12:22 | 3738 | 38.3634 | 201.0998 | 448.0051 | 453.2976 | -16.9437 | -42.5016 | 10.1229 | 6.8574 | 1.2065 | -0.4812 | 2.4085 | -1.6213 | 10.6862 | 3.4036 | 0.6101 | 0.6557 | 0.956 | 0.7332 | -129.4402 | -1.2 | 5.7206 | 1.6934 | -3.5194 | -1.9047 | 4.1701 |  | 2.6253 | 0.0384 | 4.0092 | 3.3612 | 3.3422 | 1.0623 | 10.7463 | 14.214 | 14.794 | 11.0876 | 0.0002 | -0.0033 | 0.0018 | 0.0049 | 0.0006 | -0.0005 | 0.003 | -0.0066 | 0.0055 | -360.1404 | 17.3905 | -360.4789 | 17.7087 | -360.8389 | 18.1625 | -360.8235 | 17.5013 | -352.5798 | 18.7128 | -352.6444 | 16.8381
12:22 | 3739 | 38.4088 | 201.0645 | 448.0787 | 453.3573 | -16.8858 | -42.4382 | 10.2037 | 6.9144 | 1.1877 | -0.3972 | 2.5402 | -1.6017 | 10.6794 | 3.4313 | 0.6118 | 0.655 | 0.9595 | 0.7338 | -129.4494 | -1.2111 | 5.7449 | 1.7074 | -3.4585 | -1.897 | 4.2065 |  | 2.6757 | 0.0424 | 4.0097 | 3.3632 | 3.3435 | 1.0618 | 10.7325 | 14.2521 | 14.8086 | 11.0623 | 0 | -0.0029 | 0.0007 | 0.0036 | 0.0015 | -0.0003 | 0.0287 | -0.0118 | 0.008 | -360.205 | 17.3966 | -360.4296 | 17.682 | -360.8112 | 18.2056 | -360.9404 | 17.5527 | -352.6967 | 18.7189 | -352.6444 | 16.8094
12:22 | 3740 | 38.4064 | 201.088 | 448.0747 | 453.3705 | -16.8902 | -42.4247 | 10.1816 | 6.9262 | 1.1182 | -0.5232 | 2.4787 | -1.4815 | 10.7723 | 3.5007 | 0.6109 | 0.6571 | 0.9576 | 0.7338 | -129.408 | -1.3216 | 5.7731 | 1.8307 | -3.4758 | -1.9506 | 4.2262 |  | 2.599 | 0.0888 | 4.0086 | 3.3643 | 3.3441 | 1.0637 | 10.7277 | 14.2478 | 14.8179 | 11.0684 | -0.0002 | -0.0023 | 0.001 | 0.0038 | 0.0005 | -0.0004 | 0.0062 | -0.0112 | -0.0072 | -360.2388 | 17.4274 | -360.4758 | 17.6841 | -360.7897 | 18.1543 | -360.882 | 17.5404 | -352.6998 | 18.7477 | -352.709 | 16.8176
12:22 | 3741 | 38.3177 | 201.0411 | 448.1477 | 453.307 | -16.9503 | -42.5262 | 10.1882 | 6.911 | 1.1224 | -0.5499 | 2.5305 | -1.5323 | 10.682 | 3.5271 | 0.6104 | 0.6578 | 0.9574 | 0.7333 | -129.3728 | -1.281 | 5.7875 | 1.8025 | -3.5045 | -1.8997 | 4.2365 |  | 2.6474 | 0.0507 | 4.0095 | 3.3657 | 3.344 | 1.0628 | 10.7579 | 14.2601 | 14.8334 | 11.0764 | -0.0006 | -0.0029 | 0.0007 | 0.0041 | 0.0005 | -0.0004 | 0.0114 | -0.0133 | 0.0054 | -360.1219 | 17.3782 | -360.4604 | 17.7169 | -360.8358 | 18.1563 | -360.8297 | 17.4849 | -352.5952 | 18.7148 | -352.669 | 16.8464
12:22 | 3742 | 38.3176 | 201.0547 | 448.0351 | 453.4193 | -16.9 | -42.6075 | 10.2391 | 6.8353 | 1.1004 | -0.4927 | 2.4582 | -1.4431 | 10.5784 | 3.4818 | 0.612 | 0.6575 | 0.9594 | 0.7322 | -129.395 | -1.3198 | 5.6771 | 1.8068 | -3.4696 | -1.8802 | 4.2229 |  | 2.619 | -0.023 | 4.0102 | 3.363 | 3.3419 | 1.063 | 10.7623 | 14.277 | 14.8605 | 11.0734 | 0.0004 | -0.0027 | 0.0011 | 0.0043 | 0.0004 | -0.0005 | 0.0097 | 0.0006 | -0.0115 | -360.1527 | 17.3679 | -360.4296 | 17.6779 | -360.8112 | 18.1871 | -360.9189 | 17.5137 | -352.6044 | 18.7004 | -352.5983 | 16.8053
12:22 | 3743 | 38.3393 | 201.0573 | 447.9537 | 453.4342 | -16.9503 | -42.5854 | 10.2469 | 6.7634 | 1.0826 | -0.539 | 2.4324 | -1.5121 | 10.6642 | 3.4405 | 0.6104 | 0.6584 | 0.9589 | 0.7322 | -129.3934 | -1.2018 | 5.7361 | 1.7801 | -3.5047 | -1.8881 | 4.1696 |  | 2.6696 | 0.0672 | 4.009 | 3.3661 | 3.3407 | 1.0636 | 10.7545 | 14.2567 | 14.8304 | 11.0728 | -0.0001 | -0.0031 | 0.0006 | 0.0043 | 0.0009 | -0.0004 | 0.0139 | -0.011 | -0.0151 | -360.2542 | 17.4274 | -360.5004 | 17.6841 | -360.8112 | 18.1584 | -360.8727 | 17.5465 | -352.7275 | 18.7641 | -352.6967 | 16.8135
12:22 | 3744 | 38.3259 | 201.1153 | 448.0675 | 453.4515 | -16.9227 | -42.5194 | 10.3219 | 6.8652 | 1.1181 | -0.5272 | 2.4576 | -1.495 | 10.676 | 3.5887 | 0.6103 | 0.6551 | 0.9577 | 0.7314 | -129.39 | -1.1955 | 5.696 | 1.7956 | -3.4655 | -1.8681 | 4.2235 |  | 2.641 | -0.0075 | 4.0098 | 3.3642 | 3.3405 | 1.0629 | 10.7337 | 14.2474 | 14.8263 | 11.0464 | -0.0001 | -0.0027 | 0.0008 | 0.004 | 0.0004 | -0.0007 | 0.0098 | -0.0135 | -0.0126 | -360.1558 | 17.4131 | -360.525 | 17.7293 | -360.8727 | 18.1666 | -360.8327 | 17.5013 | -352.6475 | 18.7415 | -352.7244 | 16.8546
12:22 | 3745 | 38.432 | 201.147 | 448.0526 | 453.368 | -16.9042 | -42.47 | 10.316 | 6.923 | 1.1084 | -0.5498 | 2.402 | -1.5042 | 10.6118 | 3.6222 | 0.6121 | 0.661 | 0.9594 | 0.7317 | -129.3718 | -1.2428 | 5.7616 | 1.7939 | -3.4723 | -1.8787 | 4.1703 |  | 2.6117 | 0.0219 | 4.0073 | 3.3636 | 3.3436 | 1.0626 | 10.751 | 14.2302 | 14.8447 | 11.0461 | -0.0001 | -0.0026 | 0.0009 | 0.004 | 0.0006 | -0.0006 | 0.0151 | -0.0127 | 0.0013 | -360.1373 | 17.374 | -360.405 | 17.6779 | -360.8081 | 18.1748 | -360.8543 | 17.5157 | -352.6321 | 18.7004 | -352.626 | 16.8176
12:22 | 3746 | 38.3577 | 201.1399 | 448.1585 | 453.5109 | -16.9157 | -42.4065 | 10.2344 | 6.9052 | 1.1507 | -0.4841 | 2.4338 | -1.5327 | 10.6607 | 3.5188 | 0.6113 | 0.6577 | 0.958 | 0.7321 | -129.3131 | -1.2421 | 5.7746 | 1.7623 | -3.4831 | -1.9174 | 4.1793 |  | 2.5709 | -0.0387 | 4.0084 | 3.3627 | 3.3453 | 1.0646 | 10.729 | 14.237 | 14.8219 | 11.0648 | 0.0001 | -0.0029 | 0.0008 | 0.0036 | 0.0013 | -0.0004 | 0.0005 | -0.0133 | -0.0101 | -360.1958 | 17.4192 | -360.4419 | 17.643 | -360.7404 | 18.1379 | -360.8543 | 17.5301 | -352.666 | 18.7353 | -352.6506 | 16.7786
12:22 | 3747 | 38.3255 | 201.1127 | 448.1502 | 453.3834 | -16.959 | -42.4778 | 10.1222 | 6.8014 | 1.0636 | -0.5732 | 2.4851 | -1.5614 | 10.6305 | 3.4815 | 0.6103 | 0.658 | 0.9623 | 0.7346 | -129.3463 | -1.2642 | 5.7588 | 1.7348 | -3.374 | -1.9467 | 4.2029 |  | 2.6043 | 0.0021 | 4.0089 | 3.366 | 3.3435 | 1.0651 | 10.736 | 14.2035 | 14.7885 | 11.0601 | 0.0004 | -0.0029 | 0.0007 | 0.003 | 0.0006 | -0.0005 | -0.0027 | -0.0083 | -0.0323 | -360.1804 | 17.4336 | -360.5219 | 17.719 | -360.8727 | 18.1666 | -360.8204 | 17.5055 | -352.6629 | 18.7477 | -352.7244 | 16.8423
12:22 | 3748 | 38.3881 | 201.1888 | 448.1234 | 453.5212 | -16.9139 | -42.3575 | 10.1532 | 6.8348 | 1.0612 | -0.5137 | 2.4784 | -1.4633 | 10.601 | 3.4873 | 0.6117 | 0.6586 | 0.9579 | 0.7326 | -129.3762 | -1.2043 | 5.7151 | 1.7345 | -3.5254 | -1.8758 | 4.1078 |  | 2.6283 | -0.0256 | 4.0085 | 3.363 | 3.3429 | 1.0629 | 10.7371 | 14.2161 | 14.7946 | 11.0674 | -0.0001 | -0.0028 | 0.0007 | 0.0036 | 0.0008 | -0.0007 | 0.0045 | -0.016 | -0.0163 | -360.1404 | 17.4007 | -360.445 | 17.6964 | -360.8512 | 18.2118 | -360.9097 | 17.5363 | -352.6537 | 18.723 | -352.6752 | 16.8381
12:22 | 3749 | 38.3976 | 201.2622 | 448.0928 | 453.5198 | -16.8756 | -42.3336 | 10.2691 | 6.9369 | 1.2147 | -0.4651 | 2.5574 | -1.4055 | 10.7166 | 3.5403 | 0.6103 | 0.6571 | 0.9586 | 0.732 | -129.4381 | -1.2588 | 5.7561 | 1.7342 | -3.5158 | -1.9077 | 4.2055 |  | 2.622 | 0.0367 | 4.0073 | 3.36 | 3.3432 | 1.0635 | 10.7209 | 14.2637 | 14.826 | 11.097 | -0.0002 | -0.0025 | 0.0004 | 0.0039 | 0.0005 | -0.0001 | -0.0047 | -0.0127 | -0.0146 | -360.2419 | 17.4028 | -360.4266 | 17.6636 | -360.7497 | 18.142 | -360.8697 | 17.5404 | -352.709 | 18.7415 | -352.6598 | 16.8012
12:22 | 3750 | 38.3274 | 201.1385 | 448.0669 | 453.4527 | -16.8608 | -42.4172 | 10.2366 | 7.0024 | 1.208 | -0.4186 | 2.5211 | -1.5209 | 10.5402 | 3.5229 | 0.6096 | 0.6575 | 0.956 | 0.7334 | -129.4432 | -1.2178 | 5.7469 | 1.7139 | -3.4015 | -1.8337 | 4.2222 |  | 2.5977 | 0.0217 | 4.0088 | 3.3612 | 3.341 | 1.0631 | 10.7209 | 14.2637 | 14.8028 | 11.0796 | 0.0004 | -0.0028 | 0.0005 | 0.0039 | 0.001 | -0.0007 | 0.0208 | -0.0186 | 0.0153 | -360.1558 | 17.409 | -360.4758 | 17.6861 | -360.7681 | 18.1296 | -360.8204 | 17.4972 | -352.6413 | 18.7333 | -352.6721 | 16.8176
12:22 | 3751 | 38.2799 | 201.0974 | 448.0209 | 453.4682 | -16.8637 | -42.3832 | 10.2051 | 6.9334 | 1.2054 | -0.4543 | 2.4763 | -1.5037 | 10.6024 | 3.5287 | 0.6112 | 0.6572 | 0.9581 | 0.7338 | -129.3877 | -1.1994 | 5.7283 | 1.6623 | -3.4351 | -1.8014 | 4.179 |  | 2.6094 | 0.0214 | 4.0099 | 3.3657 | 3.3473 | 1.0651 | 10.7336 | 14.2186 | 14.8216 | 11.0981 | 0.0003 | -0.0026 | 0.0009 | 0.0046 | 0.0006 | 0 | 0.0136 | -0.0079 | -0.0004 | -360.1588 | 17.3843 | -360.4635 | 17.7026 | -360.8543 | 18.1933 | -360.8758 | 17.5096 | -352.6075 | 18.7045 | -352.6629 | 16.834
12:22 | 3752 | 38.3217 | 201.209 | 448.0664 | 453.5128 | -16.8638 | -42.3066 | 10.2477 | 6.8046 | 1.1823 | -0.5737 | 2.4263 | -1.5223 | 10.5721 | 3.4814 | 0.6113 | 0.6561 | 0.9579 | 0.732 | -129.4927 | -1.2565 | 5.6172 | 1.7327 | -3.4099 | -1.8383 | 4.278 |  | 2.6549 | 0.0479 | 4.0087 | 3.3647 | 3.3449 | 1.0648 | 10.7394 | 14.2302 | 14.7984 | 11.0634 | 0 | -0.0027 | 0.0009 | 0.004 | 0.0009 | -0.0009 | 0.0185 | -0.0144 | -0.0087 | -360.2696 | 17.4069 | -360.4512 | 17.6759 | -360.7804 | 18.1851 | -360.9251 | 17.5588 | -352.7121 | 18.7415 | -352.666 | 16.8032
12:22 | 3753 | 38.4382 | 201.1191 | 448.1167 | 453.5273 | -16.9622 | -42.4205 | 10.0765 | 6.8364 | 1.2693 | -0.4587 | 2.5085 | -1.5275 | 10.6038 | 3.421 | 0.6116 | 0.6553 | 0.9605 | 0.7333 | -129.4792 | -1.2363 | 5.6444 | 1.6733 | -3.5089 | -1.9046 | 4.1203 |  | 2.7389 | 0.0703 | 4.0096 | 3.3619 | 3.3441 | 1.0644 | 10.7637 | 14.2428 | 14.8392 | 11.0591 | -0.0004 | -0.0026 | 0.0004 | 0.0037 | 0.0004 | -0.0006 | 0.0149 | -0.0163 | -0.0005 | -360.1619 | 17.4131 | -360.4481 | 17.68 | -360.802 | 18.1337 | -360.8266 | 17.5137 | -352.6598 | 18.7538 | -352.6998 | 16.8135
12:22 | 3754 | 38.4967 | 201.1247 | 448.1387 | 453.6191 | -16.9466 | -42.3602 | 10.1713 | 6.841 | 1.2632 | -0.6694 | 2.4784 | -1.6253 | 10.5384 | 3.4408 | 0.6109 | 0.6555 | 0.9564 | 0.7322 | -129.4253 | -1.2211 | 5.6846 | 1.6669 | -3.5364 | -1.9317 | 4.1767 |  | 2.7903 | 0.0299 | 4.0094 | 3.3643 | 3.3418 | 1.0654 | 10.7418 | 14.2438 | 14.7759 | 11.0432 | 0.0002 | -0.0029 | 0.0007 | 0.0034 | 0.0008 | -0.0005 | 0.0112 | 0.0012 | -0.0231 | -360.1404 | 17.374 | -360.4419 | 17.6944 | -360.8204 | 18.1625 | -360.8266 | 17.4911 | -352.589 | 18.7004 | -352.6506 | 16.8197
12:22 | 3755 | 38.3616 | 201.0928 | 448.0306 | 453.5628 | -16.9317 | -42.3243 | 10.2331 | 6.8717 | 1.2551 | -0.4631 | 2.5138 | -1.5462 | 10.5813 | 3.4791 | 0.6098 | 0.6535 | 0.9573 | 0.7326 | -129.455 | -1.2623 | 5.6032 | 1.4806 | -3.4803 | -1.9139 | 4.1994 |  | 2.7135 | 0.0511 | 4.0078 | 3.3618 | 3.3392 | 1.0634 | 10.7371 | 14.2508 | 14.7946 | 11.0616 | 0.0002 | -0.0036 | 0.0004 | 0.0031 | 0.0006 | -0.0007 | -0.0077 | -0.0012 | -0.0184 | -360.1927 | 17.3925 | -360.4173 | 17.6656 | -360.7958 | 18.1912 | -360.9312 | 17.5486 | -352.6783 | 18.7189 | -352.6352 | 16.7991
12:22 | 3756 | 38.4048 | 201.1617 | 448.1343 | 453.5346 | -16.8678 | -42.3142 | 10.2527 | 6.9384 | 1.2433 | -0.6356 | 2.5056 | -1.5346 | 10.621 | 3.5073 | 0.6103 | 0.6555 | 0.9596 | 0.7341 | -129.4612 | -1.1881 | 5.6481 | 1.5176 | -3.4122 | -1.8173 | 4.1767 |  | 2.6654 | 0.0225 | 4.008 | 3.362 | 3.3427 | 1.0647 | 10.744 | 14.2695 | 14.7912 | 11.0796 | -0.0002 | -0.0028 | 0.0008 | 0.0038 | 0.0007 | -0.0003 | 0.0107 | -0.016 | -0.0265 | -360.2481 | 17.4295 | -360.5004 | 17.682 | -360.802 | 18.1645 | -360.8697 | 17.5424 | -352.6967 | 18.7559 | -352.7121 | 16.8279
12:22 | 3757 | 38.4348 | 201.0899 | 448.044 | 453.4947 | -16.8281 | -42.2588 | 10.2459 | 6.9194 | 1.2394 | -0.6356 | 2.4542 | -1.6733 | 10.5627 | 3.4689 | 0.6109 | 0.6521 | 0.9596 | 0.7341 | -129.3965 | -1.1134 | 5.7028 | 1.5913 | -3.3469 | -1.8929 | 4.2136 |  | 2.6168 | 0.0082 | 4.0085 | 3.3618 | 3.344 | 1.0635 | 10.7486 | 14.2686 | 14.8383 | 11.1009 | -0.0002 | -0.0027 | 0.0007 | 0.0039 | 0.0012 | -0.0006 | 0.0168 | -0.0192 | -0.004 | -360.1034 | 17.3966 | -360.4727 | 17.7128 | -360.8666 | 18.1625 | -360.8358 | 17.4972 | -352.6198 | 18.7189 | -352.6875 | 16.8525
12:22 | 3758 | 38.4035 | 201.1644 | 448.0296 | 453.522 | -16.8001 | -42.3253 | 10.2463 | 6.8789 | 1.287 | -0.4655 | 2.4682 | -1.6189 | 10.5773 | 3.5214 | 0.6102 | 0.6528 | 0.9582 | 0.7331 | -129.4626 | -1.1087 | 5.7238 | 1.6525 | -3.3711 | -1.846 | 4.1912 |  | 2.6869 | 0.0646 | 4.008 | 3.3651 | 3.3442 | 1.0647 | 10.7786 | 14.2757 | 14.835 | 11.1132 | -0.0001 | -0.0027 | 0.001 | 0.004 | 0.0003 | -0.0003 | -0.0051 | -0.0024 | -0.0207 | -360.1404 | 17.3679 | -360.3896 | 17.6615 | -360.7927 | 18.1707 | -360.8758 | 17.5075 | -352.5952 | 18.684 | -352.6167 | 16.8032
12:22 | 3759 | 38.4188 | 201.1242 | 448.0861 | 453.5566 | -16.943 | -42.2476 | 10.0656 | 6.8705 | 1.31 | -0.5106 | 2.5022 | -1.4962 | 10.5761 | 3.5207 | 0.6104 | 0.6583 | 0.957 | 0.7339 | -129.4805 | -1.0559 | 5.7427 | 1.5452 | -3.2772 | -1.84 | 4.2083 |  | 2.6746 | -0.0533 | 4.0082 | 3.366 | 3.3446 | 1.0639 | 10.7578 | 14.2664 | 14.8193 | 11.1042 | 0.0002 | -0.003 | 0.0006 | 0.0043 | 0.0012 | -0.0007 | 0.0215 | -0.0026 | -0.0138 | -360.2604 | 17.4172 | -360.445 | 17.6677 | -360.7743 | 18.1522 | -360.8727 | 17.5424 | -352.6783 | 18.7353 | -352.6629 | 16.795
12:22 | 3760 | 38.4595 | 201.2379 | 448.1481 | 453.6263 | -16.9073 | -42.257 | 10.1117 | 6.8961 | 1.3343 | -0.5488 | 2.5069 | -1.4299 | 10.6678 | 3.5537 | 0.6113 | 0.6582 | 0.9573 | 0.7346 | -129.408 | -1.036 | 5.7812 | 1.4545 | -3.2975 | -1.8637 | 4.1695 |  | 2.6584 | -0.1045 | 4.0088 | 3.3675 | 3.3464 | 1.064 | 10.7476 | 14.2496 | 14.828 | 11.101 | -0.0004 | -0.0033 | 0.0005 | 0.0039 | 0.0003 | -0.0005 | 0.0045 | -0.0031 | -0.0013 | -360.1773 | 17.4377 | -360.525 | 17.7436 | -360.8727 | 18.1789 | -360.8235 | 17.5096 | -352.6783 | 18.7477 | -352.7337 | 16.8607
12:22 | 3761 | 38.4342 | 201.1358 | 448.0713 | 453.577 | -16.921 | -42.3217 | 10.1101 | 6.9443 | 1.3365 | -0.4473 | 2.615 | -1.4609 | 10.6188 | 3.5681 | 0.6112 | 0.6575 | 0.9532 | 0.7325 | -129.4073 | -1.1865 | 5.7505 | 1.5271 | -3.3337 | -1.8932 | 4.1594 |  | 2.5939 | -0.1556 | 4.0087 | 3.364 | 3.3422 | 1.0639 | 10.7278 | 14.2649 | 14.8216 | 11.0807 | -0.0005 | -0.0028 | 0.0006 | 0.0034 | 0.0008 | -0.0009 | 0.0052 | -0.0041 | -0.0061 | -360.1219 | 17.3823 | -360.4542 | 17.7108 | -360.8604 | 18.2015 | -360.9004 | 17.5178 | -352.6413 | 18.7045 | -352.6721 | 16.8443
12:22 | 3762 | 38.4841 | 201.1114 | 448.1159 | 453.5559 | -16.8921 | -42.294 | 10.0708 | 6.9838 | 1.3167 | -0.5302 | 2.5664 | -1.5381 | 10.6405 | 3.5768 | 0.6117 | 0.6539 | 0.9588 | 0.7336 | -129.4588 | -1.1285 | 5.6912 | 1.4209 | -3.3668 | -1.9593 | 4.1263 |  | 2.5936 | -0.0341 | 4.0081 | 3.3633 | 3.3413 | 1.0646 | 10.7141 | 14.2102 | 14.7704 | 11.0331 | -0.0005 | -0.0034 | 0.0009 | 0.0038 | 0.0008 | -0.0002 | -0.008 | -0.0078 | 0.0054 | -360.1681 | 17.3966 | -360.4112 | 17.6512 | -360.7589 | 18.1461 | -360.8758 | 17.5342 | -352.669 | 18.7271 | -352.626 | 16.7991
12:22 | 3763 | 38.3484 | 201.1277 | 448.0049 | 453.5537 | -16.8804 | -42.2224 | 10.3115 | 6.9554 | 1.2596 | -0.5106 | 2.5348 | -1.5453 | 10.5954 | 3.5562 | 0.6102 | 0.6522 | 0.957 | 0.7308 | -129.4436 | -1.1658 | 5.7068 | 1.6775 | -3.3398 | -1.8209 | 4.1347 |  | 2.5277 | -0.1005 | 4.0083 | 3.3595 | 3.3368 | 1.0633 | 10.7325 | 14.2289 | 14.8191 | 11.0569 | 0.0002 | -0.0032 | 0.0011 | 0.004 | 0.0008 | -0.0009 | 0.0066 | 0.0039 | -0.0151 | -360.1527 | 17.4192 | -360.4912 | 17.6923 | -360.8112 | 18.1255 | -360.7773 | 17.4849 | -352.6136 | 18.7333 | -352.6813 | 16.8299
12:22 | 3764 | 38.4274 | 201.3123 | 448.1575 | 453.6942 | -16.9306 | -42.3123 | 10.1703 | 6.9517 | 1.3151 | -0.4708 | 2.5577 | -1.5045 | 10.673 | 3.6178 | 0.6091 | 0.6535 | 0.9601 | 0.7325 | -129.3794 | -1.1589 | 5.8075 | 1.7237 | -3.343 | -1.7634 | 4.1838 |  | 2.5346 | -0.1355 | 4.0091 | 3.3635 | 3.341 | 1.064 | 10.7302 | 14.2382 | 14.8059 | 11.0659 | 0.0003 | -0.0034 | 0.0007 | 0.0036 | 0.001 | -0.0001 | 0.0157 | -0.0075 | -0.0093 | -360.165 | 17.3946 | -360.4666 | 17.7169 | -360.8481 | 18.1707 | -360.885 | 17.5013 | -352.6229 | 18.7128 | -352.669 | 16.8279
12:22 | 3765 | 38.4327 | 201.2943 | 448.1847 | 453.6112 | -16.9708 | -42.3654 | 9.983 | 6.9866 | 1.3571 | -0.4712 | 2.6133 | -1.5925 | 10.6744 | 3.6018 | 0.6103 | 0.6559 | 0.9583 | 0.7325 | -129.4056 | -1.1958 | 5.8447 | 1.6951 | -3.3048 | -1.8494 | 4.221 |  | 2.5734 | -0.2181 | 4.0082 | 3.3665 | 3.3452 | 1.0647 | 10.7648 | 14.2674 | 14.8543 | 11.1172 | -0.0002 | -0.0027 | 0.0005 | 0.0042 | 0.0009 | -0.0003 | 0.0001 | -0.012 | -0.0197 | -360.245 | 17.4131 | -360.4789 | 17.6902 | -360.7927 | 18.1666 | -360.9343 | 17.5609 | -352.6998 | 18.7333 | -352.6875 | 16.8156
12:22 | 3766 | 38.4454 | 201.2801 | 448.1908 | 453.6475 | -16.9937 | -42.3925 | 9.9496 | 6.9289 | 1.3585 | -0.5017 | 2.6124 | -1.5613 | 10.5933 | 3.5812 | 0.6096 | 0.6481 | 0.9538 | 0.7324 | -129.3586 | -1.1516 | 5.7375 | 1.6707 | -3.2563 | -1.823 | 4.2642 |  | 2.6033 | -0.1456 | 4.0082 | 3.3631 | 3.3424 | 1.0643 | 10.7705 | 14.2676 | 14.8612 | 11.111 | -0.0002 | -0.0025 | 0.0007 | 0.0039 | 0.0009 | -0.0004 | 0.0092 | -0.0063 | -0.0327 | -360.205 | 17.4356 | -360.4942 | 17.7128 | -360.8112 | 18.1173 | -360.8266 | 17.5137 | -352.6844 | 18.7559 | -352.7275 | 16.834
12:22 | 3767 | 38.4549 | 201.2283 | 448.2205 | 453.6772 | -17.0481 | -42.5331 | 9.8477 | 6.9258 | 1.2688 | -0.5005 | 2.5451 | -1.53 | 10.6421 | 3.5255 | 0.6115 | 0.6555 | 0.9574 | 0.7313 | -129.3746 | -1.1779 | 5.66 | 1.7072 | -3.2426 | -1.7774 | 4.3392 |  | 2.6428 | -0.1451 | 4.0079 | 3.3645 | 3.3421 | 1.0643 | 10.7452 | 14.2475 | 14.8216 | 11.0981 | 0.0004 | -0.003 | 0.0002 | 0.0036 | 0.0007 | -0.0002 | 0.0157 | -0.0103 | -0.0079 | -360.1096 | 17.3802 | -360.4327 | 17.6944 | -360.8235 | 18.1379 | -360.8512 | 17.489 | -352.5952 | 18.7025 | -352.6537 | 16.832
12:23 | 3768 | 38.4117 | 201.2123 | 448.1091 | 453.6804 | -17.0565 | -42.5193 | 9.9658 | 6.9273 | 1.2864 | -0.4843 | 2.4126 | -1.5563 | 10.6352 | 3.5459 | 0.61 | 0.6583 | 0.9584 | 0.734 | -129.4202 | -1.1293 | 5.7313 | 1.7011 | -3.215 | -1.8164 | 4.3034 |  | 2.7128 | -0.2165 | 4.0086 | 3.3608 | 3.3386 | 1.0644 | 10.7683 | 14.3055 | 14.8342 | 11.1035 | 0.0002 | -0.0027 | 0.0007 | 0.004 | 0.0008 | -0.0007 | 0.0168 | -0.0053 | 0 | -360.205 | 17.3823 | -360.3989 | 17.6533 | -360.7558 | 18.1461 | -360.882 | 17.5342 | -352.6598 | 18.6984 | -352.5952 | 16.7827
12:23 | 3769 | 38.4615 | 201.1749 | 448.093 | 453.679 | -17.0099 | -42.4347 | 10.0884 | 6.9464 | 1.2563 | -0.5332 | 2.4472 | -1.6005 | 10.5999 | 3.4803 | 0.6103 | 0.6553 | 0.9567 | 0.7322 | -129.4478 | -1.0609 | 5.7049 | 1.7307 | -3.2408 | -1.7916 | 4.363 |  | 2.6329 | -0.1777 | 4.0079 | 3.3604 | 3.3414 | 1.0648 | 10.7348 | 14.2601 | 14.8334 | 11.0648 | -0.0005 | -0.003 | 0.0004 | 0.0031 | 0.0003 | -0.0002 | 0.0119 | -0.0107 | -0.0083 | -360.2173 | 17.4418 | -360.5127 | 17.7026 | -360.8235 | 18.1276 | -360.8204 | 17.5239 | -352.7121 | 18.7497 | -352.7029 | 16.8176
12:23 | 3770 | 38.4919 | 201.0984 | 448.0463 | 453.6617 | -17.0363 | -42.4352 | 10.0144 | 6.9392 | 1.2355 | -0.5013 | 2.3714 | -1.4913 | 10.6924 | 3.5558 | 0.6107 | 0.6558 | 0.9577 | 0.7327 | -129.4229 | -1.1203 | 5.743 | 1.732 | -3.2344 | -1.6281 | 4.3669 |  | 2.583 | -0.2093 | 4.009 | 3.3605 | 3.3389 | 1.0633 | 10.7107 | 14.1949 | 14.7999 | 11.0418 | -0.0003 | -0.0029 | 0.0006 | 0.0036 | 0.0009 | -0.0008 | 0.0154 | -0.0184 | -0.0033 | -360.1435 | 17.4007 | -360.4942 | 17.7395 | -360.8727 | 18.1748 | -360.8881 | 17.5219 | -352.6413 | 18.7251 | -352.6906 | 16.8648
12:23 | 3771 | 38.4412 | 201.1353 | 448.2671 | 453.6707 | -16.9911 | -42.45 | 10.0451 | 6.9517 | 1.2524 | -0.3973 | 2.386 | -1.5419 | 10.6625 | 3.5348 | 0.6097 | 0.6588 | 0.9582 | 0.7314 | -129.4982 | -1.0476 | 5.6758 | 1.8076 | -3.1849 | -1.7294 | 4.3335 |  | 2.5343 | -0.1297 | 4.0092 | 3.3623 | 3.3421 | 1.065 | 10.7059 | 14.2197 | 14.7756 | 11.0533 | 0.0003 | -0.0027 | 0.0013 | 0.004 | 0.0005 | 0 | 0.009 | -0.004 | -0.0157 | -360.1927 | 17.4069 | -360.4235 | 17.6697 | -360.7958 | 18.1584 | -360.9343 | 17.5629 | -352.7183 | 18.7292 | -352.629 | 16.8094
12:23 | 3772 | 38.5178 | 201.1456 | 448.1495 | 453.6861 | -16.9714 | -42.4423 | 10.0116 | 6.8826 | 1.2413 | -0.4707 | 2.3761 | -1.4683 | 10.6732 | 3.5496 | 0.6116 | 0.6568 | 0.9609 | 0.7323 | -129.4435 | -1.1976 | 5.6421 | 1.862 | -3.1351 | -1.6559 | 4.445 |  | 2.6344 | -0.02 | 4.0093 | 3.3623 | 3.3422 | 1.0653 | 10.7118 | 14.2194 | 14.8024 | 11.0483 | 0.0001 | -0.0032 | 0.0006 | 0.0036 | 0.0007 | -0.0011 | 0.0107 | -0.0091 | -0.0056 | -360.1681 | 17.4028 | -360.4666 | 17.6697 | -360.7404 | 18.1132 | -360.8543 | 17.5321 | -352.6875 | 18.7436 | -352.6629 | 16.8115
12:23 | 3773 | 38.527 | 201.1352 | 448.2127 | 453.6607 | -16.9106 | -42.4365 | 9.9694 | 6.9286 | 1.2756 | -0.5349 | 2.3573 | -1.4626 | 10.6743 | 3.5617 | 0.6099 | 0.6569 | 0.9574 | 0.7333 | -129.4947 | -1.1721 | 5.6452 | 1.8079 | -3.1392 | -1.6781 | 4.3824 |  | 2.6054 | -0.0382 | 4.0095 | 3.3658 | 3.3432 | 1.0646 | 10.7324 | 14.2465 | 14.7923 | 11.0793 | 0.0002 | -0.0026 | 0.0006 | 0.0044 | 0.0006 | -0.0002 | 0.0075 | -0.0095 | -0.013 | -360.0911 | 17.374 | -360.4389 | 17.7087 | -360.845 | 18.1317 | -360.8358 | 17.4972 | -352.5983 | 18.7004 | -352.666 | 16.8279
12:23 | 3774 | 38.5469 | 201.1523 | 448.2201 | 453.6666 | -16.9355 | -42.4026 | 10.02 | 6.923 | 1.2847 | -0.6015 | 2.3896 | -1.5404 | 10.6211 | 3.5265 | 0.6103 | 0.6566 | 0.9602 | 0.7341 | -129.4201 | -1.2167 | 5.675 | 1.7046 | -3.2189 | -1.8137 | 4.4197 |  | 2.6649 | -0.0134 | 4.009 | 3.3616 | 3.3402 | 1.0651 | 10.759 | 14.2674 | 14.8254 | 11.0594 | -0.0002 | -0.0026 | 0.0004 | 0.0037 | 0.001 | -0.0001 | 0.0068 | 0.0016 | 0.0004 | -360.1896 | 17.3699 | -360.3835 | 17.6759 | -360.7835 | 18.1645 | -360.9066 | 17.5404 | -352.6537 | 18.6984 | -352.6106 | 16.795
12:23 | 3775 | 38.5256 | 201.1624 | 448.1869 | 453.6526 | -16.8421 | -42.4121 | 10.134 | 6.8887 | 1.2981 | -0.5335 | 2.416 | -1.4873 | 10.7063 | 3.557 | 0.6101 | 0.6577 | 0.9593 | 0.7329 | -129.3907 | -1.1144 | 5.6658 | 1.6387 | -3.2464 | -1.7807 | 4.2622 |  | 2.6122 | -0.1048 | 4.0081 | 3.363 | 3.3426 | 1.0629 | 10.7925 | 14.2721 | 14.8598 | 11.0984 | -0.0002 | -0.0028 | 0.0006 | 0.004 | 0.0008 | -0.0002 | 0.0057 | -0.0022 | -0.0129 | -360.2542 | 17.4377 | -360.4819 | 17.6923 | -360.7773 | 18.1276 | -360.885 | 17.565 | -352.6752 | 18.7395 | -352.6875 | 16.8135
12:23 | 3776 | 38.5507 | 201.2305 | 448.1942 | 453.7525 | -16.7958 | -42.3646 | 10.1593 | 6.8811 | 1.3209 | -0.5543 | 2.3826 | -1.4809 | 10.6756 | 3.4259 | 0.6111 | 0.6564 | 0.959 | 0.7332 | -129.4014 | -1.1911 | 5.7498 | 1.6502 | -3.2701 | -1.8314 | 4.3364 |  | 2.6073 | -0.0728 | 4.009 | 3.3618 | 3.3443 | 1.0643 | 10.7361 | 14.2437 | 14.8037 | 11.0898 | -0.0002 | -0.0034 | 0.0008 | 0.0038 | 0.0009 | -0.0004 | 0.0081 | -0.008 | -0.0217 | -360.1835 | 17.4131 | -360.5096 | 17.7334 | -360.9127 | 18.1481 | -360.8481 | 17.5198 | -352.6721 | 18.7312 | -352.7337 | 16.8648
12:23 | 3777 | 38.5428 | 201.1734 | 448.336 | 453.7101 | -16.8309 | -42.3132 | 10.2698 | 6.9045 | 1.32 | -0.561 | 2.3475 | -1.4245 | 10.7246 | 3.4549 | 0.6104 | 0.6517 | 0.9586 | 0.7328 | -129.4335 | -1.1746 | 5.8332 | 1.7755 | -3.2231 | -1.7822 | 4.3182 |  | 2.6637 | -0.054 | 4.0096 | 3.3646 | 3.3462 | 1.0645 | 10.7752 | 14.2604 | 14.8471 | 11.0988 | 0.0001 | -0.0028 | 0.0006 | 0.0031 | 0.0008 | -0.0006 | 0.0101 | -0.0265 | -0.0185 | -360.125 | 17.3679 | -360.4142 | 17.6964 | -360.8266 | 18.1645 | -360.922 | 17.5445 | -352.6629 | 18.6779 | -352.6383 | 16.832
12:23 | 3778 | 38.5302 | 201.1787 | 448.1882 | 453.7707 | -16.8245 | -42.3561 | 10.2405 | 6.9262 | 1.2568 | -0.5377 | 2.3829 | -1.4951 | 10.7398 | 3.4935 | 0.6102 | 0.6556 | 0.9595 | 0.7321 | -129.5102 | -1.2026 | 5.672 | 1.5159 | -3.2386 | -1.7707 | 4.224 |  | 2.7241 | -0.0823 | 4.0078 | 3.3663 | 3.343 | 1.0636 | 10.7337 | 14.2474 | 14.8147 | 11.0522 | -0.0003 | -0.0025 | 0.0006 | 0.0037 | 0.0002 | -0.0008 | -0.0001 | 0.0011 | 0.0008 | -360.1896 | 17.3864 | -360.4173 | 17.6677 | -360.725 | 18.1132 | -360.845 | 17.5321 | -352.6721 | 18.7004 | -352.6598 | 16.8053
12:23 | 3779 | 38.5018 | 201.1392 | 448.1715 | 453.7202 | -16.819 | -42.4021 | 10.1739 | 6.9059 | 1.1823 | -0.5736 | 2.3908 | -1.4795 | 10.6809 | 3.4562 | 0.6092 | 0.6553 | 0.9569 | 0.7329 | -129.4934 | -1.2133 | 5.6801 | 1.5802 | -3.321 | -1.8449 | 4.2907 |  | 2.6559 | -0.045 | 4.009 | 3.3603 | 3.3436 | 1.0642 | 10.6978 | 14.2403 | 14.766 | 11.04 | -0.0002 | -0.0033 | 0.0008 | 0.004 | 0.001 | -0.0007 | -0.0017 | 0.0012 | -0.0065 | -360.1527 | 17.3987 | -360.4819 | 17.6985 | -360.8389 | 18.105 | -360.765 | 17.4952 | -352.6167 | 18.6984 | -352.6875 | 16.8402
12:23 | 3780 | 38.5072 | 201.0936 | 448.1301 | 453.77 | -16.8816 | -42.322 | 10.3147 | 6.8696 | 1.3493 | -0.5859 | 2.4483 | -1.5106 | 10.7023 | 3.4902 | 0.6102 | 0.6565 | 0.9605 | 0.7337 | -129.4787 | -1.2142 | 5.7033 | 1.6167 | -3.3243 | -1.8039 | 4.2784 |  | 2.7983 | -0.1016 | 4.0083 | 3.3641 | 3.3418 | 1.0644 | 10.7729 | 14.2582 | 14.8049 | 11.0904 | 0.0004 | -0.0028 | 0.0007 | 0.0039 | 0.0007 | -0.0006 | 0.0142 | 0.0029 | -0.0098 | -360.1619 | 17.3843 | -360.4389 | 17.7067 | -360.8727 | 18.1666 | -360.8881 | 17.5301 | -352.6321 | 18.6861 | -352.6198 | 16.8299
12:23 | 3781 | 38.5067 | 201.1796 | 448.1943 | 453.7591 | -16.9359 | -42.3956 | 10.2944 | 6.9164 | 1.2464 | -0.4523 | 2.4088 | -1.648 | 10.5766 | 3.3935 | 0.6104 | 0.6537 | 0.9584 | 0.7328 | -129.4932 | -1.2484 | 5.6339 | 1.612 | -3.3577 | -1.7785 | 4.3072 |  | 2.7152 | -0.0654 | 4.0089 | 3.3643 | 3.344 | 1.0659 | 10.7602 | 14.2509 | 14.842 | 11.0959 | -0.0002 | -0.0033 | -0.0001 | 0.0039 | 0.0007 | -0.0009 | -0.0063 | 0.008 | -0.0117 | -360.2481 | 17.4213 | -360.4573 | 17.7005 | -360.8143 | 18.1317 | -360.9097 | 17.5753 | -352.6998 | 18.7333 | -352.6813 | 16.8074
12:23 | 3782 | 38.5871 | 201.1839 | 448.1956 | 453.7614 | -16.9065 | -42.3746 | 10.1682 | 7.0371 | 1.322 | -0.4886 | 2.4114 | -1.5633 | 10.5553 | 3.4228 | 0.609 | 0.656 | 0.9559 | 0.7331 | -129.5332 | -1.2385 | 5.6233 | 1.5978 | -3.3798 | -1.8947 | 4.3093 |  | 2.6727 | -0.0727 | 4.0087 | 3.3627 | 3.3415 | 1.0656 | 10.7635 | 14.2723 | 14.8493 | 11.1269 | -0.0002 | -0.0026 | 0.0012 | 0.0046 | 0.0009 | 0.0001 | 0.0289 | -0.0061 | -0.0026 | -360.2081 | 17.4377 | -360.5127 | 17.7272 | -360.8512 | 18.1317 | -360.845 | 17.528 | -352.6444 | 18.7395 | -352.7398 | 16.8566
12:23 | 3783 | 38.6234 | 201.2674 | 448.134 | 453.8309 | -16.9071 | -42.302 | 10.1287 | 7.0238 | 1.2411 | -0.6043 | 2.3785 | -1.5303 | 10.6049 | 3.4445 | 0.6098 | 0.6567 | 0.9596 | 0.7335 | -129.4843 | -1.1579 | 5.6684 | 1.5767 | -3.3132 | -1.8273 | 4.2626 |  | 2.6965 | -0.1155 | 4.0074 | 3.3615 | 3.3416 | 1.0647 | 10.7358 | 14.279 | 14.8485 | 11.0998 | 0 | -0.0026 | 0.0005 | 0.0036 | 0.0011 | -0.0005 | -0.0016 | -0.0058 | 0.0038 | -360.1281 | 17.3905 | -360.4542 | 17.7128 | -360.8635 | 18.1502 | -360.9004 | 17.5198 | -352.6167 | 18.6963 | -352.6752 | 16.8361
12:23 | 3784 | 38.5906 | 201.2177 | 448.1073 | 453.8148 | -16.9893 | -42.2881 | 10.1855 | 6.9617 | 1.1788 | -0.6138 | 2.4042 | -1.5044 | 10.5825 | 3.4726 | 0.6097 | 0.655 | 0.9574 | 0.734 | -129.522 | -1.3575 | 5.6652 | 1.5445 | -3.2136 | -1.676 | 4.3026 |  | 2.7704 | -0.0144 | 4.008 | 3.3609 | 3.3425 | 1.0651 | 10.7303 | 14.2148 | 14.8153 | 11.0667 | -0.0002 | -0.0034 | 0.0006 | 0.0035 | 0.0008 | 0 | 0.0171 | -0.0025 | -0.0031 | -360.2235 | 17.3884 | -360.3927 | 17.6512 | -360.7681 | 18.1358 | -360.885 | 17.5547 | -352.6937 | 18.7025 | -352.6352 | 16.7868
12:23 | 3785 | 38.5708 | 201.2206 | 448.1823 | 453.9155 | -16.876 | -42.3589 | 10.2334 | 7.0073 | 1.1907 | -0.5928 | 2.4176 | -1.5669 | 10.6063 | 3.4381 | 0.6115 | 0.6554 | 0.9591 | 0.7343 | -129.4814 | -1.2522 | 5.7002 | 1.7622 | -3.1774 | -1.6283 | 4.323 |  | 2.6925 | -0.0937 | 4.0085 | 3.3627 | 3.3403 | 1.0648 | 10.7451 | 14.2477 | 14.8284 | 11.0977 | 0.0001 | -0.0028 | 0.0015 | 0.0036 | 0.0011 | -0.0006 | 0.0085 | 0.0018 | -0.0103 | -360.1773 | 17.4172 | -360.4758 | 17.6923 | -360.7804 | 18.0906 | -360.7743 | 17.5137 | -352.629 | 18.7169 | -352.6998 | 16.8135
12:23 | 3786 | 38.5182 | 201.0643 | 448.1051 | 453.783 | -16.8534 | -42.2279 | 10.2876 | 6.9857 | 1.1545 | -0.6703 | 2.3506 | -1.5212 | 10.6042 | 3.5172 | 0.6111 | 0.6553 | 0.956 | 0.7329 | -129.4697 | -1.2673 | 5.7008 | 1.7514 | -3.1308 | -1.7717 | 4.2926 |  | 2.6659 | 0.007 | 4.0095 | 3.3625 | 3.3419 | 1.0645 | 10.735 | 14.2308 | 14.7782 | 11.066 | -0.0005 | -0.0029 | 0.0008 | 0.0037 | 0.0003 | -0.0003 | 0.0147 | -0.0184 | -0.0056 | -360.1096 | 17.3843 | -360.4604 | 17.7108 | -360.845 | 18.1543 | -360.842 | 17.5157 | -352.5798 | 18.684 | -352.6567 | 16.8299
12:23 | 3787 | 38.5749 | 201.1667 | 448.0739 | 453.7998 | -16.8998 | -42.3742 | 10.294 | 6.9612 | 1.124 | -0.5964 | 2.3554 | -1.4605 | 10.6459 | 3.4554 | 0.6095 | 0.6596 | 0.9584 | 0.7334 | -129.4772 | -1.2286 | 5.7058 | 1.7772 | -3.1073 | -1.6993 | 4.2641 |  | 2.6989 | -0.0687 | 4.0078 | 3.3609 | 3.3423 | 1.062 | 10.7208 | 14.2293 | 14.8339 | 11.0789 | -0.0001 | -0.0028 | 0.0016 | 0.0047 | 0.0009 | -0.0006 | 0.0221 | -0.0075 | -0.0019 | -360.2542 | 17.4028 | -360.4389 | 17.68 | -360.802 | 18.1584 | -360.9158 | 17.5712 | -352.6813 | 18.7128 | -352.6475 | 16.793
12:23 | 3788 | 38.5253 | 201.182 | 448.1234 | 453.8875 | -16.7635 | -42.2116 | 10.2268 | 6.959 | 1.0931 | -0.6127 | 2.4234 | -1.4301 | 10.6855 | 3.5516 | 0.6111 | 0.6584 | 0.9587 | 0.7342 | -129.4497 | -1.2074 | 5.6383 | 1.6839 | -3.1065 | -1.7017 | 4.2889 |  | 2.6972 | -0.1042 | 4.0084 | 3.3643 | 3.3415 | 1.0632 | 10.7035 | 14.2696 | 14.7865 | 11.0735 | 0.0005 | -0.0029 | 0.0004 | 0.004 | 0.0011 | -0.0006 | 0.0127 | 0 | -0.0184 | -360.2327 | 17.4582 | -360.5343 | 17.7108 | -360.8697 | 18.1235 | -360.8481 | 17.5527 | -352.6875 | 18.7518 | -352.7306 | 16.8381
12:23 | 3789 | 38.6015 | 201.1871 | 448.1072 | 453.9314 | -16.7877 | -42.2387 | 10.1707 | 6.911 | 1.137 | -0.5132 | 2.3071 | -1.5495 | 10.6102 | 3.5091 | 0.6114 | 0.6584 | 0.9594 | 0.7356 | -129.4139 | -1.194 | 5.6605 | 1.5984 | -3.2359 | -1.8372 | 4.2028 |  | 2.7295 | -0.1099 | 4.0081 | 3.3633 | 3.3428 | 1.0641 | 10.751 | 14.2475 | 14.8273 | 11.0749 | 0.0002 | -0.0031 | 0.0003 | 0.0037 | 0.0009 | -0.0001 | -0.0042 | -0.0017 | -0.0157 | -360.1496 | 17.4007 | -360.4912 | 17.7128 | -360.8727 | 18.1481 | -360.8666 | 17.5321 | -352.6475 | 18.7045 | -352.6844 | 16.8505
12:23 | 3790 | 38.5274 | 201.1787 | 448.2184 | 453.8486 | -16.8505 | -42.2784 | 10.1704 | 6.8923 | 1.2078 | -0.5105 | 2.3622 | -1.4909 | 10.6525 | 3.4606 | 0.6116 | 0.6532 | 0.9579 | 0.7342 | -129.5034 | -1.1936 | 5.7037 | 1.5811 | -3.1501 | -1.6789 | 4.2481 |  | 2.7025 | -0.052 | 4.0102 | 3.3661 | 3.343 | 1.0651 | 10.752 | 14.2549 | 14.8319 | 11.0865 | 0.0001 | -0.0023 | 0.0009 | 0.0038 | 0.0011 | -0.0006 | -0.0028 | -0.0044 | -0.0085 | -360.165 | 17.3699 | -360.3896 | 17.6677 | -360.7712 | 18.1399 | -360.9066 | 17.5445 | -352.6567 | 18.6861 | -352.6198 | 16.7991
12:23 | 3791 | 38.4765 | 201.1158 | 448.1399 | 453.7607 | -16.8589 | -42.2782 | 10.2047 | 6.9856 | 1.171 | -0.5407 | 2.4744 | -1.5394 | 10.6295 | 3.5903 | 0.6122 | 0.6561 | 0.9594 | 0.7336 | -129.4111 | -1.1837 | 5.7937 | 1.54 | -3.2649 | -1.7038 | 4.2661 |  | 2.7756 | -0.0298 | 4.0092 | 3.3624 | 3.3428 | 1.0636 | 10.7742 | 14.2474 | 14.8205 | 11.0869 | -0.0003 | -0.0025 | 0.0004 | 0.0036 | 0.0001 | -0.0007 | 0.0215 | -0.0063 | 0.0017 | -360.1896 | 17.411 | -360.4696 | 17.6656 | -360.7589 | 18.1009 | -360.805 | 17.528 | -352.6444 | 18.723 | -352.669 | 16.8032
12:23 | 3792 | 38.3937 | 201.0879 | 448.2103 | 453.7781 | -16.8559 | -42.2115 | 10.1897 | 6.9834 | 1.1273 | -0.6689 | 2.3978 | -1.5117 | 10.6482 | 3.543 | 0.6107 | 0.6528 | 0.9545 | 0.7339 | -129.5341 | -1.2721 | 5.6472 | 1.6507 | -3.2233 | -1.6674 | 4.2844 |  | 2.756 | -0.0205 | 4.0098 | 3.3609 | 3.3395 | 1.0632 | 10.7486 | 14.2744 | 14.8152 | 11.072 | 0.0004 | -0.0025 | 0.001 | 0.0038 | 0.0015 | -0.0005 | 0.0039 | -0.0004 | -0.0148 | -360.1496 | 17.3884 | -360.4758 | 17.6985 | -360.842 | 18.1235 | -360.8512 | 17.5116 | -352.6075 | 18.6943 | -352.6844 | 16.8279
12:23 | 3793 | 38.5248 | 201.1216 | 448.1577 | 453.9256 | -16.9162 | -42.2643 | 10.2275 | 7.0826 | 1.3119 | -0.508 | 2.5153 | -1.5466 | 10.6397 | 3.5643 | 0.6109 | 0.6595 | 0.957 | 0.733 | -129.481 | -1.2135 | 5.6877 | 1.561 | -3.305 | -1.7161 | 4.2356 |  | 2.6751 | -0.0723 | 4.0083 | 3.3632 | 3.3388 | 1.064 | 10.7429 | 14.2452 | 14.813 | 11.0439 | 0.0002 | -0.0031 | 0.0012 | 0.0039 | 0.0005 | -0.0002 | 0.0113 | -0.0208 | -0.0013 | -360.1404 | 17.3843 | -360.405 | 17.6841 | -360.845 | 18.1625 | -360.882 | 17.5547 | -352.6721 | 18.684 | -352.6136 | 16.8053
12:23 | 3794 | 38.4714 | 201.1314 | 448.0817 | 453.8715 | -16.8923 | -42.1986 | 10.1195 | 7.1083 | 1.1943 | -0.5243 | 2.4309 | -1.5257 | 10.6308 | 3.5156 | 0.611 | 0.6607 | 0.9586 | 0.7333 | -129.4477 | -1.2149 | 5.7456 | 1.6734 | -3.3644 | -1.716 | 4.2593 |  | 2.6698 | -0.1088 | 4.0093 | 3.3634 | 3.3441 | 1.0642 | 10.7083 | 14.2274 | 14.7693 | 11.0566 | -0.0005 | -0.0028 | 0.0005 | 0.0035 | 0.0002 | -0.0008 | 0.0243 | -0.0099 | -0.0129 | -360.2358 | 17.4418 | -360.4635 | 17.7005 | -360.8143 | 18.1255 | -360.885 | 17.5691 | -352.6998 | 18.7333 | -352.6967 | 16.8135
12:23 | 3795 | 38.467 | 201.1874 | 448.1961 | 453.8553 | -16.8933 | -42.2875 | 10.1106 | 6.9936 | 1.3104 | -0.4745 | 2.4044 | -1.5629 | 10.6023 | 3.4846 | 0.6097 | 0.6572 | 0.9566 | 0.7317 | -129.4607 | -1.163 | 5.684 | 1.7643 | -3.3328 | -1.6627 | 4.2882 |  | 2.6914 | -0.1253 | 4.0096 | 3.3665 | 3.3416 | 1.0639 | 10.7 | 14.2489 | 14.8008 | 11.0468 | -0.0002 | -0.0025 | 0.0011 | 0.0043 | 0.0009 | 0 | 0.0167 | 0.0013 | -0.0081 | -360.1404 | 17.4233 | -360.5158 | 17.7231 | -360.8697 | 18.142 | -360.842 | 17.5383 | -352.6598 | 18.7312 | -352.7398 | 16.8546
12:23 | 3796 | 38.5064 | 201.1536 | 448.1663 | 453.8442 | -16.8128 | -42.0931 | 10.2033 | 6.9652 | 1.2924 | -0.4258 | 2.4695 | -1.4449 | 10.7593 | 3.5657 | 0.6108 | 0.6576 | 0.959 | 0.7348 | -129.371 | -1.1719 | 5.5628 | 1.8253 | -3.3614 | -1.7207 | 4.2488 |  | 2.7414 | -0.0152 | 4.0082 | 3.3653 | 3.3396 | 1.0658 | 10.7336 | 14.2302 | 14.8331 | 11.0749 | 0.0001 | -0.003 | 0.0007 | 0.0039 | 0.0011 | -0.0003 | 0.0012 | 0.0031 | 0.0051 | -360.1342 | 17.3802 | -360.4296 | 17.6944 | -360.8543 | 18.1687 | -360.9066 | 17.5404 | -352.6598 | 18.7004 | -352.6506 | 16.8279
12:23 | 3797 | 38.4169 | 201.1072 | 448.177 | 453.8236 | -16.8575 | -42.1269 | 10.1752 | 6.9618 | 1.3337 | -0.3998 | 2.5051 | -1.451 | 10.6842 | 3.5505 | 0.61 | 0.6571 | 0.961 | 0.734 | -129.3463 | -1.1422 | 5.5707 | 1.8398 | -3.3461 | -1.7516 | 4.2128 |  | 2.6629 | -0.0343 | 4.0083 | 3.3655 | 3.3413 | 1.0655 | 10.7567 | 14.2592 | 14.8284 | 11.0977 | 0.0001 | -0.003 | 0.0002 | 0.0038 | 0.0015 | -0.0001 | 0.015 | -0.0024 | 0.0089 | -360.1681 | 17.3966 | -360.3958 | 17.6533 | -360.7527 | 18.1235 | -360.845 | 17.5445 | -352.6598 | 18.7128 | -352.6321 | 16.7909
12:23 | 3798 | 38.5046 | 201.1839 | 448.1928 | 453.8892 | -16.8483 | -42.2557 | 10.1619 | 7.0375 | 1.3313 | -0.3235 | 2.5107 | -1.5039 | 10.7552 | 3.5576 | 0.6106 | 0.6527 | 0.958 | 0.7349 | -129.3223 | -1.0776 | 5.651 | 1.8503 | -3.3974 | -1.6646 | 4.2335 |  | 2.6553 | -0.0247 | 4.0095 | 3.3626 | 3.3438 | 1.066 | 10.7152 | 14.2462 | 14.7902 | 11.0627 | -0.0002 | -0.0033 | 0.0008 | 0.0039 | 0.0006 | -0.0006 | 0.0028 | -0.0189 | -0.0022 | -360.1404 | 17.3966 | -360.4758 | 17.6944 | -360.805 | 18.1009 | -360.805 | 17.5055 | -352.6013 | 18.7025 | -352.6752 | 16.8176
12:23 | 3799 | 38.4355 | 201.118 | 448.2411 | 453.939 | -16.8953 | -42.1588 | 10.2286 | 7.0045 | 1.3417 | -0.3053 | 2.4645 | -1.5366 | 10.81 | 3.5634 | 0.6111 | 0.6559 | 0.9569 | 0.7331 | -129.3656 | -1.1114 | 5.6815 | 1.7805 | -3.3129 | -1.7469 | 4.1588 |  | 2.6775 | -0.0885 | 4.0078 | 3.3614 | 3.3404 | 1.0668 | 10.7683 | 14.265 | 14.8631 | 11.1035 | -0.0002 | -0.0028 | 0.0004 | 0.0036 | 0.0009 | -0.0005 | 0.0088 | 0.002 | 0.0024 | -360.1404 | 17.3782 | -360.4081 | 17.6882 | -360.8297 | 18.1584 | -360.8697 | 17.5219 | -352.6106 | 18.684 | -352.6229 | 16.8012
12:23 | 3800 | 38.5123 | 201.2313 | 448.1979 | 453.9454 | -16.7744 | -42.1596 | 10.235 | 7.0254 | 1.3876 | -0.4046 | 2.4531 | -1.5866 | 10.7147 | 3.4116 | 0.6112 | 0.6547 | 0.959 | 0.7339 | -129.406 | -1.0161 | 5.7489 | 1.7795 | -3.2848 | -1.735 | 4.248 |  | 2.6333 | -0.1981 | 4.01 | 3.3624 | 3.3425 | 1.0646 | 10.7544 | 14.2627 | 14.8083 | 11.0782 | 0 | -0.0026 | 0.0009 | 0.004 | 0.0006 | -0.0003 | 0.0177 | -0.0083 | -0.0176 | -360.1958 | 17.409 | -360.4512 | 17.6779 | -360.7897 | 18.1399 | -360.8974 | 17.5527 | -352.6813 | 18.7128 | -352.6383 | 16.7889
12:23 | 3801 | 38.511 | 201.3047 | 448.2124 | 453.9685 | -16.8417 | -42.1482 | 10.1489 | 6.9544 | 1.3034 | -0.386 | 2.4523 | -1.5612 | 10.6929 | 3.5189 | 0.6099 | 0.6555 | 0.9597 | 0.7325 | -129.3589 | -0.9633 | 5.7102 | 1.7766 | -3.3725 | -1.7197 | 4.2305 |  | 2.701 | -0.0492 | 4.0102 | 3.3661 | 3.343 | 1.0639 | 10.7393 | 14.265 | 14.8168 | 11.0572 | 0.0001 | -0.0033 | 0.0015 | 0.0045 | 0.0007 | -0.0008 | 0.0055 | -0.0152 | -0.0057 | -360.1865 | 17.4356 | -360.5066 | 17.7272 | -360.8327 | 18.1296 | -360.8481 | 17.5321 | -352.6844 | 18.7415 | -352.709 | 16.832
12:23 | 3802 | 38.5086 | 201.2215 | 448.1464 | 453.8822 | -16.8064 | -42.1106 | 10.1414 | 7.0513 | 1.3363 | -0.4647 | 2.3987 | -1.7033 | 10.5639 | 3.4441 | 0.6093 | 0.6569 | 0.9569 | 0.7333 | -129.4403 | -1.0798 | 5.6226 | 1.7384 | -3.3139 | -1.6982 | 4.2496 |  | 2.6749 | -0.0959 | 4.0098 | 3.3659 | 3.3415 | 1.0653 | 10.7612 | 14.2526 | 14.8234 | 11.0727 | 0.0001 | -0.0029 | 0.0008 | 0.0039 | 0.0006 | -0.0003 | 0.0045 | -0.0006 | -0.0201 | -360.1496 | 17.4048 | -360.4696 | 17.7231 | -360.8543 | 18.1666 | -360.9097 | 17.5424 | -352.6444 | 18.7148 | -352.6629 | 16.832
12:23 | 3803 | 38.5884 | 201.1856 | 448.0937 | 453.824 | -16.8917 | -42.1374 | 10.2419 | 7.0007 | 1.2882 | -0.4813 | 2.37 | -1.5895 | 10.656 | 3.4926 | 0.6101 | 0.6544 | 0.9562 | 0.7328 | -129.4204 | -0.9946 | 5.659 | 1.8138 | -3.2591 | -1.7477 | 4.283 |  | 2.7722 | -0.0327 | 4.0112 | 3.3648 | 3.3431 | 1.0656 | 10.7589 | 14.2849 | 14.867 | 11.1341 | -0.0006 | -0.0027 | 0.0009 | 0.0043 | 0.0011 | -0.0007 | -0.0023 | 0.0002 | -0.0168 | -360.1835 | 17.3925 | -360.445 | 17.6944 | -360.8112 | 18.1584 | -360.9189 | 17.5629 | -352.6844 | 18.7148 | -352.6813 | 16.8238
12:23 | 3804 | 38.4993 | 201.1789 | 448.1869 | 453.8373 | -16.8402 | -42.2514 | 10.1207 | 7.0173 | 1.3283 | -0.387 | 2.439 | -1.5075 | 10.6788 | 3.5282 | 0.6104 | 0.6542 | 0.9577 | 0.734 | -129.404 | -1.1469 | 5.6575 | 1.8292 | -3.1123 | -1.5873 | 4.2842 |  | 2.7682 | 0.08 | 4.0092 | 3.366 | 3.3415 | 1.0653 | 10.7487 | 14.2566 | 14.8235 | 11.0789 | 0 | -0.0029 | 0.0006 | 0.0038 | 0.0004 | -0.0002 | 0.0107 | -0.0053 | -0.0048 | -360.1804 | 17.411 | -360.4604 | 17.6882 | -360.7958 | 18.1173 | -360.8327 | 17.5321 | -352.6721 | 18.7353 | -352.666 | 16.8176
12:23 | 3805 | 38.7187 | 201.1983 | 448.073 | 453.8625 | -16.778 | -42.2589 | 10.1891 | 7.015 | 1.3414 | -0.5177 | 2.4088 | -1.534 | 10.74 | 3.6017 | 0.6108 | 0.6572 | 0.9583 | 0.7325 | -129.4665 | -1.151 | 5.6252 | 1.873 | -3.0962 | -1.6893 | 4.3325 |  | 2.7061 | -0.0349 | 4.0087 | 3.3634 | 3.3384 | 1.0651 | 10.7498 | 14.229 | 14.8202 | 11.0854 | -0.0001 | -0.0036 | 0.0001 | 0.0032 | 0.0014 | -0.0006 | 0.016 | -0.0127 | -0.0185 | -360.1158 | 17.372 | -360.4512 | 17.6944 | -360.8235 | 18.1317 | -360.8574 | 17.5013 | -352.5798 | 18.7087 | -352.6444 | 16.8217
12:23 | 3806 | 38.6991 | 201.1709 | 448.1389 | 453.9257 | -16.7777 | -42.2549 | 10.1894 | 7.011 | 1.4448 | -0.2838 | 2.3891 | -1.5728 | 10.6917 | 3.5662 | 0.6121 | 0.6533 | 0.9602 | 0.7355 | -129.3589 | -1.1613 | 5.6018 | 1.7561 | -3.1816 | -1.648 | 4.2876 |  | 2.7291 | -0.0278 | 4.0103 | 3.3671 | 3.342 | 1.065 | 10.7337 | 14.2358 | 14.8321 | 11.0522 | -0.0001 | -0.0032 | 0.0007 | 0.0044 | 0.0007 | -0.0003 | -0.0062 | -0.0145 | -0.0142 | -360.1435 | 17.374 | -360.3896 | 17.6759 | -360.7927 | 18.1358 | -360.8604 | 17.5342 | -352.6413 | 18.6861 | -352.6198 | 16.7971
12:23 | 3807 | 38.7013 | 201.106 | 448.1318 | 453.9304 | -16.9127 | -42.2622 | 10.2003 | 6.9338 | 1.3523 | -0.3969 | 2.3544 | -1.539 | 10.638 | 3.5801 | 0.6099 | 0.6555 | 0.9583 | 0.7346 | -129.322 | -1.0348 | 5.5948 | 1.7525 | -3.217 | -1.6075 | 4.3114 |  | 2.707 | 0.0414 | 4.0088 | 3.3663 | 3.3392 | 1.0644 | 10.7232 | 14.237 | 14.8103 | 11.0648 | -0.0003 | -0.0026 | 0.0005 | 0.0038 | 0.0009 | -0.0002 | -0.0051 | -0.0007 | -0.0216 | -360.2019 | 17.4213 | -360.4604 | 17.6923 | -360.7712 | 18.1132 | -360.8327 | 17.528 | -352.6813 | 18.7333 | -352.6752 | 16.7848
12:23 | 3808 | 38.6031 | 201.0912 | 448.0465 | 453.8852 | -16.8667 | -42.2256 | 10.333 | 6.9709 | 1.3934 | -0.4395 | 2.4225 | -1.5509 | 10.6754 | 3.5362 | 0.6097 | 0.6556 | 0.9593 | 0.7335 | -129.2537 | -1.0308 | 5.6023 | 1.7822 | -3.1917 | -1.6515 | 4.2586 |  | 2.7109 | -0.0513 | 4.0087 | 3.3634 | 3.3402 | 1.0648 | 10.743 | 14.2391 | 14.8283 | 11.0447 | -0.0005 | -0.0028 | 0.0008 | 0.0035 | 0.0008 | -0.0007 | 0.0138 | -0.0062 | -0.0289 | -360.1527 | 17.4213 | -360.5127 | 17.7313 | -360.8789 | 18.1502 | -360.8758 | 17.5321 | -352.6352 | 18.723 | -352.6967 | 16.8381
12:23 | 3809 | 38.6303 | 201.0601 | 448.1006 | 453.982 | -16.8421 | -42.1148 | 10.239 | 7.0316 | 1.3908 | -0.3945 | 2.448 | -1.5486 | 10.6455 | 3.5961 | 0.6111 | 0.6581 | 0.9572 | 0.7345 | -129.2833 | -1.1149 | 5.6589 | 1.78 | -3.2251 | -1.5189 | 4.3446 |  | 2.7402 | 0.0482 | 4.009 | 3.3664 | 3.3416 | 1.0664 | 10.752 | 14.2606 | 14.8714 | 11.0811 | 0.0006 | -0.0027 | 0.0015 | 0.0044 | 0.0005 | -0.0001 | 0.0067 | -0.012 | -0.0084 | -360.2081 | 17.4131 | -360.4635 | 17.7067 | -360.8358 | 18.1666 | -360.9035 | 17.5671 | -352.6844 | 18.721 | -352.6752 | 16.8176
12:23 | 3810 | 38.6299 | 201.145 | 448.125 | 453.9219 | -16.8699 | -42.1685 | 10.1502 | 7.0493 | 1.3656 | -0.453 | 2.4026 | -1.4557 | 10.6185 | 3.5137 | 0.6097 | 0.6536 | 0.9598 | 0.732 | -129.3111 | -1.1194 | 5.7451 | 1.7924 | -3.201 | -1.6341 | 4.3326 |  | 2.7004 | 0.0103 | 4.0082 | 3.3615 | 3.3408 | 1.0658 | 10.7382 | 14.2465 | 14.7981 | 11.0677 | 0.0001 | -0.0031 | 0.0007 | 0.0035 | 0.001 | -0.0005 | 0.013 | -0.0139 | 0.0007 | -360.1896 | 17.4315 | -360.4942 | 17.7087 | -360.8266 | 18.1337 | -360.8697 | 17.5588 | -352.6906 | 18.7353 | -352.6967 | 16.8135
12:23 | 3811 | 38.6351 | 201.1597 | 448.1423 | 453.9761 | -16.7641 | -42.2671 | 10.1909 | 7.0206 | 1.3795 | -0.4008 | 2.4329 | -1.4527 | 10.6683 | 3.5608 | 0.6098 | 0.6559 | 0.9609 | 0.7328 | -129.3442 | -1.2259 | 5.7348 | 1.805 | -3.3064 | -1.6304 | 4.3237 |  | 2.6395 | 0.0401 | 4.0101 | 3.3646 | 3.3392 | 1.0652 | 10.7728 | 14.2641 | 14.8176 | 11.1016 | 0 | -0.0025 | 0.0008 | 0.0036 | 0.0005 | -0.0003 | 0.0082 | -0.0108 | -0.0166 | -360.1527 | 17.411 | -360.5066 | 17.7108 | -360.8204 | 18.1481 | -360.842 | 17.5157 | -352.6537 | 18.7107 | -352.666 | 16.8381
12:23 | 3812 | 38.7522 | 201.2405 | 448.0935 | 453.96 | -16.8129 | -42.2663 | 10.2292 | 7.007 | 1.3148 | -0.3208 | 2.3822 | -1.5749 | 10.6408 | 3.5846 | 0.6125 | 0.6568 | 0.9582 | 0.7347 | -129.3363 | -1.0843 | 5.7955 | 1.7205 | -3.2943 | -1.5572 | 4.2648 |  | 2.5893 | -0.0353 | 4.0091 | 3.3668 | 3.3416 | 1.0659 | 10.7487 | 14.2567 | 14.8015 | 11.0612 | -0.0003 | -0.0027 | 0.0009 | 0.004 | 0.0009 | -0.0006 | 0.0152 | -0.0144 | -0.0207 | -360.1711 | 17.3823 | -360.4142 | 17.68 | -360.802 | 18.1379 | -360.8574 | 17.5383 | -352.6229 | 18.684 | -352.629 | 16.793
12:23 | 3813 | 38.7067 | 201.2426 | 448.0732 | 453.9274 | -16.8564 | -42.2388 | 10.1636 | 7.0309 | 1.3975 | -0.3453 | 2.4158 | -1.4925 | 10.5944 | 3.5241 | 0.6114 | 0.6551 | 0.961 | 0.7338 | -129.3288 | -1.1417 | 5.8402 | 1.5776 | -3.2389 | -1.5853 | 4.2651 |  | 2.6267 | -0.0433 | 4.0097 | 3.365 | 3.3402 | 1.0637 | 10.7615 | 14.2634 | 14.8354 | 11.0977 | -0.0002 | -0.0032 | 0.0001 | 0.0031 | 0.0006 | -0.0005 | 0.0062 | 0.0067 | -0.0063 | -360.2019 | 17.4048 | -360.445 | 17.6923 | -360.7589 | 18.1029 | -360.8297 | 17.5321 | -352.6167 | 18.7087 | -352.6567 | 16.7889
12:23 | 3814 | 38.7116 | 201.2347 | 448.1176 | 454 | -16.8927 | -42.2755 | 10.1971 | 7.0528 | 1.405 | -0.3149 | 2.5569 | -1.4766 | 10.7267 | 3.5506 | 0.6118 | 0.6524 | 0.9644 | 0.7334 | -129.2974 | -1.1107 | 5.8335 | 1.5576 | -3.287 | -1.6231 | 4.2597 |  | 2.6072 | -0.097 | 4.0094 | 3.368 | 3.3408 | 1.0658 | 10.7163 | 14.2185 | 14.7742 | 11.0869 | 0.0005 | -0.0028 | 0.0007 | 0.0037 | 0.0008 | -0.001 | 0.0164 | 0.0012 | -0.0341 | -360.1527 | 17.3987 | -360.4789 | 17.7149 | -360.7958 | 18.1317 | -360.8574 | 17.5157 | -352.626 | 18.7107 | -352.6783 | 16.8094
12:23 | 3815 | 38.7445 | 201.0978 | 448.0455 | 454.0244 | -16.8803 | -42.2591 | 10.2894 | 7.07 | 1.3675 | -0.19 | 2.62 | -1.4948 | 10.699 | 3.5236 | 0.6116 | 0.6561 | 0.961 | 0.7341 | -129.3279 | -1.0687 | 5.7764 | 1.7011 | -3.2812 | -1.6017 | 4.237 |  | 2.5675 | -0.0856 | 4.01 | 3.3631 | 3.3377 | 1.0653 | 10.759 | 14.2615 | 14.8127 | 11.0771 | -0.0003 | -0.0027 | 0.0007 | 0.0039 | 0.0006 | -0.0002 | 0.0259 | -0.0149 | -0.0163 | -360.2173 | 17.409 | -360.4696 | 17.7128 | -360.8327 | 18.142 | -360.9312 | 17.5527 | -352.6537 | 18.7107 | -352.666 | 16.8115
12:23 | 3816 | 38.7714 | 201.0412 | 448.1531 | 453.9924 | -16.863 | -42.3151 | 10.3036 | 7.1173 | 1.3625 | -0.222 | 2.6329 | -1.3464 | 10.7825 | 3.5582 | 0.6126 | 0.653 | 0.9602 | 0.7339 | -129.318 | -1.0106 | 5.793 | 1.6346 | -3.387 | -1.6847 | 4.2313 |  | 2.6172 | -0.0118 | 4.008 | 3.3639 | 3.3374 | 1.0652 | 10.7268 | 14.2345 | 14.7775 | 11.0515 | -0.0003 | -0.0025 | 0.0007 | 0.0032 | 0.0007 | -0.0011 | 0.0157 | 0.01 | -0.0166 | -360.2265 | 17.4274 | -360.5035 | 17.7272 | -360.845 | 18.1173 | -360.8635 | 17.5609 | -352.7121 | 18.7415 | -352.7337 | 16.8217
12:23 | 3817 | 38.7086 | 201.1266 | 448.1771 | 454.0033 | -16.867 | -42.2434 | 10.2376 | 7.0919 | 1.481 | -0.1308 | 2.6929 | -1.3276 | 10.7742 | 3.602 | 0.6134 | 0.6546 | 0.9583 | 0.7329 | -129.2979 | -0.9943 | 5.7223 | 1.5787 | -3.3829 | -1.7224 | 4.3241 |  | 2.6867 | -0.0039 | 4.008 | 3.3639 | 3.3406 | 1.0633 | 10.7417 | 14.2615 | 14.8475 | 11.054 | -0.0001 | -0.0032 | 0.0013 | 0.0039 | 0.0006 | 0 | -0.0052 | -0.0125 | 0.0072 | -360.1835 | 17.4069 | -360.4758 | 17.7067 | -360.8081 | 18.1235 | -360.8789 | 17.5301 | -352.6506 | 18.7128 | -352.6875 | 16.8217
12:23 | 3818 | 38.786 | 201.1455 | 448.1497 | 454.0031 | -16.913 | -42.2169 | 10.1703 | 7.0393 | 1.4535 | -0.2566 | 2.6275 | -1.4267 | 10.7665 | 3.6303 | 0.6117 | 0.6498 | 0.9549 | 0.7344 | -129.2798 | -0.9763 | 5.8063 | 1.5616 | -3.3728 | -1.714 | 4.2632 |  | 2.6328 | 0.0074 | 4.0086 | 3.3677 | 3.3391 | 1.0633 | 10.7857 | 14.2418 | 14.8447 | 11.0576 | 0.0001 | -0.0028 | 0.001 | 0.0035 | 0.0006 | -0.0005 | 0.0061 | -0.0094 | 0.0026 | -360.1496 | 17.3782 | -360.4327 | 17.682 | -360.7958 | 18.1029 | -360.8727 | 17.5321 | -352.6198 | 18.6902 | -352.6321 | 16.8074
12:23 | 3819 | 38.7653 | 201.1159 | 448.1313 | 453.9635 | -16.8496 | -42.3039 | 10.2273 | 7.0291 | 1.526 | -0.1317 | 2.6743 | -1.4708 | 10.7291 | 3.6146 | 0.611 | 0.6543 | 0.9563 | 0.733 | -129.3653 | -1.0282 | 5.6701 | 1.6995 | -3.3467 | -1.636 | 4.3019 |  | 2.6456 | -0.1139 | 4.0085 | 3.3652 | 3.3433 | 1.0652 | 10.7418 | 14.267 | 14.8106 | 11.0894 | -0.0004 | -0.0028 | 0.0007 | 0.0038 | 0.0009 | -0.0002 | -0.0003 | -0.0018 | -0.009 | -360.1496 | 17.3843 | -360.4419 | 17.6861 | -360.7773 | 18.0947 | -360.8512 | 17.5301 | -352.629 | 18.7045 | -352.6567 | 16.8074
12:23 | 3820 | 38.8291 | 201.0959 | 448.1887 | 454.0948 | -16.939 | -42.3451 | 10.1945 | 7.0758 | 1.4863 | -0.3151 | 2.7097 | -1.4895 | 10.7506 | 3.5567 | 0.6125 | 0.6504 | 0.9591 | 0.733 | -129.4418 | -1.0795 | 5.6878 | 1.7599 | -3.3601 | -1.5725 | 4.2546 |  | 2.5589 | -0.0805 | 4.0082 | 3.3636 | 3.3448 | 1.0641 | 10.7451 | 14.271 | 14.8237 | 11.0857 | -0.0005 | -0.0025 | 0.0007 | 0.0039 | 0.0012 | 0 | 0.0083 | -0.0084 | 0.001 | -360.1558 | 17.3905 | -360.4358 | 17.6902 | -360.7989 | 18.0927 | -360.8512 | 17.5239 | -352.6321 | 18.6984 | -352.629 | 16.8094
12:23 | 3821 | 38.7399 | 201.1197 | 448.1263 | 454.0075 | -16.9387 | -42.5176 | 10.2488 | 7.035 | 1.5006 | -0.3216 | 2.714 | -1.4921 | 10.7593 | 3.5535 | 0.6128 | 0.6535 | 0.9537 | 0.7335 | -129.4776 | -1.0999 | 5.6249 | 1.7528 | -3.329 | -1.6348 | 4.3864 |  | 2.7014 | -0.0251 | 4.0094 | 3.3653 | 3.344 | 1.0653 | 10.7591 | 14.2324 | 14.8406 | 11.0659 | -0.0003 | -0.0029 | 0 | 0.0034 | 0.0011 | -0.0004 | 0.0133 | 0.0004 | 0.002 | -360.1865 | 17.3966 | -360.4512 | 17.7005 | -360.7927 | 18.1091 | -360.8881 | 17.5383 | -352.6167 | 18.6984 | -352.6598 | 16.8135
12:23 | 3822 | 38.7627 | 201.1385 | 448.2451 | 454.0862 | -16.9601 | -42.5212 | 10.2423 | 7.0709 | 1.4174 | -0.2037 | 2.6768 | -1.4958 | 10.6849 | 3.487 | 0.6127 | 0.6599 | 0.9599 | 0.7319 | -129.4358 | -1.0645 | 5.711 | 1.7271 | -3.3603 | -1.5572 | 4.2913 |  | 2.6922 | 0.0341 | 4.0104 | 3.3664 | 3.3424 | 1.0656 | 10.7568 | 14.253 | 14.8194 | 11.0815 | -0.0003 | -0.0033 | 0.0007 | 0.0042 | 0.0005 | -0.0004 | 0.0051 | -0.0056 | -0.0115 | -360.1958 | 17.4131 | -360.4758 | 17.7313 | -360.8512 | 18.1214 | -360.9004 | 17.5629 | -352.6321 | 18.723 | -352.6844 | 16.8217
12:23 | 3823 | 38.6474 | 201.104 | 448.2931 | 454.0489 | -16.892 | -42.4687 | 10.3443 | 7.0379 | 1.3733 | -0.1852 | 2.697 | -1.4133 | 10.6996 | 3.5792 | 0.6115 | 0.655 | 0.9564 | 0.7337 | -129.3648 | -1.0349 | 5.7092 | 1.6847 | -3.3517 | -1.6889 | 4.2652 |  | 2.6135 | 0.0238 | 4.0088 | 3.3674 | 3.3431 | 1.0654 | 10.7567 | 14.265 | 14.84 | 11.0977 | -0.0002 | -0.0027 | 0.0003 | 0.0036 | 0.0006 | -0.0007 | 0.0033 | -0.0151 | -0.0052 | -360.2019 | 17.4233 | -360.5066 | 17.7293 | -360.8204 | 18.1255 | -360.9127 | 17.5588 | -352.6752 | 18.7395 | -352.7121 | 16.8238
12:23 | 3824 | 38.7338 | 201.1208 | 448.136 | 454.0805 | -16.9006 | -42.3926 | 10.3787 | 6.9424 | 1.3181 | -0.2222 | 2.671 | -1.4437 | 10.7365 | 3.657 | 0.611 | 0.6537 | 0.9547 | 0.7344 | -129.3693 | -0.9476 | 5.6685 | 1.7566 | -3.3709 | -1.5966 | 4.2979 |  | 2.6374 | -0.0623 | 4.0095 | 3.3686 | 3.3434 | 1.0639 | 10.7857 | 14.2764 | 14.8679 | 11.0981 | -0.0006 | -0.0031 | 0.0004 | 0.0036 | 0.0003 | -0.0002 | -0.0009 | 0.0098 | -0.0121 | -360.1681 | 17.3905 | -360.4666 | 17.7067 | -360.805 | 18.1173 | -360.8912 | 17.5445 | -352.629 | 18.7189 | -352.6906 | 16.8197
12:23 | 3825 | 38.7301 | 201.1735 | 448.1908 | 454.1576 | -16.966 | -42.4486 | 10.3688 | 6.948 | 1.3023 | -0.1986 | 2.6559 | -1.3969 | 10.8147 | 3.6179 | 0.6107 | 0.6573 | 0.9604 | 0.7342 | -129.3587 | -0.9961 | 5.6577 | 1.7885 | -3.2854 | -1.6341 | 4.3498 |  | 2.6282 | 0.004 | 4.0084 | 3.366 | 3.3426 | 1.0647 | 10.7578 | 14.2607 | 14.8551 | 11.1096 | 0.0005 | -0.0026 | 0.0009 | 0.0039 | 0.0012 | -0.0009 | -0.001 | -0.0188 | -0.0164 | -360.1281 | 17.3802 | -360.4019 | 17.682 | -360.7866 | 18.1009 | -360.8358 | 17.5445 | -352.6383 | 18.6861 | -352.6167 | 16.795
12:23 | 3826 | 38.6999 | 201.1166 | 448.2568 | 454.1183 | -16.8427 | -42.4381 | 10.4951 | 6.9932 | 1.2654 | -0.2471 | 2.6833 | -1.413 | 10.7932 | 3.6304 | 0.6113 | 0.657 | 0.9571 | 0.7328 | -129.3618 | -1.0578 | 5.6639 | 1.7298 | -3.3681 | -1.6891 | 4.2933 |  | 2.669 | -0.013 | 4.0089 | 3.3675 | 3.343 | 1.0648 | 10.7624 | 14.271 | 14.8584 | 11.1146 | 0.0002 | -0.0027 | 0.0008 | 0.004 | 0.0003 | -0.0006 | 0.0284 | -0.0129 | -0.0004 | -360.205 | 17.4069 | -360.4419 | 17.6964 | -360.7866 | 18.0968 | -360.8389 | 17.5383 | -352.6106 | 18.7087 | -352.6506 | 16.7889
12:23 | 3827 | 38.6956 | 201.1602 | 448.1322 | 454.1224 | -16.8387 | -42.3442 | 10.3826 | 6.9999 | 1.2992 | -0.1949 | 2.6447 | -1.5123 | 10.7977 | 3.5287 | 0.6099 | 0.6526 | 0.958 | 0.7327 | -129.3889 | -1.0686 | 5.5507 | 1.7159 | -3.407 | -1.6683 | 4.3573 |  | 2.6468 | -0.0866 | 4.0083 | 3.3679 | 3.3402 | 1.0638 | 10.7568 | 14.2707 | 14.8679 | 11.0981 | -0.0004 | -0.0033 | 0.0008 | 0.004 | 0.0013 | -0.0005 | 0.0089 | -0.0076 | 0.0044 | -360.1773 | 17.4192 | -360.5096 | 17.7416 | -360.845 | 18.1112 | -360.8943 | 17.5506 | -352.6229 | 18.7066 | -352.669 | 16.8258
12:24 | 3828 | 38.8467 | 201.2033 | 448.2576 | 454.2308 | -16.8493 | -42.3638 | 10.3903 | 7.0877 | 1.3138 | -0.2724 | 2.6213 | -1.3941 | 10.7601 | 3.6344 | 0.6128 | 0.6514 | 0.9613 | 0.7333 | -129.3512 | -1.0505 | 5.5671 | 1.7791 | -3.2377 | -1.6171 | 4.3736 |  | 2.5961 | -0.1101 | 4.0086 | 3.3673 | 3.3452 | 1.0647 | 10.7474 | 14.2501 | 14.8543 | 11.0767 | -0.0004 | -0.0025 | 0.0006 | 0.0037 | 0.0008 | -0.0003 | 0.0086 | 0.0006 | -0.0096 | -360.1558 | 17.4172 | -360.4696 | 17.7231 | -360.8512 | 18.144 | -360.882 | 17.5671 | -352.6629 | 18.7025 | -352.666 | 16.8238
12:24 | 3829 | 38.7873 | 201.2685 | 448.2173 | 454.1818 | -16.9766 | -42.3544 | 10.3798 | 7.0874 | 1.3818 | -0.277 | 2.5755 | -1.4791 | 10.7001 | 3.5854 | 0.6102 | 0.6555 | 0.9599 | 0.7337 | -129.4425 | -1.0716 | 5.5591 | 1.6275 | -3.3076 | -1.6318 | 4.348 |  | 2.5833 | -0.0777 | 4.0087 | 3.3646 | 3.3436 | 1.0643 | 10.714 | 14.2508 | 14.8351 | 11.0674 | -0.0006 | -0.0029 | 0.0004 | 0.0039 | 0.0011 | -0.0006 | 0.0236 | -0.0084 | -0.0121 | -360.1711 | 17.4172 | -360.4758 | 17.7169 | -360.7897 | 18.1009 | -360.9158 | 17.5732 | -352.6444 | 18.7169 | -352.669 | 16.8032
12:24 | 3830 | 38.782 | 201.168 | 448.1889 | 454.2402 | -16.8689 | -42.3168 | 10.336 | 6.9741 | 1.3914 | -0.2962 | 2.624 | -1.4955 | 10.7529 | 3.5336 | 0.6129 | 0.6544 | 0.9596 | 0.735 | -129.4322 | -1.1361 | 5.6305 | 1.6389 | -3.2158 | -1.7069 | 4.3896 |  | 2.5951 | -0.1251 | 4.0081 | 3.3662 | 3.3421 | 1.0661 | 10.7464 | 14.2197 | 14.8219 | 11.0533 | 0.0001 | -0.0031 | 0.0012 | 0.0045 | 0.0008 | -0.0005 | 0.0099 | 0.0055 | 0.0017 | -360.1219 | 17.3905 | -360.4666 | 17.7252 | -360.7989 | 18.0886 | -360.8235 | 17.528 | -352.5983 | 18.7087 | -352.669 | 16.8217
12:24 | 3831 | 38.7182 | 201.1278 | 448.166 | 454.2223 | -16.8575 | -42.327 | 10.3108 | 7.0015 | 1.3867 | -0.3084 | 2.6462 | -1.5382 | 10.7714 | 3.5815 | 0.6114 | 0.657 | 0.9562 | 0.7338 | -129.4489 | -1.1882 | 5.5774 | 1.6598 | -3.2876 | -1.5677 | 4.4295 |  | 2.5056 | -0.2368 | 4.0095 | 3.367 | 3.3456 | 1.0679 | 10.707 | 14.2266 | 14.8117 | 11.0775 | 0.0004 | -0.0029 | 0.0007 | 0.0038 | 0.0008 | -0.0002 | 0.0199 | -0.0029 | -0.0024 | -360.1404 | 17.3905 | -360.4235 | 17.7128 | -360.8512 | 18.1173 | -360.882 | 17.5424 | -352.6167 | 18.6799 | -352.6413 | 16.7991
12:24 | 3832 | 38.7308 | 201.1536 | 448.2516 | 454.2166 | -16.8253 | -42.371 | 10.3977 | 7.0751 | 1.3965 | -0.3278 | 2.6033 | -1.4531 | 10.7566 | 3.6326 | 0.6127 | 0.6567 | 0.9604 | 0.7345 | -129.3637 | -1.1595 | 5.7202 | 1.5724 | -3.3733 | -1.6851 | 4.37 |  | 2.5585 | -0.1398 | 4.009 | 3.3671 | 3.3431 | 1.0661 | 10.7579 | 14.2486 | 14.8566 | 11.088 | -0.0005 | -0.0028 | 0.001 | 0.0037 | 0.0012 | -0.0003 | 0.0169 | 0.001 | -0.015 | -360.2204 | 17.4213 | -360.4512 | 17.7067 | -360.7958 | 18.1173 | -360.9004 | 17.5794 | -352.6813 | 18.7251 | -352.6813 | 16.7909
12:24 | 3833 | 38.7464 | 201.1548 | 448.1658 | 454.1189 | -16.8572 | -42.2135 | 10.365 | 7.0244 | 1.3743 | -0.3795 | 2.5618 | -1.4315 | 10.7855 | 3.5744 | 0.6109 | 0.6544 | 0.9563 | 0.7343 | -129.3993 | -1.1234 | 5.6289 | 1.6358 | -3.2972 | -1.7083 | 4.3774 |  | 2.5112 | -0.1176 | 4.0087 | 3.367 | 3.3449 | 1.0657 | 10.7174 | 14.2429 | 14.8461 | 11.076 | 0 | -0.0024 | 0.0008 | 0.0039 | 0.0006 | -0.0004 | 0.0179 | -0.0166 | 0.0004 | -360.205 | 17.4295 | -360.5004 | 17.7518 | -360.8574 | 18.1132 | -360.8481 | 17.5527 | -352.6752 | 18.721 | -352.7367 | 16.8423
12:24 | 3834 | 38.8183 | 201.24 | 448.1535 | 454.2354 | -16.8504 | -42.2717 | 10.4124 | 7.057 | 1.3707 | -0.3395 | 2.5697 | -1.4503 | 10.8239 | 3.6967 | 0.6121 | 0.6564 | 0.9526 | 0.7344 | -129.466 | -1.1617 | 5.5928 | 1.7052 | -3.2785 | -1.6666 | 4.393 |  | 2.5215 | -0.1214 | 4.0088 | 3.3655 | 3.346 | 1.0653 | 10.7429 | 14.2567 | 14.8304 | 11.0612 | 0.0003 | -0.0029 | 0.0011 | 0.0035 | 0.0011 | -0.0008 | 0.0108 | -0.0013 | -0.0062 | -360.1219 | 17.3864 | -360.4389 | 17.7128 | -360.8204 | 18.1317 | -360.8758 | 17.5342 | -352.6352 | 18.6881 | -352.6198 | 16.8217
12:24 | 3835 | 38.7288 | 201.2516 | 448.2014 | 454.2064 | -16.9281 | -42.2869 | 10.3738 | 6.9259 | 1.4735 | -0.4225 | 2.6293 | -1.4015 | 10.8003 | 3.6328 | 0.6114 | 0.653 | 0.958 | 0.7342 | -129.4298 | -1.1755 | 5.6147 | 1.7713 | -3.1851 | -1.7124 | 4.3387 |  | 2.5519 | -0.131 | 4.0099 | 3.3655 | 3.341 | 1.0665 | 10.7521 | 14.2315 | 14.8414 | 11.0641 | 0.0003 | -0.0026 | 0.0005 | 0.0038 | 0.0006 | -0.0001 | 0.0227 | 0.0003 | -0.0024 | -360.1988 | 17.3987 | -360.4235 | 17.6677 | -360.7466 | 18.0865 | -360.8635 | 17.5527 | -352.6413 | 18.6902 | -352.6075 | 16.7807
12:24 | 3836 | 38.755 | 201.2807 | 448.2812 | 454.3112 | -16.9822 | -42.3453 | 10.3164 | 6.9636 | 1.4751 | -0.2505 | 2.6062 | -1.353 | 10.7764 | 3.716 | 0.6117 | 0.655 | 0.9585 | 0.734 | -129.4163 | -1.1521 | 5.5653 | 1.7198 | -3.2251 | -1.6884 | 4.3076 |  | 2.532 | -0.1232 | 4.01 | 3.3634 | 3.3423 | 1.0658 | 10.7209 | 14.2404 | 14.8018 | 11.0627 | -0.0002 | -0.003 | 0.0008 | 0.0042 | 0.0007 | -0.0011 | 0.0007 | -0.0001 | -0.0074 | -360.1373 | 17.4192 | -360.5158 | 17.7252 | -360.842 | 18.0865 | -360.8112 | 17.528 | -352.626 | 18.7066 | -352.6967 | 16.8361
12:24 | 3837 | 38.7711 | 201.2665 | 448.2901 | 454.3169 | -16.9933 | -42.323 | 10.1961 | 6.9385 | 1.4088 | -0.2995 | 2.6008 | -1.4237 | 10.8626 | 3.6706 | 0.6107 | 0.6582 | 0.9586 | 0.7353 | -129.5128 | -1.2392 | 5.5622 | 1.7909 | -3.165 | -1.681 | 4.3313 |  | 2.6573 | -0.0131 | 4.0086 | 3.3636 | 3.3412 | 1.0669 | 10.7231 | 14.2604 | 14.8182 | 11.0641 | -0.0002 | -0.0027 | 0.0009 | 0.0038 | 0.0002 | -0.0004 | -0.005 | -0.0024 | -0.016 | -360.1804 | 17.3946 | -360.4604 | 17.7252 | -360.845 | 18.1481 | -360.9097 | 17.5527 | -352.6537 | 18.6943 | -352.6567 | 16.8217
12:24 | 3838 | 38.7684 | 201.1307 | 448.1351 | 454.2381 | -16.9648 | -42.2601 | 10.2246 | 7.0496 | 1.3894 | -0.4549 | 2.6364 | -1.4581 | 10.8478 | 3.735 | 0.6112 | 0.6558 | 0.9566 | 0.7325 | -129.3827 | -1.2105 | 5.5735 | 1.7615 | -3.2446 | -1.6435 | 4.329 |  | 2.5957 | -0.1174 | 4.0101 | 3.3625 | 3.3397 | 1.0666 | 10.7556 | 14.2291 | 14.8039 | 11.085 | 0.0002 | -0.003 | 0.0008 | 0.0041 | 0.0013 | -0.0003 | 0.0024 | -0.008 | -0.0143 | -360.2419 | 17.4418 | -360.5035 | 17.7087 | -360.802 | 18.1112 | -360.8912 | 17.5835 | -352.6752 | 18.7333 | -352.7213 | 16.8053
12:24 | 3839 | 38.7809 | 201.1683 | 448.1304 | 454.193 | -16.8841 | -42.2806 | 10.3456 | 7.0084 | 1.3244 | -0.4127 | 2.6904 | -1.4621 | 10.7554 | 3.7379 | 0.6117 | 0.6576 | 0.9597 | 0.7334 | -129.4091 | -1.3428 | 5.6137 | 1.6778 | -3.2781 | -1.7756 | 4.2537 |  | 2.6689 | -0.0945 | 4.0095 | 3.3649 | 3.3413 | 1.0658 | 10.7406 | 14.2717 | 14.8103 | 11.0648 | 0.0001 | -0.0031 | 0.0007 | 0.0037 | 0.0007 | -0.0003 | 0.0112 | -0.0011 | -0.0031 | -360.1558 | 17.411 | -360.5004 | 17.7375 | -360.8481 | 18.0988 | -360.8574 | 17.5301 | -352.6598 | 18.7148 | -352.7367 | 16.8423
12:24 | 3840 | 38.7892 | 201.1602 | 448.2533 | 454.2202 | -16.9184 | -42.2364 | 10.3816 | 6.9743 | 1.2583 | -0.377 | 2.6533 | -1.4534 | 10.7395 | 3.6425 | 0.6115 | 0.6555 | 0.9584 | 0.7346 | -129.4098 | -1.2707 | 5.6423 | 1.6692 | -3.3277 | -1.7156 | 4.305 |  | 2.5975 | -0.114 | 4.0084 | 3.3628 | 3.3397 | 1.066 | 10.7451 | 14.2361 | 14.811 | 11.0688 | 0.0002 | -0.0024 | 0.001 | 0.0036 | 0.0009 | -0.0006 | 0.0178 | -0.003 | -0.0078 | -360.1435 | 17.3699 | -360.405 | 17.6944 | -360.7897 | 18.1235 | -360.8881 | 17.5547 | -352.6321 | 18.6758 | -352.6167 | 16.8094
12:24 | 3841 | 38.8748 | 201.187 | 448.2016 | 454.2313 | -16.9817 | -42.3114 | 10.3587 | 7.0261 | 1.3243 | -0.3261 | 2.6654 | -1.403 | 10.7239 | 3.7118 | 0.6114 | 0.6552 | 0.9592 | 0.7327 | -129.3478 | -1.1532 | 5.6286 | 1.6805 | -3.3461 | -1.7106 | 4.2719 |  | 2.6605 | -0.0486 | 4.008 | 3.3674 | 3.3427 | 1.0652 | 10.7487 | 14.2277 | 14.8004 | 11.0963 | -0.0003 | -0.0028 | 0.0007 | 0.0037 | 0.0006 | -0.0007 | 0.013 | -0.0062 | -0.0217 | -360.2235 | 17.4172 | -360.4419 | 17.6636 | -360.7497 | 18.0598 | -360.8266 | 17.5547 | -352.6629 | 18.7128 | -352.666 | 16.7827
12:24 | 3842 | 38.7304 | 201.2394 | 448.3076 | 454.1736 | -17.0168 | -42.4138 | 10.3275 | 7.0164 | 1.296 | -0.3441 | 2.7436 | -1.4641 | 10.7159 | 3.6571 | 0.611 | 0.6568 | 0.9596 | 0.735 | -129.2964 | -1.1764 | 5.623 | 1.7044 | -3.3265 | -1.6946 | 4.3526 |  | 2.6161 | 0.0325 | 4.0095 | 3.364 | 3.3414 | 1.0669 | 10.7313 | 14.2567 | 14.8246 | 11.0555 | -0.0002 | -0.0029 | 0.0007 | 0.0037 | 0.0008 | -0.0001 | 0.0224 | -0.0019 | -0.0076 | -360.1527 | 17.3966 | -360.485 | 17.7313 | -360.842 | 18.0988 | -360.8481 | 17.5198 | -352.6229 | 18.7004 | -352.6629 | 16.8258
12:24 | 3843 | 38.7227 | 201.2344 | 448.1612 | 454.235 | -16.9619 | -42.4227 | 10.3399 | 7.0926 | 1.3024 | -0.3334 | 2.6963 | -1.3132 | 10.8017 | 3.6704 | 0.6107 | 0.6557 | 0.9584 | 0.7329 | -129.4087 | -1.1933 | 5.5929 | 1.8263 | -3.3152 | -1.7291 | 4.3429 |  | 2.5977 | -0.0001 | 4.0096 | 3.3691 | 3.3404 | 1.0672 | 10.736 | 14.2555 | 14.8174 | 11.0717 | 0.0001 | -0.0031 | 0.0004 | 0.0039 | 0.0013 | -0.0003 | 0.0221 | -0.0042 | -0.0297 | -360.1958 | 17.3987 | -360.4112 | 17.6923 | -360.8235 | 18.1337 | -360.9281 | 17.5773 | -352.6721 | 18.6881 | -352.6229 | 16.7868
12:24 | 3844 | 38.7133 | 201.1451 | 448.2654 | 454.25 | -16.9702 | -42.4383 | 10.3017 | 7.1857 | 1.2742 | -0.3914 | 2.7329 | -1.3891 | 10.6914 | 3.6558 | 0.6133 | 0.6581 | 0.9616 | 0.7343 | -129.4579 | -1.2043 | 5.4947 | 1.7793 | -3.2533 | -1.7557 | 4.3923 |  | 2.622 | -0.048 | 4.0086 | 3.3669 | 3.3436 | 1.0679 | 10.7453 | 14.2183 | 14.8252 | 11.0873 | -0.0004 | -0.003 | 0.0005 | 0.0039 | 0.0005 | -0.0005 | 0.0137 | -0.017 | -0.0198 | -360.2696 | 17.45 | -360.5343 | 17.7149 | -360.8081 | 18.1091 | -360.8666 | 17.5753 | -352.7213 | 18.7395 | -352.7275 | 16.8156
12:24 | 3845 | 38.7748 | 201.1196 | 448.3746 | 454.3026 | -16.9693 | -42.4173 | 10.1976 | 7.1669 | 1.3134 | -0.374 | 2.7169 | -1.4031 | 10.7891 | 3.6256 | 0.6119 | 0.6588 | 0.9629 | 0.7337 | -129.4494 | -1.1627 | 5.5275 | 1.8423 | -3.2416 | -1.5912 | 4.3736 |  | 2.6619 | -0.0001 | 4.0097 | 3.3676 | 3.3443 | 1.0661 | 10.7451 | 14.2419 | 14.8458 | 11.0919 | -0.0004 | -0.0027 | 0.0011 | 0.004 | 0.0012 | -0.0006 | 0.0087 | 0.002 | -0.0049 | -360.1496 | 17.3987 | -360.485 | 17.7477 | -360.8666 | 18.1317 | -360.885 | 17.5424 | -352.6136 | 18.6963 | -352.7152 | 16.8443
12:24 | 3846 | 38.8356 | 201.208 | 448.2903 | 454.317 | -16.9181 | -42.2176 | 10.2715 | 7.1026 | 1.2879 | -0.5096 | 2.6869 | -1.3993 | 10.8109 | 3.6603 | 0.6111 | 0.6569 | 0.9578 | 0.7317 | -129.349 | -1.1973 | 5.5635 | 1.8824 | -3.2584 | -1.684 | 4.3326 |  | 2.631 | -0.1126 | 4.0102 | 3.3667 | 3.3416 | 1.0669 | 10.7683 | 14.2938 | 14.8273 | 11.1096 | -0.0003 | -0.003 | 0.0003 | 0.0037 | 0.0007 | -0.0006 | 0.0214 | -0.0217 | -0.0116 | -360.1804 | 17.3699 | -360.4019 | 17.6738 | -360.7712 | 18.1132 | -360.9097 | 17.565 | -352.666 | 18.684 | -352.6136 | 16.7827
12:24 | 3847 | 38.8504 | 201.2119 | 448.3236 | 454.3231 | -16.9312 | -42.3766 | 10.23 | 7.1876 | 1.3105 | -0.3982 | 2.6138 | -1.4 | 10.8199 | 3.7472 | 0.6107 | 0.655 | 0.9572 | 0.7306 | -129.4087 | -1.3061 | 5.5002 | 1.8204 | -3.2986 | -1.7352 | 4.3678 |  | 2.5993 | -0.036 | 4.0093 | 3.3652 | 3.3423 | 1.0675 | 10.7128 | 14.2499 | 14.8185 | 11.0887 | -0.0003 | -0.0033 | 0.0005 | 0.0034 | 0.0013 | -0.0006 | 0.0099 | 0.0093 | -0.0036 | -360.1742 | 17.4192 | -360.4604 | 17.6902 | -360.7712 | 18.0783 | -360.8112 | 17.5404 | -352.6537 | 18.7066 | -352.6567 | 16.795
12:24 | 3848 | 38.7479 | 201.1978 | 448.2083 | 454.2457 | -16.9337 | -42.2705 | 10.2626 | 7.1525 | 1.3565 | -0.4523 | 2.6172 | -1.3697 | 10.7602 | 3.7069 | 0.6122 | 0.6582 | 0.9609 | 0.7331 | -129.3737 | -1.2213 | 5.5546 | 1.7807 | -3.3081 | -1.7575 | 4.3002 |  | 2.6115 | -0.0359 | 4.0087 | 3.3654 | 3.3427 | 1.0664 | 10.7729 | 14.2524 | 14.8165 | 11.0789 | -0.0001 | -0.0031 | 0.0008 | 0.0034 | 0.0009 | -0.0001 | 0.0057 | -0.0114 | -0.0107 | -360.1465 | 17.3823 | -360.4604 | 17.7169 | -360.8327 | 18.1214 | -360.8574 | 17.5178 | -352.6044 | 18.6737 | -352.669 | 16.8156
12:24 | 3849 | 38.8203 | 201.1937 | 448.3086 | 454.2637 | -17.0807 | -42.2437 | 10.1925 | 7.1575 | 1.2897 | -0.5364 | 2.6255 | -1.3686 | 10.8001 | 3.6206 | 0.6109 | 0.6541 | 0.9579 | 0.7334 | -129.4857 | -1.2224 | 5.5329 | 1.8269 | -3.2787 | -1.6435 | 4.3728 |  | 2.6364 | -0.1264 | 4.0096 | 3.3655 | 3.3405 | 1.0672 | 10.7441 | 14.252 | 14.8018 | 11.0627 | -0.0004 | -0.0028 | 0.0009 | 0.0038 | 0.0007 | -0.0011 | 0.0102 | -0.0116 | -0.0153 | -360.2142 | 17.411 | -360.4266 | 17.6902 | -360.8112 | 18.1296 | -360.9097 | 17.5814 | -352.6721 | 18.6984 | -352.6198 | 16.7807
12:24 | 3850 | 38.8249 | 201.1537 | 448.2486 | 454.2482 | -16.9268 | -42.05 | 10.3649 | 7.1557 | 1.2677 | -0.4521 | 2.6711 | -1.3076 | 10.811 | 3.7519 | 0.6123 | 0.6576 | 0.9607 | 0.7348 | -129.4885 | -1.2505 | 5.6129 | 1.8938 | -3.282 | -1.7289 | 4.3407 |  | 2.6393 | -0.06 | 4.0111 | 3.3674 | 3.3428 | 1.067 | 10.7487 | 14.2163 | 14.8304 | 11.0728 | -0.0002 | -0.0032 | 0.0009 | 0.0037 | 0.0007 | 0 | 0.0006 | -0.0174 | -0.0273 | -360.2419 | 17.45 | -360.5312 | 17.7334 | -360.8358 | 18.0968 | -360.8512 | 17.5609 | -352.706 | 18.7477 | -352.7121 | 16.8258
12:24 | 3851 | 38.7777 | 201.1512 | 448.2459 | 454.1996 | -17.0111 | -42.1152 | 10.2905 | 7.2599 | 1.3296 | -0.3273 | 2.7874 | -1.3087 | 10.8056 | 3.7118 | 0.6123 | 0.6587 | 0.9605 | 0.7367 | -129.4184 | -1.2188 | 5.6291 | 1.7827 | -3.3218 | -1.9061 | 4.3612 |  | 2.6625 | -0.1255 | 4.01 | 3.3648 | 3.3382 | 1.0665 | 10.7405 | 14.2545 | 14.8287 | 11.0587 | 0.0001 | -0.0032 | 0.0006 | 0.0038 | 0.0008 | -0.0002 | -0.0029 | -0.0021 | -0.0317 | -360.1558 | 17.3905 | -360.4696 | 17.721 | -360.8789 | 18.1399 | -360.8727 | 17.5383 | -352.6229 | 18.6861 | -352.6598 | 16.8279
12:24 | 3852 | 38.7437 | 201.1562 | 448.2896 | 454.3044 | -16.8616 | -42.0074 | 10.3968 | 7.2073 | 1.3551 | -0.3438 | 2.6709 | -1.291 | 10.8067 | 3.727 | 0.6107 | 0.6591 | 0.9582 | 0.7358 | -129.4393 | -1.1584 | 5.5884 | 1.6195 | -3.34 | -1.8617 | 4.2775 |  | 2.5808 | -0.1503 | 4.0087 | 3.3661 | 3.3403 | 1.0639 | 10.7672 | 14.2521 | 14.826 | 11.0912 | 0.0004 | -0.0029 | 0.0009 | 0.0044 | 0.0009 | -0.0006 | 0.0212 | -0.0079 | -0.0128 | -360.1896 | 17.3884 | -360.4081 | 17.6882 | -360.7989 | 18.1153 | -360.885 | 17.5691 | -352.666 | 18.6861 | -352.6383 | 16.7971
12:24 | 3853 | 38.7607 | 201.091 | 448.2332 | 454.2194 | -16.975 | -42.1781 | 10.3107 | 7.1813 | 1.3471 | -0.3512 | 2.6868 | -1.3414 | 10.8621 | 3.7428 | 0.6129 | 0.6556 | 0.9614 | 0.7344 | -129.4276 | -1.2751 | 5.514 | 1.6869 | -3.2927 | -1.7785 | 4.3608 |  | 2.6349 | -0.1136 | 4.0091 | 3.3677 | 3.3374 | 1.0657 | 10.7289 | 14.2431 | 14.8182 | 11.0583 | -0.0002 | -0.0025 | 0.0006 | 0.004 | 0.0007 | -0.0002 | 0.0076 | -0.0101 | -0.0171 | -360.1588 | 17.409 | -360.4696 | 17.6985 | -360.805 | 18.0701 | -360.8112 | 17.5342 | -352.6383 | 18.7107 | -352.6475 | 16.8012
12:24 | 3854 | 38.7635 | 201.1177 | 448.2468 | 454.3276 | -16.9519 | -42.1817 | 10.2102 | 7.1033 | 1.2382 | -0.465 | 2.6324 | -1.4002 | 10.8906 | 3.7595 | 0.6117 | 0.6579 | 0.9624 | 0.7349 | -129.4628 | -1.1789 | 5.5452 | 1.671 | -3.3542 | -1.8245 | 4.3042 |  | 2.6092 | -0.1256 | 4.0096 | 3.3622 | 3.3403 | 1.0671 | 10.7556 | 14.2463 | 14.8491 | 11.0912 | -0.0002 | -0.0028 | 0.0001 | 0.0033 | 0.0008 | -0.0009 | -0.0033 | -0.0152 | -0.0174 | -360.1311 | 17.3884 | -360.4542 | 17.7272 | -360.845 | 18.1214 | -360.8635 | 17.5239 | -352.589 | 18.6779 | -352.6475 | 16.8156
12:24 | 3855 | 38.7615 | 201.1931 | 448.2209 | 454.3253 | -16.96 | -42.1116 | 10.2192 | 7.1422 | 1.3773 | -0.3769 | 2.6866 | -1.3117 | 10.8595 | 3.7549 | 0.611 | 0.655 | 0.9582 | 0.7345 | -129.3688 | -1.2012 | 5.5923 | 1.6869 | -3.3402 | -1.83 | 4.2556 |  | 2.6705 | -0.0624 | 4.0097 | 3.3625 | 3.34 | 1.066 | 10.7464 | 14.2486 | 14.845 | 11.0822 | 0.0001 | -0.0032 | 0.0007 | 0.0033 | 0.0003 | -0.0007 | 0.01 | -0.0108 | -0.0147 | -360.2235 | 17.4254 | -360.5066 | 17.7067 | -360.805 | 18.1112 | -360.9004 | 17.5835 | -352.6875 | 18.7189 | -352.6783 | 16.793
12:24 | 3856 | 38.7451 | 201.2737 | 448.2131 | 454.2824 | -16.8635 | -42.129 | 10.2319 | 7.0347 | 1.3392 | -0.412 | 2.5921 | -1.3364 | 10.8803 | 3.7143 | 0.613 | 0.6545 | 0.9583 | 0.7361 | -129.4363 | -1.1988 | 5.4765 | 1.7617 | -3.3528 | -1.8367 | 4.2473 |  | 2.7222 | -0.0046 | 4.0092 | 3.3646 | 3.3399 | 1.0657 | 10.7624 | 14.2536 | 14.8584 | 11.0973 | 0.0002 | -0.0031 | 0.001 | 0.0037 | 0.0009 | -0.0007 | 0.0067 | -0.0062 | -0.0162 | -360.1927 | 17.4254 | -360.4942 | 17.7477 | -360.8697 | 18.1214 | -360.8512 | 17.5527 | -352.6629 | 18.721 | -352.6998 | 16.8381
12:24 | 3857 | 38.76 | 201.143 | 448.2403 | 454.3353 | -16.8884 | -42.0924 | 10.2867 | 7.1692 | 1.5417 | -0.3001 | 2.6524 | -1.3436 | 10.8714 | 3.7843 | 0.6125 | 0.6572 | 0.9612 | 0.7358 | -129.5569 | -1.1809 | 5.4743 | 1.7849 | -3.3904 | -1.8262 | 4.3441 |  | 2.6738 | -0.0449 | 4.0095 | 3.3635 | 3.3363 | 1.0668 | 10.7361 | 14.2321 | 14.8385 | 11.0725 | 0 | -0.0026 | 0.0007 | 0.0039 | 0 | -0.0006 | 0.0355 | -0.0088 | 0.0094 | -360.1773 | 17.3987 | -360.4419 | 17.7067 | -360.802 | 18.1214 | -360.9343 | 17.5609 | -352.666 | 18.6943 | -352.6598 | 16.8094
12:24 | 3858 | 38.7545 | 201.1131 | 448.1296 | 454.2894 | -16.8339 | -42.0955 | 10.2561 | 7.0829 | 1.52 | -0.2577 | 2.5835 | -1.4028 | 10.8134 | 3.7944 | 0.6116 | 0.6524 | 0.9631 | 0.7354 | -129.4825 | -1.2854 | 5.4782 | 1.6621 | -3.3145 | -1.7732 | 4.2737 |  | 2.6404 | -0.0473 | 4.0098 | 3.3631 | 3.3363 | 1.064 | 10.7313 | 14.2336 | 14.813 | 11.0439 | -0.0004 | -0.0026 | 0.0012 | 0.0041 | 0.0007 | -0.0009 | 0.0344 | -0.0083 | 0.0065 | -360.165 | 17.3987 | -360.4389 | 17.6985 | -360.7773 | 18.0968 | -360.8327 | 17.565 | -352.629 | 18.7004 | -352.6506 | 16.795
12:24 | 3859 | 38.8145 | 201.205 | 448.3405 | 454.3899 | -16.7223 | -42.1032 | 10.2891 | 7.0587 | 1.5547 | -0.3465 | 2.5668 | -1.4336 | 10.8553 | 3.7381 | 0.6127 | 0.6527 | 0.9616 | 0.7342 | -129.487 | -1.4129 | 5.4415 | 1.611 | -3.355 | -1.7629 | 4.2463 |  | 2.7032 | -0.0115 | 4.01 | 3.3673 | 3.3333 | 1.0656 | 10.7163 | 14.2474 | 14.8147 | 11.0695 | 0.0005 | -0.0029 | 0.0007 | 0.0039 | 0.0004 | -0.0005 | 0.0065 | -0.0012 | -0.0103 | -360.125 | 17.3905 | -360.4358 | 17.6882 | -360.7897 | 18.1296 | -360.8112 | 17.565 | -352.6013 | 18.684 | -352.6198 | 16.795
12:24 | 3860 | 38.7581 | 201.2105 | 448.3367 | 454.4295 | -16.7939 | -42.1259 | 10.2385 | 7.1523 | 1.5255 | -0.3319 | 2.7156 | -1.4123 | 10.792 | 3.6737 | 0.6103 | 0.6554 | 0.9611 | 0.7348 | -129.4956 | -1.34 | 5.4182 | 1.6441 | -3.1947 | -1.6928 | 4.3119 |  | 2.685 | -0.0274 | 4.01 | 3.3647 | 3.338 | 1.0654 | 10.7452 | 14.2533 | 14.8505 | 11.0923 | 0.0001 | -0.0031 | 0.0008 | 0.0043 | 0.0006 | -0.0008 | 0.0089 | -0.0151 | -0.004 | -360.1588 | 17.3987 | -360.4635 | 17.6759 | -360.7927 | 18.1379 | -360.8481 | 17.604 | -352.6136 | 18.7004 | -352.6383 | 16.7827
12:24 | 3861 | 38.83 | 201.2125 | 448.3189 | 454.3735 | -16.8325 | -42.1364 | 10.1519 | 7.1661 | 1.4396 | -0.2971 | 2.6801 | -1.4018 | 10.7126 | 3.6778 | 0.6116 | 0.6585 | 0.9601 | 0.7338 | -129.4809 | -1.3376 | 5.4527 | 1.6118 | -3.2277 | -1.7473 | 4.294 |  | 2.7183 | -0.0747 | 4.0113 | 3.3675 | 3.3401 | 1.066 | 10.7416 | 14.2674 | 14.8022 | 11.0941 | 0.0001 | -0.0025 | 0.0006 | 0.004 | 0.0009 | -0.0004 | 0.0072 | 0.003 | -0.0109 | -360.1988 | 17.4151 | -360.4912 | 17.7067 | -360.8266 | 18.1399 | -360.8512 | 17.6061 | -352.6475 | 18.7107 | -352.669 | 16.7991
12:24 | 3862 | 38.7796 | 201.1524 | 448.2963 | 454.4239 | -16.8474 | -42.0721 | 10.1608 | 7.1681 | 1.4498 | -0.33 | 2.713 | -1.4076 | 10.7685 | 3.6904 | 0.6108 | 0.656 | 0.9586 | 0.7335 | -129.3698 | -1.3118 | 5.4312 | 1.6047 | -3.2283 | -1.8998 | 4.3235 |  | 2.6583 | 0.033 | 4.0109 | 3.3626 | 3.3382 | 1.065 | 10.7302 | 14.2496 | 14.7817 | 11.0548 | -0.0006 | -0.0025 | 0.0005 | 0.0035 | 0.0006 | -0.0005 | 0.0028 | -0.0044 | 0.0059 | -360.205 | 17.4151 | -360.4881 | 17.7272 | -360.8574 | 18.1604 | -360.885 | 17.6225 | -352.6352 | 18.723 | -352.6998 | 16.8197
12:24 | 3863 | 38.8045 | 201.1409 | 448.4166 | 454.3968 | -16.7617 | -42.039 | 10.2335 | 7.111 | 1.3608 | -0.2762 | 2.6817 | -1.3776 | 10.7794 | 3.6982 | 0.6119 | 0.6551 | 0.9578 | 0.7333 | -129.5432 | -1.2299 | 5.5345 | 1.5506 | -3.2296 | -1.707 | 4.289 |  | 2.7253 | -0.0342 | 4.0098 | 3.3659 | 3.3418 | 1.0664 | 10.7349 | 14.2715 | 14.8324 | 11.071 | -0.0006 | -0.0031 | 0.0004 | 0.0033 | 0.0012 | -0.0006 | 0.0167 | -0.015 | -0.0315 | -360.1988 | 17.4048 | -360.4512 | 17.7087 | -360.8204 | 18.1604 | -360.8666 | 17.5978 | -352.6352 | 18.7312 | -352.6906 | 16.8115
12:24 | 3864 | 38.8152 | 201.1904 | 448.3222 | 454.3624 | -16.8574 | -42.1061 | 10.3117 | 7.0419 | 1.3058 | -0.2703 | 2.6008 | -1.4232 | 10.8578 | 3.7218 | 0.6113 | 0.6559 | 0.9594 | 0.7327 | -129.5017 | -1.2561 | 5.5694 | 1.7371 | -3.2617 | -1.7287 | 4.2965 |  | 2.6953 | -0.0967 | 4.0117 | 3.3669 | 3.339 | 1.0656 | 10.7382 | 14.2581 | 14.8444 | 11.0966 | 0.0003 | -0.0031 | 0.0003 | 0.0033 | 0.0005 | -0.0004 | -0.0025 | -0.0087 | -0.0031 | -360.1865 | 17.3987 | -360.4635 | 17.6902 | -360.8081 | 18.1337 | -360.842 | 17.602 | -352.6383 | 18.7025 | -352.6598 | 16.795
12:24 | 3865 | 38.8588 | 201.2299 | 448.3396 | 454.343 | -16.7773 | -42.0106 | 10.3914 | 7.0734 | 1.2837 | -0.4039 | 2.5836 | -1.3321 | 10.8874 | 3.7514 | 0.6114 | 0.6528 | 0.9609 | 0.7341 | -129.5236 | -1.2761 | 5.5356 | 1.861 | -3.2139 | -1.6304 | 4.3398 |  | 2.7838 | -0.0489 | 4.0108 | 3.3664 | 3.3435 | 1.0655 | 10.713 | 14.2262 | 14.8085 | 11.0844 | -0.0003 | -0.0032 | 0.0005 | 0.0038 | 0.0008 | -0.0004 | 0.0038 | -0.0136 | 0.0003 | -360.1804 | 17.3864 | -360.4481 | 17.6985 | -360.7835 | 18.1194 | -360.805 | 17.5917 | -352.5921 | 18.7004 | -352.6506 | 16.7991
12:24 | 3866 | 38.8687 | 201.2021 | 448.3065 | 454.3901 | -16.8482 | -42.1534 | 10.3024 | 7.1163 | 1.2999 | -0.3516 | 2.67 | -1.4429 | 10.7992 | 3.6594 | 0.6104 | 0.6557 | 0.9601 | 0.7333 | -129.4134 | -1.2704 | 5.5976 | 1.8576 | -3.2545 | -1.6052 | 4.3637 |  | 2.7461 | 0.033 | 4.0109 | 3.3652 | 3.3413 | 1.0651 | 10.7186 | 14.2438 | 14.8048 | 11.0374 | -0.0003 | -0.0026 | 0.0008 | 0.0041 | 0.0007 | 0 | 0.0017 | 0.0035 | -0.0216 | -360.1373 | 17.3638 | -360.3742 | 17.6697 | -360.7773 | 18.1214 | -360.8235 | 17.5855 | -352.5983 | 18.682 | -352.5921 | 16.7848
12:24 | 3867 | 38.8451 | 201.0788 | 448.3086 | 454.306 | -16.8093 | -42.0682 | 10.3913 | 7.1279 | 1.336 | -0.2651 | 2.7843 | -1.4047 | 10.8686 | 3.6649 | 0.6128 | 0.656 | 0.9615 | 0.7336 | -129.4067 | -1.3177 | 5.6325 | 1.7573 | -3.2198 | -1.7331 | 4.3362 |  | 2.6692 | -0.0287 | 4.0104 | 3.3631 | 3.3434 | 1.0642 | 10.7417 | 14.2613 | 14.8348 | 11.0775 | -0.0004 | -0.003 | 0.0003 | 0.0037 | 0.0006 | -0.0006 | 0.015 | 0.0045 | 0.0001 | -360.1927 | 17.4233 | -360.4573 | 17.6738 | -360.7681 | 18.1132 | -360.8174 | 17.6102 | -352.6475 | 18.7271 | -352.6475 | 16.7786
12:24 | 3868 | 38.9283 | 201.1607 | 448.3431 | 454.3427 | -16.8428 | -42.0843 | 10.2902 | 7.04 | 1.4118 | -0.2971 | 2.7268 | -1.4988 | 10.7993 | 3.6517 | 0.6111 | 0.6581 | 0.9599 | 0.7351 | -129.4713 | -1.2931 | 5.6248 | 1.7117 | -3.1163 | -1.7607 | 4.3519 |  | 2.7015 | -0.0093 | 4.0125 | 3.3645 | 3.3435 | 1.0663 | 10.7394 | 14.2764 | 14.8331 | 11.0923 | 0.0002 | -0.0032 | 0.0007 | 0.0038 | 0.0006 | -0.0001 | 0.0294 | -0.0012 | -0.0096 | -360.165 | 17.4048 | -360.4912 | 17.7128 | -360.8574 | 18.1317 | -360.8235 | 17.5568 | -352.5829 | 18.7087 | -352.706 | 16.8115
12:24 | 3869 | 38.9037 | 201.2274 | 448.4338 | 454.367 | -16.8902 | -42.1914 | 10.3153 | 7.0433 | 1.3233 | -0.334 | 2.6542 | -1.4248 | 10.7972 | 3.7105 | 0.6117 | 0.6563 | 0.9594 | 0.7345 | -129.464 | -1.2842 | 5.4451 | 1.6901 | -3.2917 | -1.7217 | 4.3713 |  | 2.81 | 0.09 | 4.0116 | 3.3684 | 3.3414 | 1.065 | 10.7682 | 14.2827 | 14.8595 | 11.1027 | 0 | -0.0027 | 0.0011 | 0.0038 | 0.0013 | -0.001 | 0.0162 | -0.0089 | -0.0074 | -360.2081 | 17.4048 | -360.4481 | 17.6944 | -360.8512 | 18.1543 | -360.8943 | 17.6245 | -352.6967 | 18.7045 | -352.6506 | 16.8074
12:24 | 3870 | 38.8974 | 201.1913 | 448.3392 | 454.3232 | -16.8309 | -42.1226 | 10.4122 | 7.072 | 1.3629 | -0.2301 | 2.595 | -1.4425 | 10.7458 | 3.7065 | 0.6111 | 0.6546 | 0.9591 | 0.7337 | -129.5352 | -1.3359 | 5.4768 | 1.4742 | -3.3211 | -1.7288 | 4.3147 |  | 2.7897 | -0.0413 | 4.0117 | 3.3624 | 3.3382 | 1.0649 | 10.7753 | 14.2603 | 14.8519 | 11.0702 | -0.0005 | -0.003 | 0.0007 | 0.0036 | 0.0005 | -0.0002 | 0.0129 | -0.0151 | 0.0182 | -360.2235 | 17.4315 | -360.5066 | 17.6985 | -360.845 | 18.1255 | -360.8666 | 17.6081 | -352.7213 | 18.7436 | -352.6875 | 16.8115
12:24 | 3871 | 38.8191 | 201.1964 | 448.3727 | 454.3927 | -16.7915 | -42.0224 | 10.4196 | 7.1139 | 1.2898 | -0.3958 | 2.6334 | -1.4917 | 10.7501 | 3.6667 | 0.6114 | 0.655 | 0.9618 | 0.7345 | -129.541 | -1.3349 | 5.4455 | 1.5726 | -3.3075 | -1.7476 | 4.2778 |  | 2.7563 | -0.0485 | 4.0108 | 3.3649 | 3.3374 | 1.0639 | 10.7602 | 14.2395 | 14.8257 | 11.0724 | 0 | -0.0026 | 0.0008 | 0.004 | 0.0008 | -0.0009 | 0.0018 | -0.0022 | -0.0155 | -360.1127 | 17.3843 | -360.4604 | 17.7005 | -360.8512 | 18.1461 | -360.8481 | 17.5712 | -352.6167 | 18.6984 | -352.6752 | 16.8217
12:24 | 3872 | 38.7872 | 201.0995 | 448.3797 | 454.3568 | -16.7911 | -42 | 10.472 | 7.1727 | 1.2923 | -0.3813 | 2.6713 | -1.4155 | 10.7987 | 3.7299 | 0.6108 | 0.6543 | 0.9626 | 0.7326 | -129.5285 | -1.3806 | 5.3524 | 1.5581 | -3.3112 | -1.6903 | 4.345 |  | 2.706 | -0.0995 | 4.0123 | 3.367 | 3.3403 | 1.0644 | 10.774 | 14.2536 | 14.8295 | 11.0973 | 0 | -0.0033 | 0.0012 | 0.004 | 0.0009 | -0.0002 | 0.0153 | -0.0026 | -0.0235 | -360.1496 | 17.3823 | -360.4112 | 17.6471 | -360.7804 | 18.1379 | -360.8543 | 17.6163 | -352.6198 | 18.6881 | -352.6167 | 16.7766
12:24 | 3873 | 38.8311 | 201.1451 | 448.4509 | 454.4251 | -16.7495 | -42.202 | 10.4105 | 7.1401 | 1.3371 | -0.356 | 2.6028 | -1.3791 | 10.7677 | 3.6794 | 0.6128 | 0.6569 | 0.9599 | 0.7326 | -129.5495 | -1.4104 | 5.481 | 1.5843 | -3.2747 | -1.6755 | 4.2769 |  | 2.7161 | -0.1156 | 4.0114 | 3.3659 | 3.3435 | 1.0653 | 10.7279 | 14.2357 | 14.8252 | 11.0815 | 0.0001 | -0.0033 | 0.0009 | 0.0038 | 0.0011 | -0.0002 | 0.0211 | -0.002 | -0.0192 | -360.1773 | 17.4069 | -360.4912 | 17.6861 | -360.8081 | 18.1029 | -360.7681 | 17.5773 | -352.6413 | 18.7107 | -352.6598 | 16.8053
12:24 | 3874 | 38.9424 | 201.2162 | 448.4073 | 454.4551 | -16.9072 | -42.3119 | 10.3075 | 7.2227 | 1.3789 | -0.3141 | 2.6368 | -1.3983 | 10.7713 | 3.6271 | 0.6119 | 0.6557 | 0.961 | 0.7342 | -129.5273 | -1.2729 | 5.4099 | 1.5947 | -3.2608 | -1.7081 | 4.3564 |  | 2.739 | -0.1535 | 4.0118 | 3.3646 | 3.3415 | 1.0635 | 10.7 | 14.2256 | 14.794 | 11.0876 | -0.0002 | -0.0027 | 0.0012 | 0.0042 | 0.0011 | -0.0004 | 0.0072 | -0.0181 | -0.0176 | -360.165 | 17.3884 | -360.4666 | 17.6902 | -360.845 | 18.1543 | -360.9097 | 17.602 | -352.6136 | 18.6922 | -352.6598 | 16.8032
12:24 | 3875 | 38.9726 | 201.1833 | 448.3841 | 454.4094 | -16.9484 | -42.419 | 10.2298 | 7.1887 | 1.3199 | -0.4119 | 2.6312 | -1.4918 | 10.7525 | 3.7712 | 0.6122 | 0.6615 | 0.9607 | 0.7342 | -129.4548 | -1.3717 | 5.3043 | 1.6734 | -3.2321 | -1.7147 | 4.2852 |  | 2.7067 | -0.0417 | 4.0111 | 3.3644 | 3.3406 | 1.0643 | 10.7463 | 14.2489 | 14.824 | 11.041 | -0.0003 | -0.0026 | 0.0008 | 0.0039 | 0.0006 | -0.0002 | 0.0109 | 0.0018 | 0.0001 | -360.2573 | 17.4131 | -360.4758 | 17.6841 | -360.8174 | 18.144 | -360.9127 | 17.641 | -352.6875 | 18.723 | -352.6721 | 16.7889
12:24 | 3876 | 38.9457 | 201.3032 | 448.4946 | 454.4486 | -16.9656 | -42.3852 | 10.2653 | 7.0751 | 1.2731 | -0.3463 | 2.6577 | -1.4765 | 10.8418 | 3.7587 | 0.6136 | 0.6554 | 0.965 | 0.7343 | -129.4494 | -1.1683 | 5.3827 | 1.7126 | -3.3434 | -1.5783 | 4.3616 |  | 2.7437 | -0.0631 | 4.0107 | 3.3659 | 3.3416 | 1.0662 | 10.736 | 14.238 | 14.8106 | 11.0663 | 0.0005 | -0.0029 | 0.0005 | 0.0036 | 0.001 | -0.0008 | 0.0162 | 0.008 | -0.0095 | -360.1927 | 17.4233 | -360.5035 | 17.7231 | -360.8697 | 18.1173 | -360.8174 | 17.5978 | -352.669 | 18.7395 | -352.7152 | 16.8299
12:24 | 3877 | 38.8794 | 201.237 | 448.3984 | 454.3377 | -16.9528 | -42.3909 | 10.2622 | 7.1591 | 1.3215 | -0.3443 | 2.6571 | -1.3841 | 10.7688 | 3.7385 | 0.6121 | 0.654 | 0.9622 | 0.7345 | -129.4636 | -1.1897 | 5.5158 | 1.6864 | -3.2812 | -1.5948 | 4.3722 |  | 2.7528 | -0.071 | 4.0114 | 3.3637 | 3.3412 | 1.0659 | 10.7325 | 14.2346 | 14.8191 | 11.028 | 0 | -0.0029 | 0.0008 | 0.0041 | 0.0006 | -0.0003 | 0.0068 | -0.01 | -0.0203 | -360.1311 | 17.3638 | -360.4142 | 17.6779 | -360.845 | 18.1522 | -360.8758 | 17.5978 | -352.629 | 18.6799 | -352.6229 | 16.8053
12:24 | 3878 | 38.878 | 201.2926 | 448.3558 | 454.3671 | -16.8998 | -42.4361 | 10.2667 | 7.1078 | 1.2816 | -0.4506 | 2.6304 | -1.416 | 10.7239 | 3.7338 | 0.6125 | 0.6552 | 0.963 | 0.7351 | -129.4943 | -1.3014 | 5.4994 | 1.7563 | -3.2553 | -1.5538 | 4.4006 |  | 2.7425 | -0.1916 | 4.0117 | 3.3649 | 3.3383 | 1.066 | 10.751 | 14.2591 | 14.8158 | 11.0634 | -0.0003 | -0.0025 | 0.0005 | 0.0036 | 0.0011 | -0.0003 | 0.0039 | -0.007 | -0.0186 | -360.2019 | 17.409 | -360.445 | 17.6512 | -360.7589 | 18.0988 | -360.802 | 17.5917 | -352.6444 | 18.721 | -352.6629 | 16.7745
12:24 | 3879 | 38.9005 | 201.2199 | 448.3287 | 454.3317 | -16.9602 | -42.3675 | 10.1969 | 7.168 | 1.3258 | -0.3993 | 2.7031 | -1.4073 | 10.7217 | 3.7275 | 0.612 | 0.6527 | 0.9609 | 0.7349 | -129.5432 | -1.2616 | 5.5204 | 1.6756 | -3.3228 | -1.6968 | 4.349 |  | 2.6998 | -0.226 | 4.0103 | 3.3615 | 3.34 | 1.0649 | 10.7187 | 14.2379 | 14.7864 | 11.0609 | -0.0003 | -0.0028 | 0.0008 | 0.0037 | 0.0004 | -0.0005 | 0.0201 | -0.0111 | -0.0138 | -360.1527 | 17.3946 | -360.4819 | 17.7046 | -360.8912 | 18.1317 | -360.7835 | 17.5609 | -352.586 | 18.6922 | -352.6567 | 16.8176
12:24 | 3880 | 38.963 | 201.2178 | 448.3891 | 454.4569 | -16.9832 | -42.3457 | 10.1891 | 7.0925 | 1.2728 | -0.369 | 2.6091 | -1.5349 | 10.72 | 3.7414 | 0.612 | 0.651 | 0.962 | 0.7344 | -129.5134 | -1.1914 | 5.5395 | 1.655 | -3.4045 | -1.783 | 4.2977 |  | 2.6592 | -0.1949 | 4.0122 | 3.3666 | 3.3425 | 1.065 | 10.7394 | 14.2475 | 14.8679 | 11.0865 | 0.0001 | -0.003 | 0.0012 | 0.004 | 0.0009 | -0.0007 | 0.0036 | -0.0087 | -0.005 | -360.205 | 17.3966 | -360.4358 | 17.6841 | -360.8297 | 18.1481 | -360.8974 | 17.6266 | -352.6629 | 18.6963 | -352.6321 | 16.7909
12:24 | 3881 | 38.9201 | 201.274 | 448.4323 | 454.475 | -16.9784 | -42.288 | 10.1461 | 7.0825 | 1.2184 | -0.347 | 2.6166 | -1.4625 | 10.7649 | 3.733 | 0.612 | 0.6513 | 0.9592 | 0.7329 | -129.5266 | -1.1768 | 5.5235 | 1.7181 | -3.363 | -1.6712 | 4.3212 |  | 2.7704 | -0.1007 | 4.0126 | 3.3633 | 3.3436 | 1.0643 | 10.7521 | 14.2545 | 14.875 | 11.0991 | 0 | -0.003 | 0.001 | 0.0038 | 0.0006 | -0.0005 | 0.019 | -0.0133 | -0.0047 | -360.2173 | 17.4418 | -360.5404 | 17.7149 | -360.8543 | 18.1255 | -360.8266 | 17.6081 | -352.6752 | 18.7436 | -352.7244 | 16.8176
12:24 | 3882 | 38.8497 | 201.256 | 448.3505 | 454.4253 | -16.9349 | -42.2335 | 10.2567 | 7.1001 | 1.2521 | -0.2762 | 2.701 | -1.4354 | 10.8288 | 3.799 | 0.6106 | 0.6555 | 0.9611 | 0.735 | -129.4942 | -1.1457 | 5.4957 | 1.6802 | -3.3269 | -1.745 | 4.3253 |  | 2.7998 | -0.0821 | 4.0133 | 3.3647 | 3.3415 | 1.066 | 10.706 | 14.2541 | 14.8371 | 11.0887 | -0.0003 | -0.0029 | 0.001 | 0.0044 | 0.0008 | -0.0007 | 0.0228 | 0.0053 | 0.004 | -360.1435 | 17.3823 | -360.4881 | 17.7005 | -360.845 | 18.1687 | -360.8543 | 17.5937 | -352.6136 | 18.7045 | -352.6721 | 16.8299
12:24 | 3883 | 38.8709 | 201.3144 | 448.45 | 454.411 | -16.9678 | -42.2342 | 10.2475 | 7.1615 | 1.252 | -0.2709 | 2.6602 | -1.4324 | 10.8027 | 3.7122 | 0.6132 | 0.6546 | 0.9606 | 0.7335 | -129.4442 | -1.245 | 5.5546 | 1.7666 | -3.2502 | -1.5601 | 4.3638 |  | 2.8089 | -0.0116 | 4.0122 | 3.3639 | 3.3386 | 1.0656 | 10.7751 | 14.2318 | 14.8551 | 11.0922 | 0.0002 | -0.002 | 0.0008 | 0.0041 | 0.0007 | 0 | 0.0206 | -0.0076 | -0.0172 | -360.1619 | 17.3925 | -360.4266 | 17.6492 | -360.765 | 18.1173 | -360.8389 | 17.6184 | -352.6598 | 18.7189 | -352.6352 | 16.7868
12:24 | 3884 | 38.8999 | 201.3738 | 448.4174 | 454.4147 | -16.9265 | -42.2273 | 10.265 | 7.1593 | 1.2387 | -0.2319 | 2.6971 | -1.4482 | 10.8211 | 3.6708 | 0.6117 | 0.6545 | 0.962 | 0.7339 | -129.4827 | -1.2575 | 5.4512 | 1.6372 | -3.3424 | -1.7481 | 4.2742 |  | 2.7925 | -0.0013 | 4.0118 | 3.3658 | 3.3412 | 1.0643 | 10.7337 | 14.2705 | 14.8089 | 11.0695 | -0.0002 | -0.0031 | 0.0004 | 0.0036 | 0.0007 | -0.0001 | 0.0021 | -0.0054 | -0.012 | -360.1311 | 17.3966 | -360.4758 | 17.6985 | -360.8112 | 18.105 | -360.7835 | 17.5629 | -352.5921 | 18.7045 | -352.6937 | 16.8443
12:24 | 3885 | 38.936 | 201.3982 | 448.3788 | 454.4368 | -16.8807 | -42.2867 | 10.4077 | 7.1603 | 1.3141 | -0.1756 | 2.6761 | -1.3573 | 10.827 | 3.683 | 0.6128 | 0.6572 | 0.9634 | 0.7335 | -129.4822 | -1.1871 | 5.5124 | 1.6533 | -3.366 | -1.7212 | 4.2691 |  | 2.7331 | -0.0518 | 4.0126 | 3.3643 | 3.3415 | 1.065 | 10.7268 | 14.2461 | 14.8239 | 11.0515 | 0.0002 | -0.0032 | 0.0007 | 0.004 | 0.0005 | -0.0009 | 0.004 | -0.011 | -0.0332 | -360.1619 | 17.3638 | -360.3773 | 17.6615 | -360.805 | 18.1481 | -360.8574 | 17.604 | -352.6198 | 18.6676 | -352.5921 | 16.7971
12:24 | 3886 | 39.0112 | 201.4335 | 448.4613 | 454.4258 | -16.933 | -42.2797 | 10.4413 | 7.0916 | 1.2241 | -0.1138 | 2.7398 | -1.4097 | 10.7504 | 3.6328 | 0.6123 | 0.656 | 0.9624 | 0.7325 | -129.4873 | -1.3123 | 5.4757 | 1.4756 | -3.331 | -1.6825 | 4.322 |  | 2.7794 | 0.0371 | 4.0119 | 3.3659 | 3.3409 | 1.0642 | 10.7359 | 14.2441 | 14.8417 | 11.0829 | -0.0002 | -0.0029 | 0.0006 | 0.0033 | 0.0006 | -0.0006 | 0.0133 | -0.0038 | -0.0118 | -360.2173 | 17.4418 | -360.5127 | 17.6964 | -360.8297 | 18.0988 | -360.8235 | 17.6225 | -352.6813 | 18.7456 | -352.7029 | 16.8176
12:24 | 3887 | 38.9853 | 201.2979 | 448.3999 | 454.4082 | -16.874 | -42.2388 | 10.3925 | 7.0352 | 1.2952 | -0.1912 | 2.7495 | -1.261 | 10.7961 | 3.7291 | 0.6127 | 0.6562 | 0.9612 | 0.7339 | -129.5003 | -1.235 | 5.4701 | 1.5548 | -3.2828 | -1.7045 | 4.3162 |  | 2.7599 | -0.0332 | 4.0122 | 3.3651 | 3.3432 | 1.0663 | 10.7327 | 14.24 | 14.8333 | 11.0696 | -0.0008 | -0.0032 | 0.0006 | 0.0036 | 0.0012 | -0.0008 | 0.0138 | -0.0115 | -0.0031 | -360.1527 | 17.3966 | -360.4942 | 17.7026 | -360.882 | 18.1584 | -360.8666 | 17.5814 | -352.6044 | 18.7045 | -352.6721 | 16.8484
12:25 | 3888 | 38.966 | 201.2708 | 448.4496 | 454.4357 | -16.8786 | -42.2782 | 10.4016 | 7.0849 | 1.2884 | -0.1986 | 2.681 | -1.3511 | 10.8047 | 3.5976 | 0.6119 | 0.6526 | 0.9622 | 0.7354 | -129.4707 | -1.2484 | 5.3866 | 1.5636 | -3.328 | -1.725 | 4.2815 |  | 2.7639 | -0.0287 | 4.0134 | 3.3617 | 3.3454 | 1.0656 | 10.7117 | 14.2197 | 14.7582 | 11.0533 | -0.0001 | -0.003 | 0.0012 | 0.004 | 0.0006 | -0.0003 | 0.0042 | 0.0063 | -0.0147 | -360.1804 | 17.4069 | -360.4419 | 17.6656 | -360.765 | 18.1071 | -360.8912 | 17.5999 | -352.7121 | 18.7128 | -352.6475 | 16.8135
12:25 | 3889 | 38.9317 | 201.2343 | 448.3594 | 454.3868 | -16.9658 | -42.2108 | 10.3001 | 7.1408 | 1.3114 | -0.0802 | 2.7878 | -1.3712 | 10.857 | 3.7184 | 0.6124 | 0.6554 | 0.9604 | 0.734 | -129.5081 | -1.189 | 5.2938 | 1.64 | -3.3652 | -1.7069 | 4.2532 |  | 2.7799 | -0.0737 | 4.0116 | 3.3654 | 3.3424 | 1.0645 | 10.7764 | 14.2673 | 14.859 | 11.0771 | -0.0001 | -0.0033 | 0.0008 | 0.004 | 0.0012 | -0.0004 | 0.0093 | -0.0122 | 0.0112 | -360.1681 | 17.3987 | -360.5035 | 17.7026 | -360.8266 | 18.0763 | -360.805 | 17.528 | -352.6352 | 18.7045 | -352.6906 | 16.8423
12:25 | 3890 | 38.8462 | 201.2856 | 448.4105 | 454.3824 | -16.8779 | -42.1945 | 10.3585 | 7.1609 | 1.3102 | -0.0669 | 2.7791 | -1.3342 | 10.8059 | 3.7305 | 0.6121 | 0.6537 | 0.9584 | 0.732 | -129.574 | -1.196 | 5.369 | 1.7676 | -3.3525 | -1.7062 | 4.2697 |  | 2.7225 | -0.1037 | 4.0118 | 3.3621 | 3.3402 | 1.0655 | 10.7649 | 14.2498 | 14.8406 | 11.0775 | 0.0001 | -0.0029 | 0.0007 | 0.004 | 0.0002 | -0.0004 | 0.0233 | -0.0045 | -0.0123 | -360.1188 | 17.3576 | -360.4173 | 17.6656 | -360.8081 | 18.1132 | -360.8574 | 17.5404 | -352.6198 | 18.6573 | -352.5952 | 16.8197
12:25 | 3891 | 38.929 | 201.3365 | 448.4775 | 454.5296 | -16.8997 | -42.1776 | 10.3155 | 7.0769 | 1.3293 | -0.1725 | 2.7713 | -1.3616 | 10.8382 | 3.6777 | 0.6117 | 0.6546 | 0.9596 | 0.7341 | -129.5877 | -1.1662 | 5.3758 | 1.6732 | -3.449 | -1.8049 | 4.2336 |  | 2.7996 | -0.0852 | 4.0127 | 3.3638 | 3.3421 | 1.0653 | 10.7484 | 14.269 | 14.8589 | 11.094 | -0.0002 | -0.0025 | 0.0009 | 0.004 | 0.0013 | -0.0003 | 0.0032 | 0.002 | 0.0003 | -360.2081 | 17.4172 | -360.4635 | 17.6615 | -360.7527 | 18.0721 | -360.8327 | 17.5506 | -352.6844 | 18.7128 | -352.6506 | 16.8012
12:25 | 3892 | 38.9624 | 201.2734 | 448.4124 | 454.5229 | -16.8774 | -42.1914 | 10.3005 | 7.1513 | 1.3416 | -0.1819 | 2.7688 | -1.3073 | 10.8278 | 3.7764 | 0.6122 | 0.6572 | 0.9567 | 0.732 | -129.5375 | -1.2389 | 5.3292 | 1.7902 | -3.3452 | -1.6566 | 4.2655 |  | 2.8343 | -0.0655 | 4.0114 | 3.3632 | 3.3389 | 1.0656 | 10.7463 | 14.2314 | 14.8519 | 11.0934 | 0.0001 | -0.0027 | 0.0004 | 0.0038 | 0.0005 | -0.0001 | 0.0192 | -0.0146 | 0.0032 | -360.125 | 17.409 | -360.4973 | 17.721 | -360.8666 | 18.1214 | -360.8635 | 17.5342 | -352.5983 | 18.7025 | -352.6967 | 16.8587
12:25 | 3893 | 39.0049 | 201.3207 | 448.3772 | 454.5446 | -16.8995 | -42.2617 | 10.2687 | 7.0309 | 1.3116 | -0.236 | 2.6429 | -1.4749 | 10.8554 | 3.6904 | 0.612 | 0.6538 | 0.9573 | 0.7343 | -129.5551 | -1.1446 | 5.3875 | 1.8685 | -3.2939 | -1.6415 | 4.352 |  | 2.8775 | -0.0583 | 4.012 | 3.3653 | 3.3425 | 1.0657 | 10.7637 | 14.2428 | 14.8103 | 11.0764 | -0.0001 | -0.0033 | 0.0006 | 0.0037 | 0.0011 | -0.0004 | 0.0227 | -0.011 | -0.0144 | -360.2481 | 17.4007 | -360.4419 | 17.6738 | -360.8327 | 18.142 | -360.9404 | 17.5896 | -352.6813 | 18.6963 | -352.6475 | 16.8176
12:25 | 3894 | 39.071 | 201.4118 | 448.4269 | 454.5567 | -16.8771 | -42.185 | 10.324 | 7.0897 | 1.3875 | -0.1343 | 2.6948 | -1.4002 | 10.8438 | 3.6756 | 0.6118 | 0.6554 | 0.9587 | 0.7361 | -129.5397 | -1.2406 | 5.5091 | 1.8098 | -3.2562 | -1.6992 | 4.3916 |  | 2.8135 | -0.0025 | 4.0128 | 3.3648 | 3.3418 | 1.0666 | 10.7406 | 14.2484 | 14.844 | 11.0883 | -0.0002 | -0.0031 | 0.0009 | 0.0039 | 0.0007 | -0.0008 | 0.0137 | 0.0023 | -0.0247 | -360.1927 | 17.4213 | -360.4973 | 17.6902 | -360.7897 | 18.0886 | -360.8297 | 17.5445 | -352.6598 | 18.723 | -352.7213 | 16.8238
12:25 | 3895 | 39.0548 | 201.397 | 448.4498 | 454.4231 | -16.9099 | -42.2111 | 10.2589 | 7.0897 | 1.3474 | -0.168 | 2.622 | -1.4127 | 10.8369 | 3.6478 | 0.6109 | 0.6555 | 0.9625 | 0.7342 | -129.5935 | -1.2583 | 5.345 | 1.7574 | -3.2237 | -1.6567 | 4.3458 |  | 2.827 | -0.0085 | 4.0132 | 3.3627 | 3.3391 | 1.0662 | 10.7511 | 14.2125 | 14.8194 | 11.0468 | -0.0002 | -0.0025 | 0.0005 | 0.0035 | 0.0008 | -0.0004 | 0.0178 | 0.0009 | -0.0285 | -360.0911 | 17.3597 | -360.3989 | 17.6759 | -360.842 | 18.1153 | -360.8389 | 17.5075 | -352.5675 | 18.6553 | -352.626 | 16.832
12:25 | 3896 | 39.0243 | 201.371 | 448.3911 | 454.461 | -16.9866 | -42.2921 | 10.2243 | 7.1338 | 1.3808 | -0.2454 | 2.7105 | -1.3266 | 10.7673 | 3.6439 | 0.6112 | 0.6562 | 0.9574 | 0.7349 | -129.5593 | -1.2359 | 5.4714 | 1.7516 | -3.2681 | -1.7486 | 4.3477 |  | 2.7653 | -0.0069 | 4.0125 | 3.3612 | 3.3407 | 1.0669 | 10.7128 | 14.2208 | 14.7827 | 11.0659 | -0.0003 | -0.0028 | 0.0012 | 0.0042 | 0.0011 | -0.0006 | 0.0143 | -0.0049 | -0.0099 | -360.1865 | 17.3843 | -360.4266 | 17.6451 | -360.7497 | 18.1029 | -360.8727 | 17.5547 | -352.6537 | 18.682 | -352.6321 | 16.7909
12:25 | 3897 | 39.006 | 201.4113 | 448.4071 | 454.5611 | -16.9823 | -42.2402 | 10.1335 | 7.13 | 1.3747 | -0.1754 | 2.6298 | -1.3093 | 10.7668 | 3.6789 | 0.6113 | 0.6572 | 0.9604 | 0.7343 | -129.4914 | -1.1557 | 5.5377 | 1.8399 | -3.2768 | -1.6357 | 4.4595 |  | 2.7862 | -0.0421 | 4.0117 | 3.3628 | 3.3412 | 1.0661 | 10.7381 | 14.2466 | 14.8455 | 11.1193 | 0.0001 | -0.003 | 0.0005 | 0.004 | 0.0008 | 0 | 0.0066 | -0.0084 | -0.0162 | -360.1988 | 17.4254 | -360.5035 | 17.7149 | -360.8604 | 18.0906 | -360.8389 | 17.5383 | -352.626 | 18.6984 | -352.709 | 16.8464
12:25 | 3898 | 39.0332 | 201.3715 | 448.3917 | 454.5501 | -16.9498 | -42.1559 | 10.1817 | 7.0768 | 1.3306 | -0.2031 | 2.681 | -1.3558 | 10.7654 | 3.7011 | 0.6114 | 0.6583 | 0.96 | 0.735 | -129.5606 | -1.1341 | 5.4479 | 1.8013 | -3.2735 | -1.5719 | 4.4346 |  | 2.7746 | 0.0148 | 4.012 | 3.3626 | 3.3414 | 1.0663 | 10.7533 | 14.2499 | 14.8532 | 11.1233 | 0.0003 | -0.003 | 0.0005 | 0.004 | 0.001 | -0.0001 | 0.0069 | -0.0122 | -0.0035 | -360.1927 | 17.3843 | -360.445 | 17.7046 | -360.8604 | 18.1563 | -360.9589 | 17.5547 | -352.6506 | 18.6758 | -352.629 | 16.8423
12:25 | 3899 | 38.9664 | 201.401 | 448.519 | 454.6511 | -16.9006 | -42.0703 | 10.3121 | 7.1099 | 1.3325 | -0.0926 | 2.6965 | -1.4696 | 10.8885 | 3.5599 | 0.6124 | 0.6541 | 0.9624 | 0.735 | -129.5008 | -1.0652 | 5.5088 | 1.7776 | -3.2936 | -1.6899 | 4.4823 |  | 2.8147 | -0.0763 | 4.0129 | 3.3638 | 3.3395 | 1.0655 | 10.7624 | 14.2594 | 14.8584 | 11.08 | -0.0002 | -0.0025 | 0.0008 | 0.0039 | 0.0002 | -0.0002 | 0.0249 | -0.0081 | -0.0317 | -360.1927 | 17.4274 | -360.4819 | 17.6718 | -360.7927 | 18.1071 | -360.8881 | 17.5671 | -352.6967 | 18.7169 | -352.6967 | 16.8361
12:25 | 3900 | 38.9784 | 201.3385 | 448.3621 | 454.6126 | -16.9335 | -42.0997 | 10.1699 | 7.2379 | 1.3562 | -0.0921 | 2.856 | -1.4329 | 10.9137 | 3.7256 | 0.6119 | 0.6543 | 0.9597 | 0.7347 | -129.6306 | -1.1808 | 5.4496 | 1.6085 | -3.2668 | -1.5806 | 4.4008 |  | 2.8665 | -0.0166 | 4.011 | 3.3662 | 3.3387 | 1.0647 | 10.7556 | 14.2581 | 14.8676 | 11.0908 | 0.0001 | -0.0023 | 0.0002 | 0.0035 | 0.0012 | -0.0004 | 0.0139 | 0.0059 | -0.0165 | -360.1281 | 17.3802 | -360.4542 | 17.7005 | -360.8635 | 18.0947 | -360.8574 | 17.5137 | -352.6044 | 18.684 | -352.6629 | 16.8546
12:25 | 3901 | 38.9668 | 201.3346 | 448.3603 | 454.6371 | -16.9408 | -42.0526 | 10.1466 | 7.2534 | 1.3977 | -0.1391 | 2.7873 | -1.408 | 10.8706 | 3.7024 | 0.6103 | 0.6531 | 0.9584 | 0.7335 | -129.5076 | -0.9538 | 5.411 | 1.8509 | -3.2382 | -1.6281 | 4.4649 |  | 2.8163 | -0.1271 | 4.0099 | 3.3659 | 3.3436 | 1.0656 | 10.7349 | 14.208 | 14.8034 | 11.0652 | 0 | -0.003 | 0.0004 | 0.0037 | 0.0002 | -0.0004 | 0.0012 | -0.0125 | -0.0299 | -360.1527 | 17.3679 | -360.405 | 17.6594 | -360.765 | 18.1091 | -360.8758 | 17.5424 | -352.6598 | 18.6594 | -352.6013 | 16.8135
12:25 | 3902 | 38.9971 | 201.324 | 448.4824 | 454.6017 | -16.9708 | -42.1118 | 10.1084 | 7.1927 | 1.412 | -0.1302 | 2.7927 | -1.4033 | 10.8928 | 3.6738 | 0.6128 | 0.6581 | 0.961 | 0.7341 | -129.4997 | -1.0616 | 5.6034 | 1.8033 | -3.23 | -1.6308 | 4.421 |  | 2.7719 | -0.0761 | 4.0114 | 3.3657 | 3.343 | 1.0663 | 10.7452 | 14.236 | 14.8331 | 11.0923 | 0.0008 | -0.0029 | 0.0011 | 0.0038 | 0.0012 | -0.0009 | 0.0082 | 0.0017 | -0.0064 | -360.1927 | 17.4295 | -360.4819 | 17.6861 | -360.7989 | 18.0906 | -360.842 | 17.5527 | -352.6413 | 18.7087 | -352.6721 | 16.8135
12:25 | 3903 | 39.0327 | 201.4122 | 448.5051 | 454.5382 | -16.8458 | -42.1236 | 10.309 | 7.1855 | 1.4577 | -0.1436 | 2.736 | -1.4572 | 10.8277 | 3.7127 | 0.6117 | 0.6537 | 0.9602 | 0.734 | -129.5802 | -1.1148 | 5.4889 | 1.7208 | -3.3131 | -1.6243 | 4.4457 |  | 2.8637 | 0.0813 | 4.0131 | 3.3688 | 3.3394 | 1.0681 | 10.7383 | 14.2576 | 14.847 | 11.0631 | -0.0003 | -0.0028 | 0.0007 | 0.0036 | 0.0004 | -0.0007 | 0.0101 | -0.0078 | -0.0118 | -360.1988 | 17.4069 | -360.4942 | 17.719 | -360.885 | 18.1358 | -360.9035 | 17.5568 | -352.6413 | 18.7066 | -352.6937 | 16.8443
12:25 | 3904 | 39.1295 | 201.5189 | 448.5346 | 454.6146 | -16.8054 | -42.017 | 10.3056 | 7.1402 | 1.3888 | -0.1099 | 2.7114 | -1.3706 | 10.9063 | 3.7284 | 0.6128 | 0.6584 | 0.9611 | 0.734 | -129.5391 | -1.0131 | 5.4534 | 1.7482 | -3.3267 | -1.759 | 4.3721 |  | 2.8048 | -0.0461 | 4.0114 | 3.3651 | 3.3425 | 1.0668 | 10.7244 | 14.2555 | 14.8059 | 11.0833 | -0.0002 | -0.0024 | 0.0011 | 0.0043 | 0.0008 | -0.0009 | 0.0043 | -0.0091 | -0.0014 | -360.2111 | 17.4131 | -360.4912 | 17.682 | -360.802 | 18.105 | -360.9066 | 17.565 | -352.669 | 18.7087 | -352.6813 | 16.8258
12:25 | 3905 | 39.0302 | 201.3178 | 448.4841 | 454.5628 | -16.6874 | -41.9558 | 10.5511 | 7.1641 | 1.3869 | -0.2213 | 2.6948 | -1.3724 | 10.9105 | 3.7188 | 0.6114 | 0.6557 | 0.9642 | 0.7348 | -129.6305 | -1.2398 | 5.4872 | 1.7785 | -3.338 | -1.714 | 4.3388 |  | 2.8457 | -0.03 | 4.0099 | 3.3621 | 3.3418 | 1.0671 | 10.7337 | 14.2589 | 14.8147 | 11.058 | 0.0003 | -0.0029 | 0.0004 | 0.0036 | 0.0007 | -0.0007 | -0.0019 | -0.0158 | -0.0008 | -360.165 | 17.3966 | -360.4789 | 17.6964 | -360.8174 | 18.105 | -360.8204 | 17.5588 | -352.6444 | 18.6902 | -352.6967 | 16.8299
12:25 | 3906 | 39.0312 | 201.3843 | 448.5182 | 454.5998 | -16.691 | -42.018 | 10.517 | 7.0786 | 1.4287 | -0.1838 | 2.7662 | -1.3649 | 10.8974 | 3.7018 | 0.6115 | 0.6543 | 0.9631 | 0.7349 | -129.5964 | -1.11 | 5.4403 | 1.8014 | -3.3678 | -1.7228 | 4.4145 |  | 2.6836 | -0.0187 | 4.0096 | 3.3644 | 3.3434 | 1.0654 | 10.7255 | 14.2625 | 14.813 | 11.0959 | 0.0001 | -0.0029 | 0.0009 | 0.0037 | 0.001 | -0.0003 | 0.0222 | -0.0153 | -0.0132 | -360.1127 | 17.3782 | -360.4204 | 17.6615 | -360.7743 | 18.1235 | -360.8143 | 17.5896 | -352.6198 | 18.6737 | -352.5983 | 16.8032
12:25 | 3907 | 39.0958 | 201.3751 | 448.4924 | 454.5966 | -16.7437 | -42.0201 | 10.4078 | 7.1763 | 1.3523 | -0.2714 | 2.7901 | -1.4177 | 10.8809 | 3.6972 | 0.612 | 0.655 | 0.9621 | 0.7354 | -129.5279 | -1.0151 | 5.4788 | 1.7426 | -3.379 | -1.694 | 4.3832 |  | 2.7115 | 0.0171 | 4.0125 | 3.3655 | 3.3408 | 1.0665 | 10.736 | 14.2149 | 14.8453 | 11.0721 | -0.0002 | -0.0027 | 0.0003 | 0.0037 | 0.0009 | -0.0006 | 0.0102 | -0.0179 | -0.0138 | -360.1619 | 17.3987 | -360.4881 | 17.6759 | -360.7958 | 18.1235 | -360.8481 | 17.5794 | -352.6321 | 18.7004 | -352.629 | 16.8135
12:25 | 3908 | 39.0408 | 201.4405 | 448.4565 | 454.6392 | -16.8176 | -42.0487 | 10.414 | 7.1721 | 1.4545 | -0.2028 | 2.7276 | -1.4588 | 10.8937 | 3.6735 | 0.612 | 0.6579 | 0.965 | 0.734 | -129.5887 | -1.0881 | 5.5449 | 1.6643 | -3.4444 | -1.7328 | 4.3311 |  | 2.8197 | -0.0473 | 4.0108 | 3.3658 | 3.3392 | 1.066 | 10.7568 | 14.2472 | 14.8484 | 11.0873 | -0.0003 | -0.0027 | -0.0001 | 0.0031 | 0.0007 | -0.0003 | 0.019 | 0.0025 | -0.0321 | -360.1835 | 17.4048 | -360.4819 | 17.6944 | -360.8235 | 18.1296 | -360.8697 | 17.5958 | -352.6198 | 18.7004 | -352.6998 | 16.8299
12:25 | 3909 | 39.0386 | 201.4591 | 448.42 | 454.7038 | -16.8924 | -42.1813 | 10.3601 | 7.1691 | 1.4582 | -0.239 | 2.7114 | -1.4658 | 10.9313 | 3.6904 | 0.6133 | 0.6555 | 0.9603 | 0.7362 | -129.6185 | -1.0489 | 5.5357 | 1.7406 | -3.4055 | -1.6848 | 4.41 |  | 2.8045 | -0.0219 | 4.0107 | 3.3668 | 3.341 | 1.066 | 10.7487 | 14.2509 | 14.842 | 11.0786 | 0 | -0.0029 | 0.001 | 0.0039 | 0.0011 | -0.0008 | 0.0139 | -0.0125 | -0.0153 | -360.1896 | 17.4233 | -360.4881 | 17.6923 | -360.8481 | 18.1317 | -360.8912 | 17.5814 | -352.6875 | 18.7169 | -352.6875 | 16.8381
12:25 | 3910 | 38.9859 | 201.3318 | 448.3449 | 454.6728 | -16.9158 | -42.1305 | 10.2456 | 7.2635 | 1.558 | -0.1874 | 2.8171 | -1.4208 | 10.8717 | 3.7021 | 0.6122 | 0.6555 | 0.9621 | 0.7361 | -129.6414 | -1.0407 | 5.5411 | 1.7943 | -3.269 | -1.6357 | 4.3963 |  | 2.7296 | -0.097 | 4.0115 | 3.3647 | 3.3343 | 1.0666 | 10.721 | 14.2114 | 14.8296 | 11.0631 | 0 | -0.0033 | 0.0007 | 0.0038 | 0.0003 | -0.0004 | 0.0044 | -0.0011 | -0.0083 | -360.1896 | 17.409 | -360.4881 | 17.6841 | -360.8297 | 18.1132 | -360.8758 | 17.5527 | -352.6383 | 18.7128 | -352.6844 | 16.8423
12:25 | 3911 | 39.0828 | 201.3403 | 448.4696 | 454.6986 | -16.8441 | -42.1872 | 10.3115 | 7.2064 | 1.4793 | -0.18 | 2.8113 | -1.3565 | 10.8319 | 3.7559 | 0.6105 | 0.6574 | 0.9618 | 0.7343 | -129.5665 | -0.979 | 5.4445 | 1.7465 | -3.3074 | -1.7324 | 4.3876 |  | 2.6186 | -0.0886 | 4.0113 | 3.3634 | 3.3386 | 1.0673 | 10.7498 | 14.2349 | 14.8386 | 11.0966 | 0.0003 | -0.0026 | 0.0007 | 0.0038 | 0.0016 | 0 | 0.0022 | -0.0036 | -0.0177 | -360.1681 | 17.3761 | -360.4081 | 17.6574 | -360.7743 | 18.0927 | -360.842 | 17.5424 | -352.5983 | 18.6717 | -352.6383 | 16.8217
12:25 | 3912 | 39.0339 | 201.2572 | 448.4626 | 454.5975 | -16.8468 | -42.1806 | 10.3463 | 7.2478 | 1.4505 | -0.1403 | 2.7716 | -1.3223 | 10.922 | 3.8374 | 0.6122 | 0.6576 | 0.9619 | 0.736 | -129.5499 | -1.051 | 5.516 | 1.7945 | -3.2305 | -1.6398 | 4.4527 |  | 2.7368 | -0.0157 | 4.0124 | 3.3621 | 3.34 | 1.0663 | 10.7602 | 14.2337 | 14.8257 | 11.0955 | -0.0004 | -0.0023 | 0.0007 | 0.0036 | 0.0008 | -0.0001 | 0.0091 | -0.013 | -0.0117 | -360.1835 | 17.3987 | -360.4235 | 17.641 | -360.7743 | 18.0804 | -360.8512 | 17.5527 | -352.6383 | 18.6943 | -352.6413 | 16.8012
12:25 | 3913 | 39.0661 | 201.2632 | 448.4319 | 454.6643 | -16.8657 | -42.145 | 10.3368 | 7.2594 | 1.5168 | -0.1457 | 2.7438 | -1.3251 | 10.8997 | 3.7362 | 0.6115 | 0.655 | 0.9615 | 0.7342 | -129.4994 | -0.9734 | 5.54 | 1.8538 | -3.3469 | -1.6666 | 4.3499 |  | 2.6881 | 0.0215 | 4.013 | 3.3635 | 3.3384 | 1.0675 | 10.7533 | 14.2788 | 14.8938 | 11.0829 | -0.0005 | -0.0032 | 0.0005 | 0.0037 | 0.0007 | -0.0008 | 0.0225 | -0.0212 | -0.0058 | -360.1404 | 17.3987 | -360.4696 | 17.6533 | -360.805 | 18.0845 | -360.8327 | 17.526 | -352.6352 | 18.6799 | -352.6506 | 16.8258
12:25 | 3914 | 39.0007 | 201.2096 | 448.4462 | 454.6151 | -16.9105 | -42.2283 | 10.3115 | 7.2539 | 1.4164 | -0.1416 | 2.7778 | -1.4015 | 10.8098 | 3.7163 | 0.6109 | 0.6561 | 0.9643 | 0.7356 | -129.4447 | -0.9571 | 5.6232 | 1.824 | -3.35 | -1.5903 | 4.3552 |  | 2.6957 | -0.0338 | 4.0134 | 3.3662 | 3.3395 | 1.0662 | 10.7462 | 14.2896 | 14.8782 | 11.1096 | 0.0002 | -0.003 | 0.0008 | 0.004 | 0.0009 | -0.0003 | -0.0002 | -0.01 | -0.0186 | -360.1835 | 17.4007 | -360.4604 | 17.6718 | -360.8697 | 18.1276 | -360.8789 | 17.5445 | -352.6383 | 18.6984 | -352.6444 | 16.8238
12:25 | 3915 | 38.9751 | 201.2268 | 448.4176 | 454.5877 | -16.8521 | -42.13 | 10.3591 | 7.3269 | 1.4016 | -0.179 | 2.828 | -1.4201 | 10.8277 | 3.744 | 0.6111 | 0.6574 | 0.9637 | 0.7346 | -129.5042 | -1.0217 | 5.6199 | 1.8269 | -3.3145 | -1.6338 | 4.3169 |  | 2.7323 | -0.0195 | 4.0134 | 3.3661 | 3.3388 | 1.0669 | 10.7649 | 14.2613 | 14.8638 | 11.1121 | -0.0004 | -0.0029 | 0.0003 | 0.0039 | 0.001 | -0.0007 | 0.0103 | -0.005 | -0.0245 | -360.2235 | 17.4172 | -360.4666 | 17.6451 | -360.805 | 18.1194 | -360.8912 | 17.5876 | -352.6998 | 18.7128 | -352.6383 | 16.8094
12:25 | 3916 | 38.9659 | 201.3085 | 448.3562 | 454.6201 | -16.8936 | -42.0848 | 10.3281 | 7.312 | 1.4933 | -0.2104 | 2.7189 | -1.321 | 10.8935 | 3.7075 | 0.6101 | 0.656 | 0.9626 | 0.7339 | -129.5533 | -1.1118 | 5.5851 | 1.9799 | -3.2564 | -1.5423 | 4.4363 |  | 2.6815 | -0.0762 | 4.0122 | 3.3688 | 3.3395 | 1.067 | 10.7521 | 14.2547 | 14.8471 | 11.0814 | -0.0001 | -0.0025 | 0.0009 | 0.004 | 0.0009 | -0.0004 | 0.0185 | -0.0063 | 0.0004 | -360.2111 | 17.4131 | -360.5281 | 17.6882 | -360.882 | 18.1091 | -360.845 | 17.5342 | -352.6783 | 18.7107 | -352.7183 | 16.8525
12:25 | 3917 | 39.1045 | 201.2733 | 448.3887 | 454.707 | -16.7775 | -42.05 | 10.3794 | 7.2768 | 1.372 | -0.1453 | 2.8031 | -1.3944 | 10.9097 | 3.6988 | 0.6109 | 0.6561 | 0.9624 | 0.7345 | -129.5067 | -1.1279 | 5.5571 | 1.9266 | -3.2749 | -1.5878 | 4.4345 |  | 2.7415 | -0.1336 | 4.0109 | 3.3619 | 3.3387 | 1.066 | 10.7279 | 14.2705 | 14.8321 | 11.0695 | -0.0002 | -0.0031 | 0.001 | 0.0041 | 0.0004 | -0.0008 | -0.0033 | -0.0097 | -0.0095 | -360.1681 | 17.3679 | -360.4142 | 17.6451 | -360.8297 | 18.1337 | -360.9158 | 17.5465 | -352.6321 | 18.6655 | -352.6013 | 16.8156
12:25 | 3918 | 39.021 | 201.2909 | 448.3835 | 454.6489 | -16.8236 | -42.0801 | 10.3094 | 7.3332 | 1.4344 | -0.1382 | 2.7704 | -1.2484 | 10.9345 | 3.7809 | 0.611 | 0.6574 | 0.9638 | 0.7368 | -129.4865 | -1.0951 | 5.5067 | 1.8862 | -3.2095 | -1.5508 | 4.4356 |  | 2.7387 | -0.0744 | 4.0133 | 3.3678 | 3.3419 | 1.0672 | 10.7325 | 14.2693 | 14.8307 | 11.08 | 0.0001 | -0.0032 | 0.0008 | 0.0036 | 0.0008 | -0.0005 | 0.0041 | -0.0067 | -0.007 | -360.1865 | 17.3987 | -360.4019 | 17.6266 | -360.7466 | 18.0845 | -360.8604 | 17.5506 | -352.6198 | 18.6984 | -352.6167 | 16.7827
12:25 | 3919 | 39.1281 | 201.2671 | 448.3632 | 454.7318 | -16.862 | -42.0178 | 10.4593 | 7.356 | 1.4636 | -0.1568 | 2.7806 | -1.3266 | 10.975 | 3.7343 | 0.6119 | 0.6558 | 0.9599 | 0.7352 | -129.5333 | -1.0584 | 5.5239 | 1.8634 | -3.1434 | -1.5644 | 4.4542 |  | 2.7551 | -0.0701 | 4.012 | 3.3674 | 3.3393 | 1.067 | 10.7232 | 14.2314 | 14.8113 | 11.0645 | 0.0004 | -0.003 | 0.0009 | 0.0036 | 0.0007 | -0.0005 | 0.0175 | 0.0099 | 0.0106 | -360.1034 | 17.4069 | -360.4881 | 17.6718 | -360.8327 | 18.0947 | -360.7958 | 17.5137 | -352.6106 | 18.6902 | -352.669 | 16.8361
12:25 | 3920 | 39.1121 | 201.3231 | 448.4118 | 454.7189 | -16.8317 | -41.9341 | 10.3822 | 7.401 | 1.4419 | -0.1621 | 2.7817 | -1.3578 | 10.9225 | 3.7266 | 0.611 | 0.6605 | 0.9598 | 0.7354 | -129.5449 | -1.0443 | 5.5588 | 1.9174 | -3.064 | -1.4345 | 4.53 |  | 2.8391 | -0.0413 | 4.0124 | 3.3642 | 3.3378 | 1.067 | 10.7221 | 14.2474 | 14.8436 | 11.0811 | -0.0003 | -0.0028 | 0.0006 | 0.0039 | 0.0008 | -0.0004 | 0.0012 | 0.0031 | 0.0022 | -360.1404 | 17.3761 | -360.4204 | 17.6615 | -360.8327 | 18.1399 | -360.9158 | 17.5424 | -352.6413 | 18.6655 | -352.6321 | 16.8094
12:25 | 3921 | 39.1577 | 201.3117 | 448.3719 | 454.6728 | -16.8291 | -41.9972 | 10.3141 | 7.3565 | 1.4016 | -0.2082 | 2.6519 | -1.2993 | 10.9557 | 3.7439 | 0.6126 | 0.6577 | 0.9622 | 0.7369 | -129.6582 | -1.1061 | 5.5066 | 1.8933 | -3.1766 | -1.5134 | 4.486 |  | 2.7993 | -0.0798 | 4.0114 | 3.3654 | 3.3444 | 1.0671 | 10.7578 | 14.2723 | 14.8724 | 11.0749 | -0.0002 | -0.0025 | 0.0006 | 0.0042 | 0.0009 | 0.0001 | 0.0077 | -0.0044 | -0.0071 | -360.2327 | 17.4213 | -360.4666 | 17.6533 | -360.7743 | 18.1194 | -360.9035 | 17.5753 | -352.6967 | 18.7148 | -352.6906 | 16.8094
12:25 | 3922 | 39.046 | 201.3302 | 448.4495 | 454.6587 | -16.853 | -42.1053 | 10.2555 | 7.367 | 1.4874 | -0.1215 | 2.7205 | -1.4336 | 10.8519 | 3.5817 | 0.6112 | 0.6565 | 0.9586 | 0.7351 | -129.6148 | -1.0624 | 5.4743 | 1.859 | -3.1529 | -1.5204 | 4.4045 |  | 2.8184 | -0.0845 | 4.0112 | 3.3643 | 3.3372 | 1.0655 | 10.7545 | 14.2741 | 14.842 | 11.0786 | 0.0002 | -0.0029 | 0.0007 | 0.004 | 0.0007 | -0.0007 | 0.0048 | -0.0053 | -0.0205 | -360.2142 | 17.4233 | -360.5312 | 17.7046 | -360.8789 | 18.1173 | -360.885 | 17.5342 | -352.6444 | 18.723 | -352.7337 | 16.8587
12:25 | 3923 | 39.0619 | 201.2814 | 448.3892 | 454.6724 | -16.8955 | -42.0304 | 10.2274 | 7.2221 | 1.4676 | -0.1296 | 2.6912 | -1.333 | 10.8528 | 3.6916 | 0.6117 | 0.6559 | 0.9593 | 0.7347 | -129.5621 | -0.9233 | 5.5763 | 1.8686 | -3.1564 | -1.5316 | 4.4825 |  | 2.8733 | -0.0796 | 4.0121 | 3.3643 | 3.3389 | 1.0675 | 10.7325 | 14.2174 | 14.8202 | 11.0508 | 0.0001 | -0.0027 | 0 | 0.0038 | 0.001 | 0.0006 | -0.0033 | 0.0059 | -0.0089 | -360.1681 | 17.374 | -360.4266 | 17.6677 | -360.8389 | 18.1502 | -360.9066 | 17.5424 | -352.6444 | 18.6799 | -352.6352 | 16.8258
12:25 | 3924 | 39.0473 | 201.4313 | 448.4838 | 454.8363 | -16.8983 | -41.984 | 10.2258 | 7.1746 | 1.4802 | -0.0694 | 2.6743 | -1.3764 | 10.9135 | 3.7105 | 0.6111 | 0.6565 | 0.9635 | 0.7349 | -129.6687 | -1.1523 | 5.4018 | 1.9089 | -3.0886 | -1.5766 | 4.5526 |  | 2.7948 | -0.0932 | 4.0101 | 3.3634 | 3.3425 | 1.0661 | 10.759 | 14.2616 | 14.8369 | 11.071 | -0.0001 | -0.0027 | 0.0007 | 0.0041 | 0.0011 | -0.0004 | 0.0113 | 0.0052 | -0.0113 | -360.1711 | 17.3884 | -360.4142 | 17.6348 | -360.7558 | 18.0968 | -360.8574 | 17.5445 | -352.6383 | 18.6984 | -352.6475 | 16.8074
12:25 | 3925 | 39.0695 | 201.3804 | 448.4314 | 454.7637 | -16.8948 | -42.096 | 10.1903 | 7.2309 | 1.5203 | -0.1878 | 2.6953 | -1.304 | 10.9732 | 3.7381 | 0.6121 | 0.6576 | 0.9598 | 0.7342 | -129.5549 | -1.0478 | 5.4473 | 1.8489 | -3.1463 | -1.5271 | 4.4186 |  | 2.8873 | -0.1415 | 4.0128 | 3.3649 | 3.3395 | 1.0673 | 10.7153 | 14.2459 | 14.7939 | 11.075 | -0.0003 | -0.0027 | 0.0009 | 0.004 | 0.0003 | -0.0004 | 0.0066 | -0.0106 | -0.0143 | -360.125 | 17.3946 | -360.4666 | 17.6738 | -360.8297 | 18.0824 | -360.802 | 17.5116 | -352.5921 | 18.6943 | -352.6875 | 16.8361
12:25 | 3926 | 39.1066 | 201.4505 | 448.4742 | 454.8186 | -16.9626 | -42.1149 | 10.2929 | 7.2054 | 1.5579 | -0.2019 | 2.6777 | -1.3467 | 10.9603 | 3.7422 | 0.6118 | 0.6581 | 0.9609 | 0.7354 | -129.5315 | -1.0583 | 5.4997 | 1.8462 | -3.2224 | -1.5507 | 4.4683 |  | 2.8688 | -0.1599 | 4.0109 | 3.3636 | 3.3388 | 1.0655 | 10.7164 | 14.2415 | 14.8194 | 11.0641 | 0.0003 | -0.0027 | 0.0008 | 0.0039 | 0.0009 | -0.0004 | 0.0027 | -0.0047 | -0.0129 | -360.1465 | 17.3966 | -360.4296 | 17.6636 | -360.842 | 18.1317 | -360.8512 | 17.5321 | -352.6198 | 18.6758 | -352.6198 | 16.8156
12:25 | 3927 | 39.0991 | 201.3906 | 448.4815 | 454.8055 | -16.9387 | -42.0482 | 10.2978 | 7.2096 | 1.625 | -0.1081 | 2.708 | -1.3866 | 10.9913 | 3.6593 | 0.6127 | 0.656 | 0.9584 | 0.7356 | -129.4451 | -1.0863 | 5.5905 | 1.8437 | -3.1105 | -1.5634 | 4.4742 |  | 2.7791 | -0.1001 | 4.0113 | 3.3616 | 3.3381 | 1.0656 | 10.7348 | 14.237 | 14.8219 | 11.0302 | 0 | -0.003 | 0.0007 | 0.0038 | 0.0008 | -0.0005 | 0.016 | -0.0123 | -0.0116 | -360.1804 | 17.4295 | -360.4973 | 17.6615 | -360.805 | 18.1255 | -360.8758 | 17.5588 | -352.6413 | 18.7148 | -352.6813 | 16.8197
12:25 | 3928 | 39.1773 | 201.4027 | 448.5334 | 454.728 | -16.8069 | -41.8333 | 10.4132 | 7.2198 | 1.7533 | 0.0181 | 2.7392 | -1.3083 | 10.9076 | 3.7044 | 0.6114 | 0.6583 | 0.9573 | 0.7337 | -129.5214 | -1.1562 | 5.4597 | 1.8554 | -3.2219 | -1.5953 | 4.4576 |  | 2.8003 | -0.11 | 4.0124 | 3.3633 | 3.3402 | 1.0667 | 10.7488 | 14.2217 | 14.8456 | 11.1024 | -0.0002 | -0.003 | 0.0003 | 0.0035 | 0.0003 | -0.0008 | 0.0189 | -0.0108 | -0.0189 | -360.165 | 17.409 | -360.4758 | 17.6841 | -360.845 | 18.1194 | -360.8789 | 17.5465 | -352.6629 | 18.7066 | -352.6875 | 16.8443
12:25 | 3929 | 39.1597 | 201.4587 | 448.5737 | 454.7333 | -16.7996 | -41.8478 | 10.3679 | 7.1886 | 1.6811 | -0.0491 | 2.6896 | -1.3197 | 10.9816 | 3.6878 | 0.6114 | 0.6592 | 0.9602 | 0.7344 | -129.4825 | -1.0816 | 5.5327 | 1.8334 | -3.2226 | -1.5793 | 4.5041 |  | 2.7482 | -0.1508 | 4.0132 | 3.3666 | 3.343 | 1.0663 | 10.729 | 14.2428 | 14.845 | 11.0764 | -0.0005 | -0.0027 | 0.0005 | 0.0036 | 0.0009 | -0.0011 | -0.0037 | -0.0097 | 0.008 | -360.1342 | 17.3905 | -360.4358 | 17.6471 | -360.7773 | 18.1153 | -360.8604 | 17.5342 | -352.6383 | 18.6902 | -352.666 | 16.8217
12:25 | 3930 | 39.1592 | 201.4393 | 448.5576 | 454.7926 | -16.7344 | -41.9215 | 10.5745 | 7.2121 | 1.7486 | 0.1561 | 2.7527 | -1.3291 | 10.8778 | 3.6911 | 0.6106 | 0.6583 | 0.9607 | 0.7341 | -129.5614 | -1.0716 | 5.5687 | 1.8572 | -3.1871 | -1.6102 | 4.4901 |  | 2.7277 | -0.1633 | 4.0124 | 3.3676 | 3.3407 | 1.0669 | 10.7521 | 14.2718 | 14.8634 | 11.0934 | -0.0002 | -0.0028 | 0.0005 | 0.0037 | 0.0004 | -0.0007 | -0.0017 | -0.0037 | -0.0208 | -360.1435 | 17.3966 | -360.4789 | 17.6369 | -360.7681 | 18.1029 | -360.8297 | 17.5198 | -352.5952 | 18.682 | -352.626 | 16.8217
12:25 | 3931 | 39.1061 | 201.463 | 448.4768 | 454.7662 | -16.8121 | -41.9952 | 10.4216 | 7.2809 | 1.7041 | 0.1139 | 2.7354 | -1.242 | 10.9885 | 3.758 | 0.6129 | 0.6576 | 0.9621 | 0.7345 | -129.5642 | -1.0569 | 5.4357 | 1.7613 | -3.1765 | -1.6381 | 4.4663 |  | 2.7873 | -0.1273 | 4.0124 | 3.3661 | 3.3391 | 1.0674 | 10.7405 | 14.2545 | 14.8345 | 11.076 | 0.0003 | -0.0029 | 0.0006 | 0.004 | 0.001 | -0.0003 | 0.0101 | -0.011 | -0.0023 | -360.1958 | 17.3925 | -360.4758 | 17.68 | -360.8204 | 18.1276 | -360.8697 | 17.5301 | -352.586 | 18.6861 | -352.6752 | 16.8402
12:25 | 3932 | 39.1973 | 201.492 | 448.5822 | 454.8048 | -16.8925 | -42.1346 | 10.3653 | 7.2785 | 1.678 | -0.038 | 2.7182 | -1.2463 | 11.0105 | 3.7817 | 0.6123 | 0.6612 | 0.965 | 0.7362 | -129.4878 | -1.0291 | 5.5241 | 1.9012 | -3.1364 | -1.5036 | 4.535 |  | 2.7017 | -0.112 | 4.0134 | 3.3652 | 3.3379 | 1.0669 | 10.752 | 14.2895 | 14.8482 | 11.1099 | -0.0006 | -0.0031 | 0.0006 | 0.0039 | 0.0009 | -0.0001 | 0.0145 | -0.003 | 0.0039 | -360.1958 | 17.4131 | -360.4819 | 17.6779 | -360.8112 | 18.1399 | -360.922 | 17.5609 | -352.666 | 18.7066 | -352.6567 | 16.8381
12:25 | 3933 | 39.1629 | 201.452 | 448.4879 | 454.8396 | -16.9588 | -42.012 | 10.3536 | 7.2216 | 1.6414 | -0.0604 | 2.7187 | -1.234 | 10.9561 | 3.7925 | 0.6111 | 0.6577 | 0.9586 | 0.7347 | -129.4646 | -0.984 | 5.4527 | 1.8871 | -3.1688 | -1.5814 | 4.498 |  | 2.7796 | -0.1358 | 4.0119 | 3.3638 | 3.3381 | 1.0673 | 10.7637 | 14.2776 | 14.8577 | 11.0818 | 0 | -0.0025 | 0.0007 | 0.0037 | 0.0011 | -0.0005 | 0.0132 | 0.0059 | 0.0021 | -360.1988 | 17.4336 | -360.485 | 17.6697 | -360.8266 | 18.1112 | -360.8727 | 17.5465 | -352.7029 | 18.7456 | -352.7152 | 16.8443
12:25 | 3934 | 39.1984 | 201.4535 | 448.5348 | 454.8338 | -16.9181 | -41.9949 | 10.3725 | 7.2494 | 1.6576 | -0.1083 | 2.7405 | -1.303 | 10.9301 | 3.7393 | 0.6118 | 0.6587 | 0.9614 | 0.7345 | -129.463 | -1.0252 | 5.4906 | 2.0047 | -3.0534 | -1.4103 | 4.5843 |  | 2.875 | -0.0615 | 4.0137 | 3.3665 | 3.34 | 1.0688 | 10.7383 | 14.2346 | 14.8365 | 11.0742 | 0 | -0.0031 | 0.0008 | 0.004 | 0.0006 | 0 | 0.0027 | -0.0035 | -0.0059 | -360.1004 | 17.3843 | -360.4481 | 17.6615 | -360.8235 | 18.1255 | -360.842 | 17.5157 | -352.6013 | 18.6799 | -352.6537 | 16.8505
12:25 | 3935 | 39.1451 | 201.378 | 448.4662 | 454.7603 | -16.85 | -42.0114 | 10.4632 | 7.2252 | 1.5699 | -0.0813 | 2.8141 | -1.3776 | 10.9595 | 3.7123 | 0.6123 | 0.6609 | 0.9605 | 0.7353 | -129.4787 | -0.9115 | 5.5857 | 1.9324 | -3.016 | -1.5193 | 4.5357 |  | 2.8668 | -0.0605 | 4.0116 | 3.3676 | 3.3382 | 1.0668 | 10.7326 | 14.2287 | 14.8123 | 11.0688 | 0 | -0.0032 | 0.0006 | 0.0032 | 0.001 | -0.0007 | 0.0064 | -0.0129 | -0.0205 | -360.1588 | 17.3823 | -360.4173 | 17.6245 | -360.7589 | 18.105 | -360.8697 | 17.5609 | -352.6413 | 18.6902 | -352.6136 | 16.8053
12:25 | 3936 | 39.186 | 201.3988 | 448.5512 | 454.7538 | -16.8373 | -42.1196 | 10.4327 | 7.2446 | 1.5165 | 0.0401 | 2.7407 | -1.3139 | 10.9189 | 3.7456 | 0.6113 | 0.6566 | 0.9614 | 0.7364 | -129.4917 | -1.0287 | 5.4444 | 1.7162 | -3.1329 | -1.4897 | 4.4513 |  | 2.9046 | -0.0185 | 4.0109 | 3.3678 | 3.339 | 1.0677 | 10.7326 | 14.2287 | 14.7949 | 11.0804 | -0.0003 | -0.0035 | 0.0003 | 0.0035 | 0.0004 | -0.0004 | 0.0178 | -0.0035 | -0.012 | -360.1988 | 17.4274 | -360.4973 | 17.6574 | -360.8235 | 18.0886 | -360.8266 | 17.5342 | -352.6321 | 18.7148 | -352.6752 | 16.8402
12:25 | 3937 | 39.1706 | 201.4479 | 448.5696 | 454.8274 | -16.8346 | -42.1564 | 10.4982 | 7.2605 | 1.5409 | -0.1188 | 2.7703 | -1.3351 | 10.882 | 3.7146 | 0.6124 | 0.6574 | 0.9621 | 0.7358 | -129.5775 | -0.9018 | 5.4555 | 1.7932 | -3.1618 | -1.4984 | 4.4831 |  | 2.8031 | -0.116 | 4.0118 | 3.3661 | 3.3384 | 1.0667 | 10.7302 | 14.2555 | 14.829 | 11.0601 | -0.0005 | -0.0028 | 0.0011 | 0.0039 | 0.0007 | -0.0008 | 0.0098 | -0.0072 | -0.0275 | -360.1835 | 17.3925 | -360.4573 | 17.6841 | -360.885 | 18.1522 | -360.9189 | 17.5486 | -352.6352 | 18.6881 | -352.6537 | 16.8648
12:25 | 3938 | 39.2587 | 201.4058 | 448.4806 | 454.833 | -16.7779 | -42.0029 | 10.3803 | 7.2398 | 1.4741 | -0.0021 | 2.7216 | -1.3708 | 10.9009 | 3.6708 | 0.6117 | 0.6566 | 0.9642 | 0.7365 | -129.5146 | -1.1409 | 5.4735 | 1.8915 | -3.0686 | -1.4291 | 4.4459 |  | 2.8653 | -0.0922 | 4.0109 | 3.369 | 3.3369 | 1.0672 | 10.7659 | 14.2686 | 14.8499 | 11.0894 | 0.0001 | -0.0025 | 0.0008 | 0.0042 | 0.0009 | -0.0002 | 0.0058 | -0.007 | -0.0175 | -360.2204 | 17.4151 | -360.4573 | 17.6389 | -360.7804 | 18.1173 | -360.9097 | 17.5835 | -352.706 | 18.7271 | -352.669 | 16.834
12:25 | 3939 | 39.2356 | 201.4419 | 448.5277 | 454.802 | -16.8601 | -42.0214 | 10.2022 | 7.2478 | 1.4479 | -0.0576 | 2.7931 | -1.2924 | 10.9685 | 3.714 | 0.6118 | 0.6531 | 0.9582 | 0.7346 | -129.4932 | -1.0614 | 5.4961 | 1.8409 | -3.1438 | -1.3862 | 4.4808 |  | 2.8127 | -0.1371 | 4.0114 | 3.3645 | 3.3351 | 1.0665 | 10.7556 | 14.2696 | 14.8386 | 11.0793 | 0.0001 | -0.0029 | 0.0008 | 0.0042 | 0.001 | -0.0002 | -0.0028 | 0.002 | -0.0219 | -360.1311 | 17.3987 | -360.485 | 17.6656 | -360.8358 | 18.0988 | -360.805 | 17.5075 | -352.6383 | 18.7087 | -352.6875 | 16.8628
12:25 | 3940 | 39.1882 | 201.3976 | 448.419 | 454.7029 | -16.9373 | -42.0085 | 10.2775 | 7.217 | 1.4808 | -0.0753 | 2.7073 | -1.3969 | 10.8989 | 3.6947 | 0.6125 | 0.6566 | 0.959 | 0.734 | -129.5585 | -1.1547 | 5.4802 | 1.882 | -3.1887 | -1.5193 | 4.4223 |  | 2.7806 | -0.1439 | 4.0116 | 3.3658 | 3.3428 | 1.0668 | 10.752 | 14.2779 | 14.8482 | 11.0522 | 0.0001 | -0.0029 | 0.0012 | 0.004 | 0.0009 | -0.0006 | 0.0226 | -0.0017 | 0.0208 | -360.1835 | 17.3556 | -360.3896 | 17.6307 | -360.7989 | 18.142 | -360.9097 | 17.5363 | -352.6198 | 18.6635 | -352.5921 | 16.8258
12:25 | 3941 | 39.1415 | 201.4842 | 448.3833 | 454.7885 | -16.9457 | -42.1782 | 10.3143 | 7.2783 | 1.4274 | -0.129 | 2.7419 | -1.4246 | 10.9843 | 3.6975 | 0.6123 | 0.658 | 0.9624 | 0.7347 | -129.5272 | -1.0663 | 5.5555 | 1.69 | -3.18 | -1.5163 | 4.3207 |  | 2.7978 | -0.1471 | 4.0101 | 3.366 | 3.3376 | 1.0669 | 10.7681 | 14.2828 | 14.8837 | 11.1197 | -0.0001 | -0.0024 | 0.0004 | 0.0035 | 0.0007 | -0.0002 | 0.0157 | -0.0018 | -0.0026 | -360.2358 | 17.4213 | -360.4604 | 17.643 | -360.762 | 18.1091 | -360.8604 | 17.565 | -352.6844 | 18.7128 | -352.6475 | 16.8238
12:25 | 3942 | 39.2396 | 201.4729 | 448.3603 | 454.7634 | -16.9356 | -42.0579 | 10.2661 | 7.2635 | 1.3963 | -0.1538 | 2.7676 | -1.3721 | 10.9595 | 3.6766 | 0.6121 | 0.6559 | 0.9594 | 0.7353 | -129.5355 | -1.1161 | 5.514 | 1.6309 | -3.1682 | -1.5483 | 4.3706 |  | 2.8245 | -0.078 | 4.0119 | 3.3706 | 3.3409 | 1.0675 | 10.7209 | 14.2637 | 14.8376 | 11.097 | -0.0001 | -0.0027 | 0.0011 | 0.0041 | 0.0013 | -0.0002 | 0.0157 | -0.0082 | -0.0083 | -360.1804 | 17.4254 | -360.5219 | 17.7046 | -360.882 | 18.1296 | -360.8389 | 17.5383 | -352.629 | 18.7189 | -352.7398 | 16.8813
12:25 | 3943 | 39.2128 | 201.4266 | 448.514 | 454.7638 | -16.9799 | -42.0443 | 10.182 | 7.3235 | 1.5047 | -0.0911 | 2.7687 | -1.3447 | 10.9148 | 3.7779 | 0.6116 | 0.6548 | 0.9597 | 0.7355 | -129.4811 | -1.0776 | 5.5054 | 1.6999 | -3.1351 | -1.4683 | 4.4765 |  | 2.8643 | 0.0365 | 4.0121 | 3.368 | 3.3365 | 1.0676 | 10.7174 | 14.2544 | 14.7987 | 11.0648 | 0.0006 | -0.0027 | 0.0008 | 0.0037 | 0.0005 | -0.0004 | 0.0226 | 0.01 | 0.0075 | -360.1404 | 17.374 | -360.4173 | 17.643 | -360.8174 | 18.144 | -360.9281 | 17.5506 | -352.6537 | 18.6779 | -352.626 | 16.8423
12:25 | 3944 | 39.2593 | 201.4288 | 448.5938 | 454.7492 | -16.9622 | -42.0749 | 10.0903 | 7.289 | 1.3938 | -0.1612 | 2.8479 | -1.2892 | 10.9735 | 3.8037 | 0.6127 | 0.656 | 0.9606 | 0.7356 | -129.527 | -1.0988 | 5.4614 | 1.5862 | -3.1894 | -1.5237 | 4.4332 |  | 2.8068 | -0.0362 | 4.0116 | 3.3632 | 3.3394 | 1.0685 | 10.7107 | 14.2121 | 14.8047 | 11.0595 | -0.0001 | -0.0032 | 0.0006 | 0.0037 | 0.0009 | -0.0009 | 0.0086 | 0.0005 | -0.015 | -360.1742 | 17.4048 | -360.445 | 17.6245 | -360.7773 | 18.0886 | -360.8112 | 17.5383 | -352.6444 | 18.7045 | -352.6444 | 16.8258
12:25 | 3945 | 39.2386 | 201.3634 | 448.5067 | 454.767 | -17.042 | -42.126 | 10.1837 | 7.241 | 1.4228 | -0.2206 | 2.6995 | -1.2575 | 10.9512 | 3.7892 | 0.6121 | 0.6552 | 0.9603 | 0.7355 | -129.4993 | -1.0135 | 5.4471 | 1.5992 | -3.2427 | -1.6336 | 4.3859 |  | 2.8522 | -0.171 | 4.0119 | 3.3652 | 3.3417 | 1.0687 | 10.7326 | 14.2287 | 14.8239 | 11.0457 | 0.0001 | -0.0024 | 0.0008 | 0.0038 | 0.0002 | -0.0005 | 0.0161 | 0.0044 | 0.0018 | -360.1311 | 17.3802 | -360.4512 | 17.6738 | -360.8235 | 18.105 | -360.8389 | 17.5034 | -352.586 | 18.6861 | -352.666 | 16.8607
12:25 | 3946 | 39.294 | 201.3814 | 448.522 | 454.7403 | -16.9069 | -42.0854 | 10.2725 | 7.3509 | 1.5638 | -0.0981 | 2.7575 | -1.3723 | 10.8399 | 3.7553 | 0.6125 | 0.6547 | 0.9643 | 0.7348 | -129.4911 | -1.1333 | 5.3966 | 1.6696 | -3.2078 | -1.6445 | 4.4183 |  | 2.7914 | -0.0915 | 4.0112 | 3.3614 | 3.3364 | 1.0676 | 10.737 | 14.2512 | 14.8152 | 11.0778 | -0.0001 | -0.0027 | 0.001 | 0.0043 | 0.0013 | -0.0004 | 0.0153 | -0.0077 | 0.0053 | -360.1404 | 17.3823 | -360.4112 | 17.6471 | -360.8327 | 18.1194 | -360.882 | 17.5465 | -352.629 | 18.6737 | -352.6136 | 16.834
12:25 | 3947 | 39.3082 | 201.3987 | 448.5342 | 454.7537 | -16.9584 | -42.0992 | 10.2402 | 7.2903 | 1.4635 | -0.0867 | 2.7257 | -1.2702 | 10.9347 | 3.8067 | 0.611 | 0.6517 | 0.9606 | 0.7341 | -129.5529 | -1.1963 | 5.4063 | 1.6823 | -3.3035 | -1.5604 | 4.3594 |  | 2.8049 | -0.0593 | 4.0116 | 3.3663 | 3.3377 | 1.0686 | 10.7613 | 14.2407 | 14.8618 | 11.1082 | 0.0005 | -0.0025 | 0.0008 | 0.0043 | 0.0006 | -0.0005 | 0.0099 | -0.0104 | -0.01 | -360.2265 | 17.4377 | -360.5219 | 17.6594 | -360.8389 | 18.1173 | -360.8543 | 17.5527 | -352.6937 | 18.7312 | -352.6967 | 16.832
12:26 | 3948 | 39.242 | 201.4219 | 448.6115 | 454.6748 | -16.9339 | -42.0678 | 10.2325 | 7.4221 | 1.4473 | -0.0839 | 2.7304 | -1.3373 | 10.9195 | 3.7225 | 0.6103 | 0.6554 | 0.9637 | 0.7355 | -129.5011 | -1.0391 | 5.5309 | 1.7699 | -3.2957 | -1.679 | 4.4058 |  | 2.7394 | -0.0723 | 4.0105 | 3.3649 | 3.3396 | 1.0685 | 10.7682 | 14.2767 | 14.8816 | 11.1089 | 0.0001 | -0.0031 | 0.001 | 0.004 | 0.0007 | -0.0006 | 0.0096 | -0.0133 | -0.0189 | -360.1465 | 17.4192 | -360.4942 | 17.6841 | -360.8512 | 18.1399 | -360.885 | 17.5404 | -352.6352 | 18.7087 | -352.6844 | 16.8648
12:26 | 3949 | 39.2598 | 201.4539 | 448.5331 | 454.7333 | -16.9638 | -42.2521 | 10.1419 | 7.402 | 1.3791 | 0.0064 | 2.6902 | -1.2731 | 10.956 | 3.7204 | 0.6128 | 0.656 | 0.9636 | 0.7334 | -129.5406 | -1.009 | 5.4855 | 1.6811 | -3.3398 | -1.5894 | 4.4599 |  | 2.7574 | -0.0587 | 4.0108 | 3.3642 | 3.3381 | 1.0677 | 10.7856 | 14.2477 | 14.8689 | 11.0746 | -0.0004 | -0.0027 | 0.0005 | 0.0035 | 0.0004 | -0.0005 | 0.0059 | -0.0109 | -0.0116 | -360.1742 | 17.4048 | -360.4635 | 17.6492 | -360.8235 | 18.1276 | -360.9097 | 17.5712 | -352.6937 | 18.7107 | -352.669 | 16.832
12:26 | 3950 | 39.2571 | 201.418 | 448.608 | 454.7756 | -16.985 | -42.3091 | 10.2145 | 7.2883 | 1.3099 | 0.1205 | 2.6455 | -1.3872 | 10.9576 | 3.791 | 0.6123 | 0.6588 | 0.959 | 0.7354 | -129.5596 | -1.0438 | 5.5377 | 1.6008 | -3.263 | -1.5639 | 4.4261 |  | 2.7389 | -0.0132 | 4.0119 | 3.3652 | 3.3419 | 1.0675 | 10.7488 | 14.2678 | 14.7925 | 11.0508 | -0.0003 | -0.0025 | 0.0009 | 0.0037 | 0.0006 | -0.0005 | 0.0056 | -0.0071 | -0.005 | -360.1465 | 17.3987 | -360.4542 | 17.6369 | -360.7897 | 18.1132 | -360.8358 | 17.5219 | -352.6352 | 18.6963 | -352.6598 | 16.8443
12:26 | 3951 | 39.2664 | 201.4432 | 448.5762 | 454.7849 | -17.0117 | -42.2694 | 10.2895 | 7.2556 | 1.3962 | -0.008 | 2.7478 | -1.4453 | 10.9088 | 3.7715 | 0.6125 | 0.6596 | 0.9633 | 0.7349 | -129.574 | -1.1597 | 5.5236 | 1.6017 | -3.1932 | -1.4698 | 4.469 |  | 2.7589 | -0.1196 | 4.01 | 3.3655 | 3.3387 | 1.0679 | 10.7197 | 14.2509 | 14.8246 | 11.0728 | 0.0002 | -0.003 | 0.0009 | 0.0038 | 0.001 | -0.0006 | 0.0068 | -0.013 | -0.0009 | -360.1435 | 17.3823 | -360.4266 | 17.6369 | -360.7835 | 18.1091 | -360.845 | 17.528 | -352.6013 | 18.6861 | -352.6352 | 16.8258
12:26 | 3952 | 39.2696 | 201.4143 | 448.6122 | 454.8287 | -17.0215 | -42.2884 | 10.1722 | 7.3488 | 1.4354 | 0.008 | 2.7361 | -1.4092 | 10.9251 | 3.7297 | 0.6132 | 0.6554 | 0.9614 | 0.7355 | -129.5109 | -1.0335 | 5.5096 | 1.6003 | -3.2333 | -1.6178 | 4.5006 |  | 2.7218 | -0.0893 | 4.0114 | 3.3664 | 3.3391 | 1.0676 | 10.7383 | 14.2346 | 14.8133 | 11.08 | 0 | -0.0033 | 0.0003 | 0.0035 | 0.0006 | -0.0009 | 0.0103 | -0.0031 | -0.0063 | -360.1496 | 17.3946 | -360.4389 | 17.6492 | -360.805 | 18.105 | -360.842 | 17.5383 | -352.629 | 18.6902 | -352.6444 | 16.8279
12:26 | 3953 | 39.1976 | 201.407 | 448.6031 | 454.7243 | -16.9645 | -42.219 | 10.2787 | 7.2949 | 1.3986 | -0.0071 | 2.6567 | -1.3407 | 10.9064 | 3.6752 | 0.6126 | 0.6582 | 0.963 | 0.7354 | -129.5716 | -1.0289 | 5.6004 | 1.6349 | -3.2228 | -1.4083 | 4.4615 |  | 2.7392 | -0.0871 | 4.0116 | 3.3647 | 3.3388 | 1.0676 | 10.7268 | 14.2286 | 14.8228 | 11.0461 | -0.0004 | -0.0031 | 0.0006 | 0.0039 | 0.0009 | -0.0011 | 0.0158 | -0.0149 | -0.0056 | -360.1588 | 17.409 | -360.4819 | 17.6759 | -360.8512 | 18.1255 | -360.8697 | 17.5342 | -352.6106 | 18.7087 | -352.6937 | 16.8423
12:26 | 3954 | 39.223 | 201.4653 | 448.604 | 454.7509 | -16.9909 | -42.1735 | 10.2349 | 7.2811 | 1.4271 | -0.0428 | 2.6792 | -1.3129 | 10.9241 | 3.6908 | 0.6119 | 0.6592 | 0.9568 | 0.7351 | -129.5831 | -1.0502 | 5.5305 | 1.6986 | -3.264 | -1.4739 | 4.473 |  | 2.7649 | -0.1415 | 4.0103 | 3.3655 | 3.338 | 1.0672 | 10.7509 | 14.2939 | 14.84 | 11.0399 | -0.0003 | -0.0025 | 0.0008 | 0.004 | 0.0011 | -0.0001 | 0.0137 | 0.0111 | -0.0241 | -360.1958 | 17.409 | -360.4881 | 17.6738 | -360.8204 | 18.1317 | -360.9189 | 17.5609 | -352.6537 | 18.7169 | -352.6813 | 16.8484
12:26 | 3955 | 39.1429 | 201.3833 | 448.451 | 454.7219 | -17.0281 | -42.2108 | 10.2071 | 7.3725 | 1.3997 | 0.02 | 2.7267 | -1.3621 | 10.9569 | 3.6681 | 0.6121 | 0.6558 | 0.961 | 0.7358 | -129.6185 | -1.0641 | 5.469 | 1.8127 | -3.3397 | -1.5786 | 4.3708 |  | 2.7873 | -0.036 | 4.0114 | 3.3624 | 3.3398 | 1.0676 | 10.7695 | 14.2372 | 14.8461 | 11.0702 | -0.0001 | -0.0029 | 0.0005 | 0.0035 | 0.001 | -0.0006 | 0.015 | -0.0139 | -0.0022 | -360.2327 | 17.4233 | -360.485 | 17.6697 | -360.8081 | 18.1091 | -360.8789 | 17.5568 | -352.6875 | 18.7271 | -352.7121 | 16.8464
12:26 | 3956 | 39.1818 | 201.4468 | 448.5801 | 454.7967 | -16.8987 | -42.0603 | 10.3313 | 7.4757 | 1.3523 | 0.117 | 2.7583 | -1.3976 | 10.9937 | 3.7126 | 0.6129 | 0.6599 | 0.9626 | 0.7343 | -129.5947 | -0.9971 | 5.5031 | 1.7804 | -3.2307 | -1.5542 | 4.3739 |  | 2.8225 | -0.0783 | 4.0115 | 3.3653 | 3.3375 | 1.0682 | 10.7498 | 14.2579 | 14.826 | 11.0739 | 0 | -0.0032 | 0.0007 | 0.0036 | 0.0006 | -0.0002 | 0.0036 | -0.004 | -0.0073 | -360.1342 | 17.3843 | -360.4758 | 17.6718 | -360.8297 | 18.1173 | -360.8574 | 17.5178 | -352.6198 | 18.7128 | -352.669 | 16.8566
12:26 | 3957 | 39.2776 | 201.4874 | 448.5813 | 454.7744 | -16.8374 | -41.9208 | 10.4174 | 7.3471 | 1.3401 | 0.0799 | 2.7647 | -1.3918 | 11.0108 | 3.8101 | 0.6117 | 0.6604 | 0.9656 | 0.7358 | -129.5917 | -1.1129 | 5.5503 | 1.8412 | -3.1807 | -1.4892 | 4.4448 |  | 2.7833 | -0.0777 | 4.0115 | 3.3658 | 3.3422 | 1.0665 | 10.7798 | 14.2652 | 14.8526 | 11.0973 | -0.0001 | -0.0029 | 0.0009 | 0.0035 | 0.0014 | -0.0004 | 0.0175 | -0.0144 | -0.0071 | -360.1496 | 17.374 | -360.4081 | 17.6512 | -360.8081 | 18.1317 | -360.8512 | 17.5219 | -352.6321 | 18.6799 | -352.6167 | 16.8484
12:26 | 3958 | 39.2754 | 201.4618 | 448.5127 | 454.7856 | -16.8524 | -41.9179 | 10.4731 | 7.2595 | 1.2921 | -0.0677 | 2.7579 | -1.3736 | 10.9838 | 3.7721 | 0.6129 | 0.658 | 0.9606 | 0.7353 | -129.6016 | -1.0835 | 5.4982 | 1.7599 | -3.3019 | -1.552 | 4.4467 |  | 2.7574 | -0.0748 | 4.0115 | 3.3673 | 3.3396 | 1.0681 | 10.75 | 14.2401 | 14.8402 | 11.0808 | -0.0006 | -0.0031 | 0.0008 | 0.0038 | 0.0004 | -0.0003 | 0.0259 | -0.0038 | 0.0048 | -360.1773 | 17.3905 | -360.4204 | 17.6266 | -360.7466 | 18.0927 | -360.8574 | 17.5465 | -352.6321 | 18.7025 | -352.6383 | 16.8115
12:26 | 3959 | 39.3032 | 201.3736 | 448.5223 | 454.8119 | -16.842 | -41.9359 | 10.4241 | 7.261 | 1.4305 | -0.0247 | 2.7237 | -1.3457 | 10.934 | 3.6937 | 0.6134 | 0.6553 | 0.9625 | 0.7358 | -129.6246 | -1.0166 | 5.5339 | 1.8326 | -3.2516 | -1.5169 | 4.5193 |  | 2.7822 | -0.0558 | 4.0114 | 3.3656 | 3.3381 | 1.0695 | 10.722 | 14.2302 | 14.781 | 11.0518 | -0.0003 | -0.0026 | 0.0009 | 0.004 | 0.0011 | -0.0004 | 0.0024 | -0.0044 | 0.0046 | -360.1496 | 17.3905 | -360.4789 | 17.6636 | -360.8143 | 18.0968 | -360.7927 | 17.5075 | -352.6167 | 18.6963 | -352.6598 | 16.8505
12:26 | 3960 | 39.2601 | 201.3776 | 448.5506 | 454.7751 | -16.7909 | -41.8899 | 10.3707 | 7.2345 | 1.4404 | -0.0502 | 2.7321 | -1.4297 | 10.8972 | 3.6821 | 0.6137 | 0.6584 | 0.9636 | 0.736 | -129.6503 | -1.0982 | 5.4702 | 1.8955 | -3.2523 | -1.5241 | 4.5332 |  | 2.7639 | -0.0531 | 4.0105 | 3.3661 | 3.3387 | 1.0673 | 10.7072 | 14.2262 | 14.7911 | 11.044 | 0.0002 | -0.0031 | 0.0007 | 0.0039 | 0.0001 | -0.001 | 0.0117 | -0.0019 | 0.0038 | -360.1342 | 17.3597 | -360.4142 | 17.6471 | -360.8327 | 18.1379 | -360.9035 | 17.5198 | -352.5829 | 18.6737 | -352.6075 | 16.8197
12:26 | 3961 | 39.2252 | 201.5242 | 448.5549 | 454.8105 | -16.8102 | -41.8637 | 10.3622 | 7.2993 | 1.419 | -0.0693 | 2.7447 | -1.4433 | 10.8613 | 3.5864 | 0.6142 | 0.6582 | 0.9642 | 0.7365 | -129.5946 | -1.117 | 5.5118 | 1.7433 | -3.0982 | -1.4512 | 4.4848 |  | 2.7329 | -0.1361 | 4.0124 | 3.3659 | 3.3434 | 1.0678 | 10.7544 | 14.2512 | 14.8094 | 11.0663 | 0 | -0.0027 | 0.0007 | 0.0043 | 0.0005 | -0.0003 | 0.0244 | 0.0054 | 0.0023 | -360.1711 | 17.4172 | -360.4758 | 17.6348 | -360.7835 | 18.0988 | -360.8574 | 17.5506 | -352.6998 | 18.7128 | -352.6444 | 16.8094
12:26 | 3962 | 39.2642 | 201.5458 | 448.5247 | 454.844 | -16.8297 | -41.7997 | 10.3891 | 7.2677 | 1.4393 | -0.0137 | 2.8102 | -1.383 | 10.9403 | 3.6985 | 0.6139 | 0.6579 | 0.9639 | 0.737 | -129.6263 | -1.146 | 5.5252 | 1.648 | -3.2216 | -1.4873 | 4.3976 |  | 2.7691 | -0.0181 | 4.011 | 3.3714 | 3.3366 | 1.0686 | 10.7556 | 14.2349 | 14.8676 | 11.1024 | 0 | -0.0026 | 0.0006 | 0.0037 | 0.0012 | -0.0007 | 0.0288 | -0.0088 | -0.0343 | -360.1958 | 17.4172 | -360.5096 | 17.68 | -360.8789 | 18.1235 | -360.8635 | 17.526 | -352.6598 | 18.7292 | -352.6937 | 16.8648
12:26 | 3963 | 39.3029 | 201.5556 | 448.5047 | 454.759 | -16.81 | -41.8175 | 10.3788 | 7.2332 | 1.4441 | 0.0003 | 2.7239 | -1.3809 | 10.9847 | 3.7135 | 0.6125 | 0.6575 | 0.9609 | 0.7355 | -129.6161 | -1.0488 | 5.412 | 1.6078 | -3.2217 | -1.5468 | 4.4195 |  | 2.7778 | -0.0833 | 4.0126 | 3.3682 | 3.3398 | 1.0688 | 10.7648 | 14.2673 | 14.8648 | 11.0771 | -0.0003 | -0.0026 | 0.0006 | 0.0037 | 0.0004 | -0.0006 | 0.0153 | 0.0007 | -0.0043 | -360.1988 | 17.3905 | -360.4419 | 17.6533 | -360.8666 | 18.1584 | -360.922 | 17.5629 | -352.6783 | 18.7025 | -352.6475 | 16.8505
12:26 | 3964 | 39.3273 | 201.6252 | 448.6004 | 454.8322 | -16.8127 | -41.8756 | 10.4797 | 7.2186 | 1.4355 | 0.063 | 2.8123 | -1.3294 | 10.955 | 3.7684 | 0.6121 | 0.6549 | 0.9589 | 0.7343 | -129.5979 | -1.0436 | 5.4312 | 1.7164 | -3.3199 | -1.6215 | 4.3191 |  | 2.7296 | -0.0765 | 4.0111 | 3.3675 | 3.336 | 1.069 | 10.768 | 14.3006 | 14.8637 | 11.1128 | 0.0007 | -0.0025 | 0.0011 | 0.0044 | 0.001 | -0.0001 | -0.0064 | -0.0065 | -0.0332 | -360.2512 | 17.4233 | -360.4635 | 17.6328 | -360.7989 | 18.105 | -360.8881 | 17.5671 | -352.7337 | 18.7374 | -352.6783 | 16.8258
12:26 | 3965 | 39.2967 | 201.6265 | 448.6532 | 454.7773 | -16.7357 | -41.8299 | 10.525 | 7.2823 | 1.4179 | -0.0292 | 2.6779 | -1.2751 | 11.0328 | 3.7457 | 0.6139 | 0.6581 | 0.9613 | 0.736 | -129.5157 | -1.1358 | 5.4619 | 1.7449 | -3.2321 | -1.5798 | 4.294 |  | 2.7105 | -0.153 | 4.0115 | 3.3685 | 3.3393 | 1.068 | 10.7522 | 14.2022 | 14.8497 | 11.0537 | 0.0002 | -0.0031 | 0 | 0.0033 | 0 | -0.0003 | 0.0029 | -0.0124 | -0.0017 | -360.1373 | 17.411 | -360.5158 | 17.6738 | -360.8512 | 18.1091 | -360.8327 | 17.5239 | -352.6383 | 18.7087 | -352.6967 | 16.8689
12:26 | 3966 | 39.2951 | 201.5244 | 448.5202 | 454.638 | -16.9298 | -41.9001 | 10.4134 | 7.382 | 1.4738 | -0.0092 | 2.7695 | -1.2861 | 10.9394 | 3.8076 | 0.6118 | 0.6578 | 0.9591 | 0.7344 | -129.543 | -1.0519 | 5.5071 | 1.7762 | -3.2357 | -1.5329 | 4.4199 |  | 2.7 | -0.0064 | 4.0107 | 3.3667 | 3.3405 | 1.0678 | 10.7464 | 14.2426 | 14.8555 | 11.0537 | -0.0004 | -0.0025 | 0.0009 | 0.0038 | 0.001 | -0.0004 | 0.0053 | -0.0109 | -0.015 | -360.1619 | 17.3802 | -360.4019 | 17.6266 | -360.8174 | 18.1481 | -360.9035 | 17.5527 | -352.6537 | 18.6655 | -352.6167 | 16.8402
12:26 | 3967 | 39.3406 | 201.5124 | 448.6283 | 454.7341 | -16.8621 | -42.0022 | 10.3621 | 7.3472 | 1.5205 | 0.0091 | 2.8739 | -1.3089 | 10.9935 | 3.8106 | 0.6121 | 0.6589 | 0.961 | 0.7349 | -129.5857 | -1.1225 | 5.4602 | 1.6393 | -3.2982 | -1.5912 | 4.3196 |  | 2.715 | -0.0965 | 4.0117 | 3.3691 | 3.3419 | 1.0679 | 10.7382 | 14.229 | 14.8549 | 11.0681 | -0.0002 | -0.0027 | 0.0012 | 0.0045 | 0.0002 | -0.0003 | 0.0216 | -0.0158 | 0.0005 | -360.1681 | 17.3946 | -360.4327 | 17.602 | -360.7281 | 18.1132 | -360.8604 | 17.5465 | -352.6721 | 18.7025 | -352.626 | 16.8217
12:26 | 3968 | 39.3514 | 201.5056 | 448.6467 | 454.8088 | -16.8432 | -41.9137 | 10.3559 | 7.2728 | 1.5729 | 0.0415 | 2.8394 | -1.3495 | 10.9624 | 3.778 | 0.6131 | 0.6568 | 0.9588 | 0.7359 | -129.5968 | -1.1666 | 5.3902 | 1.6033 | -3.2387 | -1.7544 | 4.3318 |  | 2.8006 | -0.0229 | 4.0117 | 3.3667 | 3.3397 | 1.068 | 10.7083 | 14.2505 | 14.8098 | 11.0508 | 0.0001 | -0.0031 | 0.0003 | 0.0037 | 0.0007 | -0.0011 | -0.0034 | -0.0083 | 0.004 | -360.1034 | 17.3884 | -360.4758 | 17.6512 | -360.8389 | 18.1276 | -360.8081 | 17.4931 | -352.586 | 18.6943 | -352.669 | 16.8628
12:26 | 3969 | 39.3921 | 201.461 | 448.6137 | 454.7489 | -16.8515 | -41.888 | 10.3521 | 7.2977 | 1.5089 | -0.0138 | 2.7787 | -1.3799 | 10.8808 | 3.7809 | 0.6117 | 0.6538 | 0.9589 | 0.7352 | -129.6678 | -1.1223 | 5.3811 | 1.6522 | -3.2764 | -1.6244 | 4.2289 |  | 2.7646 | 0.0437 | 4.0099 | 3.3652 | 3.3379 | 1.067 | 10.6978 | 14.2114 | 14.7775 | 11.0284 | 0.0005 | -0.0028 | 0.001 | 0.0043 | 0.0011 | -0.0001 | 0.0014 | -0.0005 | 0.0042 | -360.1588 | 17.3576 | -360.3896 | 17.6163 | -360.7835 | 18.1522 | -360.8789 | 17.5301 | -352.6167 | 18.6635 | -352.586 | 16.8115
12:26 | 3970 | 39.3642 | 201.4672 | 448.5924 | 454.7565 | -16.8812 | -41.9236 | 10.4462 | 7.1815 | 1.5314 | -0.003 | 2.7475 | -1.3482 | 10.9297 | 3.7278 | 0.6098 | 0.6557 | 0.9631 | 0.736 | -129.7164 | -1.1898 | 5.2914 | 1.6853 | -3.2279 | -1.5897 | 4.4056 |  | 2.7455 | -0.0453 | 4.0093 | 3.3677 | 3.3406 | 1.0677 | 10.7382 | 14.2465 | 14.8328 | 11.0677 | -0.0003 | -0.0029 | 0.0006 | 0.0039 | 0.0009 | -0.0005 | 0.0243 | -0.0077 | 0.0061 | -360.1865 | 17.4007 | -360.4419 | 17.6122 | -360.7373 | 18.1153 | -360.8481 | 17.5383 | -352.6506 | 18.7004 | -352.626 | 16.8115
12:26 | 3971 | 39.3495 | 201.4878 | 448.5756 | 454.758 | -16.8899 | -42.0301 | 10.3487 | 7.2055 | 1.5158 | -0.0943 | 2.7234 | -1.316 | 10.9294 | 3.7985 | 0.6133 | 0.654 | 0.964 | 0.7352 | -129.7236 | -1.1579 | 5.4171 | 1.6111 | -3.2835 | -1.4979 | 4.3562 |  | 2.8375 | -0.0451 | 4.0121 | 3.3669 | 3.3416 | 1.0672 | 10.744 | 14.2465 | 14.8502 | 11.1082 | 0.0002 | -0.0023 | 0.0007 | 0.0036 | 0.001 | -0.0002 | 0.0272 | -0.0157 | -0.0186 | -360.1465 | 17.4007 | -360.4912 | 17.6512 | -360.8389 | 18.1399 | -360.8358 | 17.5116 | -352.6229 | 18.6943 | -352.669 | 16.8566
12:26 | 3972 | 39.3815 | 201.5131 | 448.5662 | 454.7692 | -16.8636 | -41.995 | 10.3354 | 7.2352 | 1.4853 | -0.0354 | 2.764 | -1.3386 | 10.946 | 3.8267 | 0.613 | 0.6529 | 0.9613 | 0.736 | -129.6787 | -1.1894 | 5.4388 | 1.4617 | -3.3177 | -1.6561 | 4.2813 |  | 2.8042 | -0.0474 | 4.0119 | 3.3672 | 3.3418 | 1.0691 | 10.7648 | 14.2616 | 14.8775 | 11.0536 | 0.0001 | -0.0029 | 0.001 | 0.0037 | 0.0009 | -0.0003 | 0.0169 | -0.0172 | -0.0134 | -360.1404 | 17.3782 | -360.4019 | 17.6348 | -360.8327 | 18.1625 | -360.9035 | 17.5465 | -352.626 | 18.6655 | -352.6075 | 16.832
12:26 | 3973 | 39.4315 | 201.5423 | 448.6258 | 454.805 | -16.8772 | -42.0089 | 10.3485 | 7.3164 | 1.5453 | 0.0489 | 2.8194 | -1.2411 | 10.9524 | 3.8636 | 0.6121 | 0.6558 | 0.9623 | 0.7367 | -129.6076 | -1.0102 | 5.3779 | 1.5353 | -3.3155 | -1.5643 | 4.3391 |  | 2.752 | -0.0234 | 4.0123 | 3.3689 | 3.3413 | 1.0686 | 10.766 | 14.2741 | 14.8651 | 11.119 | 0 | -0.0031 | 0.0008 | 0.0039 | 0.0006 | -0.0007 | 0.0029 | 0.0007 | -0.0087 | -360.2604 | 17.4254 | -360.4819 | 17.643 | -360.7989 | 18.1276 | -360.8666 | 17.5363 | -352.6721 | 18.7189 | -352.666 | 16.8299
12:26 | 3974 | 39.466 | 201.4998 | 448.6569 | 454.8217 | -16.7622 | -41.9273 | 10.391 | 7.3871 | 1.4643 | 0.0013 | 2.6748 | -1.1676 | 10.9667 | 3.8137 | 0.6141 | 0.6565 | 0.9629 | 0.7358 | -129.6047 | -1.1576 | 5.3608 | 1.6141 | -3.276 | -1.6135 | 4.2863 |  | 2.7852 | -0.0584 | 4.0112 | 3.3649 | 3.3393 | 1.0677 | 10.7313 | 14.2452 | 14.8304 | 11.0728 | -0.0003 | -0.0029 | 0.0008 | 0.0039 | 0.0001 | -0.0005 | -0.0002 | 0.0071 | -0.0031 | -360.1865 | 17.411 | -360.5312 | 17.6779 | -360.8758 | 18.1522 | -360.8635 | 17.5157 | -352.6229 | 18.7107 | -352.7121 | 16.8607
12:26 | 3975 | 39.3643 | 201.5343 | 448.4931 | 454.7312 | -16.8195 | -41.9806 | 10.4469 | 7.3435 | 1.6105 | 0.0189 | 2.7436 | -1.371 | 11.0198 | 3.852 | 0.6139 | 0.6596 | 0.9617 | 0.7349 | -129.6816 | -1.1668 | 5.4245 | 1.5966 | -3.2806 | -1.7145 | 4.269 |  | 2.746 | -0.0524 | 4.0105 | 3.3682 | 3.34 | 1.0683 | 10.7509 | 14.2766 | 14.8631 | 11.0919 | -0.0006 | -0.0026 | 0.0011 | 0.0043 | 0.0009 | -0.0006 | 0.0003 | -0.0006 | -0.0123 | -360.1958 | 17.3905 | -360.4635 | 17.6636 | -360.8358 | 18.1604 | -360.9066 | 17.5527 | -352.6598 | 18.6984 | -352.6506 | 16.8525
12:26 | 3976 | 39.3072 | 201.6176 | 448.6139 | 454.8283 | -16.8244 | -41.9599 | 10.4236 | 7.3031 | 1.5596 | -0.0024 | 2.7642 | -1.3454 | 11.0029 | 3.7901 | 0.6134 | 0.657 | 0.9629 | 0.7355 | -129.6197 | -1.2034 | 5.5466 | 1.5748 | -3.2321 | -1.6772 | 4.2661 |  | 2.6497 | -0.213 | 4.0123 | 3.3677 | 3.3413 | 1.0686 | 10.7476 | 14.238 | 14.8222 | 11.0836 | -0.0004 | -0.0028 | 0.0006 | 0.0039 | 0.0008 | -0.0003 | 0.0056 | -0.0023 | -0.004 | -360.2327 | 17.4418 | -360.5096 | 17.6656 | -360.845 | 18.1502 | -360.8758 | 17.5383 | -352.6998 | 18.7271 | -352.7121 | 16.8566
12:26 | 3977 | 39.3761 | 201.5597 | 448.5573 | 454.9273 | -16.713 | -41.8208 | 10.423 | 7.3128 | 1.6283 | 0.0697 | 2.749 | -1.3176 | 11.0185 | 3.8375 | 0.6133 | 0.6551 | 0.9649 | 0.7366 | -129.6416 | -1.1671 | 5.445 | 1.5898 | -3.2717 | -1.644 | 4.3453 |  | 2.6631 | -0.139 | 4.0118 | 3.3656 | 3.3441 | 1.0687 | 10.7014 | 14.2204 | 14.8143 | 11.044 | 0.0001 | -0.0036 | 0.0006 | 0.0038 | 0.0007 | -0.0009 | 0.0161 | -0.0049 | -0.0111 | -360.165 | 17.4028 | -360.4819 | 17.6615 | -360.8574 | 18.1563 | -360.8943 | 17.528 | -352.6352 | 18.7066 | -352.6598 | 16.8648
12:26 | 3978 | 39.4482 | 201.6033 | 448.5652 | 454.9438 | -16.7205 | -41.8317 | 10.3818 | 7.234 | 1.5092 | 0.1271 | 2.7212 | -1.3248 | 11.0004 | 3.7797 | 0.6121 | 0.6568 | 0.9616 | 0.7343 | -129.6566 | -1.2048 | 5.4172 | 1.5296 | -3.2022 | -1.7677 | 4.2811 |  | 2.6787 | -0.1012 | 4.0111 | 3.3657 | 3.3397 | 1.0688 | 10.7337 | 14.2474 | 14.8379 | 11.0869 | 0 | -0.003 | 0.0008 | 0.0038 | 0.0002 | -0.0005 | -0.0011 | -0.002 | -0.0144 | -360.1865 | 17.409 | -360.4542 | 17.6451 | -360.8389 | 18.144 | -360.8974 | 17.5404 | -352.666 | 18.7148 | -352.6721 | 16.8546
12:26 | 3979 | 39.3773 | 201.545 | 448.5931 | 454.8349 | -16.7185 | -41.8009 | 10.504 | 7.3166 | 1.5402 | 0.1128 | 2.7613 | -1.2976 | 11.0082 | 3.9436 | 0.6126 | 0.6519 | 0.9589 | 0.7359 | -129.6593 | -1.1732 | 5.4491 | 1.6731 | -3.3307 | -1.7388 | 4.2389 |  | 2.6831 | -0.1406 | 4.0118 | 3.3641 | 3.3407 | 1.0689 | 10.722 | 14.265 | 14.8631 | 11.0746 | -0.0004 | -0.0028 | 0.0007 | 0.0035 | 0.0014 | -0.0005 | 0.0066 | -0.0145 | -0.0291 | -360.1619 | 17.3966 | -360.4481 | 17.6348 | -360.7712 | 18.1522 | -360.8635 | 17.5157 | -352.6444 | 18.7148 | -352.6506 | 16.8484
12:26 | 3980 | 39.4024 | 201.551 | 448.6048 | 454.7999 | -16.7078 | -41.8012 | 10.5754 | 7.3885 | 1.5492 | 0.127 | 2.831 | -1.3041 | 11.0133 | 3.8461 | 0.6121 | 0.6573 | 0.9604 | 0.7353 | -129.6725 | -1.2163 | 5.407 | 1.6118 | -3.263 | -1.5921 | 4.2537 |  | 2.8139 | -0.1299 | 4.0113 | 3.3656 | 3.3418 | 1.0674 | 10.7671 | 14.2756 | 14.857 | 11.0731 | 0 | -0.0028 | 0.0013 | 0.0041 | 0.0007 | -0.0003 | 0.0086 | -0.0171 | -0.0251 | -360.1588 | 17.3823 | -360.4358 | 17.6286 | -360.765 | 18.1379 | -360.8604 | 17.5116 | -352.6106 | 18.6963 | -352.6475 | 16.8361
12:26 | 3981 | 39.3626 | 201.5245 | 448.5476 | 454.7786 | -16.7456 | -41.7309 | 10.5587 | 7.3398 | 1.4632 | -0.0293 | 2.7753 | -1.255 | 11.0578 | 3.9708 | 0.6129 | 0.6578 | 0.9623 | 0.7365 | -129.6464 | -1.1926 | 5.4967 | 1.5913 | -3.2966 | -1.6426 | 4.2472 |  | 2.7675 | -0.1037 | 4.0115 | 3.3644 | 3.3416 | 1.0685 | 10.7509 | 14.2652 | 14.8758 | 11.0915 | 0.0004 | -0.0029 | 0.0011 | 0.0045 | 0.0013 | 0 | 0.0154 | -0.0055 | -0.0007 | -360.1927 | 17.3905 | -360.4266 | 17.6204 | -360.7527 | 18.1296 | -360.8543 | 17.5198 | -352.626 | 18.7169 | -352.626 | 16.8279
12:26 | 3982 | 39.4577 | 201.5627 | 448.6105 | 454.826 | -16.6557 | -41.7316 | 10.4887 | 7.4141 | 1.5543 | 0.1964 | 2.7908 | -1.3047 | 10.9011 | 3.7618 | 0.6112 | 0.6528 | 0.9614 | 0.7348 | -129.5945 | -1.0965 | 5.5069 | 1.6733 | -3.1612 | -1.5593 | 4.3146 |  | 2.7465 | -0.0104 | 4.0106 | 3.3639 | 3.3417 | 1.0695 | 10.766 | 14.2453 | 14.8372 | 11.0551 | -0.0003 | -0.0028 | 0.0007 | 0.0036 | 0.0008 | -0.0005 | 0.0209 | -0.0078 | -0.0022 | -360.1404 | 17.3782 | -360.4296 | 17.6266 | -360.7743 | 18.1296 | -360.8143 | 17.4972 | -352.6075 | 18.7004 | -352.6444 | 16.8423
12:26 | 3983 | 39.4566 | 201.486 | 448.4601 | 454.7495 | -16.6802 | -41.7118 | 10.5713 | 7.3456 | 1.6083 | 0.117 | 2.7706 | -1.3415 | 10.939 | 3.9567 | 0.6132 | 0.6559 | 0.9567 | 0.7352 | -129.6166 | -1.148 | 5.3493 | 1.6618 | -3.2453 | -1.5802 | 4.3018 |  | 2.688 | -0.059 | 4.0115 | 3.3594 | 3.3399 | 1.0696 | 10.7358 | 14.2674 | 14.8369 | 11.0883 | -0.0001 | -0.0024 | 0.001 | 0.0047 | 0.0006 | -0.0006 | 0.0151 | -0.0063 | -0.0171 | -360.1281 | 17.3761 | -360.4019 | 17.6245 | -360.8112 | 18.1502 | -360.8727 | 17.5178 | -352.5921 | 18.6922 | -352.5983 | 16.834
12:26 | 3984 | 39.4791 | 201.5812 | 448.5069 | 454.794 | -16.7013 | -41.6573 | 10.5893 | 7.3837 | 1.5493 | 0.111 | 2.8255 | -1.3082 | 10.941 | 3.9134 | 0.6124 | 0.6581 | 0.9594 | 0.7348 | -129.6294 | -1.1809 | 5.3923 | 1.729 | -3.1761 | -1.7612 | 4.366 |  | 2.697 | -0.056 | 4.0112 | 3.3612 | 3.343 | 1.0701 | 10.736 | 14.2382 | 14.858 | 11.0948 | -0.0001 | -0.0027 | 0.0005 | 0.004 | 0.0007 | -0.0007 | 0.0292 | -0.0138 | 0.0074 | -360.1835 | 17.4028 | -360.4666 | 17.6102 | -360.7589 | 18.1337 | -360.8481 | 17.528 | -352.6567 | 18.7189 | -352.6136 | 16.8156
12:26 | 3985 | 39.4871 | 201.5401 | 448.5783 | 454.7841 | -16.6563 | -41.7377 | 10.5503 | 7.4025 | 1.5909 | 0.2665 | 2.7893 | -1.345 | 10.9374 | 3.856 | 0.6145 | 0.6558 | 0.9596 | 0.7355 | -129.6497 | -1.1711 | 5.3459 | 1.7543 | -3.218 | -1.6017 | 4.3344 |  | 2.6994 | -0.0831 | 4.0107 | 3.3617 | 3.3386 | 1.0689 | 10.7452 | 14.2591 | 14.8737 | 11.0923 | 0.0002 | -0.0032 | 0.0005 | 0.004 | 0.0005 | -0.0008 | 0.0153 | -0.0069 | -0.0148 | -360.1619 | 17.3925 | -360.4881 | 17.6656 | -360.8174 | 18.1358 | -360.8604 | 17.5096 | -352.6106 | 18.7128 | -352.6937 | 16.8587
12:26 | 3986 | 39.4543 | 201.6463 | 448.5166 | 454.7879 | -16.7658 | -41.7968 | 10.479 | 7.3822 | 1.516 | 0.2032 | 2.7863 | -1.1995 | 10.9519 | 3.8254 | 0.6124 | 0.6539 | 0.9604 | 0.734 | -129.6324 | -1.325 | 5.3005 | 1.7511 | -3.2064 | -1.5109 | 4.3647 |  | 2.7531 | 0.0177 | 4.0119 | 3.3633 | 3.3427 | 1.0693 | 10.7417 | 14.2498 | 14.829 | 11.0659 | 0 | -0.0031 | 0.001 | 0.0043 | 0.0009 | -0.0006 | 0.0085 | 0.0001 | -0.0194 | -360.1588 | 17.3843 | -360.4481 | 17.6615 | -360.8574 | 18.181 | -360.8697 | 17.5157 | -352.6537 | 18.6984 | -352.6444 | 16.8525
12:26 | 3987 | 39.4178 | 201.542 | 448.5361 | 454.835 | -16.8486 | -41.9344 | 10.4384 | 7.3545 | 1.6082 | 0.1599 | 2.8319 | -1.2103 | 10.9407 | 3.9525 | 0.6117 | 0.6559 | 0.9594 | 0.735 | -129.6218 | -1.2157 | 5.3717 | 1.8346 | -3.1521 | -1.5162 | 4.3327 |  | 2.7055 | 0.0268 | 4.0122 | 3.3646 | 3.346 | 1.0702 | 10.7244 | 14.244 | 14.8174 | 11.0544 | -0.0004 | -0.0028 | 0.0001 | 0.003 | 0.0007 | -0.0003 | -0.0005 | -0.0105 | -0.0133 | -360.2235 | 17.4254 | -360.4789 | 17.643 | -360.8174 | 18.1502 | -360.885 | 17.5629 | -352.6937 | 18.7395 | -352.6721 | 16.8361
12:26 | 3988 | 39.4438 | 201.583 | 448.6549 | 454.8415 | -16.8312 | -41.904 | 10.373 | 7.4903 | 1.732 | 0.1565 | 2.8814 | -1.2382 | 11.021 | 3.9164 | 0.6133 | 0.6544 | 0.9576 | 0.7344 | -129.6296 | -1.1688 | 5.3959 | 1.5781 | -3.2088 | -1.5582 | 4.3517 |  | 2.7327 | -0.112 | 4.0119 | 3.3668 | 3.343 | 1.0699 | 10.7428 | 14.2686 | 14.8383 | 11.0951 | 0.0001 | -0.0024 | 0.0013 | 0.0042 | 0.0009 | -0.0008 | 0.0027 | -0.006 | -0.021 | -360.1865 | 17.4192 | -360.5127 | 17.6985 | -360.8789 | 18.1522 | -360.8697 | 17.5219 | -352.6413 | 18.7415 | -352.7367 | 16.8915
12:26 | 3989 | 39.4032 | 201.5363 | 448.6322 | 454.8576 | -16.846 | -41.8326 | 10.4523 | 7.4394 | 1.7023 | 0.1715 | 2.9089 | -1.2464 | 11.0225 | 3.9141 | 0.6123 | 0.6527 | 0.9601 | 0.7344 | -129.6012 | -1.1928 | 5.3102 | 1.6943 | -3.2274 | -1.6134 | 4.3023 |  | 2.8136 | -0.064 | 4.0124 | 3.3642 | 3.3414 | 1.0691 | 10.7555 | 14.2524 | 14.8628 | 11.0847 | 0.0004 | -0.0028 | 0.0009 | 0.0037 | 0.0007 | 0.0002 | 0.0093 | -0.0131 | 0.001 | -360.1742 | 17.3884 | -360.4204 | 17.6512 | -360.8358 | 18.1687 | -360.9189 | 17.5404 | -352.666 | 18.7004 | -352.6383 | 16.8484
12:26 | 3990 | 39.385 | 201.5365 | 448.598 | 454.8126 | -16.812 | -41.8378 | 10.2966 | 7.4878 | 1.6979 | 0.1616 | 2.896 | -1.1728 | 11.0883 | 3.9515 | 0.6114 | 0.6553 | 0.9607 | 0.7356 | -129.6054 | -1.161 | 5.4478 | 1.6265 | -3.21 | -1.5904 | 4.2888 |  | 2.6788 | 0.0019 | 4.0118 | 3.3652 | 3.3421 | 1.0685 | 10.7533 | 14.2441 | 14.8706 | 11.0829 | 0.0002 | -0.0028 | 0.0008 | 0.0038 | 0.0015 | -0.0005 | 0.0043 | -0.0155 | -0.0165 | -360.2111 | 17.4131 | -360.4666 | 17.6143 | -360.7589 | 18.1173 | -360.8389 | 17.528 | -352.6813 | 18.7353 | -352.6813 | 16.8381
12:26 | 3991 | 39.4096 | 201.4452 | 448.546 | 454.8087 | -16.7667 | -41.9054 | 10.4004 | 7.541 | 1.7224 | 0.0903 | 2.883 | -1.1496 | 11.0287 | 4.0332 | 0.6125 | 0.6532 | 0.9626 | 0.7343 | -129.5911 | -1.1707 | 5.4148 | 1.6507 | -3.2391 | -1.5656 | 4.2504 |  | 2.794 | -0.0062 | 4.0116 | 3.3681 | 3.343 | 1.0687 | 10.7475 | 14.2613 | 14.829 | 11.1064 | -0.0002 | -0.0028 | 0.0008 | 0.0041 | 0.0005 | 0.0003 | 0.0005 | -0.0065 | -0.0251 | -360.0942 | 17.3761 | -360.4542 | 17.6697 | -360.8297 | 18.1522 | -360.8081 | 17.4808 | -352.589 | 18.7004 | -352.6967 | 16.8833
12:26 | 3992 | 39.543 | 201.5194 | 448.6409 | 454.8313 | -16.8412 | -41.9938 | 10.3512 | 7.445 | 1.7372 | 0.1489 | 2.899 | -1.1781 | 11.0319 | 3.9645 | 0.6115 | 0.6558 | 0.9561 | 0.7355 | -129.576 | -1.1939 | 5.4885 | 1.5747 | -3.1839 | -1.6251 | 4.2428 |  | 2.8115 | 0.0835 | 4.0114 | 3.3667 | 3.3393 | 1.0701 | 10.7348 | 14.2428 | 14.8219 | 11.0648 | -0.0003 | -0.0024 | 0.0006 | 0.0035 | 0.001 | -0.0004 | 0.0275 | -0.006 | -0.0019 | -360.1558 | 17.3638 | -360.3835 | 17.604 | -360.762 | 18.1461 | -360.8697 | 17.5116 | -352.626 | 18.6779 | -352.5736 | 16.8279
12:26 | 3993 | 39.4556 | 201.5279 | 448.6235 | 454.8307 | -16.8176 | -42.0582 | 10.3865 | 7.4231 | 1.7374 | 0.0702 | 2.8566 | -1.0874 | 11.0687 | 4.0201 | 0.6126 | 0.6534 | 0.9584 | 0.7353 | -129.5768 | -1.1499 | 5.4807 | 1.5942 | -3.1137 | -1.5878 | 4.2706 |  | 2.8007 | -0.01 | 4.0113 | 3.3655 | 3.3404 | 1.0693 | 10.7602 | 14.2509 | 14.8593 | 11.0959 | 0.0001 | -0.0029 | 0.0009 | 0.0042 | 0.0009 | -0.0006 | 0.0175 | -0.0082 | -0.0101 | -360.2204 | 17.4151 | -360.4789 | 17.6328 | -360.7927 | 18.105 | -360.8512 | 17.5137 | -352.6413 | 18.7312 | -352.666 | 16.8381
12:26 | 3994 | 39.4924 | 201.5579 | 448.6893 | 454.85 | -16.8274 | -41.9057 | 10.3927 | 7.4005 | 1.6855 | 0.0494 | 2.9643 | -1.036 | 10.9915 | 4.049 | 0.6133 | 0.6538 | 0.96 | 0.7356 | -129.5608 | -1.259 | 5.444 | 1.7811 | -3.118 | -1.4987 | 4.2836 |  | 2.8454 | 0.0686 | 4.0104 | 3.3606 | 3.3401 | 1.0699 | 10.7233 | 14.2309 | 14.8429 | 11.0367 | 0.0001 | -0.0034 | 0.0012 | 0.0042 | 0.0008 | -0.0006 | 0.0058 | -0.003 | -0.0073 | -360.1804 | 17.3905 | -360.4973 | 17.68 | -360.8635 | 18.1563 | -360.842 | 17.5013 | -352.5983 | 18.7045 | -352.6567 | 16.8792
12:26 | 3995 | 39.5007 | 201.5427 | 448.7403 | 454.7869 | -16.7569 | -41.9169 | 10.3908 | 7.3763 | 1.748 | 0.1333 | 2.9265 | -1.0653 | 10.9421 | 4.0243 | 0.6117 | 0.6576 | 0.9581 | 0.7363 | -129.4872 | -1.2007 | 5.4625 | 1.8381 | -3.2083 | -1.461 | 4.382 |  | 2.7792 | -0.0396 | 4.0125 | 3.3607 | 3.3394 | 1.0698 | 10.7302 | 14.2438 | 14.8453 | 11.0779 | -0.0001 | -0.0029 | 0.0006 | 0.0037 | 0.0007 | -0.001 | 0.0054 | -0.0089 | 0.0099 | -360.205 | 17.4069 | -360.4389 | 17.6369 | -360.805 | 18.1748 | -360.9066 | 17.5609 | -352.7121 | 18.7107 | -352.6475 | 16.8361
12:26 | 3996 | 39.516 | 201.5508 | 448.6785 | 454.8488 | -16.8057 | -41.9527 | 10.3875 | 7.389 | 1.7832 | 0.0985 | 2.8786 | -1.15 | 10.9835 | 4.0047 | 0.6121 | 0.658 | 0.9606 | 0.7356 | -129.4566 | -1.0988 | 5.5032 | 1.8291 | -3.1282 | -1.6027 | 4.3494 |  | 2.7932 | -0.0066 | 4.0114 | 3.3629 | 3.3397 | 1.0705 | 10.7094 | 14.2518 | 14.8181 | 11.0573 | -0.0006 | -0.003 | 0.0006 | 0.0036 | 0.0005 | -0.0004 | 0.0215 | -0.002 | -0.0039 | -360.2327 | 17.4418 | -360.5373 | 17.6718 | -360.8358 | 18.1358 | -360.8512 | 17.5301 | -352.7029 | 18.76 | -352.7275 | 16.8751
12:26 | 3997 | 39.4494 | 201.5729 | 448.7194 | 454.9047 | -16.8338 | -42.0038 | 10.3517 | 7.4155 | 1.7266 | 0.1922 | 2.8025 | -1.0398 | 10.9785 | 3.9692 | 0.6141 | 0.6546 | 0.9609 | 0.7348 | -129.4756 | -1.1229 | 5.4637 | 1.7613 | -3.1938 | -1.542 | 4.3489 |  | 2.8244 | 0.0109 | 4.0123 | 3.3649 | 3.342 | 1.0698 | 10.7613 | 14.287 | 14.8618 | 11.0966 | 0.0001 | -0.0029 | 0.0005 | 0.0036 | 0.0006 | -0.0006 | 0.0167 | -0.007 | -0.007 | -360.1435 | 17.3679 | -360.4389 | 17.6512 | -360.8204 | 18.1666 | -360.8666 | 17.5239 | -352.5921 | 18.6984 | -352.6506 | 16.8689
12:26 | 3998 | 39.5141 | 201.569 | 448.7127 | 454.868 | -16.7796 | -41.996 | 10.412 | 7.4439 | 1.6967 | 0.2679 | 2.8525 | -1.1077 | 10.9687 | 3.9184 | 0.614 | 0.6543 | 0.9606 | 0.7349 | -129.5872 | -1.2445 | 5.5412 | 1.7048 | -3.2837 | -1.5466 | 4.3376 |  | 2.7738 | -0.0688 | 4.0119 | 3.3637 | 3.3399 | 1.0671 | 10.7463 | 14.2661 | 14.8461 | 11.1049 | 0.0004 | -0.003 | 0.0009 | 0.0042 | 0.0008 | -0.0002 | 0.0282 | -0.0037 | -0.0027 | -360.1927 | 17.3864 | -360.3896 | 17.6061 | -360.7404 | 18.1481 | -360.8727 | 17.5794 | -352.6537 | 18.6943 | -352.5736 | 16.8135
12:26 | 3999 | 39.4528 | 201.576 | 448.6681 | 454.8938 | -16.8413 | -42.0422 | 10.3621 | 7.4236 | 1.7351 | 0.2337 | 2.8359 | -1.106 | 10.9398 | 3.898 | 0.6126 | 0.6557 | 0.9602 | 0.7348 | -129.5837 | -1.2006 | 5.4226 | 1.7436 | -3.249 | -1.5222 | 4.4028 |  | 2.7689 | -0.0733 | 4.0117 | 3.3641 | 3.3401 | 1.0692 | 10.7556 | 14.2696 | 14.8676 | 11.0793 | -0.0003 | -0.003 | 0.0006 | 0.0041 | 0.0011 | -0.0003 | 0.0125 | -0.005 | -0.0105 | -360.1527 | 17.4131 | -360.4696 | 17.6307 | -360.8112 | 18.142 | -360.7866 | 17.5445 | -352.6198 | 18.7189 | -352.6537 | 16.8464
12:26 | 4000 | 39.4901 | 201.6414 | 448.6539 | 454.8442 | -16.8267 | -41.9261 | 10.4055 | 7.449 | 1.737 | 0.0464 | 2.9218 | -1.138 | 10.975 | 3.9897 | 0.6124 | 0.6566 | 0.9625 | 0.7346 | -129.5608 | -1.1802 | 5.4631 | 1.7819 | -3.2189 | -1.6013 | 4.3597 |  | 2.7721 | 0.0048 | 4.0123 | 3.3629 | 3.3385 | 1.0664 | 10.737 | 14.2744 | 14.8673 | 11.0778 | -0.0004 | -0.0026 | 0.0006 | 0.0037 | 0.0007 | -0.0002 | 0.0176 | -0.0021 | -0.0064 | -360.1773 | 17.3823 | -360.4481 | 17.6636 | -360.8697 | 18.1974 | -360.8789 | 17.5794 | -352.6044 | 18.6984 | -352.6444 | 16.8546
12:26 | 4001 | 39.4725 | 201.561 | 448.7161 | 454.8919 | -16.878 | -41.9442 | 10.3254 | 7.4478 | 1.7422 | 0.0522 | 2.8593 | -1.1367 | 10.9503 | 4.0199 | 0.6124 | 0.6522 | 0.9597 | 0.7359 | -129.6075 | -1.2948 | 5.414 | 1.7345 | -3.1653 | -1.5595 | 4.3345 |  | 2.7288 | -0.0742 | 4.0115 | 3.3663 | 3.3388 | 1.0689 | 10.75 | 14.2575 | 14.8749 | 11.0808 | -0.0004 | -0.0033 | 0.0005 | 0.0038 | 0.0007 | -0.0011 | -0.0097 | -0.0134 | 0.0059 | -360.2819 | 17.4254 | -360.4481 | 17.6225 | -360.7958 | 18.1871 | -360.8881 | 17.6307 | -352.749 | 18.7436 | -352.6844 | 16.8381
12:26 | 4002 | 39.5923 | 201.6346 | 448.6653 | 454.8665 | -16.8473 | -41.9421 | 10.332 | 7.434 | 1.7066 | 0.0704 | 2.8726 | -1.1522 | 10.9588 | 3.9474 | 0.6127 | 0.656 | 0.9588 | 0.7357 | -129.574 | -1.1707 | 5.4117 | 1.6693 | -3.241 | -1.483 | 4.3677 |  | 2.77 | -0.0021 | 4.0113 | 3.367 | 3.3383 | 1.0683 | 10.7152 | 14.2404 | 14.8365 | 11.0742 | 0.0002 | -0.0029 | 0.0004 | 0.0037 | 0.0009 | -0.0005 | 0.0182 | -0.0179 | 0.0017 | -360.1404 | 17.4048 | -360.5219 | 17.6697 | -360.8604 | 18.1769 | -360.8235 | 17.5527 | -352.6629 | 18.7292 | -352.6967 | 16.8751
12:26 | 4003 | 39.5396 | 201.6402 | 448.7367 | 454.9217 | -16.8503 | -41.9991 | 10.3303 | 7.4018 | 1.7233 | 0.0428 | 2.9236 | -1.1483 | 10.9774 | 3.9566 | 0.6138 | 0.6549 | 0.9595 | 0.7363 | -129.6081 | -1.1729 | 5.5797 | 1.6602 | -3.1948 | -1.4805 | 4.4084 |  | 2.8039 | -0.0145 | 4.0105 | 3.363 | 3.3386 | 1.0675 | 10.7268 | 14.2575 | 14.817 | 11.0692 | -0.0003 | -0.0034 | 0.0008 | 0.0036 | 0.0008 | -0.0007 | -0.0004 | -0.005 | -0.0186 | -360.165 | 17.3576 | -360.3865 | 17.6204 | -360.805 | 18.181 | -360.8727 | 17.5753 | -352.6136 | 18.6902 | -352.626 | 16.832
12:26 | 4004 | 39.541 | 201.6717 | 448.7481 | 454.8099 | -16.7726 | -42.0021 | 10.4231 | 7.405 | 1.6241 | 0.0827 | 2.8847 | -1.1239 | 11.067 | 3.9257 | 0.6148 | 0.6549 | 0.9616 | 0.7364 | -129.5778 | -1.1984 | 5.6086 | 1.5659 | -3.2696 | -1.574 | 4.2809 |  | 2.7719 | 0.03 | 4.0112 | 3.3634 | 3.3423 | 1.0675 | 10.7463 | 14.2604 | 14.8587 | 11.0872 | -0.0004 | -0.0028 | 0.0007 | 0.0037 | 0.0007 | -0.0006 | 0.0091 | 0.0034 | -0.0026 | -360.2142 | 17.4048 | -360.4542 | 17.6184 | -360.7527 | 18.1358 | -360.8235 | 17.5753 | -352.669 | 18.723 | -352.6413 | 16.8176
12:26 | 4005 | 39.53 | 201.6132 | 448.6777 | 454.8066 | -16.7716 | -41.9601 | 10.4023 | 7.4243 | 1.719 | 0.0695 | 2.9026 | -1.1195 | 11.0152 | 3.9071 | 0.6133 | 0.6555 | 0.9585 | 0.7373 | -129.5764 | -1.268 | 5.5405 | 1.4929 | -3.2523 | -1.5981 | 4.3246 |  | 2.7939 | -0.023 | 4.0129 | 3.3635 | 3.3421 | 1.0684 | 10.7509 | 14.2594 | 14.8526 | 11.0915 | 0.0001 | -0.0029 | 0.0011 | 0.0037 | 0.0008 | -0.0003 | 0.0195 | -0.0057 | -0.0065 | -360.1527 | 17.3905 | -360.4819 | 17.6697 | -360.8789 | 18.1748 | -360.8297 | 17.5445 | -352.6013 | 18.7025 | -352.666 | 16.8669
12:26 | 4006 | 39.4523 | 201.6086 | 448.6972 | 454.912 | -16.8495 | -41.9914 | 10.3625 | 7.4195 | 1.6435 | 0.0707 | 2.8676 | -1.1259 | 11.0363 | 4.0225 | 0.6127 | 0.6558 | 0.9614 | 0.7369 | -129.6916 | -1.3267 | 5.4675 | 1.6862 | -3.1967 | -1.6408 | 4.4007 |  | 2.7538 | -0.0234 | 4.0123 | 3.3619 | 3.3409 | 1.0679 | 10.7487 | 14.2625 | 14.8478 | 11.067 | 0.0001 | -0.003 | 0.0008 | 0.0036 | 0.0009 | -0.0005 | 0.007 | 0.0006 | -0.0138 | -360.1988 | 17.3987 | -360.4481 | 17.6492 | -360.8297 | 18.1974 | -360.9035 | 17.602 | -352.6783 | 18.723 | -352.6506 | 16.8402
12:26 | 4007 | 39.5107 | 201.6307 | 448.6948 | 454.902 | -16.7491 | -41.9632 | 10.3918 | 7.4274 | 1.5867 | 0.0872 | 2.8869 | -1.0998 | 11.0684 | 4.0332 | 0.6135 | 0.6543 | 0.9597 | 0.7388 | -129.6613 | -1.2627 | 5.4284 | 1.5478 | -3.2393 | -1.6001 | 4.2929 |  | 2.7714 | -0.0422 | 4.0119 | 3.363 | 3.3402 | 1.0675 | 10.7601 | 14.3033 | 14.8788 | 11.072 | 0.0002 | -0.0024 | 0.0008 | 0.0044 | 0.0007 | -0.0003 | 0.0106 | -0.004 | -0.0073 | -360.2204 | 17.4254 | -360.4973 | 17.6697 | -360.842 | 18.1604 | -360.8543 | 17.5753 | -352.6475 | 18.7497 | -352.7152 | 16.8628
12:27 | 4008 | 39.5029 | 201.6348 | 448.7034 | 454.9599 | -16.7145 | -42.0396 | 10.3974 | 7.355 | 1.602 | 0.176 | 2.8493 | -1.1825 | 11.0627 | 3.984 | 0.6121 | 0.6564 | 0.9605 | 0.7374 | -129.5839 | -1.2765 | 5.4407 | 1.6236 | -3.1738 | -1.5659 | 4.3579 |  | 2.8258 | -0.0522 | 4.0124 | 3.3642 | 3.339 | 1.0681 | 10.7533 | 14.2613 | 14.8695 | 11.1121 | -0.0003 | -0.0026 | 0.0005 | 0.0036 | 0.0005 | -0.0007 | 0.0239 | -0.0173 | -0.0027 | -360.1034 | 17.372 | -360.4389 | 17.6492 | -360.8635 | 18.1933 | -360.8174 | 17.5568 | -352.6136 | 18.6881 | -352.6537 | 16.8607
12:27 | 4009 | 39.5556 | 201.6297 | 448.6712 | 454.9999 | -16.6491 | -42.1411 | 10.407 | 7.3719 | 1.5567 | 0.0472 | 2.8403 | -1.1792 | 11.0114 | 3.9544 | 0.6128 | 0.6551 | 0.96 | 0.7365 | -129.6093 | -1.2903 | 5.473 | 1.6083 | -3.2143 | -1.5873 | 4.2956 |  | 2.7674 | -0.0816 | 4.0124 | 3.3633 | 3.3433 | 1.068 | 10.7624 | 14.2883 | 14.8295 | 11.0915 | -0.0001 | -0.0022 | 0.0008 | 0.0042 | 0.0007 | 0 | 0.0069 | -0.0194 | -0.0046 | -360.1927 | 17.3823 | -360.4142 | 17.6081 | -360.7343 | 18.1522 | -360.8297 | 17.5773 | -352.6198 | 18.7087 | -352.6136 | 16.8135
12:27 | 4010 | 39.5541 | 201.7498 | 448.7384 | 455.0498 | -16.6839 | -42.1395 | 10.3775 | 7.3971 | 1.5594 | 0.1868 | 2.8269 | -1.0804 | 11.0502 | 4.1143 | 0.6144 | 0.6546 | 0.9573 | 0.7361 | -129.6274 | -1.2671 | 5.4309 | 1.6786 | -3.2108 | -1.6407 | 4.3048 |  | 2.842 | -0.071 | 4.0114 | 3.3651 | 3.3391 | 1.0679 | 10.7568 | 14.2416 | 14.8321 | 11.058 | 0 | -0.0032 | 0.0007 | 0.0037 | 0.001 | -0.0006 | 0.0242 | -0.0089 | 0.0008 | -360.1465 | 17.4028 | -360.5312 | 17.6697 | -360.8604 | 18.1666 | -360.8174 | 17.5588 | -352.6352 | 18.721 | -352.6998 | 16.8628
12:27 | 4011 | 39.5454 | 201.6531 | 448.7207 | 455.0104 | -16.7173 | -41.9513 | 10.3685 | 7.436 | 1.5413 | 0.1542 | 2.9906 | -1.1686 | 10.9493 | 3.9801 | 0.6146 | 0.6544 | 0.9613 | 0.7372 | -129.64 | -1.2733 | 5.4527 | 1.7013 | -3.1847 | -1.6005 | 4.2668 |  | 2.8719 | -0.0442 | 4.0137 | 3.3658 | 3.3404 | 1.0682 | 10.7199 | 14.2505 | 14.8098 | 11.0393 | -0.0001 | -0.0032 | 0.0012 | 0.0038 | 0.0007 | -0.0001 | 0.0055 | 0.0026 | 0.0146 | -360.1988 | 17.3987 | -360.4604 | 17.6615 | -360.8512 | 18.2015 | -360.885 | 17.5917 | -352.6629 | 18.7148 | -352.6413 | 16.8525
12:27 | 4012 | 39.5166 | 201.6743 | 448.7155 | 454.9965 | -16.6404 | -42.0363 | 10.4198 | 7.4766 | 1.5743 | 0.1594 | 2.9048 | -1.1879 | 10.9359 | 3.9778 | 0.6139 | 0.6534 | 0.9609 | 0.736 | -129.5602 | -1.2658 | 5.4101 | 1.7684 | -3.1771 | -1.6129 | 4.3004 |  | 2.8219 | 0.0084 | 4.0106 | 3.3626 | 3.3407 | 1.068 | 10.722 | 14.2707 | 14.81 | 11.0807 | -0.0001 | -0.0025 | 0.0005 | 0.0034 | 0.0016 | -0.0004 | 0.0051 | -0.0124 | 0.0025 | -360.1927 | 17.4233 | -360.4912 | 17.6369 | -360.8204 | 18.1728 | -360.842 | 17.5937 | -352.6937 | 18.7456 | -352.7121 | 16.8423
12:27 | 4013 | 39.5828 | 201.6602 | 448.7074 | 455.0531 | -16.5905 | -41.9143 | 10.5307 | 7.4614 | 1.5293 | 0.0473 | 2.9213 | -1.3417 | 10.9359 | 3.9804 | 0.6146 | 0.655 | 0.9635 | 0.7353 | -129.4651 | -1.1715 | 5.4795 | 1.8497 | -3.3292 | -1.6217 | 4.272 |  | 2.8542 | 0.0298 | 4.0128 | 3.3655 | 3.3403 | 1.0678 | 10.7325 | 14.2637 | 14.826 | 11.0912 | -0.0004 | -0.0026 | 0.0007 | 0.0037 | 0.0008 | -0.0002 | -0.0006 | -0.0218 | -0.035 | -360.1065 | 17.3823 | -360.4696 | 17.6492 | -360.8174 | 18.1563 | -360.842 | 17.5527 | -352.6044 | 18.7189 | -352.666 | 16.8484
12:27 | 4014 | 39.5634 | 201.7529 | 448.7269 | 455.0542 | -16.6414 | -41.9844 | 10.3798 | 7.3771 | 1.4522 | -0.0274 | 2.9173 | -1.2722 | 10.9435 | 3.856 | 0.6129 | 0.6516 | 0.9574 | 0.7349 | -129.5981 | -1.1536 | 5.3558 | 1.806 | -3.2463 | -1.496 | 4.2697 |  | 2.7755 | 0.0477 | 4.0117 | 3.3598 | 3.3417 | 1.0685 | 10.7371 | 14.2278 | 14.7957 | 11.067 | 0.0006 | -0.0024 | 0.0005 | 0.0035 | 0.0007 | -0.0001 | 0.0089 | -0.0164 | 0.0024 | -360.1311 | 17.3617 | -360.4019 | 17.6163 | -360.762 | 18.1563 | -360.8358 | 17.5753 | -352.6352 | 18.6984 | -352.6013 | 16.8217
12:27 | 4015 | 39.5884 | 201.6477 | 448.6864 | 455.0126 | -16.6525 | -42.0272 | 10.4029 | 7.4087 | 1.4874 | -0.0086 | 2.8667 | -1.2728 | 10.9664 | 3.9046 | 0.6146 | 0.6528 | 0.9599 | 0.7349 | -129.6397 | -1.2152 | 5.3934 | 1.8156 | -3.2248 | -1.5254 | 4.3332 |  | 2.853 | 0.0761 | 4.013 | 3.3646 | 3.3389 | 1.0682 | 10.7153 | 14.2459 | 14.817 | 11.0519 | 0 | -0.003 | 0.0006 | 0.0037 | 0.0006 | -0.0005 | 0.0023 | -0.012 | 0.0016 | -360.1496 | 17.4151 | -360.4696 | 17.6451 | -360.8081 | 18.1461 | -360.8204 | 17.5629 | -352.6321 | 18.7312 | -352.6444 | 16.8217
12:27 | 4016 | 39.5406 | 201.635 | 448.6924 | 455.1005 | -16.6755 | -41.9597 | 10.3776 | 7.3642 | 1.4741 | -0.0956 | 2.8559 | -1.2182 | 10.9265 | 3.8774 | 0.6142 | 0.6537 | 0.9578 | 0.7354 | -129.6664 | -1.2128 | 5.3967 | 1.7952 | -3.257 | -1.5102 | 4.3034 |  | 2.7635 | 0.0234 | 4.013 | 3.3626 | 3.3391 | 1.0684 | 10.7533 | 14.244 | 14.858 | 11.0601 | -0.0005 | -0.0028 | 0.0008 | 0.0043 | 0.0007 | 0 | 0.0168 | -0.0072 | -0.0006 | -360.1588 | 17.4048 | -360.5035 | 17.6636 | -360.845 | 18.1953 | -360.882 | 17.5773 | -352.6044 | 18.7148 | -352.6721 | 16.8525
12:27 | 4017 | 39.5593 | 201.6405 | 448.6548 | 455.0635 | -16.6977 | -42.0685 | 10.3999 | 7.3217 | 1.4555 | -0.132 | 2.8437 | -1.1833 | 10.8514 | 3.9144 | 0.6123 | 0.6576 | 0.9611 | 0.7367 | -129.6379 | -1.1653 | 5.5006 | 1.6144 | -3.2953 | -1.5513 | 4.2105 |  | 2.843 | 0.0899 | 4.0123 | 3.3651 | 3.3353 | 1.0688 | 10.7452 | 14.2705 | 14.8321 | 11.0753 | -0.0003 | -0.0026 | 0.0007 | 0.0038 | 0.0005 | -0.0009 | -0.0089 | -0.0091 | -0.0142 | -360.2142 | 17.4131 | -360.4573 | 17.6553 | -360.845 | 18.181 | -360.9004 | 17.6061 | -352.6844 | 18.7292 | -352.6752 | 16.8525
12:27 | 4018 | 39.5604 | 201.5783 | 448.7508 | 455.1266 | -16.68 | -41.994 | 10.3311 | 7.3062 | 1.62 | -0.0958 | 2.8627 | -1.2072 | 10.8466 | 3.8669 | 0.6142 | 0.6537 | 0.9581 | 0.7369 | -129.5734 | -1.1873 | 5.5474 | 1.685 | -3.2765 | -1.5204 | 4.2983 |  | 2.8525 | 0.0306 | 4.0116 | 3.3629 | 3.3373 | 1.0675 | 10.7648 | 14.2557 | 14.8648 | 11.0771 | -0.0001 | -0.0029 | 0.0009 | 0.0044 | 0.0007 | -0.0004 | 0.0035 | -0.0167 | -0.022 | -360.1619 | 17.4007 | -360.4696 | 17.6594 | -360.8204 | 18.181 | -360.8358 | 17.5835 | -352.666 | 18.7312 | -352.6875 | 16.8607
12:27 | 4019 | 39.6126 | 201.5946 | 448.7002 | 455.0874 | -16.6421 | -41.8901 | 10.4412 | 7.3245 | 1.7403 | 0.0541 | 2.9486 | -1.1644 | 10.8671 | 4.0101 | 0.6135 | 0.6573 | 0.9629 | 0.7379 | -129.5119 | -1.1149 | 5.5443 | 1.7247 | -3.2444 | -1.6074 | 4.2374 |  | 2.8214 | -0.0323 | 4.0131 | 3.3614 | 3.3403 | 1.068 | 10.7578 | 14.2836 | 14.8935 | 11.1161 | 0.0003 | -0.0029 | 0.0006 | 0.0039 | 0.001 | -0.0007 | 0.0122 | -0.0125 | 0.0001 | -360.1527 | 17.3761 | -360.4327 | 17.6369 | -360.802 | 18.1933 | -360.845 | 17.5753 | -352.6413 | 18.7025 | -352.6383 | 16.8361
12:27 | 4020 | 39.4902 | 201.4711 | 448.6815 | 455.0117 | -16.5844 | -41.9615 | 10.4162 | 7.2898 | 1.6401 | -0.0805 | 2.8824 | -1.0614 | 10.9983 | 3.976 | 0.6132 | 0.6542 | 0.9603 | 0.7343 | -129.5953 | -1.0518 | 5.4643 | 1.8047 | -3.2617 | -1.5938 | 4.2946 |  | 2.8055 | 0.066 | 4.0138 | 3.3608 | 3.3379 | 1.0677 | 10.7326 | 14.2575 | 14.8517 | 11.0403 | -0.0003 | -0.0029 | 0.0004 | 0.0034 | 0.0003 | -0.001 | 0.0012 | -0.0131 | -0.026 | -360.1619 | 17.3843 | -360.4296 | 17.6286 | -360.7527 | 18.1871 | -360.8081 | 17.5794 | -352.6106 | 18.7107 | -352.629 | 16.8279
12:27 | 4021 | 39.5394 | 201.465 | 448.6079 | 455.1014 | -16.665 | -42.0702 | 10.3114 | 7.3513 | 1.5671 | -0.0833 | 2.8255 | -1.175 | 10.9185 | 3.9959 | 0.6144 | 0.6542 | 0.9588 | 0.7368 | -129.6884 | -1.2299 | 5.3602 | 1.824 | -3.2405 | -1.652 | 4.3574 |  | 2.8075 | 0.1341 | 4.0147 | 3.3639 | 3.3393 | 1.0688 | 10.7405 | 14.2545 | 14.8229 | 11.076 | -0.0003 | -0.0024 | 0.0007 | 0.0038 | 0.0009 | -0.0007 | -0.0005 | 0.0025 | -0.0117 | -360.1804 | 17.3905 | -360.4512 | 17.6553 | -360.8112 | 18.1851 | -360.8358 | 17.5732 | -352.6106 | 18.7066 | -352.6598 | 16.8381
12:27 | 4022 | 39.5797 | 201.56 | 448.6863 | 455.1429 | -16.7307 | -42.0636 | 10.3074 | 7.3629 | 1.5383 | -0.0031 | 2.8497 | -1.1477 | 10.8667 | 4.0892 | 0.6144 | 0.6575 | 0.9634 | 0.7355 | -129.6466 | -1.1264 | 5.4364 | 1.6444 | -3.25 | -1.623 | 4.3052 |  | 2.8318 | 0.0369 | 4.013 | 3.3643 | 3.3381 | 1.0682 | 10.7347 | 14.2836 | 14.8471 | 11.0756 | 0 | -0.003 | 0.0006 | 0.0039 | 0.0008 | 0.0003 | 0.0068 | 0.0019 | -0.0233 | -360.1865 | 17.4069 | -360.4604 | 17.6553 | -360.8389 | 18.2077 | -360.8635 | 17.5855 | -352.6444 | 18.7189 | -352.6413 | 16.8423
12:27 | 4023 | 39.5871 | 201.6333 | 448.7622 | 455.1494 | -16.733 | -42.0117 | 10.2958 | 7.2901 | 1.4608 | -0.0683 | 2.8274 | -1.2658 | 10.845 | 4.1318 | 0.6134 | 0.6517 | 0.9615 | 0.7336 | -129.5867 | -1.1276 | 5.4661 | 1.6933 | -3.28 | -1.5664 | 4.3026 |  | 2.8232 | 0.0709 | 4.014 | 3.3665 | 3.3402 | 1.0694 | 10.7719 | 14.2391 | 14.8283 | 11.0678 | 0.0002 | -0.0032 | 0.0006 | 0.0038 | 0.0007 | -0.001 | 0.0088 | -0.0062 | -0.0009 | -360.205 | 17.4131 | -360.4789 | 17.6718 | -360.845 | 18.22 | -360.8543 | 17.5855 | -352.666 | 18.7374 | -352.709 | 16.8505
12:27 | 4024 | 39.6155 | 201.6294 | 448.7648 | 455.1605 | -16.8352 | -41.9663 | 10.2629 | 7.2798 | 1.355 | 0.0741 | 2.8619 | -1.1996 | 10.9629 | 4.1151 | 0.6132 | 0.6518 | 0.9591 | 0.7357 | -129.5818 | -1.0613 | 5.5134 | 1.6448 | -3.2238 | -1.6061 | 4.293 |  | 2.8617 | 0.1051 | 4.013 | 3.3645 | 3.3369 | 1.0697 | 10.7555 | 14.2466 | 14.8628 | 11.0558 | -0.0002 | -0.0028 | 0.0011 | 0.0042 | 0.0009 | 0.0003 | 0.0244 | -0.0024 | -0.0008 | -360.1711 | 17.3966 | -360.4819 | 17.6553 | -360.8266 | 18.2097 | -360.8635 | 17.5753 | -352.6629 | 18.7292 | -352.6752 | 16.8546
12:27 | 4025 | 39.6289 | 201.6818 | 448.7659 | 455.1501 | -16.8113 | -41.9576 | 10.3257 | 7.2956 | 1.3961 | -0.1458 | 2.9009 | -1.1235 | 10.9742 | 4.0714 | 0.6129 | 0.6509 | 0.9601 | 0.7365 | -129.64 | -1.1718 | 5.4993 | 1.7345 | -3.2426 | -1.5784 | 4.3293 |  | 2.8802 | 0.0401 | 4.0126 | 3.3635 | 3.3376 | 1.0661 | 10.7452 | 14.2764 | 14.8505 | 11.0807 | -0.0007 | -0.0031 | 0.0008 | 0.0036 | 0.001 | -0.0006 | -0.0079 | -0.0131 | -0.0209 | -360.1496 | 17.3864 | -360.4235 | 17.6492 | -360.7804 | 18.1851 | -360.8327 | 17.5671 | -352.6136 | 18.7148 | -352.6444 | 16.8423
12:27 | 4026 | 39.5924 | 201.6209 | 448.6769 | 455.0969 | -16.835 | -41.9198 | 10.3863 | 7.3249 | 1.3922 | -0.0831 | 2.8799 | -1.1103 | 10.9185 | 4.1156 | 0.6138 | 0.6505 | 0.9591 | 0.7371 | -129.5649 | -1.131 | 5.4429 | 1.8416 | -3.2671 | -1.5305 | 4.2925 |  | 2.8682 | -0.0281 | 4.0128 | 3.3641 | 3.341 | 1.066 | 10.7556 | 14.2581 | 14.8676 | 11.0793 | 0 | -0.0026 | 0.0011 | 0.0041 | 0.0008 | -0.0004 | 0.0092 | -0.012 | -0.0112 | -360.1527 | 17.374 | -360.4266 | 17.6389 | -360.7958 | 18.1892 | -360.8297 | 17.5506 | -352.6075 | 18.7045 | -352.6229 | 16.8402
12:27 | 4027 | 39.6146 | 201.7271 | 448.811 | 455.1279 | -16.7889 | -41.8477 | 10.4357 | 7.2783 | 1.4102 | -0.0145 | 2.9805 | -1.1281 | 10.937 | 3.9815 | 0.6133 | 0.6488 | 0.96 | 0.7349 | -129.6196 | -1.1158 | 5.4826 | 1.8221 | -3.2385 | -1.6296 | 4.3855 |  | 2.8643 | 0.0476 | 4.0131 | 3.3666 | 3.3406 | 1.068 | 10.7416 | 14.2674 | 14.889 | 11.0883 | 0.0003 | -0.0032 | 0.0006 | 0.0039 | 0.0005 | -0.0008 | 0.0068 | 0.0001 | -0.0042 | -360.1619 | 17.3864 | -360.4266 | 17.6225 | -360.7835 | 18.1912 | -360.8297 | 17.5588 | -352.629 | 18.6984 | -352.5952 | 16.8217
12:27 | 4028 | 39.6209 | 201.6518 | 448.7694 | 455.168 | -16.8267 | -41.8368 | 10.4685 | 7.3935 | 1.3991 | 0.0157 | 2.9683 | -1.1783 | 10.8715 | 3.9342 | 0.6125 | 0.6522 | 0.9625 | 0.7353 | -129.6021 | -1.1421 | 5.4191 | 1.8987 | -3.2521 | -1.6086 | 4.2943 |  | 2.9162 | 0.0526 | 4.0132 | 3.3624 | 3.3386 | 1.0672 | 10.7718 | 14.2627 | 14.8546 | 11.0955 | 0 | -0.0028 | 0.0005 | 0.0035 | 0.0009 | -0.0009 | 0.0086 | -0.0039 | -0.0023 | -360.1958 | 17.409 | -360.5096 | 17.6636 | -360.8297 | 18.2056 | -360.8327 | 17.5773 | -352.6352 | 18.7415 | -352.6783 | 16.8525
12:27 | 4029 | 39.6752 | 201.5521 | 448.7359 | 455.1593 | -16.8931 | -41.8933 | 10.4399 | 7.282 | 1.3566 | -0.0033 | 2.966 | -1.1821 | 10.9609 | 3.8778 | 0.614 | 0.6541 | 0.9628 | 0.7373 | -129.5951 | -1.1295 | 5.3727 | 1.8305 | -3.2027 | -1.6107 | 4.2927 |  | 2.8797 | 0.0245 | 4.0118 | 3.3622 | 3.3398 | 1.067 | 10.7141 | 14.2274 | 14.8041 | 11.0624 | -0.0002 | -0.0027 | 0.0005 | 0.0039 | 0.0005 | -0.0005 | -0.0055 | -0.0188 | 0.011 | -360.1681 | 17.3966 | -360.4389 | 17.6615 | -360.882 | 18.2323 | -360.8666 | 17.5855 | -352.6413 | 18.7169 | -352.6783 | 16.8628
12:27 | 4030 | 39.6243 | 201.6427 | 448.7161 | 455.101 | -16.856 | -41.8617 | 10.4432 | 7.2845 | 1.4183 | 0.0394 | 2.918 | -1.2327 | 10.9093 | 3.9068 | 0.6129 | 0.6507 | 0.9616 | 0.7355 | -129.6467 | -1.1049 | 5.368 | 1.9275 | -3.2406 | -1.5855 | 4.2826 |  | 2.9284 | 0.1553 | 4.0121 | 3.3641 | 3.3425 | 1.0679 | 10.7474 | 14.2501 | 14.8427 | 11.071 | -0.0001 | -0.0025 | 0.0005 | 0.0031 | 0.0009 | -0.0005 | 0.0185 | -0.0122 | -0.0087 | -360.2111 | 17.4028 | -360.4512 | 17.641 | -360.8143 | 18.2015 | -360.8758 | 17.5732 | -352.6598 | 18.7374 | -352.666 | 16.8402
12:27 | 4031 | 39.6271 | 201.6764 | 448.6402 | 455.1117 | -16.7594 | -41.8844 | 10.4314 | 7.2903 | 1.4683 | -0.0074 | 3.0224 | -1.1616 | 10.9328 | 3.9226 | 0.6141 | 0.6533 | 0.9597 | 0.7368 | -129.685 | -1.152 | 5.2409 | 1.8557 | -3.1957 | -1.5406 | 4.3234 |  | 2.9263 | 0.0922 | 4.0127 | 3.3666 | 3.3384 | 1.0673 | 10.7186 | 14.267 | 14.8395 | 11.0779 | 0.0002 | -0.0032 | 0.0008 | 0.0037 | 0.0003 | -0.0006 | 0.0202 | -0.0063 | 0.0019 | -360.1558 | 17.3782 | -360.4666 | 17.6533 | -360.7989 | 18.1728 | -360.8204 | 17.5506 | -352.626 | 18.7333 | -352.669 | 16.8505
12:27 | 4032 | 39.6542 | 201.6265 | 448.6817 | 455.0756 | -16.848 | -41.8925 | 10.3682 | 7.2735 | 1.4863 | -0.0767 | 2.9474 | -1.2838 | 10.9171 | 3.8561 | 0.6138 | 0.654 | 0.9615 | 0.7384 | -129.5791 | -1.2026 | 5.4221 | 1.9009 | -3.1474 | -1.5697 | 4.384 |  | 2.8607 | -0.0039 | 4.0124 | 3.365 | 3.3392 | 1.0665 | 10.7416 | 14.2674 | 14.8196 | 11.0652 | 0.0001 | -0.0027 | 0.0012 | 0.0044 | 0.0011 | -0.0006 | -0.0018 | -0.0102 | 0.004 | -360.165 | 17.3597 | -360.4296 | 17.641 | -360.8143 | 18.2097 | -360.8358 | 17.5424 | -352.5644 | 18.6963 | -352.6198 | 16.8443
12:27 | 4033 | 39.6071 | 201.685 | 448.7481 | 455.2219 | -16.8213 | -41.9764 | 10.34 | 7.1486 | 1.4561 | -0.0801 | 2.8812 | -1.3466 | 10.8457 | 3.8284 | 0.6128 | 0.6548 | 0.9635 | 0.7366 | -129.5349 | -1.1179 | 5.3703 | 1.804 | -3.2615 | -1.4944 | 4.2945 |  | 2.8828 | -0.0582 | 4.0123 | 3.3628 | 3.3406 | 1.066 | 10.7508 | 14.2711 | 14.8537 | 11.0796 | 0 | -0.0025 | 0.0008 | 0.004 | 0.0008 | 0 | 0.0006 | -0.0026 | -0.007 | -360.1835 | 17.3966 | -360.4481 | 17.6328 | -360.7989 | 18.1974 | -360.8881 | 17.5896 | -352.6813 | 18.7312 | -352.6229 | 16.8197
12:27 | 4034 | 39.5456 | 201.5949 | 448.7081 | 455.0871 | -16.8156 | -41.964 | 10.3209 | 7.1762 | 1.3768 | -0.0893 | 2.7633 | -1.2577 | 10.9433 | 3.8402 | 0.6119 | 0.6527 | 0.9596 | 0.7367 | -129.6183 | -1.1204 | 5.4366 | 1.8066 | -3.2007 | -1.6767 | 4.2619 |  | 2.851 | -0.0603 | 4.0132 | 3.3663 | 3.3422 | 1.0667 | 10.7476 | 14.238 | 14.8337 | 11.0779 | -0.0001 | -0.0026 | 0.0005 | 0.0036 | 0.0007 | -0.0006 | -0.0015 | -0.0229 | -0.0191 | -360.1711 | 17.4254 | -360.5219 | 17.6923 | -360.8727 | 18.2015 | -360.8174 | 17.5588 | -352.6598 | 18.7477 | -352.7183 | 16.8792
12:27 | 4035 | 39.6346 | 201.6105 | 448.7009 | 455.1379 | -16.8286 | -41.8535 | 10.3834 | 7.2232 | 1.3698 | -0.0802 | 2.8568 | -1.2503 | 10.9747 | 3.9178 | 0.6138 | 0.6546 | 0.9599 | 0.737 | -129.6552 | -1.0962 | 5.39 | 1.7919 | -3.2512 | -1.6727 | 4.2461 |  | 2.9568 | -0.0376 | 4.013 | 3.3662 | 3.3389 | 1.0673 | 10.737 | 14.2223 | 14.8673 | 11.0663 | 0.0003 | -0.0026 | 0.001 | 0.0035 | 0.0011 | -0.0001 | 0.0105 | -0.0073 | -0.0075 | -360.205 | 17.3823 | -360.4081 | 17.6512 | -360.8481 | 18.2282 | -360.8974 | 17.5794 | -352.6537 | 18.7251 | -352.6383 | 16.8402
12:27 | 4036 | 39.591 | 201.5359 | 448.634 | 455.1217 | -16.6937 | -41.7991 | 10.4442 | 7.2401 | 1.4026 | -0.0434 | 2.8262 | -1.2965 | 10.9283 | 3.9189 | 0.615 | 0.6557 | 0.9592 | 0.7372 | -129.647 | -1.1468 | 5.4493 | 1.8926 | -3.2627 | -1.6082 | 4.3149 |  | 2.8948 | 0.1087 | 4.0132 | 3.364 | 3.34 | 1.0684 | 10.7477 | 14.2262 | 14.7853 | 11.0902 | 0 | -0.0033 | 0.0006 | 0.0034 | 0.0011 | -0.0007 | 0.005 | 0.0019 | 0.0014 | -360.1773 | 17.4213 | -360.4573 | 17.6369 | -360.802 | 18.1666 | -360.8235 | 17.5691 | -352.6537 | 18.7477 | -352.6629 | 16.8258
12:27 | 4037 | 39.6515 | 201.5902 | 448.6174 | 455.0559 | -16.6984 | -41.7178 | 10.4896 | 7.2297 | 1.4944 | -0.0519 | 2.8636 | -1.239 | 11.0687 | 3.8872 | 0.612 | 0.6586 | 0.9604 | 0.7371 | -129.6451 | -1.1262 | 5.4532 | 1.8669 | -3.2027 | -1.4773 | 4.2931 |  | 2.9777 | 0.0597 | 4.014 | 3.3613 | 3.3388 | 1.0667 | 10.6899 | 14.2087 | 14.7901 | 11.0501 | -0.0004 | -0.0029 | 0.0008 | 0.0037 | 0.0006 | -0.0007 | 0.0036 | -0.0012 | -0.0197 | -360.0758 | 17.3802 | -360.445 | 17.6594 | -360.8266 | 18.1994 | -360.8081 | 17.5239 | -352.546 | 18.7148 | -352.6352 | 16.8484
12:27 | 4038 | 39.6453 | 201.5672 | 448.6735 | 455.0755 | -16.8312 | -41.7451 | 10.465 | 7.1868 | 1.4374 | 0.0009 | 2.796 | -1.2028 | 11.037 | 3.918 | 0.6138 | 0.656 | 0.962 | 0.7385 | -129.665 | -1.1723 | 5.3427 | 1.8882 | -3.205 | -1.53 | 4.348 |  | 2.9135 | 0.0273 | 4.0124 | 3.3655 | 3.3401 | 1.0681 | 10.7336 | 14.2649 | 14.8389 | 11.0807 | -0.0002 | -0.0027 | 0.0013 | 0.0044 | 0.0009 | -0.0002 | 0.0164 | -0.0053 | -0.0032 | -360.1835 | 17.3843 | -360.4327 | 17.6204 | -360.7558 | 18.1871 | -360.8727 | 17.5855 | -352.6598 | 18.7148 | -352.629 | 16.8074
12:27 | 4039 | 39.7043 | 201.6514 | 448.7836 | 455.1489 | -16.9079 | -41.8204 | 10.4084 | 7.0867 | 1.4026 | 0.1064 | 2.7909 | -1.1747 | 11.0363 | 3.9707 | 0.6137 | 0.6522 | 0.9579 | 0.7358 | -129.6353 | -1.1144 | 5.2902 | 1.822 | -3.236 | -1.6218 | 4.3316 |  | 2.8303 | 0.0684 | 4.013 | 3.3672 | 3.3387 | 1.0676 | 10.7279 | 14.2646 | 14.8542 | 11.1161 | -0.0001 | -0.0032 | 0.0004 | 0.0038 | 0.0006 | -0.0007 | -0.0057 | -0.022 | -0.0216 | -360.2019 | 17.4254 | -360.5127 | 17.6841 | -360.8481 | 18.1707 | -360.8081 | 17.5424 | -352.6475 | 18.762 | -352.7152 | 16.8566
12:27 | 4040 | 39.6882 | 201.6029 | 448.7223 | 455.1417 | -16.9341 | -41.798 | 10.3572 | 7.1517 | 1.3686 | -0.0082 | 2.7259 | -1.1469 | 10.9908 | 3.9921 | 0.6142 | 0.6546 | 0.9588 | 0.7368 | -129.6208 | -0.979 | 5.3116 | 1.8887 | -3.2074 | -1.5896 | 4.3356 |  | 2.8519 | -0.0077 | 4.0119 | 3.3684 | 3.341 | 1.0684 | 10.737 | 14.2397 | 14.8267 | 11.0836 | 0.0006 | -0.0029 | 0.0012 | 0.0041 | 0.0006 | -0.0003 | 0.004 | 0.0033 | -0.0239 | -360.1835 | 17.3987 | -360.4666 | 17.6759 | -360.8789 | 18.2261 | -360.9004 | 17.565 | -352.666 | 18.7312 | -352.6321 | 16.8607
12:27 | 4041 | 39.8216 | 201.6774 | 448.7871 | 455.2458 | -16.8905 | -41.7649 | 10.3938 | 7.2012 | 1.4865 | -0.0548 | 2.7956 | -1.1504 | 11.066 | 3.9745 | 0.613 | 0.6548 | 0.965 | 0.7371 | -129.6402 | -1.1013 | 5.3291 | 1.7754 | -3.1528 | -1.7808 | 4.4087 |  | 2.8076 | 0.0131 | 4.0114 | 3.3644 | 3.3381 | 1.0681 | 10.7822 | 14.2615 | 14.8706 | 11.0713 | -0.0002 | -0.0028 | 0.001 | 0.0037 | 0.0006 | -0.0006 | 0.0212 | -0.0025 | -0.02 | -360.2327 | 17.4274 | -360.4727 | 17.6369 | -360.805 | 18.1912 | -360.882 | 17.5978 | -352.706 | 18.7641 | -352.6875 | 16.834
12:27 | 4042 | 39.7155 | 201.6444 | 448.6987 | 455.2023 | -16.9139 | -41.6552 | 10.3698 | 7.2411 | 1.488 | -0.0499 | 2.854 | -1.0521 | 11.0595 | 3.9147 | 0.6112 | 0.6547 | 0.9604 | 0.7363 | -129.5629 | -1.1641 | 5.3343 | 1.8699 | -3.0647 | -1.5335 | 4.3299 |  | 2.8492 | -0.106 | 4.0113 | 3.3644 | 3.3377 | 1.0674 | 10.7672 | 14.2579 | 14.8376 | 11.097 | -0.0007 | -0.0027 | 0.0003 | 0.0033 | 0.0005 | -0.0002 | 0.0175 | -0.0037 | -0.0083 | -360.125 | 17.4028 | -360.4973 | 17.68 | -360.8604 | 18.181 | -360.8174 | 17.5383 | -352.6106 | 18.7415 | -352.6967 | 16.8731
12:27 | 4043 | 39.7473 | 201.7265 | 448.8739 | 455.2229 | -16.8964 | -41.6596 | 10.4143 | 7.2531 | 1.5182 | 0.1041 | 2.8386 | -1.1802 | 11.0087 | 3.9216 | 0.6133 | 0.651 | 0.9559 | 0.7381 | -129.5556 | -1.1122 | 5.3935 | 1.8066 | -3.0722 | -1.5711 | 4.3383 |  | 2.8174 | -0.0546 | 4.0122 | 3.364 | 3.3411 | 1.0686 | 10.7624 | 14.2594 | 14.8468 | 11.08 | 0.0005 | -0.0026 | 0.0014 | 0.0043 | 0.0008 | -0.0009 | 0.0165 | -0.0016 | -0.0123 | -360.1342 | 17.3474 | -360.3619 | 17.6225 | -360.7589 | 18.1892 | -360.8727 | 17.565 | -352.6106 | 18.6963 | -352.586 | 16.8156
12:27 | 4044 | 39.7621 | 201.6524 | 448.8647 | 455.1538 | -16.9394 | -41.8405 | 10.3092 | 7.2586 | 1.5147 | 0.1414 | 2.787 | -1.1485 | 11.1178 | 4.0015 | 0.6131 | 0.6565 | 0.9625 | 0.7369 | -129.5606 | -1.0712 | 5.5091 | 1.8799 | -3.1042 | -1.6148 | 4.3897 |  | 2.8933 | -0.0521 | 4.0128 | 3.3677 | 3.3404 | 1.0689 | 10.758 | 14.26 | 14.8382 | 11.0826 | -0.0001 | -0.0033 | 0.0004 | 0.0034 | 0.0008 | -0.0001 | 0.0059 | -0.0042 | -0.024 | -360.1711 | 17.4172 | -360.4727 | 17.6389 | -360.7589 | 18.1502 | -360.7958 | 17.5527 | -352.6413 | 18.7436 | -352.6752 | 16.834
12:27 | 4045 | 39.7634 | 201.7278 | 448.8587 | 455.2346 | -16.804 | -41.8278 | 10.3894 | 7.3805 | 1.5535 | 0.169 | 2.8268 | -1.2082 | 11.0495 | 3.9686 | 0.6145 | 0.6507 | 0.9606 | 0.738 | -129.6278 | -1.1737 | 5.5394 | 1.8353 | -3.1945 | -1.5986 | 4.3558 |  | 2.7588 | 0.0218 | 4.011 | 3.3648 | 3.339 | 1.0682 | 10.7395 | 14.2299 | 14.8426 | 11.0757 | -0.0004 | -0.003 | 0.0003 | 0.0037 | 0.0012 | -0.0007 | 0.02 | -0.0113 | 0.0125 | -360.1435 | 17.3699 | -360.4419 | 17.6718 | -360.845 | 18.2118 | -360.842 | 17.5445 | -352.5829 | 18.7045 | -352.6321 | 16.8587
12:27 | 4046 | 39.8116 | 201.6487 | 448.9255 | 455.2829 | -16.8362 | -41.8224 | 10.3467 | 7.3223 | 1.5275 | 0.0946 | 2.8176 | -1.0849 | 11.0758 | 4.0452 | 0.6139 | 0.654 | 0.9626 | 0.7355 | -129.6126 | -1.176 | 5.5129 | 1.765 | -3.1424 | -1.5249 | 4.339 |  | 2.8814 | 0.0357 | 4.0114 | 3.3685 | 3.3389 | 1.0681 | 10.7255 | 14.2509 | 14.8593 | 11.0497 | -0.001 | -0.0032 | 0.0012 | 0.0043 | 0.0009 | -0.0001 | 0.007 | -0.0175 | 0.0021 | -360.2204 | 17.409 | -360.4481 | 17.643 | -360.8081 | 18.2179 | -360.8943 | 17.6081 | -352.7121 | 18.7395 | -352.6721 | 16.8176
12:27 | 4047 | 39.8007 | 201.7068 | 448.8626 | 455.2766 | -16.8472 | -41.9286 | 10.3752 | 7.3652 | 1.5051 | 0.131 | 2.7354 | -1.2186 | 11.1183 | 4.0637 | 0.614 | 0.6542 | 0.9596 | 0.7363 | -129.55 | -1.027 | 5.4224 | 1.7611 | -3.1722 | -1.6348 | 4.3074 |  | 2.8624 | 0.0694 | 4.0125 | 3.368 | 3.3415 | 1.0684 | 10.7244 | 14.2496 | 14.8395 | 11.0952 | 0 | -0.0028 | 0.0006 | 0.0037 | 0.0008 | -0.0008 | 0.0111 | -0.0051 | -0.0205 | -360.1988 | 17.4254 | -360.5189 | 17.6861 | -360.8543 | 18.1974 | -360.8327 | 17.565 | -352.6844 | 18.76 | -352.7213 | 16.8731
12:27 | 4048 | 39.8169 | 201.5835 | 448.8486 | 455.1573 | -16.7862 | -41.8695 | 10.4951 | 7.3295 | 1.5022 | 0.0548 | 2.809 | -1.2629 | 11.1243 | 3.9878 | 0.6132 | 0.6535 | 0.9579 | 0.7381 | -129.6273 | -1.116 | 5.4024 | 1.7222 | -3.0986 | -1.538 | 4.3664 |  | 2.7401 | -0.0605 | 4.0102 | 3.3645 | 3.3371 | 1.0683 | 10.714 | 14.2394 | 14.8015 | 11.0843 | 0.0003 | -0.0031 | 0.0009 | 0.0041 | 0.001 | -0.0004 | 0.0008 | -0.009 | 0.0003 | -360.1496 | 17.3679 | -360.4266 | 17.6594 | -360.8481 | 18.2179 | -360.9035 | 17.5568 | -352.6321 | 18.7107 | -352.6167 | 16.8505
12:27 | 4049 | 39.8056 | 201.6595 | 448.8426 | 455.2666 | -16.8401 | -41.8363 | 10.4691 | 7.2953 | 1.4374 | 0.0061 | 2.7958 | -1.2723 | 11.0461 | 4.0366 | 0.6137 | 0.6586 | 0.9634 | 0.7377 | -129.6012 | -1.1054 | 5.4212 | 1.9118 | -3.0848 | -1.5516 | 4.372 |  | 2.7703 | -0.0818 | 4.0125 | 3.3623 | 3.3375 | 1.0675 | 10.7578 | 14.2664 | 14.8308 | 11.0753 | 0.0002 | -0.0028 | 0.0008 | 0.0038 | 0.0008 | -0.0001 | 0.0325 | -0.0083 | 0.0128 | -360.1865 | 17.3987 | -360.4142 | 17.6266 | -360.7558 | 18.1625 | -360.8266 | 17.5712 | -352.6383 | 18.723 | -352.6383 | 16.8074
12:27 | 4050 | 39.7037 | 201.6515 | 448.8836 | 455.2328 | -16.8168 | -41.8313 | 10.3677 | 7.3906 | 1.4587 | -0.0289 | 2.7817 | -1.3378 | 11.0134 | 3.886 | 0.613 | 0.6536 | 0.9627 | 0.7376 | -129.5949 | -1.1542 | 5.4274 | 1.822 | -3.0514 | -1.5112 | 4.4275 |  | 2.8404 | -0.1848 | 4.0122 | 3.3637 | 3.3359 | 1.0677 | 10.7601 | 14.2975 | 14.8615 | 11.0836 | -0.0005 | -0.0025 | 0.0003 | 0.0035 | 0.0008 | -0.0007 | 0.007 | -0.0192 | -0.0191 | -360.1158 | 17.3987 | -360.4819 | 17.68 | -360.8543 | 18.1851 | -360.7804 | 17.5321 | -352.5798 | 18.721 | -352.6752 | 16.8546
12:27 | 4051 | 39.7381 | 201.6005 | 448.8321 | 455.2512 | -16.8398 | -41.7594 | 10.4709 | 7.3523 | 1.4119 | 0.0383 | 2.7982 | -1.3439 | 11.0544 | 3.9367 | 0.6135 | 0.6529 | 0.9639 | 0.7361 | -129.5681 | -1.1233 | 5.3461 | 1.8089 | -3.1748 | -1.6651 | 4.3666 |  | 2.8728 | -0.0403 | 4.011 | 3.3608 | 3.34 | 1.0669 | 10.7545 | 14.2567 | 14.8651 | 11.0786 | -0.0001 | -0.003 | 0.0009 | 0.0036 | 0.0006 | -0.0003 | 0.0015 | -0.0019 | -0.0048 | -360.1588 | 17.3761 | -360.4173 | 17.6451 | -360.8235 | 18.2261 | -360.922 | 17.602 | -352.6413 | 18.6984 | -352.5983 | 16.8279
12:27 | 4052 | 39.8298 | 201.6971 | 448.8518 | 455.2777 | -16.869 | -41.7205 | 10.5971 | 7.4559 | 1.5108 | 0.0507 | 2.8651 | -1.3717 | 11.0394 | 3.9259 | 0.6139 | 0.6534 | 0.9607 | 0.7377 | -129.6732 | -1.2155 | 5.3503 | 1.8329 | -3.0694 | -1.555 | 4.4378 |  | 2.8742 | -0.0988 | 4.0124 | 3.3631 | 3.3348 | 1.0688 | 10.7648 | 14.2558 | 14.8775 | 11.1114 | 0.0003 | -0.0031 | 0.0003 | 0.0034 | 0.0012 | -0.0005 | -0.0047 | -0.0217 | -0.0241 | -360.2204 | 17.4418 | -360.5158 | 17.6779 | -360.8266 | 18.1953 | -360.8604 | 17.5835 | -352.6998 | 18.7723 | -352.6967 | 16.8587
12:27 | 4053 | 39.7133 | 201.6485 | 448.8326 | 455.3018 | -16.8843 | -41.5945 | 10.5239 | 7.4206 | 1.4658 | -0.0814 | 2.8668 | -1.3453 | 11.0593 | 3.9723 | 0.6145 | 0.6513 | 0.9624 | 0.7356 | -129.6412 | -1.1925 | 5.3854 | 1.8946 | -3.0556 | -1.5956 | 4.4396 |  | 2.8744 | -0.0395 | 4.012 | 3.3639 | 3.3394 | 1.0681 | 10.7418 | 14.2437 | 14.8153 | 11.0782 | 0.0001 | -0.0029 | 0.0003 | 0.0038 | 0.0002 | -0.0008 | 0.0193 | 0.002 | -0.0234 | -360.0881 | 17.372 | -360.4481 | 17.6779 | -360.8604 | 18.2138 | -360.8574 | 17.5527 | -352.5644 | 18.7169 | -352.6537 | 16.8648
12:27 | 4054 | 39.7546 | 201.7168 | 448.838 | 455.2293 | -16.8373 | -41.6563 | 10.574 | 7.4116 | 1.4812 | -0.0666 | 2.8916 | -1.2368 | 11.1116 | 4.0034 | 0.6132 | 0.6535 | 0.9631 | 0.7387 | -129.6055 | -1.2438 | 5.3749 | 1.8129 | -3.1261 | -1.4929 | 4.3121 |  | 2.9408 | 0.0337 | 4.0107 | 3.3603 | 3.3402 | 1.0671 | 10.7001 | 14.2253 | 14.7977 | 11.0306 | -0.0002 | -0.0025 | 0.001 | 0.0042 | 0.0007 | -0.0009 | 0.0055 | -0.0094 | -0.0061 | -360.165 | 17.3823 | -360.4204 | 17.6348 | -360.765 | 18.1851 | -360.8574 | 17.5609 | -352.6383 | 18.7045 | -352.6013 | 16.8238
12:27 | 4055 | 39.8309 | 201.6784 | 448.8241 | 455.1965 | -16.7049 | -41.6518 | 10.6608 | 7.3089 | 1.3521 | -0.0716 | 2.861 | -1.2384 | 11.0917 | 3.9901 | 0.6144 | 0.6539 | 0.9652 | 0.7378 | -129.6253 | -1.2216 | 5.3761 | 1.7452 | -3.1619 | -1.4972 | 4.3039 |  | 2.9186 | 0.0617 | 4.0098 | 3.3592 | 3.3381 | 1.0695 | 10.7382 | 14.2638 | 14.856 | 11.0562 | 0.0001 | -0.0022 | 0.0005 | 0.0036 | 0.0005 | -0.0005 | 0.0048 | -0.0104 | -0.0194 | -360.1496 | 17.409 | -360.4696 | 17.6697 | -360.8204 | 18.1625 | -360.8174 | 17.5383 | -352.589 | 18.7395 | -352.6721 | 16.8546
12:27 | 4056 | 39.7967 | 201.7356 | 448.8333 | 455.2077 | -16.8296 | -41.7636 | 10.6027 | 7.4065 | 1.5005 | -0.1751 | 2.8979 | -1.2185 | 11.1593 | 3.9641 | 0.6146 | 0.6567 | 0.9632 | 0.7393 | -129.5885 | -1.1643 | 5.4464 | 1.7704 | -3.1194 | -1.5152 | 4.3749 |  | 2.881 | 0.0423 | 4.0101 | 3.3641 | 3.3389 | 1.0696 | 10.7395 | 14.2357 | 14.831 | 11.0699 | 0.0001 | -0.003 | 0.0006 | 0.0037 | 0.0009 | -0.0008 | 0.0051 | -0.0173 | -0.007 | -360.1988 | 17.4028 | -360.4666 | 17.6677 | -360.882 | 18.2261 | -360.8604 | 17.5732 | -352.6413 | 18.7292 | -352.6598 | 16.8566
12:27 | 4057 | 39.8659 | 201.7572 | 448.8256 | 455.2167 | -16.8091 | -41.733 | 10.5451 | 7.3626 | 1.4124 | -0.114 | 2.832 | -1.1592 | 11.1336 | 3.8946 | 0.6129 | 0.6556 | 0.9615 | 0.7359 | -129.5831 | -1.2055 | 5.4737 | 1.6881 | -3.124 | -1.5178 | 4.3091 |  | 2.904 | 0.1937 | 4.0109 | 3.3651 | 3.3406 | 1.0688 | 10.7486 | 14.2512 | 14.8383 | 11.0663 | 0.0006 | -0.0027 | 0.001 | 0.0038 | 0.0008 | 0 | 0.0118 | -0.001 | -0.0078 | -360.1927 | 17.4213 | -360.485 | 17.6471 | -360.8112 | 18.1994 | -360.8758 | 17.5999 | -352.6906 | 18.76 | -352.6813 | 16.8464
12:27 | 4058 | 39.8088 | 201.7204 | 448.8425 | 455.1998 | -16.7391 | -41.766 | 10.6002 | 7.3523 | 1.4066 | -0.0824 | 2.8158 | -1.1881 | 11.1259 | 3.889 | 0.6127 | 0.6554 | 0.9625 | 0.7389 | -129.5769 | -1.1552 | 5.5012 | 1.8208 | -3.1051 | -1.5711 | 4.2915 |  | 2.8915 | 0.1178 | 4.0105 | 3.3616 | 3.3407 | 1.0706 | 10.7417 | 14.2673 | 14.859 | 11.0771 | -0.0003 | -0.0026 | 0.0006 | 0.0038 | 0.0007 | -0.0005 | 0.0013 | -0.0082 | 0.0142 | -360.1681 | 17.4048 | -360.4696 | 17.6759 | -360.845 | 18.1871 | -360.8327 | 17.5568 | -352.6567 | 18.7456 | -352.706 | 16.8607
12:27 | 4059 | 39.7691 | 201.7334 | 448.8248 | 455.2018 | -16.7421 | -41.7456 | 10.5705 | 7.4069 | 1.4083 | -0.0874 | 2.8841 | -1.2499 | 11.1679 | 3.9689 | 0.6139 | 0.6542 | 0.9639 | 0.7388 | -129.5512 | -1.1149 | 5.6517 | 1.8219 | -3.187 | -1.5208 | 4.3428 |  | 2.9144 | 0.0561 | 4.0112 | 3.363 | 3.3381 | 1.0681 | 10.7754 | 14.2367 | 14.8834 | 11.0483 | -0.0006 | -0.0027 | 0.0007 | 0.0036 | 0.0004 | -0.0007 | 0.0126 | -0.015 | -0.0099 | -360.1496 | 17.374 | -360.405 | 17.6184 | -360.7773 | 18.2077 | -360.8389 | 17.5671 | -352.6106 | 18.7128 | -352.6106 | 16.8238
12:27 | 4060 | 39.8165 | 201.732 | 448.8117 | 455.2078 | -16.7753 | -41.7038 | 10.5915 | 7.4047 | 1.4711 | -0.111 | 2.8415 | -1.2914 | 11.1518 | 3.9085 | 0.6146 | 0.6544 | 0.9603 | 0.7358 | -129.6044 | -1.1718 | 5.4692 | 1.5336 | -3.2043 | -1.5223 | 4.3817 |  | 2.9543 | 0.1264 | 4.0113 | 3.3631 | 3.34 | 1.0682 | 10.7313 | 14.2569 | 14.8604 | 11.0782 | 0 | -0.003 | 0.0006 | 0.0037 | 0.0007 | -0.0004 | 0.0038 | -0.0206 | -0.0151 | -360.1773 | 17.3987 | -360.4666 | 17.6492 | -360.7927 | 18.181 | -360.8358 | 17.5609 | -352.5921 | 18.7333 | -352.6537 | 16.834
12:27 | 4061 | 39.8327 | 201.7052 | 448.9123 | 455.1465 | -16.8036 | -41.7508 | 10.5344 | 7.3859 | 1.4812 | -0.1147 | 2.8554 | -1.2805 | 11.1458 | 3.9089 | 0.6137 | 0.6534 | 0.963 | 0.7366 | -129.6641 | -1.1803 | 5.3871 | 1.7635 | -3.1678 | -1.5978 | 4.3493 |  | 2.9608 | 0.0394 | 4.0122 | 3.3652 | 3.3384 | 1.0695 | 10.7003 | 14.2364 | 14.8466 | 11.0548 | 0 | -0.0032 | 0.0003 | 0.0041 | 0.0006 | -0.001 | 0.0067 | -0.0061 | 0.0058 | -360.1742 | 17.3966 | -360.4758 | 17.6656 | -360.8266 | 18.2077 | -360.8481 | 17.5712 | -352.6136 | 18.723 | -352.6598 | 16.8484
12:27 | 4062 | 39.8076 | 201.7232 | 448.8453 | 455.2361 | -16.8214 | -41.7869 | 10.5918 | 7.425 | 1.5045 | -0.0917 | 2.8822 | -1.3554 | 11.0891 | 3.9793 | 0.6135 | 0.6539 | 0.9624 | 0.7366 | -129.5052 | -1.1264 | 5.4719 | 1.8081 | -3.2406 | -1.6122 | 4.3523 |  | 2.9938 | 0.0642 | 4.0114 | 3.3627 | 3.3418 | 1.0689 | 10.744 | 14.2521 | 14.8607 | 11.0912 | -0.0003 | -0.0027 | 0.001 | 0.0044 | 0.0006 | -0.0002 | 0.0065 | -0.0109 | -0.012 | -360.1435 | 17.4192 | -360.485 | 17.6718 | -360.8635 | 18.2138 | -360.8789 | 17.5917 | -352.6413 | 18.7456 | -352.7029 | 16.8628
12:27 | 4063 | 39.7106 | 201.682 | 448.7087 | 455.2226 | -16.7173 | -41.8069 | 10.4567 | 7.4511 | 1.5721 | 0.0113 | 2.9818 | -1.3492 | 11.0925 | 3.8827 | 0.6133 | 0.6531 | 0.9635 | 0.7353 | -129.5249 | -1.1251 | 5.3767 | 1.8537 | -3.2085 | -1.6046 | 4.3604 |  | 2.9315 | 0.0654 | 4.0113 | 3.3675 | 3.3417 | 1.07 | 10.7474 | 14.2674 | 14.889 | 11.0998 | 0 | -0.0027 | 0.0011 | 0.004 | 0.001 | -0.0006 | 0.009 | -0.0051 | -0.0068 | -360.1958 | 17.4233 | -360.4881 | 17.682 | -360.8143 | 18.2097 | -360.8697 | 17.5712 | -352.6506 | 18.7538 | -352.6875 | 16.8546
12:27 | 4064 | 39.8804 | 201.6834 | 448.7043 | 455.2013 | -16.8149 | -41.8435 | 10.5388 | 7.465 | 1.5662 | 0.092 | 2.9398 | -1.3981 | 11.0965 | 3.8589 | 0.6132 | 0.6527 | 0.9606 | 0.7372 | -129.6165 | -1.1946 | 5.4077 | 1.9367 | -3.2236 | -1.5269 | 4.4077 |  | 2.8639 | 0.0761 | 4.0129 | 3.3607 | 3.3384 | 1.0691 | 10.7591 | 14.244 | 14.8638 | 11.0544 | 0 | -0.003 | 0.001 | 0.0039 | 0.0005 | -0.0001 | 0.0019 | 0.0011 | 0.0052 | -360.165 | 17.3802 | -360.445 | 17.6779 | -360.7958 | 18.1994 | -360.8727 | 17.565 | -352.6136 | 18.7148 | -352.6537 | 16.8484
12:27 | 4065 | 39.8394 | 201.682 | 448.8942 | 455.2998 | -16.7904 | -41.7977 | 10.3904 | 7.4711 | 1.6167 | 0.0665 | 2.9047 | -1.3786 | 11.15 | 3.8838 | 0.6132 | 0.6522 | 0.9604 | 0.7375 | -129.7633 | -1.1707 | 5.4048 | 1.8987 | -3.2316 | -1.5207 | 4.4145 |  | 2.9287 | 0.0675 | 4.0112 | 3.3607 | 3.3397 | 1.0692 | 10.7982 | 14.29 | 14.8919 | 11.1377 | 0.0001 | -0.0033 | 0.0015 | 0.0043 | 0.0013 | -0.0003 | 0.0184 | -0.0062 | -0.0082 | -360.1527 | 17.3966 | -360.4481 | 17.6512 | -360.7681 | 18.1789 | -360.7681 | 17.565 | -352.6506 | 18.7251 | -352.6352 | 16.8299
12:27 | 4066 | 39.8617 | 201.6301 | 448.8042 | 455.2638 | -16.7806 | -41.843 | 10.4262 | 7.4835 | 1.5935 | -0.002 | 2.9367 | -1.1784 | 11.2166 | 4.0145 | 0.6131 | 0.6534 | 0.9656 | 0.737 | -129.6639 | -1.1397 | 5.3774 | 1.8912 | -3.246 | -1.5586 | 4.3899 |  | 2.9228 | 0.1016 | 4.0103 | 3.3656 | 3.3361 | 1.0683 | 10.7707 | 14.267 | 14.8453 | 11.0894 | 0.0001 | -0.0027 | 0.0004 | 0.0034 | 0.0004 | -0.0003 | 0.0065 | -0.0108 | -0.013 | -360.1435 | 17.3802 | -360.4358 | 17.6636 | -360.8174 | 18.1769 | -360.805 | 17.5404 | -352.5798 | 18.7087 | -352.6537 | 16.8464
12:27 | 4067 | 39.8683 | 201.7691 | 448.7673 | 455.2079 | -16.8123 | -41.749 | 10.408 | 7.5448 | 1.5895 | 0.0043 | 2.9607 | -1.2156 | 11.1711 | 3.9026 | 0.6129 | 0.6542 | 0.964 | 0.7363 | -129.6034 | -1.2084 | 5.4919 | 1.8781 | -3.2775 | -1.5947 | 4.3169 |  | 2.8962 | 0.1336 | 4.0103 | 3.3625 | 3.337 | 1.069 | 10.7521 | 14.2431 | 14.824 | 11.0988 | -0.0004 | -0.0026 | 0.0009 | 0.0038 | 0.0013 | -0.0005 | 0.0116 | 0.0005 | -0.0061 | -360.1711 | 17.3884 | -360.4389 | 17.6718 | -360.8204 | 18.2118 | -360.8697 | 17.5773 | -352.629 | 18.7169 | -352.6229 | 16.832
12:28 | 4068 | 39.8593 | 201.7492 | 448.8112 | 455.1708 | -16.7732 | -41.766 | 10.3766 | 7.4592 | 1.528 | -0.1125 | 2.9039 | -1.1319 | 11.1917 | 3.9348 | 0.6149 | 0.6555 | 0.9625 | 0.7369 | -129.62 | -1.1941 | 5.4895 | 1.8147 | -3.2321 | -1.62 | 4.3999 |  | 2.9139 | 0.0709 | 4.0112 | 3.3609 | 3.3381 | 1.069 | 10.7174 | 14.237 | 14.8566 | 11.0822 | -0.0002 | -0.0031 | 0.0007 | 0.0038 | 0.0008 | -0.0004 | 0.0073 | -0.0061 | -0.0045 | -360.1835 | 17.4295 | -360.4758 | 17.6636 | -360.8174 | 18.2159 | -360.8789 | 17.5978 | -352.6937 | 18.7538 | -352.6967 | 16.8402
12:28 | 4069 | 39.8885 | 201.7258 | 448.764 | 455.2968 | -16.8302 | -41.6896 | 10.3686 | 7.4679 | 1.5172 | 0.0135 | 2.8678 | -1.18 | 11.1584 | 4.0466 | 0.6126 | 0.6571 | 0.9636 | 0.736 | -129.6978 | -1.1904 | 5.4685 | 1.8695 | -3.2549 | -1.6669 | 4.3003 |  | 2.9521 | 0.0705 | 4.0107 | 3.3622 | 3.3361 | 1.0677 | 10.7487 | 14.2336 | 14.8188 | 11.067 | 0.0002 | -0.0031 | 0.0007 | 0.0042 | 0.0008 | -0.0005 | 0.0089 | -0.0127 | -0.0192 | -360.125 | 17.4151 | -360.5189 | 17.7067 | -360.8574 | 18.2097 | -360.8389 | 17.5629 | -352.6321 | 18.7456 | -352.7213 | 16.8751
12:28 | 4070 | 39.857 | 201.6845 | 448.7451 | 455.1691 | -16.8259 | -41.7223 | 10.5235 | 7.4648 | 1.598 | -0.0064 | 2.892 | -1.2847 | 11.1265 | 3.952 | 0.6136 | 0.6526 | 0.9604 | 0.7374 | -129.6342 | -1.1595 | 5.4242 | 1.8808 | -3.1612 | -1.5361 | 4.4166 |  | 2.9764 | 0.0893 | 4.0128 | 3.3639 | 3.3391 | 1.0681 | 10.7267 | 14.2346 | 14.8423 | 11.0627 | 0 | -0.0028 | 0.0009 | 0.0043 | 0.0012 | -0.0003 | 0.0027 | -0.0118 | -0.0012 | -360.125 | 17.3699 | -360.3958 | 17.6492 | -360.7927 | 18.2118 | -360.885 | 17.5835 | -352.6198 | 18.7004 | -352.6044 | 16.8238
12:28 | 4071 | 39.8961 | 201.6981 | 448.8093 | 455.2834 | -16.6919 | -41.5757 | 10.6071 | 7.4612 | 1.6915 | 0.1027 | 2.8492 | -1.2919 | 11.1454 | 3.9373 | 0.6126 | 0.6567 | 0.9586 | 0.7351 | -129.6126 | -1.0565 | 5.438 | 1.7275 | -3.2662 | -1.5709 | 4.4263 |  | 2.9037 | 0.0234 | 4.0116 | 3.364 | 3.3382 | 1.0693 | 10.7648 | 14.2963 | 14.8601 | 11.0998 | -0.0004 | -0.0026 | 0.0009 | 0.0036 | 0.0007 | -0.0003 | 0.0073 | -0.0016 | -0.0219 | -360.1773 | 17.4131 | -360.4666 | 17.6677 | -360.7681 | 18.181 | -360.7712 | 17.5671 | -352.6567 | 18.7395 | -352.6383 | 16.834
12:28 | 4072 | 39.8744 | 201.6732 | 448.648 | 455.218 | -16.6497 | -41.7081 | 10.6605 | 7.4714 | 1.5942 | -0.0662 | 2.8358 | -1.2174 | 11.1384 | 3.9864 | 0.6126 | 0.6605 | 0.9633 | 0.7358 | -129.6372 | -1.0693 | 5.4749 | 1.7907 | -3.2532 | -1.563 | 4.3355 |  | 2.9273 | 0.0637 | 4.0114 | 3.3642 | 3.3424 | 1.0673 | 10.759 | 14.273 | 14.8996 | 11.1002 | 0.0001 | -0.0028 | 0.001 | 0.0039 | 0.0007 | -0.0003 | 0.0017 | 0.0074 | -0.0087 | -360.1065 | 17.3864 | -360.4666 | 17.6902 | -360.8543 | 18.2159 | -360.8174 | 17.5445 | -352.5983 | 18.7045 | -352.6167 | 16.8587
12:28 | 4073 | 39.8625 | 201.6845 | 448.6756 | 455.346 | -16.5759 | -41.6771 | 10.6331 | 7.5087 | 1.5747 | 0.0325 | 2.8812 | -1.2878 | 11.1652 | 3.9374 | 0.6137 | 0.6595 | 0.9621 | 0.7357 | -129.5866 | -1.191 | 5.3748 | 1.7851 | -3.2299 | -1.5888 | 4.3402 |  | 2.9356 | 0.1001 | 4.0123 | 3.3631 | 3.3423 | 1.0672 | 10.7416 | 14.2501 | 14.8601 | 11.0883 | 0.0002 | -0.0031 | 0.0015 | 0.0041 | 0.0005 | -0.0004 | -0.0034 | -0.0096 | -0.0223 | -360.2204 | 17.411 | -360.4512 | 17.6677 | -360.8266 | 18.2261 | -360.8912 | 17.6061 | -352.709 | 18.7374 | -352.6352 | 16.8238
12:28 | 4074 | 39.8826 | 201.6222 | 448.714 | 455.2727 | -16.6959 | -41.6842 | 10.642 | 7.5332 | 1.6493 | 0.1347 | 2.8904 | -1.3199 | 11.0872 | 3.9239 | 0.6131 | 0.6553 | 0.9606 | 0.7336 | -129.623 | -1.2182 | 5.3525 | 1.7218 | -3.2304 | -1.5629 | 4.2722 |  | 2.9341 | 0.0541 | 4.0122 | 3.3658 | 3.342 | 1.0687 | 10.7405 | 14.2661 | 14.8577 | 11.1049 | 0.0002 | -0.0028 | 0.0007 | 0.0036 | 0.0012 | -0.0004 | 0.0012 | -0.0015 | -0.0201 | -360.1558 | 17.4336 | -360.5158 | 17.7108 | -360.8697 | 18.2015 | -360.8112 | 17.5568 | -352.6567 | 18.76 | -352.706 | 16.8792
12:28 | 4075 | 39.8205 | 201.6787 | 448.7666 | 455.3362 | -16.7497 | -41.723 | 10.5504 | 7.5064 | 1.6308 | 0.1345 | 2.8986 | -1.2237 | 11.1392 | 3.9516 | 0.6146 | 0.6525 | 0.9585 | 0.7349 | -129.6182 | -1.0791 | 5.3906 | 1.7234 | -3.2584 | -1.6266 | 4.2787 |  | 2.898 | 0.0772 | 4.0127 | 3.3686 | 3.3439 | 1.067 | 10.737 | 14.2569 | 14.8315 | 11.0782 | -0.0001 | -0.0026 | 0.001 | 0.0039 | 0.0002 | -0.0005 | 0.0179 | -0.0154 | -0.0164 | -360.1465 | 17.3802 | -360.4327 | 17.7046 | -360.8512 | 18.2467 | -360.9066 | 17.5773 | -352.6352 | 18.7087 | -352.6352 | 16.8587
12:28 | 4076 | 39.8972 | 201.6761 | 448.7312 | 455.335 | -16.6785 | -41.6338 | 10.6289 | 7.4061 | 1.5714 | -0.0574 | 2.9412 | -1.3457 | 11.0492 | 3.7726 | 0.6119 | 0.6553 | 0.9614 | 0.7351 | -129.5922 | -1.218 | 5.381 | 1.8347 | -3.2529 | -1.5127 | 4.2719 |  | 2.8632 | -0.0573 | 4.013 | 3.364 | 3.343 | 1.0682 | 10.7302 | 14.2612 | 14.8395 | 11.0836 | -0.0002 | -0.0025 | 0.0007 | 0.0038 | 0.0009 | -0.0011 | 0.0134 | -0.0031 | -0.0151 | -360.1742 | 17.411 | -360.4419 | 17.6656 | -360.7497 | 18.1912 | -360.8235 | 17.5753 | -352.6721 | 18.7374 | -352.6475 | 16.8238
12:28 | 4077 | 39.8187 | 201.6422 | 448.7949 | 455.3169 | -16.6523 | -41.578 | 10.7036 | 7.5068 | 1.5431 | -0.1179 | 2.8948 | -1.3079 | 11.115 | 3.9234 | 0.6141 | 0.6582 | 0.9622 | 0.7349 | -129.5301 | -1.1278 | 5.4958 | 1.903 | -3.1781 | -1.5251 | 4.3533 |  | 2.9038 | -0.0133 | 4.0117 | 3.3654 | 3.3417 | 1.0682 | 10.7209 | 14.2695 | 14.8491 | 11.0796 | 0.0003 | -0.0033 | 0.0005 | 0.0039 | 0.0005 | -0.0002 | -0.0005 | -0.0119 | -0.0088 | -360.0788 | 17.3843 | -360.4542 | 17.7005 | -360.8574 | 18.2036 | -360.7897 | 17.5239 | -352.5798 | 18.7045 | -352.6752 | 16.8587
12:28 | 4078 | 39.7663 | 201.6947 | 448.7753 | 455.2567 | -16.6656 | -41.5464 | 10.6268 | 7.4889 | 1.6364 | -0.0582 | 2.8608 | -1.1698 | 11.1104 | 3.8969 | 0.6137 | 0.6563 | 0.9642 | 0.7346 | -129.545 | -1.0727 | 5.4809 | 1.78 | -3.2457 | -1.6077 | 4.2871 |  | 2.8965 | -0.0099 | 4.01 | 3.3669 | 3.3386 | 1.0672 | 10.7244 | 14.2496 | 14.8337 | 11.0605 | 0.0001 | -0.0026 | 0.0004 | 0.004 | 0.0009 | -0.0009 | 0.0004 | -0.0102 | -0.0007 | -360.1558 | 17.3761 | -360.3804 | 17.6553 | -360.7773 | 18.22 | -360.8974 | 17.5753 | -352.6537 | 18.6943 | -352.5921 | 16.8115
12:28 | 4079 | 39.7927 | 201.6639 | 448.7463 | 455.2214 | -16.6717 | -41.5446 | 10.6301 | 7.46 | 1.6585 | -0.0407 | 2.9059 | -1.1935 | 11.0873 | 3.9739 | 0.6133 | 0.6514 | 0.9617 | 0.7348 | -129.6343 | -1.2196 | 5.4207 | 1.7069 | -3.3284 | -1.5849 | 4.2901 |  | 2.977 | 0.0741 | 4.012 | 3.3646 | 3.3418 | 1.069 | 10.7509 | 14.2592 | 14.8747 | 11.0919 | -0.0002 | -0.0027 | 0.0009 | 0.0039 | 0.0007 | -0.0001 | 0.0101 | -0.0146 | 0.0048 | -360.2296 | 17.4356 | -360.5404 | 17.7046 | -360.845 | 18.1953 | -360.8266 | 17.5609 | -352.6783 | 18.762 | -352.7029 | 16.8546
12:28 | 4080 | 39.8374 | 201.6896 | 448.7881 | 455.255 | -16.6715 | -41.6212 | 10.5835 | 7.3755 | 1.7103 | -0.0157 | 2.9477 | -1.1302 | 11.1963 | 3.9677 | 0.613 | 0.6539 | 0.9627 | 0.7364 | -129.5736 | -1.1555 | 5.3916 | 1.737 | -3.2865 | -1.5656 | 4.2774 |  | 2.9741 | 0.0204 | 4.0118 | 3.369 | 3.3409 | 1.0686 | 10.7626 | 14.2474 | 14.8494 | 11.0869 | -0.0003 | -0.0026 | 0.0006 | 0.0036 | 0.0007 | -0.0007 | 0.0246 | -0.0067 | 0.0034 | -360.1373 | 17.3905 | -360.4758 | 17.7108 | -360.8789 | 18.2467 | -360.8666 | 17.5568 | -352.6198 | 18.7251 | -352.6506 | 16.8751
12:28 | 4081 | 39.7799 | 201.6894 | 448.8895 | 455.3482 | -16.714 | -41.6344 | 10.5954 | 7.4254 | 1.7292 | 0.0267 | 2.8778 | -1.1504 | 11.1499 | 3.981 | 0.6136 | 0.6521 | 0.9632 | 0.7354 | -129.5526 | -1.1618 | 5.3742 | 1.6545 | -3.2658 | -1.6914 | 4.3067 |  | 2.9488 | -0.0018 | 4.0116 | 3.3656 | 3.3399 | 1.068 | 10.7545 | 14.2277 | 14.8467 | 11.0905 | 0.0002 | -0.0031 | 0.0007 | 0.0038 | 0.0005 | -0.0006 | 0.0107 | 0.0074 | -0.036 | -360.2265 | 17.4172 | -360.4512 | 17.6656 | -360.7927 | 18.2138 | -360.8697 | 17.602 | -352.6998 | 18.7436 | -352.6721 | 16.832
12:28 | 4082 | 39.8436 | 201.6711 | 448.9183 | 455.3897 | -16.6439 | -41.6693 | 10.6124 | 7.3863 | 1.7093 | -0.0189 | 2.8786 | -1.1519 | 11.1861 | 3.9363 | 0.6139 | 0.6548 | 0.9652 | 0.7355 | -129.6096 | -1.139 | 5.3848 | 1.6731 | -3.1821 | -1.6212 | 4.2476 |  | 2.9154 | -0.0904 | 4.0125 | 3.3678 | 3.3422 | 1.0678 | 10.721 | 14.217 | 14.8054 | 11.075 | -0.0001 | -0.0033 | 0.0007 | 0.0038 | 0.0006 | 0 | 0.025 | -0.0047 | 0.0019 | -360.125 | 17.409 | -360.4881 | 17.6923 | -360.8358 | 18.1728 | -360.7681 | 17.5342 | -352.6044 | 18.7395 | -352.6906 | 16.8587
12:28 | 4083 | 39.9338 | 201.6598 | 448.8326 | 455.3641 | -16.5854 | -41.6242 | 10.5513 | 7.4437 | 1.7148 | 0.1193 | 2.9256 | -1.1972 | 11.1999 | 3.9194 | 0.6139 | 0.6543 | 0.9605 | 0.7345 | -129.6279 | -1.1308 | 5.3915 | 1.6867 | -3.1792 | -1.616 | 4.3124 |  | 2.868 | -0.0313 | 4.0107 | 3.3653 | 3.3406 | 1.0672 | 10.7232 | 14.2544 | 14.8392 | 11.0764 | -0.0004 | -0.0029 | 0.0008 | 0.004 | 0.0012 | -0.0004 | 0.002 | -0.0092 | 0.0054 | -360.1158 | 17.3638 | -360.3865 | 17.6574 | -360.8235 | 18.2179 | -360.8481 | 17.5486 | -352.6075 | 18.7087 | -352.6075 | 16.8361
12:28 | 4084 | 39.9733 | 201.7634 | 448.8718 | 455.3169 | -16.7074 | -41.9277 | 10.4773 | 7.4283 | 1.6772 | 0.0565 | 2.9871 | -1.1824 | 11.1431 | 3.9681 | 0.6133 | 0.6551 | 0.963 | 0.7371 | -129.605 | -1.1189 | 5.4006 | 1.6836 | -3.1898 | -1.5722 | 4.3004 |  | 2.855 | -0.0971 | 4.0109 | 3.3696 | 3.3398 | 1.07 | 10.7395 | 14.2182 | 14.8589 | 11.053 | 0 | -0.0025 | 0.0007 | 0.0039 | 0.0006 | -0.0005 | 0.0144 | -0.0081 | 0.0014 | -360.205 | 17.4336 | -360.4789 | 17.6574 | -360.7773 | 18.1748 | -360.8389 | 17.5732 | -352.6413 | 18.7415 | -352.6413 | 16.8156
12:28 | 4085 | 39.8185 | 201.7018 | 448.7543 | 455.2702 | -16.7211 | -41.84 | 10.5054 | 7.3827 | 1.7218 | 0.1582 | 3.031 | -1.1273 | 11.1362 | 3.9909 | 0.6143 | 0.6566 | 0.9641 | 0.7367 | -129.609 | -1.0758 | 5.386 | 1.6632 | -3.2009 | -1.5434 | 4.3816 |  | 2.8685 | -0.0637 | 4.0115 | 3.3671 | 3.3369 | 1.0682 | 10.744 | 14.2348 | 14.8549 | 11.1028 | -0.0003 | -0.003 | 0.0005 | 0.0038 | 0.0011 | -0.0008 | 0.0026 | -0.0081 | -0.0253 | -360.1927 | 17.4192 | -360.5066 | 17.7108 | -360.8389 | 18.2077 | -360.8543 | 17.5465 | -352.6106 | 18.7497 | -352.706 | 16.8587
12:28 | 4086 | 39.8241 | 201.7131 | 448.6691 | 455.3009 | -16.6927 | -41.8496 | 10.409 | 7.3765 | 1.6851 | 0.0406 | 2.8961 | -1.167 | 11.1634 | 3.9885 | 0.6137 | 0.6592 | 0.9641 | 0.7366 | -129.5782 | -1.1048 | 5.5327 | 1.7381 | -3.1494 | -1.5777 | 4.315 |  | 2.9138 | -0.0237 | 4.0121 | 3.3704 | 3.3383 | 1.0683 | 10.7451 | 14.2708 | 14.8747 | 11.0919 | 0.0004 | -0.0029 | 0.001 | 0.0038 | 0.0004 | -0.0004 | 0.0096 | -0.0161 | -0.0155 | -360.205 | 17.3884 | -360.4573 | 17.68 | -360.8081 | 18.2302 | -360.8912 | 17.5794 | -352.7029 | 18.7333 | -352.6413 | 16.8423
12:28 | 4087 | 39.8888 | 201.6303 | 448.7295 | 455.3638 | -16.7893 | -41.7525 | 10.4706 | 7.3544 | 1.7567 | 0.0758 | 2.8542 | -1.2136 | 11.1093 | 3.9312 | 0.6149 | 0.6538 | 0.963 | 0.7374 | -129.577 | -1.0458 | 5.4221 | 1.6781 | -3.2034 | -1.6065 | 4.2956 |  | 2.9927 | 0.1574 | 4.0112 | 3.3671 | 3.3391 | 1.068 | 10.7694 | 14.2893 | 14.8819 | 11.1045 | -0.0001 | -0.0027 | 0.0007 | 0.0036 | 0.0009 | -0.0006 | 0.0031 | -0.0121 | -0.0064 | -360.2081 | 17.4172 | -360.4666 | 17.6759 | -360.805 | 18.1892 | -360.842 | 17.5671 | -352.669 | 18.7518 | -352.6906 | 16.8299
12:28 | 4088 | 39.9687 | 201.7502 | 448.8547 | 455.4611 | -16.727 | -41.7833 | 10.389 | 7.3803 | 1.7739 | 0.0378 | 2.8885 | -1.2102 | 11.0832 | 3.9461 | 0.6146 | 0.6538 | 0.963 | 0.737 | -129.643 | -1.1419 | 5.2663 | 1.732 | -3.2233 | -1.63 | 4.2732 |  | 2.8856 | 0.031 | 4.0109 | 3.3666 | 3.3416 | 1.0673 | 10.744 | 14.2638 | 14.8618 | 11.0735 | -0.0003 | -0.0026 | 0.001 | 0.0038 | 0.0007 | -0.0002 | 0.0046 | -0.0054 | -0.0125 | -360.1158 | 17.3802 | -360.4266 | 17.6677 | -360.8081 | 18.2036 | -360.8235 | 17.5527 | -352.5921 | 18.7025 | -352.6321 | 16.8279
12:28 | 4089 | 39.9277 | 201.7182 | 448.7384 | 455.514 | -16.7567 | -41.7843 | 10.4351 | 7.3819 | 1.7921 | 0.1919 | 2.8684 | -1.2531 | 11.1492 | 3.9115 | 0.6142 | 0.6541 | 0.9587 | 0.7367 | -129.6298 | -1.1444 | 5.4627 | 1.7367 | -3.1997 | -1.6129 | 4.3469 |  | 2.912 | -0.0508 | 4.0112 | 3.3682 | 3.3437 | 1.0689 | 10.7568 | 14.2532 | 14.8552 | 11.0927 | -0.0001 | -0.0031 | 0.0015 | 0.0042 | 0.0009 | -0.0008 | 0.0179 | -0.0186 | -0.0188 | -360.165 | 17.3987 | -360.4142 | 17.6512 | -360.7835 | 18.1933 | -360.8297 | 17.565 | -352.6198 | 18.721 | -352.6383 | 16.8074
12:28 | 4090 | 39.9266 | 201.7264 | 448.7954 | 455.4224 | -16.6838 | -41.7206 | 10.4353 | 7.359 | 1.7364 | 0.1719 | 2.8084 | -1.2087 | 11.1365 | 3.9832 | 0.6135 | 0.6545 | 0.9605 | 0.7357 | -129.6314 | -1.2238 | 5.4261 | 1.8119 | -3.2979 | -1.6026 | 4.3695 |  | 2.8674 | -0.0514 | 4.0113 | 3.3686 | 3.3364 | 1.0685 | 10.7475 | 14.273 | 14.8011 | 11.054 | 0.0003 | -0.0031 | 0.0007 | 0.0035 | 0.0005 | 0 | 0.0081 | -0.0052 | -0.0181 | -360.2111 | 17.4048 | -360.4604 | 17.6759 | -360.805 | 18.2118 | -360.8358 | 17.565 | -352.6106 | 18.723 | -352.629 | 16.834
12:28 | 4091 | 39.9452 | 201.7099 | 448.8711 | 455.4369 | -16.68 | -41.8121 | 10.4948 | 7.3708 | 1.6455 | -0.0482 | 2.7798 | -1.1968 | 11.0797 | 3.9565 | 0.6135 | 0.6539 | 0.9635 | 0.7365 | -129.6574 | -1.3385 | 5.4342 | 1.7674 | -3.2299 | -1.5546 | 4.2702 |  | 2.8493 | -0.0899 | 4.0115 | 3.3691 | 3.3372 | 1.0675 | 10.7325 | 14.2579 | 14.8491 | 11.0854 | 0.0002 | -0.0026 | 0.0007 | 0.004 | 0.0003 | -0.001 | 0.0225 | 0.002 | -0.002 | -360.1958 | 17.4213 | -360.4942 | 17.6861 | -360.8174 | 18.2282 | -360.8697 | 17.5732 | -352.6567 | 18.7477 | -352.6721 | 16.8484
12:28 | 4092 | 39.9474 | 201.7607 | 448.8382 | 455.4379 | -16.735 | -41.8506 | 10.3182 | 7.4509 | 1.6401 | 0.0383 | 2.8677 | -1.2272 | 11.1363 | 3.9702 | 0.6147 | 0.6544 | 0.9597 | 0.7351 | -129.6464 | -1.2147 | 5.4173 | 1.7549 | -3.187 | -1.4934 | 4.2702 |  | 2.9331 | 0.0286 | 4.0117 | 3.3676 | 3.3361 | 1.0692 | 10.7071 | 14.2438 | 14.8453 | 11.0548 | -0.0002 | -0.0028 | 0.0005 | 0.0038 | 0.0007 | -0.0004 | 0.0237 | -0.0184 | -0.0312 | -360.1711 | 17.4192 | -360.4881 | 17.6882 | -360.805 | 18.2118 | -360.8666 | 17.5773 | -352.6598 | 18.7559 | -352.6783 | 16.8505
12:28 | 4093 | 39.9713 | 201.6924 | 448.8866 | 455.5336 | -16.6136 | -41.9122 | 10.4185 | 7.469 | 1.6198 | -0.0394 | 2.8852 | -1.2455 | 11.118 | 3.9354 | 0.6147 | 0.6552 | 0.9654 | 0.7356 | -129.5949 | -1.033 | 5.4622 | 1.7592 | -3.1179 | -1.5792 | 4.3443 |  | 2.986 | -0.001 | 4.0106 | 3.3671 | 3.3391 | 1.0685 | 10.7323 | 14.2757 | 14.8639 | 11.0785 | 0.0001 | -0.0027 | 0.0011 | 0.004 | 0.0012 | -0.0001 | 0.0183 | -0.0167 | -0.0212 | -360.1373 | 17.3946 | -360.4604 | 17.6718 | -360.8112 | 18.2138 | -360.8174 | 17.5691 | -352.669 | 18.7312 | -352.6506 | 16.8443
12:28 | 4094 | 40.0067 | 201.7301 | 448.9916 | 455.5407 | -16.6977 | -41.9108 | 10.5117 | 7.4366 | 1.6239 | -0.0349 | 2.8425 | -1.2723 | 11.1379 | 3.9461 | 0.6158 | 0.6516 | 0.9667 | 0.7346 | -129.648 | -1.1352 | 5.3939 | 1.7514 | -3.1442 | -1.558 | 4.2866 |  | 2.9587 | 0.0572 | 4.0111 | 3.3674 | 3.3379 | 1.0671 | 10.7361 | 14.2031 | 14.7911 | 11.0497 | 0.0003 | -0.0032 | 0.0008 | 0.0036 | 0.0008 | -0.0006 | 0.0053 | 0.0062 | -0.022 | -360.1588 | 17.3884 | -360.3927 | 17.6348 | -360.765 | 18.1871 | -360.8174 | 17.5527 | -352.6475 | 18.723 | -352.6167 | 16.8074
12:28 | 4095 | 39.986 | 201.7029 | 448.8407 | 455.4535 | -16.7001 | -41.9117 | 10.4936 | 7.4127 | 1.631 | -0.1299 | 2.8656 | -1.3156 | 11.0808 | 3.8942 | 0.6144 | 0.6565 | 0.9601 | 0.7369 | -129.7294 | -1.1423 | 5.431 | 1.6805 | -3.1638 | -1.5592 | 4.3151 |  | 2.9922 | 0.0622 | 4.0095 | 3.3647 | 3.3377 | 1.0682 | 10.7601 | 14.2802 | 14.8499 | 11.0778 | 0.0002 | -0.0026 | 0.0008 | 0.0036 | 0.0007 | -0.0003 | 0.0234 | -0.0105 | -0.0146 | -360.1435 | 17.3905 | -360.4573 | 17.6533 | -360.7989 | 18.1953 | -360.805 | 17.5342 | -352.6044 | 18.723 | -352.6413 | 16.8299
12:28 | 4096 | 40.0321 | 201.707 | 448.9191 | 455.5038 | -16.5508 | -41.78 | 10.5747 | 7.4101 | 1.6509 | -0.0663 | 2.859 | -1.2177 | 11.1363 | 3.9516 | 0.6143 | 0.6535 | 0.9617 | 0.7363 | -129.6704 | -1.1631 | 5.3637 | 1.6603 | -3.1766 | -1.5561 | 4.2232 |  | 2.9414 | 0.0422 | 4.0116 | 3.3633 | 3.3397 | 1.0674 | 10.7681 | 14.2886 | 14.8721 | 11.0792 | -0.0001 | -0.0022 | 0.001 | 0.0039 | 0.0007 | -0.0006 | 0.0075 | 0.0066 | -0.0033 | -360.1465 | 17.3782 | -360.4358 | 17.6656 | -360.8389 | 18.222 | -360.8358 | 17.5445 | -352.6198 | 18.7087 | -352.6383 | 16.8258
12:28 | 4097 | 40.0836 | 201.7478 | 448.9144 | 455.4151 | -16.549 | -41.7686 | 10.5141 | 7.4289 | 1.667 | -0.1356 | 2.841 | -1.288 | 11.2586 | 4.0307 | 0.6146 | 0.6548 | 0.9644 | 0.7365 | -129.5413 | -1.172 | 5.3902 | 1.7446 | -3.1058 | -1.5593 | 4.3374 |  | 2.9559 | 0.0788 | 4.0108 | 3.3674 | 3.336 | 1.0683 | 10.7429 | 14.2681 | 14.8872 | 11.0847 | -0.0005 | -0.0029 | 0.0008 | 0.0041 | 0.0007 | -0.0001 | 0.007 | -0.0073 | -0.021 | -360.2296 | 17.4028 | -360.4758 | 17.6738 | -360.8235 | 18.2323 | -360.8943 | 17.5917 | -352.6629 | 18.7271 | -352.6383 | 16.832
12:28 | 4098 | 39.9876 | 201.7032 | 448.9542 | 455.4624 | -16.4446 | -41.6169 | 10.6233 | 7.4615 | 1.7278 | -0.0152 | 2.88 | -1.26 | 11.2227 | 3.9271 | 0.6142 | 0.6544 | 0.9608 | 0.7371 | -129.583 | -1.1112 | 5.3134 | 1.7452 | -3.1282 | -1.5453 | 4.3509 |  | 2.9323 | 0.0236 | 4.0116 | 3.3617 | 3.3344 | 1.0685 | 10.7566 | 14.2655 | 14.8779 | 11.085 | 0.0007 | -0.0025 | 0.0011 | 0.0044 | 0.0013 | -0.0006 | 0.0126 | -0.0094 | -0.0186 | -360.2604 | 17.4397 | -360.5004 | 17.682 | -360.8481 | 18.2138 | -360.8604 | 17.5671 | -352.7029 | 18.7744 | -352.7213 | 16.8464
12:28 | 4099 | 39.9875 | 201.745 | 448.9581 | 455.5246 | -16.4936 | -41.6164 | 10.6511 | 7.4965 | 1.7489 | -0.163 | 2.8659 | -1.2334 | 11.1914 | 3.9315 | 0.6153 | 0.6553 | 0.9615 | 0.7346 | -129.6603 | -1.1568 | 5.3249 | 1.7845 | -3.1495 | -1.6557 | 4.2937 |  | 2.8947 | 0.0242 | 4.0116 | 3.3632 | 3.338 | 1.0679 | 10.7637 | 14.2717 | 14.8566 | 11.088 | 0.0001 | -0.0029 | 0.0002 | 0.0039 | 0.0004 | -0.0004 | -0.0069 | -0.0081 | 0.0083 | -360.1065 | 17.3823 | -360.4635 | 17.68 | -360.8266 | 18.2241 | -360.8604 | 17.5424 | -352.6383 | 18.7148 | -352.6752 | 16.8566
12:28 | 4100 | 40.0164 | 201.6648 | 448.8511 | 455.518 | -16.5574 | -41.6112 | 10.5886 | 7.5181 | 1.6736 | -0.1834 | 2.8702 | -1.1365 | 11.2421 | 3.9012 | 0.6139 | 0.6551 | 0.9602 | 0.7357 | -129.6595 | -1.1446 | 5.3427 | 1.7 | -3.1715 | -1.5287 | 4.3023 |  | 2.8375 | 0.0572 | 4.0115 | 3.3651 | 3.3374 | 1.0679 | 10.7475 | 14.2499 | 14.8648 | 11.0829 | -0.0003 | -0.0026 | 0.0009 | 0.0041 | 0.0011 | -0.0006 | 0.0075 | -0.0132 | 0.0199 | -360.2019 | 17.374 | -360.3742 | 17.641 | -360.762 | 18.2159 | -360.845 | 17.5732 | -352.6229 | 18.7025 | -352.586 | 16.8094
12:28 | 4101 | 40.0005 | 201.7286 | 448.9379 | 455.4791 | -16.5707 | -41.5446 | 10.6551 | 7.5018 | 1.6968 | -0.1368 | 2.947 | -1.111 | 11.2363 | 3.8888 | 0.6146 | 0.6565 | 0.9613 | 0.7356 | -129.6375 | -1.1408 | 5.3591 | 1.7935 | -3.0786 | -1.4761 | 4.3376 |  | 2.8657 | -0.0435 | 4.0117 | 3.3646 | 3.3355 | 1.0675 | 10.7255 | 14.2394 | 14.8535 | 11.0901 | -0.0003 | -0.0027 | 0.0005 | 0.0038 | 0.0006 | -0.0007 | 0.0215 | -0.0103 | -0.0127 | -360.2111 | 17.4274 | -360.4912 | 17.6697 | -360.8174 | 18.1666 | -360.7712 | 17.5445 | -352.6475 | 18.7353 | -352.6721 | 16.8258
12:28 | 4102 | 39.9906 | 201.6597 | 448.9935 | 455.4883 | -16.5292 | -41.5376 | 10.6292 | 7.4501 | 1.6335 | -0.0886 | 2.9787 | -1.1245 | 11.2168 | 3.9317 | 0.6144 | 0.6533 | 0.9643 | 0.7377 | -129.5744 | -1.1474 | 5.3131 | 1.7194 | -3.1771 | -1.4624 | 4.3915 |  | 2.8362 | -0.0132 | 4.0125 | 3.366 | 3.3393 | 1.0677 | 10.7245 | 14.2609 | 14.8258 | 11.0728 | -0.0003 | -0.0032 | 0.0008 | 0.004 | 0.0008 | -0.0007 | 0.0096 | -0.0095 | -0.0079 | -360.1158 | 17.3925 | -360.4573 | 17.6902 | -360.8697 | 18.2323 | -360.8604 | 17.5363 | -352.6506 | 18.7045 | -352.6629 | 16.8566
12:28 | 4103 | 40.0227 | 201.6297 | 448.9379 | 455.5258 | -16.6045 | -41.5911 | 10.6248 | 7.4935 | 1.7321 | -0.0868 | 2.9511 | -1.1776 | 11.1638 | 3.9853 | 0.6151 | 0.6566 | 0.9586 | 0.737 | -129.625 | -1.1501 | 5.3206 | 1.79 | -3.1524 | -1.4334 | 4.4145 |  | 2.8935 | 0.0869 | 4.0107 | 3.3648 | 3.3399 | 1.0673 | 10.7313 | 14.2395 | 14.8315 | 11.0724 | 0.0001 | -0.0031 | 0.0012 | 0.0035 | 0.001 | -0.0006 | 0.007 | -0.0107 | -0.0067 | -360.2419 | 17.411 | -360.4389 | 17.6615 | -360.8081 | 18.2282 | -360.885 | 17.5999 | -352.709 | 18.7374 | -352.6537 | 16.834
12:28 | 4104 | 39.9666 | 201.5999 | 448.8391 | 455.5304 | -16.6609 | -41.6557 | 10.5835 | 7.4818 | 1.7111 | -0.1219 | 2.9365 | -1.2317 | 11.1384 | 3.9945 | 0.6154 | 0.6564 | 0.9644 | 0.7359 | -129.623 | -1.1808 | 5.3626 | 1.785 | -3.1569 | -1.566 | 4.3495 |  | 2.9353 | 0.0393 | 4.0114 | 3.3618 | 3.341 | 1.0693 | 10.751 | 14.2591 | 14.8447 | 11.0749 | -0.0006 | -0.0028 | 0.0011 | 0.0043 | 0.0008 | -0.0004 | 0.0133 | 0.0006 | -0.0152 | -360.1588 | 17.4295 | -360.5066 | 17.6944 | -360.8666 | 18.1851 | -360.7866 | 17.5383 | -352.6475 | 18.7518 | -352.7183 | 16.8607
12:28 | 4105 | 39.9917 | 201.6653 | 449.0025 | 455.504 | -16.4829 | -41.4639 | 10.6841 | 7.5589 | 1.7863 | -0.0155 | 2.9262 | -1.2412 | 11.1249 | 3.9093 | 0.6147 | 0.6563 | 0.9627 | 0.7381 | -129.5867 | -1.1725 | 5.4104 | 1.6456 | -3.1415 | -1.6381 | 4.3366 |  | 2.9724 | 0.1377 | 4.0114 | 3.3643 | 3.3382 | 1.067 | 10.7636 | 14.2836 | 14.8703 | 11.1045 | -0.0003 | -0.0029 | 0.0007 | 0.004 | 0.0012 | -0.0002 | 0.001 | 0.0027 | -0.0111 | -360.1127 | 17.3597 | -360.3927 | 17.6718 | -360.8358 | 18.2097 | -360.8481 | 17.5363 | -352.586 | 18.7107 | -352.6352 | 16.8361
12:28 | 4106 | 39.9982 | 201.7068 | 448.9758 | 455.4606 | -16.4635 | -41.4946 | 10.7229 | 7.4529 | 1.682 | -0.1708 | 2.8325 | -1.1808 | 11.2072 | 4.0035 | 0.6134 | 0.6579 | 0.9625 | 0.7372 | -129.6317 | -1.1983 | 5.3765 | 1.6071 | -3.1034 | -1.6282 | 4.2934 |  | 2.9886 | 0.1429 | 4.0119 | 3.3645 | 3.3404 | 1.0693 | 10.7451 | 14.2592 | 14.8226 | 11.0688 | 0.0002 | -0.0031 | 0.0007 | 0.0039 | 0.0006 | -0.0004 | 0.0037 | 0.0054 | -0.0173 | -360.1804 | 17.3987 | -360.3958 | 17.6266 | -360.7497 | 18.1748 | -360.8266 | 17.5671 | -352.6537 | 18.7292 | -352.6198 | 16.7971
12:28 | 4107 | 39.9584 | 201.7012 | 448.925 | 455.5531 | -16.5112 | -41.4521 | 10.6628 | 7.4741 | 1.7397 | -0.0876 | 2.9628 | -1.1532 | 11.14 | 3.9802 | 0.6127 | 0.6578 | 0.9638 | 0.7366 | -129.6937 | -1.1687 | 5.4508 | 1.6153 | -3.2483 | -1.6533 | 4.3462 |  | 2.9887 | 0.0933 | 4.0113 | 3.3643 | 3.34 | 1.0698 | 10.7857 | 14.2938 | 14.8737 | 11.0923 | 0.0001 | -0.0029 | 0.0004 | 0.0042 | 0.0009 | -0.0003 | 0.0192 | -0.0037 | 0.0009 | -360.1311 | 17.4213 | -360.5004 | 17.6923 | -360.842 | 18.1871 | -360.7927 | 17.5239 | -352.6013 | 18.7292 | -352.6813 | 16.8566
12:28 | 4108 | 39.9943 | 201.7987 | 448.9828 | 455.467 | -16.5725 | -41.5259 | 10.7331 | 7.5973 | 1.7737 | 0.0603 | 3.0143 | -1.1985 | 11.174 | 3.9883 | 0.6143 | 0.661 | 0.9633 | 0.7364 | -129.6949 | -1.1937 | 5.3613 | 1.7269 | -3.3161 | -1.6142 | 4.278 |  | 2.9604 | 0.0133 | 4.0112 | 3.3623 | 3.3414 | 1.0689 | 10.774 | 14.271 | 14.8816 | 11.0915 | -0.0003 | -0.0031 | 0.0006 | 0.0042 | 0.0008 | -0.0002 | -0.0004 | -0.004 | -0.0124 | -360.2235 | 17.3905 | -360.4296 | 17.6677 | -360.8266 | 18.2487 | -360.8974 | 17.5691 | -352.666 | 18.7189 | -352.6537 | 16.8299
12:28 | 4109 | 40.0267 | 201.8253 | 448.8491 | 455.4442 | -16.5127 | -41.3877 | 10.6867 | 7.5109 | 1.7287 | -0.0657 | 2.994 | -1.0896 | 11.1954 | 4.0487 | 0.6145 | 0.663 | 0.9601 | 0.7372 | -129.6866 | -1.2262 | 5.4961 | 1.8471 | -3.2504 | -1.6061 | 4.279 |  | 2.9261 | 0.1107 | 4.012 | 3.367 | 3.3413 | 1.068 | 10.744 | 14.2637 | 14.8433 | 11.1143 | -0.0004 | -0.0027 | 0.0009 | 0.0038 | 0.0009 | -0.001 | 0.0076 | -0.0062 | -0.0248 | -360.2512 | 17.4439 | -360.4942 | 17.6553 | -360.7958 | 18.2015 | -360.845 | 17.5855 | -352.7244 | 18.762 | -352.6937 | 16.8423
12:28 | 4110 | 40.0226 | 201.8729 | 448.8548 | 455.5482 | -16.4382 | -41.3393 | 10.7384 | 7.3806 | 1.6996 | -0.1612 | 2.9913 | -1.1734 | 11.2352 | 4.0562 | 0.6139 | 0.6586 | 0.9615 | 0.7367 | -129.6671 | -1.142 | 5.5081 | 1.8511 | -3.1919 | -1.7888 | 4.2611 |  | 2.9826 | 0.2379 | 4.0115 | 3.3652 | 3.3421 | 1.0687 | 10.7498 | 14.2695 | 14.8665 | 11.0739 | -0.0001 | -0.0032 | 0.001 | 0.0041 | 0.0007 | -0.0003 | 0.0107 | -0.0245 | -0.0148 | -360.1527 | 17.409 | -360.485 | 17.6923 | -360.8543 | 18.1974 | -360.8174 | 17.5445 | -352.626 | 18.7415 | -352.7029 | 16.8648
12:28 | 4111 | 40.0326 | 201.864 | 448.9257 | 455.5319 | -16.4914 | -41.3666 | 10.817 | 7.3324 | 1.624 | -0.124 | 3.0032 | -1.1619 | 11.2532 | 4.1398 | 0.6152 | 0.6579 | 0.9641 | 0.7353 | -129.5637 | -1.1275 | 5.5216 | 1.7714 | -3.2225 | -1.6332 | 4.2639 |  | 2.9938 | 0.1755 | 4.0109 | 3.3633 | 3.3375 | 1.0677 | 10.7429 | 14.2509 | 14.8535 | 11.067 | -0.0003 | -0.0035 | 0.0008 | 0.0038 | 0.0012 | -0.0008 | 0.0054 | 0.0016 | -0.0177 | -360.1219 | 17.3576 | -360.3742 | 17.6328 | -360.7743 | 18.2159 | -360.8758 | 17.565 | -352.6383 | 18.6881 | -352.5983 | 16.8197
12:28 | 4112 | 40.1109 | 201.7641 | 448.9775 | 455.5403 | -16.475 | -41.4459 | 10.9167 | 7.441 | 1.6022 | -0.1092 | 2.9653 | -1.2153 | 11.3263 | 4.1223 | 0.615 | 0.6549 | 0.9629 | 0.7361 | -129.5777 | -1.0897 | 5.5341 | 1.8231 | -3.2513 | -1.6138 | 4.2313 |  | 2.9634 | 0.1632 | 4.0118 | 3.3627 | 3.3416 | 1.0681 | 10.7647 | 14.256 | 14.8901 | 11.111 | 0.0001 | -0.0027 | 0.0008 | 0.0039 | 0.0007 | 0 | 0.024 | -0.0059 | -0.0201 | -360.1804 | 17.4213 | -360.4419 | 17.643 | -360.7589 | 18.1748 | -360.8297 | 17.5547 | -352.6598 | 18.7436 | -352.666 | 16.8012
12:28 | 4113 | 40.0168 | 201.7612 | 448.8905 | 455.4861 | -16.527 | -41.43 | 10.9494 | 7.4074 | 1.6902 | -0.101 | 2.8842 | -1.183 | 11.2382 | 4.044 | 0.6149 | 0.656 | 0.9587 | 0.7376 | -129.6725 | -1.2326 | 5.4227 | 1.8291 | -3.2243 | -1.596 | 4.2845 |  | 2.9957 | 0.098 | 4.0103 | 3.3638 | 3.3376 | 1.0679 | 10.759 | 14.2616 | 14.8485 | 11.1056 | -0.0002 | -0.0026 | 0.0012 | 0.0043 | 0.0012 | -0.0004 | 0.0027 | -0.0226 | -0.0035 | -360.1188 | 17.409 | -360.4912 | 17.6985 | -360.8635 | 18.2241 | -360.8297 | 17.5445 | -352.6013 | 18.7374 | -352.6906 | 16.8607
12:28 | 4114 | 40.0066 | 201.9018 | 448.889 | 455.5048 | -16.4274 | -41.4166 | 10.9774 | 7.5763 | 1.855 | 0.0016 | 2.9846 | -1.1252 | 11.217 | 4.126 | 0.6151 | 0.657 | 0.9624 | 0.7371 | -129.6074 | -1.2022 | 5.3834 | 1.8532 | -3.2174 | -1.5813 | 4.3246 |  | 2.8712 | 0.0501 | 4.012 | 3.3634 | 3.3397 | 1.0698 | 10.789 | 14.2747 | 14.8752 | 11.1117 | 0 | -0.0029 | 0.0008 | 0.0039 | 0.0011 | 0 | 0.0011 | -0.0084 | -0.0211 | -360.205 | 17.3987 | -360.4235 | 17.6738 | -360.8143 | 18.2344 | -360.885 | 17.5917 | -352.669 | 18.721 | -352.6383 | 16.832
12:28 | 4115 | 40.0895 | 201.9141 | 448.9557 | 455.5065 | -16.496 | -41.4987 | 10.8673 | 7.4813 | 1.8966 | 0.1297 | 2.9836 | -1.0727 | 11.2575 | 4.2219 | 0.6135 | 0.6575 | 0.9599 | 0.7358 | -129.6373 | -1.2677 | 5.2806 | 1.8856 | -3.2171 | -1.6193 | 4.2754 |  | 2.9106 | 0.0668 | 4.012 | 3.3636 | 3.3368 | 1.0685 | 10.759 | 14.2385 | 14.8543 | 11.1056 | 0.0005 | -0.003 | 0.0001 | 0.0039 | 0.0013 | 0 | 0.0309 | -0.0112 | 0.0218 | -360.2111 | 17.4274 | -360.4635 | 17.682 | -360.7958 | 18.1912 | -360.8358 | 17.565 | -352.669 | 18.7559 | -352.6967 | 16.8299
12:28 | 4116 | 40.0974 | 201.8175 | 448.9651 | 455.5153 | -16.4562 | -41.4657 | 10.9548 | 7.5747 | 1.9248 | 0.1092 | 2.928 | -1.055 | 11.3435 | 4.1294 | 0.6144 | 0.6593 | 0.9638 | 0.736 | -129.7025 | -1.2624 | 5.3734 | 1.8387 | -3.2132 | -1.6284 | 4.2901 |  | 2.9002 | 0.0062 | 4.0115 | 3.3633 | 3.3405 | 1.0693 | 10.7441 | 14.2635 | 14.8191 | 11.0742 | -0.0002 | -0.0028 | 0.0008 | 0.0039 | 0.0009 | -0.0003 | -0.0053 | -0.0111 | 0.002 | -360.0973 | 17.3782 | -360.4112 | 17.6759 | -360.8235 | 18.222 | -360.802 | 17.5342 | -352.5983 | 18.7004 | -352.6229 | 16.8361
12:28 | 4117 | 40.0308 | 201.8182 | 448.933 | 455.5183 | -16.5378 | -41.5336 | 10.795 | 7.6407 | 1.9305 | 0.1518 | 2.9946 | -0.9556 | 11.3295 | 4.1169 | 0.6145 | 0.6558 | 0.9635 | 0.7376 | -129.6699 | -1.1783 | 5.3396 | 1.8964 | -3.1983 | -1.5781 | 4.3426 |  | 2.8956 | -0.0068 | 4.0115 | 3.3663 | 3.3402 | 1.0712 | 10.7256 | 14.2449 | 14.8109 | 11.0562 | -0.0002 | -0.0025 | 0.0007 | 0.004 | 0.0001 | -0.0007 | 0.0083 | 0.0012 | -0.0189 | -360.1281 | 17.3884 | -360.4204 | 17.6512 | -360.7558 | 18.2077 | -360.8512 | 17.5794 | -352.6167 | 18.7189 | -352.6167 | 16.8115
12:28 | 4118 | 40.0425 | 201.828 | 449.0063 | 455.5075 | -16.4829 | -41.4082 | 10.802 | 7.6065 | 1.9117 | 0.1204 | 2.9924 | -0.9892 | 11.3254 | 4.0601 | 0.6135 | 0.6544 | 0.9577 | 0.7366 | -129.6459 | -1.1219 | 5.4149 | 1.7666 | -3.2609 | -1.6539 | 4.2819 |  | 2.92 | 0.0023 | 4.0118 | 3.3667 | 3.3396 | 1.0705 | 10.7256 | 14.2335 | 14.8293 | 11.0732 | 0 | -0.0028 | 0.0011 | 0.0039 | 0.0014 | -0.0005 | -0.0053 | -0.0156 | 0.0036 | -360.1558 | 17.4213 | -360.4942 | 17.7128 | -360.8481 | 18.1953 | -360.8174 | 17.5547 | -352.6229 | 18.7497 | -352.7029 | 16.8484
12:28 | 4119 | 40.0473 | 201.7835 | 448.8382 | 455.4443 | -16.6188 | -41.5261 | 10.752 | 7.584 | 1.9639 | 0.1 | 2.975 | -1.0461 | 11.2573 | 3.9805 | 0.6151 | 0.6579 | 0.9606 | 0.7363 | -129.7022 | -1.1586 | 5.2743 | 1.8184 | -3.2625 | -1.6461 | 4.3461 |  | 2.8532 | -0.0287 | 4.0116 | 3.3654 | 3.3407 | 1.0721 | 10.7186 | 14.244 | 14.8059 | 11.0601 | 0.0004 | -0.0028 | 0.0012 | 0.0039 | 0.0007 | -0.0006 | 0.0171 | -0.0128 | -0.0034 | -360.1927 | 17.3884 | -360.4573 | 17.6923 | -360.8481 | 18.2405 | -360.9004 | 17.5691 | -352.6352 | 18.7292 | -352.6537 | 16.8464
12:28 | 4120 | 39.9864 | 201.7946 | 448.902 | 455.5383 | -16.6541 | -41.575 | 10.6601 | 7.5125 | 1.8943 | 0.181 | 2.9703 | -1.0859 | 11.2706 | 4.0905 | 0.6139 | 0.6554 | 0.9589 | 0.7366 | -129.6387 | -1.2545 | 5.2831 | 1.699 | -3.3004 | -1.7328 | 4.2718 |  | 2.8826 | -0.0564 | 4.0111 | 3.3643 | 3.3408 | 1.0707 | 10.7532 | 14.2676 | 14.8438 | 11.0879 | 0.0003 | -0.0026 | 0.0009 | 0.0039 | 0.0013 | -0.0006 | 0.0078 | -0.0108 | -0.0221 | -360.2204 | 17.4151 | -360.4912 | 17.6718 | -360.7773 | 18.1933 | -360.8235 | 17.5588 | -352.6506 | 18.7477 | -352.6721 | 16.834
12:28 | 4121 | 40.0698 | 201.7577 | 448.9872 | 455.5632 | -16.6861 | -41.6092 | 10.5966 | 7.5586 | 1.8247 | 0.0667 | 2.965 | -1.0689 | 11.1741 | 3.959 | 0.6142 | 0.6563 | 0.9576 | 0.7391 | -129.6125 | -1.1344 | 5.3091 | 1.8072 | -3.2414 | -1.7746 | 4.2634 |  | 2.9083 | -0.0049 | 4.0106 | 3.3638 | 3.3432 | 1.0715 | 10.7729 | 14.2985 | 14.8618 | 11.1139 | -0.0003 | -0.0023 | 0.0003 | 0.0036 | 0.0004 | -0.0001 | 0.001 | -0.0006 | 0.0018 | -360.1373 | 17.3782 | -360.4389 | 17.6861 | -360.7927 | 18.1892 | -360.7989 | 17.5301 | -352.5767 | 18.7128 | -352.6413 | 16.832
12:28 | 4122 | 40.0805 | 201.8359 | 448.9643 | 455.5352 | -16.5888 | -41.5725 | 10.6799 | 7.4499 | 1.8099 | 0.1515 | 2.9442 | -1.0242 | 11.2403 | 4.1539 | 0.6135 | 0.6557 | 0.9624 | 0.7389 | -129.5785 | -1.2157 | 5.4359 | 1.8313 | -3.1726 | -1.5679 | 4.3446 |  | 2.8941 | 0.0316 | 4.0112 | 3.364 | 3.3377 | 1.0699 | 10.7856 | 14.2594 | 14.87 | 11.0915 | 0 | -0.0025 | 0.001 | 0.004 | 0.0009 | -0.0007 | 0.033 | -0.0097 | 0.0117 | -360.2081 | 17.409 | -360.445 | 17.6759 | -360.8143 | 18.1994 | -360.8574 | 17.5732 | -352.6783 | 18.7312 | -352.626 | 16.8197
12:28 | 4123 | 40.0836 | 201.8355 | 449.0074 | 455.5324 | -16.5683 | -41.5541 | 10.8172 | 7.4996 | 1.8917 | 0.1617 | 2.9813 | -0.9551 | 11.2956 | 4.0716 | 0.6146 | 0.6566 | 0.9625 | 0.7378 | -129.6345 | -1.165 | 5.4099 | 1.7033 | -3.2626 | -1.6311 | 4.3427 |  | 2.8699 | -0.013 | 4.0105 | 3.3628 | 3.3385 | 1.0691 | 10.766 | 14.28 | 14.8604 | 11.0782 | 0 | -0.0033 | 0.0004 | 0.0035 | 0.0009 | -0.0002 | 0.0036 | 0.0016 | 0.0045 | -360.1927 | 17.4233 | -360.4912 | 17.7108 | -360.8512 | 18.2015 | -360.8297 | 17.5732 | -352.6537 | 18.7559 | -352.6537 | 16.8443
12:28 | 4124 | 40.0655 | 201.9115 | 448.9235 | 455.5514 | -16.6021 | -41.5419 | 10.6908 | 7.3969 | 1.79 | 0.0122 | 2.9194 | -1.1423 | 11.2481 | 4.0824 | 0.6139 | 0.6607 | 0.9587 | 0.7379 | -129.6953 | -1.1169 | 5.4957 | 1.7896 | -3.2753 | -1.6639 | 4.3309 |  | 2.8564 | -0.0497 | 4.0087 | 3.3634 | 3.3387 | 1.0702 | 10.7453 | 14.2646 | 14.8542 | 11.1104 | 0.0003 | -0.0029 | 0.0004 | 0.0038 | 0.001 | -0.0008 | 0.0048 | 0.0018 | -0.0021 | -360.1896 | 17.4172 | -360.4666 | 17.6944 | -360.8297 | 18.2159 | -360.8604 | 17.5855 | -352.6783 | 18.7436 | -352.6875 | 16.8484
12:28 | 4125 | 40.1159 | 201.8837 | 448.9766 | 455.6649 | -16.5821 | -41.5142 | 10.7318 | 7.3874 | 1.8604 | 0.136 | 2.9633 | -1.1002 | 11.2085 | 4.0772 | 0.6131 | 0.6567 | 0.9576 | 0.7365 | -129.7138 | -1.1292 | 5.3799 | 1.8436 | -3.1474 | -1.7034 | 4.3531 |  | 2.909 | 0.0517 | 4.0107 | 3.3643 | 3.3418 | 1.0708 | 10.7234 | 14.2481 | 14.8013 | 11.0544 | -0.0004 | -0.0031 | 0.0011 | 0.0038 | 0.0003 | -0.0009 | 0.0012 | 0.0016 | -0.0105 | -360.1619 | 17.3966 | -360.4604 | 17.682 | -360.802 | 18.183 | -360.8174 | 17.5671 | -352.626 | 18.7353 | -352.666 | 16.834
12:28 | 4126 | 40.0832 | 201.8772 | 448.9387 | 455.5894 | -16.5272 | -41.5426 | 10.7464 | 7.4004 | 1.8228 | 0.0186 | 2.9718 | -1.0589 | 11.169 | 4.0636 | 0.6133 | 0.6574 | 0.963 | 0.7382 | -129.7667 | -1.1116 | 5.3045 | 1.8725 | -3.1276 | -1.647 | 4.3486 |  | 2.933 | 0.0896 | 4.0111 | 3.3629 | 3.341 | 1.0702 | 10.7429 | 14.2509 | 14.8362 | 11.0843 | -0.0002 | -0.0025 | 0.0008 | 0.0036 | 0.0012 | -0.0006 | 0.0169 | -0.0114 | -0.006 | -360.1342 | 17.3966 | -360.4204 | 17.6779 | -360.802 | 18.1912 | -360.802 | 17.5629 | -352.6198 | 18.723 | -352.6229 | 16.8238
12:28 | 4127 | 40.1498 | 201.7916 | 448.9049 | 455.6339 | -16.4967 | -41.437 | 10.6966 | 7.446 | 1.8918 | -0.0135 | 2.9018 | -1.0833 | 11.1619 | 4.0461 | 0.6133 | 0.6588 | 0.9603 | 0.7367 | -129.7046 | -1.171 | 5.4002 | 1.8845 | -3.077 | -1.6048 | 4.3818 |  | 2.9337 | 0.0631 | 4.0108 | 3.3669 | 3.3407 | 1.0699 | 10.7256 | 14.2277 | 14.8583 | 11.0558 | 0.0002 | -0.0031 | 0.0011 | 0.004 | 0.001 | -0.0005 | 0.0125 | -0.0182 | 0.0109 | -360.1311 | 17.3823 | -360.3989 | 17.6512 | -360.7866 | 18.1912 | -360.8143 | 17.5547 | -352.6106 | 18.723 | -352.6198 | 16.8053
12:29 | 4128 | 40.126 | 201.8554 | 448.978 | 455.6512 | -16.5286 | -41.3896 | 10.7021 | 7.4351 | 1.7853 | 0.0551 | 2.8945 | -1.1621 | 11.1463 | 4.0265 | 0.6141 | 0.659 | 0.9607 | 0.7366 | -129.6926 | -1.1499 | 5.4784 | 1.7814 | -3.1114 | -1.611 | 4.321 |  | 2.9809 | 0.0665 | 4.0113 | 3.367 | 3.344 | 1.0712 | 10.7798 | 14.2536 | 14.8353 | 11.0973 | 0.0001 | -0.0032 | 0.0011 | 0.004 | 0.0007 | -0.0003 | 0.0154 | -0.0005 | 0.0026 | -360.1096 | 17.4131 | -360.4727 | 17.6759 | -360.7927 | 18.1851 | -360.8112 | 17.5609 | -352.6229 | 18.7353 | -352.6598 | 16.8197
12:29 | 4129 | 40.1692 | 201.8181 | 448.9536 | 455.6819 | -16.6052 | -41.4176 | 10.7224 | 7.4683 | 1.8398 | 0.2185 | 2.978 | -1.1056 | 11.1105 | 3.9832 | 0.6146 | 0.659 | 0.96 | 0.7367 | -129.6309 | -1.0928 | 5.4535 | 1.7745 | -3.1105 | -1.5455 | 4.3477 |  | 3.0524 | 0.0886 | 4.0116 | 3.3668 | 3.3416 | 1.0704 | 10.7613 | 14.264 | 14.8976 | 11.0847 | -0.0002 | -0.0027 | 0.0005 | 0.0036 | 0.0011 | -0.0005 | 0.0095 | -0.017 | -0.0308 | -360.1835 | 17.4007 | -360.4542 | 17.6985 | -360.842 | 18.2138 | -360.8666 | 17.5896 | -352.6229 | 18.7189 | -352.6506 | 16.832
12:29 | 4130 | 40.1311 | 201.7964 | 448.9579 | 455.5821 | -16.6474 | -41.5779 | 10.7887 | 7.4371 | 1.7702 | 0.1937 | 2.9185 | -1.1562 | 11.1858 | 4.0734 | 0.6143 | 0.6581 | 0.957 | 0.7366 | -129.6207 | -1.0755 | 5.4478 | 1.744 | -3.1508 | -1.5621 | 4.335 |  | 3.0181 | 0.2257 | 4.0107 | 3.3677 | 3.3368 | 1.0694 | 10.8191 | 14.2874 | 14.8997 | 11.0897 | -0.0003 | -0.0025 | 0.0008 | 0.0042 | 0.0006 | 0.0001 | 0.0181 | 0.0039 | -0.0056 | -360.2296 | 17.4315 | -360.4881 | 17.6923 | -360.8266 | 18.2077 | -360.8574 | 17.5917 | -352.6844 | 18.7579 | -352.6813 | 16.832
12:29 | 4131 | 40.1706 | 201.8029 | 448.9957 | 455.5787 | -16.5425 | -41.6867 | 10.6554 | 7.4345 | 1.7304 | 0.0132 | 2.8701 | -1.0478 | 11.1718 | 3.9765 | 0.6141 | 0.659 | 0.961 | 0.7372 | -129.6724 | -1.0613 | 5.4426 | 1.8084 | -3.2186 | -1.6201 | 4.3447 |  | 3.0016 | 0.089 | 4.011 | 3.3646 | 3.3403 | 1.0696 | 10.7937 | 14.2385 | 14.8775 | 11.0941 | 0.0002 | -0.0028 | 0.0002 | 0.0037 | 0.0011 | -0.0005 | 0.0054 | -0.0135 | -0.0116 | -360.1527 | 17.409 | -360.4819 | 17.7087 | -360.8204 | 18.1933 | -360.8389 | 17.5629 | -352.669 | 18.7538 | -352.6906 | 16.8505
12:29 | 4132 | 40.1827 | 201.8043 | 448.9663 | 455.6303 | -16.5027 | -41.7686 | 10.6481 | 7.5099 | 1.7482 | 0.1473 | 2.8819 | -1.09 | 11.2358 | 4.1056 | 0.6134 | 0.6586 | 0.9594 | 0.7385 | -129.6573 | -0.9997 | 5.395 | 1.8275 | -3.2132 | -1.6171 | 4.35 |  | 2.9276 | 0.042 | 4.0123 | 3.3673 | 3.34 | 1.0689 | 10.7268 | 14.2576 | 14.8702 | 11.0977 | 0.0001 | -0.0036 | 0.0006 | 0.0039 | 0.0002 | -0.0005 | 0.0008 | -0.0045 | -0.0263 | -360.1342 | 17.3761 | -360.3958 | 17.6861 | -360.7989 | 18.2036 | -360.8543 | 17.5691 | -352.6198 | 18.7045 | -352.6075 | 16.8381
12:29 | 4133 | 40.1269 | 201.7306 | 448.901 | 455.5094 | -16.6311 | -41.7404 | 10.7121 | 7.3702 | 1.7088 | 0.017 | 2.8688 | -1.0905 | 11.256 | 4.0757 | 0.6137 | 0.6575 | 0.9588 | 0.7379 | -129.6027 | -1.0093 | 5.4496 | 1.7787 | -3.2133 | -1.6189 | 4.2856 |  | 2.9361 | 0.098 | 4.0121 | 3.366 | 3.3403 | 1.0695 | 10.7163 | 14.2358 | 14.8263 | 11.0869 | -0.0002 | -0.0027 | 0.0009 | 0.0043 | 0.0014 | -0.0008 | 0.008 | -0.0106 | -0.023 | -360.1896 | 17.4007 | -360.4204 | 17.643 | -360.7343 | 18.1728 | -360.8204 | 17.5691 | -352.6444 | 18.7292 | -352.6352 | 16.7971
12:29 | 4134 | 40.11 | 201.8503 | 448.9891 | 455.5964 | -16.5837 | -41.7971 | 10.727 | 7.5305 | 1.7151 | 0.0571 | 2.8919 | -1.1431 | 11.3883 | 4.077 | 0.6135 | 0.6564 | 0.9588 | 0.7375 | -129.6534 | -1.0236 | 5.4793 | 1.6432 | -3.196 | -1.628 | 4.2868 |  | 2.9404 | 0.0114 | 4.0122 | 3.3651 | 3.3387 | 1.07 | 10.7694 | 14.2547 | 14.8587 | 11.0756 | -0.0001 | -0.0028 | 0.0008 | 0.0037 | 0.0004 | -0.0004 | 0.002 | -0.0048 | -0.0201 | -360.1742 | 17.4069 | -360.485 | 17.7087 | -360.8327 | 18.1728 | -360.7989 | 17.5486 | -352.6537 | 18.7292 | -352.6629 | 16.8484
12:29 | 4135 | 40.1434 | 201.8706 | 448.9707 | 455.5819 | -16.5475 | -41.7702 | 10.6905 | 7.5534 | 1.7513 | 0.0958 | 2.9633 | -1.0699 | 11.4102 | 4.1068 | 0.614 | 0.6574 | 0.9568 | 0.7371 | -129.6133 | -0.9738 | 5.4954 | 1.5215 | -3.2257 | -1.7219 | 4.2427 |  | 2.953 | 0.1046 | 4.0115 | 3.3645 | 3.3402 | 1.0691 | 10.7381 | 14.2409 | 14.8281 | 11.0847 | 0.0001 | -0.0031 | 0.0018 | 0.0048 | 0.0008 | -0.0005 | 0.0238 | -0.0093 | -0.0057 | -360.1958 | 17.3966 | -360.4389 | 17.6861 | -360.8574 | 18.2323 | -360.8943 | 17.5876 | -352.6352 | 18.7045 | -352.629 | 16.8279
12:29 | 4136 | 40.1161 | 201.8562 | 448.9764 | 455.6114 | -16.5779 | -41.7835 | 10.6821 | 7.5518 | 1.7809 | 0.027 | 2.9681 | -1.0535 | 11.3316 | 4.0876 | 0.6129 | 0.6544 | 0.9553 | 0.7362 | -129.6276 | -0.9697 | 5.5254 | 1.568 | -3.2447 | -1.7759 | 4.2462 |  | 2.8895 | 0.0238 | 4.011 | 3.3651 | 3.3408 | 1.0698 | 10.7566 | 14.2713 | 14.8663 | 11.0966 | 0.0007 | -0.0028 | 0.001 | 0.004 | 0.0008 | -0.0005 | 0.0019 | 0.0077 | 0.0009 | -360.1927 | 17.4356 | -360.4573 | 17.6841 | -360.7681 | 18.1933 | -360.885 | 17.5835 | -352.7213 | 18.7641 | -352.6813 | 16.8238
12:29 | 4137 | 40.1111 | 201.889 | 448.9749 | 455.5392 | -16.6575 | -41.8086 | 10.7625 | 7.5379 | 1.8184 | 0.0714 | 3.0161 | -1.0221 | 11.3146 | 4.1164 | 0.613 | 0.6579 | 0.9579 | 0.7368 | -129.6468 | -0.9297 | 5.4687 | 1.6684 | -3.343 | -1.6933 | 4.2098 |  | 2.9913 | 0.0731 | 4.0112 | 3.3682 | 3.3416 | 1.0699 | 10.7764 | 14.2673 | 14.8764 | 11.0944 | -0.0002 | -0.0028 | 0.0004 | 0.0036 | 0.0009 | -0.0004 | 0.0025 | -0.0113 | -0.0069 | -360.0881 | 17.3925 | -360.4604 | 17.7005 | -360.8297 | 18.2077 | -360.8081 | 17.5321 | -352.5921 | 18.7169 | -352.6752 | 16.8464
12:29 | 4138 | 40.1813 | 201.9196 | 449.0955 | 455.5853 | -16.6176 | -41.7558 | 10.7129 | 7.4944 | 1.7983 | -0.0918 | 2.9215 | -1.0025 | 11.3147 | 4.084 | 0.614 | 0.6542 | 0.9614 | 0.7371 | -129.6534 | -1.0373 | 5.4416 | 1.7142 | -3.354 | -1.6537 | 4.2377 |  | 2.9993 | 0.0777 | 4.012 | 3.3652 | 3.3397 | 1.0703 | 10.7856 | 14.271 | 14.8642 | 11.0857 | 0 | -0.0023 | 0.0008 | 0.0042 | 0.0011 | 0 | 0.0094 | 0.0029 | -0.0187 | -360.1342 | 17.3679 | -360.3589 | 17.6512 | -360.762 | 18.1933 | -360.8758 | 17.5773 | -352.626 | 18.7045 | -352.5706 | 16.7807
12:29 | 4139 | 40.1714 | 201.936 | 449.0225 | 455.5346 | -16.589 | -41.7299 | 10.7008 | 7.5324 | 1.7993 | -0.1294 | 2.9524 | -1.1049 | 11.2529 | 4.0803 | 0.6136 | 0.6538 | 0.9589 | 0.7386 | -129.6282 | -1.1679 | 5.3948 | 1.7358 | -3.1682 | -1.6771 | 4.3339 |  | 2.8769 | 0.1268 | 4.0104 | 3.3639 | 3.3394 | 1.0697 | 10.766 | 14.2627 | 14.8604 | 11.084 | 0 | -0.0028 | 0.001 | 0.0045 | 0.001 | -0.0002 | 0.0221 | -0.0146 | 0.0026 | -360.1527 | 17.4192 | -360.4758 | 17.6779 | -360.7804 | 18.1687 | -360.7866 | 17.5547 | -352.6075 | 18.7436 | -352.666 | 16.8115
12:29 | 4140 | 40.1769 | 201.8847 | 449.0242 | 455.5213 | -16.6023 | -41.7444 | 10.624 | 7.5995 | 1.8461 | -0.1109 | 3.0064 | -1.0483 | 11.3458 | 4.1607 | 0.6154 | 0.6588 | 0.9614 | 0.7385 | -129.666 | -1.1015 | 5.2915 | 1.8915 | -3.161 | -1.5843 | 4.3346 |  | 2.939 | 0.1466 | 4.0123 | 3.3652 | 3.3416 | 1.0684 | 10.7095 | 14.2343 | 14.8228 | 11.0634 | 0 | -0.0032 | 0.0008 | 0.0042 | 0.0014 | -0.0003 | 0.019 | -0.0059 | -0.0043 | -360.125 | 17.3843 | -360.4358 | 17.7087 | -360.8789 | 18.2261 | -360.8697 | 17.5753 | -352.6075 | 18.7045 | -352.6506 | 16.8156
12:29 | 4141 | 40.1319 | 201.8212 | 448.9069 | 455.5667 | -16.5073 | -41.5246 | 10.6262 | 7.5601 | 1.8733 | 0.0367 | 3.0613 | -1.0108 | 11.2943 | 4.1407 | 0.615 | 0.6594 | 0.9614 | 0.7378 | -129.6508 | -1.2072 | 5.292 | 1.8079 | -3.1519 | -1.6019 | 4.3566 |  | 2.9183 | 0.0352 | 4.0121 | 3.3663 | 3.3431 | 1.0703 | 10.7081 | 14.2164 | 14.7967 | 11.0609 | 0.0004 | -0.0026 | 0.0014 | 0.0043 | 0.0008 | -0.0003 | 0.0143 | -0.0011 | 0.0114 | -360.2296 | 17.4192 | -360.4666 | 17.682 | -360.7712 | 18.2159 | -360.9035 | 17.6061 | -352.7121 | 18.7415 | -352.666 | 16.8074
12:29 | 4142 | 40.2276 | 201.8748 | 449.0191 | 455.6655 | -16.5336 | -41.631 | 10.7626 | 7.6197 | 1.8632 | 0.0886 | 3.0104 | -1.1226 | 11.2829 | 4.1027 | 0.6132 | 0.6576 | 0.9595 | 0.738 | -129.6522 | -1.0954 | 5.2748 | 1.9582 | -3.1327 | -1.5695 | 4.4274 |  | 3.012 | 0.0771 | 4.012 | 3.3645 | 3.3408 | 1.0695 | 10.7233 | 14.2484 | 14.844 | 11.0826 | -0.0006 | -0.0028 | 0.0008 | 0.0035 | 0.0013 | -0.0004 | 0.0126 | -0.0084 | -0.0217 | -360.1188 | 17.4213 | -360.525 | 17.721 | -360.8543 | 18.1871 | -360.805 | 17.5568 | -352.6321 | 18.7395 | -352.7429 | 16.8443
12:29 | 4143 | 40.2163 | 201.9434 | 448.8903 | 455.6443 | -16.5988 | -41.7124 | 10.6685 | 7.5256 | 1.8511 | 0.1017 | 3.045 | -1.0537 | 11.4092 | 4.0504 | 0.6122 | 0.659 | 0.9624 | 0.7396 | -129.6987 | -1.0885 | 5.3674 | 1.9126 | -3.1139 | -1.5446 | 4.3224 |  | 3.0242 | 0.1636 | 4.0102 | 3.3642 | 3.3391 | 1.068 | 10.7371 | 14.2567 | 14.8188 | 11.0843 | 0.0004 | -0.0026 | 0.0007 | 0.0037 | 0.0007 | -0.0003 | 0.0017 | 0.0015 | -0.0183 | -360.1435 | 17.3699 | -360.3773 | 17.6718 | -360.8174 | 18.2241 | -360.8758 | 17.565 | -352.6321 | 18.6861 | -352.6013 | 16.8053
12:29 | 4144 | 40.2531 | 201.925 | 449.0281 | 455.6222 | -16.59 | -41.6158 | 10.8044 | 7.4796 | 1.8356 | 0.0535 | 3.0307 | -1.0841 | 11.3653 | 4.1434 | 0.6125 | 0.6575 | 0.9587 | 0.7386 | -129.624 | -1.0747 | 5.3028 | 1.8814 | -3.1337 | -1.6786 | 4.3097 |  | 2.9976 | 0.1688 | 4.0113 | 3.3642 | 3.34 | 1.0697 | 10.7706 | 14.2615 | 14.8417 | 11.0887 | 0.0005 | -0.0031 | 0.0011 | 0.0038 | 0.0011 | -0.0008 | 0.0026 | -0.0077 | -0.0082 | -360.1958 | 17.4233 | -360.4358 | 17.6594 | -360.765 | 18.1543 | -360.7743 | 17.5732 | -352.6506 | 18.7333 | -352.669 | 16.7889
12:29 | 4145 | 40.2927 | 201.8883 | 449.0077 | 455.6591 | -16.592 | -41.5085 | 10.8181 | 7.5151 | 1.7876 | 0.1615 | 3.0292 | -1.1008 | 11.3907 | 4.1739 | 0.6136 | 0.657 | 0.9576 | 0.7383 | -129.6058 | -1.0534 | 5.2861 | 1.8539 | -3.142 | -1.5422 | 4.3671 |  | 2.9941 | 0.1778 | 4.0096 | 3.3626 | 3.3418 | 1.0682 | 10.7845 | 14.2695 | 14.8723 | 11.0912 | -0.0003 | -0.0031 | -0.0002 | 0.0031 | 0.0009 | -0.0003 | 0.0031 | -0.0104 | -0.0272 | -360.1065 | 17.4028 | -360.4973 | 17.7128 | -360.8943 | 18.2159 | -360.7927 | 17.5506 | -352.6044 | 18.7087 | -352.6752 | 16.834
12:29 | 4146 | 40.1926 | 201.8592 | 448.9655 | 455.6908 | -16.6135 | -41.5278 | 10.6611 | 7.5286 | 1.8491 | 0.1713 | 2.9905 | -1.0769 | 11.4138 | 4.1588 | 0.6153 | 0.6571 | 0.9615 | 0.7387 | -129.6541 | -1.0724 | 5.3834 | 1.8005 | -3.0858 | -1.5314 | 4.4879 |  | 2.9145 | 0.1976 | 4.0119 | 3.3648 | 3.3354 | 1.0686 | 10.7544 | 14.2455 | 14.8557 | 11.1009 | -0.0003 | -0.0025 | 0.0009 | 0.0044 | 0.0011 | -0.0004 | 0.0185 | -0.0096 | -0.0251 | -360.2081 | 17.4069 | -360.4389 | 17.6964 | -360.8297 | 18.2282 | -360.9066 | 17.6102 | -352.6783 | 18.7312 | -352.6506 | 16.8115
12:29 | 4147 | 40.2698 | 201.9341 | 448.9774 | 455.6596 | -16.6082 | -41.4719 | 10.8402 | 7.6127 | 1.8322 | 0.1238 | 3.039 | -1.0097 | 11.3158 | 4.1014 | 0.6145 | 0.6592 | 0.9606 | 0.7392 | -129.6122 | -0.8998 | 5.3611 | 1.7819 | -3.2148 | -1.5364 | 4.4088 |  | 3.0126 | 0.2235 | 4.0115 | 3.367 | 3.3394 | 1.0692 | 10.7671 | 14.2812 | 14.856 | 11.0735 | -0.0005 | -0.0028 | 0.0007 | 0.0039 | 0.0005 | -0.0004 | -0.0014 | 0.0077 | -0.0212 | -360.1988 | 17.4418 | -360.5189 | 17.7149 | -360.8574 | 18.1871 | -360.8297 | 17.5855 | -352.6844 | 18.7682 | -352.7213 | 16.8423
12:29 | 4148 | 40.2993 | 201.9394 | 448.9972 | 455.625 | -16.6385 | -41.487 | 10.773 | 7.6112 | 1.7895 | 0.1017 | 3.0365 | -0.9403 | 11.4427 | 4.2444 | 0.6133 | 0.6594 | 0.9621 | 0.7386 | -129.5591 | -0.8974 | 5.4775 | 1.8419 | -3.1044 | -1.4476 | 4.4438 |  | 2.8801 | 0.1779 | 4.0104 | 3.3638 | 3.3384 | 1.0705 | 10.7546 | 14.2622 | 14.8572 | 11.0735 | 0.0001 | -0.0031 | 0.0007 | 0.0038 | 0.0006 | -0.0003 | 0.0124 | -0.0119 | 0.0025 | -360.0758 | 17.3761 | -360.4542 | 17.7026 | -360.8297 | 18.2118 | -360.8204 | 17.5404 | -352.5983 | 18.6963 | -352.666 | 16.8258
12:29 | 4149 | 40.261 | 201.9948 | 449.0565 | 455.685 | -16.5643 | -41.5698 | 10.7522 | 7.5354 | 1.823 | 0.0663 | 2.9579 | -0.9388 | 11.4054 | 4.2093 | 0.6139 | 0.659 | 0.9651 | 0.7388 | -129.5999 | -1.0043 | 5.4018 | 1.8616 | -3.1594 | -1.4426 | 4.3994 |  | 2.8352 | 0.0524 | 4.0115 | 3.3646 | 3.3408 | 1.0716 | 10.7441 | 14.252 | 14.8423 | 11.0685 | -0.0001 | -0.0035 | 0.0013 | 0.0043 | 0.0003 | -0.0008 | 0.002 | -0.0113 | -0.0155 | -360.1804 | 17.3905 | -360.3835 | 17.6533 | -360.7712 | 18.1769 | -360.8635 | 17.5917 | -352.6537 | 18.7189 | -352.6013 | 16.7786
12:29 | 4150 | 40.2881 | 201.9836 | 449.0403 | 455.6749 | -16.6578 | -41.5342 | 10.6751 | 7.5291 | 1.791 | 0.0918 | 2.9667 | -0.9967 | 11.332 | 4.1804 | 0.6145 | 0.6604 | 0.9603 | 0.7378 | -129.6258 | -1.0326 | 5.287 | 1.7855 | -3.0857 | -1.5358 | 4.43 |  | 2.8367 | -0.0022 | 4.0116 | 3.3621 | 3.3408 | 1.069 | 10.7603 | 14.2566 | 14.8583 | 11.102 | -0.0003 | -0.0026 | 0.0008 | 0.0036 | 0.0006 | -0.0006 | 0.0123 | -0.0165 | -0.0123 | -360.1281 | 17.4172 | -360.5004 | 17.7128 | -360.8112 | 18.1728 | -360.7589 | 17.5404 | -352.6075 | 18.7353 | -352.709 | 16.8258
12:29 | 4151 | 40.2593 | 201.8594 | 448.9773 | 455.6616 | -16.6319 | -41.5822 | 10.6273 | 7.4225 | 1.8376 | 0.1266 | 2.9657 | -0.9886 | 11.3222 | 4.186 | 0.6148 | 0.6532 | 0.96 | 0.7391 | -129.6022 | -1.0522 | 5.4023 | 1.7674 | -3.1065 | -1.4357 | 4.4401 |  | 2.876 | -0.0106 | 4.0103 | 3.3652 | 3.3399 | 1.0694 | 10.7117 | 14.2426 | 14.8208 | 11.071 | -0.0004 | -0.003 | 0.0008 | 0.0036 | 0.0013 | -0.0002 | 0.0021 | -0.0175 | -0.0269 | -360.1927 | 17.3987 | -360.4358 | 17.7026 | -360.8604 | 18.2261 | -360.882 | 17.5855 | -352.6321 | 18.7189 | -352.6413 | 16.8156
12:29 | 4152 | 40.2727 | 201.8905 | 448.9941 | 455.6489 | -16.6168 | -41.5644 | 10.6831 | 7.5531 | 1.9544 | -0.0236 | 3.064 | -0.9638 | 11.3146 | 4.0689 | 0.6131 | 0.6561 | 0.9604 | 0.7394 | -129.5955 | -0.9858 | 5.3887 | 1.8511 | -3.1416 | -1.5574 | 4.3708 |  | 2.9346 | 0.0365 | 4.0107 | 3.3659 | 3.3389 | 1.0678 | 10.7511 | 14.2704 | 14.8426 | 11.0757 | -0.0001 | -0.003 | 0.0007 | 0.0039 | 0.0004 | -0.0005 | -0.0006 | 0.0036 | -0.0192 | -360.2388 | 17.45 | -360.4789 | 17.6841 | -360.7989 | 18.1912 | -360.8666 | 17.602 | -352.7152 | 18.76 | -352.6906 | 16.8053
12:29 | 4153 | 40.3273 | 201.9027 | 448.9142 | 455.7503 | -16.6137 | -41.4229 | 10.7226 | 7.5288 | 1.9388 | 0.0218 | 3.0388 | -1.0124 | 11.3304 | 4.0699 | 0.6133 | 0.6566 | 0.9627 | 0.7379 | -129.7393 | -1.0758 | 5.3103 | 1.7647 | -3.2079 | -1.582 | 4.324 |  | 2.9541 | 0.063 | 4.011 | 3.3639 | 3.3421 | 1.0703 | 10.7787 | 14.2756 | 14.8802 | 11.0962 | 0.0005 | -0.0027 | 0 | 0.0035 | 0.0009 | -0.0006 | 0.0141 | -0.0193 | -0.0005 | -360.1219 | 17.4151 | -360.5127 | 17.7169 | -360.8543 | 18.1933 | -360.8174 | 17.5609 | -352.6321 | 18.7333 | -352.7275 | 16.8443
12:29 | 4154 | 40.2707 | 201.9057 | 449.0264 | 455.7333 | -16.5996 | -41.3791 | 10.6899 | 7.5826 | 1.9338 | 0.1044 | 3.0205 | -1.0192 | 11.3883 | 3.9992 | 0.614 | 0.6569 | 0.9629 | 0.7375 | -129.6758 | -1.026 | 5.3403 | 1.742 | -3.1432 | -1.488 | 4.3832 |  | 2.978 | 0.1374 | 4.0117 | 3.3652 | 3.338 | 1.0701 | 10.7682 | 14.3114 | 14.8642 | 11.0857 | -0.0004 | -0.003 | 0.001 | 0.0042 | 0.0007 | 0 | 0.0291 | -0.0096 | -0.0024 | -360.1527 | 17.3617 | -360.3804 | 17.6677 | -360.7897 | 18.2015 | -360.8389 | 17.5753 | -352.6321 | 18.6779 | -352.6106 | 16.8012
12:29 | 4155 | 40.1811 | 201.8084 | 448.9794 | 455.6765 | -16.5686 | -41.4437 | 10.7198 | 7.6251 | 1.962 | 0.0516 | 3.1272 | -0.9422 | 11.4579 | 4.1539 | 0.6141 | 0.6593 | 0.9642 | 0.7382 | -129.6776 | -1.1083 | 5.3235 | 1.8215 | -3.0751 | -1.3867 | 4.4351 |  | 2.8705 | 0.0332 | 4.011 | 3.3629 | 3.3373 | 1.0701 | 10.7648 | 14.279 | 14.8775 | 11.1287 | -0.0001 | -0.0023 | 0.0007 | 0.004 | 0.0013 | -0.0005 | 0.0135 | 0.0005 | -0.0261 | -360.1865 | 17.4131 | -360.4419 | 17.6656 | -360.7897 | 18.1748 | -360.7958 | 17.5835 | -352.6506 | 18.7312 | -352.6506 | 16.7991
12:29 | 4156 | 40.1266 | 201.8076 | 448.9245 | 455.5972 | -16.5638 | -41.523 | 10.6812 | 7.4486 | 1.9092 | 0.0033 | 3.0239 | -1.0056 | 11.3419 | 4.0118 | 0.6145 | 0.6564 | 0.9624 | 0.739 | -129.7274 | -1.0921 | 5.3773 | 1.7236 | -3.1964 | -1.4564 | 4.3777 |  | 2.9802 | 0.1743 | 4.0114 | 3.3613 | 3.3384 | 1.0693 | 10.7602 | 14.2683 | 14.8362 | 11.1074 | 0 | -0.0031 | 0.0007 | 0.0035 | 0.0004 | -0.0001 | 0.0135 | -0.0032 | -0.0241 | -360.1558 | 17.4007 | -360.4819 | 17.7128 | -360.8512 | 18.2179 | -360.8512 | 17.5691 | -352.6229 | 18.721 | -352.669 | 16.832
12:29 | 4157 | 40.1514 | 201.7609 | 448.9495 | 455.5559 | -16.6529 | -41.5537 | 10.7153 | 7.4943 | 1.8928 | 0.0608 | 3.0115 | -1.0171 | 11.3327 | 4.1083 | 0.6131 | 0.6563 | 0.9601 | 0.7382 | -129.6756 | -1.0463 | 5.4454 | 1.8374 | -3.2102 | -1.5307 | 4.3988 |  | 3.0287 | 0.1431 | 4.0115 | 3.3645 | 3.3417 | 1.0688 | 10.7464 | 14.3006 | 14.8392 | 11.0822 | 0.0003 | -0.003 | 0.0006 | 0.0038 | 0.0003 | -0.0011 | 0.0083 | -0.0081 | 0.0053 | -360.1896 | 17.4131 | -360.4542 | 17.7005 | -360.8297 | 18.2323 | -360.8789 | 17.6102 | -352.6721 | 18.723 | -352.6783 | 16.8238
12:29 | 4158 | 40.1388 | 201.8631 | 449.0116 | 455.6743 | -16.4296 | -41.4441 | 10.7731 | 7.5042 | 1.8845 | -0.0395 | 3.0189 | -1.1527 | 11.3272 | 4.0776 | 0.6142 | 0.6565 | 0.9586 | 0.7385 | -129.6492 | -1.028 | 5.4702 | 1.7971 | -3.1468 | -1.5319 | 4.3681 |  | 3.0442 | 0.1406 | 4.0114 | 3.3682 | 3.3394 | 1.0698 | 10.7348 | 14.2428 | 14.7929 | 11.0475 | 0.0002 | -0.0028 | 0.0008 | 0.0035 | 0.0005 | -0.0006 | 0.0221 | -0.0098 | -0.0022 | -360.1958 | 17.4048 | -360.4481 | 17.6841 | -360.8081 | 18.1974 | -360.8204 | 17.5691 | -352.6136 | 18.7189 | -352.6906 | 16.8217
12:29 | 4159 | 40.2599 | 201.9014 | 449.1217 | 455.6987 | -16.5328 | -41.4522 | 10.7106 | 7.4764 | 1.9067 | 0.0353 | 2.972 | -1.1563 | 11.3614 | 4.067 | 0.6137 | 0.6587 | 0.9612 | 0.7366 | -129.6791 | -1.0487 | 5.3414 | 1.8891 | -3.1495 | -1.5565 | 4.4542 |  | 2.9412 | -0.0407 | 4.0106 | 3.3638 | 3.3382 | 1.0695 | 10.7336 | 14.2649 | 14.8505 | 11.0692 | -0.0002 | -0.0025 | 0.0011 | 0.0041 | 0.0005 | -0.0009 | 0.0155 | 0.0024 | 0.0005 | -360.1373 | 17.3925 | -360.4266 | 17.6677 | -360.7712 | 18.1871 | -360.8327 | 17.5568 | -352.589 | 18.7025 | -352.629 | 16.8074
12:29 | 4160 | 40.2609 | 201.854 | 449.0913 | 455.7543 | -16.4565 | -41.3103 | 10.822 | 7.5113 | 1.9765 | 0.2158 | 3.0144 | -1.0451 | 11.3348 | 4.1396 | 0.6133 | 0.6567 | 0.9609 | 0.7371 | -129.6174 | -1.0286 | 5.3229 | 1.7472 | -3.2302 | -1.4933 | 4.4553 |  | 2.9378 | 0.0387 | 4.0103 | 3.3644 | 3.3408 | 1.0703 | 10.7071 | 14.2379 | 14.7922 | 11.0378 | 0 | -0.0027 | 0.0002 | 0.0036 | 0.0007 | -0.0007 | 0.0071 | -0.0116 | 0.0059 | -360.2111 | 17.3966 | -360.4327 | 17.6738 | -360.7989 | 18.1769 | -360.842 | 17.5773 | -352.5952 | 18.7189 | -352.6352 | 16.8012
12:29 | 4161 | 40.234 | 201.8591 | 449.0661 | 455.739 | -16.4529 | -41.375 | 10.8795 | 7.4864 | 1.9506 | 0.2377 | 3.0155 | -1.1166 | 11.2412 | 4.1045 | 0.6142 | 0.659 | 0.9612 | 0.7405 | -129.6932 | -1.072 | 5.3736 | 1.6194 | -3.2315 | -1.5604 | 4.3528 |  | 2.8927 | 0.0568 | 4.0093 | 3.3607 | 3.3393 | 1.0696 | 10.7336 | 14.2882 | 14.8458 | 11.0803 | 0 | -0.003 | 0.0008 | 0.0042 | 0.0008 | -0.0003 | -0.0003 | -0.0215 | -0.0146 | -360.1927 | 17.4151 | -360.4666 | 17.7026 | -360.8389 | 18.2097 | -360.8635 | 17.5712 | -352.626 | 18.7251 | -352.6629 | 16.8176
12:29 | 4162 | 40.1947 | 201.8375 | 448.9858 | 455.6521 | -16.4182 | -41.4244 | 10.8537 | 7.4957 | 1.9691 | 0.2584 | 3.0174 | -1.0689 | 11.2691 | 4.0888 | 0.6141 | 0.6578 | 0.9635 | 0.7372 | -129.6578 | -1.0367 | 5.5356 | 1.6755 | -3.1908 | -1.5196 | 4.3733 |  | 2.9084 | -0.0039 | 4.0112 | 3.3642 | 3.3426 | 1.0689 | 10.7475 | 14.2844 | 14.8406 | 11.0833 | -0.0002 | -0.0028 | 0.0005 | 0.0038 | 0.0005 | -0.0008 | 0.0015 | -0.0054 | 0.0129 | -360.2111 | 17.409 | -360.4696 | 17.6964 | -360.8204 | 18.22 | -360.9004 | 17.5958 | -352.6813 | 18.7374 | -352.6537 | 16.8197
12:29 | 4163 | 40.212 | 201.8039 | 448.9982 | 455.6838 | -16.4221 | -41.3769 | 10.854 | 7.5452 | 1.9793 | 0.2827 | 3.0158 | -1.1173 | 11.2808 | 4.0972 | 0.6142 | 0.6591 | 0.9649 | 0.7371 | -129.6363 | -1.1227 | 5.5257 | 1.7832 | -3.2426 | -1.5119 | 4.4069 |  | 2.9911 | -0.006 | 4.0107 | 3.3656 | 3.3422 | 1.0696 | 10.7429 | 14.2683 | 14.8304 | 11.0497 | -0.0004 | -0.0026 | 0.0005 | 0.0041 | 0.001 | 0.0004 | 0.0072 | 0.0006 | -0.0076 | -360.1619 | 17.4048 | -360.4389 | 17.6861 | -360.7773 | 18.181 | -360.8297 | 17.5712 | -352.6444 | 18.7292 | -352.6629 | 16.8115
12:29 | 4164 | 40.2485 | 201.7574 | 448.9863 | 455.6561 | -16.4582 | -41.4167 | 10.8775 | 7.5912 | 2.0122 | 0.3521 | 3.0645 | -1.1025 | 11.242 | 4.1716 | 0.6141 | 0.6587 | 0.9611 | 0.7372 | -129.6247 | -1.0613 | 5.5634 | 1.817 | -3.2353 | -1.6123 | 4.3469 |  | 2.9587 | 0.0251 | 4.0122 | 3.3674 | 3.3434 | 1.0708 | 10.7648 | 14.2616 | 14.8659 | 11.071 | 0 | -0.0023 | 0.0007 | 0.0035 | 0.001 | -0.0008 | 0.0229 | -0.005 | 0.0189 | -360.1096 | 17.3884 | -360.4389 | 17.6902 | -360.8204 | 18.1871 | -360.8081 | 17.5506 | -352.5675 | 18.7025 | -352.6813 | 16.8176
12:29 | 4165 | 40.2143 | 201.6615 | 449.0493 | 455.623 | -16.5075 | -41.474 | 10.8406 | 7.5721 | 1.9455 | 0.2101 | 3.0678 | -1.1772 | 11.1654 | 4.0333 | 0.6138 | 0.6542 | 0.9603 | 0.7363 | -129.6934 | -1.034 | 5.4555 | 1.774 | -3.2136 | -1.6274 | 4.3889 |  | 2.8836 | 0.0231 | 4.0103 | 3.3605 | 3.3396 | 1.0692 | 10.7429 | 14.2508 | 14.893 | 11.0905 | 0.0001 | -0.0032 | 0.0007 | 0.0037 | 0.0007 | -0.0003 | -0.0016 | -0.0097 | -0.0188 | -360.1465 | 17.3782 | -360.3958 | 17.6759 | -360.7958 | 18.2159 | -360.8512 | 17.5794 | -352.6167 | 18.6922 | -352.5983 | 16.8053
12:29 | 4166 | 40.2732 | 201.7687 | 449.0009 | 455.7177 | -16.4639 | -41.4966 | 10.9369 | 7.5394 | 1.9461 | 0.2461 | 3.0137 | -1.1398 | 11.1996 | 3.9558 | 0.6151 | 0.6557 | 0.9677 | 0.7378 | -129.6556 | -0.9827 | 5.4378 | 1.7061 | -3.1935 | -1.584 | 4.3362 |  | 2.8395 | 0.1057 | 4.0099 | 3.3626 | 3.3379 | 1.0682 | 10.7371 | 14.2508 | 14.8351 | 11.0905 | -0.0001 | -0.003 | 0.0005 | 0.0032 | 0.0013 | -0.0005 | 0.0029 | -0.0117 | -0.0114 | -360.2173 | 17.4459 | -360.5035 | 17.7128 | -360.845 | 18.1994 | -360.8204 | 17.5917 | -352.6906 | 18.7518 | -352.7029 | 16.8217
12:29 | 4167 | 40.3045 | 201.8461 | 448.9677 | 455.7137 | -16.4165 | -41.3983 | 10.9944 | 7.5433 | 2.0351 | 0.1582 | 2.9747 | -1.1691 | 11.2774 | 4.0985 | 0.6143 | 0.6555 | 0.9623 | 0.7372 | -129.7008 | -1.0468 | 5.39 | 1.7516 | -3.2664 | -1.5989 | 4.2791 |  | 2.812 | -0.0187 | 4.011 | 3.3663 | 3.3395 | 1.0714 | 10.7463 | 14.2893 | 14.8703 | 11.0814 | -0.0004 | -0.0027 | 0.0007 | 0.0036 | 0.0009 | -0.0003 | 0.0194 | -0.008 | 0.0108 | -360.1188 | 17.3946 | -360.4942 | 17.7293 | -360.9004 | 18.2159 | -360.8574 | 17.5588 | -352.6198 | 18.7148 | -352.6937 | 16.8402
12:29 | 4168 | 40.307 | 201.7901 | 449.0359 | 455.681 | -16.3528 | -41.2637 | 10.918 | 7.556 | 2.0601 | 0.0939 | 3.0142 | -1.1127 | 11.2791 | 4.1739 | 0.6139 | 0.6552 | 0.9634 | 0.7373 | -129.6337 | -1.0155 | 5.4375 | 1.7394 | -3.1851 | -1.6247 | 4.3463 |  | 2.8697 | 0.0015 | 4.0118 | 3.3664 | 3.3407 | 1.0699 | 10.7787 | 14.2637 | 14.8839 | 11.0796 | -0.0003 | -0.0023 | 0.0009 | 0.0041 | 0.0011 | -0.0005 | 0.003 | -0.0165 | -0.0086 | -360.1958 | 17.4069 | -360.4112 | 17.6677 | -360.7558 | 18.1912 | -360.882 | 17.5937 | -352.6783 | 18.721 | -352.626 | 16.7889
12:29 | 4169 | 40.2562 | 201.8152 | 449.1224 | 455.7187 | -16.4332 | -41.3595 | 10.9141 | 7.6209 | 2.046 | 0.1829 | 3.089 | -1.1076 | 11.3344 | 4.1549 | 0.615 | 0.6567 | 0.9644 | 0.7389 | -129.5684 | -1.0559 | 5.4466 | 1.7229 | -3.2464 | -1.5686 | 4.351 |  | 2.9138 | 0.0127 | 4.0103 | 3.3646 | 3.3388 | 1.0697 | 10.7556 | 14.2581 | 14.8618 | 11.1024 | 0.0004 | -0.0029 | 0.0006 | 0.004 | 0.0004 | -0.0009 | 0.0128 | -0.0079 | 0.0114 | -360.1527 | 17.4028 | -360.4727 | 17.7026 | -360.7958 | 18.1502 | -360.7712 | 17.526 | -352.629 | 18.7271 | -352.6598 | 16.8238
12:29 | 4170 | 40.201 | 201.8407 | 449.0795 | 455.7392 | -16.3795 | -41.3387 | 10.976 | 7.5498 | 1.9043 | 0.0566 | 3.0973 | -1.1324 | 11.3133 | 4.1623 | 0.6155 | 0.6556 | 0.9623 | 0.7377 | -129.5591 | -1.0458 | 5.3903 | 1.7031 | -3.2656 | -1.7467 | 4.4263 |  | 2.9353 | 0.0811 | 4.0108 | 3.3686 | 3.3413 | 1.0702 | 10.7521 | 14.2372 | 14.8982 | 11.1049 | 0.0001 | -0.0031 | 0.0009 | 0.0042 | 0.0008 | -0.0005 | 0.0057 | 0.0007 | 0.0001 | -360.1311 | 17.372 | -360.4081 | 17.6861 | -360.8204 | 18.1953 | -360.8543 | 17.5465 | -352.5983 | 18.6922 | -352.6106 | 16.8012
12:29 | 4171 | 40.2394 | 201.8433 | 449.0557 | 455.7498 | -16.449 | -41.356 | 11.0783 | 7.5335 | 1.936 | 0.0802 | 2.9978 | -1.1391 | 11.3573 | 4.123 | 0.6132 | 0.6589 | 0.9642 | 0.7379 | -129.6435 | -1.0741 | 5.4022 | 1.7387 | -3.3301 | -1.6196 | 4.3495 |  | 2.9742 | 0.0074 | 4.0116 | 3.366 | 3.3411 | 1.0686 | 10.7544 | 14.2917 | 14.8441 | 11.0894 | -0.0004 | -0.0026 | 0.0009 | 0.004 | 0.0011 | -0.0003 | 0.0148 | -0.0047 | -0.0001 | -360.2111 | 17.4377 | -360.4727 | 17.6779 | -360.7958 | 18.144 | -360.8143 | 17.5753 | -352.6629 | 18.7415 | -352.669 | 16.7971
12:29 | 4172 | 40.2672 | 201.8321 | 449.0148 | 455.6984 | -16.3862 | -41.3388 | 10.9956 | 7.6336 | 1.9652 | 0.1933 | 2.9924 | -1.0464 | 11.3372 | 4.2308 | 0.6148 | 0.6557 | 0.965 | 0.7379 | -129.6197 | -1.0892 | 5.3735 | 1.7795 | -3.2039 | -1.5442 | 4.3365 |  | 2.9483 | 0.0176 | 4.012 | 3.3653 | 3.3407 | 1.0672 | 10.7509 | 14.2592 | 14.8747 | 11.0919 | -0.0001 | -0.0026 | 0.0007 | 0.0039 | 0.0009 | 0 | 0.007 | -0.0072 | -0.0175 | -360.1496 | 17.411 | -360.4819 | 17.7313 | -360.9035 | 18.1892 | -360.8266 | 17.5527 | -352.6044 | 18.7107 | -352.7152 | 16.8443
12:29 | 4173 | 40.1454 | 201.7617 | 448.9711 | 455.6551 | -16.3255 | -41.3827 | 10.9371 | 7.5926 | 1.9946 | 0.1542 | 2.9767 | -1.0668 | 11.3128 | 4.2429 | 0.6143 | 0.6578 | 0.9638 | 0.738 | -129.6335 | -1.1074 | 5.3322 | 1.7356 | -3.2048 | -1.6594 | 4.2926 |  | 2.9486 | 0.0208 | 4.0119 | 3.3609 | 3.3416 | 1.0674 | 10.758 | 14.2715 | 14.8787 | 11.0883 | -0.0002 | -0.0032 | 0.0008 | 0.0035 | 0.0011 | -0.0004 | 0.0147 | -0.0199 | 0.0026 | -360.2388 | 17.4172 | -360.445 | 17.6841 | -360.7958 | 18.1933 | -360.9066 | 17.6204 | -352.709 | 18.7128 | -352.626 | 16.8115
12:29 | 4174 | 40.1984 | 201.8056 | 449.0372 | 455.7332 | -16.4213 | -41.3334 | 10.8949 | 7.6349 | 1.9741 | 0.1905 | 3.0642 | -1.0234 | 11.3346 | 4.1876 | 0.615 | 0.6589 | 0.9636 | 0.7396 | -129.6657 | -1.0629 | 5.377 | 1.729 | -3.2157 | -1.6281 | 4.303 |  | 2.899 | 0.0698 | 4.0111 | 3.366 | 3.3399 | 1.0693 | 10.7325 | 14.2404 | 14.8539 | 11.0973 | 0 | -0.0031 | 0.0007 | 0.0034 | 0.0007 | -0.0004 | 0.0154 | -0.0211 | -0.0096 | -360.1896 | 17.4336 | -360.5127 | 17.7252 | -360.8389 | 18.1502 | -360.8297 | 17.5671 | -352.669 | 18.7579 | -352.7244 | 16.8464
12:29 | 4175 | 40.2623 | 201.8831 | 449.0303 | 455.8084 | -16.3917 | -41.3367 | 10.7873 | 7.5675 | 1.9718 | 0.211 | 3.0605 | -1.0539 | 11.3125 | 4.1476 | 0.6145 | 0.6573 | 0.9632 | 0.7388 | -129.6947 | -0.913 | 5.386 | 1.7923 | -3.1728 | -1.5936 | 4.3687 |  | 2.9389 | 0.0554 | 4.0096 | 3.364 | 3.3419 | 1.0686 | 10.7383 | 14.2345 | 14.8123 | 11.0688 | -0.0006 | -0.003 | 0.0007 | 0.0035 | 0.001 | -0.0009 | 0.0132 | -0.0131 | 0.0039 | -360.1681 | 17.3823 | -360.4235 | 17.6882 | -360.8235 | 18.2056 | -360.8666 | 17.5958 | -352.629 | 18.7045 | -352.6413 | 16.8238
12:29 | 4176 | 40.2157 | 201.8923 | 449.0975 | 455.8216 | -16.4457 | -41.3071 | 10.9245 | 7.6033 | 2.0368 | 0.2046 | 3.1272 | -1.1492 | 11.3224 | 4.1048 | 0.6145 | 0.6586 | 0.9644 | 0.7387 | -129.6135 | -0.9624 | 5.381 | 1.7784 | -3.2461 | -1.5461 | 4.3722 |  | 2.9347 | 0.0249 | 4.0105 | 3.3637 | 3.3402 | 1.0693 | 10.7545 | 14.2625 | 14.8304 | 11.0728 | 0.0001 | -0.0024 | 0.0007 | 0.004 | 0.0005 | -0.0004 | 0.0208 | -0.0095 | -0.0153 | -360.1619 | 17.4131 | -360.4419 | 17.6656 | -360.762 | 18.1358 | -360.8235 | 17.5937 | -352.6844 | 18.7374 | -352.6413 | 16.7991
12:29 | 4177 | 40.1986 | 201.9332 | 449.0741 | 455.8224 | -16.4021 | -41.3297 | 10.913 | 7.5239 | 1.9412 | 0.2444 | 3.1109 | -1.1682 | 11.2904 | 4.136 | 0.614 | 0.6544 | 0.9661 | 0.7393 | -129.623 | -0.9588 | 5.3624 | 1.7851 | -3.2815 | -1.5793 | 4.2852 |  | 2.9029 | 0.0473 | 4.011 | 3.3643 | 3.3418 | 1.07 | 10.7209 | 14.2579 | 14.8144 | 11.0276 | 0.0001 | -0.0031 | 0.0004 | 0.004 | 0.0005 | -0.0007 | 0.0208 | -0.0085 | -0.0042 | -360.1188 | 17.3782 | -360.4296 | 17.6985 | -360.8204 | 18.1666 | -360.7927 | 17.5568 | -352.5706 | 18.7045 | -352.626 | 16.8299
12:29 | 4178 | 40.1871 | 201.8906 | 449.0113 | 455.7814 | -16.4075 | -41.3351 | 10.7432 | 7.6417 | 1.8963 | 0.0923 | 3.0554 | -1.1488 | 11.3311 | 4.1304 | 0.616 | 0.6585 | 0.9662 | 0.738 | -129.6303 | -1.0058 | 5.3393 | 1.6815 | -3.282 | -1.6708 | 4.3617 |  | 2.9348 | 0.0772 | 4.0117 | 3.3616 | 3.3391 | 1.0702 | 10.781 | 14.2718 | 14.8692 | 11.0934 | 0.0002 | -0.003 | 0.0005 | 0.004 | 0.0005 | -0.0003 | -0.001 | -0.0005 | -0.0075 | -360.1588 | 17.3905 | -360.3927 | 17.6697 | -360.7743 | 18.1645 | -360.845 | 17.6081 | -352.626 | 18.7087 | -352.5952 | 16.793
12:29 | 4179 | 40.2027 | 201.8506 | 449.0963 | 455.7253 | -16.5015 | -41.4661 | 10.7073 | 7.615 | 1.9168 | 0.2385 | 3.0536 | -1.1974 | 11.2537 | 4.0143 | 0.6148 | 0.6541 | 0.9642 | 0.7382 | -129.6451 | -1.0115 | 5.3385 | 1.7585 | -3.232 | -1.5576 | 4.378 |  | 2.9524 | 0.0588 | 4.0107 | 3.3611 | 3.3397 | 1.0687 | 10.7669 | 14.2818 | 14.8892 | 11.1067 | -0.0001 | -0.0025 | 0.0006 | 0.0041 | 0.0011 | -0.0002 | 0.0245 | -0.0007 | 0.003 | -360.1496 | 17.4274 | -360.4727 | 17.6944 | -360.8174 | 18.1625 | -360.7835 | 17.5958 | -352.6506 | 18.723 | -352.6783 | 16.8258
12:29 | 4180 | 40.2415 | 201.8425 | 449.074 | 455.7752 | -16.505 | -41.351 | 10.6219 | 7.5448 | 1.8271 | 0.1607 | 2.9863 | -1.2213 | 11.2003 | 4.1046 | 0.6149 | 0.6537 | 0.9619 | 0.7395 | -129.5555 | -0.9921 | 5.4613 | 1.6449 | -3.2894 | -1.6398 | 4.3463 |  | 2.9744 | 0.048 | 4.0115 | 3.3627 | 3.3385 | 1.0688 | 10.7463 | 14.2545 | 14.8519 | 11.076 | -0.0002 | -0.0026 | 0.0008 | 0.0034 | 0.0005 | -0.0005 | 0.0121 | -0.0155 | -0.0211 | -360.1988 | 17.411 | -360.4881 | 17.719 | -360.8543 | 18.2097 | -360.8758 | 17.5978 | -352.666 | 18.7189 | -352.6629 | 16.8299
12:29 | 4181 | 40.2262 | 201.8233 | 449.1015 | 455.8131 | -16.4981 | -41.3098 | 10.7236 | 7.6108 | 1.8319 | 0.1137 | 3.0784 | -1.1974 | 11.2503 | 4.1025 | 0.615 | 0.6595 | 0.9621 | 0.7398 | -129.5836 | -0.9196 | 5.4037 | 1.6465 | -3.2034 | -1.6224 | 4.3479 |  | 3.0047 | 0.0134 | 4.0112 | 3.3629 | 3.3417 | 1.07 | 10.7636 | 14.2778 | 14.8471 | 11.0814 | 0.0001 | -0.0025 | 0.0007 | 0.0035 | 0.0008 | -0.0004 | 0.025 | -0.0039 | 0.0141 | -360.2019 | 17.4172 | -360.4973 | 17.7108 | -360.8235 | 18.1912 | -360.8727 | 17.5958 | -352.6537 | 18.7374 | -352.6752 | 16.832
12:29 | 4182 | 40.2642 | 201.8833 | 449.1113 | 455.805 | -16.5907 | -41.4724 | 10.6466 | 7.5924 | 1.8977 | -0.0617 | 3.0341 | -1.0786 | 11.231 | 4.1202 | 0.6139 | 0.6572 | 0.9639 | 0.7381 | -129.5993 | -0.9738 | 5.4628 | 1.6442 | -3.1446 | -1.5307 | 4.3353 |  | 2.954 | 0.0328 | 4.012 | 3.3605 | 3.3409 | 1.0703 | 10.7382 | 14.2406 | 14.826 | 11.0796 | 0 | -0.0031 | 0.001 | 0.0036 | 0.0004 | -0.0006 | 0.0087 | -0.0076 | 0.0064 | -360.1496 | 17.4028 | -360.4542 | 17.7149 | -360.8297 | 18.1769 | -360.8543 | 17.5917 | -352.6352 | 18.7189 | -352.6567 | 16.834
12:29 | 4183 | 40.3387 | 201.8676 | 449.0548 | 455.8092 | -16.5108 | -41.4822 | 10.7714 | 7.6403 | 1.8648 | -0.0087 | 3.068 | -1.1502 | 11.2421 | 4.1724 | 0.6151 | 0.6595 | 0.9606 | 0.7398 | -129.6439 | -1.1364 | 5.407 | 1.6642 | -3.1568 | -1.5838 | 4.3072 |  | 2.9446 | 0.0637 | 4.0114 | 3.3635 | 3.3411 | 1.0692 | 10.7419 | 14.2318 | 14.7901 | 11.0617 | -0.0003 | -0.003 | 0.0008 | 0.0036 | 0.0005 | -0.0007 | -0.0033 | -0.0086 | -0.0107 | -360.1681 | 17.4048 | -360.4327 | 17.68 | -360.7866 | 18.1625 | -360.8297 | 17.5835 | -352.6321 | 18.7025 | -352.6444 | 16.8115
12:29 | 4184 | 40.2916 | 201.7939 | 449.0401 | 455.848 | -16.5973 | -41.4306 | 10.7895 | 7.5312 | 1.7685 | 0.0537 | 3.0237 | -1.1551 | 11.1797 | 4.1223 | 0.6137 | 0.6577 | 0.961 | 0.7374 | -129.6006 | -0.9429 | 5.377 | 1.5901 | -3.1175 | -1.5145 | 4.379 |  | 2.9238 | 0.0493 | 4.011 | 3.3617 | 3.3415 | 1.0711 | 10.7463 | 14.2314 | 14.8461 | 11.0818 | 0.0001 | -0.0024 | 0.0007 | 0.0041 | 0.0011 | -0.0009 | 0.0299 | -0.0187 | 0.0112 | -360.1342 | 17.3946 | -360.4512 | 17.6759 | -360.7804 | 18.1543 | -360.7835 | 17.5568 | -352.589 | 18.7004 | -352.6383 | 16.8217
12:29 | 4185 | 40.3094 | 201.8007 | 449.0635 | 455.7487 | -16.4858 | -41.4549 | 10.8236 | 7.6008 | 1.8821 | 0.0101 | 3.0719 | -1.1513 | 11.2202 | 4.1929 | 0.614 | 0.6563 | 0.961 | 0.7382 | -129.6701 | -0.9635 | 5.4661 | 1.8111 | -3.1607 | -1.6455 | 4.3211 |  | 2.9401 | 0.0468 | 4.0107 | 3.3627 | 3.3392 | 1.0706 | 10.7302 | 14.2498 | 14.829 | 11.0775 | 0.0001 | -0.0028 | 0.0007 | 0.0041 | 0.0004 | -0.0003 | 0.0178 | -0.0118 | -0.0096 | -360.1588 | 17.374 | -360.3958 | 17.6718 | -360.7743 | 18.1728 | -360.8543 | 17.5855 | -352.6198 | 18.6779 | -352.5921 | 16.8074
12:29 | 4186 | 40.2959 | 201.8986 | 449.1409 | 455.8393 | -16.5422 | -41.4349 | 10.8973 | 7.5586 | 1.9042 | 0.046 | 3.1115 | -1.0107 | 11.2821 | 4.2638 | 0.6141 | 0.6616 | 0.9612 | 0.7385 | -129.7119 | -1.0225 | 5.4186 | 1.7466 | -3.2235 | -1.5722 | 4.3056 |  | 2.9316 | 0.0771 | 4.0127 | 3.3625 | 3.3389 | 1.0692 | 10.7325 | 14.2346 | 14.8191 | 11.0627 | 0.0006 | -0.0026 | 0.0005 | 0.0038 | 0.0009 | -0.0005 | -0.0017 | -0.0193 | -0.0142 | -360.1773 | 17.411 | -360.445 | 17.6841 | -360.7743 | 18.1461 | -360.8112 | 17.5773 | -352.6352 | 18.7045 | -352.6229 | 16.7971
12:29 | 4187 | 40.297 | 201.889 | 449.0699 | 455.7928 | -16.5447 | -41.4022 | 10.8175 | 7.5346 | 1.901 | -0.0728 | 3.0278 | -1.0565 | 11.2608 | 4.2397 | 0.6143 | 0.6591 | 0.9656 | 0.739 | -129.718 | -1.0354 | 5.3727 | 1.7888 | -3.1543 | -1.5821 | 4.3633 |  | 3.008 | 0.2232 | 4.0118 | 3.3642 | 3.3384 | 1.0689 | 10.7498 | 14.229 | 14.8376 | 11.097 | 0.0001 | -0.0028 | 0.0007 | 0.0037 | 0.0007 | 0 | 0.011 | -0.0003 | -0.0049 | -360.1435 | 17.4151 | -360.5127 | 17.721 | -360.8543 | 18.1707 | -360.8358 | 17.5732 | -352.6229 | 18.7128 | -352.6967 | 16.8402
12:30 | 4188 | 40.4143 | 201.987 | 449.1199 | 455.7847 | -16.4011 | -41.3377 | 10.8996 | 7.5471 | 1.8037 | -0.0684 | 2.9816 | -1.0411 | 11.2458 | 4.1718 | 0.6136 | 0.6543 | 0.96 | 0.739 | -129.7712 | -1.1226 | 5.2908 | 1.7008 | -3.2864 | -1.6324 | 4.2859 |  | 2.9664 | 0.1533 | 4.0111 | 3.3629 | 3.3402 | 1.0684 | 10.7856 | 14.2883 | 14.8584 | 11.1146 | -0.0003 | -0.0026 | 0.001 | 0.0033 | 0.0009 | -0.0005 | -0.0099 | -0.0034 | -0.0139 | -360.1773 | 17.3966 | -360.4142 | 17.7046 | -360.8481 | 18.1994 | -360.9035 | 17.6102 | -352.6844 | 18.6943 | -352.6383 | 16.8053
12:30 | 4189 | 40.4014 | 201.9196 | 449.1088 | 455.7767 | -16.4358 | -41.344 | 10.8561 | 7.5175 | 1.9348 | -0.0432 | 3.029 | -0.9964 | 11.3171 | 4.0819 | 0.615 | 0.6551 | 0.964 | 0.7394 | -129.6832 | -0.9722 | 5.3176 | 1.6342 | -3.2628 | -1.6831 | 4.2801 |  | 2.987 | 0.1815 | 4.0122 | 3.3644 | 3.3405 | 1.0689 | 10.7579 | 14.2601 | 14.8855 | 11.088 | 0 | -0.0027 | 0.0008 | 0.0036 | 0.0006 | -0.0004 | 0.0047 | -0.0139 | -0.0219 | -360.1773 | 17.4541 | -360.5219 | 17.7149 | -360.8235 | 18.1543 | -360.8112 | 17.604 | -352.7029 | 18.7436 | -352.709 | 16.8381
12:30 | 4190 | 40.3547 | 201.9021 | 449.0341 | 455.7702 | -16.3929 | -41.3418 | 10.9627 | 7.5429 | 1.889 | -0.0978 | 3.0879 | -0.9743 | 11.3294 | 4.1292 | 0.6145 | 0.6562 | 0.9629 | 0.7389 | -129.6035 | -0.936 | 5.4563 | 1.7234 | -3.2589 | -1.5224 | 4.3113 |  | 2.9172 | 0.0254 | 4.0115 | 3.3664 | 3.3401 | 1.07 | 10.7256 | 14.2566 | 14.8409 | 11.0905 | 0 | -0.0033 | 0.001 | 0.0039 | 0.0006 | -0.001 | 0.0017 | -0.0029 | 0.0034 | -360.1219 | 17.374 | -360.4358 | 17.7087 | -360.8543 | 18.2036 | -360.8481 | 17.5712 | -352.6167 | 18.6799 | -352.6383 | 16.8361
12:30 | 4191 | 40.2759 | 201.915 | 449.1566 | 455.7387 | -16.4422 | -41.3847 | 11.0157 | 7.6014 | 1.8808 | -0.0131 | 3.0811 | -1.0702 | 11.312 | 4.1624 | 0.6147 | 0.6554 | 0.9597 | 0.7387 | -129.7193 | -1.0001 | 5.5622 | 1.72 | -3.2501 | -1.5802 | 4.3626 |  | 3.0047 | 0.0775 | 4.0121 | 3.3646 | 3.3412 | 1.0694 | 10.7463 | 14.2431 | 14.8471 | 11.0756 | 0.0002 | -0.0027 | 0.001 | 0.0039 | 0.0006 | -0.0004 | 0.0188 | -0.0221 | -0.0141 | -360.1742 | 17.3946 | -360.4019 | 17.6636 | -360.7343 | 18.1481 | -360.8297 | 17.5958 | -352.666 | 18.7025 | -352.6167 | 16.7909
12:30 | 4192 | 40.3316 | 201.9156 | 449.1187 | 455.8233 | -16.3808 | -41.446 | 10.8842 | 7.6325 | 1.9219 | -0.1052 | 3.0165 | -1.047 | 11.2595 | 4.0437 | 0.6134 | 0.6574 | 0.9618 | 0.7388 | -129.7194 | -0.9675 | 5.4423 | 1.7085 | -3.3466 | -1.6231 | 4.2491 |  | 2.9882 | 0.0564 | 4.0137 | 3.365 | 3.3382 | 1.0703 | 10.7546 | 14.2622 | 14.8109 | 11.0793 | -0.0005 | -0.003 | 0.0007 | 0.0039 | 0.0001 | -0.0013 | 0.0031 | -0.0025 | -0.0095 | -360.125 | 17.4007 | -360.4758 | 17.7231 | -360.8697 | 18.1645 | -360.7835 | 17.5588 | -352.5521 | 18.7025 | -352.6752 | 16.8381
12:30 | 4193 | 40.4293 | 201.98 | 449.238 | 455.9555 | -16.4555 | -41.4357 | 10.751 | 7.649 | 1.9153 | -0.1076 | 3.0636 | -1.1099 | 11.2529 | 4.0313 | 0.614 | 0.6531 | 0.9588 | 0.7391 | -129.524 | -0.9853 | 5.4984 | 1.7373 | -3.322 | -1.5653 | 4.2587 |  | 2.9547 | 0.0181 | 4.0122 | 3.3636 | 3.3393 | 1.0688 | 10.7717 | 14.2687 | 14.851 | 11.1005 | -0.0002 | -0.0028 | 0.0005 | 0.0041 | 0.0009 | -0.0001 | -0.002 | -0.0156 | 0.0021 | -360.2111 | 17.3884 | -360.4266 | 17.6964 | -360.8327 | 18.2015 | -360.9035 | 17.6061 | -352.6721 | 18.6963 | -352.629 | 16.7971
12:30 | 4194 | 40.4731 | 201.9657 | 449.1996 | 456.0217 | -16.4934 | -41.4422 | 10.7363 | 7.6101 | 1.9128 | -0.0391 | 3.0619 | -1.1478 | 11.2769 | 4.0805 | 0.6163 | 0.6589 | 0.9619 | 0.7378 | -129.5444 | -0.9004 | 5.5222 | 1.7675 | -3.2838 | -1.5981 | 4.3066 |  | 2.9549 | 0.0863 | 4.0116 | 3.3667 | 3.3415 | 1.0697 | 10.7672 | 14.2695 | 14.8723 | 11.0681 | 0.0002 | -0.0034 | 0.0005 | 0.0037 | 0.0009 | -0.0005 | 0.0061 | -0.01 | -0.0153 | -360.2142 | 17.4439 | -360.5281 | 17.7252 | -360.8266 | 18.1543 | -360.805 | 17.5937 | -352.7213 | 18.7477 | -352.7244 | 16.8361
12:30 | 4195 | 40.4404 | 201.8831 | 449.2268 | 455.9302 | -16.444 | -41.2952 | 10.7537 | 7.5698 | 1.9009 | 0.1335 | 3.0655 | -1.1013 | 11.2849 | 4.0781 | 0.6147 | 0.6598 | 0.96 | 0.7393 | -129.5372 | -0.982 | 5.5306 | 1.7409 | -3.3502 | -1.582 | 4.2826 |  | 2.9266 | 0.0743 | 4.0103 | 3.3666 | 3.3382 | 1.0688 | 10.7071 | 14.2437 | 14.7922 | 11.0725 | 0.0001 | -0.0029 | 0.0007 | 0.0038 | 0.001 | -0.0006 | 0.0138 | -0.0183 | -0.013 | -360.1158 | 17.3679 | -360.4142 | 17.6985 | -360.8389 | 18.1789 | -360.8543 | 17.5691 | -352.6013 | 18.6779 | -352.6198 | 16.834
12:30 | 4196 | 40.4025 | 201.9292 | 449.2541 | 455.9209 | -16.4887 | -41.2986 | 10.7846 | 7.5821 | 1.8933 | -0.0081 | 3.0934 | -1.146 | 11.3215 | 4.0461 | 0.614 | 0.6583 | 0.9635 | 0.7393 | -129.6752 | -0.943 | 5.5517 | 1.7109 | -3.2802 | -1.6568 | 4.2225 |  | 2.9615 | 0.1297 | 4.0116 | 3.3693 | 3.3406 | 1.0688 | 10.7635 | 14.2665 | 14.8666 | 11.0922 | -0.0001 | -0.0024 | 0.0013 | 0.0038 | 0.0006 | 0.0001 | 0.0059 | -0.0183 | -0.0005 | -360.2019 | 17.409 | -360.4142 | 17.6451 | -360.7281 | 18.1358 | -360.802 | 17.5876 | -352.6721 | 18.7087 | -352.6352 | 16.7766
12:30 | 4197 | 40.456 | 201.9328 | 449.2504 | 455.8945 | -16.4734 | -41.2551 | 10.8893 | 7.547 | 1.8804 | -0.0539 | 3.003 | -1.1929 | 11.3352 | 4.1612 | 0.6139 | 0.6582 | 0.9624 | 0.7391 | -129.6623 | -1.0101 | 5.4567 | 1.731 | -3.3236 | -1.7126 | 4.2151 |  | 3.0252 | 0.1004 | 4.0102 | 3.3631 | 3.3404 | 1.0697 | 10.7568 | 14.2821 | 14.8552 | 11.0753 | -0.0006 | -0.0029 | 0.0002 | 0.0033 | 0.0006 | -0.001 | 0.0086 | -0.0051 | -0.0084 | -360.1435 | 17.4007 | -360.5189 | 17.7334 | -360.8697 | 18.1748 | -360.8297 | 17.5588 | -352.5921 | 18.7045 | -352.666 | 16.8381
12:30 | 4198 | 40.4631 | 201.941 | 449.2078 | 455.8348 | -16.5184 | -41.3558 | 10.8282 | 7.5526 | 1.9131 | -0.0934 | 2.9898 | -1.1271 | 11.2509 | 4.0691 | 0.6138 | 0.6567 | 0.9636 | 0.7382 | -129.5842 | -0.8538 | 5.5299 | 1.8064 | -3.2122 | -1.5782 | 4.3468 |  | 3.0119 | 0.0994 | 4.0114 | 3.3672 | 3.3406 | 1.0689 | 10.744 | 14.2754 | 14.8618 | 11.085 | 0.0002 | -0.0029 | 0.0012 | 0.0044 | 0.0004 | -0.0003 | 0.0087 | -0.0004 | -0.0005 | -360.2265 | 17.4151 | -360.4204 | 17.6882 | -360.802 | 18.1933 | -360.9189 | 17.6245 | -352.6906 | 18.7148 | -352.629 | 16.7971
12:30 | 4199 | 40.4101 | 201.95 | 449.2274 | 455.8616 | -16.501 | -41.3175 | 10.8029 | 7.5362 | 1.9198 | -0.019 | 3.0562 | -1.0492 | 11.2745 | 4.0858 | 0.6145 | 0.6556 | 0.9599 | 0.7387 | -129.5919 | -0.8342 | 5.4535 | 1.7879 | -3.1383 | -1.5275 | 4.3054 |  | 2.9586 | 0.0597 | 4.01 | 3.3655 | 3.3382 | 1.0696 | 10.759 | 14.2674 | 14.8601 | 11.1114 | -0.0001 | -0.0032 | 0.0009 | 0.004 | 0.0011 | -0.0003 | 0.0012 | -0.0137 | -0.0053 | -360.1958 | 17.4336 | -360.5373 | 17.7313 | -360.842 | 18.1543 | -360.7989 | 17.5712 | -352.6567 | 18.7518 | -352.7337 | 16.8279
12:30 | 4200 | 40.5014 | 201.9899 | 449.2021 | 455.8652 | -16.5565 | -41.305 | 10.7274 | 7.5744 | 1.9348 | 0.0551 | 3.0674 | -1.1282 | 11.1574 | 4.0405 | 0.6138 | 0.656 | 0.9605 | 0.739 | -129.5929 | -0.8314 | 5.438 | 1.837 | -3.1852 | -1.508 | 4.2905 |  | 2.9829 | 0.001 | 4.01 | 3.3668 | 3.3367 | 1.0699 | 10.7406 | 14.2484 | 14.8092 | 11.071 | -0.0001 | -0.0025 | 0.0005 | 0.0043 | 0.0003 | -0.0004 | 0.0013 | -0.0051 | 0 | -360.0911 | 17.3679 | -360.3804 | 17.6861 | -360.8143 | 18.1892 | -360.8881 | 17.5814 | -352.5952 | 18.682 | -352.5952 | 16.8012
12:30 | 4201 | 40.494 | 202.0618 | 449.2655 | 455.9127 | -16.5186 | -41.2468 | 10.8321 | 7.5946 | 1.9705 | 0.1043 | 3.0691 | -1.0856 | 11.2146 | 4.0836 | 0.6157 | 0.6555 | 0.9617 | 0.7392 | -129.6372 | -0.8579 | 5.4495 | 1.8569 | -3.107 | -1.4841 | 4.3653 |  | 2.9942 | 0.1183 | 4.0105 | 3.3656 | 3.3368 | 1.0706 | 10.7578 | 14.2721 | 14.8366 | 11.0926 | 0.0002 | -0.0025 | 0.0009 | 0.0045 | 0.0014 | -0.0003 | 0.0256 | -0.008 | -0.0272 | -360.2173 | 17.4295 | -360.4604 | 17.6759 | -360.7497 | 18.1214 | -360.802 | 17.5835 | -352.6629 | 18.7251 | -352.669 | 16.7848
12:30 | 4202 | 40.5365 | 201.9977 | 449.3166 | 455.9088 | -16.5022 | -41.3059 | 10.7745 | 7.664 | 1.9483 | 0.1849 | 3.1367 | -1.1754 | 11.2132 | 4.0914 | 0.616 | 0.6584 | 0.9663 | 0.7381 | -129.6054 | -0.8635 | 5.415 | 1.8524 | -3.1935 | -1.513 | 4.3738 |  | 3.0306 | 0.1842 | 4.0109 | 3.3661 | 3.3395 | 1.0695 | 10.7545 | 14.2394 | 14.8535 | 11.0843 | 0.0002 | -0.0028 | 0.0003 | 0.0036 | 0.0005 | -0.0005 | 0.0169 | -0.0028 | -0.0168 | -360.125 | 17.3761 | -360.4666 | 17.719 | -360.8481 | 18.1892 | -360.8481 | 17.5527 | -352.589 | 18.682 | -352.6506 | 16.8258
12:30 | 4203 | 40.5523 | 202.1123 | 449.2339 | 456.0436 | -16.5129 | -41.1921 | 10.8117 | 7.728 | 1.9236 | 0.1392 | 3.1596 | -1.1837 | 11.2456 | 4.1253 | 0.6137 | 0.6563 | 0.9617 | 0.7378 | -129.5953 | -0.8879 | 5.4048 | 1.7582 | -3.2529 | -1.5357 | 4.3571 |  | 3.0493 | 0.0974 | 4.0111 | 3.3651 | 3.3385 | 1.0682 | 10.7429 | 14.2161 | 14.8467 | 11.0674 | 0.0002 | -0.003 | 0.0008 | 0.004 | 0.0008 | -0.0007 | 0.0069 | -0.0075 | 0.0028 | -360.2604 | 17.4274 | -360.4389 | 17.6861 | -360.8081 | 18.1707 | -360.8974 | 17.6286 | -352.7183 | 18.7333 | -352.6444 | 16.7868
12:30 | 4204 | 40.4811 | 202.0272 | 449.0891 | 455.9233 | -16.5591 | -41.3424 | 10.8934 | 7.6174 | 1.9263 | 0.0932 | 3.0681 | -1.117 | 11.2535 | 4.0848 | 0.6137 | 0.6552 | 0.9575 | 0.7391 | -129.6246 | -0.8149 | 5.3913 | 1.7257 | -3.2284 | -1.551 | 4.4035 |  | 2.9971 | 0.0364 | 4.0107 | 3.3645 | 3.3391 | 1.0707 | 10.7475 | 14.2615 | 14.8417 | 11.0713 | -0.0001 | -0.0028 | 0.0015 | 0.0039 | 0.001 | 0.0001 | 0.0175 | -0.0014 | -0.0132 | -360.1742 | 17.4213 | -360.4973 | 17.7395 | -360.8697 | 18.1687 | -360.8204 | 17.5691 | -352.6537 | 18.7292 | -352.7213 | 16.8484
12:30 | 4205 | 40.5424 | 202.0514 | 449.1292 | 456.0103 | -16.6768 | -41.4001 | 10.7505 | 7.6517 | 1.8996 | 0.0314 | 3.1077 | -1.0895 | 11.2212 | 4.1916 | 0.6155 | 0.6579 | 0.9587 | 0.7383 | -129.563 | -0.8645 | 5.4537 | 1.6783 | -3.1055 | -1.5212 | 4.4228 |  | 2.9966 | 0.0908 | 4.0106 | 3.3681 | 3.3391 | 1.0695 | 10.7637 | 14.2603 | 14.8519 | 11.0702 | -0.0002 | -0.0022 | 0.0006 | 0.0036 | 0.0003 | -0.0004 | 0.0184 | -0.0024 | -0.0099 | -360.1835 | 17.3699 | -360.3958 | 17.6615 | -360.7804 | 18.1912 | -360.8758 | 17.604 | -352.6413 | 18.682 | -352.5952 | 16.7868
12:30 | 4206 | 40.5257 | 202.0232 | 449.2122 | 455.9419 | -16.6143 | -41.2953 | 10.8095 | 7.6525 | 1.8882 | 0.0962 | 3.0747 | -1.1174 | 11.1877 | 4.0969 | 0.6137 | 0.6572 | 0.9639 | 0.7388 | -129.5563 | -0.8287 | 5.4052 | 1.7558 | -3.1697 | -1.601 | 4.3668 |  | 2.9936 | -0.0516 | 4.0115 | 3.3666 | 3.3427 | 1.0708 | 10.7406 | 14.2659 | 14.8103 | 11.088 | 0 | -0.003 | 0.0013 | 0.0042 | 0.0011 | 0 | 0.0169 | -0.0094 | -0.0191 | -360.1619 | 17.4151 | -360.4635 | 17.6923 | -360.7743 | 18.142 | -360.7743 | 17.5732 | -352.6352 | 18.7169 | -352.6721 | 16.8012
12:30 | 4207 | 40.5728 | 202.1086 | 449.2329 | 455.9946 | -16.6969 | -41.3338 | 10.7517 | 7.6938 | 1.845 | 0.2357 | 3.1003 | -1.0599 | 11.2359 | 4.0244 | 0.6144 | 0.6581 | 0.9619 | 0.7393 | -129.4856 | -0.884 | 5.5071 | 1.7223 | -3.1535 | -1.5403 | 4.4032 |  | 3.02 | 0.0366 | 4.0108 | 3.3637 | 3.3402 | 1.0702 | 10.759 | 14.3079 | 14.8775 | 11.0941 | 0.0003 | -0.0025 | 0.0008 | 0.004 | 0.0008 | -0.0002 | 0.0001 | -0.0072 | -0.0109 | -360.1127 | 17.3679 | -360.4173 | 17.7046 | -360.7989 | 18.2015 | -360.885 | 17.5753 | -352.586 | 18.6676 | -352.5921 | 16.8094
12:30 | 4208 | 40.5016 | 201.9616 | 449.1494 | 455.9154 | -16.6513 | -41.3603 | 10.7642 | 7.5897 | 1.9218 | 0.1509 | 3.0887 | -1.17 | 11.2267 | 4.0227 | 0.613 | 0.6562 | 0.9591 | 0.7391 | -129.6424 | -0.9165 | 5.3842 | 1.7832 | -3.0635 | -1.4996 | 4.4444 |  | 2.991 | 0.0688 | 4.0108 | 3.3683 | 3.3416 | 1.0678 | 10.7545 | 14.2392 | 14.8641 | 11.102 | -0.0003 | -0.003 | 0 | 0.0037 | 0.0008 | -0.001 | 0.0047 | -0.0145 | 0.0061 | -360.2142 | 17.4336 | -360.4758 | 17.6964 | -360.7743 | 18.1481 | -360.8635 | 17.604 | -352.6998 | 18.7292 | -352.6537 | 16.793
12:30 | 4209 | 40.5817 | 202.0746 | 449.1594 | 455.9676 | -16.6073 | -41.349 | 10.7879 | 7.6055 | 1.8554 | 0.108 | 3.0558 | -1.1725 | 11.219 | 4.101 | 0.614 | 0.6587 | 0.9622 | 0.7386 | -129.6861 | -0.9726 | 5.3453 | 1.887 | -3.0766 | -1.5697 | 4.4306 |  | 2.9979 | 0.1204 | 4.0108 | 3.3639 | 3.34 | 1.0691 | 10.73 | 14.256 | 14.8496 | 11.0937 | -0.0002 | -0.0024 | 0.001 | 0.0043 | 0.0009 | 0.0002 | 0.001 | -0.0021 | -0.0078 | -360.0911 | 17.3987 | -360.5004 | 17.7498 | -360.9127 | 18.2056 | -360.8543 | 17.5814 | -352.5983 | 18.7045 | -352.709 | 16.8525
12:30 | 4210 | 40.5314 | 202.0359 | 449.1303 | 455.9812 | -16.6128 | -41.3947 | 10.7972 | 7.5862 | 1.8102 | 0.2083 | 3.1198 | -1.1155 | 11.2451 | 4.0864 | 0.6157 | 0.6608 | 0.9637 | 0.7393 | -129.5493 | -0.8811 | 5.467 | 1.8802 | -3.1335 | -1.5078 | 4.3845 |  | 3.0645 | 0.1171 | 4.0109 | 3.3668 | 3.3365 | 1.0694 | 10.7384 | 14.2401 | 14.8402 | 11.0577 | -0.0001 | -0.0027 | 0.0001 | 0.0032 | 0.001 | -0.001 | 0.0041 | -0.0055 | -0.0123 | -360.2419 | 17.4151 | -360.4542 | 17.6964 | -360.7989 | 18.1933 | -360.8943 | 17.6286 | -352.7244 | 18.7148 | -352.6475 | 16.8074
12:30 | 4211 | 40.5057 | 202.0076 | 449.1021 | 456.0387 | -16.5835 | -41.3762 | 10.8211 | 7.6735 | 1.7989 | 0.1088 | 3.0904 | -1.0704 | 11.2629 | 4.0198 | 0.6148 | 0.6605 | 0.9626 | 0.7409 | -129.5832 | -0.8146 | 5.4487 | 1.8299 | -3.1488 | -1.5625 | 4.3374 |  | 3.0246 | 0.1344 | 4.0111 | 3.367 | 3.3379 | 1.0714 | 10.7095 | 14.2515 | 14.8159 | 11.0523 | 0.0006 | -0.0035 | 0.0006 | 0.0036 | 0.0004 | -0.0004 | 0.0154 | -0.0149 | -0.0159 | -360.1219 | 17.4131 | -360.4942 | 17.7375 | -360.8758 | 18.1625 | -360.7958 | 17.5568 | -352.6321 | 18.723 | -352.709 | 16.8464
12:30 | 4212 | 40.512 | 202.0124 | 449.1506 | 455.9322 | -16.5996 | -41.3349 | 10.7532 | 7.6425 | 1.7694 | 0.0466 | 3.1384 | -1.0556 | 11.3619 | 4.1138 | 0.6139 | 0.6617 | 0.963 | 0.74 | -129.5704 | -0.8707 | 5.3837 | 1.8283 | -3.1642 | -1.5231 | 4.2192 |  | 3.0216 | 0.1238 | 4.0121 | 3.3657 | 3.3379 | 1.0703 | 10.7497 | 14.2582 | 14.8455 | 11.0789 | 0.0001 | -0.0027 | 0.0014 | 0.0043 | 0.0012 | -0.0003 | 0.0077 | -0.0062 | -0.0048 | -360.125 | 17.3597 | -360.3804 | 17.6677 | -360.7743 | 18.1871 | -360.8943 | 17.5876 | -352.626 | 18.6799 | -352.589 | 16.7889
12:30 | 4213 | 40.635 | 202.0091 | 449.1709 | 455.9342 | -16.5868 | -41.4298 | 10.8134 | 7.7582 | 1.8338 | 0.0645 | 3.1485 | -1.1274 | 11.3255 | 4.0751 | 0.6148 | 0.6534 | 0.9605 | 0.7393 | -129.6086 | -0.859 | 5.5253 | 1.7936 | -3.102 | -1.5442 | 4.2738 |  | 2.9902 | 0.0491 | 4.0123 | 3.3658 | 3.3398 | 1.0715 | 10.7741 | 14.2707 | 14.8794 | 11.0865 | -0.0004 | -0.0028 | 0.001 | 0.0037 | 0.0005 | -0.0004 | 0.0021 | -0.0078 | -0.0034 | -360.165 | 17.4151 | -360.4696 | 17.7046 | -360.765 | 18.1214 | -360.7897 | 17.5547 | -352.6075 | 18.721 | -352.669 | 16.8115
12:30 | 4214 | 40.6533 | 202.0708 | 449.2997 | 456.0141 | -16.539 | -41.4105 | 10.8206 | 7.6275 | 1.7641 | -0.0351 | 3.0484 | -1.1344 | 11.2663 | 4.0874 | 0.6153 | 0.6536 | 0.9639 | 0.7393 | -129.6015 | -0.8335 | 5.3942 | 1.7818 | -3.1456 | -1.5357 | 4.2301 |  | 3.0464 | 0.0786 | 4.0117 | 3.3641 | 3.3389 | 1.0703 | 10.7498 | 14.2696 | 14.8386 | 11.1024 | -0.0005 | -0.0031 | 0.0016 | 0.0044 | 0.0008 | -0.0003 | 0.0176 | -0.0083 | -0.014 | -360.0696 | 17.3556 | -360.4019 | 17.7005 | -360.8358 | 18.1851 | -360.8604 | 17.5527 | -352.5767 | 18.6614 | -352.5952 | 16.8217
12:30 | 4215 | 40.6192 | 202.0424 | 449.2387 | 455.9884 | -16.5606 | -41.38 | 10.782 | 7.5281 | 1.81 | 0.0408 | 3.1523 | -1.1294 | 11.2997 | 4.1238 | 0.6162 | 0.6566 | 0.9597 | 0.7402 | -129.6384 | -0.8904 | 5.3459 | 1.7778 | -3.1642 | -1.4794 | 4.3037 |  | 3.029 | 0.0654 | 4.0098 | 3.3639 | 3.3389 | 1.0695 | 10.7926 | 14.3009 | 14.8819 | 11.0988 | 0.0003 | -0.003 | 0.0006 | 0.0039 | 0.0005 | -0.0004 | 0.0042 | -0.014 | -0.0073 | -360.2296 | 17.4356 | -360.4696 | 17.6779 | -360.802 | 18.1502 | -360.8358 | 17.5978 | -352.6906 | 18.7333 | -352.6629 | 16.7909
12:30 | 4216 | 40.5401 | 202.0187 | 449.2115 | 455.8623 | -16.559 | -41.2947 | 10.8198 | 7.5912 | 1.8336 | 0.1312 | 3.162 | -1.0952 | 11.255 | 4.1732 | 0.6159 | 0.6548 | 0.9637 | 0.7408 | -129.5871 | -0.8285 | 5.3862 | 1.7023 | -3.1605 | -1.5757 | 4.2876 |  | 3.009 | 0.113 | 4.0117 | 3.3667 | 3.3405 | 1.0705 | 10.773 | 14.2693 | 14.8828 | 11.1147 | -0.0004 | -0.0031 | 0 | 0.0037 | 0.0003 | -0.0004 | 0.0117 | -0.0021 | -0.0139 | -360.1373 | 17.4213 | -360.525 | 17.7457 | -360.9189 | 18.2015 | -360.842 | 17.5732 | -352.6136 | 18.7128 | -352.7244 | 16.8587
12:30 | 4217 | 40.5673 | 202.0831 | 449.2555 | 455.9194 | -16.4827 | -41.2734 | 10.8561 | 7.5788 | 1.759 | 0.0524 | 3.073 | -1.1529 | 11.2804 | 4.0734 | 0.6157 | 0.6561 | 0.9617 | 0.7393 | -129.4928 | -0.7068 | 5.4751 | 1.7123 | -3.236 | -1.5409 | 4.3745 |  | 2.967 | 0.0444 | 4.0116 | 3.3649 | 3.3395 | 1.0713 | 10.7428 | 14.2742 | 14.8199 | 11.0897 | -0.0003 | -0.0025 | 0.0006 | 0.004 | 0.001 | -0.0004 | 0.0018 | -0.0054 | 0.0074 | -360.2019 | 17.411 | -360.4358 | 17.68 | -360.7897 | 18.1871 | -360.9004 | 17.6184 | -352.706 | 18.7189 | -352.6506 | 16.8032
12:30 | 4218 | 40.567 | 202.0601 | 449.2771 | 455.9631 | -16.5588 | -41.3212 | 10.812 | 7.5288 | 1.8152 | 0.0517 | 2.9951 | -1.181 | 11.2182 | 4.1393 | 0.6144 | 0.657 | 0.9611 | 0.7387 | -129.5166 | -0.7769 | 5.3516 | 1.7621 | -3.3205 | -1.6008 | 4.3022 |  | 3.072 | 0.2296 | 4.0113 | 3.3649 | 3.3388 | 1.0694 | 10.7533 | 14.2615 | 14.8532 | 11.0887 | -0.0003 | -0.003 | 0.0011 | 0.0039 | 0.0006 | -0.0004 | 0.0142 | -0.0121 | 0.0053 | -360.1281 | 17.4151 | -360.4973 | 17.7108 | -360.805 | 18.1522 | -360.7804 | 17.5588 | -352.6567 | 18.7271 | -352.709 | 16.834
12:30 | 4219 | 40.5043 | 202.0623 | 449.3064 | 455.9368 | -16.5887 | -41.3343 | 10.9175 | 7.528 | 1.7785 | 0.0144 | 3.0892 | -1.1417 | 11.2413 | 4.0373 | 0.6145 | 0.6583 | 0.9638 | 0.7396 | -129.6293 | -0.8448 | 5.4803 | 1.8813 | -3.3325 | -1.5443 | 4.2517 |  | 2.9671 | 0.0899 | 4.0106 | 3.3694 | 3.3388 | 1.0706 | 10.7255 | 14.2337 | 14.8257 | 11.0493 | 0.0003 | -0.0031 | 0.0009 | 0.0036 | 0.0009 | -0.0006 | 0.0065 | -0.0009 | 0.0078 | -360.1681 | 17.3782 | -360.3835 | 17.6718 | -360.805 | 18.1789 | -360.8389 | 17.5835 | -352.6167 | 18.6717 | -352.6106 | 16.8032
12:30 | 4220 | 40.5773 | 202.0321 | 449.1786 | 455.8895 | -16.6005 | -41.2782 | 10.9447 | 7.5934 | 1.7529 | 0.0902 | 3.0169 | -1.1082 | 11.2537 | 4.1741 | 0.6142 | 0.6556 | 0.962 | 0.7391 | -129.6637 | -0.8257 | 5.5615 | 1.8843 | -3.2995 | -1.5966 | 4.2204 |  | 3.0282 | 0.1181 | 4.0106 | 3.3653 | 3.341 | 1.0724 | 10.7198 | 14.2391 | 14.8804 | 11.0678 | 0 | -0.0034 | 0.0015 | 0.0042 | 0.0001 | -0.0008 | 0.0171 | -0.0035 | -0.0069 | -360.1865 | 17.4192 | -360.4635 | 17.6738 | -360.7804 | 18.1194 | -360.7804 | 17.5732 | -352.6629 | 18.721 | -352.6537 | 16.7991
12:30 | 4221 | 40.5634 | 201.988 | 449.1819 | 455.8725 | -16.5338 | -41.1948 | 10.9723 | 7.6038 | 1.8048 | 0.1491 | 3.0889 | -1.2297 | 11.3047 | 4.1273 | 0.6137 | 0.657 | 0.9638 | 0.7391 | -129.6987 | -0.8308 | 5.4785 | 1.9813 | -3.1741 | -1.5485 | 4.3755 |  | 2.9877 | 0.0619 | 4.0114 | 3.3673 | 3.336 | 1.0708 | 10.7544 | 14.2858 | 14.872 | 11.1013 | -0.0003 | -0.0028 | 0.0009 | 0.0041 | 0.0008 | -0.0007 | 0.0017 | -0.0088 | -0.0016 | -360.125 | 17.3802 | -360.4512 | 17.6944 | -360.8358 | 18.1584 | -360.8666 | 17.5527 | -352.5706 | 18.6861 | -352.666 | 16.8115
12:30 | 4222 | 40.555 | 201.9711 | 449.1675 | 455.8639 | -16.5379 | -41.0735 | 10.8544 | 7.5774 | 1.8884 | 0.1648 | 3.1205 | -1.1411 | 11.252 | 4.096 | 0.6151 | 0.6581 | 0.9613 | 0.7387 | -129.7176 | -0.8129 | 5.4752 | 1.9573 | -3.0753 | -1.5226 | 4.2829 |  | 3.0343 | 0.2163 | 4.0111 | 3.3653 | 3.3386 | 1.0718 | 10.7439 | 14.2698 | 14.8744 | 11.0847 | -0.0001 | -0.0025 | 0.0008 | 0.0037 | 0.0008 | -0.0002 | 0.0334 | -0.0018 | -0.0127 | -360.1988 | 17.4172 | -360.4327 | 17.6697 | -360.7712 | 18.1481 | -360.8666 | 17.6102 | -352.6813 | 18.7066 | -352.629 | 16.7868
12:30 | 4223 | 40.5448 | 202.0724 | 449.2721 | 455.9185 | -16.5462 | -41.0734 | 10.9413 | 7.6155 | 1.8871 | 0.194 | 3.0573 | -1.0901 | 11.2379 | 4.1362 | 0.6146 | 0.6582 | 0.9663 | 0.7392 | -129.728 | -0.8939 | 5.477 | 1.8601 | -3.0768 | -1.6438 | 4.2657 |  | 3.0336 | 0.056 | 4.0102 | 3.365 | 3.3407 | 1.0692 | 10.7798 | 14.2827 | 14.9 | 11.1258 | 0.0003 | -0.0029 | 0.0011 | 0.0045 | 0.001 | -0.0006 | 0.0167 | 0.0038 | -0.0008 | -360.1988 | 17.4254 | -360.5035 | 17.721 | -360.8666 | 18.1502 | -360.8297 | 17.5794 | -352.6475 | 18.7415 | -352.7244 | 16.832
12:30 | 4224 | 40.5761 | 202.1192 | 449.3506 | 456.0084 | -16.5573 | -41.1388 | 10.8664 | 7.6109 | 1.902 | 0.1756 | 3.1105 | -1.0111 | 11.239 | 4.1739 | 0.6148 | 0.659 | 0.961 | 0.7385 | -129.6964 | -0.7583 | 5.4816 | 1.8128 | -3.0559 | -1.5698 | 4.3066 |  | 3.1238 | 0.1172 | 4.0107 | 3.3662 | 3.3393 | 1.0717 | 10.7497 | 14.2871 | 14.8918 | 11.1251 | 0.0003 | -0.0029 | 0.0004 | 0.0037 | 0.0009 | 0 | 0.0163 | -0.0154 | -0.0009 | -360.1835 | 17.4131 | -360.4419 | 17.6882 | -360.8327 | 18.1645 | -360.9097 | 17.604 | -352.6629 | 18.7107 | -352.6413 | 16.8135
12:30 | 4225 | 40.6429 | 202.034 | 449.3299 | 455.9965 | -16.5628 | -41.1456 | 10.8968 | 7.6994 | 1.9367 | 0.2314 | 3.2284 | -1.0484 | 11.3495 | 4.1164 | 0.6162 | 0.6579 | 0.9633 | 0.7379 | -129.635 | -0.7427 | 5.4633 | 1.7544 | -3.1901 | -1.6154 | 4.292 |  | 3.0091 | -0.0141 | 4.0115 | 3.3681 | 3.34 | 1.0703 | 10.751 | 14.2822 | 14.8737 | 11.0865 | -0.0002 | -0.0028 | 0.0008 | 0.004 | 0.0002 | -0.0011 | -0.0049 | -0.0116 | -0.021 | -360.1835 | 17.4397 | -360.5035 | 17.7046 | -360.845 | 18.1502 | -360.8389 | 17.5999 | -352.6629 | 18.7477 | -352.7029 | 16.832
12:30 | 4226 | 40.6524 | 202.0391 | 449.2245 | 455.9973 | -16.5211 | -41.2015 | 11.0197 | 7.669 | 2.0545 | 0.2419 | 3.1562 | -1.1941 | 11.2724 | 4.1545 | 0.6161 | 0.6565 | 0.9616 | 0.7362 | -129.6713 | -0.8005 | 5.4321 | 1.7137 | -3.2438 | -1.6353 | 4.3122 |  | 3.0249 | 0.0016 | 4.0109 | 3.363 | 3.3408 | 1.0712 | 10.767 | 14.2584 | 14.8639 | 11.1074 | -0.0001 | -0.0027 | 0.0009 | 0.0041 | 0.0008 | -0.0002 | 0.0154 | 0.0008 | 0.0085 | -360.1835 | 17.3946 | -360.4358 | 17.6985 | -360.8174 | 18.1645 | -360.8943 | 17.604 | -352.6598 | 18.7107 | -352.6629 | 16.8115
12:30 | 4227 | 40.6789 | 202.0849 | 449.3056 | 456.0078 | -16.4701 | -41.1459 | 10.8995 | 7.7058 | 2.0112 | 0.2272 | 3.1474 | -1.1139 | 11.374 | 4.1523 | 0.6144 | 0.658 | 0.9637 | 0.7384 | -129.6447 | -0.7232 | 5.5124 | 1.7358 | -3.244 | -1.5578 | 4.4394 |  | 3.0337 | 0.041 | 4.0105 | 3.3654 | 3.3404 | 1.0721 | 10.7568 | 14.2591 | 14.8331 | 11.0749 | 0.0003 | -0.0027 | 0.001 | 0.0036 | 0.0006 | -0.0008 | 0 | -0.0148 | -0.0159 | -360.1804 | 17.4048 | -360.4727 | 17.6841 | -360.7989 | 18.1379 | -360.8174 | 17.6061 | -352.6721 | 18.7128 | -352.6598 | 16.8074
12:30 | 4228 | 40.6671 | 202.0634 | 449.2945 | 456.0684 | -16.5974 | -41.1693 | 10.8673 | 7.6249 | 2.0118 | 0.1816 | 3.1343 | -1.1745 | 11.3114 | 4.1142 | 0.6139 | 0.6561 | 0.9651 | 0.7381 | -129.7047 | -0.7085 | 5.5089 | 1.6729 | -3.1958 | -1.6552 | 4.4066 |  | 2.9498 | 0.0397 | 4.0098 | 3.3652 | 3.3435 | 1.0714 | 10.7348 | 14.2486 | 14.8508 | 11.0764 | 0.0003 | -0.0031 | 0.0015 | 0.0045 | 0.0012 | -0.0004 | 0.0077 | -0.0119 | -0.0206 | -360.1711 | 17.3864 | -360.405 | 17.6779 | -360.8174 | 18.1379 | -360.7989 | 17.5855 | -352.5983 | 18.6984 | -352.6321 | 16.8032
12:30 | 4229 | 40.6765 | 202.0142 | 449.1791 | 455.9199 | -16.5212 | -41.1072 | 10.9414 | 7.6611 | 2.0434 | 0.2514 | 3.0653 | -1.1399 | 11.2885 | 4.1198 | 0.6145 | 0.6556 | 0.9641 | 0.7387 | -129.6597 | -0.6526 | 5.5021 | 1.707 | -3.1976 | -1.656 | 4.4172 |  | 2.9772 | 0.0616 | 4.01 | 3.37 | 3.3391 | 1.071 | 10.7406 | 14.2659 | 14.8219 | 11.0706 | 0.0004 | -0.0024 | 0.0005 | 0.0038 | 0.0008 | 0 | 0.0037 | -0.0066 | -0.0166 | -360.165 | 17.3946 | -360.3927 | 17.6656 | -360.762 | 18.1276 | -360.805 | 17.5835 | -352.5983 | 18.7087 | -352.6198 | 16.7909
12:30 | 4230 | 40.6714 | 202.0717 | 449.2043 | 455.9187 | -16.5074 | -41.1103 | 10.9835 | 7.6283 | 2.0795 | 0.2777 | 3.1365 | -1.126 | 11.2855 | 4.0976 | 0.6148 | 0.6548 | 0.9608 | 0.7402 | -129.579 | -0.5995 | 5.5632 | 1.6957 | -3.2157 | -1.5214 | 4.3469 |  | 2.9709 | 0.1082 | 4.0111 | 3.3643 | 3.3421 | 1.071 | 10.7313 | 14.2799 | 14.813 | 11.0728 | -0.0003 | -0.0026 | 0.0006 | 0.0037 | 0.0009 | -0.0007 | 0.0185 | -0.0167 | -0.0052 | -360.1804 | 17.409 | -360.445 | 17.6779 | -360.7958 | 18.1255 | -360.845 | 17.5917 | -352.6198 | 18.7251 | -352.6537 | 16.7909
12:30 | 4231 | 40.5067 | 201.9757 | 449.1401 | 455.8653 | -16.5286 | -41.1885 | 10.9171 | 7.6295 | 2.1272 | 0.2716 | 3.1688 | -1.0724 | 11.2456 | 4.0825 | 0.615 | 0.656 | 0.9592 | 0.7396 | -129.484 | -0.638 | 5.4871 | 1.7491 | -3.2017 | -1.4515 | 4.5699 |  | 2.9888 | 0.1958 | 4.0104 | 3.3661 | 3.3373 | 1.0718 | 10.7324 | 14.2407 | 14.8212 | 11.0793 | 0.0005 | -0.0025 | 0.0008 | 0.0039 | 0.0009 | 0.0002 | 0.0124 | -0.0064 | 0.0023 | -360.1804 | 17.4131 | -360.4604 | 17.6923 | -360.842 | 18.1584 | -360.805 | 17.5978 | -352.5952 | 18.7128 | -352.6506 | 16.8135
12:30 | 4232 | 40.5717 | 202.0148 | 449.0818 | 455.9047 | -16.5696 | -41.2199 | 10.9111 | 7.5906 | 2.0603 | 0.362 | 3.1759 | -1.2125 | 11.2846 | 4.1017 | 0.6137 | 0.657 | 0.9605 | 0.7391 | -129.5666 | -0.7342 | 5.4044 | 1.7984 | -3.1489 | -1.6257 | 4.5109 |  | 3.0481 | 0.153 | 4.0109 | 3.3655 | 3.3365 | 1.0707 | 10.7776 | 14.2684 | 14.8662 | 11.1013 | 0 | -0.0032 | 0.0004 | 0.0035 | 0.0012 | -0.0008 | -0.0028 | -0.0181 | -0.0089 | -360.2081 | 17.4192 | -360.4604 | 17.6902 | -360.845 | 18.1645 | -360.8758 | 17.6348 | -352.6998 | 18.7251 | -352.666 | 16.8115
12:30 | 4233 | 40.5909 | 202.0419 | 449.0582 | 455.9049 | -16.5535 | -41.2154 | 10.9471 | 7.5988 | 1.9693 | 0.2158 | 3.0112 | -1.1479 | 11.3798 | 4.2009 | 0.6145 | 0.6546 | 0.963 | 0.7396 | -129.5691 | -0.7465 | 5.4429 | 1.7919 | -3.1093 | -1.6142 | 4.4752 |  | 3.0507 | 0.1 | 4.0093 | 3.3666 | 3.3386 | 1.0721 | 10.7579 | 14.2544 | 14.8334 | 11.088 | -0.0003 | -0.0029 | 0.0005 | 0.0042 | 0.0003 | -0.0005 | 0.0097 | -0.0094 | -0.0125 | -360.205 | 17.4192 | -360.485 | 17.6882 | -360.8174 | 18.1502 | -360.8327 | 17.6061 | -352.6844 | 18.7189 | -352.6783 | 16.8258
12:30 | 4234 | 40.5772 | 201.9536 | 449.0773 | 455.8582 | -16.5918 | -41.1081 | 10.9225 | 7.6557 | 2.1016 | 0.1951 | 3.1333 | -1.1478 | 11.3385 | 4.1312 | 0.6151 | 0.6538 | 0.9616 | 0.7377 | -129.6154 | -0.6901 | 5.381 | 1.6009 | -3.0966 | -1.6459 | 4.3924 |  | 2.9141 | 0.1357 | 4.0087 | 3.3629 | 3.336 | 1.0708 | 10.7371 | 14.2741 | 14.8535 | 11.0959 | -0.0005 | -0.0028 | 0.0004 | 0.0035 | 0.0007 | -0.0008 | 0.0181 | -0.0112 | -0.0081 | -360.1465 | 17.3905 | -360.4573 | 17.6882 | -360.8574 | 18.1625 | -360.8543 | 17.5958 | -352.6352 | 18.7004 | -352.6598 | 16.8299
12:30 | 4235 | 40.5643 | 202.0828 | 449.1603 | 455.8952 | -16.4543 | -41.105 | 10.9261 | 7.7099 | 1.9838 | 0.2464 | 3.1716 | -1.1871 | 11.3095 | 4.1372 | 0.6146 | 0.6547 | 0.9624 | 0.7379 | -129.6851 | -0.6809 | 5.4591 | 1.527 | -3.2237 | -1.594 | 4.3751 |  | 2.9264 | 0.0251 | 4.0101 | 3.3658 | 3.3398 | 1.0715 | 10.7279 | 14.2415 | 14.8484 | 11.0988 | -0.0002 | -0.003 | 0.0008 | 0.0039 | 0.0007 | -0.0005 | 0.0016 | -0.009 | 0.0074 | -360.165 | 17.3925 | -360.4142 | 17.6389 | -360.7466 | 18.1317 | -360.845 | 17.6081 | -352.626 | 18.6922 | -352.6321 | 16.7848
12:30 | 4236 | 40.5378 | 202.0811 | 449.2195 | 455.87 | -16.471 | -41.2269 | 10.9116 | 7.6827 | 1.9865 | 0.1709 | 3.1502 | -1.2242 | 11.3407 | 4.0899 | 0.6156 | 0.6566 | 0.9635 | 0.7401 | -129.5988 | -0.6931 | 5.4283 | 1.6011 | -3.2052 | -1.6254 | 4.3416 |  | 2.9862 | 0.1073 | 4.0089 | 3.3642 | 3.3387 | 1.0722 | 10.7278 | 14.2533 | 14.8216 | 11.0749 | 0.0003 | -0.003 | 0.0009 | 0.0038 | 0.0011 | -0.0009 | -0.0047 | 0.0006 | 0.0095 | -360.1435 | 17.4028 | -360.4604 | 17.6841 | -360.8235 | 18.1153 | -360.7804 | 17.5732 | -352.5829 | 18.6984 | -352.6598 | 16.8156
12:30 | 4237 | 40.6342 | 202.1341 | 449.3088 | 455.9178 | -16.5122 | -41.2341 | 10.9046 | 7.6712 | 1.9515 | 0.2209 | 3.0889 | -1.2221 | 11.2797 | 4.0985 | 0.6149 | 0.6563 | 0.9598 | 0.7402 | -129.6755 | -0.8092 | 5.3421 | 1.5067 | -3.1656 | -1.5107 | 4.3359 |  | 2.971 | -0.0097 | 4.0104 | 3.367 | 3.3395 | 1.0721 | 10.7671 | 14.2638 | 14.8618 | 11.085 | -0.0002 | -0.0032 | 0.0009 | 0.0035 | 0.0007 | -0.0001 | 0.0134 | -0.005 | -0.0095 | -360.1465 | 17.374 | -360.4142 | 17.6656 | -360.8266 | 18.1707 | -360.8666 | 17.5917 | -352.626 | 18.6758 | -352.5983 | 16.795
12:30 | 4238 | 40.6136 | 202.1154 | 449.2712 | 455.9599 | -16.5456 | -41.2303 | 10.9647 | 7.6414 | 1.9854 | 0.1745 | 3.1644 | -1.2008 | 11.2185 | 4.072 | 0.6149 | 0.6579 | 0.9619 | 0.7389 | -129.6213 | -0.5899 | 5.4097 | 1.4748 | -3.1788 | -1.6175 | 4.2898 |  | 2.9888 | 0.0498 | 4.0098 | 3.3669 | 3.3414 | 1.071 | 10.7671 | 14.2754 | 14.8734 | 11.0908 | -0.0004 | -0.0025 | 0.0009 | 0.004 | 0.0009 | -0.0005 | 0.0079 | -0.0089 | 0.007 | -360.1558 | 17.4295 | -360.4789 | 17.6738 | -360.8081 | 18.1399 | -360.8512 | 17.6061 | -352.669 | 18.723 | -352.6875 | 16.7971
12:30 | 4239 | 40.588 | 202.0466 | 449.1489 | 455.9136 | -16.5031 | -41.2003 | 11.0476 | 7.6035 | 2.0638 | 0.2717 | 3.1356 | -1.2436 | 11.2735 | 4.0176 | 0.6153 | 0.6583 | 0.9624 | 0.7394 | -129.6152 | -0.7465 | 5.436 | 1.4834 | -3.0933 | -1.5602 | 4.3315 |  | 2.9656 | -0.001 | 4.0101 | 3.368 | 3.337 | 1.0715 | 10.7798 | 14.2885 | 14.8826 | 11.0796 | 0 | -0.0025 | 0.0009 | 0.0042 | 0.0009 | -0.0005 | 0.0083 | -0.0204 | -0.0115 | -360.0911 | 17.4151 | -360.4942 | 17.7128 | -360.8881 | 18.1604 | -360.8543 | 17.5937 | -352.6444 | 18.7087 | -352.7121 | 16.8381
12:30 | 4240 | 40.6006 | 202.0567 | 449.1705 | 455.9291 | -16.5084 | -41.1596 | 11.0533 | 7.6968 | 2.0083 | 0.2384 | 3.1517 | -1.1226 | 11.407 | 4.1224 | 0.6154 | 0.6599 | 0.966 | 0.7399 | -129.6314 | -0.772 | 5.3816 | 1.5384 | -3.1611 | -1.6376 | 4.4219 |  | 2.9646 | 0.0371 | 4.0096 | 3.3617 | 3.3354 | 1.0714 | 10.7416 | 14.2616 | 14.8659 | 11.0941 | 0.0001 | -0.0032 | 0.0011 | 0.0045 | 0.0008 | -0.0001 | 0.0103 | 0.0095 | 0.0073 | -360.1558 | 17.4048 | -360.3989 | 17.6738 | -360.8297 | 18.1625 | -360.8758 | 17.6328 | -352.666 | 18.6984 | -352.626 | 16.8012
12:30 | 4241 | 40.535 | 201.9635 | 449.1111 | 455.7625 | -16.4429 | -41.2121 | 11.0322 | 7.719 | 1.9849 | 0.1685 | 3.0988 | -1.1593 | 11.4123 | 4.1475 | 0.6159 | 0.6582 | 0.9614 | 0.74 | -129.5974 | -0.6877 | 5.433 | 1.689 | -3.2376 | -1.5297 | 4.3064 |  | 3.0018 | 0.0497 | 4.0091 | 3.3666 | 3.3383 | 1.0703 | 10.7452 | 14.2591 | 14.8389 | 11.0923 | 0 | -0.003 | 0.0007 | 0.0042 | 0.0009 | -0.0005 | 0.0061 | -0.0183 | -0.0033 | -360.1865 | 17.4397 | -360.5158 | 17.6902 | -360.8081 | 18.1214 | -360.8235 | 17.6102 | -352.6752 | 18.7353 | -352.706 | 16.8258
12:30 | 4242 | 40.5019 | 201.9665 | 449.103 | 455.8196 | -16.5002 | -41.206 | 10.9991 | 7.7283 | 1.9866 | 0.2126 | 3.1047 | -1.2241 | 11.3607 | 4.1031 | 0.6164 | 0.6601 | 0.9645 | 0.7396 | -129.5747 | -0.5779 | 5.4453 | 1.7923 | -3.2306 | -1.6318 | 4.2943 |  | 2.97 | 0.1515 | 4.0089 | 3.368 | 3.3369 | 1.07 | 10.744 | 14.2521 | 14.8607 | 11.1085 | -0.0006 | -0.003 | 0.0009 | 0.0041 | 0.0009 | -0.0003 | 0.0091 | -0.0002 | 0.003 | -360.085 | 17.372 | -360.4389 | 17.6779 | -360.8358 | 18.1502 | -360.8574 | 17.565 | -352.6013 | 18.6779 | -352.6598 | 16.8279
12:30 | 4243 | 40.583 | 202.0005 | 449.0999 | 455.9023 | -16.4293 | -41.284 | 11.065 | 7.7873 | 2.0494 | 0.3573 | 3.1273 | -1.2404 | 11.3479 | 4.1015 | 0.6162 | 0.6612 | 0.9648 | 0.7391 | -129.4997 | -0.5945 | 5.6114 | 1.6881 | -3.2769 | -1.7167 | 4.2754 |  | 2.923 | 0.0112 | 4.0097 | 3.3685 | 3.3365 | 1.0707 | 10.7545 | 14.2277 | 14.8293 | 11.102 | -0.0003 | -0.0029 | 0.0006 | 0.0034 | 0.001 | -0.0008 | 0.0139 | -0.014 | -0.0218 | -360.165 | 17.3782 | -360.3958 | 17.6512 | -360.7343 | 18.1379 | -360.8481 | 17.6081 | -352.6383 | 18.684 | -352.6075 | 16.7848
12:30 | 4244 | 40.5589 | 201.9811 | 449.0964 | 455.904 | -16.5516 | -41.3148 | 11.0156 | 7.6837 | 2.1026 | 0.2905 | 3.121 | -1.2484 | 11.3382 | 4.1398 | 0.6163 | 0.6617 | 0.9622 | 0.7406 | -129.5691 | -0.6208 | 5.4577 | 1.5818 | -3.1498 | -1.6533 | 4.344 |  | 2.9053 | 0.0805 | 4.0086 | 3.3679 | 3.339 | 1.0704 | 10.7232 | 14.237 | 14.8103 | 11.0475 | 0.0005 | -0.003 | 0.0008 | 0.0039 | 0.001 | 0.0002 | 0.0256 | -0.0025 | -0.0153 | -360.1988 | 17.4151 | -360.4758 | 17.68 | -360.8112 | 18.1009 | -360.765 | 17.5753 | -352.6198 | 18.7128 | -352.6875 | 16.8074
12:30 | 4245 | 40.6362 | 201.972 | 449.1092 | 455.9107 | -16.4941 | -41.3305 | 10.9743 | 7.6415 | 2.0174 | 0.3107 | 3.201 | -1.2148 | 11.3703 | 4.2206 | 0.6165 | 0.6591 | 0.9628 | 0.7392 | -129.6061 | -0.6964 | 5.3804 | 1.5901 | -3.1587 | -1.5865 | 4.3461 |  | 2.9515 | 0.0425 | 4.0102 | 3.367 | 3.3409 | 1.0712 | 10.7545 | 14.2452 | 14.8478 | 11.0728 | 0.0002 | -0.0032 | 0.0008 | 0.0035 | 0.001 | -0.0009 | 0.0145 | -0.0064 | -0.0215 | -360.1681 | 17.3802 | -360.4296 | 17.6861 | -360.8481 | 18.181 | -360.8512 | 17.5876 | -352.6229 | 18.6758 | -352.6044 | 16.8135
12:30 | 4246 | 40.5656 | 201.9925 | 449.1047 | 455.9642 | -16.5632 | -41.3604 | 10.8921 | 7.6424 | 2.0745 | 0.2168 | 3.1453 | -1.1807 | 11.3766 | 4.1441 | 0.6163 | 0.657 | 0.9594 | 0.7392 | -129.628 | -0.7467 | 5.4478 | 1.6324 | -3.1473 | -1.5198 | 4.3541 |  | 2.9345 | 0.1219 | 4.0088 | 3.3648 | 3.3349 | 1.0689 | 10.7382 | 14.281 | 14.8491 | 11.0796 | 0 | -0.0027 | 0.0009 | 0.0041 | 0.0008 | -0.0002 | 0.0077 | -0.0062 | -0.0146 | -360.2665 | 17.4274 | -360.4389 | 17.6656 | -360.7804 | 18.1584 | -360.8543 | 17.6307 | -352.7029 | 18.723 | -352.6629 | 16.793
12:30 | 4247 | 40.6431 | 202.0421 | 449.1618 | 455.9927 | -16.5322 | -41.3967 | 10.9128 | 7.62 | 2.0513 | 0.2625 | 3.0818 | -1.1458 | 11.4539 | 4.1806 | 0.6138 | 0.6574 | 0.9622 | 0.7401 | -129.5519 | -0.6346 | 5.4417 | 1.7784 | -3.0963 | -1.5586 | 4.4443 |  | 2.9135 | 0.1033 | 4.0102 | 3.366 | 3.3407 | 1.0713 | 10.7856 | 14.271 | 14.8584 | 11.1146 | -0.0003 | -0.0026 | 0.0006 | 0.004 | 0.0012 | -0.0005 | 0.0227 | -0.002 | -0.0057 | -360.1927 | 17.4233 | -360.5127 | 17.7252 | -360.9004 | 18.144 | -360.8174 | 17.5814 | -352.6844 | 18.7292 | -352.709 | 16.8484
12:31 | 4248 | 40.6685 | 202.0584 | 449.1939 | 456.0098 | -16.5409 | -41.2793 | 10.9543 | 7.7327 | 1.9984 | 0.4176 | 3.1383 | -1.1214 | 11.4467 | 4.2452 | 0.6157 | 0.6569 | 0.9611 | 0.7392 | -129.6791 | -0.6102 | 5.5469 | 1.8325 | -3.0793 | -1.4749 | 4.4346 |  | 2.9745 | 0.1264 | 4.0092 | 3.3654 | 3.3371 | 1.0708 | 10.7705 | 14.2849 | 14.867 | 11.0995 | 0.0003 | -0.0025 | 0.001 | 0.004 | 0.0005 | -0.0004 | -0.0084 | -0.0107 | -0.0173 | -360.1465 | 17.3864 | -360.4358 | 17.68 | -360.8481 | 18.183 | -360.9004 | 17.6081 | -352.6506 | 18.6963 | -352.6413 | 16.8238
12:31 | 4249 | 40.6048 | 202.0382 | 449.2012 | 455.9755 | -16.5982 | -41.3215 | 10.8677 | 7.6729 | 1.9219 | 0.2018 | 3.0856 | -1.087 | 11.5014 | 4.2367 | 0.6156 | 0.6601 | 0.9606 | 0.7397 | -129.6542 | -0.6109 | 5.533 | 1.7737 | -3.1624 | -1.5615 | 4.3758 |  | 2.957 | 0.1015 | 4.0096 | 3.3668 | 3.3359 | 1.0712 | 10.7822 | 14.2557 | 14.8822 | 11.0655 | 0.0003 | -0.003 | 0.0011 | 0.0043 | 0.0007 | -0.0005 | 0.0285 | 0.0009 | -0.0107 | -360.2358 | 17.4233 | -360.445 | 17.6451 | -360.7989 | 18.1214 | -360.7958 | 17.6061 | -352.6629 | 18.7189 | -352.6844 | 16.8012
12:31 | 4250 | 40.6575 | 202.0414 | 449.1647 | 455.9796 | -16.599 | -41.3237 | 10.8681 | 7.6927 | 1.922 | 0.2905 | 3.0416 | -1.1299 | 11.4367 | 4.1577 | 0.6148 | 0.6591 | 0.9608 | 0.7386 | -129.6675 | -0.5958 | 5.4492 | 1.9091 | -3.1059 | -1.4747 | 4.4356 |  | 2.8925 | -0.0116 | 4.009 | 3.3677 | 3.3389 | 1.0719 | 10.7348 | 14.2428 | 14.8566 | 11.0995 | -0.0001 | -0.0024 | 0.0008 | 0.0036 | 0.0008 | -0.0008 | 0.0003 | -0.0125 | -0.0074 | -360.1496 | 17.3905 | -360.4419 | 17.6902 | -360.842 | 18.1399 | -360.7927 | 17.5547 | -352.5798 | 18.6861 | -352.6752 | 16.8443
12:31 | 4251 | 40.7975 | 202.1114 | 449.2682 | 456.0089 | -16.5615 | -41.3018 | 10.9887 | 7.738 | 1.9681 | 0.4044 | 3.1533 | -1.114 | 11.4659 | 4.2017 | 0.6143 | 0.6569 | 0.9615 | 0.739 | -129.5915 | -0.6186 | 5.443 | 1.9133 | -3.1448 | -1.5601 | 4.4477 |  | 2.8957 | 0.0517 | 4.0089 | 3.3651 | 3.3361 | 1.0712 | 10.7673 | 14.2345 | 14.8239 | 11.1035 | -0.0004 | -0.0028 | 0.0009 | 0.0034 | 0.0007 | -0.0007 | -0.003 | -0.0052 | -0.0137 | -360.1342 | 17.3597 | -360.3742 | 17.6328 | -360.7527 | 18.142 | -360.8666 | 17.602 | -352.6229 | 18.6737 | -352.5583 | 16.7724
12:31 | 4252 | 40.7375 | 202.1255 | 449.4093 | 455.9784 | -16.5862 | -41.4186 | 10.9493 | 7.7025 | 1.9422 | 0.3888 | 3.1609 | -1.1115 | 11.4566 | 4.1853 | 0.6143 | 0.656 | 0.9652 | 0.7395 | -129.5597 | -0.6088 | 5.4239 | 1.9115 | -3.1579 | -1.5176 | 4.5082 |  | 2.9232 | 0.1795 | 4.0076 | 3.3696 | 3.3384 | 1.0715 | 10.7025 | 14.2332 | 14.8214 | 11.0508 | -0.0003 | -0.0033 | 0.0007 | 0.0036 | 0.0011 | -0.0008 | 0.0137 | -0.0002 | 0.0003 | -360.1865 | 17.4356 | -360.4912 | 17.682 | -360.765 | 18.1153 | -360.7773 | 17.5773 | -352.6383 | 18.7169 | -352.6752 | 16.8074
12:31 | 4253 | 40.7055 | 202.1044 | 449.1783 | 455.9035 | -16.5534 | -41.3724 | 10.9357 | 7.6146 | 1.8172 | 0.2495 | 3.0656 | -1.1368 | 11.4468 | 4.2113 | 0.614 | 0.6568 | 0.9635 | 0.7392 | -129.6058 | -0.6765 | 5.4224 | 1.8208 | -3.1927 | -1.5777 | 4.4444 |  | 2.9352 | 0.1421 | 4.0096 | 3.368 | 3.337 | 1.0722 | 10.7579 | 14.2545 | 14.8461 | 11.0818 | 0.0004 | -0.0029 | 0.0005 | 0.0035 | 0.0005 | -0.0003 | 0.0079 | -0.0171 | -0.0265 | -360.1158 | 17.3884 | -360.4604 | 17.7005 | -360.845 | 18.1625 | -360.8204 | 17.5794 | -352.5767 | 18.6737 | -352.669 | 16.8217
12:31 | 4254 | 40.697 | 202.0421 | 449.2168 | 455.9619 | -16.5261 | -41.5281 | 10.8937 | 7.6777 | 1.7907 | 0.3202 | 3.1374 | -1.2573 | 11.3843 | 4.1405 | 0.6148 | 0.6579 | 0.9639 | 0.7394 | -129.5934 | -0.6696 | 5.4582 | 1.871 | -3.1302 | -1.4971 | 4.5291 |  | 3.017 | 0.1619 | 4.009 | 3.3675 | 3.338 | 1.0709 | 10.7383 | 14.2289 | 14.8596 | 11.0858 | 0 | -0.003 | 0.0007 | 0.004 | 0.0009 | -0.0006 | -0.0052 | -0.0091 | -0.0248 | -360.2481 | 17.4336 | -360.4419 | 17.6779 | -360.7866 | 18.1543 | -360.9251 | 17.643 | -352.6998 | 18.7148 | -352.6444 | 16.7909
12:31 | 4255 | 40.7084 | 201.9731 | 449.2346 | 455.9875 | -16.5075 | -41.3872 | 10.8928 | 7.6974 | 1.8085 | 0.2465 | 3.1181 | -1.1018 | 11.3858 | 4.1511 | 0.6155 | 0.6587 | 0.9627 | 0.7398 | -129.6304 | -0.7109 | 5.3208 | 1.8911 | -3.1441 | -1.4339 | 4.5563 |  | 2.9778 | 0.188 | 4.008 | 3.3659 | 3.3341 | 1.0715 | 10.7533 | 14.2673 | 14.8417 | 11.106 | -0.0004 | -0.0025 | 0.0005 | 0.0039 | 0.0004 | -0.0005 | -0.0018 | -0.0166 | -0.0065 | -360.1558 | 17.4356 | -360.5096 | 17.7149 | -360.8697 | 18.1317 | -360.7989 | 17.5937 | -352.666 | 18.7374 | -352.7367 | 16.8381
12:31 | 4256 | 40.7368 | 202.0879 | 449.2503 | 455.9326 | -16.5739 | -41.4821 | 10.9159 | 7.7013 | 1.8405 | 0.3406 | 3.0759 | -1.1527 | 11.4287 | 4.1694 | 0.6165 | 0.6559 | 0.9617 | 0.7405 | -129.4791 | -0.6585 | 5.3468 | 1.8974 | -3.052 | -1.4078 | 4.6062 |  | 2.9828 | 0.2251 | 4.0087 | 3.3627 | 3.3394 | 1.0707 | 10.7325 | 14.2579 | 14.8202 | 11.0854 | 0.0001 | -0.0029 | 0.0004 | 0.0038 | 0.0009 | -0.0005 | 0.0267 | -0.0165 | 0.007 | -360.1465 | 17.3782 | -360.4173 | 17.68 | -360.8358 | 18.1871 | -360.8974 | 17.6143 | -352.6352 | 18.682 | -352.6413 | 16.8238
12:31 | 4257 | 40.769 | 202.0876 | 449.3799 | 455.9575 | -16.5429 | -41.4002 | 10.8097 | 7.7366 | 1.8878 | 0.3892 | 3.1982 | -1.196 | 11.3619 | 4.1921 | 0.6147 | 0.6581 | 0.9643 | 0.7394 | -129.5172 | -0.6899 | 5.4203 | 1.9072 | -3.0373 | -1.4321 | 4.5564 |  | 2.9565 | 0.1607 | 4.0091 | 3.3629 | 3.3375 | 1.0724 | 10.7752 | 14.2778 | 14.8877 | 11.1161 | 0.0002 | -0.0029 | 0.0003 | 0.0038 | 0.0009 | 0 | 0.021 | -0.0244 | -0.0214 | -360.2019 | 17.4172 | -360.4389 | 17.6574 | -360.762 | 18.1071 | -360.8112 | 17.6102 | -352.6875 | 18.7148 | -352.6721 | 16.7909
12:31 | 4258 | 40.6892 | 202.0654 | 449.2039 | 455.9624 | -16.5127 | -41.241 | 10.753 | 7.6484 | 1.7417 | 0.3257 | 3.131 | -1.2302 | 11.3684 | 4.0822 | 0.6137 | 0.6598 | 0.9637 | 0.7396 | -129.645 | -0.7443 | 5.4235 | 1.8643 | -3.0431 | -1.4261 | 4.4314 |  | 2.9877 | 0.2285 | 4.0091 | 3.364 | 3.3398 | 1.0719 | 10.7591 | 14.2555 | 14.8464 | 11.0659 | 0.0001 | -0.003 | 0.001 | 0.004 | 0.001 | -0.0007 | -0.0036 | 0.0014 | -0.0152 | -360.1065 | 17.3802 | -360.4727 | 17.6964 | -360.8143 | 18.1214 | -360.7866 | 17.5547 | -352.5767 | 18.684 | -352.6629 | 16.8258
12:31 | 4259 | 40.6938 | 202.0175 | 449.2723 | 455.9817 | -16.4986 | -41.1641 | 10.808 | 7.5958 | 1.8042 | 0.2027 | 3.1513 | -1.2285 | 11.4118 | 4.09 | 0.6157 | 0.6614 | 0.962 | 0.7407 | -129.6762 | -0.7846 | 5.3848 | 1.7845 | -2.9115 | -1.5423 | 4.4811 |  | 2.9618 | 0.2296 | 4.0097 | 3.3675 | 3.3361 | 1.0719 | 10.7845 | 14.2696 | 14.9023 | 11.1139 | -0.0005 | -0.0028 | 0.0009 | 0.004 | 0.0008 | -0.0002 | 0.0312 | 0.0011 | -0.004 | -360.1527 | 17.3699 | -360.3681 | 17.6245 | -360.7589 | 18.1379 | -360.8604 | 17.5917 | -352.629 | 18.6594 | -352.5921 | 16.7807
12:31 | 4260 | 40.7227 | 202.002 | 449.2734 | 456.0403 | -16.5515 | -41.3016 | 10.8525 | 7.5971 | 1.8085 | 0.2457 | 3.118 | -1.0609 | 11.4352 | 4.1807 | 0.6163 | 0.6601 | 0.9615 | 0.7392 | -129.6781 | -0.8546 | 5.3735 | 1.7248 | -3.0101 | -1.5285 | 4.4509 |  | 3.0386 | 0.2035 | 4.0105 | 3.3652 | 3.3407 | 1.0719 | 10.7394 | 14.2532 | 14.8089 | 11.0695 | 0.0001 | -0.0028 | 0.001 | 0.0037 | 0.0006 | -0.0011 | 0.0006 | -0.0144 | 0.0139 | -360.2081 | 17.4233 | -360.4789 | 17.6841 | -360.7958 | 18.1091 | -360.7866 | 17.5794 | -352.6567 | 18.721 | -352.6906 | 16.793
12:31 | 4261 | 40.8012 | 202.0567 | 449.2499 | 456.0938 | -16.6672 | -41.3267 | 10.8694 | 7.6122 | 1.7782 | 0.1997 | 3.0853 | -1.156 | 11.3598 | 4.1954 | 0.6144 | 0.6552 | 0.9607 | 0.739 | -129.6863 | -0.8271 | 5.2908 | 1.7179 | -3.0529 | -1.5016 | 4.5032 |  | 3.0043 | 0.1585 | 4.008 | 3.3633 | 3.3366 | 1.0706 | 10.7545 | 14.2683 | 14.8535 | 11.0728 | 0.0001 | -0.0034 | 0.001 | 0.0039 | 0.0006 | -0.0004 | 0.013 | -0.0049 | -0.0171 | -360.1435 | 17.3782 | -360.4327 | 17.7005 | -360.8635 | 18.1728 | -360.8543 | 17.5855 | -352.5952 | 18.6655 | -352.6383 | 16.8197
12:31 | 4262 | 40.645 | 202.0575 | 449.2417 | 456.1024 | -16.5631 | -41.2322 | 10.895 | 7.6629 | 1.9143 | 0.1376 | 3.163 | -1.1173 | 11.392 | 4.2022 | 0.6145 | 0.6565 | 0.9585 | 0.7394 | -129.63 | -0.7896 | 5.4001 | 1.8006 | -3.0243 | -1.5027 | 4.4977 |  | 2.9809 | 0.0794 | 4.0106 | 3.3655 | 3.3409 | 1.0708 | 10.7855 | 14.2944 | 14.8721 | 11.1081 | 0.0001 | -0.0028 | 0.0007 | 0.0041 | 0.001 | 0 | -0.0053 | 0.0042 | -0.0075 | -360.2573 | 17.4274 | -360.4666 | 17.6759 | -360.802 | 18.1461 | -360.8943 | 17.6492 | -352.7152 | 18.723 | -352.666 | 16.795
12:31 | 4263 | 40.6498 | 202.0459 | 449.2184 | 456.0011 | -16.6228 | -41.2064 | 10.8777 | 7.6223 | 1.8566 | 0.1821 | 3.1694 | -1.0512 | 11.3478 | 4.1854 | 0.6153 | 0.659 | 0.9594 | 0.7403 | -129.6521 | -0.7049 | 5.4476 | 1.7887 | -3.0427 | -1.4839 | 4.5191 |  | 2.8859 | 0.146 | 4.0092 | 3.3647 | 3.3383 | 1.072 | 10.7741 | 14.2418 | 14.8852 | 11.1154 | -0.0002 | -0.003 | 0.0008 | 0.0044 | 0.0012 | -0.0003 | 0.0053 | 0.0037 | -0.0051 | -360.1773 | 17.4377 | -360.5066 | 17.7334 | -360.8912 | 18.144 | -360.8112 | 17.5876 | -352.6629 | 18.7292 | -352.7121 | 16.8443
12:31 | 4264 | 40.6535 | 202.0431 | 449.2375 | 456.0392 | -16.5649 | -41.1918 | 10.7423 | 7.6068 | 1.9064 | 0.0363 | 3.0905 | -1.1621 | 11.3864 | 4.1594 | 0.6145 | 0.6562 | 0.9629 | 0.7388 | -129.6434 | -0.828 | 5.4312 | 1.8413 | -3.042 | -1.4929 | 4.5203 |  | 2.9494 | 0.1019 | 4.0099 | 3.3651 | 3.3362 | 1.0712 | 10.7521 | 14.2718 | 14.8634 | 11.1049 | -0.0002 | -0.0025 | 0.0006 | 0.004 | 0.0009 | -0.0002 | 0.0168 | 0.0031 | -0.0036 | -360.2204 | 17.4007 | -360.4173 | 17.6738 | -360.8266 | 18.1748 | -360.9127 | 17.6225 | -352.6906 | 18.6963 | -352.6506 | 16.8074
12:31 | 4265 | 40.6348 | 202.0372 | 449.2538 | 456.0189 | -16.5323 | -41.1814 | 10.8042 | 7.6706 | 1.9161 | 0.1392 | 3.1823 | -1.0944 | 11.3722 | 4.0996 | 0.6147 | 0.6585 | 0.9595 | 0.7381 | -129.6292 | -0.6976 | 5.4381 | 1.8245 | -2.9921 | -1.4584 | 4.4846 |  | 2.9831 | 0.0779 | 4.0111 | 3.3628 | 3.3392 | 1.0714 | 10.7567 | 14.2708 | 14.8226 | 11.0803 | 0.0002 | -0.0028 | 0.0005 | 0.0036 | 0.0014 | -0.0003 | 0.0133 | 0.002 | -0.0244 | -360.2296 | 17.4377 | -360.4942 | 17.682 | -360.7958 | 18.1337 | -360.8327 | 17.6163 | -352.7183 | 18.7353 | -352.6906 | 16.8115
12:31 | 4266 | 40.5262 | 202.0114 | 449.2353 | 456.0255 | -16.4889 | -41.2276 | 10.8268 | 7.6472 | 1.9595 | 0.22 | 3.2935 | -1.1485 | 11.3426 | 4.217 | 0.6146 | 0.6583 | 0.9603 | 0.7385 | -129.5867 | -0.7297 | 5.3389 | 1.7517 | -3.1249 | -1.4682 | 4.4406 |  | 2.9752 | 0.0309 | 4.0105 | 3.3645 | 3.3369 | 1.0723 | 10.7476 | 14.2727 | 14.8627 | 11.0779 | -0.0002 | -0.0031 | 0.0003 | 0.0033 | 0.0004 | -0.0003 | 0.0064 | 0.0065 | -0.0047 | -360.1281 | 17.3843 | -360.4481 | 17.6964 | -360.8574 | 18.1625 | -360.8297 | 17.5753 | -352.6075 | 18.6881 | -352.6813 | 16.8402
12:31 | 4267 | 40.6505 | 201.9694 | 449.3332 | 456.0207 | -16.5305 | -41.1805 | 10.8599 | 7.6577 | 1.9503 | 0.1076 | 3.2146 | -1.0959 | 11.376 | 4.2425 | 0.6147 | 0.6592 | 0.9604 | 0.7382 | -129.6458 | -0.8554 | 5.39 | 1.6913 | -3.0888 | -1.5017 | 4.3873 |  | 2.9984 | 0.0858 | 4.009 | 3.3621 | 3.338 | 1.0708 | 10.7359 | 14.2499 | 14.8475 | 11.1118 | -0.0002 | -0.0027 | 0.0008 | 0.0034 | 0.0011 | -0.0007 | 0.0006 | -0.018 | -0.028 | -360.1773 | 17.3946 | -360.4019 | 17.6286 | -360.7743 | 18.142 | -360.8512 | 17.6225 | -352.669 | 18.6902 | -352.6229 | 16.7766
12:31 | 4268 | 40.6955 | 202.0127 | 449.2854 | 456.0424 | -16.4954 | -41.0737 | 10.8813 | 7.6372 | 1.9673 | 0.1862 | 3.1887 | -1.125 | 11.436 | 4.302 | 0.6141 | 0.6607 | 0.9632 | 0.7385 | -129.6431 | -0.8408 | 5.4007 | 1.7218 | -3.0867 | -1.3996 | 4.4865 |  | 3.0021 | 0.1338 | 4.0104 | 3.3661 | 3.339 | 1.0728 | 10.7348 | 14.2429 | 14.8519 | 11.076 | -0.0004 | -0.0026 | 0.0007 | 0.0042 | 0.0005 | -0.0004 | 0.0092 | -0.0075 | 0.005 | -360.1373 | 17.4048 | -360.4635 | 17.6677 | -360.7958 | 18.1112 | -360.7527 | 17.5691 | -352.6167 | 18.7066 | -352.6783 | 16.8135
12:31 | 4269 | 40.6312 | 202.0308 | 449.3436 | 456.0155 | -16.4841 | -41.1564 | 10.9689 | 7.6137 | 1.9022 | 0.1336 | 3.173 | -1.1427 | 11.3531 | 4.2058 | 0.6138 | 0.6574 | 0.9647 | 0.7399 | -129.6108 | -0.7797 | 5.4553 | 1.7617 | -3.1161 | -1.4366 | 4.5068 |  | 2.999 | 0.1379 | 4.0104 | 3.3657 | 3.3404 | 1.0711 | 10.7336 | 14.2477 | 14.8458 | 11.0861 | 0.0003 | -0.0028 | 0.0008 | 0.004 | 0.001 | -0.0006 | 0.0052 | -0.0037 | -0.0063 | -360.0942 | 17.3576 | -360.3773 | 17.643 | -360.805 | 18.1604 | -360.8512 | 17.5917 | -352.586 | 18.6594 | -352.586 | 16.7868
12:31 | 4270 | 40.699 | 202.0852 | 449.3116 | 456.026 | -16.4741 | -41.1122 | 10.9204 | 7.6304 | 1.9632 | 0.1779 | 3.2141 | -1.2071 | 11.3972 | 4.1887 | 0.6158 | 0.6596 | 0.9633 | 0.7389 | -129.6179 | -0.7008 | 5.4726 | 1.7805 | -3.071 | -1.4307 | 4.5036 |  | 3.0289 | 0.1654 | 4.0111 | 3.3623 | 3.3371 | 1.072 | 10.7671 | 14.264 | 14.8513 | 11.0847 | 0.0006 | -0.0026 | 0.0008 | 0.0043 | 0.001 | -0.0001 | 0.0026 | -0.0118 | -0.0062 | -360.1927 | 17.4254 | -360.4481 | 17.6451 | -360.7743 | 18.1029 | -360.8174 | 17.5978 | -352.6567 | 18.7107 | -352.6229 | 16.7766
12:31 | 4271 | 40.7635 | 202.0245 | 449.296 | 456.0517 | -16.3996 | -41.0404 | 10.9525 | 7.6435 | 1.9394 | 0.0854 | 3.2399 | -1.2088 | 11.3571 | 4.1892 | 0.6159 | 0.6583 | 0.9607 | 0.7407 | -129.5996 | -0.6247 | 5.4526 | 1.8326 | -3.0931 | -1.4819 | 4.3761 |  | 3.0004 | 0.1657 | 4.0109 | 3.3667 | 3.3396 | 1.0726 | 10.7568 | 14.2474 | 14.8263 | 11.0753 | -0.0003 | -0.0028 | 0.0009 | 0.0044 | 0.0006 | -0.0006 | 0.0014 | -0.0178 | -0.0207 | -360.1311 | 17.3987 | -360.4789 | 17.6902 | -360.8635 | 18.1543 | -360.8481 | 17.5671 | -352.5767 | 18.6943 | -352.669 | 16.8299
12:31 | 4272 | 40.7285 | 201.9599 | 449.2462 | 456.0066 | -16.3426 | -41.0624 | 10.9607 | 7.6267 | 1.9585 | 0.1405 | 3.2209 | -1.2329 | 11.3476 | 4.1661 | 0.6166 | 0.6616 | 0.9618 | 0.7413 | -129.5787 | -0.7046 | 5.3799 | 1.63 | -3.1016 | -1.4479 | 4.3683 |  | 2.9996 | 0.2289 | 4.0108 | 3.3673 | 3.3406 | 1.0728 | 10.7716 | 14.2747 | 14.8752 | 11.0713 | 0.0003 | -0.0019 | 0.0011 | 0.0044 | 0.0009 | 0 | 0.0227 | -0.0075 | -0.0124 | -360.2235 | 17.4007 | -360.4204 | 17.6553 | -360.8174 | 18.1707 | -360.8974 | 17.6266 | -352.6813 | 18.7025 | -352.629 | 16.7889
12:31 | 4273 | 40.7267 | 202.0799 | 449.382 | 456.051 | -16.537 | -41.13 | 10.8508 | 7.7003 | 1.999 | 0.2592 | 3.2585 | -1.2597 | 11.3691 | 4.1715 | 0.6156 | 0.6612 | 0.965 | 0.7409 | -129.6614 | -0.8068 | 5.2666 | 1.7394 | -3.1582 | -1.4522 | 4.3835 |  | 2.9514 | 0.2121 | 4.0116 | 3.3679 | 3.3368 | 1.0721 | 10.766 | 14.2741 | 14.8593 | 11.0786 | 0.0004 | -0.0029 | 0.0004 | 0.0033 | 0.0006 | -0.0006 | 0.0216 | 0.0009 | -0.0103 | -360.1773 | 17.4459 | -360.5404 | 17.6923 | -360.8512 | 18.1255 | -360.8297 | 17.602 | -352.6567 | 18.7374 | -352.7152 | 16.8402
12:31 | 4274 | 40.7663 | 202.0248 | 449.3785 | 455.9796 | -16.489 | -41.0446 | 10.835 | 7.6494 | 1.9176 | 0.2123 | 3.1724 | -1.2771 | 11.3308 | 4.1685 | 0.6163 | 0.6592 | 0.9621 | 0.7382 | -129.691 | -0.8277 | 5.2603 | 1.6605 | -3.1701 | -1.4862 | 4.2881 |  | 2.9461 | 0.0969 | 4.0087 | 3.365 | 3.3364 | 1.0713 | 10.7233 | 14.2367 | 14.8255 | 11.0714 | -0.0003 | -0.003 | 0.0006 | 0.0034 | 0.0011 | -0.0009 | 0.0135 | 0.0035 | -0.0123 | -360.1619 | 17.3823 | -360.4296 | 17.68 | -360.8635 | 18.1707 | -360.882 | 17.5999 | -352.6444 | 18.684 | -352.6383 | 16.8299
12:31 | 4275 | 40.806 | 202.0225 | 449.3152 | 456.0203 | -16.4773 | -41.0555 | 10.8735 | 7.577 | 1.9883 | 0.2042 | 3.0721 | -1.2535 | 11.3428 | 4.2106 | 0.6169 | 0.659 | 0.9621 | 0.7388 | -129.5886 | -0.7135 | 5.2559 | 1.7268 | -3.1057 | -1.4911 | 4.3702 |  | 2.9138 | 0.1872 | 4.0094 | 3.3638 | 3.3398 | 1.0729 | 10.7312 | 14.257 | 14.8499 | 11.1125 | -0.0001 | -0.0028 | 0.0009 | 0.0035 | 0.0009 | -0.0002 | 0.0035 | 0.0006 | -0.017 | -360.1958 | 17.4151 | -360.4389 | 17.6369 | -360.765 | 18.1194 | -360.8327 | 17.5835 | -352.6475 | 18.7066 | -352.6383 | 16.793
12:31 | 4276 | 40.7131 | 202.0623 | 449.3857 | 456.0009 | -16.5058 | -41.1943 | 10.9051 | 7.6724 | 2.0093 | 0.2711 | 3.1345 | -1.3388 | 11.3418 | 4.0781 | 0.6156 | 0.6588 | 0.961 | 0.7405 | -129.5291 | -0.6729 | 5.2956 | 1.7153 | -3.0968 | -1.4298 | 4.3889 |  | 2.9263 | 0.1075 | 4.0116 | 3.3647 | 3.3367 | 1.0724 | 10.7188 | 14.2549 | 14.8363 | 11.0732 | -0.0007 | -0.0028 | 0.0007 | 0.0035 | 0.0009 | -0.0011 | 0.0207 | -0.0136 | 0.0099 | -360.1158 | 17.3884 | -360.4542 | 17.6779 | -360.8266 | 18.1214 | -360.7989 | 17.5486 | -352.5921 | 18.6799 | -352.6721 | 16.832
12:31 | 4277 | 40.7779 | 202.0092 | 449.2861 | 455.993 | -16.4663 | -41.1392 | 10.9879 | 7.6266 | 2.0018 | 0.3261 | 3.2448 | -1.222 | 11.3009 | 4.171 | 0.6157 | 0.6609 | 0.9635 | 0.7391 | -129.5444 | -0.7983 | 5.3591 | 1.7985 | -3.1701 | -1.4387 | 4.453 |  | 2.9424 | 0.092 | 4.0107 | 3.3624 | 3.3379 | 1.0722 | 10.7266 | 14.2524 | 14.8339 | 11.0847 | 0 | -0.0029 | 0.0016 | 0.0046 | 0.0009 | 0 | 0.0239 | -0.0001 | 0.004 | -360.1496 | 17.3638 | -360.405 | 17.643 | -360.7835 | 18.1358 | -360.8327 | 17.5937 | -352.6106 | 18.6553 | -352.589 | 16.793
12:31 | 4278 | 40.7535 | 201.9877 | 449.2686 | 455.9776 | -16.5084 | -41.1728 | 10.9582 | 7.6734 | 2.0043 | 0.3046 | 3.2199 | -1.1949 | 11.4975 | 4.1402 | 0.6169 | 0.6644 | 0.9625 | 0.739 | -129.5739 | -0.8212 | 5.3524 | 1.7604 | -3.2275 | -1.4457 | 4.4394 |  | 2.9363 | 0.0675 | 4.0114 | 3.3645 | 3.3391 | 1.0708 | 10.7429 | 14.2278 | 14.8188 | 11.0786 | 0.0002 | -0.003 | 0.0006 | 0.0035 | 0.0013 | -0.0005 | 0.0236 | -0.0037 | 0.0071 | -360.2204 | 17.4274 | -360.4789 | 17.6615 | -360.8081 | 18.1112 | -360.805 | 17.5896 | -352.6567 | 18.7107 | -352.669 | 16.8053
12:31 | 4279 | 40.7469 | 201.991 | 449.2637 | 456.0179 | -16.5248 | -41.2547 | 10.841 | 7.6343 | 1.893 | 0.1023 | 3.147 | -1.2553 | 11.3634 | 4.1115 | 0.617 | 0.6612 | 0.9636 | 0.739 | -129.5589 | -0.795 | 5.4059 | 1.7774 | -3.2429 | -1.5215 | 4.4127 |  | 2.9854 | 0.0488 | 4.0095 | 3.3663 | 3.3378 | 1.0721 | 10.766 | 14.28 | 14.8662 | 11.1129 | 0 | -0.0027 | 0.0001 | 0.0036 | 0.0006 | -0.0003 | 0.0257 | -0.0029 | -0.0018 | -360.1096 | 17.4069 | -360.4696 | 17.6923 | -360.8574 | 18.1625 | -360.842 | 17.5773 | -352.6136 | 18.6881 | -352.6906 | 16.832
12:31 | 4280 | 40.8023 | 201.9689 | 449.2589 | 456.0222 | -16.4756 | -41.3375 | 10.8353 | 7.6805 | 1.8898 | 0.2846 | 3.1863 | -1.2157 | 11.3519 | 4.1076 | 0.6159 | 0.6616 | 0.963 | 0.7398 | -129.58 | -0.7719 | 5.4251 | 1.7569 | -3.2089 | -1.4633 | 4.325 |  | 2.9376 | 0.0469 | 4.0105 | 3.3629 | 3.3382 | 1.0705 | 10.744 | 14.2581 | 14.8386 | 11.0793 | -0.0003 | -0.0028 | 0.0008 | 0.0039 | 0.0008 | -0.0008 | 0.0123 | -0.0054 | -0.009 | -360.1773 | 17.4233 | -360.4696 | 17.6615 | -360.8112 | 18.1625 | -360.8881 | 17.6369 | -352.6844 | 18.7045 | -352.6198 | 16.8115
12:31 | 4281 | 40.7298 | 201.9811 | 449.2406 | 455.9799 | -16.4459 | -41.2114 | 11.0007 | 7.7109 | 1.9366 | 0.341 | 3.1521 | -1.2605 | 11.4023 | 4.1555 | 0.6158 | 0.6603 | 0.9642 | 0.7392 | -129.5589 | -0.7967 | 5.4061 | 1.7058 | -3.2709 | -1.5737 | 4.3204 |  | 2.9567 | 0.085 | 4.0108 | 3.3663 | 3.3364 | 1.072 | 10.7972 | 14.265 | 14.84 | 11.1208 | 0.0001 | -0.0028 | 0.0007 | 0.0036 | 0.0006 | -0.0001 | 0.0134 | -0.0142 | 0.0098 | -360.1742 | 17.4295 | -360.5096 | 17.7026 | -360.8543 | 18.1399 | -360.8235 | 17.5999 | -352.6598 | 18.7148 | -352.7121 | 16.8443
12:31 | 4282 | 40.7572 | 201.9707 | 449.3061 | 455.9785 | -16.4959 | -41.1852 | 10.9223 | 7.7008 | 2.0557 | 0.4091 | 3.1851 | -1.2805 | 11.4072 | 4.1058 | 0.6168 | 0.6614 | 0.9609 | 0.7385 | -129.6197 | -0.74 | 5.4369 | 1.6971 | -3.2505 | -1.4953 | 4.3906 |  | 2.879 | 0.0258 | 4.0121 | 3.3672 | 3.3391 | 1.0727 | 10.7498 | 14.2521 | 14.8607 | 11.1085 | 0.0002 | -0.003 | 0.0007 | 0.0037 | 0.0008 | -0.0007 | 0.015 | 0.0064 | -0.0117 | -360.1711 | 17.3946 | -360.445 | 17.6841 | -360.8666 | 18.1728 | -360.8789 | 17.6204 | -352.666 | 18.7004 | -352.6506 | 16.8217
12:31 | 4283 | 40.7334 | 201.9923 | 449.2268 | 456.0127 | -16.4582 | -41.2111 | 10.9225 | 7.6556 | 1.9488 | 0.2368 | 3.1208 | -1.2388 | 11.4198 | 4.1619 | 0.6166 | 0.6651 | 0.9635 | 0.7412 | -129.6365 | -0.7594 | 5.3784 | 1.6439 | -3.2099 | -1.4912 | 4.4322 |  | 2.8699 | 0.1137 | 4.0097 | 3.3643 | 3.3382 | 1.0716 | 10.7475 | 14.2613 | 14.858 | 11.0659 | -0.0005 | -0.0034 | 0.0012 | 0.0038 | 0.0007 | -0.0006 | 0.0169 | -0.0215 | -0.0079 | -360.2081 | 17.4315 | -360.5004 | 17.6656 | -360.805 | 18.142 | -360.845 | 17.6307 | -352.6813 | 18.7251 | -352.6752 | 16.8074
12:31 | 4284 | 40.8766 | 202.0854 | 449.2987 | 456.0544 | -16.4867 | -41.2481 | 11.0285 | 7.6904 | 2.0178 | 0.328 | 3.1574 | -1.2387 | 11.4399 | 4.2236 | 0.6145 | 0.6593 | 0.9635 | 0.7401 | -129.6343 | -0.7513 | 5.4466 | 1.4787 | -3.1899 | -1.5252 | 4.3191 |  | 2.8971 | 0.0703 | 4.0084 | 3.3663 | 3.3401 | 1.0725 | 10.7324 | 14.2638 | 14.8386 | 11.085 | -0.0002 | -0.0024 | 0.0005 | 0.0037 | 0.0005 | -0.0005 | 0.0214 | -0.0127 | -0.0074 | -360.1558 | 17.4069 | -360.4881 | 17.7026 | -360.8574 | 18.1543 | -360.8481 | 17.5917 | -352.6383 | 18.7066 | -352.7121 | 16.8464
12:31 | 4285 | 40.9137 | 202.1131 | 449.3627 | 456.048 | -16.5447 | -41.2844 | 10.8718 | 7.7664 | 2.0645 | 0.3442 | 3.1604 | -1.2357 | 11.4198 | 4.2115 | 0.6149 | 0.6611 | 0.964 | 0.7384 | -129.5811 | -0.7925 | 5.4853 | 1.4795 | -3.2777 | -1.5107 | 4.3219 |  | 2.8817 | 0.2074 | 4.0074 | 3.3658 | 3.3401 | 1.0711 | 10.7544 | 14.28 | 14.8372 | 11.0551 | -0.0007 | -0.0034 | 0.0012 | 0.0045 | 0.0011 | -0.0004 | -0.0073 | -0.0054 | -0.0166 | -360.165 | 17.3925 | -360.4235 | 17.643 | -360.805 | 18.1481 | -360.8666 | 17.6348 | -352.6413 | 18.6779 | -352.629 | 16.8053
12:31 | 4286 | 40.8846 | 202.0327 | 449.2255 | 456.0547 | -16.4864 | -41.1767 | 10.9598 | 7.7771 | 2.0151 | 0.2015 | 3.1039 | -1.312 | 11.3401 | 4.1605 | 0.6157 | 0.6611 | 0.9618 | 0.738 | -129.6448 | -0.819 | 5.3684 | 1.4997 | -3.2727 | -1.5596 | 4.3193 |  | 2.9627 | 0.2543 | 4.0096 | 3.3653 | 3.3406 | 1.0717 | 10.7636 | 14.2721 | 14.8424 | 11.0637 | 0.0002 | -0.0029 | 0.0011 | 0.0044 | 0.0008 | 0 | 0.0254 | -0.0118 | 0.0073 | -360.1558 | 17.4151 | -360.4819 | 17.6656 | -360.805 | 18.1132 | -360.805 | 17.5794 | -352.6475 | 18.7128 | -352.6813 | 16.8094
12:31 | 4287 | 40.973 | 202.1405 | 449.3946 | 456.142 | -16.5136 | -41.2078 | 10.9209 | 7.7967 | 2.1751 | 0.3543 | 3.1576 | -1.2943 | 11.3523 | 4.1201 | 0.6158 | 0.6583 | 0.9621 | 0.7394 | -129.5651 | -0.7599 | 5.4627 | 1.5291 | -3.2999 | -1.5317 | 4.3602 |  | 2.923 | 0.2151 | 4.01 | 3.3652 | 3.3399 | 1.0713 | 10.7393 | 14.2535 | 14.8458 | 11.063 | 0.0002 | -0.0029 | 0.0003 | 0.004 | 0.0009 | -0.0004 | 0.0148 | -0.0064 | 0.0069 | -360.1034 | 17.372 | -360.4266 | 17.6594 | -360.8112 | 18.144 | -360.8389 | 17.5712 | -352.5829 | 18.6717 | -352.6321 | 16.8238
12:31 | 4288 | 40.8876 | 202.1316 | 449.4112 | 456.1143 | -16.4388 | -41.1237 | 10.9538 | 7.6867 | 2.1379 | 0.2901 | 3.2176 | -1.2331 | 11.4239 | 4.1492 | 0.6149 | 0.6594 | 0.9607 | 0.7378 | -129.6049 | -0.7255 | 5.4731 | 1.4904 | -3.2943 | -1.5664 | 4.2879 |  | 2.8868 | 0.1525 | 4.0106 | 3.3676 | 3.3371 | 1.0706 | 10.7775 | 14.2455 | 14.8499 | 11.0836 | -0.0002 | -0.0027 | 0.0011 | 0.0039 | 0.0003 | -0.0001 | -0.0017 | -0.0048 | -0.0146 | -360.1588 | 17.3905 | -360.4173 | 17.6204 | -360.7497 | 18.1173 | -360.8266 | 17.5999 | -352.6198 | 18.684 | -352.6198 | 16.7786
12:31 | 4289 | 40.9395 | 202.0213 | 449.2889 | 456.028 | -16.4607 | -41.128 | 11.0147 | 7.718 | 2.0824 | 0.245 | 3.2818 | -1.2112 | 11.4795 | 4.3021 | 0.6148 | 0.659 | 0.9645 | 0.7386 | -129.5809 | -0.7267 | 5.412 | 1.5299 | -3.2638 | -1.5974 | 4.3611 |  | 2.9227 | 0.0736 | 4.0096 | 3.3642 | 3.3384 | 1.071 | 10.7659 | 14.2745 | 14.8336 | 11.0948 | 0.0001 | -0.0025 | 0.0005 | 0.0034 | 0.0014 | -0.0001 | 0.0073 | -0.0091 | -0.0233 | -360.1342 | 17.4028 | -360.4789 | 17.68 | -360.8112 | 18.1173 | -360.7712 | 17.5691 | -352.6013 | 18.6943 | -352.6783 | 16.834
12:31 | 4290 | 40.9159 | 202.0364 | 449.3092 | 456.061 | -16.4008 | -41.081 | 10.9782 | 7.7596 | 2.0785 | 0.3643 | 3.1835 | -1.3623 | 11.3626 | 4.1 | 0.6139 | 0.6593 | 0.962 | 0.7386 | -129.7304 | -0.7891 | 5.3272 | 1.5966 | -3.3052 | -1.5232 | 4.363 |  | 2.9749 | 0.0699 | 4.0094 | 3.3662 | 3.3361 | 1.0707 | 10.7291 | 14.26 | 14.8382 | 11.0479 | -0.0001 | -0.0035 | 0.0006 | 0.0034 | 0.0003 | -0.0007 | 0.0029 | -0.0128 | -0.0165 | -360.1865 | 17.3843 | -360.3989 | 17.6553 | -360.802 | 18.1584 | -360.8543 | 17.602 | -352.6198 | 18.6717 | -352.5983 | 16.8115
12:31 | 4291 | 40.8918 | 202.0193 | 449.2963 | 456.079 | -16.4265 | -41.1169 | 11.0029 | 7.6819 | 2.1072 | 0.4052 | 3.2649 | -1.2227 | 11.415 | 4.2658 | 0.6159 | 0.659 | 0.9638 | 0.738 | -129.6856 | -0.7057 | 5.4581 | 1.6252 | -3.2052 | -1.5459 | 4.3995 |  | 2.8995 | 0.1097 | 4.0099 | 3.3622 | 3.3385 | 1.0711 | 10.7463 | 14.2429 | 14.7882 | 11.0587 | -0.0001 | -0.0028 | 0.0012 | 0.004 | 0.0012 | -0.0005 | 0.0117 | -0.0096 | -0.0217 | -360.2265 | 17.45 | -360.5004 | 17.6841 | -360.805 | 18.1379 | -360.8481 | 17.6102 | -352.6967 | 18.7312 | -352.6875 | 16.8258
12:31 | 4292 | 40.9058 | 202.045 | 449.3337 | 456.0448 | -16.4884 | -41.1046 | 10.9491 | 7.5732 | 2.0444 | 0.3612 | 3.2549 | -1.1137 | 11.4633 | 4.1803 | 0.6163 | 0.6595 | 0.9622 | 0.7405 | -129.5893 | -0.8873 | 5.4743 | 1.5862 | -3.2059 | -1.6183 | 4.4286 |  | 2.9279 | 0.1452 | 4.0098 | 3.3691 | 3.3342 | 1.0719 | 10.7568 | 14.2649 | 14.8563 | 11.0749 | -0.0006 | -0.0027 | 0.0008 | 0.004 | 0.0006 | -0.0004 | 0.0183 | -0.0082 | -0.0063 | -360.1865 | 17.411 | -360.4912 | 17.7046 | -360.8697 | 18.1461 | -360.8512 | 17.5773 | -352.6229 | 18.7025 | -352.6937 | 16.8587
12:31 | 4293 | 40.9294 | 202.0751 | 449.2959 | 456.0253 | -16.4869 | -41.0986 | 10.9148 | 7.5502 | 2.0424 | 0.3068 | 3.2458 | -1.1627 | 11.4233 | 4.1652 | 0.616 | 0.6576 | 0.9641 | 0.7393 | -129.6385 | -0.9349 | 5.3821 | 1.6097 | -3.2193 | -1.5436 | 4.4497 |  | 3.0181 | 0.2823 | 4.0108 | 3.3684 | 3.3378 | 1.0725 | 10.7382 | 14.2581 | 14.8444 | 11.1024 | 0 | -0.0023 | 0.0011 | 0.0045 | 0.0009 | -0.001 | 0.0019 | -0.0064 | -0.0037 | -360.2204 | 17.411 | -360.4666 | 17.6697 | -360.8235 | 18.1604 | -360.9158 | 17.6286 | -352.6937 | 18.6963 | -352.6629 | 16.8217
12:31 | 4294 | 40.9498 | 202.1748 | 449.3372 | 456.0357 | -16.5607 | -41.0572 | 10.9518 | 7.5915 | 2.0304 | 0.3774 | 3.3063 | -1.1595 | 11.3839 | 4.2146 | 0.6143 | 0.6593 | 0.9627 | 0.7389 | -129.5691 | -0.7079 | 5.409 | 1.4933 | -3.1742 | -1.4888 | 4.3562 |  | 2.9764 | 0.1818 | 4.0095 | 3.3694 | 3.3404 | 1.0714 | 10.7809 | 14.2664 | 14.8714 | 11.0926 | -0.0001 | -0.0033 | 0.0009 | 0.004 | 0.0009 | -0.0002 | 0.0009 | -0.0089 | -0.0186 | -360.1865 | 17.4356 | -360.5158 | 17.6861 | -360.842 | 18.1276 | -360.8327 | 17.5999 | -352.6598 | 18.7353 | -352.7213 | 16.8464
12:31 | 4295 | 40.9744 | 202.0808 | 449.2843 | 456.0041 | -16.6154 | -41.1789 | 10.9441 | 7.6183 | 2.0822 | 0.49 | 3.35 | -1.1245 | 11.4087 | 4.1848 | 0.6162 | 0.6621 | 0.9625 | 0.7403 | -129.6142 | -0.7819 | 5.4455 | 1.5453 | -3.2651 | -1.6609 | 4.3198 |  | 2.9329 | 0.1551 | 4.0102 | 3.3674 | 3.3364 | 1.0711 | 10.7579 | 14.2776 | 14.8461 | 11.076 | 0.0003 | -0.0032 | 0.0004 | 0.0034 | 0.0005 | -0.0004 | 0.0059 | -0.0084 | -0.0072 | -360.1373 | 17.3925 | -360.4542 | 17.68 | -360.845 | 18.1707 | -360.8758 | 17.5999 | -352.6475 | 18.6881 | -352.6321 | 16.8381
12:31 | 4296 | 40.8881 | 202.0707 | 449.2973 | 456.0807 | -16.5825 | -41.1661 | 10.9325 | 7.6182 | 1.9693 | 0.3613 | 3.3034 | -1.0578 | 11.406 | 4.267 | 0.616 | 0.6609 | 0.9634 | 0.7396 | -129.6379 | -0.7586 | 5.4392 | 1.5194 | -3.2521 | -1.6493 | 4.354 |  | 2.9764 | 0.1919 | 4.0075 | 3.3682 | 3.339 | 1.0708 | 10.7787 | 14.2348 | 14.8433 | 11.0912 | 0.0003 | -0.0022 | 0.001 | 0.0039 | 0.0009 | -0.0004 | -0.0039 | -0.0162 | -0.0089 | -360.2111 | 17.411 | -360.4481 | 17.6553 | -360.7527 | 18.1153 | -360.8512 | 17.5958 | -352.7029 | 18.7189 | -352.6444 | 16.8074
12:31 | 4297 | 40.8324 | 201.9929 | 449.1885 | 455.9653 | -16.5695 | -41.1795 | 10.9925 | 7.5579 | 1.9145 | 0.2433 | 3.2739 | -1.1165 | 11.413 | 4.2549 | 0.614 | 0.6589 | 0.9649 | 0.74 | -129.6144 | -0.6664 | 5.3695 | 1.6619 | -3.2717 | -1.6365 | 4.4473 |  | 2.9876 | 0.2523 | 4.009 | 3.3685 | 3.3366 | 1.072 | 10.7383 | 14.2693 | 14.8539 | 11.0742 | -0.0006 | -0.003 | 0.0008 | 0.0035 | 0.0007 | 0 | 0.0064 | 0.0015 | -0.011 | -360.1373 | 17.3884 | -360.4389 | 17.682 | -360.8174 | 18.1255 | -360.7897 | 17.5691 | -352.5983 | 18.6922 | -352.6721 | 16.8381
12:31 | 4298 | 40.7816 | 201.9886 | 449.182 | 455.943 | -16.5904 | -41.1995 | 10.9143 | 7.6195 | 2.0019 | 0.3508 | 3.2138 | -1.098 | 11.3643 | 4.3079 | 0.6138 | 0.6625 | 0.962 | 0.7386 | -129.6201 | -0.7978 | 5.4085 | 1.6514 | -3.285 | -1.6167 | 4.4325 |  | 2.9224 | 0.1668 | 4.0108 | 3.3686 | 3.3352 | 1.073 | 10.7557 | 14.2287 | 14.8296 | 11.0919 | 0.0002 | -0.0029 | 0.0009 | 0.0039 | 0.0008 | -0.0005 | 0.0118 | -0.0129 | 0.0091 | -360.1835 | 17.3843 | -360.4081 | 17.6389 | -360.765 | 18.1296 | -360.8574 | 17.5999 | -352.6383 | 18.6737 | -352.586 | 16.8032
12:31 | 4299 | 40.8242 | 202.0035 | 449.1324 | 455.9551 | -16.5867 | -41.2229 | 10.8615 | 7.7049 | 1.9568 | 0.2909 | 3.1717 | -1.1794 | 11.3961 | 4.2035 | 0.6148 | 0.6599 | 0.9624 | 0.7412 | -129.5661 | -0.6777 | 5.454 | 1.5868 | -3.2487 | -1.6849 | 4.3416 |  | 2.9592 | 0.0737 | 4.0098 | 3.3641 | 3.3347 | 1.0717 | 10.7036 | 14.252 | 14.7844 | 11.0222 | 0.0001 | -0.003 | 0.0012 | 0.004 | 0.0008 | -0.0003 | 0.0285 | -0.0112 | 0.0067 | -360.1435 | 17.4069 | -360.4419 | 17.6615 | -360.7958 | 18.105 | -360.7773 | 17.5753 | -352.6044 | 18.7045 | -352.666 | 16.8238
12:31 | 4300 | 40.9231 | 202.0691 | 449.1924 | 455.9809 | -16.6074 | -41.1323 | 10.8997 | 7.774 | 2.0513 | 0.2803 | 3.2229 | -1.1375 | 11.5276 | 4.3563 | 0.6139 | 0.6608 | 0.9603 | 0.7408 | -129.5478 | -0.7847 | 5.4583 | 1.6336 | -3.2084 | -1.5956 | 4.3967 |  | 3.0465 | 0.0372 | 4.0092 | 3.3654 | 3.3374 | 1.0705 | 10.7152 | 14.2289 | 14.8365 | 11.0627 | -0.0004 | -0.003 | 0.0005 | 0.0035 | 0.001 | -0.0006 | 0.0127 | -0.0059 | -0.0163 | -360.0973 | 17.372 | -360.4266 | 17.6533 | -360.7927 | 18.1379 | -360.845 | 17.5937 | -352.5736 | 18.6635 | -352.586 | 16.8115
12:31 | 4301 | 40.8833 | 202.0971 | 449.2081 | 455.987 | -16.5678 | -41.2769 | 10.9286 | 7.7245 | 2.0092 | 0.3459 | 3.3 | -1.0909 | 11.4486 | 4.3046 | 0.6146 | 0.6633 | 0.9614 | 0.7405 | -129.5791 | -0.7932 | 5.5259 | 1.533 | -3.1256 | -1.6094 | 4.3952 |  | 3.0633 | 0.1497 | 4.0101 | 3.3657 | 3.3379 | 1.0708 | 10.7533 | 14.2555 | 14.8522 | 11.0659 | -0.0004 | -0.0027 | 0.0008 | 0.0039 | 0.0005 | -0.0004 | 0.0184 | -0.0222 | 0.0058 | -360.1373 | 17.4028 | -360.4358 | 17.6512 | -360.7866 | 18.1029 | -360.802 | 17.5978 | -352.6567 | 18.6963 | -352.629 | 16.793
12:31 | 4302 | 40.8165 | 202.0256 | 449.3543 | 455.9169 | -16.5158 | -41.2718 | 10.9587 | 7.7499 | 2.0514 | 0.3418 | 3.2916 | -1.0697 | 11.4216 | 4.3676 | 0.6158 | 0.6602 | 0.9606 | 0.7408 | -129.5452 | -0.7327 | 5.5346 | 1.6386 | -3.1826 | -1.5555 | 4.3604 |  | 2.9835 | 0.0449 | 4.0094 | 3.3625 | 3.3352 | 1.0726 | 10.744 | 14.2638 | 14.8676 | 11.0966 | -0.0002 | -0.0032 | 0.0009 | 0.0045 | 0.0008 | -0.0007 | 0.012 | -0.0075 | -0.01 | -360.1558 | 17.4028 | -360.4573 | 17.682 | -360.8358 | 18.1522 | -360.8266 | 17.5814 | -352.5921 | 18.6943 | -352.666 | 16.834
12:31 | 4303 | 40.8702 | 202.068 | 449.292 | 456.0293 | -16.5927 | -41.2229 | 10.8906 | 7.689 | 1.9401 | 0.2589 | 3.2488 | -0.9756 | 11.4653 | 4.3927 | 0.6156 | 0.6602 | 0.9652 | 0.7389 | -129.5714 | -0.6988 | 5.4123 | 1.6579 | -3.2475 | -1.5942 | 4.3777 |  | 2.9564 | 0.0959 | 4.0096 | 3.3657 | 3.3362 | 1.0733 | 10.7509 | 14.2767 | 14.8989 | 11.1031 | 0.0004 | -0.0029 | 0.0003 | 0.0038 | 0.0005 | -0.0002 | -0.0007 | -0.01 | -0.0173 | -360.1835 | 17.409 | -360.445 | 17.6553 | -360.7927 | 18.1399 | -360.8543 | 17.6225 | -352.6475 | 18.7025 | -352.6444 | 16.7991
12:31 | 4304 | 40.8789 | 202.0546 | 449.2809 | 455.9601 | -16.6515 | -41.3373 | 10.9401 | 7.6728 | 2.0423 | 0.2308 | 3.2089 | -1.0729 | 11.3965 | 4.2682 | 0.6154 | 0.657 | 0.9636 | 0.7403 | -129.5152 | -0.7918 | 5.4098 | 1.4952 | -3.0801 | -1.661 | 4.3557 |  | 2.9711 | 0.1225 | 4.009 | 3.3685 | 3.3339 | 1.0714 | 10.7279 | 14.2646 | 14.8542 | 11.0757 | -0.0004 | -0.0035 | 0.0006 | 0.0041 | 0.0005 | -0.0004 | 0.0123 | 0.0011 | 0.01 | -360.2142 | 17.4254 | -360.5035 | 17.6882 | -360.8327 | 18.1358 | -360.8327 | 17.6102 | -352.6444 | 18.7169 | -352.6906 | 16.8279
12:31 | 4305 | 40.836 | 202.1468 | 449.2226 | 455.978 | -16.4344 | -41.1043 | 11.1528 | 7.6039 | 2.0435 | 0.2012 | 3.2262 | -1.1281 | 11.3765 | 4.1027 | 0.6162 | 0.6631 | 0.963 | 0.7391 | -129.5781 | -0.7574 | 5.4634 | 1.5993 | -3.1114 | -1.7039 | 4.3655 |  | 2.9285 | 0.1279 | 4.0086 | 3.3654 | 3.3398 | 1.0728 | 10.7393 | 14.271 | 14.8295 | 11.0684 | -0.0001 | -0.0026 | 0.0014 | 0.004 | 0.0012 | 0 | 0.0049 | -0.0071 | 0.0182 | -360.2296 | 17.4131 | -360.4542 | 17.68 | -360.8635 | 18.1584 | -360.8543 | 17.6204 | -352.669 | 18.7004 | -352.6813 | 16.8299
12:31 | 4306 | 40.8842 | 202.0055 | 449.1517 | 455.9929 | -16.3877 | -41.1225 | 11.1275 | 7.6168 | 1.9655 | 0.1515 | 3.1473 | -1.1144 | 11.4396 | 4.2447 | 0.6151 | 0.6606 | 0.9671 | 0.7401 | -129.6166 | -0.8511 | 5.3564 | 1.496 | -3.2353 | -1.653 | 4.3449 |  | 2.9099 | 0.1122 | 4.0094 | 3.3687 | 3.3358 | 1.0723 | 10.7522 | 14.2544 | 14.874 | 11.0995 | -0.0002 | -0.0033 | 0.0008 | 0.0036 | 0.0006 | -0.0005 | 0.0177 | -0.0088 | -0.0029 | -360.2358 | 17.4315 | -360.4819 | 17.6779 | -360.8204 | 18.1502 | -360.8789 | 17.6286 | -352.6937 | 18.7271 | -352.6813 | 16.832
12:31 | 4307 | 40.8611 | 201.9734 | 449.1391 | 455.9261 | -16.4706 | -41.0918 | 11.035 | 7.6984 | 1.9986 | 0.1838 | 3.209 | -1.1265 | 11.5083 | 4.2999 | 0.6154 | 0.656 | 0.9602 | 0.7391 | -129.5726 | -0.7748 | 5.3746 | 1.4826 | -3.2705 | -1.5791 | 4.3865 |  | 3.0303 | 0.0836 | 4.0104 | 3.3642 | 3.3376 | 1.0707 | 10.736 | 14.2034 | 14.8337 | 11.0548 | 0.0003 | -0.0031 | 0.0012 | 0.0047 | 0.0011 | -0.0002 | 0.0066 | -0.0029 | -0.009 | -360.1435 | 17.4131 | -360.4758 | 17.6861 | -360.8235 | 18.1399 | -360.8481 | 17.5958 | -352.6383 | 18.7128 | -352.6813 | 16.8402
12:32 | 4308 | 40.8744 | 201.888 | 449.2122 | 455.9456 | -16.449 | -41.0926 | 11.0111 | 7.6912 | 1.9609 | 0.3185 | 3.241 | -1.0748 | 11.4783 | 4.3536 | 0.6135 | 0.658 | 0.962 | 0.7401 | -129.6457 | -0.7182 | 5.3537 | 1.5292 | -3.1847 | -1.5474 | 4.4064 |  | 2.9718 | 0.2059 | 4.0087 | 3.3632 | 3.3389 | 1.0725 | 10.7451 | 14.2708 | 14.8689 | 11.0746 | -0.0001 | -0.0028 | 0.0004 | 0.004 | 0.0005 | -0.0003 | 0.0071 | -0.0125 | -0.0174 | -360.1865 | 17.4069 | -360.4358 | 17.6718 | -360.8327 | 18.1481 | -360.885 | 17.6122 | -352.6813 | 18.7087 | -352.666 | 16.8279
12:32 | 4309 | 40.8875 | 201.934 | 449.0871 | 455.9486 | -16.4977 | -41.119 | 10.9215 | 7.7231 | 1.9683 | 0.3191 | 3.2516 | -1.1325 | 11.4917 | 4.2752 | 0.6155 | 0.6596 | 0.9641 | 0.7389 | -129.5952 | -0.7477 | 5.3485 | 1.5146 | -3.2557 | -1.6265 | 4.3522 |  | 2.9709 | 0.3143 | 4.0085 | 3.3684 | 3.3383 | 1.0725 | 10.7349 | 14.2541 | 14.8255 | 11.0887 | -0.0003 | -0.0023 | 0.0006 | 0.004 | 0.0006 | -0.0007 | 0.0056 | -0.0113 | -0.0216 | -360.1404 | 17.3987 | -360.4512 | 17.6656 | -360.7804 | 18.1317 | -360.8327 | 17.5896 | -352.6198 | 18.6943 | -352.6598 | 16.8156
12:32 | 4310 | 40.7663 | 201.9618 | 449.1499 | 455.8739 | -16.5974 | -41.1188 | 10.97 | 7.5737 | 1.9554 | 0.2235 | 3.2213 | -1.1409 | 11.5336 | 4.3039 | 0.6138 | 0.6555 | 0.9603 | 0.7398 | -129.4949 | -0.6365 | 5.4389 | 1.6866 | -3.2876 | -1.5834 | 4.3535 |  | 2.9672 | 0.1787 | 4.0098 | 3.3641 | 3.3409 | 1.0719 | 10.7485 | 14.2861 | 14.8567 | 11.1121 | 0.0003 | -0.0023 | 0.0007 | 0.0039 | 0.0008 | -0.0002 | 0.0043 | -0.0019 | -0.0099 | -360.1404 | 17.3864 | -360.4296 | 17.6574 | -360.8112 | 18.1296 | -360.8327 | 17.5814 | -352.6044 | 18.682 | -352.6352 | 16.8217
12:32 | 4311 | 40.8797 | 202.0787 | 449.2975 | 456.0549 | -16.5708 | -41.2089 | 10.8005 | 7.6767 | 2.0481 | 0.2518 | 3.2573 | -1.1101 | 11.4521 | 4.3157 | 0.6151 | 0.656 | 0.9608 | 0.7387 | -129.5262 | -0.6836 | 5.5068 | 1.8022 | -3.1731 | -1.5609 | 4.3374 |  | 2.9533 | 0.1604 | 4.0087 | 3.3642 | 3.3392 | 1.0719 | 10.7683 | 14.2824 | 14.8631 | 11.0919 | 0.0001 | -0.0032 | 0.0005 | 0.0032 | 0.001 | -0.0006 | 0.0112 | -0.0184 | -0.0056 | -360.1435 | 17.3823 | -360.4173 | 17.6512 | -360.7743 | 18.1296 | -360.8327 | 17.5794 | -352.5829 | 18.6799 | -352.6044 | 16.8115
12:32 | 4312 | 40.8871 | 202.0999 | 449.314 | 456.0454 | -16.545 | -41.2098 | 10.86 | 7.6775 | 2.1347 | 0.2716 | 3.2615 | -1.1701 | 11.4171 | 4.281 | 0.6146 | 0.6566 | 0.9618 | 0.7404 | -129.5582 | -0.8224 | 5.4607 | 1.7063 | -3.1751 | -1.5422 | 4.3848 |  | 2.9834 | 0.1294 | 4.0106 | 3.3682 | 3.3409 | 1.0719 | 10.7452 | 14.2707 | 14.8737 | 11.0807 | -0.0001 | -0.003 | 0.001 | 0.0037 | 0.0008 | 0.0002 | -0.0021 | -0.0077 | -0.0156 | -360.1096 | 17.3925 | -360.4481 | 17.6594 | -360.762 | 18.1173 | -360.7989 | 17.5773 | -352.6106 | 18.6943 | -352.6352 | 16.8032
12:32 | 4313 | 40.8217 | 201.9707 | 449.3222 | 455.9362 | -16.5729 | -41.2144 | 10.8873 | 7.655 | 2.0624 | 0.2842 | 3.2075 | -1.1126 | 11.3472 | 4.1878 | 0.6158 | 0.661 | 0.9602 | 0.7388 | -129.5664 | -0.8106 | 5.3985 | 1.7111 | -3.1608 | -1.5374 | 4.4295 |  | 2.9757 | 0.1254 | 4.0114 | 3.3663 | 3.3385 | 1.0742 | 10.7613 | 14.2696 | 14.8502 | 11.085 | 0.0003 | -0.0023 | 0.0012 | 0.004 | 0.0006 | -0.0009 | -0.0022 | -0.0113 | -0.0167 | -360.1804 | 17.3966 | -360.4327 | 17.6697 | -360.8266 | 18.1317 | -360.8389 | 17.5958 | -352.589 | 18.684 | -352.629 | 16.8115
12:32 | 4314 | 40.8685 | 201.958 | 449.3194 | 456.0104 | -16.5613 | -41.167 | 10.8443 | 7.6768 | 2.0743 | 0.4172 | 3.2905 | -1.1579 | 11.3712 | 4.2702 | 0.6163 | 0.6626 | 0.9636 | 0.7398 | -129.6043 | -0.7534 | 5.4364 | 1.79 | -3.1627 | -1.466 | 4.3381 |  | 2.9694 | 0.0493 | 4.0101 | 3.363 | 3.3382 | 1.0719 | 10.7487 | 14.2799 | 14.8767 | 11.0843 | -0.0005 | -0.0026 | 0.0006 | 0.0036 | -0.0001 | -0.0006 | 0.0265 | 0.0071 | -0.0153 | -360.2142 | 17.409 | -360.4573 | 17.6636 | -360.7773 | 18.1317 | -360.8358 | 17.604 | -352.6352 | 18.7004 | -352.6383 | 16.7991
12:32 | 4315 | 40.8482 | 201.9687 | 449.169 | 455.9542 | -16.4695 | -41.187 | 10.8465 | 7.7131 | 2.0604 | 0.3255 | 3.3013 | -1.0702 | 11.4394 | 4.2874 | 0.616 | 0.6573 | 0.9626 | 0.7402 | -129.5876 | -0.7278 | 5.3275 | 1.6693 | -3.1082 | -1.4798 | 4.4173 |  | 2.9746 | 0.1214 | 4.0089 | 3.3634 | 3.3378 | 1.0721 | 10.7093 | 14.2348 | 14.826 | 11.0854 | 0.0003 | -0.0029 | 0.0008 | 0.0042 | 0.0009 | -0.0006 | 0.0338 | 0.0001 | -0.0178 | -360.2019 | 17.4254 | -360.5158 | 17.7005 | -360.8666 | 18.1481 | -360.8481 | 17.5978 | -352.6444 | 18.7107 | -352.6937 | 16.8381
12:32 | 4316 | 40.988 | 201.9814 | 449.2111 | 456.0403 | -16.5664 | -41.2227 | 10.8071 | 7.7295 | 1.9904 | 0.2467 | 3.2915 | -1.1383 | 11.3822 | 4.2467 | 0.616 | 0.6594 | 0.964 | 0.7397 | -129.5109 | -0.7073 | 5.5132 | 1.7243 | -3.0981 | -1.5298 | 4.4361 |  | 2.9994 | 0.0933 | 4.0094 | 3.3674 | 3.3418 | 1.0732 | 10.7463 | 14.2776 | 14.8924 | 11.0934 | -0.0001 | -0.0032 | 0.0004 | 0.0038 | 0.0007 | -0.0008 | 0.0035 | -0.0083 | 0.0103 | -360.1835 | 17.3966 | -360.4358 | 17.6779 | -360.845 | 18.1645 | -360.9004 | 17.6184 | -352.6475 | 18.6902 | -352.6537 | 16.834
12:32 | 4317 | 40.9419 | 201.9742 | 449.2701 | 455.9725 | -16.4753 | -41.197 | 10.8795 | 7.7359 | 1.9596 | 0.3554 | 3.3544 | -1.0488 | 11.4516 | 4.3217 | 0.6146 | 0.6596 | 0.965 | 0.7385 | -129.5369 | -0.7242 | 5.4587 | 1.7246 | -3.0501 | -1.4553 | 4.4897 |  | 2.9423 | 0.0324 | 4.0094 | 3.3669 | 3.3396 | 1.0722 | 10.7695 | 14.237 | 14.874 | 11.0764 | 0 | -0.0024 | 0.0006 | 0.004 | 0.0005 | -0.0006 | 0.0272 | 0.0096 | -0.0042 | -360.2358 | 17.4459 | -360.4942 | 17.6697 | -360.8235 | 18.1337 | -360.8635 | 17.6184 | -352.7029 | 18.7415 | -352.7029 | 16.834
12:32 | 4318 | 40.904 | 201.9778 | 449.3184 | 456.042 | -16.4655 | -41.0864 | 10.8509 | 7.7713 | 2.0068 | 0.3629 | 3.3894 | -1.1471 | 11.4083 | 4.2603 | 0.6145 | 0.6586 | 0.9619 | 0.7389 | -129.5711 | -0.6689 | 5.4715 | 1.7262 | -3.0866 | -1.5187 | 4.4654 |  | 2.983 | 0.0225 | 4.0081 | 3.363 | 3.3377 | 1.0705 | 10.7336 | 14.2475 | 14.8621 | 11.0865 | -0.0002 | -0.0027 | 0.0009 | 0.0042 | 0.001 | -0.0009 | 0.0124 | 0.0001 | -0.0005 | -360.1496 | 17.4007 | -360.4758 | 17.682 | -360.845 | 18.1584 | -360.8604 | 17.5958 | -352.6167 | 18.6902 | -352.666 | 16.8484
12:32 | 4319 | 40.8949 | 202.0033 | 449.4535 | 456.069 | -16.4752 | -41.1698 | 10.823 | 7.7698 | 1.9298 | 0.3499 | 3.2521 | -1.0357 | 11.487 | 4.3313 | 0.6154 | 0.6563 | 0.9609 | 0.7399 | -129.5978 | -0.7443 | 5.4486 | 1.7174 | -3.1662 | -1.5634 | 4.4261 |  | 2.979 | 0.015 | 4.0098 | 3.3636 | 3.3427 | 1.0721 | 10.7568 | 14.2822 | 14.8679 | 11.0865 | 0.0002 | -0.003 | 0.0007 | 0.0042 | 0.0004 | -0.0003 | 0.0025 | -0.0129 | -0.003 | -360.245 | 17.409 | -360.4358 | 17.6348 | -360.805 | 18.1481 | -360.8697 | 17.6369 | -352.6721 | 18.7004 | -352.669 | 16.8176
12:32 | 4320 | 40.9164 | 201.9243 | 449.3214 | 456.0681 | -16.4656 | -41.2153 | 10.8957 | 7.7798 | 2.0021 | 0.2685 | 3.2015 | -1.0679 | 11.4299 | 4.3021 | 0.6155 | 0.6577 | 0.9641 | 0.7396 | -129.5879 | -0.6459 | 5.5279 | 1.7037 | -3.1761 | -1.3863 | 4.4782 |  | 2.9757 | 0.0783 | 4.0097 | 3.3648 | 3.3392 | 1.0728 | 10.7302 | 14.2787 | 14.8638 | 11.0717 | 0.0001 | -0.0035 | 0.0011 | 0.004 | 0.0007 | -0.0007 | 0.0182 | -0.0137 | 0.0047 | -360.2081 | 17.4233 | -360.4973 | 17.6718 | -360.8266 | 18.1276 | -360.7989 | 17.5773 | -352.6783 | 18.7189 | -352.6937 | 16.8505
12:32 | 4321 | 40.9102 | 202.0217 | 449.3895 | 456.0259 | -16.442 | -41.1616 | 10.9383 | 7.8 | 2.0807 | 0.4106 | 3.218 | -0.8959 | 11.4081 | 4.3107 | 0.6157 | 0.6596 | 0.9627 | 0.7401 | -129.6265 | -0.7145 | 5.4746 | 1.5893 | -3.2392 | -1.4482 | 4.3486 |  | 2.9534 | 0.1027 | 4.0085 | 3.3634 | 3.3382 | 1.0717 | 10.7314 | 14.2564 | 14.8341 | 11.114 | -0.0004 | -0.0029 | 0.0005 | 0.0036 | 0.0004 | -0.0004 | 0.0204 | -0.006 | -0.0085 | -360.1404 | 17.3699 | -360.4081 | 17.643 | -360.8112 | 18.1687 | -360.8635 | 17.5937 | -352.6383 | 18.6676 | -352.6444 | 16.8238
12:32 | 4322 | 40.9199 | 201.9216 | 449.3013 | 456.0353 | -16.4422 | -41.2159 | 10.9935 | 7.8185 | 2.0894 | 0.3103 | 3.2471 | -0.8565 | 11.4843 | 4.2846 | 0.6144 | 0.6571 | 0.9621 | 0.7399 | -129.6327 | -0.7496 | 5.4453 | 1.5162 | -3.3044 | -1.4979 | 4.4004 |  | 2.9386 | 0.0302 | 4.01 | 3.365 | 3.3412 | 1.0724 | 10.7348 | 14.2544 | 14.8682 | 11.0706 | -0.0002 | -0.0025 | 0.0009 | 0.0038 | 0.001 | -0.0005 | 0.0075 | 0.0007 | -0.0203 | -360.1681 | 17.4254 | -360.4635 | 17.6286 | -360.762 | 18.1112 | -360.8235 | 17.5978 | -352.6567 | 18.7128 | -352.6875 | 16.8176
12:32 | 4323 | 40.8399 | 201.9128 | 449.3261 | 456.0583 | -16.5004 | -41.2458 | 10.9459 | 7.8027 | 2.1089 | 0.4596 | 3.2318 | -0.9966 | 11.4141 | 4.2106 | 0.6149 | 0.6542 | 0.9621 | 0.7403 | -129.6163 | -0.7816 | 5.3654 | 1.4932 | -3.1545 | -1.5599 | 4.4565 |  | 3.0444 | 0.0512 | 4.0104 | 3.3662 | 3.3401 | 1.0719 | 10.7442 | 14.269 | 14.8344 | 11.0461 | -0.0004 | -0.0034 | 0.0009 | 0.0041 | 0.0006 | -0.0004 | -0.0062 | -0.0133 | -0.004 | -360.0942 | 17.372 | -360.445 | 17.6594 | -360.8266 | 18.142 | -360.7989 | 17.565 | -352.5736 | 18.6655 | -352.6383 | 16.8443
12:32 | 4324 | 40.9932 | 202.0486 | 449.3572 | 456.0292 | -16.5129 | -41.2134 | 10.9928 | 7.7841 | 2.1848 | 0.5346 | 3.2403 | -1.044 | 11.3788 | 4.0487 | 0.6157 | 0.6511 | 0.9631 | 0.74 | -129.6127 | -0.8981 | 5.3929 | 1.5037 | -3.2123 | -1.396 | 4.392 |  | 2.9811 | 0.0452 | 4.01 | 3.3658 | 3.3381 | 1.0728 | 10.7256 | 14.2622 | 14.8456 | 11.0793 | 0 | -0.0033 | 0.0006 | 0.0038 | 0.001 | -0.0009 | 0.0073 | -0.0084 | -0.0167 | -360.1219 | 17.3782 | -360.405 | 17.6081 | -360.7281 | 18.142 | -360.845 | 17.6143 | -352.6198 | 18.6614 | -352.5767 | 16.793
12:32 | 4325 | 41.0013 | 202.0544 | 449.3563 | 456.0027 | -16.5022 | -41.1231 | 11.0606 | 7.7823 | 2.1479 | 0.5473 | 3.2479 | -1.0638 | 11.4401 | 4.1252 | 0.6159 | 0.6519 | 0.9638 | 0.7399 | -129.5991 | -0.7516 | 5.3606 | 1.5879 | -3.1941 | -1.4406 | 4.3696 |  | 3.0055 | 0.062 | 4.0108 | 3.363 | 3.3383 | 1.0714 | 10.7578 | 14.2895 | 14.8656 | 11.1273 | -0.0001 | -0.0028 | 0.0008 | 0.0041 | 0.001 | 0.0001 | 0.0283 | 0.0005 | -0.0012 | -360.1835 | 17.4192 | -360.4696 | 17.6533 | -360.8235 | 18.1235 | -360.765 | 17.5712 | -352.6106 | 18.7148 | -352.6783 | 16.8279
12:32 | 4326 | 41.0769 | 202.1402 | 449.4764 | 456.1847 | -16.4672 | -41.0633 | 11.1999 | 7.7392 | 2.1884 | 0.7104 | 3.2419 | -0.9781 | 11.4486 | 4.2397 | 0.6159 | 0.6496 | 0.9629 | 0.7393 | -129.6478 | -0.7207 | 5.4415 | 1.5665 | -3.2129 | -1.4817 | 4.3408 |  | 3.0044 | 0.0672 | 4.0088 | 3.3647 | 3.3356 | 1.0724 | 10.7556 | 14.2579 | 14.8549 | 11.0681 | -0.0006 | -0.003 | 0.0007 | 0.004 | 0.0006 | -0.0008 | 0.0315 | -0.0057 | -0.0005 | -360.1711 | 17.3802 | -360.4604 | 17.6697 | -360.8574 | 18.181 | -360.882 | 17.5855 | -352.5921 | 18.6758 | -352.626 | 16.832
12:32 | 4327 | 41.0868 | 202.1318 | 449.4255 | 456.1254 | -16.4228 | -41.0593 | 11.0279 | 7.7784 | 2.2031 | 0.4942 | 3.1911 | -1.028 | 11.4491 | 4.2244 | 0.6173 | 0.6548 | 0.9614 | 0.7413 | -129.5652 | -0.6793 | 5.4804 | 1.4324 | -3.3119 | -1.4923 | 4.3214 |  | 3.0394 | 0.0643 | 4.0094 | 3.3631 | 3.3391 | 1.0712 | 10.7613 | 14.2929 | 14.857 | 11.102 | 0.0001 | -0.0026 | 0.0007 | 0.004 | 0.0009 | 0 | 0.0093 | -0.01 | 0.006 | -360.2512 | 17.4356 | -360.4604 | 17.6348 | -360.7958 | 18.1584 | -360.8789 | 17.6389 | -352.6937 | 18.7251 | -352.6721 | 16.7991
12:32 | 4328 | 41.028 | 202.031 | 449.3807 | 456.1959 | -16.4466 | -41.0216 | 11.0104 | 7.8143 | 2.1674 | 0.4526 | 3.1998 | -0.9781 | 11.4215 | 4.2305 | 0.6151 | 0.6557 | 0.9619 | 0.74 | -129.516 | -0.7876 | 5.5773 | 1.5219 | -3.2991 | -1.5097 | 4.3606 |  | 3.0629 | 0.0481 | 4.0098 | 3.3625 | 3.3361 | 1.0712 | 10.7809 | 14.2895 | 14.9119 | 11.1157 | -0.0002 | -0.0033 | 0.0014 | 0.0044 | 0.0008 | -0.0003 | 0.0119 | -0.0064 | -0.0161 | -360.1681 | 17.4356 | -360.5189 | 17.7005 | -360.8881 | 18.1584 | -360.8327 | 17.5794 | -352.6567 | 18.7189 | -352.6783 | 16.8628
12:32 | 4329 | 41.0287 | 202.0353 | 449.3872 | 456.1141 | -16.5441 | -41.0122 | 10.9286 | 7.7583 | 2.1074 | 0.4685 | 3.1334 | -1.0367 | 11.4448 | 4.1852 | 0.6165 | 0.6517 | 0.9622 | 0.7407 | -129.524 | -0.6367 | 5.4968 | 1.6468 | -3.3049 | -1.6554 | 4.334 |  | 2.9966 | 0.0015 | 4.0115 | 3.3653 | 3.3399 | 1.0732 | 10.7382 | 14.2753 | 14.8665 | 11.1085 | -0.0002 | -0.0029 | 0.0008 | 0.004 | 0.0004 | -0.0009 | 0.025 | -0.0121 | -0.0054 | -360.1435 | 17.3843 | -360.4296 | 17.6492 | -360.842 | 18.1892 | -360.9404 | 17.604 | -352.6598 | 18.6943 | -352.6413 | 16.834
12:32 | 4330 | 40.9662 | 202.0952 | 449.3921 | 456.0305 | -16.4473 | -40.9773 | 10.9652 | 7.7521 | 2.0891 | 0.4711 | 3.0955 | -1.037 | 11.4366 | 4.2286 | 0.6156 | 0.6522 | 0.9609 | 0.739 | -129.5755 | -0.5823 | 5.4344 | 1.6545 | -3.2928 | -1.6373 | 4.3197 |  | 2.9675 | 0.1015 | 4.0098 | 3.3642 | 3.3383 | 1.0725 | 10.7266 | 14.2351 | 14.8339 | 11.0847 | 0.0001 | -0.0026 | 0.0006 | 0.004 | 0.0008 | 0 | 0.0102 | -0.0176 | -0.0172 | -360.205 | 17.4356 | -360.4573 | 17.6451 | -360.8112 | 18.1235 | -360.8481 | 17.6204 | -352.6906 | 18.7271 | -352.6875 | 16.8258
12:32 | 4331 | 41.0251 | 202.1518 | 449.3533 | 456.1026 | -16.5349 | -41.0596 | 10.9576 | 7.7955 | 2.1495 | 0.4334 | 3.1391 | -1.0159 | 11.4329 | 4.202 | 0.6144 | 0.653 | 0.9612 | 0.7386 | -129.5253 | -0.7226 | 5.4185 | 1.6095 | -3.2421 | -1.6164 | 4.4409 |  | 2.9986 | 0.0066 | 4.0108 | 3.3642 | 3.3389 | 1.0727 | 10.7488 | 14.2217 | 14.8225 | 11.0678 | -0.0004 | -0.0027 | 0.0003 | 0.0041 | 0.001 | -0.0005 | 0.0061 | -0.0102 | -0.0057 | -360.0881 | 17.3905 | -360.4666 | 17.6718 | -360.8604 | 18.1584 | -360.8143 | 17.5629 | -352.6167 | 18.6861 | -352.6783 | 16.8607
12:32 | 4332 | 40.9704 | 202.0844 | 449.3547 | 456.0522 | -16.5119 | -41.0271 | 10.9786 | 7.8348 | 2.1291 | 0.4225 | 3.2326 | -1.072 | 11.4367 | 4.2411 | 0.6142 | 0.6497 | 0.9615 | 0.7393 | -129.4925 | -0.7067 | 5.4534 | 1.6354 | -3.2277 | -1.6208 | 4.363 |  | 3.0275 | 0.0431 | 4.0104 | 3.3627 | 3.3421 | 1.0719 | 10.7106 | 14.253 | 14.8194 | 11.0815 | 0.0007 | -0.003 | 0.0001 | 0.0034 | 0.0005 | -0.0003 | 0.0021 | -0.0108 | -0.0131 | -360.165 | 17.3823 | -360.3773 | 17.6122 | -360.7558 | 18.1502 | -360.8758 | 17.6102 | -352.6537 | 18.6717 | -352.5952 | 16.7889
12:32 | 4333 | 40.969 | 202.0904 | 449.264 | 456.0636 | -16.5404 | -41.0716 | 10.9066 | 7.6601 | 2.149 | 0.3904 | 3.1638 | -1.0386 | 11.4947 | 4.2535 | 0.6158 | 0.6508 | 0.9629 | 0.7408 | -129.5733 | -0.6221 | 5.5018 | 1.584 | -3.321 | -1.6395 | 4.3467 |  | 2.9793 | 0.0311 | 4.011 | 3.3635 | 3.339 | 1.0733 | 10.7243 | 14.2499 | 14.8417 | 11.0655 | -0.0002 | -0.003 | 0.0008 | 0.0042 | 0.0014 | -0.0005 | 0.0121 | -0.0091 | -0.0113 | -360.1927 | 17.4213 | -360.4696 | 17.641 | -360.7897 | 18.1091 | -360.7712 | 17.5773 | -352.6321 | 18.7189 | -352.6783 | 16.834
12:32 | 4334 | 40.9597 | 202.1013 | 449.271 | 456.0848 | -16.5233 | -41.1292 | 10.921 | 7.6468 | 2.1628 | 0.3663 | 3.137 | -0.9406 | 11.4955 | 4.2879 | 0.6156 | 0.6519 | 0.9605 | 0.7387 | -129.5719 | -0.6577 | 5.4359 | 1.6555 | -3.2063 | -1.5631 | 4.4242 |  | 2.9984 | -0.0095 | 4.0112 | 3.365 | 3.3382 | 1.0727 | 10.7429 | 14.2741 | 14.8246 | 11.0901 | -0.0002 | -0.0024 | 0.001 | 0.0044 | 0.0006 | -0.0001 | 0.0156 | 0.0117 | -0.0005 | -360.0419 | 17.3699 | -360.3989 | 17.6451 | -360.845 | 18.1502 | -360.7866 | 17.565 | -352.5644 | 18.6594 | -352.6444 | 16.834
12:32 | 4335 | 40.9835 | 202.0445 | 449.1782 | 456.0454 | -16.5227 | -41.0813 | 10.9063 | 7.6768 | 2.1547 | 0.4216 | 3.1775 | -1.09 | 11.4746 | 4.2488 | 0.6155 | 0.6524 | 0.9612 | 0.7399 | -129.5423 | -0.6069 | 5.4091 | 1.648 | -3.2264 | -1.5871 | 4.3886 |  | 3.0411 | 0.0991 | 4.0114 | 3.3669 | 3.3385 | 1.0731 | 10.7451 | 14.265 | 14.8631 | 11.0803 | -0.0002 | -0.0028 | 0.0011 | 0.0034 | 0.001 | -0.0006 | 0.0106 | -0.0109 | 0.0081 | -360.205 | 17.4028 | -360.3989 | 17.5978 | -360.7127 | 18.142 | -360.845 | 17.6061 | -352.6506 | 18.6963 | -352.629 | 16.793
12:32 | 4336 | 40.9657 | 202.1033 | 449.4501 | 456.1303 | -16.3742 | -40.937 | 11.0864 | 7.7335 | 2.1269 | 0.4509 | 3.245 | -0.9234 | 11.5171 | 4.3098 | 0.6156 | 0.6548 | 0.9591 | 0.739 | -129.4704 | -0.5501 | 5.4523 | 1.4689 | -3.2268 | -1.6264 | 4.2929 |  | 2.8877 | 0.0143 | 4.0096 | 3.3645 | 3.3361 | 1.0727 | 10.7626 | 14.2821 | 14.8379 | 11.0927 | 0.0003 | -0.0026 | 0.0002 | 0.0032 | 0.0005 | -0.0002 | 0.012 | 0.0026 | -0.0031 | -360.1373 | 17.411 | -360.5004 | 17.6636 | -360.8081 | 18.1091 | -360.7773 | 17.5527 | -352.5952 | 18.7025 | -352.6967 | 16.8299
12:32 | 4337 | 41.0306 | 202.1832 | 449.5111 | 456.1661 | -16.3537 | -40.8818 | 11.03 | 7.7007 | 2.2018 | 0.4839 | 3.1774 | -0.9945 | 11.5428 | 4.2233 | 0.6145 | 0.652 | 0.9616 | 0.7388 | -129.5698 | -0.6146 | 5.382 | 1.4932 | -3.2333 | -1.777 | 4.2888 |  | 2.8717 | 0.0487 | 4.0111 | 3.3652 | 3.335 | 1.0735 | 10.751 | 14.2822 | 14.8679 | 11.1385 | 0.0002 | -0.003 | 0.0009 | 0.004 | 0.0007 | -0.0005 | 0.0116 | -0.0006 | -0.0078 | -360.1496 | 17.3864 | -360.4204 | 17.6389 | -360.8604 | 18.1687 | -360.885 | 17.5958 | -352.5983 | 18.682 | -352.6198 | 16.8135
12:32 | 4338 | 41.1138 | 202.1458 | 449.4384 | 456.1543 | -16.4583 | -41.0154 | 10.9687 | 7.7504 | 2.1423 | 0.4262 | 3.1357 | -1.0191 | 11.5996 | 4.2945 | 0.6153 | 0.6518 | 0.9622 | 0.7403 | -129.5676 | -0.6062 | 5.4782 | 1.4841 | -3.1934 | -1.6549 | 4.3062 |  | 2.9115 | 0.1379 | 4.0104 | 3.3657 | 3.3386 | 1.0747 | 10.7451 | 14.2882 | 14.8226 | 11.0977 | -0.0002 | -0.0026 | 0.0006 | 0.0035 | 0.0008 | -0.0003 | 0.013 | -0.0109 | -0.0138 | -360.2327 | 17.4356 | -360.4666 | 17.6389 | -360.7866 | 18.1337 | -360.845 | 17.6081 | -352.6598 | 18.7333 | -352.6875 | 16.8032
12:32 | 4339 | 41.1164 | 202.1466 | 449.402 | 456.1782 | -16.4295 | -40.9446 | 10.9467 | 7.6863 | 2.0945 | 0.4297 | 3.1561 | -0.9218 | 11.5516 | 4.2255 | 0.6138 | 0.6509 | 0.9615 | 0.7392 | -129.5709 | -0.5506 | 5.5195 | 1.5532 | -3.1101 | -1.6718 | 4.3063 |  | 2.9741 | 0.1517 | 4.0097 | 3.3652 | 3.3358 | 1.0722 | 10.751 | 14.2591 | 14.8679 | 11.0865 | 0.0003 | -0.0022 | 0.0002 | 0.0037 | 0.0006 | -0.0006 | 0.008 | -0.0024 | -0.0084 | -360.1804 | 17.4151 | -360.5373 | 17.6841 | -360.8943 | 18.1625 | -360.8266 | 17.5773 | -352.6198 | 18.7271 | -352.7152 | 16.8689
12:32 | 4340 | 41.0879 | 202.2066 | 449.455 | 456.2621 | -16.3596 | -40.9218 | 10.9709 | 7.7327 | 2.1475 | 0.4655 | 3.1884 | -0.9942 | 11.4813 | 4.1833 | 0.6145 | 0.6482 | 0.9589 | 0.7414 | -129.5871 | -0.5591 | 5.5477 | 1.432 | -3.1466 | -1.6681 | 4.3263 |  | 3.0331 | 0.1103 | 4.011 | 3.365 | 3.3402 | 1.0729 | 10.7417 | 14.2729 | 14.8174 | 11.0601 | 0.0001 | -0.0031 | 0.0011 | 0.0041 | 0.001 | -0.0004 | -0.0011 | 0.0092 | -0.0147 | -360.1958 | 17.3884 | -360.4235 | 17.6471 | -360.8297 | 18.1789 | -360.8697 | 17.6122 | -352.6629 | 18.6984 | -352.6352 | 16.8238
12:32 | 4341 | 41.0846 | 202.1404 | 449.3503 | 456.1111 | -16.4345 | -40.9521 | 10.9299 | 7.6848 | 2.0566 | 0.323 | 3.0607 | -0.9503 | 11.542 | 4.2781 | 0.6156 | 0.6554 | 0.963 | 0.7407 | -129.6163 | -0.6024 | 5.4862 | 1.5551 | -3.2355 | -1.5995 | 4.2959 |  | 2.9422 | 0.1076 | 4.0103 | 3.3614 | 3.3346 | 1.0725 | 10.7636 | 14.2604 | 14.8529 | 11.0814 | 0.0004 | -0.0029 | 0.0009 | 0.0037 | 0.0006 | -0.0006 | 0.0088 | 0.0017 | -0.0228 | -360.2327 | 17.448 | -360.4881 | 17.6677 | -360.8389 | 18.1399 | -360.8358 | 17.6102 | -352.7121 | 18.7559 | -352.7306 | 16.8505
12:32 | 4342 | 41.1123 | 202.196 | 449.4384 | 456.1359 | -16.3511 | -40.9163 | 10.9266 | 7.8489 | 2.1122 | 0.3381 | 3.1615 | -0.9423 | 11.5727 | 4.2531 | 0.615 | 0.6515 | 0.9611 | 0.742 | -129.6854 | -0.6806 | 5.4692 | 1.6489 | -3.1756 | -1.5075 | 4.3343 |  | 2.8503 | 0.0258 | 4.0081 | 3.3626 | 3.337 | 1.0724 | 10.75 | 14.2517 | 14.8402 | 11.0808 | -0.0007 | -0.003 | 0.0006 | 0.0038 | 0.001 | -0.0008 | 0.0258 | -0.0111 | 0.0067 | -360.1773 | 17.4069 | -360.485 | 17.6779 | -360.8358 | 18.1769 | -360.8512 | 17.5773 | -352.6383 | 18.7189 | -352.6813 | 16.871
12:32 | 4343 | 41.1452 | 202.1688 | 449.3799 | 456.1914 | -16.3879 | -40.9111 | 10.9533 | 7.6969 | 2.0501 | 0.225 | 3.0626 | -0.9495 | 11.4894 | 4.2492 | 0.6134 | 0.6511 | 0.9617 | 0.7411 | -129.6375 | -0.7431 | 5.4581 | 1.664 | -3.14 | -1.5004 | 4.353 |  | 2.8732 | 0.0032 | 4.0099 | 3.363 | 3.3344 | 1.072 | 10.7751 | 14.2954 | 14.8666 | 11.098 | -0.0004 | -0.0024 | 0.001 | 0.0038 | 0.0008 | -0.0004 | 0.0081 | -0.004 | 0.0031 | -360.1927 | 17.409 | -360.4481 | 17.6574 | -360.7835 | 18.1707 | -360.9189 | 17.6286 | -352.6752 | 18.7148 | -352.6475 | 16.8402
12:32 | 4344 | 41.0748 | 202.1788 | 449.4398 | 456.2119 | -16.4106 | -40.8774 | 10.9882 | 7.7299 | 2.0335 | 0.3038 | 3.1308 | -0.9132 | 11.4839 | 4.2228 | 0.6144 | 0.6525 | 0.9604 | 0.7416 | -129.5631 | -0.6728 | 5.4874 | 1.5041 | -3.141 | -1.5957 | 4.28 |  | 2.9218 | 0.0752 | 4.0105 | 3.3673 | 3.3406 | 1.0726 | 10.7533 | 14.2671 | 14.8869 | 11.0948 | 0.0002 | -0.0032 | 0.0005 | 0.0038 | 0.0008 | -0.0007 | 0.0078 | -0.0066 | -0.0122 | -360.1896 | 17.4254 | -360.5035 | 17.6779 | -360.8389 | 18.142 | -360.8297 | 17.5855 | -352.6752 | 18.7312 | -352.7275 | 16.8628
12:32 | 4345 | 41.0896 | 202.2209 | 449.3845 | 456.2875 | -16.3986 | -40.8794 | 10.9589 | 7.6605 | 2.0312 | 0.2461 | 3.1223 | -1.0767 | 11.4811 | 4.2104 | 0.6149 | 0.6539 | 0.9642 | 0.7383 | -129.5797 | -0.6885 | 5.402 | 1.5238 | -3.1461 | -1.5225 | 4.3438 |  | 2.9621 | 0.049 | 4.0105 | 3.3687 | 3.3349 | 1.0712 | 10.7579 | 14.2776 | 14.8634 | 11.076 | 0 | -0.0032 | 0.0009 | 0.0036 | 0.0005 | -0.0002 | -0.0008 | -0.0128 | -0.0132 | -360.1496 | 17.3843 | -360.4666 | 17.6471 | -360.8327 | 18.1851 | -360.9004 | 17.6122 | -352.6567 | 18.6922 | -352.6629 | 16.8464
12:32 | 4346 | 41.0757 | 202.2058 | 449.4683 | 456.1681 | -16.3092 | -40.8883 | 10.9477 | 7.7422 | 2.0647 | 0.2658 | 3.1617 | -1.0896 | 11.5279 | 4.3137 | 0.6169 | 0.6538 | 0.9622 | 0.7407 | -129.5932 | -0.6897 | 5.445 | 1.5536 | -3.1657 | -1.4842 | 4.3143 |  | 2.9997 | 0.1036 | 4.01 | 3.3664 | 3.3384 | 1.0726 | 10.7474 | 14.2732 | 14.8659 | 11.0825 | 0 | -0.0029 | 0.0011 | 0.0038 | 0.0008 | -0.0006 | 0.0001 | -0.0032 | -0.0205 | -360.1896 | 17.411 | -360.4819 | 17.6574 | -360.805 | 18.1337 | -360.8358 | 17.5958 | -352.6752 | 18.7271 | -352.6721 | 16.8464
12:32 | 4347 | 41.1012 | 202.1502 | 449.4974 | 456.1654 | -16.3623 | -40.9146 | 10.9676 | 7.6477 | 2.0799 | 0.3214 | 3.0932 | -1.1078 | 11.554 | 4.2021 | 0.6156 | 0.6566 | 0.9657 | 0.7394 | -129.627 | -0.6022 | 5.4115 | 1.6247 | -3.06 | -1.4556 | 4.4307 |  | 2.9622 | 0.0751 | 4.0089 | 3.3675 | 3.3342 | 1.0722 | 10.7672 | 14.2753 | 14.8433 | 11.0508 | -0.0007 | -0.0029 | 0.0007 | 0.0039 | 0.0006 | 0 | 0.0049 | 0.0041 | -0.0364 | -360.1588 | 17.3925 | -360.4542 | 17.6656 | -360.845 | 18.1728 | -360.8789 | 17.5753 | -352.6413 | 18.7004 | -352.6383 | 16.8669
12:32 | 4348 | 41.1972 | 202.2137 | 449.5223 | 456.2207 | -16.3388 | -40.8468 | 11.0754 | 7.7587 | 2.0727 | 0.2564 | 3.1562 | -1.0899 | 11.5284 | 4.3078 | 0.6169 | 0.6573 | 0.965 | 0.7398 | -129.5632 | -0.5844 | 5.4482 | 1.5724 | -3.077 | -1.502 | 4.3876 |  | 2.9721 | 0.0803 | 4.0107 | 3.3663 | 3.3374 | 1.074 | 10.7487 | 14.2567 | 14.8593 | 11.0612 | 0 | -0.003 | 0.0012 | 0.0042 | 0.0007 | -0.0009 | 0.0103 | -0.0185 | -0.0007 | -360.1681 | 17.4048 | -360.4327 | 17.6348 | -360.7835 | 18.144 | -360.8389 | 17.5937 | -352.6413 | 18.7025 | -352.6537 | 16.8381
12:32 | 4349 | 41.1629 | 202.2698 | 449.5125 | 456.2162 | -16.3726 | -40.7343 | 11.1424 | 7.8309 | 2.0974 | 0.4057 | 3.193 | -1.094 | 11.598 | 4.3927 | 0.618 | 0.6582 | 0.9634 | 0.7405 | -129.5598 | -0.5974 | 5.3732 | 1.4761 | -3.0519 | -1.5497 | 4.4095 |  | 2.9526 | 0.1441 | 4.0083 | 3.3634 | 3.3328 | 1.0732 | 10.7798 | 14.2708 | 14.8747 | 11.0861 | 0.0002 | -0.0031 | 0.0009 | 0.0042 | 0.0005 | -0.0005 | 0.0232 | -0.013 | 0.0137 | -360.1342 | 17.3966 | -360.445 | 17.6512 | -360.8266 | 18.1358 | -360.8235 | 17.5835 | -352.6013 | 18.7004 | -352.6383 | 16.8566
12:32 | 4350 | 41.1363 | 202.1855 | 449.4193 | 456.2177 | -16.3065 | -40.8526 | 11.1938 | 7.9039 | 2.1259 | 0.4371 | 3.2701 | -1.0557 | 11.4772 | 4.3513 | 0.6145 | 0.6557 | 0.9623 | 0.741 | -129.6311 | -0.6315 | 5.4889 | 1.4993 | -3.0426 | -1.5266 | 4.3216 |  | 2.9851 | 0.1272 | 4.0091 | 3.3694 | 3.3377 | 1.0714 | 10.7659 | 14.2859 | 14.8846 | 11.0778 | -0.0001 | -0.0027 | 0.0011 | 0.0042 | 0.0009 | -0.0004 | 0.0209 | -0.0088 | -0.002 | -360.0973 | 17.3843 | -360.4358 | 17.6369 | -360.7927 | 18.144 | -360.8204 | 17.5732 | -352.6075 | 18.6922 | -352.629 | 16.8361
12:32 | 4351 | 41.1229 | 202.1088 | 449.4484 | 456.1913 | -16.3526 | -40.8832 | 11.1408 | 7.7485 | 1.9507 | 0.2684 | 3.1606 | -0.9831 | 11.5659 | 4.3146 | 0.6146 | 0.6535 | 0.9628 | 0.7396 | -129.5864 | -0.6137 | 5.533 | 1.4022 | -3.0609 | -1.5025 | 4.3726 |  | 2.9643 | 0.1306 | 4.0094 | 3.3649 | 3.3361 | 1.0737 | 10.7878 | 14.2736 | 14.898 | 11.0929 | -0.0002 | -0.0022 | 0.0007 | 0.0039 | 0.0011 | -0.0007 | 0.003 | -0.0105 | -0.0109 | -360.1496 | 17.3946 | -360.4327 | 17.641 | -360.7989 | 18.1399 | -360.7897 | 17.5855 | -352.626 | 18.6984 | -352.6383 | 16.8402
12:32 | 4352 | 41.2046 | 202.1892 | 449.4367 | 456.3003 | -16.3253 | -40.8607 | 11.0734 | 7.763 | 1.9834 | 0.2305 | 3.1822 | -0.9669 | 11.49 | 4.4436 | 0.6155 | 0.6601 | 0.9635 | 0.7404 | -129.5951 | -0.6708 | 5.3883 | 1.4826 | -3.0655 | -1.4484 | 4.4369 |  | 3.0085 | 0.1254 | 4.009 | 3.3657 | 3.3385 | 1.0732 | 10.7602 | 14.2799 | 14.8883 | 11.1017 | 0.0001 | -0.0027 | 0.0007 | 0.0039 | 0.0008 | -0.0003 | 0.0224 | 0.0031 | 0.0061 | -360.1373 | 17.3987 | -360.4266 | 17.641 | -360.7927 | 18.1255 | -360.7989 | 17.5712 | -352.6198 | 18.7045 | -352.666 | 16.8258
12:32 | 4353 | 41.2613 | 202.2353 | 449.5713 | 456.2803 | -16.321 | -40.9024 | 10.9826 | 7.6944 | 2.0527 | 0.2919 | 3.216 | -0.9782 | 11.5349 | 4.4108 | 0.6165 | 0.6625 | 0.9609 | 0.7404 | -129.6569 | -0.7041 | 5.327 | 1.4345 | -3.1006 | -1.4904 | 4.3996 |  | 2.9858 | 0.1577 | 4.0089 | 3.3617 | 3.3327 | 1.0717 | 10.7463 | 14.2489 | 14.8761 | 11.0814 | 0.0004 | -0.0029 | 0.0006 | 0.004 | 0.0007 | -0.0009 | 0.0164 | -0.0025 | -0.009 | -360.1527 | 17.3782 | -360.4235 | 17.6328 | -360.802 | 18.1543 | -360.805 | 17.5835 | -352.6167 | 18.6922 | -352.6229 | 16.8361
12:32 | 4354 | 41.344 | 202.1383 | 449.4656 | 456.2741 | -16.3977 | -40.7961 | 11.0711 | 7.7613 | 2.0781 | 0.32 | 2.94 | -1.0289 | 11.6071 | 4.3391 | 0.6143 | 0.6635 | 0.9611 | 0.7396 | -129.6749 | -0.6685 | 5.4242 | 1.4202 | -3.0212 | -1.4315 | 4.3975 |  | 3.0113 | 0.1165 | 4.0094 | 3.3648 | 3.3361 | 1.0723 | 10.7406 | 14.2717 | 14.8566 | 11.0822 | -0.0001 | -0.0029 | 0.0003 | 0.0036 | 0.0008 | -0.0006 | 0.012 | -0.0062 | -0.0038 | -360.1281 | 17.3905 | -360.4204 | 17.6266 | -360.7773 | 18.1255 | -360.8204 | 17.5814 | -352.6413 | 18.7025 | -352.6506 | 16.8217
12:32 | 4355 | 41.2269 | 202.1028 | 449.4426 | 456.288 | -16.384 | -40.8597 | 11.1232 | 7.6908 | 2.0703 | 0.3893 | 3.032 | -0.9988 | 11.5492 | 4.3206 | 0.6145 | 0.66 | 0.9603 | 0.7411 | -129.5899 | -0.7189 | 5.4704 | 1.4637 | -3.0795 | -1.3673 | 4.5411 |  | 2.9717 | 0.189 | 4.0083 | 3.3631 | 3.3364 | 1.0724 | 10.7706 | 14.2557 | 14.8648 | 11.0713 | -0.0002 | -0.0024 | 0.001 | 0.0038 | 0.0012 | -0.0005 | 0.0206 | -0.007 | 0.0014 | -360.1281 | 17.3966 | -360.4542 | 17.6615 | -360.8112 | 18.142 | -360.8143 | 17.565 | -352.589 | 18.6963 | -352.6506 | 16.8299
12:32 | 4356 | 41.2346 | 202.1339 | 449.4357 | 456.2434 | -16.3865 | -40.8475 | 11.019 | 7.7098 | 2.0571 | 0.4701 | 3.0331 | -1.012 | 11.584 | 4.3038 | 0.6151 | 0.6592 | 0.9611 | 0.7422 | -129.5777 | -0.6864 | 5.4641 | 1.5002 | -3.1014 | -1.4715 | 4.4812 |  | 2.8767 | 0.1075 | 4.0087 | 3.3629 | 3.3341 | 1.0726 | 10.7324 | 14.2523 | 14.8444 | 11.085 | 0.0001 | -0.0026 | 0.0011 | 0.0043 | 0.0009 | 0.0001 | 0.0167 | -0.002 | -0.0185 | -360.1896 | 17.3864 | -360.4173 | 17.6348 | -360.7989 | 18.1379 | -360.8297 | 17.5958 | -352.6136 | 18.6902 | -352.5983 | 16.8156
12:32 | 4357 | 41.1352 | 202.1364 | 449.378 | 456.1765 | -16.4405 | -40.8971 | 10.9733 | 7.7604 | 2.0342 | 0.3397 | 3.0451 | -1.0282 | 11.522 | 4.3707 | 0.6163 | 0.6607 | 0.9642 | 0.7413 | -129.6166 | -0.6796 | 5.4901 | 1.519 | -2.9813 | -1.458 | 4.4588 |  | 2.9148 | 0.13 | 4.0099 | 3.3686 | 3.3385 | 1.0733 | 10.7267 | 14.252 | 14.8481 | 11.0916 | 0 | -0.0031 | 0.0006 | 0.004 | 0.0009 | -0.0005 | 0.0132 | -0.0106 | -0.0198 | -360.1835 | 17.4151 | -360.4758 | 17.6369 | -360.802 | 18.1379 | -360.8266 | 17.5814 | -352.6444 | 18.7189 | -352.6321 | 16.8279
12:32 | 4358 | 41.1616 | 202.2545 | 449.4871 | 456.1042 | -16.4199 | -40.9272 | 10.9107 | 7.7163 | 1.9721 | 0.2596 | 3.0032 | -1.0098 | 11.6092 | 4.3066 | 0.6165 | 0.6653 | 0.9638 | 0.7424 | -129.5208 | -0.6067 | 5.539 | 1.6339 | -3.064 | -1.4882 | 4.4259 |  | 2.9265 | -0.0369 | 4.0095 | 3.361 | 3.3351 | 1.0726 | 10.7394 | 14.2533 | 14.8447 | 11.0576 | 0.0001 | -0.0028 | 0.0002 | 0.0033 | 0.001 | 0.0002 | 0.016 | 0.0081 | -0.012 | -360.1496 | 17.4007 | -360.4542 | 17.6718 | -360.845 | 18.1645 | -360.8604 | 17.5773 | -352.6075 | 18.7004 | -352.629 | 16.832
12:32 | 4359 | 41.2902 | 202.1767 | 449.5305 | 456.2474 | -16.3925 | -40.8587 | 10.9679 | 7.7191 | 1.9371 | 0.4249 | 2.9625 | -0.9527 | 11.6315 | 4.3082 | 0.6155 | 0.6643 | 0.9626 | 0.7429 | -129.514 | -0.6766 | 5.504 | 1.6671 | -3.1861 | -1.482 | 4.4064 |  | 2.9678 | 0.1224 | 4.0097 | 3.364 | 3.3371 | 1.0741 | 10.766 | 14.2684 | 14.8604 | 11.1186 | -0.0002 | -0.0026 | 0.0005 | 0.0033 | 0.0009 | -0.0009 | 0.0078 | -0.0063 | -0.0091 | -360.2419 | 17.4233 | -360.4512 | 17.6369 | -360.7989 | 18.1481 | -360.8635 | 17.6184 | -352.6506 | 18.7189 | -352.6629 | 16.8074
12:32 | 4360 | 41.209 | 202.2123 | 449.4611 | 456.1043 | -16.4279 | -40.8645 | 10.9661 | 7.7435 | 1.9318 | 0.4031 | 2.9771 | -1.0026 | 11.6303 | 4.4022 | 0.6159 | 0.666 | 0.9649 | 0.742 | -129.5036 | -0.637 | 5.5554 | 1.7725 | -3.1942 | -1.5136 | 4.4074 |  | 3.0045 | 0.0825 | 4.0088 | 3.3631 | 3.3356 | 1.0733 | 10.7405 | 14.2661 | 14.8634 | 11.0818 | -0.0001 | -0.0025 | 0.0003 | 0.0037 | 0.001 | -0.0004 | 0.0164 | -0.0095 | -0.0216 | -360.1835 | 17.4254 | -360.5189 | 17.6902 | -360.8697 | 18.1563 | -360.842 | 17.5855 | -352.6598 | 18.7333 | -352.6967 | 16.8566
12:32 | 4361 | 41.2196 | 202.1824 | 449.5012 | 456.1312 | -16.3799 | -40.7809 | 11.0587 | 7.8302 | 1.9127 | 0.3807 | 3.0944 | -0.9977 | 11.5591 | 4.2858 | 0.6157 | 0.6657 | 0.9607 | 0.7418 | -129.5421 | -0.7834 | 5.5258 | 1.8186 | -3.1454 | -1.5196 | 4.331 |  | 3.0607 | 0.0287 | 4.0087 | 3.3619 | 3.3373 | 1.0726 | 10.7568 | 14.2822 | 14.8389 | 11.0749 | 0.0002 | -0.003 | 0.001 | 0.0044 | 0.0008 | -0.0007 | 0.0027 | -0.0008 | -0.0307 | -360.1711 | 17.3987 | -360.4419 | 17.6594 | -360.845 | 18.181 | -360.9035 | 17.6204 | -352.6444 | 18.7045 | -352.6475 | 16.832
12:32 | 4362 | 41.2375 | 202.2245 | 449.5428 | 456.1816 | -16.4193 | -40.9489 | 10.9579 | 7.8076 | 2.0199 | 0.5095 | 3.0688 | -0.9901 | 11.5754 | 4.2673 | 0.6153 | 0.6675 | 0.961 | 0.7419 | -129.5805 | -0.6268 | 5.5718 | 1.8091 | -3.1698 | -1.6028 | 4.4098 |  | 2.9662 | 0.0031 | 4.01 | 3.3644 | 3.337 | 1.0733 | 10.795 | 14.2856 | 14.8651 | 11.1017 | 0.0001 | -0.003 | 0.0012 | 0.0042 | 0.0008 | -0.0004 | 0.0056 | -0.0022 | -0.0166 | -360.245 | 17.4418 | -360.5035 | 17.6615 | -360.8143 | 18.1584 | -360.8512 | 17.6163 | -352.7306 | 18.7374 | -352.6906 | 16.8381
12:32 | 4363 | 41.2807 | 202.1728 | 449.5267 | 456.309 | -16.5172 | -40.9114 | 11.0074 | 7.7703 | 1.9761 | 0.4308 | 3.0615 | -0.9859 | 11.6118 | 4.3212 | 0.6156 | 0.6627 | 0.9573 | 0.7423 | -129.5727 | -0.7504 | 5.5397 | 1.6718 | -3.1709 | -1.7152 | 4.4184 |  | 3.0465 | -0.0133 | 4.0106 | 3.3655 | 3.3378 | 1.074 | 10.7636 | 14.2778 | 14.8645 | 11.1103 | -0.0002 | -0.0024 | 0.0006 | 0.004 | 0.0003 | -0.0003 | 0.0051 | -0.0012 | -0.0187 | -360.085 | 17.4131 | -360.5127 | 17.7026 | -360.8727 | 18.1687 | -360.8543 | 17.5814 | -352.6106 | 18.723 | -352.706 | 16.8731
12:32 | 4364 | 41.1787 | 202.0939 | 449.4694 | 456.1382 | -16.4206 | -40.8819 | 10.9561 | 7.792 | 2.0574 | 0.427 | 2.9959 | -0.9575 | 11.5348 | 4.3115 | 0.6154 | 0.6608 | 0.9598 | 0.7409 | -129.6013 | -0.7246 | 5.5923 | 1.6666 | -3.1534 | -1.5992 | 4.371 |  | 3.0603 | 0.0775 | 4.0112 | 3.3658 | 3.3382 | 1.0728 | 10.7198 | 14.2275 | 14.782 | 11.0447 | -0.0005 | -0.003 | 0.0009 | 0.0043 | 0.0009 | -0.0007 | 0.0006 | 0.0115 | 0.0013 | -360.2111 | 17.409 | -360.4604 | 17.6574 | -360.8327 | 18.1769 | -360.9127 | 17.6348 | -352.6906 | 18.7169 | -352.629 | 16.8361
12:32 | 4365 | 41.2313 | 202.1447 | 449.4278 | 456.2415 | -16.4176 | -40.9745 | 10.9631 | 7.7888 | 2.0111 | 0.4362 | 2.995 | -1.0094 | 11.5432 | 4.2118 | 0.6152 | 0.6597 | 0.9612 | 0.7426 | -129.5611 | -0.7581 | 5.4759 | 1.5107 | -3.2349 | -1.6415 | 4.386 |  | 3.0524 | 0.0957 | 4.0114 | 3.3647 | 3.3391 | 1.072 | 10.7727 | 14.2876 | 14.895 | 11.1124 | 0.0004 | -0.003 | 0.001 | 0.0037 | 0.0008 | -0.0003 | 0.0083 | -0.0107 | -0.0044 | -360.2019 | 17.4459 | -360.4973 | 17.68 | -360.8604 | 18.1399 | -360.8297 | 17.604 | -352.6752 | 18.7477 | -352.7029 | 16.8525
12:32 | 4366 | 41.2031 | 202.0686 | 449.5091 | 456.1573 | -16.4159 | -40.8979 | 10.9031 | 7.837 | 2.0437 | 0.4181 | 3.0512 | -1.0231 | 11.5563 | 4.3115 | 0.6159 | 0.665 | 0.9555 | 0.7416 | -129.6789 | -0.7652 | 5.4136 | 1.5424 | -3.2314 | -1.6263 | 4.3879 |  | 3.0067 | 0.0087 | 4.0091 | 3.3657 | 3.3339 | 1.0716 | 10.7221 | 14.2474 | 14.8436 | 11.0869 | 0.0004 | -0.0032 | 0.0004 | 0.0035 | 0.0011 | -0.0009 | 0.0295 | -0.009 | -0.0239 | -360.1311 | 17.3987 | -360.4635 | 17.6759 | -360.8758 | 18.1871 | -360.8727 | 17.5896 | -352.629 | 18.7066 | -352.6752 | 16.8546
12:32 | 4367 | 41.1935 | 202.0612 | 449.3636 | 456.1486 | -16.5094 | -41.0036 | 10.9187 | 7.7835 | 2.087 | 0.4601 | 3.1145 | -1.0083 | 11.5103 | 4.3561 | 0.6176 | 0.6622 | 0.9596 | 0.742 | -129.6705 | -0.7529 | 5.4153 | 1.5937 | -3.226 | -1.5618 | 4.3681 |  | 2.9995 | 0.0467 | 4.0103 | 3.366 | 3.3337 | 1.072 | 10.7312 | 14.257 | 14.8441 | 11.072 | -0.0003 | -0.0025 | 0.0007 | 0.0039 | 0.0008 | -0.0001 | 0.0255 | -0.013 | 0.0027 | -360.2696 | 17.4315 | -360.4696 | 17.6328 | -360.7866 | 18.1502 | -360.8789 | 17.6245 | -352.669 | 18.7251 | -352.6567 | 16.8258
12:33 | 4368 | 41.2389 | 202.1682 | 449.5415 | 456.3026 | -16.4507 | -41.0245 | 10.8806 | 7.7074 | 2.0847 | 0.6216 | 3.107 | -1.0671 | 11.5786 | 4.352 | 0.6156 | 0.6623 | 0.9593 | 0.7416 | -129.6372 | -0.6846 | 5.4482 | 1.6162 | -3.2461 | -1.5231 | 4.4143 |  | 3.1035 | 0.1147 | 4.0106 | 3.3699 | 3.3385 | 1.074 | 10.7532 | 14.2618 | 14.8727 | 11.1052 | -0.0005 | -0.0027 | 0.001 | 0.0033 | 0.001 | -0.0007 | 0.0121 | -0.02 | -0.0165 | -360.1742 | 17.4213 | -360.5312 | 17.6923 | -360.8574 | 18.1502 | -360.8327 | 17.5691 | -352.629 | 18.7353 | -352.7183 | 16.8751
12:33 | 4369 | 41.3083 | 202.231 | 449.4962 | 456.2565 | -16.3475 | -40.8379 | 11.078 | 7.8159 | 2.1095 | 0.5529 | 3.161 | -1.0084 | 11.6118 | 4.3685 | 0.6158 | 0.6638 | 0.9586 | 0.7428 | -129.6435 | -0.6982 | 5.4227 | 1.5509 | -3.1934 | -1.5922 | 4.3801 |  | 3.0838 | 0.0413 | 4.0093 | 3.3656 | 3.3374 | 1.0739 | 10.7417 | 14.2671 | 14.8348 | 11.0601 | -0.0002 | -0.0031 | 0.0007 | 0.0039 | 0.0006 | -0.0003 | 0.0219 | -0.0056 | 0.0166 | -360.1773 | 17.3905 | -360.4235 | 17.6266 | -360.8174 | 18.1584 | -360.8943 | 17.6204 | -352.6537 | 18.6922 | -352.6321 | 16.8258
12:33 | 4370 | 41.2992 | 202.164 | 449.4227 | 456.261 | -16.5017 | -40.9644 | 11.0085 | 7.8378 | 2.077 | 0.4221 | 3.206 | -1.0275 | 11.5136 | 4.2282 | 0.6159 | 0.6618 | 0.9551 | 0.7412 | -129.6014 | -0.6773 | 5.3876 | 1.6022 | -3.2016 | -1.59 | 4.3625 |  | 3.0556 | -0.0054 | 4.0112 | 3.3697 | 3.3375 | 1.0746 | 10.7521 | 14.2487 | 14.8461 | 11.0645 | 0 | -0.0032 | 0.0011 | 0.0043 | 0.0012 | -0.0005 | -0.0044 | -0.0096 | 0.0001 | -360.2265 | 17.4254 | -360.4973 | 17.6389 | -360.7897 | 18.1255 | -360.8174 | 17.5937 | -352.669 | 18.7436 | -352.7121 | 16.8402
12:33 | 4371 | 41.2706 | 202.341 | 449.4989 | 456.4177 | -16.5178 | -40.9761 | 11.096 | 7.8724 | 2.0783 | 0.4385 | 3.1098 | -0.9886 | 11.5377 | 4.2026 | 0.6163 | 0.6603 | 0.9547 | 0.7437 | -129.5053 | -0.7349 | 5.3962 | 1.6007 | -3.1746 | -1.6091 | 4.4571 |  | 3.0625 | 0.0406 | 4.0096 | 3.3701 | 3.3376 | 1.0735 | 10.7648 | 14.2673 | 14.8532 | 11.0887 | -0.0004 | -0.0031 | 0.0011 | 0.0042 | 0.0009 | 0 | 0.0053 | -0.0021 | 0.0109 | -360.1219 | 17.3782 | -360.4512 | 17.6574 | -360.845 | 18.1645 | -360.8327 | 17.565 | -352.586 | 18.684 | -352.6537 | 16.8648
12:33 | 4372 | 41.202 | 202.2911 | 449.4287 | 456.306 | -16.4346 | -40.8778 | 11.0552 | 7.8243 | 2.0605 | 0.4581 | 3.1258 | -0.9709 | 11.5298 | 4.3067 | 0.615 | 0.6573 | 0.9597 | 0.7423 | -129.6897 | -0.6703 | 5.3442 | 1.6006 | -3.1589 | -1.5198 | 4.4501 |  | 3.0287 | -0.0112 | 4.01 | 3.3649 | 3.3385 | 1.075 | 10.7545 | 14.245 | 14.8178 | 11.0847 | -0.0004 | -0.0028 | 0.001 | 0.0042 | 0.0006 | -0.0008 | 0.0096 | -0.0106 | -0.012 | -360.2204 | 17.4007 | -360.4112 | 17.604 | -360.762 | 18.1522 | -360.8574 | 17.6122 | -352.6875 | 18.7087 | -352.6198 | 16.8074
12:33 | 4373 | 41.2856 | 202.2436 | 449.5238 | 456.1911 | -16.4079 | -40.9274 | 10.8811 | 7.8023 | 2.0887 | 0.6021 | 3.0779 | -1.0343 | 11.6026 | 4.3571 | 0.6162 | 0.6586 | 0.9588 | 0.742 | -129.6059 | -0.6658 | 5.369 | 1.4504 | -3.174 | -1.5404 | 4.4718 |  | 3.0105 | 0.0078 | 4.0101 | 3.3679 | 3.3341 | 1.0738 | 10.7301 | 14.2732 | 14.8775 | 11.123 | 0.0004 | -0.0026 | 0.0009 | 0.0038 | 0.0004 | -0.0007 | 0.0102 | -0.0076 | -0.016 | -360.1342 | 17.4131 | -360.485 | 17.6451 | -360.8235 | 18.1379 | -360.7743 | 17.5527 | -352.6352 | 18.7148 | -352.6721 | 16.8484
12:33 | 4374 | 41.2521 | 202.2352 | 449.4742 | 456.2126 | -16.3219 | -40.8415 | 10.9981 | 7.91 | 2.1342 | 0.4552 | 3.1487 | -0.8962 | 11.6277 | 4.3062 | 0.6172 | 0.6595 | 0.9639 | 0.7422 | -129.5832 | -0.6563 | 5.3609 | 1.5248 | -3.0753 | -1.5854 | 4.3956 |  | 3.0284 | -0.0137 | 4.0096 | 3.3651 | 3.3359 | 1.0743 | 10.751 | 14.2707 | 14.8505 | 11.0923 | 0.0002 | -0.0032 | 0.0008 | 0.0039 | 0.0007 | -0.0006 | 0.0212 | -0.0141 | -0.0121 | -360.1096 | 17.3617 | -360.3712 | 17.6225 | -360.8081 | 18.1851 | -360.8481 | 17.5814 | -352.6167 | 18.6696 | -352.6106 | 16.832
12:33 | 4375 | 41.231 | 202.2101 | 449.4566 | 456.2876 | -16.3929 | -40.9035 | 11.0636 | 7.8646 | 2.1208 | 0.4159 | 3.147 | -0.9835 | 11.6631 | 4.3319 | 0.6171 | 0.6621 | 0.9607 | 0.7419 | -129.577 | -0.6985 | 5.3484 | 1.5622 | -3.0612 | -1.5404 | 4.3629 |  | 3.0711 | 0.0058 | 4.0113 | 3.3677 | 3.3369 | 1.0736 | 10.736 | 14.2382 | 14.8638 | 11.0948 | 0.0002 | -0.0027 | 0.0006 | 0.0039 | 0.0007 | -0.0006 | 0.0157 | -0.007 | -0.0255 | -360.1711 | 17.4028 | -360.405 | 17.5978 | -360.722 | 18.1399 | -360.7897 | 17.5937 | -352.6506 | 18.7066 | -352.626 | 16.8032
12:33 | 4376 | 41.2053 | 202.2176 | 449.5775 | 456.2446 | -16.4632 | -40.9166 | 11.0154 | 7.8313 | 2.0613 | 0.415 | 3.1308 | -1.0003 | 11.6062 | 4.3615 | 0.6162 | 0.6605 | 0.9621 | 0.7414 | -129.6082 | -0.689 | 5.3505 | 1.5909 | -3.1192 | -1.6137 | 4.4053 |  | 2.9847 | 0.0027 | 4.0093 | 3.3658 | 3.3338 | 1.073 | 10.7556 | 14.2465 | 14.827 | 11.0966 | 0 | -0.0027 | 0.001 | 0.0042 | 0.0009 | -0.0003 | 0.0024 | -0.0075 | -0.008 | -360.1342 | 17.3905 | -360.4573 | 17.6594 | -360.8389 | 18.1666 | -360.7804 | 17.5506 | -352.5921 | 18.6881 | -352.6721 | 16.8546
12:33 | 4377 | 41.2276 | 202.3153 | 449.5327 | 456.32 | -16.4464 | -40.9965 | 11.0505 | 7.7746 | 2.1736 | 0.4263 | 3.1287 | -0.9374 | 11.5844 | 4.4618 | 0.6157 | 0.6619 | 0.9603 | 0.7414 | -129.642 | -0.7449 | 5.3911 | 1.82 | -3.031 | -1.4681 | 4.4721 |  | 3.0752 | 0.0549 | 4.0106 | 3.366 | 3.3369 | 1.073 | 10.7557 | 14.2404 | 14.8365 | 11.08 | 0.0001 | -0.0026 | 0.0009 | 0.0039 | 0.0008 | -0.0006 | 0.006 | -0.012 | -0.0142 | -360.1188 | 17.3658 | -360.3619 | 17.602 | -360.765 | 18.1851 | -360.8604 | 17.5855 | -352.6044 | 18.6758 | -352.5921 | 16.8094
12:33 | 4378 | 41.1729 | 202.263 | 449.5129 | 456.28 | -16.3296 | -40.8534 | 11.1007 | 7.748 | 2.1997 | 0.46 | 3.0993 | -0.9508 | 11.5822 | 4.3784 | 0.6161 | 0.661 | 0.9617 | 0.7416 | -129.631 | -0.6649 | 5.3932 | 1.8086 | -3.0983 | -1.4735 | 4.4379 |  | 3.015 | 0.0846 | 4.0111 | 3.3666 | 3.336 | 1.0725 | 10.7441 | 14.2578 | 14.8423 | 11.0858 | 0.0001 | -0.003 | 0.0009 | 0.004 | 0.0003 | -0.0005 | 0.015 | -0.0074 | -0.0057 | -360.1588 | 17.4131 | -360.4727 | 17.6307 | -360.7681 | 18.1379 | -360.7835 | 17.5671 | -352.6475 | 18.7169 | -352.6567 | 16.832
12:33 | 4379 | 41.1653 | 202.3598 | 449.5301 | 456.2195 | -16.2903 | -40.8369 | 11.1397 | 7.7979 | 2.1364 | 0.4766 | 3.0102 | -0.908 | 11.5568 | 4.3883 | 0.6175 | 0.6619 | 0.968 | 0.7417 | -129.5892 | -0.653 | 5.4489 | 1.7416 | -3.1235 | -1.3991 | 4.4339 |  | 3.0858 | 0.1587 | 4.0103 | 3.3632 | 3.3364 | 1.073 | 10.7545 | 14.2509 | 14.8651 | 11.1132 | 0 | -0.0027 | 0.0003 | 0.004 | 0.0009 | -0.0004 | -0.0039 | -0.0124 | -0.0082 | -360.0881 | 17.3638 | -360.4173 | 17.6471 | -360.8327 | 18.1728 | -360.7866 | 17.5445 | -352.5521 | 18.6655 | -352.626 | 16.8464
12:33 | 4380 | 41.2732 | 202.3006 | 449.5415 | 456.2587 | -16.3391 | -40.9105 | 11.2264 | 7.7341 | 2.1995 | 0.4513 | 3.1073 | -0.9908 | 11.5754 | 4.3468 | 0.6159 | 0.6637 | 0.962 | 0.741 | -129.5632 | -0.7026 | 5.4702 | 1.7685 | -3.2015 | -1.4259 | 4.3626 |  | 3.0188 | 0.19 | 4.01 | 3.371 | 3.3362 | 1.0751 | 10.7302 | 14.2613 | 14.8174 | 11.0659 | -0.0002 | -0.0023 | 0.0006 | 0.0039 | 0.0004 | 0 | 0.0302 | -0.005 | -0.0027 | -360.2204 | 17.3925 | -360.3896 | 17.5896 | -360.7558 | 18.1789 | -360.8297 | 17.5876 | -352.6444 | 18.7025 | -352.6075 | 16.8053
12:33 | 4381 | 41.3035 | 202.3542 | 449.535 | 456.3089 | -16.326 | -40.8267 | 11.2377 | 7.7645 | 2.2259 | 0.3861 | 3.0954 | -1.0017 | 11.6593 | 4.3399 | 0.6169 | 0.6619 | 0.9617 | 0.7412 | -129.6414 | -0.729 | 5.3691 | 1.7212 | -3.1835 | -1.5394 | 4.3125 |  | 2.9794 | 0.026 | 4.0105 | 3.3712 | 3.3365 | 1.0729 | 10.7602 | 14.2684 | 14.8199 | 11.0724 | -0.0003 | -0.0029 | 0.0012 | 0.0039 | 0.0011 | -0.0006 | 0.0055 | -0.0101 | 0.0034 | -360.1404 | 17.4048 | -360.4727 | 17.6451 | -360.8143 | 18.1543 | -360.7589 | 17.5486 | -352.6075 | 18.7025 | -352.6783 | 16.8443
12:33 | 4382 | 41.2765 | 202.3171 | 449.5833 | 456.2932 | -16.3034 | -40.8808 | 11.1822 | 7.8062 | 2.2197 | 0.4424 | 3.1599 | -1.04 | 11.5917 | 4.2838 | 0.618 | 0.6669 | 0.965 | 0.7428 | -129.536 | -0.6797 | 5.4049 | 1.6792 | -3.1945 | -1.5085 | 4.258 |  | 2.944 | 0.0005 | 4.0113 | 3.3694 | 3.3387 | 1.0748 | 10.7568 | 14.2474 | 14.8552 | 11.0753 | 0.0005 | -0.0027 | 0.0002 | 0.0035 | 0.0005 | -0.0002 | -0.0005 | -0.0133 | 0.0014 | -360.0973 | 17.3658 | -360.3804 | 17.6204 | -360.8235 | 18.1974 | -360.8574 | 17.5629 | -352.6013 | 18.6676 | -352.5921 | 16.8279
12:33 | 4383 | 41.2546 | 202.33 | 449.5694 | 456.3772 | -16.273 | -40.74 | 11.2743 | 7.7434 | 2.2065 | 0.4253 | 3.1339 | -1.0299 | 11.6678 | 4.2996 | 0.6168 | 0.6617 | 0.9628 | 0.7429 | -129.5756 | -0.6978 | 5.5173 | 1.6389 | -3.2325 | -1.5558 | 4.3129 |  | 3.0557 | 0.055 | 4.0099 | 3.367 | 3.3358 | 1.0738 | 10.7418 | 14.2438 | 14.8048 | 11.0779 | 0.0002 | -0.003 | 0.0017 | 0.0041 | 0.0009 | -0.0007 | 0.024 | -0.0088 | -0.0132 | -360.1773 | 17.4028 | -360.4142 | 17.5958 | -360.7312 | 18.1502 | -360.8297 | 17.5753 | -352.6383 | 18.7107 | -352.629 | 16.8032
12:33 | 4384 | 41.3811 | 202.3072 | 449.5514 | 456.402 | -16.296 | -40.8756 | 11.1749 | 7.7322 | 2.1466 | 0.3383 | 2.9533 | -1.0572 | 11.6683 | 4.3129 | 0.6183 | 0.6638 | 0.9634 | 0.7443 | -129.551 | -0.5507 | 5.4265 | 1.6032 | -3.2489 | -1.6003 | 4.2698 |  | 2.9721 | 0.0586 | 4.0089 | 3.3683 | 3.3358 | 1.0727 | 10.766 | 14.2741 | 14.8651 | 11.0786 | -0.0004 | -0.0028 | 0.0009 | 0.0039 | 0.0008 | -0.0006 | 0.004 | -0.0104 | -0.0121 | -360.1158 | 17.3884 | -360.4758 | 17.6574 | -360.8174 | 18.1604 | -360.7835 | 17.5383 | -352.5829 | 18.7004 | -352.666 | 16.8505
12:33 | 4385 | 41.2672 | 202.3165 | 449.501 | 456.3002 | -16.2959 | -40.8213 | 11.2236 | 7.7291 | 2.0693 | 0.4157 | 3.0284 | -1.0841 | 11.6937 | 4.4046 | 0.618 | 0.6632 | 0.9633 | 0.7427 | -129.4626 | -0.6501 | 5.521 | 1.6359 | -3.181 | -1.5479 | 4.2528 |  | 3.0108 | 0.0658 | 4.0107 | 3.3675 | 3.3382 | 1.074 | 10.7672 | 14.2115 | 14.796 | 11.08 | 0 | -0.0026 | 0.0004 | 0.0035 | 0.0007 | -0.0007 | 0.0173 | -0.002 | -0.0109 | -360.1465 | 17.3556 | -360.3712 | 17.6102 | -360.7866 | 18.1933 | -360.8635 | 17.5712 | -352.6321 | 18.682 | -352.5767 | 16.8012
12:33 | 4386 | 41.305 | 202.2243 | 449.4265 | 456.3236 | -16.3379 | -40.8605 | 11.1634 | 7.6997 | 2.1216 | 0.4838 | 3.0134 | -1.112 | 11.6177 | 4.3821 | 0.6168 | 0.6616 | 0.9616 | 0.7434 | -129.5074 | -0.6581 | 5.554 | 1.6842 | -3.1818 | -1.5239 | 4.28 |  | 3.1264 | 0.0809 | 4.01 | 3.3679 | 3.3354 | 1.0737 | 10.7509 | 14.2825 | 14.8642 | 11.1262 | 0.0001 | -0.0028 | 0.0011 | 0.0046 | 0.0008 | -0.0005 | 0.0118 | -0.0161 | -0.0226 | -360.1711 | 17.4172 | -360.4758 | 17.6245 | -360.7527 | 18.1543 | -360.8112 | 17.5732 | -352.6321 | 18.7353 | -352.6537 | 16.8156
12:33 | 4387 | 41.3328 | 202.2561 | 449.3896 | 456.3315 | -16.2777 | -40.8655 | 11.1482 | 7.903 | 2.0954 | 0.4453 | 3.121 | -1.048 | 11.6662 | 4.3238 | 0.6166 | 0.658 | 0.9623 | 0.7422 | -129.4004 | -0.4811 | 5.5827 | 1.7144 | -3.257 | -1.6286 | 4.322 |  | 3.1752 | 0.1302 | 4.0085 | 3.3664 | 3.3325 | 1.073 | 10.7776 | 14.2799 | 14.8941 | 11.1017 | 0 | -0.0032 | 0.0004 | 0.0037 | 0.0002 | -0.0007 | 0.0155 | -0.0132 | -0.0081 | -360.0911 | 17.3884 | -360.4635 | 17.6615 | -360.8635 | 18.1748 | -360.7835 | 17.5445 | -352.6013 | 18.6902 | -352.6598 | 16.8464
12:33 | 4388 | 41.369 | 202.2983 | 449.3893 | 456.2474 | -16.3102 | -40.8466 | 11.2 | 7.9191 | 2.1388 | 0.4368 | 3.0918 | -1.0303 | 11.6448 | 4.3117 | 0.6159 | 0.6619 | 0.963 | 0.7405 | -129.3974 | -0.5139 | 5.5769 | 1.7108 | -3.2415 | -1.5853 | 4.2769 |  | 3.0757 | -0.0379 | 4.01 | 3.3682 | 3.3359 | 1.0733 | 10.744 | 14.2581 | 14.8444 | 11.0793 | -0.0002 | -0.0028 | 0.0006 | 0.0036 | 0.001 | -0.0007 | 0.0138 | -0.013 | -0.0025 | -360.1742 | 17.3884 | -360.4235 | 17.6163 | -360.7773 | 18.1871 | -360.8758 | 17.5917 | -352.6567 | 18.7066 | -352.6075 | 16.8053
12:33 | 4389 | 41.4311 | 202.258 | 449.5223 | 456.2663 | -16.2303 | -40.8097 | 11.2064 | 7.8819 | 2.0703 | 0.4964 | 3.061 | -1.0082 | 11.6764 | 4.3533 | 0.6155 | 0.6608 | 0.9649 | 0.7424 | -129.5343 | -0.637 | 5.5013 | 1.6959 | -3.2522 | -1.6667 | 4.2579 |  | 3.0973 | 0.0053 | 4.0104 | 3.3712 | 3.3357 | 1.0747 | 10.7463 | 14.2547 | 14.8587 | 11.0988 | 0.0001 | -0.0025 | 0.0011 | 0.0037 | 0.0009 | 0.0001 | 0.0193 | -0.0148 | -0.0079 | -360.205 | 17.4295 | -360.5004 | 17.6656 | -360.842 | 18.1604 | -360.805 | 17.565 | -352.6475 | 18.7538 | -352.6875 | 16.8381
12:33 | 4390 | 41.3551 | 202.29 | 449.5018 | 456.3076 | -16.2561 | -40.8464 | 11.1813 | 7.9075 | 2.0908 | 0.4732 | 3.0249 | -0.8971 | 11.6445 | 4.3229 | 0.6166 | 0.6622 | 0.9644 | 0.7418 | -129.5302 | -0.5733 | 5.4561 | 1.6991 | -3.2096 | -1.5667 | 4.3146 |  | 3.1054 | 0.0137 | 4.0108 | 3.3687 | 3.3366 | 1.0743 | 10.7465 | 14.2539 | 14.836 | 11.0718 | 0 | -0.0033 | 0.0004 | 0.0034 | 0.0008 | -0.0006 | -0.0008 | -0.0157 | -0.0141 | -360.1835 | 17.3884 | -360.4481 | 17.6574 | -360.882 | 18.2097 | -360.8789 | 17.5794 | -352.5921 | 18.7066 | -352.6598 | 16.8505
12:33 | 4391 | 41.4352 | 202.3207 | 449.4919 | 456.3072 | -16.3102 | -40.9057 | 11.1618 | 7.8605 | 2.0016 | 0.3699 | 3.0375 | -0.8377 | 11.6343 | 4.3714 | 0.6174 | 0.6581 | 0.965 | 0.7439 | -129.5594 | -0.6121 | 5.4778 | 1.6943 | -3.1887 | -1.5429 | 4.3546 |  | 3.1043 | -0.0323 | 4.0099 | 3.3687 | 3.3378 | 1.0741 | 10.7567 | 14.2477 | 14.8516 | 11.1035 | 0.0002 | -0.0031 | 0.0006 | 0.0039 | 0.0008 | -0.0002 | 0.0088 | -0.0136 | -0.0033 | -360.2296 | 17.4254 | -360.4481 | 17.641 | -360.8081 | 18.1953 | -360.9004 | 17.6163 | -352.7213 | 18.7395 | -352.6537 | 16.8279
12:33 | 4392 | 41.3942 | 202.3525 | 449.5435 | 456.2817 | -16.3413 | -40.8746 | 11.0406 | 7.9169 | 2.0937 | 0.3581 | 3.059 | -0.859 | 11.6419 | 4.3675 | 0.6172 | 0.6614 | 0.964 | 0.7414 | -129.5676 | -0.5094 | 5.4875 | 1.6112 | -3.2786 | -1.5013 | 4.3225 |  | 3.086 | 0.0316 | 4.0081 | 3.3663 | 3.3345 | 1.0731 | 10.7465 | 14.2367 | 14.8371 | 11.0772 | -0.0001 | -0.0031 | 0.0007 | 0.0036 | 0.0007 | -0.0012 | 0.0069 | -0.0036 | 0.0043 | -360.2081 | 17.4356 | -360.525 | 17.6759 | -360.8543 | 18.1687 | -360.8235 | 17.5773 | -352.6383 | 18.7518 | -352.7121 | 16.8772
12:33 | 4393 | 41.5088 | 202.3916 | 449.5795 | 456.4456 | -16.2677 | -40.9355 | 11.1042 | 7.9872 | 2.2018 | 0.4011 | 3.0815 | -0.863 | 11.5976 | 4.3091 | 0.6162 | 0.6594 | 0.9621 | 0.7436 | -129.5624 | -0.6045 | 5.4922 | 1.5854 | -3.1913 | -1.5616 | 4.332 |  | 3.0645 | -0.0349 | 4.0095 | 3.3676 | 3.3368 | 1.075 | 10.7302 | 14.2266 | 14.8232 | 11.0833 | -0.0004 | -0.0027 | 0.0005 | 0.004 | 0.0009 | -0.0001 | 0.0047 | -0.0125 | -0.0095 | -360.1742 | 17.3864 | -360.4512 | 17.6594 | -360.845 | 18.2159 | -360.9251 | 17.5835 | -352.6567 | 18.7087 | -352.6444 | 16.8525
12:33 | 4394 | 41.5273 | 202.3777 | 449.5454 | 456.4513 | -16.2775 | -40.9718 | 11.1652 | 7.9877 | 2.2036 | 0.4152 | 3.0641 | -0.8354 | 11.639 | 4.3222 | 0.6184 | 0.6591 | 0.9649 | 0.7421 | -129.5199 | -0.5392 | 5.5379 | 1.716 | -3.1607 | -1.5033 | 4.3774 |  | 2.9911 | -0.0633 | 4.0086 | 3.364 | 3.3382 | 1.0749 | 10.7751 | 14.2954 | 14.8724 | 11.1038 | 0.0004 | -0.0027 | 0.0015 | 0.0046 | 0.0008 | -0.0005 | 0.0068 | -0.0085 | 0.0002 | -360.2327 | 17.4213 | -360.4573 | 17.6369 | -360.7897 | 18.1748 | -360.8543 | 17.5855 | -352.6783 | 18.7477 | -352.669 | 16.8361
12:33 | 4395 | 41.4265 | 202.3899 | 449.4284 | 456.2665 | -16.2772 | -41.0508 | 11.1867 | 8.0429 | 2.1078 | 0.3603 | 3.0373 | -0.9096 | 11.573 | 4.2873 | 0.6184 | 0.66 | 0.9589 | 0.7418 | -129.5371 | -0.4918 | 5.5368 | 1.673 | -3.1652 | -1.5159 | 4.2943 |  | 3.001 | -0.0118 | 4.01 | 3.3679 | 3.3364 | 1.0743 | 10.7671 | 14.2523 | 14.8676 | 11.0966 | 0.0002 | -0.0031 | 0.0003 | 0.0034 | 0.0005 | -0.0002 | 0.0075 | -0.0165 | 0.005 | -360.1435 | 17.3966 | -360.5004 | 17.6656 | -360.8574 | 18.1645 | -360.845 | 17.5486 | -352.6075 | 18.721 | -352.7029 | 16.8648
12:33 | 4396 | 41.474 | 202.3426 | 449.4164 | 456.3152 | -16.3381 | -41.04 | 11.2429 | 7.9076 | 2.2544 | 0.4029 | 3.016 | -0.8962 | 11.6804 | 4.3153 | 0.618 | 0.6615 | 0.9596 | 0.7422 | -129.5437 | -0.5809 | 5.4686 | 1.6568 | -3.1835 | -1.4872 | 4.361 |  | 3.1227 | 0.1144 | 4.0102 | 3.3658 | 3.3421 | 1.0746 | 10.7646 | 14.3026 | 14.8807 | 11.1334 | 0 | -0.0026 | 0.001 | 0.0039 | 0.001 | -0.0002 | 0.011 | -0.0134 | -0.0168 | -360.1558 | 17.3823 | -360.4081 | 17.6245 | -360.7927 | 18.183 | -360.8604 | 17.5732 | -352.6413 | 18.6943 | -352.6044 | 16.8381
12:33 | 4397 | 41.4135 | 202.3051 | 449.4566 | 456.3076 | -16.3453 | -40.9929 | 11.1568 | 7.8946 | 2.2062 | 0.3658 | 2.9912 | -0.9049 | 11.62 | 4.376 | 0.6161 | 0.6629 | 0.9599 | 0.741 | -129.4851 | -0.5576 | 5.4742 | 1.5773 | -3.2642 | -1.4585 | 4.3497 |  | 3.0895 | 0.1404 | 4.0106 | 3.3696 | 3.3401 | 1.0745 | 10.7464 | 14.2775 | 14.8392 | 11.0764 | -0.0005 | -0.0026 | 0.0009 | 0.0036 | 0.0006 | -0.0007 | 0.0162 | 0.002 | -0.034 | -360.1588 | 17.4131 | -360.4635 | 17.6225 | -360.7835 | 18.1543 | -360.7958 | 17.5527 | -352.6229 | 18.7395 | -352.669 | 16.8443
12:33 | 4398 | 41.3372 | 202.2965 | 449.3097 | 456.2879 | -16.2396 | -40.973 | 11.2665 | 7.9275 | 2.1937 | 0.4207 | 3.0516 | -0.8346 | 11.5724 | 4.4199 | 0.6172 | 0.6635 | 0.9599 | 0.7414 | -129.5257 | -0.5597 | 5.4986 | 1.5479 | -3.1806 | -1.4451 | 4.4273 |  | 2.9865 | -0.0179 | 4.0097 | 3.3674 | 3.3342 | 1.0737 | 10.7856 | 14.2652 | 14.841 | 11.1089 | 0.0001 | -0.0028 | 0.0011 | 0.0039 | 0.0007 | 0 | 0.0264 | -0.0063 | 0.0021 | -360.0788 | 17.3761 | -360.405 | 17.6307 | -360.8174 | 18.1789 | -360.8327 | 17.5568 | -352.6044 | 18.6922 | -352.6167 | 16.8423
12:33 | 4399 | 41.3424 | 202.3377 | 449.4515 | 456.3381 | -16.2662 | -40.9907 | 11.2566 | 7.9354 | 2.2524 | 0.4562 | 3.195 | -0.8787 | 11.5695 | 4.4433 | 0.6167 | 0.6626 | 0.9597 | 0.7407 | -129.4826 | -0.5076 | 5.5687 | 1.5466 | -3.1275 | -1.4797 | 4.4383 |  | 3.0602 | 0.067 | 4.0106 | 3.3676 | 3.3367 | 1.0738 | 10.7302 | 14.2323 | 14.7874 | 11.0779 | 0.0002 | -0.0032 | 0.0009 | 0.0041 | 0.0009 | -0.0008 | 0.0199 | -0.022 | -0.0036 | -360.1927 | 17.4048 | -360.4296 | 17.6184 | -360.7743 | 18.1481 | -360.8081 | 17.5773 | -352.629 | 18.7148 | -352.6075 | 16.8115
12:33 | 4400 | 41.3471 | 202.2295 | 449.3264 | 456.3045 | -16.2822 | -40.986 | 11.2373 | 7.9167 | 2.2783 | 0.4118 | 3.1017 | -0.9624 | 11.5038 | 4.2724 | 0.6167 | 0.6596 | 0.9652 | 0.7402 | -129.573 | -0.5993 | 5.4862 | 1.552 | -3.1093 | -1.5551 | 4.4775 |  | 3.0276 | 0.0566 | 4.0102 | 3.3682 | 3.3401 | 1.0745 | 10.7268 | 14.2286 | 14.8286 | 11.0634 | 0.0001 | -0.0027 | 0.0008 | 0.0039 | 0.0004 | -0.0004 | 0.0089 | -0.0063 | -0.0075 | -360.1034 | 17.3905 | -360.4481 | 17.6389 | -360.8081 | 18.1728 | -360.7897 | 17.5445 | -352.5736 | 18.7025 | -352.6352 | 16.8505
12:33 | 4401 | 41.4656 | 202.3146 | 449.4161 | 456.3005 | -16.3101 | -40.9365 | 11.2153 | 7.8788 | 2.2903 | 0.4965 | 3.1542 | -0.9341 | 11.5024 | 4.3425 | 0.6171 | 0.6614 | 0.9582 | 0.7395 | -129.5674 | -0.6614 | 5.533 | 1.5706 | -3.1673 | -1.701 | 4.4043 |  | 2.972 | 0.0015 | 4.0093 | 3.3664 | 3.3364 | 1.0752 | 10.7105 | 14.2244 | 14.8273 | 11.0807 | 0.0001 | -0.0023 | 0.0009 | 0.0039 | 0.0015 | -0.0007 | 0.0154 | -0.0067 | 0.0099 | -360.1496 | 17.3864 | -360.4419 | 17.6204 | -360.7712 | 18.181 | -360.8604 | 17.5732 | -352.6106 | 18.7148 | -352.6383 | 16.8258
12:33 | 4402 | 41.4787 | 202.3342 | 449.4224 | 456.3073 | -16.376 | -40.9093 | 11.1306 | 7.8672 | 2.2013 | 0.4028 | 3.0932 | -0.9046 | 11.5604 | 4.3219 | 0.617 | 0.663 | 0.9594 | 0.7416 | -129.5526 | -0.5787 | 5.5666 | 1.4065 | -3.1667 | -1.5922 | 4.3715 |  | 3.0511 | 0.0083 | 4.0084 | 3.3639 | 3.3339 | 1.0731 | 10.7336 | 14.2938 | 14.8158 | 11.0518 | -0.0001 | -0.0027 | 0.0011 | 0.0043 | 0.0005 | -0.0001 | -0.0025 | 0.0022 | -0.0005 | -360.2111 | 17.4048 | -360.4696 | 17.6389 | -360.7835 | 18.1563 | -360.8297 | 17.5629 | -352.6383 | 18.7251 | -352.6506 | 16.832
12:33 | 4403 | 41.4495 | 202.2744 | 449.5767 | 456.2339 | -16.3916 | -40.9221 | 11.0844 | 7.8613 | 2.2568 | 0.3896 | 3.1312 | -0.8389 | 11.5367 | 4.3587 | 0.617 | 0.66 | 0.9603 | 0.7413 | -129.4959 | -0.5706 | 5.4877 | 1.5011 | -3.133 | -1.5132 | 4.384 |  | 3.0333 | 0.0277 | 4.0079 | 3.3655 | 3.3364 | 1.074 | 10.7475 | 14.2613 | 14.8638 | 11.0833 | 0.0002 | -0.003 | 0.0006 | 0.0034 | 0.001 | -0.0005 | -0.0014 | -0.0001 | -0.0119 | -360.1558 | 17.4172 | -360.4666 | 17.6471 | -360.8543 | 18.183 | -360.8512 | 17.5732 | -352.6383 | 18.723 | -352.6598 | 16.8525
12:33 | 4404 | 41.4535 | 202.1888 | 449.5713 | 456.3059 | -16.4835 | -41.057 | 11.0204 | 7.8989 | 2.3288 | 0.3742 | 3.2122 | -0.799 | 11.5533 | 4.3612 | 0.617 | 0.6584 | 0.9608 | 0.7402 | -129.6411 | -0.6615 | 5.4364 | 1.5474 | -3.172 | -1.5135 | 4.4887 |  | 3.0052 | 0.0544 | 4.0081 | 3.365 | 3.3358 | 1.0725 | 10.7174 | 14.2718 | 14.8461 | 11.0818 | 0.0001 | -0.0026 | 0.001 | 0.004 | 0.0005 | -0.0003 | 0.0286 | -0.0163 | -0.0109 | -360.2265 | 17.4274 | -360.4512 | 17.6348 | -360.8143 | 18.1851 | -360.8512 | 17.5917 | -352.6537 | 18.7415 | -352.6567 | 16.8258
12:33 | 4405 | 41.4263 | 202.3129 | 449.4818 | 456.3241 | -16.4382 | -40.9345 | 11.019 | 7.8145 | 2.2885 | 0.3384 | 3.0873 | -0.8263 | 11.544 | 4.3672 | 0.6179 | 0.6567 | 0.9617 | 0.7397 | -129.5752 | -0.5873 | 5.4207 | 1.5197 | -3.2067 | -1.5953 | 4.3557 |  | 2.997 | 0.0541 | 4.0078 | 3.3679 | 3.3364 | 1.0738 | 10.7683 | 14.2824 | 14.8631 | 11.0861 | -0.0003 | -0.0024 | 0.0006 | 0.0038 | 0.0009 | -0.0008 | 0.0047 | -0.0094 | 0.0043 | -360.1619 | 17.4356 | -360.4758 | 17.6697 | -360.8297 | 18.1769 | -360.8666 | 17.5855 | -352.6321 | 18.7518 | -352.6875 | 16.8464
12:33 | 4406 | 41.3358 | 202.2421 | 449.3629 | 456.293 | -16.473 | -41.0592 | 10.8996 | 7.863 | 2.3225 | 0.2723 | 3.1232 | -0.9112 | 11.5083 | 4.3021 | 0.6167 | 0.6588 | 0.9623 | 0.741 | -129.5055 | -0.545 | 5.4396 | 1.5259 | -3.2243 | -1.5292 | 4.401 |  | 2.9944 | 0.0476 | 4.0089 | 3.367 | 3.3389 | 1.0742 | 10.7337 | 14.2358 | 14.8379 | 11.0984 | -0.0002 | -0.0027 | 0.0008 | 0.0038 | 0.001 | -0.0002 | 0.0305 | -0.0193 | -0.0054 | -360.1773 | 17.4048 | -360.4819 | 17.6656 | -360.8358 | 18.1974 | -360.8727 | 17.5896 | -352.6352 | 18.7353 | -352.6413 | 16.8464
12:33 | 4407 | 41.4191 | 202.3665 | 449.4894 | 456.3046 | -16.466 | -40.9441 | 10.9744 | 7.8989 | 2.2995 | 0.4501 | 3.0733 | -0.9887 | 11.4978 | 4.2874 | 0.6166 | 0.6592 | 0.9611 | 0.7413 | -129.5318 | -0.606 | 5.5104 | 1.5717 | -3.1052 | -1.4735 | 4.3168 |  | 3.0421 | 0.0696 | 4.0092 | 3.3664 | 3.3331 | 1.0731 | 10.714 | 14.2508 | 14.812 | 11.0789 | 0.0002 | -0.0034 | 0.0011 | 0.0044 | 0.0009 | -0.0006 | 0.0093 | -0.0057 | -0.0005 | -360.2019 | 17.4192 | -360.5035 | 17.6553 | -360.8481 | 18.1892 | -360.8481 | 17.602 | -352.6844 | 18.7436 | -352.666 | 16.8546
12:33 | 4408 | 41.447 | 202.3172 | 449.5434 | 456.2893 | -16.4409 | -40.9861 | 11.1022 | 7.9612 | 2.3653 | 0.4396 | 3.1672 | -0.9735 | 11.4997 | 4.3011 | 0.6166 | 0.6632 | 0.961 | 0.7401 | -129.5913 | -0.5509 | 5.5152 | 1.5602 | -3.0892 | -1.461 | 4.3768 |  | 3.0559 | 0.1447 | 4.0085 | 3.3667 | 3.3346 | 1.0738 | 10.7452 | 14.2533 | 14.8447 | 11.0865 | -0.0001 | -0.0033 | 0.0007 | 0.0038 | 0.0006 | -0.0005 | 0.0203 | 0.01 | -0.0055 | -360.1988 | 17.4233 | -360.4666 | 17.6697 | -360.845 | 18.1871 | -360.8666 | 17.5691 | -352.629 | 18.7436 | -352.6967 | 16.8566
12:33 | 4409 | 41.458 | 202.3101 | 449.476 | 456.3196 | -16.4205 | -40.9146 | 11.0013 | 7.9722 | 2.2852 | 0.5556 | 3.1568 | -0.9202 | 11.4971 | 4.2974 | 0.6157 | 0.6596 | 0.9597 | 0.7399 | -129.532 | -0.5757 | 5.5507 | 1.7834 | -3.0741 | -1.5228 | 4.3614 |  | 3.0753 | 0.1862 | 4.0088 | 3.3636 | 3.3378 | 1.0751 | 10.7314 | 14.2391 | 14.8283 | 11.0793 | -0.0003 | -0.0027 | 0.0007 | 0.0039 | 0.0006 | -0.0009 | -0.0031 | -0.0051 | 0.0097 | -360.1742 | 17.4254 | -360.4604 | 17.6615 | -360.8604 | 18.1974 | -360.8697 | 17.5958 | -352.6629 | 18.7415 | -352.709 | 16.8505
12:33 | 4410 | 41.4259 | 202.2636 | 449.3494 | 456.3203 | -16.3849 | -40.8674 | 11.1002 | 7.9407 | 2.2855 | 0.5987 | 3.0373 | -0.9295 | 11.493 | 4.2743 | 0.6163 | 0.6618 | 0.961 | 0.7409 | -129.5789 | -0.5013 | 5.5337 | 1.6368 | -3.0616 | -1.5563 | 4.3351 |  | 3.1501 | 0.1795 | 4.01 | 3.3678 | 3.3372 | 1.0757 | 10.7476 | 14.2554 | 14.828 | 11.0952 | -0.0001 | -0.0026 | 0.0004 | 0.004 | 0.0011 | -0.0008 | 0.0186 | -0.0074 | -0.0024 | -360.1865 | 17.4151 | -360.4881 | 17.6533 | -360.8081 | 18.1851 | -360.8543 | 17.5855 | -352.6475 | 18.7353 | -352.6752 | 16.8546
12:33 | 4411 | 41.4509 | 202.2374 | 449.4099 | 456.2763 | -16.3575 | -40.8286 | 11.1242 | 7.8774 | 2.3161 | 0.5742 | 3.1319 | -0.88 | 11.4897 | 4.3251 | 0.6174 | 0.6593 | 0.9616 | 0.742 | -129.6136 | -0.5393 | 5.5532 | 1.675 | -3.1286 | -1.4284 | 4.3561 |  | 3.1033 | 0.0843 | 4.0097 | 3.3698 | 3.3344 | 1.0749 | 10.774 | 14.2827 | 14.8537 | 11.0912 | 0.0004 | -0.0028 | 0.0006 | 0.0034 | 0.0005 | -0.0001 | 0.0199 | -0.0015 | -0.0027 | -360.1896 | 17.4069 | -360.4819 | 17.6471 | -360.8204 | 18.1789 | -360.8543 | 17.5794 | -352.6537 | 18.7271 | -352.6844 | 16.8587
12:33 | 4412 | 41.4562 | 202.3095 | 449.5047 | 456.333 | -16.4437 | -40.8825 | 11.0879 | 7.8147 | 2.3048 | 0.5063 | 3.0797 | -0.9029 | 11.5161 | 4.2341 | 0.6182 | 0.6601 | 0.9593 | 0.7416 | -129.688 | -0.6775 | 5.4827 | 1.7576 | -3.1485 | -1.5178 | 4.3805 |  | 3.0736 | 0.0144 | 4.0108 | 3.3682 | 3.338 | 1.0741 | 10.7625 | 14.2764 | 14.8621 | 11.0749 | -0.0002 | -0.0032 | 0.001 | 0.0041 | 0.0012 | -0.0006 | 0.0103 | 0.0001 | -0.0157 | -360.1927 | 17.4028 | -360.4727 | 17.6553 | -360.7958 | 18.1851 | -360.8512 | 17.5835 | -352.6475 | 18.7312 | -352.6413 | 16.8361
12:33 | 4413 | 41.3864 | 202.252 | 449.4964 | 456.3502 | -16.4426 | -40.8436 | 11.0918 | 7.9121 | 2.3832 | 0.6154 | 3.1245 | -0.9083 | 11.5168 | 4.2766 | 0.6164 | 0.664 | 0.9652 | 0.7429 | -129.7218 | -0.7627 | 5.338 | 1.7922 | -3.0932 | -1.5215 | 4.3254 |  | 3.1142 | 0.0354 | 4.0094 | 3.3668 | 3.3361 | 1.0753 | 10.7486 | 14.2744 | 14.8846 | 11.124 | -0.0001 | -0.0026 | 0.0009 | 0.0039 | 0.0008 | 0 | 0.0084 | -0.0108 | -0.0208 | -360.1527 | 17.409 | -360.4666 | 17.6328 | -360.8235 | 18.1871 | -360.8327 | 17.5629 | -352.6383 | 18.7312 | -352.6783 | 16.8546
12:33 | 4414 | 41.4469 | 202.2503 | 449.481 | 456.3228 | -16.4799 | -40.8146 | 11.0061 | 7.8563 | 2.4595 | 0.5998 | 3.1391 | -0.8708 | 11.4467 | 4.3173 | 0.6152 | 0.6604 | 0.9593 | 0.7418 | -129.7354 | -0.6095 | 5.4152 | 1.7449 | -3.1371 | -1.5005 | 4.3529 |  | 3.0798 | 0.1356 | 4.0088 | 3.3656 | 3.3322 | 1.0742 | 10.7971 | 14.2828 | 14.8837 | 11.1312 | -0.0003 | -0.0028 | 0.0009 | 0.004 | 0.0011 | -0.0004 | 0.0145 | -0.0021 | 0.012 | -360.165 | 17.4069 | -360.4419 | 17.6328 | -360.8297 | 18.1789 | -360.8481 | 17.5753 | -352.6721 | 18.7292 | -352.6783 | 16.8587
12:33 | 4415 | 41.4486 | 202.3241 | 449.4603 | 456.2588 | -16.4296 | -40.8674 | 11.1039 | 7.8558 | 2.3726 | 0.5754 | 3.1665 | -0.8538 | 11.4864 | 4.3398 | 0.6158 | 0.6623 | 0.9621 | 0.7431 | -129.6565 | -0.507 | 5.5574 | 1.648 | -3.0809 | -1.5058 | 4.3312 |  | 3.0534 | 0.1737 | 4.0101 | 3.3686 | 3.3315 | 1.0756 | 10.7314 | 14.2739 | 14.8467 | 11.0847 | 0 | -0.0031 | 0.0003 | 0.0039 | 0.0008 | -0.0004 | 0.0075 | -0.0088 | 0.0032 | -360.1927 | 17.3987 | -360.4481 | 17.6348 | -360.7958 | 18.1789 | -360.8543 | 17.5794 | -352.6352 | 18.7189 | -352.666 | 16.8423
12:33 | 4416 | 41.4337 | 202.275 | 449.4353 | 456.2221 | -16.3897 | -40.7918 | 10.9698 | 7.8858 | 2.3223 | 0.5905 | 3.1922 | -0.8398 | 11.5407 | 4.3508 | 0.6165 | 0.6627 | 0.9639 | 0.7407 | -129.5743 | -0.5909 | 5.5225 | 1.5871 | -3.141 | -1.5532 | 4.3335 |  | 3.0813 | 0.1591 | 4.0101 | 3.3683 | 3.3355 | 1.0756 | 10.7371 | 14.2163 | 14.813 | 11.0786 | -0.0008 | -0.0034 | 0.0005 | 0.0039 | 0.0012 | -0.0002 | 0.0114 | -0.0131 | -0.0145 | -360.1804 | 17.3946 | -360.4358 | 17.6245 | -360.8235 | 18.183 | -360.8174 | 17.5691 | -352.6198 | 18.723 | -352.6413 | 16.8381
12:33 | 4417 | 41.4815 | 202.2623 | 449.4288 | 456.2953 | -16.417 | -40.8648 | 11.0775 | 7.8486 | 2.2852 | 0.4546 | 3.2099 | -0.7819 | 11.5011 | 4.2874 | 0.6166 | 0.6628 | 0.9661 | 0.7404 | -129.614 | -0.5241 | 5.5521 | 1.6137 | -3.1064 | -1.4802 | 4.3673 |  | 3.0276 | 0.1487 | 4.0083 | 3.3642 | 3.3327 | 1.0742 | 10.7314 | 14.2624 | 14.8351 | 11.0905 | -0.0002 | -0.0027 | 0.0006 | 0.0037 | 0.0007 | -0.0005 | 0.0161 | -0.0159 | 0.0047 | -360.1681 | 17.3946 | -360.4204 | 17.6102 | -360.7958 | 18.1769 | -360.842 | 17.565 | -352.6229 | 18.7107 | -352.669 | 16.834
12:33 | 4418 | 41.5154 | 202.248 | 449.4794 | 456.2577 | -16.3076 | -40.8943 | 10.9718 | 7.9061 | 2.3434 | 0.5159 | 3.2059 | -0.7951 | 11.6032 | 4.3166 | 0.616 | 0.6593 | 0.9636 | 0.7407 | -129.501 | -0.4288 | 5.6123 | 1.7099 | -3.0692 | -1.4496 | 4.4021 |  | 3.0181 | -0.0386 | 4.0089 | 3.3682 | 3.3356 | 1.0741 | 10.706 | 14.2194 | 14.8082 | 11.0598 | -0.0002 | -0.0028 | 0.0007 | 0.004 | 0.0008 | -0.0007 | 0.0278 | -0.0146 | -0.0071 | -360.1681 | 17.3946 | -360.4542 | 17.6122 | -360.7712 | 18.1707 | -360.8358 | 17.5671 | -352.6229 | 18.7169 | -352.6475 | 16.832
12:33 | 4419 | 41.4889 | 202.1803 | 449.478 | 456.2906 | -16.3178 | -40.9232 | 10.9919 | 7.9639 | 2.3713 | 0.6438 | 3.2776 | -0.8534 | 11.5406 | 4.3778 | 0.6158 | 0.6601 | 0.9636 | 0.7422 | -129.5826 | -0.4989 | 5.5531 | 1.6456 | -3.1221 | -1.4901 | 4.3759 |  | 2.9609 | -0.0192 | 4.0094 | 3.3658 | 3.337 | 1.0745 | 10.7601 | 14.2572 | 14.8683 | 11.0948 | 0.0004 | -0.0027 | 0.0013 | 0.0042 | 0.001 | -0.0003 | 0.0185 | -0.0017 | -0.0073 | -360.1681 | 17.3843 | -360.4142 | 17.6225 | -360.762 | 18.1625 | -360.8266 | 17.5609 | -352.586 | 18.6963 | -352.6229 | 16.8402
12:33 | 4420 | 41.4891 | 202.1746 | 449.5171 | 456.3389 | -16.3401 | -40.8583 | 11.1468 | 8.0175 | 2.332 | 0.6696 | 3.2876 | -0.883 | 11.4956 | 4.4338 | 0.6155 | 0.6586 | 0.96 | 0.7418 | -129.5647 | -0.4856 | 5.6055 | 1.628 | -3.1124 | -1.5232 | 4.3588 |  | 3.0645 | 0.104 | 4.0105 | 3.3642 | 3.3348 | 1.0747 | 10.7694 | 14.2664 | 14.8598 | 11.0811 | 0.0003 | -0.0028 | 0.0012 | 0.0042 | 0.0007 | -0.0004 | 0.024 | -0.0027 | -0.0078 | -360.1558 | 17.3905 | -360.4266 | 17.5999 | -360.7958 | 18.1707 | -360.8235 | 17.565 | -352.5983 | 18.7025 | -352.6075 | 16.8361
12:33 | 4421 | 41.4668 | 202.2166 | 449.5264 | 456.3773 | -16.3404 | -40.9349 | 11.0413 | 7.8996 | 2.244 | 0.4513 | 3.2063 | -0.8384 | 11.5397 | 4.3923 | 0.616 | 0.66 | 0.9623 | 0.7418 | -129.5662 | -0.5453 | 5.5968 | 1.645 | -3.0711 | -1.4386 | 4.4009 |  | 3.0718 | 0.0851 | 4.0096 | 3.3672 | 3.3356 | 1.0733 | 10.7533 | 14.2673 | 14.8706 | 11.106 | 0 | -0.0026 | 0.001 | 0.0045 | 0.0006 | -0.0008 | -0.0002 | -0.0055 | -0.0073 | -360.1496 | 17.3925 | -360.4327 | 17.6143 | -360.7773 | 18.1563 | -360.7773 | 17.5547 | -352.5829 | 18.7169 | -352.6413 | 16.8361
12:33 | 4422 | 41.509 | 202.2575 | 449.5281 | 456.3454 | -16.3954 | -40.8767 | 11.0547 | 7.8192 | 2.2175 | 0.6272 | 3.2122 | -0.8661 | 11.5278 | 4.4123 | 0.6171 | 0.6635 | 0.9609 | 0.7427 | -129.5862 | -0.6694 | 5.5256 | 1.6432 | -3.0963 | -1.4365 | 4.3573 |  | 3.0376 | 0.1268 | 4.0106 | 3.3645 | 3.338 | 1.0745 | 10.7901 | 14.2932 | 14.8823 | 11.1128 | 0.0001 | -0.0021 | 0.0008 | 0.0036 | 0.0008 | -0.0001 | 0.0187 | -0.0124 | -0.018 | -360.1404 | 17.374 | -360.4296 | 17.6184 | -360.7773 | 18.1769 | -360.8174 | 17.5732 | -352.626 | 18.7004 | -352.626 | 16.8361
12:33 | 4423 | 41.6205 | 202.1984 | 449.6067 | 456.3699 | -16.3483 | -40.8852 | 11.0877 | 7.8436 | 2.2676 | 0.5827 | 3.2069 | -0.9173 | 11.5577 | 4.3728 | 0.6149 | 0.6641 | 0.9594 | 0.742 | -129.6557 | -0.4746 | 5.5317 | 1.7366 | -3.1146 | -1.4765 | 4.3595 |  | 3.0801 | 0.1629 | 4.0099 | 3.3649 | 3.3376 | 1.074 | 10.7568 | 14.2704 | 14.8194 | 11.0988 | 0.0002 | -0.0028 | 0.0004 | 0.0038 | 0.0009 | -0.0008 | 0.0192 | -0.0231 | -0.0087 | -360.1711 | 17.3884 | -360.4142 | 17.6061 | -360.7497 | 18.1645 | -360.7958 | 17.5794 | -352.5921 | 18.7066 | -352.6413 | 16.8299
12:33 | 4424 | 41.583 | 202.2071 | 449.5091 | 456.3839 | -16.3607 | -40.9013 | 11.089 | 7.8317 | 2.3012 | 0.6417 | 3.177 | -0.9486 | 11.518 | 4.3612 | 0.6154 | 0.6608 | 0.9561 | 0.7415 | -129.5891 | -0.4035 | 5.5127 | 1.7223 | -3.1629 | -1.4378 | 4.2808 |  | 3.027 | 0.0429 | 4.0094 | 3.365 | 3.333 | 1.0743 | 10.7071 | 14.238 | 14.8222 | 11.0721 | 0.0003 | -0.0032 | 0.0004 | 0.004 | 0.0007 | -0.0003 | 0.018 | -0.0126 | -0.0131 | -360.1219 | 17.3946 | -360.4296 | 17.6328 | -360.8143 | 18.1769 | -360.7958 | 17.5588 | -352.6013 | 18.7066 | -352.6321 | 16.8381
12:33 | 4425 | 41.5524 | 202.2975 | 449.5256 | 456.3604 | -16.227 | -40.8112 | 11.134 | 7.828 | 2.3473 | 0.5659 | 3.1073 | -0.8862 | 11.5588 | 4.3716 | 0.6173 | 0.6604 | 0.9606 | 0.7425 | -129.618 | -0.3819 | 5.6397 | 1.7084 | -3.2057 | -1.5608 | 4.2138 |  | 3.0562 | -0.0155 | 4.0096 | 3.3676 | 3.3391 | 1.0747 | 10.7406 | 14.2601 | 14.8334 | 11.0822 | 0.0001 | -0.0027 | 0.0004 | 0.0038 | 0.0008 | -0.0006 | 0.0108 | -0.024 | -0.0137 | -360.1311 | 17.3679 | -360.405 | 17.6184 | -360.7373 | 18.183 | -360.8389 | 17.5671 | -352.6013 | 18.6984 | -352.6075 | 16.8238
12:33 | 4426 | 41.5206 | 202.2407 | 449.4515 | 456.3399 | -16.1811 | -40.7231 | 11.2282 | 7.7859 | 2.2212 | 0.5885 | 3.2297 | -0.855 | 11.5333 | 4.4074 | 0.6168 | 0.6593 | 0.959 | 0.7421 | -129.7347 | -0.4841 | 5.575 | 1.8524 | -3.1275 | -1.5077 | 4.2993 |  | 3.0531 | 0.0246 | 4.0115 | 3.3678 | 3.3379 | 1.0752 | 10.7592 | 14.2495 | 14.8443 | 11.0378 | -0.0002 | -0.0027 | 0.0008 | 0.0036 | 0.0007 | 0.0001 | 0.0124 | -0.0111 | -0.0003 | -360.1835 | 17.3987 | -360.4266 | 17.6348 | -360.7804 | 18.1687 | -360.7989 | 17.5588 | -352.5952 | 18.7107 | -352.6198 | 16.834
12:33 | 4427 | 41.5053 | 202.1856 | 449.4289 | 456.2853 | -16.2311 | -40.689 | 11.3388 | 7.7894 | 2.2024 | 0.5631 | 3.1945 | -0.8813 | 11.5603 | 4.3848 | 0.6156 | 0.6565 | 0.9615 | 0.7405 | -129.665 | -0.4464 | 5.5655 | 1.7191 | -3.1079 | -1.488 | 4.3231 |  | 3.1372 | 0.1731 | 4.0116 | 3.3652 | 3.3346 | 1.075 | 10.7533 | 14.2326 | 14.859 | 11.0771 | 0 | -0.0028 | 0.0012 | 0.0037 | 0.0009 | -0.0013 | 0.0211 | -0.0044 | -0.023 | -360.1096 | 17.3782 | -360.4296 | 17.6348 | -360.8081 | 18.1994 | -360.8358 | 17.5465 | -352.5952 | 18.7004 | -352.6229 | 16.8423
12:34 | 4428 | 41.5347 | 202.2589 | 449.4383 | 456.3429 | -16.1915 | -40.7195 | 11.342 | 7.7666 | 2.1926 | 0.5665 | 3.207 | -0.9332 | 11.4883 | 4.3286 | 0.616 | 0.66 | 0.9608 | 0.7418 | -129.7151 | -0.5089 | 5.4781 | 1.7108 | -3.1563 | -1.5562 | 4.2607 |  | 3.1161 | 0.1207 | 4.0104 | 3.3659 | 3.3347 | 1.0732 | 10.7383 | 14.2693 | 14.8654 | 11.1031 | 0.0003 | -0.0031 | 0.0005 | 0.0035 | 0.0002 | -0.0005 | 0.0058 | -0.012 | -0.0236 | -360.1527 | 17.3864 | -360.4081 | 17.6081 | -360.7743 | 18.183 | -360.8112 | 17.5568 | -352.6013 | 18.6963 | -352.6106 | 16.8197
12:34 | 4429 | 41.5939 | 202.2987 | 449.5645 | 456.3075 | -16.2325 | -40.61 | 11.3341 | 7.7347 | 2.1344 | 0.4592 | 3.148 | -0.9943 | 11.5092 | 4.3958 | 0.6156 | 0.6557 | 0.9592 | 0.7402 | -129.6189 | -0.4567 | 5.5036 | 1.7947 | -3.1297 | -1.5565 | 4.2701 |  | 3.016 | 0.1883 | 4.0114 | 3.3656 | 3.339 | 1.0762 | 10.774 | 14.2825 | 14.87 | 11.08 | -0.0002 | -0.0029 | 0.001 | 0.004 | 0.001 | -0.0003 | 0.0123 | -0.01 | -0.009 | -360.125 | 17.3925 | -360.4512 | 17.6533 | -360.7866 | 18.183 | -360.805 | 17.5424 | -352.6136 | 18.7045 | -352.6598 | 16.8505
12:34 | 4430 | 41.5717 | 202.2443 | 449.4743 | 456.2754 | -16.2853 | -40.6209 | 11.2451 | 7.8115 | 2.0989 | 0.4312 | 3.0509 | -0.9065 | 11.6186 | 4.5157 | 0.6155 | 0.659 | 0.9633 | 0.7416 | -129.6819 | -0.5301 | 5.446 | 1.741 | -3.1782 | -1.5205 | 4.3118 |  | 3.0774 | 0.1633 | 4.0115 | 3.3664 | 3.3358 | 1.076 | 10.7694 | 14.3242 | 14.8945 | 11.1042 | -0.0003 | -0.0028 | 0.0007 | 0.0036 | 0.0005 | -0.0005 | 0.0095 | -0.0069 | -0.0208 | -360.1435 | 17.3617 | -360.3742 | 17.6184 | -360.7927 | 18.1953 | -360.845 | 17.5588 | -352.6013 | 18.6963 | -352.5767 | 16.834
12:34 | 4431 | 41.5721 | 202.2818 | 449.5261 | 456.3229 | -16.3131 | -40.5705 | 11.217 | 7.8553 | 2.1394 | 0.3685 | 3.1269 | -0.911 | 11.5681 | 4.379 | 0.6154 | 0.6627 | 0.9652 | 0.742 | -129.6869 | -0.5369 | 5.4975 | 1.6619 | -3.2181 | -1.791 | 4.3105 |  | 3.1163 | 0.1821 | 4.0123 | 3.366 | 3.3385 | 1.0755 | 10.7902 | 14.2871 | 14.8513 | 11.0789 | -0.0003 | -0.0028 | 0 | 0.0035 | 0.0011 | -0.0002 | 0.0026 | -0.0195 | -0.0175 | -360.2081 | 17.4131 | -360.4358 | 17.6348 | -360.7835 | 18.1748 | -360.8081 | 17.5486 | -352.6352 | 18.723 | -352.6413 | 16.8402
12:34 | 4432 | 41.4835 | 202.2897 | 449.5438 | 456.2893 | -16.2571 | -40.5368 | 11.2131 | 7.7927 | 2.1333 | 0.484 | 3.1023 | -0.9977 | 11.5544 | 4.4505 | 0.6168 | 0.6625 | 0.9619 | 0.7414 | -129.6109 | -0.5314 | 5.5836 | 1.6739 | -3.117 | -1.4864 | 4.3501 |  | 3.0446 | 0.0735 | 4.0117 | 3.3669 | 3.3364 | 1.0752 | 10.7314 | 14.2508 | 14.812 | 11.0847 | 0.0002 | -0.0031 | 0.0008 | 0.0043 | 0.0007 | -0.0012 | 0.0249 | 0.0007 | -0.005 | -360.1004 | 17.3782 | -360.4389 | 17.6451 | -360.7989 | 18.2015 | -360.8389 | 17.5404 | -352.6383 | 18.7087 | -352.6629 | 16.8505
12:34 | 4433 | 41.5146 | 202.278 | 449.5017 | 456.2931 | -16.2839 | -40.5556 | 11.3137 | 7.7191 | 2.0823 | 0.4754 | 3.146 | -0.9933 | 11.4738 | 4.3679 | 0.6159 | 0.6609 | 0.9637 | 0.7402 | -129.641 | -0.4971 | 5.5484 | 1.7672 | -3.0833 | -1.5664 | 4.2689 |  | 2.9822 | 0.0314 | 4.0108 | 3.367 | 3.3391 | 1.076 | 10.7418 | 14.2612 | 14.799 | 11.0779 | -0.0001 | -0.0033 | 0.0005 | 0.0035 | 0.0003 | -0.0005 | 0.0132 | -0.009 | 0.0118 | -360.1804 | 17.3946 | -360.405 | 17.6266 | -360.7527 | 18.1871 | -360.8604 | 17.5773 | -352.6352 | 18.7128 | -352.6352 | 16.8238
12:34 | 4434 | 41.5642 | 202.3301 | 449.4934 | 456.3485 | -16.3128 | -40.5603 | 11.2477 | 7.7756 | 2.0461 | 0.4214 | 3.1363 | -0.9051 | 11.5964 | 4.4222 | 0.6155 | 0.6567 | 0.9654 | 0.74 | -129.6174 | -0.4682 | 5.7057 | 1.7969 | -3.0241 | -1.5233 | 4.3437 |  | 3.0432 | 0.08 | 4.0101 | 3.3679 | 3.3374 | 1.0762 | 10.7209 | 14.2346 | 14.8423 | 11.0569 | -0.0003 | -0.0025 | 0.0008 | 0.0036 | 0.001 | -0.0011 | 0.0216 | -0.0165 | -0.0087 | -360.1373 | 17.4007 | -360.5004 | 17.6697 | -360.8297 | 18.1974 | -360.8143 | 17.5383 | -352.6321 | 18.7251 | -352.706 | 16.8731
12:34 | 4435 | 41.6245 | 202.3435 | 449.5468 | 456.3277 | -16.3563 | -40.604 | 11.2928 | 7.843 | 2.1169 | 0.3676 | 3.0997 | -0.9197 | 11.6048 | 4.4181 | 0.616 | 0.6618 | 0.964 | 0.7404 | -129.6258 | -0.4541 | 5.595 | 1.8006 | -3.0455 | -1.5225 | 4.33 |  | 2.971 | -0.0034 | 4.0111 | 3.364 | 3.3341 | 1.0751 | 10.7405 | 14.2603 | 14.8577 | 11.1049 | -0.0003 | -0.0031 | 0.0015 | 0.0042 | 0.0007 | -0.0004 | 0.0013 | -0.0052 | -0.0056 | -360.1558 | 17.3802 | -360.405 | 17.6184 | -360.8204 | 18.2118 | -360.8635 | 17.5712 | -352.6352 | 18.7025 | -352.6198 | 16.8484
12:34 | 4436 | 41.564 | 202.2891 | 449.5635 | 456.2766 | -16.2851 | -40.6673 | 11.2729 | 7.7497 | 2.1105 | 0.2306 | 3.1366 | -0.9797 | 11.5384 | 4.339 | 0.6182 | 0.6584 | 0.964 | 0.7412 | -129.6578 | -0.4406 | 5.5514 | 1.7989 | -3.0587 | -1.5173 | 4.3334 |  | 3.0232 | 0.0737 | 4.0118 | 3.3694 | 3.3384 | 1.0753 | 10.7463 | 14.2603 | 14.8287 | 11.076 | 0.0002 | -0.003 | 0.0009 | 0.0037 | 0.0012 | -0.0005 | 0.0106 | -0.0189 | 0.0094 | -360.1804 | 17.4192 | -360.4635 | 17.6286 | -360.7835 | 18.1871 | -360.802 | 17.5671 | -352.6506 | 18.7395 | -352.669 | 16.8443
12:34 | 4437 | 41.6843 | 202.2481 | 449.6495 | 456.3937 | -16.4268 | -40.6673 | 11.2269 | 7.8812 | 2.1437 | 0.342 | 3.1499 | -1.0048 | 11.4842 | 4.3527 | 0.616 | 0.6602 | 0.9624 | 0.7407 | -129.6173 | -0.4201 | 5.5229 | 1.8161 | -3.0487 | -1.4261 | 4.373 |  | 3.0233 | 0.0663 | 4.0106 | 3.3664 | 3.336 | 1.0746 | 10.7648 | 14.2732 | 14.8543 | 11.0998 | 0.0003 | -0.0031 | 0.0013 | 0.0045 | 0.0008 | -0.0002 | -0.0091 | -0.0087 | 0.0064 | -360.1096 | 17.3823 | -360.4419 | 17.641 | -360.8143 | 18.2077 | -360.8204 | 17.5383 | -352.6044 | 18.7128 | -352.629 | 16.8648
12:34 | 4438 | 41.6397 | 202.2992 | 449.6518 | 456.3619 | -16.3576 | -40.6585 | 11.1552 | 7.8673 | 2.1934 | 0.3482 | 3.1442 | -0.9693 | 11.4635 | 4.3996 | 0.6156 | 0.6612 | 0.9651 | 0.7409 | -129.7027 | -0.4612 | 5.5701 | 1.8112 | -2.9766 | -1.4033 | 4.3737 |  | 3.0895 | 0.1218 | 4.0104 | 3.3656 | 3.3376 | 1.0749 | 10.7601 | 14.2628 | 14.8267 | 11.1183 | -0.0005 | -0.0028 | 0.0004 | 0.0037 | 0.0011 | 0 | 0.0047 | -0.0198 | -0.0025 | -360.1896 | 17.3864 | -360.4204 | 17.6122 | -360.7743 | 18.2015 | -360.8635 | 17.5855 | -352.6629 | 18.7189 | -352.6136 | 16.8197
12:34 | 4439 | 41.5902 | 202.3301 | 449.5955 | 456.2662 | -16.3869 | -40.7122 | 11.3058 | 7.8969 | 2.142 | 0.3141 | 3.1193 | -0.9457 | 11.4684 | 4.3801 | 0.6176 | 0.662 | 0.9648 | 0.7399 | -129.6803 | -0.4812 | 5.6152 | 1.7387 | -3.0615 | -1.3946 | 4.3919 |  | 3.0813 | 0.0755 | 4.0106 | 3.3634 | 3.3353 | 1.075 | 10.7809 | 14.3012 | 14.8898 | 11.1558 | -0.0002 | -0.0024 | 0.0002 | 0.0037 | 0.0007 | -0.0003 | 0.0065 | -0.004 | -0.0113 | -360.1435 | 17.411 | -360.4819 | 17.6553 | -360.8327 | 18.1687 | -360.7558 | 17.5465 | -352.6229 | 18.7312 | -352.6906 | 16.8648
12:34 | 4440 | 41.6364 | 202.4274 | 449.6464 | 456.3699 | -16.3965 | -40.6592 | 11.107 | 7.9497 | 2.199 | 0.3357 | 3.1534 | -1.0106 | 11.5454 | 4.3622 | 0.6172 | 0.6635 | 0.9657 | 0.7415 | -129.653 | -0.5268 | 5.488 | 1.7235 | -3.0503 | -1.4901 | 4.352 |  | 3.0388 | -0.0007 | 4.0093 | 3.3651 | 3.336 | 1.0755 | 10.7118 | 14.2539 | 14.8013 | 11.0544 | 0.0001 | -0.0031 | 0.0004 | 0.0038 | 0.0007 | -0.0008 | -0.0018 | -0.0186 | 0.0022 | -360.125 | 17.3679 | -360.3896 | 17.6266 | -360.8174 | 18.2159 | -360.8635 | 17.5629 | -352.5798 | 18.6943 | -352.6167 | 16.8443
12:34 | 4441 | 41.6116 | 202.3112 | 449.6751 | 456.358 | -16.3518 | -40.7027 | 11.1534 | 7.9127 | 2.1303 | 0.4196 | 3.1452 | -0.9384 | 11.5046 | 4.4112 | 0.6156 | 0.6613 | 0.9621 | 0.7417 | -129.6601 | -0.5573 | 5.5405 | 1.7639 | -3.0678 | -1.5121 | 4.3275 |  | 3.0481 | 0.1366 | 4.0109 | 3.3628 | 3.3368 | 1.076 | 10.7393 | 14.2361 | 14.8342 | 11.0861 | 0.0002 | -0.0029 | 0.0008 | 0.0038 | 0.0009 | -0.0001 | 0.0171 | -0.0013 | -0.0084 | -360.2235 | 17.4048 | -360.4573 | 17.6122 | -360.762 | 18.1728 | -360.7927 | 17.5568 | -352.6783 | 18.7374 | -352.6475 | 16.8176
12:34 | 4442 | 41.6148 | 202.2631 | 449.5837 | 456.407 | -16.3372 | -40.761 | 11.0927 | 7.9157 | 2.0989 | 0.3332 | 3.1754 | -0.9157 | 11.5686 | 4.3899 | 0.6168 | 0.6618 | 0.9648 | 0.7423 | -129.6017 | -0.5251 | 5.5726 | 1.7639 | -3.1065 | -1.4471 | 4.3211 |  | 2.9883 | 0.111 | 4.01 | 3.3654 | 3.3353 | 1.0758 | 10.7314 | 14.2624 | 14.8525 | 11.102 | 0 | -0.0028 | 0.0008 | 0.0037 | 0.0004 | -0.0011 | 0.0031 | -0.0099 | 0.0052 | -360.1188 | 17.3823 | -360.4696 | 17.643 | -360.802 | 18.1892 | -360.7989 | 17.526 | -352.5644 | 18.7107 | -352.6506 | 16.8546
12:34 | 4443 | 41.526 | 202.2827 | 449.6091 | 456.3321 | -16.2375 | -40.5965 | 11.2311 | 7.9632 | 2.2646 | 0.49 | 3.211 | -0.7894 | 11.5776 | 4.392 | 0.6155 | 0.6632 | 0.9632 | 0.7415 | -129.6588 | -0.5103 | 5.4956 | 1.7764 | -3.0418 | -1.4302 | 4.3065 |  | 3.0317 | 0.0862 | 4.0106 | 3.3662 | 3.3363 | 1.0751 | 10.7405 | 14.2429 | 14.8519 | 11.0818 | -0.0001 | -0.0027 | 0.0015 | 0.0047 | 0.0013 | -0.0001 | 0.0164 | 0.0018 | -0.0196 | -360.1773 | 17.3761 | -360.3865 | 17.5999 | -360.7743 | 18.1953 | -360.8574 | 17.5794 | -352.6136 | 18.7045 | -352.5952 | 16.8135
12:34 | 4444 | 41.624 | 202.355 | 449.684 | 456.5007 | -16.3506 | -40.6287 | 11.2428 | 7.8827 | 2.2955 | 0.5948 | 3.2309 | -0.9247 | 11.5376 | 4.4337 | 0.6145 | 0.6651 | 0.9631 | 0.7411 | -129.6242 | -0.4656 | 5.5676 | 1.6653 | -3.1985 | -1.4204 | 4.3645 |  | 2.9905 | 0.1008 | 4.0085 | 3.3628 | 3.3393 | 1.0756 | 10.767 | 14.2757 | 14.8523 | 11.0958 | 0.0004 | -0.0026 | 0.0007 | 0.0036 | 0.0006 | -0.0005 | 0.0106 | -0.016 | 0.0011 | -360.1742 | 17.4007 | -360.4758 | 17.6389 | -360.7712 | 18.1728 | -360.7866 | 17.5383 | -352.5983 | 18.7436 | -352.6721 | 16.8361
12:34 | 4445 | 41.5998 | 202.3066 | 449.51 | 456.3356 | -16.3536 | -40.8368 | 11.1512 | 7.9869 | 2.2888 | 0.5898 | 3.2554 | -0.9725 | 11.4862 | 4.3796 | 0.6157 | 0.6634 | 0.9656 | 0.7398 | -129.6686 | -0.578 | 5.5585 | 1.7188 | -3.1574 | -1.6778 | 4.2504 |  | 3.0106 | 0.0637 | 4.0102 | 3.3663 | 3.3377 | 1.0755 | 10.7938 | 14.2844 | 14.9216 | 11.1179 | 0.0001 | -0.0031 | 0.0004 | 0.0037 | 0.0007 | -0.001 | 0.0125 | -0.0058 | 0.0158 | -360.1435 | 17.3699 | -360.4112 | 17.6328 | -360.8081 | 18.2118 | -360.8574 | 17.5424 | -352.5706 | 18.7025 | -352.6013 | 16.834
12:34 | 4446 | 41.5676 | 202.3131 | 449.4778 | 456.3346 | -16.2983 | -40.7063 | 11.1906 | 7.9436 | 2.3313 | 0.6396 | 3.2204 | -0.9793 | 11.5072 | 4.3852 | 0.6156 | 0.6599 | 0.963 | 0.7407 | -129.6323 | -0.4852 | 5.4703 | 1.6901 | -3.149 | -1.5071 | 4.2404 |  | 3.0184 | 0.067 | 4.0105 | 3.3671 | 3.3355 | 1.0764 | 10.7659 | 14.2744 | 14.8904 | 11.124 | -0.0002 | -0.0026 | 0.0008 | 0.0041 | 0.0007 | -0.0003 | 0.0217 | -0.0161 | -0.0048 | -360.2204 | 17.4131 | -360.4358 | 17.604 | -360.7835 | 18.1707 | -360.8297 | 17.5753 | -352.6413 | 18.7333 | -352.626 | 16.8012
12:34 | 4447 | 41.5443 | 202.3346 | 449.4964 | 456.2519 | -16.3092 | -40.6519 | 11.1795 | 7.8253 | 2.3075 | 0.6152 | 3.1509 | -0.887 | 11.5484 | 4.3984 | 0.6169 | 0.664 | 0.9639 | 0.7407 | -129.6937 | -0.4643 | 5.4534 | 1.7431 | -3.1329 | -1.4534 | 4.2703 |  | 3.0073 | 0.1172 | 4.0109 | 3.3656 | 3.3352 | 1.0757 | 10.7533 | 14.2671 | 14.8638 | 11.0717 | -0.0005 | -0.0026 | 0.0002 | 0.0034 | 0.0011 | -0.0006 | 0.0116 | -0.0061 | 0.0012 | -360.1435 | 17.4131 | -360.5066 | 17.6656 | -360.8635 | 18.2036 | -360.802 | 17.5301 | -352.629 | 18.7312 | -352.6813 | 16.871
12:34 | 4448 | 41.665 | 202.3128 | 449.5971 | 456.3315 | -16.3999 | -40.6711 | 11.1948 | 7.8157 | 2.2821 | 0.5762 | 3.1425 | -0.9528 | 11.5317 | 4.3805 | 0.6145 | 0.6624 | 0.9631 | 0.7417 | -129.7207 | -0.4622 | 5.507 | 1.7663 | -3.1682 | -1.5639 | 4.294 |  | 3.008 | 0.0294 | 4.0114 | 3.368 | 3.3362 | 1.0754 | 10.7222 | 14.2297 | 14.8415 | 11.0703 | -0.0001 | -0.0028 | 0.0008 | 0.004 | 0.0007 | -0.0002 | 0.0041 | -0.0123 | -0.0037 | -360.1865 | 17.3864 | -360.4112 | 17.6266 | -360.7866 | 18.2159 | -360.8881 | 17.5835 | -352.6629 | 18.7148 | -352.5921 | 16.8074
12:34 | 4449 | 41.5993 | 202.1968 | 449.4921 | 456.2133 | -16.3141 | -40.6116 | 11.2296 | 7.7659 | 2.3556 | 0.51 | 3.1395 | -0.8622 | 11.5296 | 4.3819 | 0.6165 | 0.6593 | 0.9623 | 0.7421 | -129.6846 | -0.4422 | 5.5323 | 1.8654 | -3.094 | -1.4219 | 4.4224 |  | 3.0364 | 0.1229 | 4.011 | 3.3666 | 3.331 | 1.0749 | 10.7417 | 14.2557 | 14.8243 | 11.0424 | 0.0001 | -0.003 | 0.0011 | 0.0043 | 0.001 | -0.0002 | 0.0046 | 0.0031 | -0.0098 | -360.2142 | 17.4562 | -360.5343 | 17.6677 | -360.8297 | 18.1871 | -360.8174 | 17.5712 | -352.6752 | 18.7682 | -352.706 | 16.8607
12:34 | 4450 | 41.5869 | 202.2937 | 449.5755 | 456.1667 | -16.2687 | -40.6348 | 11.205 | 7.7655 | 2.3386 | 0.3719 | 3.0955 | -0.8221 | 11.5523 | 4.4191 | 0.6163 | 0.6625 | 0.963 | 0.7381 | -129.6886 | -0.4797 | 5.5418 | 1.7542 | -3.1101 | -1.4417 | 4.3476 |  | 3.0451 | 0.1699 | 4.0112 | 3.3672 | 3.3385 | 1.0763 | 10.7166 | 14.2409 | 14.8383 | 11.0426 | -0.0002 | -0.0032 | 0.0007 | 0.0035 | 0 | -0.001 | 0.0037 | -0.0042 | -0.0201 | -360.1681 | 17.4007 | -360.4481 | 17.6718 | -360.8881 | 18.2426 | -360.8789 | 17.5712 | -352.626 | 18.7251 | -352.6567 | 16.8628
12:34 | 4451 | 41.5494 | 202.1553 | 449.4919 | 456.2076 | -16.2776 | -40.6966 | 11.1862 | 7.7564 | 2.2655 | 0.3847 | 3.0598 | -0.8289 | 11.6084 | 4.4453 | 0.6158 | 0.6637 | 0.9633 | 0.7383 | -129.6849 | -0.522 | 5.4955 | 1.7109 | -3.1324 | -1.5611 | 4.3629 |  | 3.0538 | 0.1581 | 4.0101 | 3.3706 | 3.3345 | 1.0754 | 10.7359 | 14.2441 | 14.8648 | 11.0655 | -0.0002 | -0.0026 | 0.0012 | 0.0041 | 0.0008 | -0.0006 | 0.0166 | -0.0111 | -0.0115 | -360.2173 | 17.4439 | -360.4727 | 17.6307 | -360.7989 | 18.1871 | -360.8574 | 17.5978 | -352.6998 | 18.7723 | -352.6783 | 16.8279
12:34 | 4452 | 41.6029 | 202.2425 | 449.4436 | 456.2064 | -16.4482 | -40.6598 | 11.2242 | 7.7794 | 2.2295 | 0.5148 | 3.1054 | -0.832 | 11.5904 | 4.3994 | 0.6148 | 0.6643 | 0.9623 | 0.7387 | -129.7415 | -0.5274 | 5.5303 | 1.8583 | -3.055 | -1.4277 | 4.4267 |  | 3.1414 | 0.0988 | 4.0097 | 3.3715 | 3.3357 | 1.0753 | 10.7672 | 14.2695 | 14.8549 | 11.0681 | 0 | -0.0028 | 0.0007 | 0.0037 | 0.0008 | -0.0009 | 0.0036 | -0.0182 | -0.0209 | -360.1404 | 17.4028 | -360.5035 | 17.6718 | -360.8727 | 18.2118 | -360.8143 | 17.5465 | -352.6198 | 18.7456 | -352.706 | 16.8813
12:34 | 4453 | 41.5315 | 202.2589 | 449.4952 | 456.2316 | -16.3784 | -40.6201 | 11.3091 | 7.7545 | 2.2727 | 0.6207 | 3.1336 | -0.8524 | 11.6856 | 4.4544 | 0.615 | 0.6635 | 0.9622 | 0.7393 | -129.6296 | -0.5115 | 5.5504 | 1.8432 | -3.0565 | -1.3956 | 4.4553 |  | 3.1223 | 0.234 | 4.0112 | 3.3687 | 3.3381 | 1.0751 | 10.7671 | 14.2581 | 14.8849 | 11.0908 | 0.0002 | -0.0031 | 0.0006 | 0.0038 | 0.0008 | -0.0004 | 0.0135 | -0.0072 | -0.0098 | -360.1742 | 17.3802 | -360.4019 | 17.5978 | -360.7527 | 18.222 | -360.8789 | 17.5876 | -352.6475 | 18.7087 | -352.6229 | 16.8176
12:34 | 4454 | 41.5811 | 202.2235 | 449.4477 | 456.2098 | -16.408 | -40.6692 | 11.3418 | 7.825 | 2.2769 | 0.5498 | 3.1729 | -0.844 | 11.7217 | 4.4465 | 0.6143 | 0.6653 | 0.9623 | 0.7409 | -129.6714 | -0.4506 | 5.5308 | 1.775 | -3.1482 | -1.4476 | 4.3968 |  | 3.0509 | 0.2187 | 4.0106 | 3.3661 | 3.3343 | 1.0751 | 10.7578 | 14.2604 | 14.8471 | 11.0872 | 0.0001 | -0.0028 | 0.0008 | 0.0044 | 0.0007 | -0.0006 | 0.0067 | -0.0064 | -0.0023 | -360.1896 | 17.4151 | -360.4696 | 17.6389 | -360.7866 | 18.1543 | -360.7712 | 17.5363 | -352.6136 | 18.7436 | -352.6998 | 16.8381
12:34 | 4455 | 41.5983 | 202.2214 | 449.47 | 456.1798 | -16.3733 | -40.6364 | 11.2501 | 7.7828 | 2.2727 | 0.473 | 3.148 | -0.7968 | 11.6592 | 4.3957 | 0.6154 | 0.6646 | 0.9637 | 0.741 | -129.6389 | -0.4329 | 5.6562 | 1.8242 | -3.1112 | -1.4391 | 4.3273 |  | 3.017 | 0.1956 | 4.0113 | 3.3691 | 3.3351 | 1.0757 | 10.7556 | 14.2868 | 14.8549 | 11.0796 | -0.0005 | -0.0025 | 0.0004 | 0.0038 | 0.0002 | -0.0004 | 0.0022 | -0.004 | -0.01 | -360.1219 | 17.3535 | -360.3989 | 17.6204 | -360.8112 | 18.222 | -360.8604 | 17.5445 | -352.586 | 18.6922 | -352.589 | 16.832
12:34 | 4456 | 41.5806 | 202.2058 | 449.5158 | 456.2018 | -16.4054 | -40.7267 | 11.1909 | 7.8459 | 2.2764 | 0.4077 | 3.1917 | -0.8499 | 11.6233 | 4.4167 | 0.6143 | 0.6657 | 0.9645 | 0.7406 | -129.6735 | -0.4649 | 5.6203 | 1.8248 | -3.1291 | -1.4162 | 4.3884 |  | 3.1052 | 0.2115 | 4.0106 | 3.3652 | 3.3354 | 1.0754 | 10.7348 | 14.2776 | 14.8634 | 11.1165 | -0.0002 | -0.0029 | 0.0005 | 0.0039 | 0.0013 | -0.0005 | 0.0103 | 0.0065 | -0.0122 | -360.1896 | 17.4233 | -360.4296 | 17.5978 | -360.7589 | 18.1645 | -360.7958 | 17.5773 | -352.6813 | 18.7353 | -352.629 | 16.8032
12:34 | 4457 | 41.5753 | 202.2207 | 449.4693 | 456.2237 | -16.2597 | -40.585 | 11.2142 | 7.7711 | 2.2462 | 0.456 | 3.207 | -0.8369 | 11.6603 | 4.4267 | 0.6152 | 0.6624 | 0.9627 | 0.7414 | -129.5928 | -0.4414 | 5.5823 | 1.8481 | -3.0678 | -1.4588 | 4.4186 |  | 3.0369 | 0.0525 | 4.0085 | 3.3673 | 3.334 | 1.075 | 10.7498 | 14.2754 | 14.8676 | 11.0793 | 0.0001 | -0.0033 | 0.0014 | 0.0043 | 0.0007 | -0.0004 | -0.0048 | -0.0016 | -0.0177 | -360.1373 | 17.3925 | -360.4635 | 17.6594 | -360.882 | 18.1933 | -360.8327 | 17.5424 | -352.5798 | 18.7148 | -352.6413 | 16.8607
12:34 | 4458 | 41.569 | 202.2804 | 449.5143 | 456.319 | -16.2037 | -40.4857 | 11.278 | 7.7308 | 2.1273 | 0.4266 | 3.1609 | -0.8265 | 11.6768 | 4.3824 | 0.6152 | 0.665 | 0.9631 | 0.7407 | -129.6319 | -0.5445 | 5.5221 | 1.9072 | -3.0302 | -1.3655 | 4.4022 |  | 3.0458 | 0.0932 | 4.0097 | 3.366 | 3.3331 | 1.0744 | 10.7464 | 14.2659 | 14.8219 | 11.0533 | 0.0003 | -0.0029 | 0.0007 | 0.0039 | 0.0007 | -0.0006 | 0.013 | -0.0098 | 0.0117 | -360.1804 | 17.3884 | -360.3958 | 17.6102 | -360.7989 | 18.2097 | -360.882 | 17.5896 | -352.6567 | 18.7169 | -352.6044 | 16.8053
12:34 | 4459 | 41.6495 | 202.2642 | 449.5389 | 456.3279 | -16.2283 | -40.5799 | 11.1306 | 7.8314 | 2.1686 | 0.5836 | 3.1822 | -0.8425 | 11.6576 | 4.4039 | 0.6142 | 0.6653 | 0.9642 | 0.7421 | -129.6628 | -0.4536 | 5.5756 | 1.8885 | -3.0506 | -1.3598 | 4.421 |  | 3.1056 | 0.0607 | 4.01 | 3.3683 | 3.3384 | 1.0757 | 10.7278 | 14.2418 | 14.8331 | 11.0749 | -0.0005 | -0.0032 | 0.0015 | 0.0045 | 0.0006 | -0.0002 | 0.0194 | -0.0153 | -0.0163 | -360.1988 | 17.4397 | -360.5343 | 17.643 | -360.8512 | 18.1769 | -360.7989 | 17.5629 | -352.6567 | 18.7559 | -352.6998 | 16.8484
12:34 | 4460 | 41.6932 | 202.2282 | 449.5164 | 456.3219 | -16.2827 | -40.5214 | 11.1381 | 7.8048 | 2.1162 | 0.4102 | 3.1487 | -0.7972 | 11.733 | 4.5432 | 0.6159 | 0.6658 | 0.9628 | 0.7413 | -129.6741 | -0.4377 | 5.5083 | 1.7542 | -3.1444 | -1.4477 | 4.2704 |  | 3.1414 | 0.0907 | 4.0099 | 3.3649 | 3.3341 | 1.0749 | 10.7521 | 14.2603 | 14.8634 | 11.0702 | -0.0001 | -0.0026 | 0.0008 | 0.004 | 0.001 | -0.0006 | 0.0124 | -0.0203 | -0.016 | -360.165 | 17.3761 | -360.4389 | 17.6594 | -360.8574 | 18.2385 | -360.8912 | 17.5629 | -352.5921 | 18.7189 | -352.6444 | 16.8566
12:34 | 4461 | 41.5508 | 202.2316 | 449.4609 | 456.2823 | -16.4733 | -40.6927 | 11.0042 | 7.8421 | 2.1152 | 0.3657 | 3.1232 | -0.8329 | 11.6171 | 4.3961 | 0.6156 | 0.6641 | 0.9633 | 0.7409 | -129.5921 | -0.3987 | 5.5604 | 1.8319 | -3.0751 | -1.3715 | 4.3084 |  | 3.0845 | 0.0656 | 4.01 | 3.3678 | 3.3386 | 1.0745 | 10.7475 | 14.2557 | 14.8243 | 11.0655 | 0.0006 | -0.0032 | 0.0004 | 0.0036 | 0.0006 | 0.0002 | 0.0058 | -0.0124 | -0.0296 | -360.2696 | 17.4315 | -360.4881 | 17.6163 | -360.7866 | 18.2015 | -360.8727 | 17.5937 | -352.7275 | 18.7538 | -352.6506 | 16.8217
12:34 | 4462 | 41.5297 | 202.2534 | 449.5079 | 456.2491 | -16.4937 | -40.6936 | 10.974 | 7.8355 | 2.1008 | 0.3874 | 3.074 | -0.8068 | 11.636 | 4.4335 | 0.6163 | 0.6659 | 0.9648 | 0.741 | -129.5457 | -0.3811 | 5.6895 | 1.7801 | -3.1103 | -1.4834 | 4.2651 |  | 3.0641 | 0.052 | 4.01 | 3.3647 | 3.3378 | 1.0733 | 10.7405 | 14.2776 | 14.8345 | 11.0934 | 0 | -0.003 | 0.0005 | 0.0039 | 0.0009 | -0.0006 | 0.0103 | -0.0019 | -0.013 | -360.1711 | 17.4274 | -360.5219 | 17.682 | -360.8881 | 18.222 | -360.8512 | 17.5609 | -352.6444 | 18.7477 | -352.6906 | 16.8792
12:34 | 4463 | 41.6146 | 202.2376 | 449.5551 | 456.3329 | -16.4197 | -40.7321 | 11.1149 | 7.8294 | 2.029 | 0.3942 | 3.1697 | -0.8204 | 11.6316 | 4.4404 | 0.614 | 0.6639 | 0.9644 | 0.7405 | -129.6256 | -0.3744 | 5.5493 | 1.781 | -3.1387 | -1.3797 | 4.2833 |  | 3.0711 | 0.0533 | 4.0089 | 3.3664 | 3.3337 | 1.0728 | 10.7866 | 14.2898 | 14.9198 | 11.1381 | 0 | -0.0022 | 0.0009 | 0.0041 | 0.0007 | -0.0002 | 0.0075 | -0.0057 | -0.009 | -360.1896 | 17.3925 | -360.4266 | 17.6266 | -360.8204 | 18.2364 | -360.882 | 17.6061 | -352.6906 | 18.723 | -352.6383 | 16.8361
12:34 | 4464 | 41.6532 | 202.2358 | 449.5795 | 456.3521 | -16.4587 | -40.7545 | 11.0217 | 7.8125 | 2.1121 | 0.3874 | 3.1442 | -0.7964 | 11.5695 | 4.4181 | 0.6168 | 0.6614 | 0.9633 | 0.7403 | -129.6089 | -0.4444 | 5.6033 | 1.7729 | -3.1188 | -1.5212 | 4.2929 |  | 3.0391 | 0.088 | 4.0091 | 3.3655 | 3.3349 | 1.0741 | 10.7302 | 14.2555 | 14.8464 | 11.089 | -0.0002 | -0.0029 | 0.0008 | 0.0042 | 0.001 | -0.0003 | 0.0139 | -0.0019 | -0.0254 | -360.2635 | 17.4459 | -360.5373 | 17.6594 | -360.8266 | 18.1953 | -360.8327 | 17.5588 | -352.6967 | 18.7744 | -352.7244 | 16.871
12:34 | 4465 | 41.5482 | 202.2359 | 449.5976 | 456.2821 | -16.4805 | -40.9607 | 11.0545 | 7.7893 | 2.1366 | 0.5103 | 3.1355 | -0.7412 | 11.6286 | 4.4134 | 0.617 | 0.6656 | 0.9632 | 0.7408 | -129.5893 | -0.4977 | 5.6097 | 1.7967 | -3.1085 | -1.3597 | 4.3614 |  | 3.1383 | 0.0939 | 4.0099 | 3.3647 | 3.3351 | 1.0744 | 10.7798 | 14.2652 | 14.8642 | 11.1146 | 0.0001 | -0.0028 | 0.0012 | 0.0042 | 0.0007 | -0.0005 | 0.0019 | 0.0004 | -0.0067 | -360.1465 | 17.3864 | -360.4481 | 17.6594 | -360.8635 | 18.2487 | -360.8697 | 17.5629 | -352.6537 | 18.7087 | -352.6567 | 16.8669
12:34 | 4466 | 41.6404 | 202.2307 | 449.6721 | 456.4013 | -16.4322 | -40.8953 | 11.0279 | 7.803 | 2.1042 | 0.4131 | 3.1741 | -0.612 | 11.6525 | 4.4562 | 0.6167 | 0.665 | 0.9636 | 0.74 | -129.5477 | -0.3417 | 5.641 | 1.7194 | -3.1492 | -1.3645 | 4.2992 |  | 3.1481 | 0.0989 | 4.0091 | 3.3661 | 3.3337 | 1.0757 | 10.7614 | 14.2579 | 14.8433 | 11.0796 | 0.0001 | -0.0031 | 0.0008 | 0.0034 | 0.0006 | -0.0006 | 0.0054 | -0.0004 | -0.0048 | -360.2388 | 17.4254 | -360.4758 | 17.6225 | -360.7897 | 18.1851 | -360.8297 | 17.5835 | -352.6783 | 18.7518 | -352.6629 | 16.8423
12:34 | 4467 | 41.6706 | 202.2913 | 449.5788 | 456.3759 | -16.4203 | -40.9393 | 11.0061 | 7.8388 | 2.2193 | 0.4934 | 3.1449 | -0.7488 | 11.692 | 4.5191 | 0.6156 | 0.6626 | 0.963 | 0.7412 | -129.5609 | -0.4202 | 5.5808 | 1.5972 | -3.0625 | -1.3252 | 4.2913 |  | 3.1455 | 0.1217 | 4.0094 | 3.3644 | 3.335 | 1.0745 | 10.7037 | 14.2169 | 14.8217 | 11.0754 | -0.0002 | -0.0025 | 0.0005 | 0.0036 | 0.0009 | -0.0013 | 0.0153 | -0.0161 | -0.0032 | -360.125 | 17.3864 | -360.4973 | 17.682 | -360.8604 | 18.222 | -360.8174 | 17.5404 | -352.5921 | 18.7251 | -352.6844 | 16.8833
12:34 | 4468 | 41.6089 | 202.3114 | 449.7186 | 456.3919 | -16.3652 | -40.8404 | 11.0281 | 7.9072 | 2.2261 | 0.5056 | 3.2047 | -0.8248 | 11.6621 | 4.5131 | 0.6173 | 0.6669 | 0.9626 | 0.7425 | -129.5257 | -0.384 | 5.6084 | 1.5922 | -3.0902 | -1.3309 | 4.3035 |  | 3.1792 | 0.1958 | 4.0091 | 3.3651 | 3.3364 | 1.075 | 10.7232 | 14.2487 | 14.8287 | 11.0818 | 0.0001 | -0.0023 | 0.0004 | 0.0037 | 0.0008 | -0.0004 | 0.0176 | -0.0079 | -0.0253 | -360.205 | 17.3884 | -360.3989 | 17.6184 | -360.7773 | 18.2118 | -360.882 | 17.604 | -352.6967 | 18.7292 | -352.6167 | 16.8156
12:34 | 4469 | 41.6235 | 202.2935 | 449.5943 | 456.3891 | -16.3325 | -40.8219 | 11.1072 | 7.8335 | 2.1774 | 0.4148 | 3.1271 | -0.8907 | 11.6957 | 4.4609 | 0.6167 | 0.6626 | 0.9639 | 0.7415 | -129.4783 | -0.2918 | 5.5709 | 1.582 | -3.0345 | -1.3873 | 4.3841 |  | 3.142 | 0.1421 | 4.009 | 3.366 | 3.335 | 1.0755 | 10.7291 | 14.26 | 14.8324 | 11.0941 | 0 | -0.0032 | -0.0001 | 0.0035 | 0.0014 | -0.0004 | 0.0076 | -0.0066 | -0.0149 | -360.1465 | 17.4048 | -360.485 | 17.6594 | -360.802 | 18.1933 | -360.805 | 17.5424 | -352.6352 | 18.7538 | -352.6813 | 16.8669
12:34 | 4470 | 41.656 | 202.2187 | 449.6389 | 456.3252 | -16.3441 | -40.7501 | 11.1058 | 7.9222 | 2.088 | 0.4753 | 3.1381 | -0.8598 | 11.6236 | 4.5174 | 0.616 | 0.6625 | 0.9643 | 0.7412 | -129.5421 | -0.3299 | 5.6806 | 1.7746 | -3.0814 | -1.3484 | 4.4187 |  | 3.1016 | 0.0778 | 4.0099 | 3.3644 | 3.3373 | 1.0755 | 10.7382 | 14.2406 | 14.8723 | 11.0508 | 0.0006 | -0.0026 | 0.0007 | 0.0039 | 0.0008 | -0.0001 | 0.0261 | -0.0168 | -0.0259 | -360.1711 | 17.374 | -360.3896 | 17.6492 | -360.8112 | 18.2159 | -360.8789 | 17.5671 | -352.6598 | 18.7169 | -352.6075 | 16.834
12:34 | 4471 | 41.6119 | 202.1532 | 449.6189 | 456.4269 | -16.3685 | -40.8038 | 11.1202 | 7.8784 | 2.1438 | 0.513 | 3.0089 | -0.8847 | 11.7779 | 4.5904 | 0.6174 | 0.663 | 0.9655 | 0.7415 | -129.5662 | -0.4083 | 5.6307 | 1.7455 | -3.0897 | -1.2884 | 4.3979 |  | 3.0766 | 0.0625 | 4.0094 | 3.3658 | 3.3363 | 1.0766 | 10.7556 | 14.2406 | 14.8491 | 11.0854 | 0 | -0.0027 | 0.0008 | 0.0043 | 0.0012 | -0.0003 | 0.0022 | -0.0105 | 0.0064 | -360.2327 | 17.4192 | -360.4573 | 17.643 | -360.7497 | 18.1728 | -360.802 | 17.5671 | -352.6813 | 18.762 | -352.6629 | 16.834
12:34 | 4472 | 41.6876 | 202.2095 | 449.6714 | 456.4108 | -16.3495 | -40.7974 | 11.099 | 7.8441 | 2.1758 | 0.589 | 3.0668 | -0.9149 | 11.6981 | 4.5232 | 0.6162 | 0.6658 | 0.9647 | 0.7403 | -129.5645 | -0.4173 | 5.6435 | 1.7062 | -3.1448 | -1.4022 | 4.2985 |  | 3.0771 | 0.1197 | 4.0095 | 3.367 | 3.339 | 1.0786 | 10.7315 | 14.2447 | 14.8388 | 11.0624 | -0.0009 | -0.0029 | 0.0003 | 0.0032 | 0.0002 | -0.0005 | 0.0023 | -0.0095 | 0.0028 | -360.0819 | 17.3699 | -360.4358 | 17.6677 | -360.8389 | 18.2179 | -360.7897 | 17.5239 | -352.6136 | 18.7128 | -352.669 | 16.8607
12:34 | 4473 | 41.6138 | 202.14 | 449.5073 | 456.3919 | -16.3259 | -40.7518 | 11.061 | 7.8804 | 2.1332 | 0.5218 | 3.1017 | -0.9023 | 11.6546 | 4.5015 | 0.617 | 0.6646 | 0.9642 | 0.7415 | -129.5307 | -0.4723 | 5.5166 | 1.7607 | -3.1508 | -1.4448 | 4.3084 |  | 3.158 | 0.1932 | 4.011 | 3.3678 | 3.3387 | 1.0755 | 10.7394 | 14.2474 | 14.8321 | 11.0927 | 0.0001 | -0.0027 | 0.0014 | 0.0041 | 0.0008 | -0.0006 | 0.0124 | -0.0153 | -0.0122 | -360.1865 | 17.3987 | -360.4204 | 17.6184 | -360.7589 | 18.1933 | -360.8543 | 17.5917 | -352.6875 | 18.7271 | -352.6413 | 16.8135
12:34 | 4474 | 41.6994 | 202.1286 | 449.6415 | 456.4214 | -16.3329 | -40.7422 | 11.0974 | 7.9401 | 2.0954 | 0.5805 | 3.1088 | -0.9086 | 11.7225 | 4.4989 | 0.617 | 0.6665 | 0.9666 | 0.7414 | -129.5489 | -0.4876 | 5.4499 | 1.8362 | -3.2074 | -1.5624 | 4.2227 |  | 3.2201 | 0.1277 | 4.0111 | 3.3697 | 3.3415 | 1.0753 | 10.7568 | 14.2589 | 14.861 | 11.11 | 0 | -0.0033 | 0.001 | 0.0037 | 0.0006 | -0.0002 | 0.0183 | -0.0159 | -0.0036 | -360.1188 | 17.3987 | -360.4789 | 17.6718 | -360.8389 | 18.1789 | -360.7743 | 17.5301 | -352.5829 | 18.7292 | -352.6813 | 16.8669
12:34 | 4475 | 41.6982 | 202.181 | 449.7554 | 456.4132 | -16.4343 | -40.818 | 11.1484 | 7.9551 | 2.195 | 0.5874 | 3.1386 | -0.9733 | 11.6067 | 4.5113 | 0.617 | 0.6664 | 0.9676 | 0.7408 | -129.561 | -0.5875 | 5.4514 | 1.8464 | -3.1518 | -1.5071 | 4.3258 |  | 3.1738 | 0.0696 | 4.009 | 3.365 | 3.3371 | 1.0756 | 10.7487 | 14.2567 | 14.8593 | 11.0959 | -0.0002 | -0.0031 | 0.0009 | 0.0038 | 0.0007 | -0.0004 | 0.02 | -0.0095 | -0.0235 | -360.1342 | 17.3617 | -360.3773 | 17.6286 | -360.7835 | 18.2179 | -360.8389 | 17.5609 | -352.6198 | 18.6922 | -352.5706 | 16.8238
12:34 | 4476 | 41.6686 | 202.1521 | 449.7554 | 456.4346 | -16.3873 | -40.8581 | 11.1501 | 7.919 | 2.1153 | 0.5478 | 3.0787 | -0.9065 | 11.6034 | 4.4792 | 0.6186 | 0.6626 | 0.9669 | 0.741 | -129.5954 | -0.6315 | 5.5012 | 1.8273 | -3.122 | -1.5159 | 4.2782 |  | 3.2254 | 0.121 | 4.0096 | 3.363 | 3.3352 | 1.0744 | 10.7279 | 14.2416 | 14.8147 | 11.0753 | -0.0003 | -0.0028 | 0.0001 | 0.0036 | 0.0005 | -0.0007 | 0.0225 | -0.0098 | -0.012 | -360.2081 | 17.4172 | -360.4604 | 17.6451 | -360.7435 | 18.1604 | -360.7712 | 17.5588 | -352.629 | 18.7456 | -352.6721 | 16.8361
12:34 | 4477 | 41.6313 | 202.161 | 449.7414 | 456.4479 | -16.4454 | -40.8534 | 11.0058 | 7.8029 | 1.9992 | 0.576 | 3.0656 | -0.8694 | 11.6275 | 4.5067 | 0.617 | 0.666 | 0.9639 | 0.7409 | -129.5158 | -0.4902 | 5.4429 | 1.7263 | -3.237 | -1.4695 | 4.1852 |  | 3.1582 | 0.1131 | 4.0097 | 3.3642 | 3.3347 | 1.075 | 10.7659 | 14.3092 | 14.9031 | 11.1352 | 0.0001 | -0.0027 | 0.0004 | 0.0035 | 0.0009 | -0.0003 | -0.0077 | -0.0225 | 0.0172 | -360.1158 | 17.3556 | -360.405 | 17.6636 | -360.8358 | 18.2159 | -360.7835 | 17.5301 | -352.5983 | 18.6984 | -352.6198 | 16.8505
12:34 | 4478 | 41.682 | 202.2466 | 449.7781 | 456.5091 | -16.4506 | -40.8405 | 11.1313 | 7.8051 | 2.1008 | 0.6717 | 3.0517 | -0.816 | 11.6608 | 4.5557 | 0.6173 | 0.6613 | 0.9637 | 0.7419 | -129.5915 | -0.5155 | 5.3826 | 1.7716 | -3.1506 | -1.4849 | 4.2383 |  | 3.1777 | 0.1095 | 4.0087 | 3.3644 | 3.3369 | 1.0751 | 10.7684 | 14.2647 | 14.8379 | 11.0927 | 0 | -0.0033 | 0.0009 | 0.0045 | 0.0007 | -0.0004 | 0.0056 | -0.0075 | -0.0155 | -360.2204 | 17.3884 | -360.405 | 17.6245 | -360.7589 | 18.181 | -360.8389 | 17.5732 | -352.6352 | 18.7271 | -352.5798 | 16.8135
12:34 | 4479 | 41.6488 | 202.1636 | 449.723 | 456.3955 | -16.3167 | -40.7998 | 11.1279 | 7.7743 | 2.106 | 0.6531 | 3.0707 | -0.8275 | 11.6277 | 4.6202 | 0.618 | 0.6647 | 0.964 | 0.7422 | -129.4975 | -0.4987 | 5.4952 | 1.6933 | -3.1477 | -1.5423 | 4.3002 |  | 3.1954 | 0.1309 | 4.0101 | 3.3652 | 3.3339 | 1.0752 | 10.7429 | 14.2567 | 14.8246 | 11.0381 | 0 | -0.0028 | 0.0007 | 0.0038 | 0.0005 | -0.0001 | 0.0153 | -0.0088 | 0.0003 | -360.1465 | 17.3987 | -360.4789 | 17.6759 | -360.8358 | 18.183 | -360.762 | 17.5198 | -352.5829 | 18.7251 | -352.6629 | 16.8566
12:34 | 4480 | 41.7612 | 202.2835 | 449.7319 | 456.5068 | -16.3597 | -40.8129 | 11.1267 | 7.7688 | 2.2186 | 0.6721 | 3.0756 | -0.7638 | 11.5904 | 4.4462 | 0.6174 | 0.6667 | 0.9624 | 0.7398 | -129.5375 | -0.5559 | 5.4429 | 1.7096 | -3.2172 | -1.5386 | 4.2029 |  | 3.2466 | 0.1127 | 4.0111 | 3.3669 | 3.3357 | 1.0756 | 10.7393 | 14.2478 | 14.87 | 11.0857 | -0.0004 | -0.0024 | 0.0007 | 0.0036 | 0.0012 | -0.0006 | 0.0171 | -0.0227 | -0.007 | -360.1496 | 17.3597 | -360.3804 | 17.6286 | -360.7835 | 18.2159 | -360.8604 | 17.5753 | -352.5921 | 18.6922 | -352.5644 | 16.8135
12:34 | 4481 | 41.7179 | 202.231 | 449.6848 | 456.5576 | -16.4072 | -40.8684 | 11.1384 | 7.8272 | 2.1113 | 0.629 | 3.0444 | -0.8316 | 11.5969 | 4.4629 | 0.6175 | 0.6632 | 0.9649 | 0.7407 | -129.4875 | -0.5352 | 5.4581 | 1.8028 | -3.1073 | -1.5085 | 4.2507 |  | 3.1506 | 0.1277 | 4.0112 | 3.3691 | 3.3363 | 1.0764 | 10.7476 | 14.2785 | 14.8685 | 11.1067 | -0.0006 | -0.0033 | 0.0008 | 0.0039 | 0.0003 | -0.0006 | 0.0236 | -0.0101 | -0.0059 | -360.1742 | 17.4233 | -360.4727 | 17.6553 | -360.8112 | 18.1912 | -360.7927 | 17.5629 | -352.6537 | 18.7415 | -352.6413 | 16.8381
12:34 | 4482 | 41.7346 | 202.315 | 449.7142 | 456.5095 | -16.4179 | -40.8271 | 11.1695 | 7.75 | 2.0368 | 0.5235 | 3.0392 | -0.8215 | 11.6469 | 4.5073 | 0.6169 | 0.6671 | 0.9633 | 0.7411 | -129.4969 | -0.5636 | 5.4512 | 1.7889 | -3.1761 | -1.5536 | 4.3207 |  | 3.1072 | 0.1508 | 4.01 | 3.3649 | 3.3368 | 1.0753 | 10.7439 | 14.2757 | 14.8581 | 11.0785 | 0.0001 | -0.0028 | 0.0008 | 0.0035 | 0.0011 | -0.0008 | 0.0063 | -0.0018 | -0.0092 | -360.1219 | 17.374 | -360.4419 | 17.6553 | -360.882 | 18.2323 | -360.842 | 17.5486 | -352.5983 | 18.6922 | -352.626 | 16.8505
12:34 | 4483 | 41.8128 | 202.213 | 449.8083 | 456.5418 | -16.3599 | -40.9103 | 11.1155 | 7.8082 | 2.0602 | 0.5735 | 3.0602 | -0.8244 | 11.6764 | 4.5762 | 0.6179 | 0.6635 | 0.9601 | 0.7418 | -129.544 | -0.5411 | 5.4702 | 1.5348 | -3.2309 | -1.6748 | 4.2262 |  | 3.181 | 0.0775 | 4.0099 | 3.3674 | 3.3368 | 1.0742 | 10.7591 | 14.238 | 14.8164 | 11.0316 | 0 | -0.0029 | 0.0009 | 0.004 | 0.0005 | -0.0003 | 0.0026 | -0.0165 | 0.0003 | -360.2111 | 17.4007 | -360.4266 | 17.6348 | -360.7743 | 18.2056 | -360.8574 | 17.5876 | -352.6413 | 18.723 | -352.5829 | 16.8115
12:34 | 4484 | 41.7971 | 202.2903 | 449.8023 | 456.5671 | -16.3863 | -40.8843 | 11.0832 | 7.9509 | 2.1461 | 0.5084 | 3.059 | -0.7966 | 11.5799 | 4.6088 | 0.616 | 0.6598 | 0.96 | 0.7403 | -129.5875 | -0.5376 | 5.5077 | 1.5779 | -3.1991 | -1.5642 | 4.3314 |  | 3.1735 | 0.1145 | 4.0099 | 3.3653 | 3.3359 | 1.0749 | 10.7555 | 14.2582 | 14.8628 | 11.0673 | -0.0003 | -0.0028 | 0.0007 | 0.0038 | 0.0011 | -0.0004 | 0.0093 | -0.0074 | -0.0009 | -360.1804 | 17.4192 | -360.4881 | 17.6841 | -360.8974 | 18.2097 | -360.8204 | 17.5506 | -352.6044 | 18.7292 | -352.709 | 16.8813
12:34 | 4485 | 41.655 | 202.1771 | 449.7827 | 456.5232 | -16.4561 | -40.993 | 11.1551 | 7.8806 | 2.141 | 0.445 | 3.0454 | -0.831 | 11.5734 | 4.6453 | 0.6157 | 0.6637 | 0.9593 | 0.7404 | -129.5658 | -0.4605 | 5.575 | 1.5478 | -3.1936 | -1.5213 | 4.2542 |  | 3.238 | 0.1987 | 4.0093 | 3.3684 | 3.3367 | 1.0757 | 10.7579 | 14.2486 | 14.8566 | 11.0533 | -0.0001 | -0.0025 | 0.0007 | 0.004 | 0.0005 | -0.0004 | 0.0096 | -0.0175 | -0.0045 | -360.1619 | 17.3802 | -360.4173 | 17.6451 | -360.8204 | 18.2467 | -360.9127 | 17.5855 | -352.6413 | 18.6984 | -352.6106 | 16.8299
12:34 | 4486 | 41.7309 | 202.2533 | 449.8256 | 456.4854 | -16.4969 | -41.074 | 11.094 | 7.9544 | 2.1988 | 0.6573 | 3.1048 | -0.8711 | 11.6009 | 4.5398 | 0.6164 | 0.6662 | 0.9642 | 0.7409 | -129.5366 | -0.5229 | 5.5178 | 1.5582 | -3.1376 | -1.5187 | 4.2907 |  | 3.2333 | 0.2031 | 4.01 | 3.3693 | 3.3353 | 1.0758 | 10.7601 | 14.2802 | 14.8557 | 11.0836 | 0 | -0.0033 | 0.0005 | 0.0042 | 0.0007 | -0.0003 | -0.0043 | -0.0012 | -0.0185 | -360.2635 | 17.4459 | -360.4942 | 17.6656 | -360.8358 | 18.1994 | -360.8297 | 17.5773 | -352.6721 | 18.7518 | -352.6998 | 16.8525
12:34 | 4487 | 41.7425 | 202.1809 | 449.6428 | 456.4526 | -16.4651 | -40.9941 | 11.106 | 7.9445 | 2.2126 | 0.5167 | 3.0475 | -0.8165 | 11.6463 | 4.631 | 0.6158 | 0.6662 | 0.9628 | 0.7415 | -129.5674 | -0.5016 | 5.4881 | 1.56 | -3.0742 | -1.6109 | 4.3228 |  | 3.1337 | 0.2883 | 4.0111 | 3.367 | 3.3317 | 1.0773 | 10.744 | 14.2696 | 14.8618 | 11.085 | 0.0005 | -0.0029 | 0.0007 | 0.0039 | 0.0006 | -0.0005 | 0.008 | -0.0152 | 0.0031 | -360.165 | 17.3884 | -360.4542 | 17.6841 | -360.8789 | 18.2508 | -360.8635 | 17.5547 | -352.6106 | 18.7128 | -352.6475 | 16.8731
12:35 | 4488 | 41.7768 | 202.1613 | 449.7137 | 456.4304 | -16.3522 | -40.9355 | 11.1714 | 7.9642 | 2.252 | 0.5414 | 3.0647 | -0.7919 | 11.7454 | 4.6685 | 0.6159 | 0.6631 | 0.9626 | 0.7402 | -129.5621 | -0.474 | 5.4945 | 1.5851 | -3.1508 | -1.5771 | 4.2978 |  | 3.1744 | 0.2565 | 4.0091 | 3.3652 | 3.3355 | 1.0753 | 10.7671 | 14.2928 | 14.8791 | 11.1139 | 0 | -0.0025 | 0.0009 | 0.0036 | 0.0005 | -0.0006 | 0.0038 | -0.0037 | -0.0096 | -360.2481 | 17.4274 | -360.4542 | 17.641 | -360.8081 | 18.2159 | -360.8789 | 17.6081 | -352.6844 | 18.7374 | -352.6352 | 16.834
12:35 | 4489 | 41.799 | 202.1494 | 449.7016 | 456.4643 | -16.2385 | -40.8419 | 11.2568 | 7.9007 | 2.2026 | 0.4735 | 3.0544 | -0.8739 | 11.7012 | 4.7151 | 0.6171 | 0.6669 | 0.9656 | 0.7422 | -129.5101 | -0.4946 | 5.5695 | 1.5286 | -3.1824 | -1.6154 | 4.321 |  | 3.1866 | 0.1265 | 4.0103 | 3.3677 | 3.3343 | 1.0758 | 10.7532 | 14.279 | 14.8717 | 11.0825 | 0 | -0.0023 | 0.001 | 0.004 | 0.0007 | -0.0008 | 0.0092 | -0.0048 | -0.0154 | -360.1865 | 17.4315 | -360.5158 | 17.7005 | -360.8727 | 18.2138 | -360.8112 | 17.5609 | -352.626 | 18.7497 | -352.709 | 16.8895
12:35 | 4490 | 41.8007 | 202.0592 | 449.6437 | 456.4163 | -16.1328 | -40.826 | 11.2896 | 7.7977 | 2.1903 | 0.4248 | 3.0234 | -0.7717 | 11.7676 | 4.7404 | 0.618 | 0.6623 | 0.962 | 0.7411 | -129.4393 | -0.4373 | 5.548 | 1.5456 | -3.1432 | -1.5432 | 4.2544 |  | 3.214 | 0.1325 | 4.0097 | 3.3661 | 3.3324 | 1.0745 | 10.7648 | 14.2615 | 14.8822 | 11.0771 | 0.0001 | -0.003 | 0.001 | 0.0038 | 0.0005 | -0.0007 | 0.0039 | -0.0002 | -0.0202 | -360.1711 | 17.3843 | -360.4266 | 17.6594 | -360.8143 | 18.2426 | -360.9189 | 17.604 | -352.6783 | 18.7087 | -352.6167 | 16.8361
12:35 | 4491 | 41.7403 | 202.081 | 449.6132 | 456.3371 | -16.2608 | -40.7809 | 11.2846 | 7.8409 | 2.2739 | 0.4914 | 3.1037 | -0.6727 | 11.7296 | 4.6666 | 0.6168 | 0.6628 | 0.9637 | 0.7419 | -129.4379 | -0.4559 | 5.6067 | 1.48 | -3.1253 | -1.6673 | 4.255 |  | 3.1365 | 0.059 | 4.009 | 3.3662 | 3.3349 | 1.0739 | 10.7394 | 14.2532 | 14.8379 | 11.0811 | 0.0003 | -0.0027 | 0.001 | 0.004 | 0.0012 | -0.0007 | 0.0164 | -0.0069 | -0.0138 | -360.2358 | 17.4418 | -360.5343 | 17.68 | -360.8358 | 18.1974 | -360.8204 | 17.5814 | -352.6537 | 18.7682 | -352.6937 | 16.8546
12:35 | 4492 | 41.7011 | 202.0629 | 449.5552 | 456.3758 | -16.3354 | -40.7717 | 11.2566 | 7.8699 | 2.2303 | 0.4568 | 3.0935 | -0.7461 | 11.6855 | 4.6849 | 0.6165 | 0.6625 | 0.9604 | 0.7418 | -129.4905 | -0.4527 | 5.6499 | 1.4949 | -3.1418 | -1.6082 | 4.2021 |  | 3.2183 | 0.0524 | 4.0092 | 3.3659 | 3.3362 | 1.0759 | 10.7475 | 14.2671 | 14.858 | 11.0833 | -0.0001 | -0.0027 | 0.0009 | 0.0043 | 0.0005 | -0.0004 | 0.0268 | 0.0033 | 0 | -360.1681 | 17.3925 | -360.4512 | 17.68 | -360.8789 | 18.2446 | -360.8758 | 17.5753 | -352.6167 | 18.7066 | -352.6413 | 16.8566
12:35 | 4493 | 41.7676 | 202.1968 | 449.669 | 456.4379 | -16.3678 | -40.8528 | 11.2287 | 7.867 | 2.1972 | 0.5132 | 3.0393 | -0.7653 | 11.6626 | 4.6796 | 0.6151 | 0.6616 | 0.9621 | 0.7417 | -129.5285 | -0.4327 | 5.5551 | 1.4942 | -3.141 | -1.5408 | 4.2004 |  | 3.1966 | 0.0427 | 4.0101 | 3.3673 | 3.3334 | 1.0753 | 10.736 | 14.2496 | 14.8395 | 11.0548 | -0.0003 | -0.0025 | 0.0004 | 0.0041 | 0.0008 | -0.001 | 0.0127 | -0.0132 | 0.013 | -360.2481 | 17.4336 | -360.4727 | 17.643 | -360.7958 | 18.2138 | -360.8666 | 17.602 | -352.6875 | 18.7415 | -352.6475 | 16.8217
12:35 | 4494 | 41.8049 | 202.2048 | 449.6244 | 456.4989 | -16.308 | -40.7754 | 11.1361 | 7.8165 | 2.1603 | 0.4531 | 3.0713 | -0.7523 | 11.7546 | 4.6999 | 0.6167 | 0.663 | 0.9626 | 0.7399 | -129.5825 | -0.4302 | 5.6247 | 1.6318 | -3.0676 | -1.5159 | 4.2478 |  | 3.1859 | -0.0061 | 4.0113 | 3.3679 | 3.3359 | 1.0755 | 10.7625 | 14.2591 | 14.8563 | 11.1096 | 0 | -0.0028 | 0.0009 | 0.0041 | 0.0008 | 0 | 0.013 | 0.0052 | 0.0059 | -360.1742 | 17.4274 | -360.5373 | 17.7005 | -360.8912 | 18.22 | -360.805 | 17.5629 | -352.5983 | 18.7415 | -352.7152 | 16.8792
12:35 | 4495 | 41.682 | 202.2213 | 449.663 | 456.398 | -16.1999 | -40.7087 | 11.2579 | 7.8197 | 2.1944 | 0.4901 | 3.118 | -0.7712 | 11.701 | 4.7113 | 0.6161 | 0.6642 | 0.9612 | 0.7416 | -129.569 | -0.4351 | 5.5305 | 1.5375 | -3.0399 | -1.6049 | 4.1938 |  | 3.2013 | 0.0023 | 4.0112 | 3.3659 | 3.3381 | 1.0772 | 10.7314 | 14.2391 | 14.8283 | 11.0735 | -0.0001 | -0.0033 | 0.0005 | 0.0038 | 0.0013 | -0.0007 | 0.0097 | 0.0018 | -0.0058 | -360.2358 | 17.3946 | -360.4142 | 17.6471 | -360.8235 | 18.2426 | -360.8789 | 17.5917 | -352.6537 | 18.721 | -352.6106 | 16.8176
12:35 | 4496 | 41.777 | 202.1769 | 449.8473 | 456.4322 | -16.2306 | -40.6978 | 11.2255 | 7.8729 | 2.2063 | 0.4838 | 3.0875 | -0.8127 | 11.701 | 4.6848 | 0.618 | 0.666 | 0.9616 | 0.7435 | -129.5961 | -0.5095 | 5.4929 | 1.5551 | -2.9549 | -1.5434 | 4.2199 |  | 3.2447 | 0.1 | 4.0095 | 3.3656 | 3.3404 | 1.0752 | 10.7382 | 14.2637 | 14.8086 | 11.097 | -0.0002 | -0.003 | 0.0007 | 0.0036 | 0.0007 | 0 | 0.0128 | -0.012 | -0.0131 | -360.2019 | 17.4315 | -360.5466 | 17.6882 | -360.8481 | 18.1994 | -360.7958 | 17.5486 | -352.6506 | 18.762 | -352.7244 | 16.8546
12:35 | 4497 | 41.8059 | 202.1502 | 449.764 | 456.3748 | -16.1711 | -40.7152 | 11.1623 | 7.8327 | 2.1999 | 0.5207 | 3.0215 | -0.906 | 11.6241 | 4.5802 | 0.6175 | 0.661 | 0.9646 | 0.7416 | -129.5699 | -0.4935 | 5.5128 | 1.5807 | -3.0256 | -1.5565 | 4.1878 |  | 3.227 | 0.1602 | 4.0094 | 3.3666 | 3.3344 | 1.0755 | 10.7522 | 14.237 | 14.845 | 11.0995 | -0.0004 | -0.0028 | 0.0008 | 0.0035 | 0.0009 | -0.0005 | 0.0084 | -0.0028 | -0.0144 | -360.1742 | 17.3823 | -360.4481 | 17.6779 | -360.8758 | 18.2467 | -360.8789 | 17.5712 | -352.6044 | 18.7148 | -352.629 | 16.8443
12:35 | 4498 | 41.7866 | 202.1781 | 449.7694 | 456.3682 | -16.2334 | -40.631 | 11.1452 | 7.8791 | 2.149 | 0.5414 | 2.988 | -0.86 | 11.65 | 4.5822 | 0.6147 | 0.6608 | 0.9633 | 0.7417 | -129.5186 | -0.3134 | 5.6247 | 1.5034 | -3.1119 | -1.5035 | 4.2451 |  | 3.2784 | 0.1113 | 4.0077 | 3.3637 | 3.3359 | 1.0754 | 10.7544 | 14.2858 | 14.8778 | 11.1129 | -0.0002 | -0.0028 | 0.0005 | 0.0035 | 0.0006 | -0.0004 | 0.013 | -0.0011 | -0.027 | -360.2296 | 17.4459 | -360.4973 | 17.6574 | -360.7958 | 18.2077 | -360.8481 | 17.5773 | -352.6906 | 18.7723 | -352.6844 | 16.8299
12:35 | 4499 | 41.7426 | 202.27 | 449.7488 | 456.3545 | -16.3006 | -40.7213 | 11.0438 | 7.8366 | 2.109 | 0.4896 | 3.0273 | -0.8112 | 11.6409 | 4.6604 | 0.6161 | 0.6637 | 0.9626 | 0.7417 | -129.5055 | -0.4142 | 5.5796 | 1.6038 | -3.1157 | -1.4992 | 4.2252 |  | 3.1985 | 0.0744 | 4.0097 | 3.3676 | 3.3357 | 1.0765 | 10.7601 | 14.257 | 14.8673 | 11.0951 | 0.0003 | -0.0028 | 0.0009 | 0.0043 | 0.0009 | -0.0004 | 0.013 | -0.0117 | -0.0065 | -360.1588 | 17.3987 | -360.4881 | 17.6985 | -360.8974 | 18.2446 | -360.8543 | 17.5486 | -352.6106 | 18.723 | -352.6844 | 16.8731
12:35 | 4500 | 41.7811 | 202.2457 | 449.7271 | 456.3999 | -16.3181 | -40.6473 | 11.0759 | 7.8529 | 2.1744 | 0.703 | 3.1234 | -0.8488 | 11.5849 | 4.6838 | 0.6172 | 0.662 | 0.9635 | 0.7413 | -129.5275 | -0.4485 | 5.5395 | 1.5524 | -3.0917 | -1.5174 | 4.219 |  | 3.1623 | 0.0115 | 4.0108 | 3.3663 | 3.3338 | 1.0756 | 10.7463 | 14.2603 | 14.8634 | 11.076 | -0.0002 | -0.0032 | 0.0011 | 0.0045 | 0.0008 | -0.001 | 0.0006 | 0.0043 | -0.0014 | -360.2296 | 17.4131 | -360.4542 | 17.6574 | -360.805 | 18.222 | -360.9066 | 17.6081 | -352.6813 | 18.7374 | -352.6537 | 16.8238
12:35 | 4501 | 41.7095 | 202.15 | 449.745 | 456.2944 | -16.3075 | -40.7227 | 11.11 | 7.8358 | 2.1764 | 0.633 | 3.0765 | -0.8155 | 11.6434 | 4.6611 | 0.6184 | 0.6625 | 0.9636 | 0.7414 | -129.5647 | -0.4308 | 5.5943 | 1.565 | -3.0604 | -1.5565 | 4.18 |  | 3.1467 | 0.0416 | 4.0102 | 3.3664 | 3.3329 | 1.0754 | 10.7486 | 14.2628 | 14.8615 | 11.0778 | -0.0002 | -0.0026 | 0.0007 | 0.0041 | 0.0002 | -0.0002 | -0.0031 | -0.0222 | 0.004 | -360.1988 | 17.4377 | -360.5343 | 17.7334 | -360.8943 | 18.2118 | -360.8112 | 17.5609 | -352.6475 | 18.7497 | -352.7337 | 16.8772
12:35 | 4502 | 41.6243 | 202.1441 | 449.6938 | 456.2909 | -16.2655 | -40.5793 | 11.1759 | 7.8838 | 2.198 | 0.5789 | 3.0163 | -0.7964 | 11.633 | 4.6941 | 0.617 | 0.6622 | 0.9603 | 0.7393 | -129.4986 | -0.4198 | 5.6337 | 1.5436 | -3.0996 | -1.5333 | 4.2398 |  | 3.2287 | 0.0866 | 4.0098 | 3.3679 | 3.3331 | 1.0754 | 10.7705 | 14.256 | 14.8785 | 11.1226 | 0.0002 | -0.0028 | 0.0005 | 0.004 | 0.0007 | -0.0008 | 0.0121 | -0.006 | 0.0039 | -360.1742 | 17.3925 | -360.4358 | 17.7005 | -360.8204 | 18.2405 | -360.9035 | 17.5855 | -352.6629 | 18.7128 | -352.6229 | 16.834
12:35 | 4503 | 41.7435 | 202.1779 | 449.7082 | 456.3332 | -16.2265 | -40.4857 | 11.2056 | 7.861 | 2.14 | 0.6244 | 2.9914 | -0.8542 | 11.6813 | 4.7493 | 0.617 | 0.6622 | 0.9596 | 0.7409 | -129.5355 | -0.4073 | 5.5815 | 1.6705 | -3.1679 | -1.4706 | 4.2495 |  | 3.1711 | 0.1279 | 4.0097 | 3.3663 | 3.3349 | 1.076 | 10.7613 | 14.2696 | 14.8444 | 11.1139 | 0.0002 | -0.003 | 0.0008 | 0.0039 | 0.0009 | -0.0002 | 0.0033 | -0.007 | -0.0129 | -360.1958 | 17.45 | -360.5496 | 17.7149 | -360.8358 | 18.1912 | -360.8081 | 17.5712 | -352.6937 | 18.7661 | -352.709 | 16.8505
12:35 | 4504 | 41.7494 | 202.2188 | 449.7343 | 456.4038 | -16.1765 | -40.5781 | 11.1628 | 7.8851 | 2.1693 | 0.5993 | 3.0138 | -0.8123 | 11.608 | 4.7026 | 0.6174 | 0.6611 | 0.9607 | 0.7403 | -129.5114 | -0.3023 | 5.6299 | 1.7478 | -3.1365 | -1.5042 | 4.3082 |  | 3.1462 | 0.1288 | 4.0098 | 3.3703 | 3.3341 | 1.0752 | 10.7451 | 14.2419 | 14.8342 | 11.063 | 0.0001 | -0.0027 | 0.0008 | 0.0036 | 0.0013 | -0.0002 | 0.0072 | -0.0003 | -0.0206 | -360.1158 | 17.3946 | -360.4696 | 17.7231 | -360.8912 | 18.2426 | -360.885 | 17.565 | -352.6321 | 18.7066 | -352.626 | 16.8505
12:35 | 4505 | 41.7089 | 202.3652 | 449.8143 | 456.3546 | -16.3502 | -40.7095 | 11.0621 | 7.9161 | 2.0557 | 0.5399 | 3.1621 | -0.8749 | 11.5993 | 4.7574 | 0.6178 | 0.6606 | 0.9635 | 0.7407 | -129.5642 | -0.3468 | 5.5594 | 1.6805 | -3.1709 | -1.51 | 4.251 |  | 3.0931 | -0.0075 | 4.0086 | 3.3657 | 3.3331 | 1.0748 | 10.7487 | 14.2624 | 14.8351 | 11.0905 | -0.0007 | -0.0026 | 0.0009 | 0.0034 | 0.0005 | -0.0003 | 0.024 | -0.0059 | 0.008 | -360.2388 | 17.4377 | -360.5035 | 17.6902 | -360.7743 | 18.1994 | -360.845 | 17.5855 | -352.6875 | 18.7436 | -352.6598 | 16.8258
12:35 | 4506 | 41.7959 | 202.3314 | 449.7666 | 456.383 | -16.2698 | -40.8663 | 11.0845 | 7.9055 | 2.1018 | 0.6042 | 3.31 | -0.8588 | 11.6206 | 4.6463 | 0.6164 | 0.6619 | 0.9611 | 0.7399 | -129.5631 | -0.5437 | 5.6012 | 1.6891 | -3.1042 | -1.5336 | 4.3027 |  | 3.188 | 0.0907 | 4.0113 | 3.3656 | 3.3335 | 1.0747 | 10.7278 | 14.2591 | 14.8216 | 11.0576 | -0.0001 | -0.0024 | 0.001 | 0.0043 | 0.0011 | -0.0004 | 0.0154 | -0.0046 | 0.0026 | -360.125 | 17.4069 | -360.5096 | 17.7334 | -360.882 | 18.222 | -360.8604 | 17.5424 | -352.6167 | 18.723 | -352.6906 | 16.8792
12:35 | 4507 | 41.7553 | 202.2729 | 449.8424 | 456.4251 | -16.2928 | -40.7845 | 11.1495 | 7.9025 | 2.083 | 0.4793 | 3.194 | -0.8237 | 11.6751 | 4.7281 | 0.6169 | 0.6647 | 0.964 | 0.7422 | -129.5259 | -0.4041 | 5.5684 | 1.652 | -3.0113 | -1.4897 | 4.3257 |  | 3.1651 | 0.0898 | 4.0095 | 3.3677 | 3.3364 | 1.0746 | 10.759 | 14.2673 | 14.8648 | 11.0771 | 0.0003 | -0.0032 | 0.0008 | 0.0035 | 0.0007 | -0.0001 | -0.0036 | -0.0051 | -0.0019 | -360.1896 | 17.409 | -360.445 | 17.6779 | -360.7927 | 18.22 | -360.885 | 17.6122 | -352.6844 | 18.723 | -352.6167 | 16.8238
12:35 | 4508 | 41.772 | 202.2999 | 449.8071 | 456.459 | -16.3327 | -40.7651 | 11.1142 | 7.8721 | 2.0972 | 0.4607 | 3.2412 | -0.7007 | 11.7011 | 4.7241 | 0.6167 | 0.6611 | 0.9648 | 0.7402 | -129.557 | -0.4796 | 5.6001 | 1.665 | -3.0781 | -1.5167 | 4.293 |  | 3.1373 | 0.168 | 4.009 | 3.366 | 3.3335 | 1.0744 | 10.781 | 14.2603 | 14.8577 | 11.1049 | -0.0002 | -0.003 | 0.0006 | 0.0042 | 0.0012 | 0.0001 | 0.0086 | -0.0143 | -0.0026 | -360.1927 | 17.4233 | -360.5281 | 17.7128 | -360.8358 | 18.1953 | -360.7743 | 17.5486 | -352.6352 | 18.7456 | -352.709 | 16.8689
12:35 | 4509 | 41.7218 | 202.199 | 449.6433 | 456.4521 | -16.348 | -40.6935 | 11.1462 | 7.8761 | 2.1409 | 0.5151 | 3.1869 | -0.7758 | 11.6897 | 4.6357 | 0.6172 | 0.6642 | 0.9622 | 0.7431 | -129.5407 | -0.377 | 5.5894 | 1.6971 | -2.9905 | -1.5108 | 4.3306 |  | 3.1788 | 0.1431 | 4.0103 | 3.3675 | 3.337 | 1.0743 | 10.729 | 14.2776 | 14.8287 | 11.0645 | -0.0002 | -0.0028 | 0.0008 | 0.0038 | 0.0008 | -0.0003 | 0.0138 | -0.0205 | 0.0014 | -360.1373 | 17.3843 | -360.405 | 17.6697 | -360.7897 | 18.2344 | -360.8758 | 17.5855 | -352.6383 | 18.6943 | -352.5983 | 16.8217
12:35 | 4510 | 41.7909 | 202.2239 | 449.7021 | 456.5116 | -16.28 | -40.7177 | 11.1892 | 7.8294 | 2.1517 | 0.5169 | 3.2749 | -0.8454 | 11.6357 | 4.6971 | 0.6178 | 0.6633 | 0.9644 | 0.7431 | -129.5016 | -0.3574 | 5.5995 | 1.5673 | -3.05 | -1.5855 | 4.3411 |  | 3.1389 | 0.1466 | 4.0101 | 3.3667 | 3.3342 | 1.0744 | 10.7625 | 14.2708 | 14.8342 | 11.0861 | -0.0001 | -0.0026 | 0.0003 | 0.004 | 0.0005 | -0.0006 | 0.0178 | -0.0213 | -0.0055 | -360.2173 | 17.4418 | -360.5158 | 17.6841 | -360.7866 | 18.1789 | -360.7958 | 17.5732 | -352.6813 | 18.7538 | -352.7183 | 16.8402
12:35 | 4511 | 41.7718 | 202.3199 | 449.7086 | 456.3858 | -16.2558 | -40.5196 | 11.1763 | 7.8882 | 2.0898 | 0.5223 | 3.2482 | -0.7246 | 11.7202 | 4.7822 | 0.6163 | 0.6623 | 0.964 | 0.7407 | -129.5291 | -0.3703 | 5.5832 | 1.6033 | -3.0682 | -1.5315 | 4.387 |  | 3.1026 | 0.1298 | 4.0111 | 3.3662 | 3.3348 | 1.0738 | 10.7174 | 14.237 | 14.8103 | 11.0822 | 0.0007 | -0.0028 | 0.0008 | 0.004 | 0.0009 | -0.0003 | 0.0072 | 0.0052 | 0.0073 | -360.1096 | 17.3864 | -360.4512 | 17.6902 | -360.8697 | 18.2385 | -360.8574 | 17.5629 | -352.6013 | 18.7004 | -352.6198 | 16.8546
12:35 | 4512 | 41.7536 | 202.3484 | 449.7092 | 456.4075 | -16.2592 | -40.6292 | 11.2038 | 7.8658 | 2.1395 | 0.4697 | 3.271 | -0.7563 | 11.6845 | 4.7098 | 0.6165 | 0.6629 | 0.9625 | 0.7407 | -129.463 | -0.3978 | 5.5641 | 1.6131 | -2.9562 | -1.4823 | 4.4452 |  | 3.1042 | 0.2457 | 4.0104 | 3.3698 | 3.3362 | 1.0746 | 10.7521 | 14.2603 | 14.8345 | 11.0645 | 0.0001 | -0.0031 | 0.0007 | 0.0036 | 0.0006 | -0.0004 | 0.0134 | -0.0033 | -0.0149 | -360.2265 | 17.4274 | -360.4542 | 17.6492 | -360.7589 | 18.1912 | -360.8327 | 17.5917 | -352.6721 | 18.7374 | -352.626 | 16.8156
12:35 | 4513 | 41.8195 | 202.2668 | 449.7459 | 456.3204 | -16.2302 | -40.6548 | 11.1129 | 7.8573 | 2.1426 | 0.5076 | 3.2879 | -0.7485 | 11.6877 | 4.6223 | 0.6169 | 0.6621 | 0.9629 | 0.7408 | -129.5625 | -0.4389 | 5.5867 | 1.6042 | -3.0029 | -1.5099 | 4.3432 |  | 3.1331 | 0.2057 | 4.0096 | 3.3661 | 3.3343 | 1.0751 | 10.7475 | 14.2788 | 14.8532 | 11.1002 | 0 | -0.0026 | 0.0012 | 0.0041 | 0.0009 | -0.0006 | 0.0035 | -0.0192 | -0.0019 | -360.1127 | 17.4007 | -360.4789 | 17.7046 | -360.8789 | 18.22 | -360.8235 | 17.5404 | -352.5952 | 18.7128 | -352.6721 | 16.8669
12:35 | 4514 | 41.8175 | 202.2421 | 449.755 | 456.411 | -16.2392 | -40.5157 | 11.0712 | 7.8125 | 2.0989 | 0.6213 | 3.2023 | -0.7411 | 11.6603 | 4.6773 | 0.6169 | 0.6598 | 0.9603 | 0.7407 | -129.5765 | -0.5624 | 5.5843 | 1.6407 | -3.0413 | -1.4543 | 4.3385 |  | 3.0941 | 0.2473 | 4.0108 | 3.3677 | 3.336 | 1.0748 | 10.7544 | 14.2569 | 14.8315 | 11.0782 | -0.0004 | -0.0024 | 0.0011 | 0.0043 | 0.0005 | -0.0004 | 0.0152 | -0.0109 | 0.0026 | -360.165 | 17.3864 | -360.3989 | 17.641 | -360.7743 | 18.222 | -360.8666 | 17.5855 | -352.6598 | 18.7169 | -352.6013 | 16.8074
12:35 | 4515 | 41.8211 | 202.267 | 449.759 | 456.4417 | -16.2845 | -40.6103 | 11.1644 | 7.7644 | 2.1277 | 0.5848 | 3.172 | -0.8002 | 11.7392 | 4.6271 | 0.6148 | 0.6587 | 0.961 | 0.742 | -129.6011 | -0.4241 | 5.5967 | 1.7735 | -3.0239 | -1.4162 | 4.3542 |  | 3.0953 | 0.1297 | 4.0116 | 3.3677 | 3.3368 | 1.0751 | 10.737 | 14.2802 | 14.8788 | 11.1009 | 0.0001 | -0.0031 | 0.0011 | 0.0042 | 0.0013 | -0.0008 | 0.014 | 0.0021 | 0.0093 | -360.1527 | 17.4233 | -360.4881 | 17.6923 | -360.8204 | 18.1728 | -360.7804 | 17.5383 | -352.5983 | 18.7477 | -352.6875 | 16.8484
12:35 | 4516 | 41.8402 | 202.2041 | 449.7613 | 456.3747 | -16.3372 | -40.6356 | 11.0469 | 7.8726 | 2.0884 | 0.5685 | 3.2958 | -0.9325 | 11.6599 | 4.5407 | 0.6163 | 0.6635 | 0.9638 | 0.7422 | -129.67 | -0.5151 | 5.5244 | 1.8215 | -3.0721 | -1.4175 | 4.3589 |  | 3.153 | 0.2594 | 4.0101 | 3.3706 | 3.3362 | 1.0756 | 10.7418 | 14.2554 | 14.8395 | 11.0432 | 0.0003 | -0.0031 | 0.0007 | 0.0041 | 0.0004 | -0.0004 | -0.0039 | -0.0044 | -0.0006 | -360.1588 | 17.3843 | -360.3896 | 17.6574 | -360.7897 | 18.2302 | -360.8604 | 17.5671 | -352.6075 | 18.7087 | -352.5798 | 16.8197
12:35 | 4517 | 41.8484 | 202.3504 | 449.7435 | 456.438 | -16.329 | -40.7073 | 11.0712 | 7.819 | 2.0438 | 0.6537 | 3.2501 | -0.8865 | 11.6733 | 4.5667 | 0.6166 | 0.662 | 0.9619 | 0.7426 | -129.6351 | -0.4529 | 5.4353 | 1.7977 | -3.084 | -1.4775 | 4.3237 |  | 3.1381 | 0.1987 | 4.0109 | 3.3648 | 3.3371 | 1.0753 | 10.7532 | 14.2676 | 14.8612 | 11.0879 | -0.0004 | -0.0026 | 0.0005 | 0.004 | 0.0011 | -0.0005 | 0.0199 | 0.005 | 0.0097 | -360.2204 | 17.4377 | -360.485 | 17.6718 | -360.7558 | 18.1645 | -360.7527 | 17.565 | -352.669 | 18.76 | -352.6937 | 16.8299
12:35 | 4518 | 41.8215 | 202.2899 | 449.6752 | 456.4389 | -16.3324 | -40.6544 | 11.0432 | 7.8283 | 2.1024 | 0.6272 | 3.2207 | -0.9465 | 11.6948 | 4.6328 | 0.6157 | 0.6637 | 0.964 | 0.7426 | -129.6009 | -0.389 | 5.5361 | 1.7316 | -3.0341 | -1.4492 | 4.2838 |  | 3.1726 | 0.124 | 4.0102 | 3.3672 | 3.335 | 1.075 | 10.766 | 14.2453 | 14.8662 | 11.0897 | 0 | -0.0025 | 0.0004 | 0.0039 | 0.0006 | -0.0005 | 0.0044 | -0.0089 | -0.0174 | -360.1034 | 17.3782 | -360.4266 | 17.6902 | -360.8358 | 18.2261 | -360.8358 | 17.5445 | -352.5829 | 18.6943 | -352.6106 | 16.8361
12:35 | 4519 | 41.9296 | 202.2658 | 449.7198 | 456.3867 | -16.2923 | -40.6368 | 11.1667 | 7.9075 | 2.1358 | 0.6827 | 3.3158 | -0.8606 | 11.715 | 4.6754 | 0.6163 | 0.6633 | 0.9611 | 0.7432 | -129.6513 | -0.4872 | 5.4016 | 1.7194 | -3.0466 | -1.5043 | 4.3397 |  | 3.1514 | 0.13 | 4.0111 | 3.3657 | 3.3316 | 1.0745 | 10.7199 | 14.2332 | 14.7867 | 11.0508 | -0.0002 | -0.0033 | 0.0009 | 0.0034 | 0.001 | -0.0004 | 0.0204 | -0.0189 | -0.0133 | -360.2081 | 17.4254 | -360.4204 | 17.6512 | -360.7343 | 18.183 | -360.8143 | 17.5691 | -352.6229 | 18.7436 | -352.6229 | 16.7991
12:35 | 4520 | 41.9134 | 202.2542 | 449.7717 | 456.4325 | -16.1833 | -40.5361 | 11.2637 | 7.9351 | 2.1215 | 0.7181 | 3.3256 | -0.9368 | 11.6727 | 4.6129 | 0.6182 | 0.6617 | 0.9634 | 0.7424 | -129.6339 | -0.4255 | 5.3674 | 1.7307 | -3.0601 | -1.4052 | 4.3326 |  | 3.1603 | 0.096 | 4.0116 | 3.3684 | 3.3347 | 1.0745 | 10.7613 | 14.2756 | 14.8802 | 11.0962 | 0.0003 | -0.0032 | 0.0012 | 0.0039 | 0.0003 | -0.0003 | -0.0058 | -0.0083 | -0.0088 | -360.1096 | 17.3966 | -360.4604 | 17.6964 | -360.882 | 18.2138 | -360.7927 | 17.5363 | -352.586 | 18.7169 | -352.6475 | 16.8546
12:35 | 4521 | 41.9389 | 202.3397 | 449.7895 | 456.4674 | -16.3029 | -40.617 | 11.1274 | 7.9298 | 2.1865 | 0.7961 | 3.2738 | -0.811 | 11.6975 | 4.6025 | 0.616 | 0.6623 | 0.9614 | 0.7413 | -129.5575 | -0.4039 | 5.5268 | 1.6896 | -3.16 | -1.5011 | 4.313 |  | 3.0932 | 0.1118 | 4.0103 | 3.3652 | 3.3365 | 1.0738 | 10.7359 | 14.2673 | 14.8475 | 11.1002 | -0.0003 | -0.0031 | 0.0011 | 0.0039 | 0.0008 | -0.0002 | 0.0271 | -0.0019 | 0.0168 | -360.1896 | 17.3987 | -360.405 | 17.6471 | -360.7804 | 18.2138 | -360.8604 | 17.5835 | -352.6629 | 18.7066 | -352.5921 | 16.8012
12:35 | 4522 | 41.9321 | 202.3721 | 449.8376 | 456.5433 | -16.2237 | -40.6115 | 11.1446 | 7.8931 | 2.2327 | 0.7039 | 3.3412 | -0.8028 | 11.6457 | 4.5351 | 0.6172 | 0.6575 | 0.9619 | 0.7421 | -129.577 | -0.3432 | 5.5367 | 1.7217 | -3.1256 | -1.4921 | 4.323 |  | 3.1259 | 0.2277 | 4.0114 | 3.3662 | 3.3324 | 1.0765 | 10.7393 | 14.2535 | 14.8342 | 11.0861 | -0.0003 | -0.0025 | 0.0013 | 0.0041 | 0.0011 | 0 | 0.0235 | 0.0008 | -0.0269 | -360.1465 | 17.4295 | -360.5096 | 17.6964 | -360.8143 | 18.1707 | -360.7343 | 17.5383 | -352.5983 | 18.7333 | -352.709 | 16.8464
12:35 | 4523 | 41.8071 | 202.287 | 449.7046 | 456.3399 | -16.2863 | -40.4902 | 11.2721 | 7.934 | 2.311 | 0.6604 | 3.3733 | -0.8629 | 11.5758 | 4.5912 | 0.6167 | 0.6602 | 0.9637 | 0.7408 | -129.6671 | -0.3578 | 5.5902 | 1.7053 | -3.1603 | -1.4756 | 4.2644 |  | 3.0562 | 0.1454 | 4.0116 | 3.3698 | 3.3375 | 1.0749 | 10.767 | 14.2932 | 14.8418 | 11.107 | 0.0002 | -0.0028 | 0.0011 | 0.0042 | 0.0007 | -0.0006 | 0.0135 | 0.0041 | -0.0056 | -360.1065 | 17.3802 | -360.3865 | 17.6615 | -360.805 | 18.2302 | -360.8389 | 17.5547 | -352.5983 | 18.6922 | -352.5644 | 16.8135
12:35 | 4524 | 41.9061 | 202.3805 | 449.7385 | 456.4866 | -16.3708 | -40.5591 | 11.1761 | 7.9226 | 2.2487 | 0.5635 | 3.3647 | -0.858 | 11.5913 | 4.6508 | 0.6162 | 0.6605 | 0.9646 | 0.7416 | -129.7578 | -0.4581 | 5.4348 | 1.7959 | -3.1967 | -1.5309 | 4.3391 |  | 3.0947 | 0.0563 | 4.0115 | 3.3683 | 3.3373 | 1.0776 | 10.7695 | 14.3123 | 14.8866 | 11.1222 | -0.0002 | -0.0034 | 0.0002 | 0.0036 | 0.001 | -0.0004 | 0.0021 | 0.0046 | 0.0028 | -360.2235 | 17.4377 | -360.4696 | 17.682 | -360.7373 | 18.1522 | -360.7712 | 17.5547 | -352.626 | 18.7497 | -352.6537 | 16.8135
12:35 | 4525 | 41.9886 | 202.3709 | 449.8292 | 456.5809 | -16.3155 | -40.4853 | 11.1356 | 7.9553 | 2.2326 | 0.5496 | 3.2898 | -0.8012 | 11.6999 | 4.6529 | 0.6159 | 0.6598 | 0.9631 | 0.7429 | -129.7283 | -0.4825 | 5.4076 | 1.6935 | -3.1242 | -1.3945 | 4.3539 |  | 3.053 | 0.0616 | 4.0117 | 3.3676 | 3.337 | 1.076 | 10.7669 | 14.2934 | 14.8602 | 11.1009 | 0.0001 | -0.0027 | 0.001 | 0.0044 | 0.0009 | 0 | 0.0118 | -0.0054 | -0.0206 | -360.0788 | 17.3802 | -360.4235 | 17.6841 | -360.842 | 18.2118 | -360.8143 | 17.5342 | -352.5644 | 18.6943 | -352.589 | 16.8402
12:35 | 4526 | 41.9522 | 202.3786 | 449.6343 | 456.5081 | -16.3617 | -40.6079 | 11.0425 | 7.9492 | 2.2155 | 0.6432 | 3.3321 | -0.7902 | 11.7215 | 4.5804 | 0.6177 | 0.6605 | 0.9649 | 0.7429 | -129.699 | -0.4658 | 5.5944 | 1.5954 | -3.131 | -1.4547 | 4.3205 |  | 3.1135 | 0.0336 | 4.0107 | 3.3651 | 3.3316 | 1.0747 | 10.7625 | 14.2822 | 14.8737 | 11.0981 | -0.0004 | -0.0027 | 0.0003 | 0.0034 | 0.0011 | -0.0008 | 0.0086 | -0.0149 | -0.0086 | -360.1865 | 17.411 | -360.4081 | 17.6615 | -360.7312 | 18.181 | -360.8297 | 17.5732 | -352.6506 | 18.7333 | -352.586 | 16.795
12:35 | 4527 | 41.8286 | 202.2779 | 449.7564 | 456.4045 | -16.3329 | -40.5241 | 11.0457 | 8.0325 | 2.237 | 0.7512 | 3.398 | -0.7609 | 11.7148 | 4.6274 | 0.6179 | 0.6609 | 0.9616 | 0.7417 | -129.6386 | -0.3515 | 5.585 | 1.7718 | -3.1266 | -1.4226 | 4.2823 |  | 3.1658 | 0.0949 | 4.0104 | 3.367 | 3.3319 | 1.0748 | 10.7256 | 14.2449 | 14.8514 | 11.0966 | -0.0002 | -0.0029 | 0.0005 | 0.0038 | 0.0007 | -0.0001 | 0.0104 | -0.0129 | 0.0117 | -360.1034 | 17.4151 | -360.4481 | 17.7046 | -360.8297 | 18.181 | -360.7866 | 17.5239 | -352.586 | 18.7189 | -352.6444 | 16.8423
12:35 | 4528 | 41.9391 | 202.3576 | 449.7645 | 456.5 | -16.2728 | -40.541 | 11.0752 | 8.0001 | 2.3084 | 0.7775 | 3.3225 | -0.8134 | 11.7218 | 4.5813 | 0.6173 | 0.6621 | 0.9622 | 0.7416 | -129.6543 | -0.3352 | 5.5536 | 1.8435 | -3.0969 | -1.3772 | 4.34 |  | 3.1168 | 0.0957 | 4.0109 | 3.3663 | 3.3331 | 1.0767 | 10.7254 | 14.2512 | 14.8094 | 11.072 | 0.0003 | -0.003 | 0.0011 | 0.0039 | 0.0011 | -0.0006 | 0.0074 | -0.0113 | -0.0207 | -360.1435 | 17.3802 | -360.3742 | 17.6553 | -360.7712 | 18.1933 | -360.8635 | 17.5814 | -352.629 | 18.6984 | -352.5767 | 16.8032
12:35 | 4529 | 41.9699 | 202.2685 | 449.7026 | 456.4491 | -16.3594 | -40.5748 | 11.1003 | 7.9688 | 2.3425 | 0.6859 | 3.3154 | -0.7629 | 11.7447 | 4.6749 | 0.6172 | 0.6649 | 0.9619 | 0.7423 | -129.6194 | -0.2947 | 5.519 | 1.753 | -3.1497 | -1.3695 | 4.279 |  | 3.1738 | 0.0485 | 4.0102 | 3.3669 | 3.334 | 1.075 | 10.7452 | 14.2418 | 14.8447 | 11.0692 | 0 | -0.003 | 0.0008 | 0.0035 | 0.0007 | -0.0001 | 0.019 | -0.0095 | -0.0067 | -360.1773 | 17.4418 | -360.4727 | 17.6923 | -360.805 | 18.1563 | -360.7435 | 17.5445 | -352.5736 | 18.7436 | -352.669 | 16.8258
12:35 | 4530 | 42.0236 | 202.3312 | 449.7481 | 456.5223 | -16.3078 | -40.5758 | 11.1689 | 7.9082 | 2.3759 | 0.6922 | 3.294 | -0.8404 | 11.7559 | 4.6939 | 0.617 | 0.6619 | 0.9609 | 0.7428 | -129.6493 | -0.279 | 5.6187 | 1.8443 | -3.1019 | -1.4484 | 4.328 |  | 3.1848 | 0.0853 | 4.0114 | 3.3675 | 3.3347 | 1.0761 | 10.7278 | 14.236 | 14.7984 | 11.0576 | -0.0002 | -0.0027 | 0.0013 | 0.004 | 0.0009 | -0.0007 | -0.0052 | 0.0007 | -0.0297 | -360.1219 | 17.372 | -360.4204 | 17.6882 | -360.8112 | 18.2138 | -360.845 | 17.5465 | -352.6106 | 18.6922 | -352.5736 | 16.8238
12:35 | 4531 | 41.971 | 202.3446 | 449.8213 | 456.5603 | -16.3257 | -40.7155 | 11.1819 | 7.8995 | 2.299 | 0.6536 | 3.3558 | -0.8707 | 11.6894 | 4.5915 | 0.6163 | 0.6605 | 0.9596 | 0.7428 | -129.694 | -0.2861 | 5.5718 | 1.7288 | -3.085 | -1.3559 | 4.3586 |  | 3.1843 | 0.1173 | 4.0111 | 3.3655 | 3.3331 | 1.0757 | 10.7463 | 14.2547 | 14.8414 | 11.093 | 0 | -0.0028 | 0.0004 | 0.0036 | 0.0004 | -0.0005 | 0.0056 | -0.0094 | -0.0176 | -360.2296 | 17.4397 | -360.4819 | 17.6615 | -360.7527 | 18.1584 | -360.7804 | 17.5671 | -352.626 | 18.7538 | -352.6506 | 16.8012
12:35 | 4532 | 42.0182 | 202.369 | 449.7293 | 456.5406 | -16.3757 | -40.6282 | 11.1163 | 7.8634 | 2.2808 | 0.5537 | 3.1148 | -0.8041 | 11.6783 | 4.6133 | 0.6174 | 0.6621 | 0.9656 | 0.7416 | -129.6517 | -0.3151 | 5.6384 | 1.7253 | -3.0591 | -1.3002 | 4.4287 |  | 3.1003 | 0.1367 | 4.0109 | 3.3646 | 3.3347 | 1.0752 | 10.7451 | 14.2477 | 14.8458 | 11.063 | 0.0004 | -0.0027 | 0.0003 | 0.004 | 0.0008 | -0.0004 | 0.0016 | -0.0053 | -0.003 | -360.125 | 17.3925 | -360.4666 | 17.719 | -360.8635 | 18.2159 | -360.8112 | 17.5363 | -352.5798 | 18.7087 | -352.6383 | 16.8484
12:35 | 4533 | 42.0487 | 202.3597 | 449.7335 | 456.5581 | -16.4554 | -40.7645 | 10.9764 | 7.9327 | 2.2829 | 0.5306 | 3.1611 | -0.8209 | 11.7274 | 4.5679 | 0.6162 | 0.6591 | 0.963 | 0.7405 | -129.6742 | -0.287 | 5.6391 | 1.6092 | -3.1776 | -1.4582 | 4.3023 |  | 3.1 | 0.1497 | 4.012 | 3.3706 | 3.337 | 1.0764 | 10.7613 | 14.2582 | 14.8513 | 11.0962 | 0 | -0.0029 | 0.0009 | 0.0042 | 0.0012 | -0.0004 | 0.0233 | -0.0029 | 0.0012 | -360.2327 | 17.4377 | -360.4542 | 17.6636 | -360.7773 | 18.1953 | -360.8574 | 17.602 | -352.6598 | 18.7395 | -352.6198 | 16.7991
12:35 | 4534 | 41.9673 | 202.328 | 449.6875 | 456.4547 | -16.4874 | -40.7928 | 11.0109 | 7.8917 | 2.3113 | 0.6126 | 3.1909 | -0.8081 | 11.68 | 4.6143 | 0.6171 | 0.6597 | 0.9643 | 0.743 | -129.6656 | -0.3011 | 5.5773 | 1.5755 | -3.1817 | -1.5747 | 4.293 |  | 3.115 | 0.1103 | 4.01 | 3.3665 | 3.3359 | 1.0761 | 10.7371 | 14.2508 | 14.8409 | 11.0847 | -0.0002 | -0.0023 | 0.0002 | 0.0034 | 0.0006 | -0.0009 | 0.0094 | -0.0109 | -0.0059 | -360.1588 | 17.4418 | -360.5189 | 17.7334 | -360.8943 | 18.1933 | -360.805 | 17.5568 | -352.5983 | 18.7436 | -352.6937 | 16.8607
12:35 | 4535 | 42.0039 | 202.3428 | 449.7616 | 456.5294 | -16.4223 | -40.7749 | 11.0324 | 7.8775 | 2.3168 | 0.6868 | 3.1753 | -0.7364 | 11.7731 | 4.5417 | 0.6158 | 0.66 | 0.9615 | 0.7413 | -129.713 | -0.3079 | 5.6134 | 1.8002 | -3.1717 | -1.4275 | 4.3581 |  | 3.1694 | 0.1571 | 4.0103 | 3.3675 | 3.3361 | 1.0752 | 10.7614 | 14.2579 | 14.8665 | 11.0854 | -0.0003 | -0.0026 | 0.0011 | 0.0038 | 0.0011 | -0.0005 | 0.0172 | -0.0029 | 0.0062 | -360.1896 | 17.411 | -360.4358 | 17.68 | -360.7989 | 18.222 | -360.8758 | 17.604 | -352.629 | 18.7148 | -352.626 | 16.8074
12:35 | 4536 | 41.9809 | 202.3681 | 449.8052 | 456.5458 | -16.3594 | -40.7959 | 11.085 | 7.8357 | 2.2317 | 0.6944 | 3.171 | -0.7376 | 11.7042 | 4.6254 | 0.6156 | 0.6595 | 0.9598 | 0.7422 | -129.6811 | -0.3421 | 5.633 | 1.8068 | -3.1575 | -1.5511 | 4.2898 |  | 3.1765 | 0.1128 | 4.0103 | 3.3678 | 3.3345 | 1.0753 | 10.7302 | 14.2613 | 14.829 | 11.089 | 0 | -0.0031 | 0.0009 | 0.0039 | 0.0004 | -0.0004 | 0.0069 | -0.0184 | -0.0137 | -360.1865 | 17.4664 | -360.5373 | 17.7272 | -360.8574 | 18.1789 | -360.7773 | 17.5712 | -352.626 | 18.762 | -352.706 | 16.8423
12:35 | 4537 | 42.0296 | 202.4157 | 449.832 | 456.6198 | -16.3607 | -40.7895 | 11.1038 | 7.8968 | 2.2536 | 0.62 | 3.1446 | -0.7951 | 11.7089 | 4.5786 | 0.6167 | 0.6629 | 0.9625 | 0.7405 | -129.7262 | -0.3119 | 5.6307 | 1.8745 | -3.122 | -1.4422 | 4.2575 |  | 3.1504 | 0.1241 | 4.01 | 3.3685 | 3.3379 | 1.0759 | 10.7452 | 14.2649 | 14.8389 | 11.0923 | 0 | -0.0032 | 0.0007 | 0.0035 | 0.001 | -0.0002 | 0.0044 | -0.0085 | -0.0125 | -360.1681 | 17.4028 | -360.4542 | 17.7128 | -360.8727 | 18.2405 | -360.9066 | 17.5876 | -352.6198 | 18.7107 | -352.6198 | 16.8279
12:35 | 4538 | 42.0007 | 202.2679 | 449.7921 | 456.5329 | -16.3476 | -40.7426 | 11.1022 | 7.8858 | 2.3041 | 0.6052 | 3.2474 | -0.8195 | 11.7214 | 4.5578 | 0.6175 | 0.6601 | 0.9634 | 0.7409 | -129.6572 | -0.2772 | 5.6376 | 1.7976 | -3.0994 | -1.4277 | 4.4071 |  | 3.1505 | 0.1382 | 4.0113 | 3.3688 | 3.3356 | 1.0744 | 10.728 | 14.2124 | 14.8184 | 11.0761 | -0.0003 | -0.0028 | 0.0013 | 0.0044 | 0.0006 | -0.0004 | 0.0131 | -0.0006 | -0.0095 | -360.2573 | 17.4623 | -360.5066 | 17.7046 | -360.8174 | 18.181 | -360.8235 | 17.5978 | -352.6844 | 18.762 | -352.6752 | 16.8299
12:35 | 4539 | 41.9763 | 202.2102 | 449.7393 | 456.4732 | -16.3141 | -40.7189 | 11.1293 | 7.8869 | 2.2234 | 0.6496 | 3.2447 | -0.8135 | 11.6968 | 4.553 | 0.6166 | 0.6612 | 0.965 | 0.7415 | -129.7644 | -0.3441 | 5.5449 | 1.7321 | -3.0538 | -1.4105 | 4.4291 |  | 3.1589 | 0.1272 | 4.0105 | 3.3631 | 3.3328 | 1.0744 | 10.7475 | 14.2499 | 14.8359 | 11.0829 | -0.0002 | -0.0025 | 0.0008 | 0.004 | 0.0013 | -0.0004 | -0.0043 | -0.007 | -0.0168 | -360.1619 | 17.4069 | -360.4727 | 17.7354 | -360.885 | 18.2323 | -360.8697 | 17.565 | -352.629 | 18.7066 | -352.6537 | 16.8525
12:35 | 4540 | 42.0019 | 202.223 | 449.7444 | 456.5138 | -16.3773 | -40.6039 | 11.1436 | 8.0001 | 2.1944 | 0.6539 | 3.2525 | -0.8098 | 11.7274 | 4.5449 | 0.6172 | 0.6615 | 0.9652 | 0.742 | -129.7418 | -0.2161 | 5.4925 | 1.7071 | -3.1344 | -1.3896 | 4.3065 |  | 3.1626 | 0.147 | 4.0093 | 3.3671 | 3.3364 | 1.0767 | 10.7312 | 14.2512 | 14.8209 | 11.0836 | 0.0004 | -0.0028 | 0.0003 | 0.0035 | 0.0011 | -0.0001 | -0.0037 | 0.0035 | -0.0338 | -360.2327 | 17.4603 | -360.5035 | 17.68 | -360.7958 | 18.183 | -360.8789 | 17.6163 | -352.7029 | 18.762 | -352.6844 | 16.8094
12:35 | 4541 | 41.9656 | 202.1946 | 449.7836 | 456.4774 | -16.4011 | -40.6356 | 11.115 | 8.0045 | 2.2728 | 0.6922 | 3.2654 | -0.7833 | 11.6614 | 4.4473 | 0.618 | 0.6618 | 0.9649 | 0.7421 | -129.767 | -0.3564 | 5.4709 | 1.6856 | -3.0399 | -1.3359 | 4.4171 |  | 3.229 | 0.1671 | 4.0088 | 3.3682 | 3.3396 | 1.0765 | 10.7499 | 14.2576 | 14.8586 | 11.1035 | -0.0001 | -0.0033 | 0.0008 | 0.0042 | 0.0009 | -0.0007 | 0.0198 | -0.0003 | -0.0111 | -360.1558 | 17.4377 | -360.5343 | 17.7539 | -360.8943 | 18.2138 | -360.845 | 17.565 | -352.5983 | 18.7415 | -352.709 | 16.8628
12:35 | 4542 | 41.9819 | 202.1686 | 449.7309 | 456.4908 | -16.4689 | -40.6762 | 11.1236 | 7.9783 | 2.1823 | 0.7493 | 3.2995 | -0.8392 | 11.7377 | 4.5143 | 0.6171 | 0.6629 | 0.9627 | 0.7433 | -129.7068 | -0.2709 | 5.4009 | 1.4998 | -3.0657 | -1.343 | 4.4258 |  | 3.2273 | 0.1444 | 4.0113 | 3.3685 | 3.3354 | 1.0762 | 10.7532 | 14.2327 | 14.8601 | 11.0998 | -0.0001 | -0.0029 | 0.0005 | 0.0036 | 0.0007 | 0.0001 | 0.007 | -0.0249 | -0.0208 | -360.245 | 17.4233 | -360.4389 | 17.6944 | -360.8112 | 18.222 | -360.9035 | 17.6163 | -352.6598 | 18.7333 | -352.6167 | 16.8012
12:35 | 4543 | 41.9558 | 202.2672 | 449.7838 | 456.4092 | -16.4411 | -40.626 | 11.1223 | 7.9579 | 2.2054 | 0.6355 | 3.2595 | -0.8047 | 11.6772 | 4.4888 | 0.6172 | 0.6623 | 0.9658 | 0.7419 | -129.7068 | -0.409 | 5.4698 | 1.5737 | -3.0341 | -1.3668 | 4.3728 |  | 3.1792 | 0.2164 | 4.01 | 3.3639 | 3.3336 | 1.0768 | 10.7926 | 14.2893 | 14.905 | 11.0988 | -0.0005 | -0.0027 | 0.0012 | 0.0041 | 0.0009 | -0.0005 | 0.0154 | 0.0002 | 0.0044 | -360.2204 | 17.4623 | -360.5189 | 17.7395 | -360.8574 | 18.1851 | -360.805 | 17.5629 | -352.6444 | 18.7559 | -352.7213 | 16.8443
12:35 | 4544 | 42.0074 | 202.2489 | 449.8594 | 456.4776 | -16.4024 | -40.6555 | 11.126 | 7.9702 | 2.1395 | 0.5469 | 3.1124 | -0.8606 | 11.6906 | 4.5285 | 0.6177 | 0.6601 | 0.9655 | 0.7427 | -129.6427 | -0.38 | 5.4194 | 1.6735 | -3.0883 | -1.4695 | 4.4242 |  | 3.1702 | 0.1006 | 4.0103 | 3.366 | 3.3365 | 1.0757 | 10.7348 | 14.2314 | 14.8808 | 11.076 | -0.0001 | -0.0028 | 0.0014 | 0.0042 | 0.001 | -0.0003 | 0.0258 | 0.0016 | -0.0146 | -360.1588 | 17.4069 | -360.4419 | 17.7026 | -360.8666 | 18.2302 | -360.885 | 17.5917 | -352.6413 | 18.7045 | -352.6136 | 16.8135
12:35 | 4545 | 42.0683 | 202.3562 | 449.7885 | 456.5879 | -16.3905 | -40.5432 | 11.2437 | 7.9951 | 2.2753 | 0.6627 | 3.178 | -0.8057 | 11.7631 | 4.5043 | 0.6168 | 0.6619 | 0.9621 | 0.7441 | -129.5373 | -0.3569 | 5.5246 | 1.7063 | -3.0984 | -1.4544 | 4.3484 |  | 3.2089 | 0.0899 | 4.0095 | 3.3644 | 3.3353 | 1.0769 | 10.7532 | 14.2674 | 14.8659 | 11.123 | 0.0002 | -0.0034 | 0.0007 | 0.0038 | 0.001 | -0.0002 | 0.0118 | -0.0132 | -0.0003 | -360.245 | 17.4685 | -360.5127 | 17.6985 | -360.8174 | 18.1892 | -360.8358 | 17.5876 | -352.6752 | 18.7682 | -352.6813 | 16.8053
12:35 | 4546 | 42.0421 | 202.3294 | 449.7728 | 456.4813 | -16.4264 | -40.6553 | 11.1834 | 7.9299 | 2.1624 | 0.623 | 3.1483 | -0.7979 | 11.7117 | 4.4571 | 0.6162 | 0.6609 | 0.9629 | 0.7415 | -129.5669 | -0.3733 | 5.5395 | 1.762 | -3.073 | -1.4204 | 4.4022 |  | 3.2503 | 0.0543 | 4.0105 | 3.3693 | 3.334 | 1.0775 | 10.7637 | 14.2892 | 14.8692 | 11.0991 | -0.0002 | -0.0029 | 0.0007 | 0.0038 | 0.0007 | -0.0009 | 0.0021 | -0.0059 | -0.0022 | -360.1496 | 17.4028 | -360.4635 | 17.7169 | -360.8604 | 18.2426 | -360.8758 | 17.5588 | -352.629 | 18.7025 | -352.6444 | 16.834
12:35 | 4547 | 42.0812 | 202.4202 | 449.7922 | 456.5443 | -16.4081 | -40.5973 | 11.2439 | 7.9267 | 2.1662 | 0.5408 | 3.1415 | -0.7882 | 11.7565 | 4.4687 | 0.6173 | 0.6603 | 0.9634 | 0.742 | -129.5728 | -0.3273 | 5.5088 | 1.8192 | -3.0021 | -1.3171 | 4.3948 |  | 3.1762 | 0.0972 | 4.0103 | 3.3658 | 3.3355 | 1.0765 | 10.767 | 14.2931 | 14.8697 | 11.1074 | 0.0002 | -0.0022 | 0.0009 | 0.0045 | 0.0005 | -0.0003 | 0.0214 | -0.0022 | -0.0186 | -360.2573 | 17.4541 | -360.4881 | 17.68 | -360.7835 | 18.181 | -360.8512 | 17.6143 | -352.6906 | 18.7518 | -352.6444 | 16.7827
12:36 | 4548 | 42.0444 | 202.4248 | 449.7034 | 456.5022 | -16.3714 | -40.5784 | 11.2277 | 7.9981 | 2.3136 | 0.5942 | 3.1506 | -0.7701 | 11.686 | 4.5735 | 0.6159 | 0.6611 | 0.963 | 0.743 | -129.4829 | -0.2423 | 5.5292 | 1.7024 | -3.1042 | -1.4513 | 4.389 |  | 3.2207 | 0.2292 | 4.0107 | 3.3676 | 3.3329 | 1.0751 | 10.7475 | 14.2613 | 14.8638 | 11.0948 | 0.0001 | -0.003 | 0.0003 | 0.0038 | 0.0012 | -0.0009 | 0.0041 | -0.0065 | -0.027 | -360.1558 | 17.4274 | -360.525 | 17.7313 | -360.8912 | 18.2015 | -360.802 | 17.5486 | -352.6044 | 18.7312 | -352.6998 | 16.8299
12:36 | 4549 | 41.9976 | 202.3726 | 449.7489 | 456.5027 | -16.3829 | -40.6607 | 11.1934 | 8.0006 | 2.2511 | 0.6251 | 3.1781 | -0.8495 | 11.7179 | 4.5746 | 0.6175 | 0.662 | 0.9665 | 0.7424 | -129.4515 | -0.2956 | 5.5761 | 1.7944 | -3.1388 | -1.4525 | 4.419 |  | 3.2212 | 0.1383 | 4.0106 | 3.3679 | 3.3379 | 1.0758 | 10.7764 | 14.2385 | 14.8543 | 11.0767 | 0.0004 | -0.0026 | 0.0012 | 0.0044 | 0.0006 | -0.0001 | 0.0239 | -0.0212 | -0.0118 | -360.1988 | 17.4192 | -360.4419 | 17.6779 | -360.7958 | 18.2077 | -360.922 | 17.6081 | -352.669 | 18.7148 | -352.6013 | 16.8012
12:36 | 4550 | 42.0148 | 202.3362 | 449.6804 | 456.5451 | -16.2811 | -40.5152 | 11.3402 | 8.0301 | 2.295 | 0.6266 | 3.1673 | -0.7905 | 11.7563 | 4.6609 | 0.6175 | 0.6615 | 0.9634 | 0.7424 | -129.4527 | -0.2711 | 5.5624 | 1.7684 | -3.1342 | -1.5073 | 4.3889 |  | 3.2141 | 0.0989 | 4.0105 | 3.3661 | 3.3349 | 1.0758 | 10.7533 | 14.2615 | 14.8822 | 11.054 | 0 | -0.0029 | 0.0008 | 0.0036 | 0.0011 | -0.0008 | 0.0124 | -0.0047 | -0.0016 | -360.1865 | 17.4562 | -360.5281 | 17.7231 | -360.8481 | 18.183 | -360.802 | 17.5547 | -352.6321 | 18.7456 | -352.6875 | 16.8279
12:36 | 4551 | 42.0212 | 202.4139 | 449.7248 | 456.6168 | -16.2915 | -40.4858 | 11.3425 | 8.0874 | 2.3805 | 0.5085 | 3.1506 | -0.8336 | 11.7225 | 4.6644 | 0.6164 | 0.6609 | 0.9657 | 0.7421 | -129.4717 | -0.2686 | 5.6176 | 1.6704 | -3.145 | -1.3676 | 4.4337 |  | 3.1565 | 0.1951 | 4.0114 | 3.3663 | 3.3364 | 1.076 | 10.7464 | 14.2715 | 14.8382 | 11.0826 | -0.0003 | -0.0024 | 0.0009 | 0.0036 | 0.0004 | -0.0003 | 0.0098 | 0.0021 | -0.0122 | -360.1619 | 17.3987 | -360.4266 | 17.6964 | -360.8543 | 18.22 | -360.8758 | 17.5937 | -352.6136 | 18.6922 | -352.5983 | 16.7971
12:36 | 4552 | 42.063 | 202.4681 | 449.8105 | 456.6 | -16.3235 | -40.4291 | 11.3673 | 7.9707 | 2.3085 | 0.4986 | 3.1528 | -0.9292 | 11.7078 | 4.6228 | 0.6172 | 0.6642 | 0.9646 | 0.7412 | -129.5197 | -0.2143 | 5.5486 | 1.6508 | -3.0401 | -1.3544 | 4.4777 |  | 3.1327 | 0.1636 | 4.0094 | 3.3665 | 3.3332 | 1.0745 | 10.7302 | 14.2613 | 14.8232 | 11.089 | 0 | -0.0028 | 0.0013 | 0.0042 | 0.0013 | -0.0003 | 0.0233 | -0.0053 | -0.0069 | -360.2388 | 17.4521 | -360.5066 | 17.682 | -360.805 | 18.1666 | -360.802 | 17.5691 | -352.6567 | 18.7518 | -352.666 | 16.7991
12:36 | 4553 | 41.9928 | 202.4377 | 449.7444 | 456.5521 | -16.3564 | -40.5155 | 11.3132 | 7.9315 | 2.2445 | 0.6692 | 3.0986 | -0.9985 | 11.6789 | 4.554 | 0.6182 | 0.6626 | 0.9641 | 0.742 | -129.5286 | -0.2552 | 5.6055 | 1.6548 | -3.0433 | -1.4812 | 4.4475 |  | 3.1489 | 0.1381 | 4.0089 | 3.3673 | 3.3343 | 1.0753 | 10.7557 | 14.2404 | 14.8365 | 11.0742 | 0.0002 | -0.003 | 0.0008 | 0.0035 | 0.0005 | -0.0002 | 0.0277 | -0.0075 | -0.0124 | -360.1096 | 17.3946 | -360.4481 | 17.7128 | -360.8697 | 18.22 | -360.8543 | 17.5527 | -352.5675 | 18.6943 | -352.6413 | 16.8258
12:36 | 4554 | 42.0225 | 202.4159 | 449.7605 | 456.5069 | -16.3744 | -40.508 | 11.3611 | 7.9338 | 2.2918 | 0.6287 | 3.1785 | -0.9122 | 11.7653 | 4.5836 | 0.6172 | 0.6599 | 0.9613 | 0.7413 | -129.5695 | -0.3138 | 5.5095 | 1.6258 | -3.0667 | -1.4607 | 4.5055 |  | 3.1975 | 0.193 | 4.0089 | 3.3705 | 3.3355 | 1.0753 | 10.7556 | 14.2463 | 14.8665 | 11.1028 | 0.0004 | -0.0026 | 0.0007 | 0.0042 | 0.0009 | -0.0007 | 0.0067 | -0.0112 | -0.0237 | -360.2235 | 17.4397 | -360.4542 | 17.6636 | -360.7497 | 18.181 | -360.8266 | 17.5958 | -352.6752 | 18.7415 | -352.6321 | 16.7766
12:36 | 4555 | 41.9921 | 202.4448 | 449.7338 | 456.5436 | -16.2773 | -40.4213 | 11.4144 | 7.9567 | 2.3243 | 0.7011 | 3.2256 | -0.8576 | 11.8219 | 4.682 | 0.6159 | 0.6584 | 0.9629 | 0.7409 | -129.5141 | -0.3141 | 5.6182 | 1.5928 | -2.9878 | -1.367 | 4.4618 |  | 3.169 | 0.1356 | 4.0105 | 3.3686 | 3.3344 | 1.0746 | 10.7267 | 14.2404 | 14.8365 | 11.0685 | -0.0002 | -0.0026 | 0.0004 | 0.0036 | 0.0008 | -0.0005 | -0.0089 | -0.0099 | -0.0112 | -360.1127 | 17.4151 | -360.5096 | 17.7252 | -360.882 | 18.1933 | -360.802 | 17.5404 | -352.586 | 18.7148 | -352.6937 | 16.8258
12:36 | 4556 | 42.0222 | 202.477 | 449.8088 | 456.5679 | -16.3153 | -40.4682 | 11.3687 | 7.9281 | 2.3285 | 0.6523 | 3.108 | -0.7822 | 11.7381 | 4.6154 | 0.616 | 0.6591 | 0.9628 | 0.7432 | -129.6196 | -0.2192 | 5.6687 | 1.584 | -3.1177 | -1.3118 | 4.4513 |  | 3.2753 | 0.0847 | 4.0098 | 3.3695 | 3.3332 | 1.0763 | 10.7544 | 14.2569 | 14.8951 | 11.0724 | 0.0002 | -0.0024 | 0.0003 | 0.0035 | 0.0008 | -0.0008 | 0.0091 | 0.0003 | -0.0156 | -360.1865 | 17.411 | -360.4389 | 17.6697 | -360.7773 | 18.1933 | -360.8697 | 17.5876 | -352.6106 | 18.7107 | -352.6136 | 16.7807
12:36 | 4557 | 42.0251 | 202.4563 | 449.7319 | 456.5682 | -16.401 | -40.5423 | 11.3787 | 7.949 | 2.3038 | 0.7601 | 3.1244 | -0.93 | 11.6548 | 4.6156 | 0.615 | 0.6608 | 0.9599 | 0.7429 | -129.5445 | -0.3229 | 5.5569 | 1.5896 | -3.1715 | -1.3743 | 4.3868 |  | 3.2523 | 0.1397 | 4.0108 | 3.3662 | 3.3338 | 1.0754 | 10.7441 | 14.2635 | 14.8249 | 11.0511 | 0.0004 | -0.0032 | 0.0012 | 0.0041 | 0.0009 | -0.0003 | -0.0013 | -0.0148 | 0.0097 | -360.1373 | 17.4315 | -360.5035 | 17.7046 | -360.8512 | 18.1707 | -360.7804 | 17.5383 | -352.6044 | 18.7148 | -352.6844 | 16.8258
12:36 | 4558 | 42.0249 | 202.409 | 449.7932 | 456.5461 | -16.3976 | -40.5363 | 11.3066 | 7.8603 | 2.2942 | 0.7617 | 3.1637 | -0.8982 | 11.7008 | 4.6234 | 0.6161 | 0.6625 | 0.9597 | 0.742 | -129.5309 | -0.2687 | 5.5712 | 1.8032 | -3.0716 | -1.4205 | 4.4149 |  | 3.1185 | 0.1051 | 4.0102 | 3.3664 | 3.3369 | 1.0767 | 10.7591 | 14.2727 | 14.8627 | 11.1125 | -0.0002 | -0.003 | 0.001 | 0.0039 | 0.0005 | -0.0007 | 0.0072 | -0.0132 | -0.0144 | -360.1588 | 17.3946 | -360.3958 | 17.6574 | -360.765 | 18.1974 | -360.8697 | 17.5773 | -352.6136 | 18.6963 | -352.5983 | 16.7909
12:36 | 4559 | 42.059 | 202.5613 | 449.8898 | 456.5749 | -16.4304 | -40.4474 | 11.2603 | 7.8203 | 2.2675 | 0.769 | 3.1262 | -0.9485 | 11.7108 | 4.6118 | 0.6177 | 0.6643 | 0.9629 | 0.7419 | -129.5141 | -0.2451 | 5.5967 | 1.8304 | -2.9608 | -1.3832 | 4.4273 |  | 3.1266 | 0.1679 | 4.0106 | 3.3672 | 3.3357 | 1.0762 | 10.7533 | 14.273 | 14.8532 | 11.0944 | -0.0003 | -0.0026 | 0.001 | 0.0041 | 0.001 | -0.0006 | 0.0024 | 0.0011 | -0.0078 | -360.1681 | 17.4274 | -360.4942 | 17.682 | -360.7835 | 18.1481 | -360.765 | 17.5568 | -352.586 | 18.7292 | -352.6229 | 16.8074
12:36 | 4560 | 41.952 | 202.4882 | 449.7318 | 456.4799 | -16.3995 | -40.4992 | 11.396 | 7.8255 | 2.217 | 0.7935 | 3.1664 | -0.9792 | 11.7205 | 4.5603 | 0.6173 | 0.6591 | 0.9599 | 0.7418 | -129.4079 | -0.2253 | 5.5282 | 1.9035 | -2.9974 | -1.3081 | 4.4722 |  | 3.1234 | 0.1288 | 4.0113 | 3.3664 | 3.3328 | 1.0775 | 10.7497 | 14.2871 | 14.8513 | 11.1078 | -0.0001 | -0.0024 | 0.0011 | 0.004 | 0.0007 | -0.0001 | 0.0069 | -0.0148 | -0.0024 | -360.1496 | 17.374 | -360.4173 | 17.6636 | -360.7958 | 18.1974 | -360.845 | 17.5671 | -352.5798 | 18.6881 | -352.5798 | 16.793
12:36 | 4561 | 41.9917 | 202.4605 | 449.7855 | 456.478 | -16.3444 | -40.425 | 11.3448 | 7.9199 | 2.2955 | 0.8296 | 3.1179 | -0.8909 | 11.7899 | 4.5541 | 0.6177 | 0.6617 | 0.96 | 0.7403 | -129.4577 | -0.2378 | 5.569 | 1.787 | -3.0534 | -1.4204 | 4.428 |  | 3.1455 | 0.2006 | 4.0095 | 3.3626 | 3.3332 | 1.0775 | 10.7441 | 14.2578 | 14.8712 | 11.0858 | 0.0002 | -0.003 | 0.0009 | 0.0039 | 0.0009 | -0.0007 | 0.0203 | -0.0023 | -0.0174 | -360.1711 | 17.4233 | -360.4604 | 17.6759 | -360.7712 | 18.1584 | -360.7927 | 17.565 | -352.6136 | 18.7251 | -352.6506 | 16.7971
12:36 | 4562 | 42.0651 | 202.481 | 449.8531 | 456.6439 | -16.3922 | -40.5426 | 11.3242 | 7.9132 | 2.2446 | 0.8968 | 3.1613 | -0.7694 | 11.688 | 4.6338 | 0.6177 | 0.661 | 0.9678 | 0.7421 | -129.5837 | -0.2809 | 5.6326 | 1.8064 | -3.0742 | -1.3606 | 4.4859 |  | 3.1116 | 0.1637 | 4.0097 | 3.3677 | 3.332 | 1.0767 | 10.7383 | 14.2578 | 14.8481 | 11.0858 | -0.0002 | -0.0032 | 0.0006 | 0.0039 | 0.0005 | 0 | 0.0181 | -0.0075 | -0.0177 | -360.1342 | 17.3864 | -360.4019 | 17.6718 | -360.8143 | 18.2056 | -360.8204 | 17.5547 | -352.5706 | 18.684 | -352.6136 | 16.8176
12:36 | 4563 | 42.0537 | 202.5289 | 449.7046 | 456.657 | -16.3491 | -40.5376 | 11.4094 | 7.9518 | 2.1474 | 0.8799 | 3.2022 | -0.8329 | 11.7505 | 4.5978 | 0.6174 | 0.6642 | 0.9648 | 0.7416 | -129.6038 | -0.2879 | 5.614 | 1.7671 | -3.0736 | -1.3571 | 4.4783 |  | 3.145 | 0.1599 | 4.0091 | 3.3668 | 3.3333 | 1.0756 | 10.7578 | 14.2893 | 14.8529 | 11.0872 | -0.0001 | -0.0024 | 0.0008 | 0.0044 | 0.001 | -0.0005 | 0.0189 | -0.0094 | -0.0178 | -360.1896 | 17.4254 | -360.4389 | 17.6512 | -360.7466 | 18.1748 | -360.8297 | 17.5712 | -352.629 | 18.7292 | -352.6167 | 16.7889
12:36 | 4564 | 42.0314 | 202.5422 | 449.8064 | 456.6809 | -16.3911 | -40.5746 | 11.3468 | 7.9714 | 2.1827 | 0.9171 | 3.1504 | -0.7695 | 11.7254 | 4.5837 | 0.6172 | 0.6623 | 0.9632 | 0.7419 | -129.5758 | -0.2196 | 5.6059 | 1.8358 | -2.9943 | -1.309 | 4.483 |  | 3.0777 | 0.1406 | 4.0098 | 3.368 | 3.3296 | 1.0762 | 10.7302 | 14.2554 | 14.8569 | 11.0952 | -0.0004 | -0.0029 | 0.001 | 0.0042 | 0.0007 | -0.0004 | 0.0207 | -0.0116 | -0.0165 | -360.1342 | 17.3987 | -360.4389 | 17.6923 | -360.8174 | 18.1912 | -360.8297 | 17.5424 | -352.5552 | 18.7004 | -352.6444 | 16.8279
12:36 | 4565 | 42.1497 | 202.6407 | 449.9415 | 456.6999 | -16.4687 | -40.6082 | 11.301 | 7.9461 | 2.2704 | 0.8843 | 3.2053 | -0.7557 | 11.7443 | 4.5486 | 0.6171 | 0.6595 | 0.9578 | 0.7422 | -129.5619 | -0.2106 | 5.6094 | 1.7534 | -3.04 | -1.3963 | 4.4473 |  | 3.1914 | 0.16 | 4.0107 | 3.3663 | 3.3368 | 1.0765 | 10.7475 | 14.2499 | 14.8417 | 11.0482 | 0.0001 | -0.0027 | 0.0011 | 0.0043 | 0.0011 | -0.0003 | 0.0036 | 0.0035 | -0.0064 | -360.1558 | 17.4048 | -360.3989 | 17.6471 | -360.7712 | 18.1789 | -360.842 | 17.5732 | -352.6229 | 18.7169 | -352.589 | 16.7971
12:36 | 4566 | 42.1109 | 202.5702 | 449.7925 | 456.6136 | -16.4537 | -40.6979 | 11.4069 | 7.9539 | 2.2569 | 0.8269 | 3.21 | -0.8473 | 11.7079 | 4.6182 | 0.6176 | 0.6599 | 0.9674 | 0.7425 | -129.5781 | -0.2533 | 5.5066 | 1.7864 | -3.061 | -1.4122 | 4.4177 |  | 3.2399 | 0.12 | 4.0102 | 3.3676 | 3.3368 | 1.078 | 10.7567 | 14.2477 | 14.8458 | 11.0746 | 0 | -0.003 | 0.0011 | 0.0038 | 0.0007 | -0.0002 | 0.0095 | -0.0157 | 0.0028 | -360.0973 | 17.4069 | -360.4419 | 17.6697 | -360.8358 | 18.1974 | -360.7958 | 17.5629 | -352.6136 | 18.7107 | -352.6506 | 16.8258
12:36 | 4567 | 42.0784 | 202.5085 | 449.8604 | 456.6466 | -16.3874 | -40.5394 | 11.3889 | 7.916 | 2.2501 | 0.845 | 3.1816 | -0.9139 | 11.6638 | 4.5367 | 0.6185 | 0.6608 | 0.9605 | 0.7426 | -129.5798 | -0.2053 | 5.5391 | 1.824 | -2.96 | -1.4491 | 4.426 |  | 3.2681 | 0.195 | 4.0089 | 3.3691 | 3.3344 | 1.077 | 10.759 | 14.2557 | 14.8706 | 11.1118 | -0.0002 | -0.003 | 0.0008 | 0.0034 | 0.0006 | -0.001 | 0.0055 | -0.0145 | -0.0172 | -360.1927 | 17.3987 | -360.4173 | 17.6492 | -360.7897 | 18.1994 | -360.8604 | 17.5855 | -352.626 | 18.721 | -352.626 | 16.7991
12:36 | 4568 | 42.1512 | 202.4682 | 449.8926 | 456.5778 | -16.3517 | -40.5736 | 11.3189 | 7.8748 | 2.2666 | 0.8907 | 3.2274 | -0.841 | 11.6524 | 4.6225 | 0.6178 | 0.6612 | 0.965 | 0.7433 | -129.4819 | -0.191 | 5.7139 | 1.765 | -3.0222 | -1.3459 | 4.3527 |  | 3.1812 | 0.1279 | 4.0074 | 3.3659 | 3.3343 | 1.0763 | 10.7809 | 14.2781 | 14.884 | 11.1096 | 0 | -0.0024 | 0.0007 | 0.0039 | 0.0008 | -0.0005 | 0.0132 | -0.0188 | -0.0165 | -360.1742 | 17.4233 | -360.4696 | 17.6677 | -360.8297 | 18.181 | -360.7927 | 17.5773 | -352.6136 | 18.7353 | -352.6721 | 16.8279
12:36 | 4569 | 42.1026 | 202.5178 | 449.9159 | 456.5261 | -16.4913 | -40.7698 | 11.2252 | 7.8756 | 2.2807 | 0.7404 | 3.1438 | -0.8503 | 11.6681 | 4.6042 | 0.6173 | 0.6606 | 0.9618 | 0.743 | -129.4516 | -0.0928 | 5.7584 | 1.8416 | -3.0004 | -1.3167 | 4.4503 |  | 3.1477 | 0.2283 | 4.0094 | 3.3696 | 3.3343 | 1.0762 | 10.7753 | 14.295 | 14.8924 | 11.1107 | 0 | -0.003 | 0.0003 | 0.0037 | 0.0003 | -0.0006 | 0.0131 | -0.0076 | -0.0073 | -360.2142 | 17.4131 | -360.4419 | 17.6574 | -360.8327 | 18.2179 | -360.8697 | 17.5917 | -352.629 | 18.7189 | -352.629 | 16.8197
12:36 | 4570 | 42.0833 | 202.4618 | 449.9221 | 456.6718 | -16.3837 | -40.6989 | 11.2052 | 7.8875 | 2.3419 | 0.8278 | 3.141 | -0.8308 | 11.6492 | 4.5054 | 0.6169 | 0.6645 | 0.9587 | 0.7434 | -129.5779 | -0.1785 | 5.6665 | 1.8513 | -2.9543 | -1.3599 | 4.4616 |  | 3.1086 | 0.151 | 4.009 | 3.3699 | 3.335 | 1.0768 | 10.7544 | 14.2628 | 14.8441 | 11.1009 | 0.0003 | -0.003 | 0.0008 | 0.004 | 0.0012 | -0.0004 | -0.0011 | -0.0167 | 0 | -360.1988 | 17.4521 | -360.4912 | 17.68 | -360.8358 | 18.1953 | -360.8543 | 17.5896 | -352.6598 | 18.7456 | -352.6752 | 16.8279
12:36 | 4571 | 42.0624 | 202.3468 | 449.7635 | 456.6331 | -16.4653 | -40.7065 | 11.1558 | 7.8941 | 2.3188 | 0.7167 | 3.0891 | -0.8164 | 11.7199 | 4.6594 | 0.6165 | 0.6629 | 0.9626 | 0.7428 | -129.5448 | -0.2128 | 5.645 | 1.9068 | -3.0096 | -1.313 | 4.4546 |  | 3.1623 | 0.1379 | 4.0115 | 3.3694 | 3.3379 | 1.077 | 10.7348 | 14.2486 | 14.8277 | 11.088 | -0.0001 | -0.0027 | 0.0005 | 0.0038 | 0.0001 | -0.0008 | 0.0173 | -0.0093 | -0.0089 | -360.1527 | 17.4254 | -360.4604 | 17.682 | -360.8635 | 18.2118 | -360.8666 | 17.5896 | -352.6106 | 18.7395 | -352.669 | 16.832
12:36 | 4572 | 42.0145 | 202.4216 | 449.8434 | 456.6839 | -16.4037 | -40.7491 | 11.2453 | 7.8682 | 2.2547 | 0.6978 | 3.0414 | -0.7746 | 11.682 | 4.6983 | 0.6169 | 0.6633 | 0.964 | 0.7443 | -129.4338 | -0.0974 | 5.806 | 1.9384 | -2.9574 | -1.3022 | 4.5085 |  | 3.2097 | 0.1059 | 4.0101 | 3.364 | 3.3332 | 1.077 | 10.7603 | 14.2449 | 14.8572 | 11.0793 | -0.0001 | -0.0027 | 0.001 | 0.0041 | 0.0008 | -0.0007 | 0.0064 | -0.0037 | -0.0191 | -360.2265 | 17.4356 | -360.4666 | 17.6656 | -360.8143 | 18.2056 | -360.8758 | 17.5978 | -352.6598 | 18.7395 | -352.6352 | 16.8156
12:36 | 4573 | 42.0753 | 202.3804 | 449.8509 | 456.6995 | -16.4872 | -40.7913 | 11.2781 | 7.8903 | 2.2827 | 0.7806 | 3.1262 | -0.7884 | 11.7563 | 4.6912 | 0.6176 | 0.6635 | 0.9632 | 0.7412 | -129.4954 | -0.0161 | 5.8362 | 1.923 | -2.8948 | -1.2835 | 4.4709 |  | 3.2265 | 0.1899 | 4.0103 | 3.3654 | 3.3375 | 1.0777 | 10.736 | 14.2498 | 14.8348 | 11.0544 | 0.0002 | -0.0028 | 0.0011 | 0.0041 | 0.0006 | -0.0005 | 0.0161 | -0.0091 | -0.0187 | -360.1988 | 17.4233 | -360.4942 | 17.6882 | -360.842 | 18.2159 | -360.8574 | 17.5876 | -352.6321 | 18.7292 | -352.6537 | 16.8238
12:36 | 4574 | 42.1481 | 202.3093 | 449.8088 | 456.626 | -16.4881 | -40.6798 | 11.2747 | 7.8244 | 2.1868 | 0.67 | 3.0145 | -0.8949 | 11.7227 | 4.5637 | 0.617 | 0.6615 | 0.9623 | 0.7419 | -129.4867 | -0.1504 | 5.8217 | 1.9725 | -2.8992 | -1.2966 | 4.487 |  | 3.2569 | 0.1458 | 4.0098 | 3.3669 | 3.3327 | 1.0774 | 10.7326 | 14.2459 | 14.7881 | 11.0923 | 0.0001 | -0.0031 | 0.001 | 0.0038 | 0.0011 | -0.0008 | 0.0015 | -0.0077 | -0.0226 | -360.1681 | 17.4048 | -360.4389 | 17.6636 | -360.8297 | 18.1974 | -360.8543 | 17.5794 | -352.6167 | 18.7169 | -352.6444 | 16.8053
12:36 | 4575 | 42.0996 | 202.3378 | 449.7912 | 456.6121 | -16.47 | -40.7416 | 11.3014 | 7.8781 | 2.285 | 0.7201 | 3.1076 | -0.895 | 11.7483 | 4.6155 | 0.6181 | 0.664 | 0.9614 | 0.7422 | -129.4842 | -0.1318 | 5.7469 | 1.9207 | -2.9256 | -1.2678 | 4.507 |  | 3.2281 | 0.1886 | 4.0088 | 3.3668 | 3.3357 | 1.0762 | 10.7348 | 14.2718 | 14.8519 | 11.1107 | 0 | -0.0026 | 0.0008 | 0.0032 | 0.0006 | -0.0002 | 0.0141 | -0.0033 | -0.0264 | -360.1988 | 17.4254 | -360.4542 | 17.6594 | -360.7927 | 18.1892 | -360.8358 | 17.5629 | -352.626 | 18.7292 | -352.6383 | 16.8135
12:36 | 4576 | 42.1875 | 202.3571 | 449.7845 | 456.5713 | -16.5486 | -40.6685 | 11.2773 | 7.8837 | 2.3028 | 0.8109 | 3.1188 | -0.9235 | 11.673 | 4.6405 | 0.6171 | 0.661 | 0.9626 | 0.7424 | -129.377 | -0.0729 | 5.7517 | 1.9724 | -2.842 | -1.1802 | 4.5599 |  | 3.1248 | 0.1647 | 4.0097 | 3.3685 | 3.3348 | 1.0766 | 10.7429 | 14.2452 | 14.8478 | 11.0786 | -0.0002 | -0.0027 | 0.0007 | 0.0034 | 0.001 | -0.0008 | 0.0127 | -0.0139 | -0.0089 | -360.1588 | 17.4151 | -360.445 | 17.6677 | -360.8174 | 18.1666 | -360.8543 | 17.5691 | -352.5829 | 18.7066 | -352.6383 | 16.8053
12:36 | 4577 | 42.1693 | 202.4958 | 449.8068 | 456.645 | -16.5304 | -40.6875 | 11.2538 | 7.915 | 2.2527 | 0.8261 | 3.1535 | -0.966 | 11.7516 | 4.7083 | 0.6171 | 0.6645 | 0.9632 | 0.743 | -129.4825 | -0.1402 | 5.6945 | 1.8952 | -2.9121 | -1.25 | 4.4868 |  | 3.1802 | 0.1189 | 4.0103 | 3.3682 | 3.335 | 1.0784 | 10.7833 | 14.2742 | 14.8893 | 11.1071 | 0.0002 | -0.0027 | 0.0004 | 0.0033 | 0.0003 | -0.0002 | 0.0044 | -0.0046 | -0.0249 | -360.1896 | 17.4151 | -360.4419 | 17.6615 | -360.7866 | 18.1707 | -360.845 | 17.5629 | -352.5798 | 18.7128 | -352.6475 | 16.8094
12:36 | 4578 | 42.213 | 202.4673 | 449.8497 | 456.7282 | -16.5152 | -40.6627 | 11.2695 | 7.945 | 2.2516 | 0.7639 | 3.091 | -0.9527 | 11.6919 | 4.6659 | 0.6175 | 0.6649 | 0.9651 | 0.7422 | -129.4501 | -0.0517 | 5.7242 | 1.8682 | -2.9659 | -1.285 | 4.4754 |  | 3.2235 | 0.1369 | 4.0112 | 3.3691 | 3.3356 | 1.0782 | 10.7936 | 14.2735 | 14.8796 | 11.0991 | 0.0003 | -0.0031 | 0.0006 | 0.0038 | 0.0007 | -0.0003 | 0.009 | -0.0139 | -0.0119 | -360.1835 | 17.4069 | -360.4512 | 17.6615 | -360.7897 | 18.1645 | -360.842 | 17.565 | -352.6167 | 18.7169 | -352.6321 | 16.8053
12:36 | 4579 | 42.197 | 202.5051 | 449.8932 | 456.7245 | -16.5127 | -40.6576 | 11.2664 | 7.961 | 2.1873 | 0.6772 | 3.098 | -0.9301 | 11.7109 | 4.6955 | 0.6167 | 0.6599 | 0.959 | 0.7411 | -129.4883 | -0.1327 | 5.6977 | 1.9026 | -2.8814 | -1.278 | 4.5562 |  | 3.2124 | 0.1042 | 4.0096 | 3.3673 | 3.3348 | 1.0771 | 10.7499 | 14.2345 | 14.8412 | 11.0631 | -0.0001 | -0.003 | 0.0008 | 0.0039 | 0.0005 | -0.0006 | 0.0172 | -0.0159 | -0.0002 | -360.1619 | 17.4048 | -360.4358 | 17.6471 | -360.802 | 18.1728 | -360.8297 | 17.5629 | -352.5952 | 18.7189 | -352.629 | 16.795
12:36 | 4580 | 42.1949 | 202.4979 | 449.9771 | 456.7613 | -16.4407 | -40.6615 | 11.262 | 7.9587 | 2.1306 | 0.6131 | 3.1249 | -0.9396 | 11.6276 | 4.7931 | 0.6172 | 0.6626 | 0.9644 | 0.7423 | -129.5586 | -0.1426 | 5.782 | 1.8864 | -2.909 | -1.2308 | 4.5413 |  | 3.1684 | 0.1072 | 4.0103 | 3.3695 | 3.3362 | 1.0782 | 10.7636 | 14.2721 | 14.8598 | 11.0868 | -0.0005 | -0.0025 | 0.0008 | 0.0037 | 0.0009 | -0.0003 | 0.0123 | -0.0112 | -0.0269 | -360.1958 | 17.4315 | -360.4696 | 17.6656 | -360.8327 | 18.1645 | -360.8358 | 17.5876 | -352.629 | 18.7312 | -352.669 | 16.8115
12:36 | 4581 | 42.2432 | 202.5675 | 449.9196 | 456.673 | -16.4575 | -40.7655 | 11.3007 | 7.9127 | 2.2002 | 0.5999 | 3.1505 | -0.9556 | 11.6503 | 4.7089 | 0.6161 | 0.6647 | 0.9646 | 0.7436 | -129.4266 | -0.1628 | 5.7429 | 1.883 | -2.9692 | -1.2175 | 4.5256 |  | 3.2416 | 0.162 | 4.0084 | 3.3671 | 3.3354 | 1.0763 | 10.7568 | 14.253 | 14.8715 | 11.1219 | -0.0003 | -0.0033 | 0.0002 | 0.0033 | 0.0007 | -0.0013 | 0.0138 | -0.0059 | -0.0225 | -360.165 | 17.4131 | -360.4542 | 17.6636 | -360.8174 | 18.1789 | -360.8389 | 17.5917 | -352.6537 | 18.7169 | -352.629 | 16.8135
12:36 | 4582 | 42.2725 | 202.5249 | 449.9362 | 456.7097 | -16.4659 | -40.7507 | 11.3166 | 7.9506 | 2.2089 | 0.5777 | 3.1112 | -0.8989 | 11.7794 | 4.8009 | 0.6171 | 0.6629 | 0.9599 | 0.743 | -129.5312 | -0.1762 | 5.623 | 1.7832 | -2.9917 | -1.4113 | 4.5156 |  | 3.1405 | 0.045 | 4.0103 | 3.3686 | 3.3349 | 1.0785 | 10.759 | 14.2846 | 14.8475 | 11.106 | 0.0001 | -0.0032 | 0.0007 | 0.0038 | 0.0007 | 0 | 0.0163 | 0.008 | 0.0108 | -360.2296 | 17.4356 | -360.4758 | 17.682 | -360.8297 | 18.1645 | -360.8358 | 17.5978 | -352.6598 | 18.7415 | -352.6506 | 16.8074
12:36 | 4583 | 42.1909 | 202.5046 | 449.8899 | 456.6823 | -16.407 | -40.6467 | 11.4014 | 7.916 | 2.1987 | 0.5054 | 3.0127 | -0.8799 | 11.8085 | 4.8005 | 0.616 | 0.6623 | 0.9598 | 0.7428 | -129.5306 | -0.225 | 5.6028 | 1.7591 | -3.008 | -1.3777 | 4.497 |  | 3.1638 | 0.1502 | 4.0105 | 3.3682 | 3.338 | 1.079 | 10.7313 | 14.2509 | 14.8709 | 11.1017 | 0 | -0.0031 | 0.0011 | 0.0036 | 0.0013 | -0.0009 | 0.0183 | -0.0058 | -0.0049 | -360.1865 | 17.4172 | -360.4604 | 17.682 | -360.8512 | 18.183 | -360.8481 | 17.5794 | -352.6106 | 18.7333 | -352.6383 | 16.8156
12:36 | 4584 | 42.2235 | 202.4719 | 449.8168 | 456.6964 | -16.4307 | -40.5962 | 11.3635 | 7.9304 | 2.2573 | 0.5177 | 3.0409 | -1.0222 | 11.7238 | 4.7332 | 0.6159 | 0.6602 | 0.9589 | 0.7421 | -129.5267 | -0.108 | 5.6356 | 1.7616 | -3.0229 | -1.3695 | 4.4437 |  | 3.147 | 0.2236 | 4.0089 | 3.3633 | 3.335 | 1.077 | 10.7521 | 14.2603 | 14.8403 | 11.1049 | -0.0006 | -0.0026 | 0.0004 | 0.004 | 0.0004 | -0.0002 | 0.0174 | -0.0022 | 0.0059 | -360.1958 | 17.4274 | -360.445 | 17.6656 | -360.8081 | 18.181 | -360.8789 | 17.604 | -352.6444 | 18.7292 | -352.6413 | 16.7909
12:36 | 4585 | 42.1637 | 202.4461 | 449.7908 | 456.6558 | -16.5188 | -40.7796 | 11.3643 | 7.8792 | 2.1973 | 0.5335 | 3.0358 | -0.9349 | 11.6809 | 4.6154 | 0.6181 | 0.6634 | 0.9616 | 0.7411 | -129.4799 | -0.113 | 5.6121 | 1.6635 | -3.082 | -1.4373 | 4.4296 |  | 3.1079 | 0.1563 | 4.0084 | 3.3648 | 3.3379 | 1.0781 | 10.7556 | 14.2118 | 14.8212 | 11.0908 | -0.0001 | -0.0027 | 0.0008 | 0.004 | 0.0011 | -0.0004 | 0.0092 | -0.0048 | -0.0213 | -360.2327 | 17.4295 | -360.4942 | 17.6841 | -360.8389 | 18.1584 | -360.8204 | 17.5958 | -352.6567 | 18.7518 | -352.6444 | 16.8094
12:36 | 4586 | 42.1951 | 202.4273 | 449.7134 | 456.5981 | -16.437 | -40.6503 | 11.3102 | 7.9243 | 2.2164 | 0.7051 | 3.0645 | -1.0169 | 11.6242 | 4.5646 | 0.6181 | 0.6625 | 0.9606 | 0.742 | -129.4034 | -0.1358 | 5.6261 | 1.8014 | -3.0736 | -1.4262 | 4.4276 |  | 3.1283 | 0.195 | 4.0093 | 3.3642 | 3.3355 | 1.0777 | 10.7499 | 14.2462 | 14.8539 | 11.1089 | -0.0003 | -0.0036 | 0.0006 | 0.004 | 0.0007 | -0.0001 | 0.0177 | -0.0024 | -0.0057 | -360.1404 | 17.4131 | -360.4173 | 17.6697 | -360.8574 | 18.183 | -360.8512 | 17.5937 | -352.5798 | 18.7066 | -352.6506 | 16.8012
12:36 | 4587 | 42.1328 | 202.3491 | 449.8886 | 456.6113 | -16.5979 | -40.7412 | 11.1963 | 8.006 | 2.0985 | 0.5332 | 3.0281 | -1.0005 | 11.6413 | 4.6773 | 0.6168 | 0.6629 | 0.961 | 0.7431 | -129.3682 | -0.0622 | 5.5543 | 1.6694 | -3.0516 | -1.374 | 4.4884 |  | 3.074 | 0.0607 | 4.009 | 3.3645 | 3.3351 | 1.0781 | 10.7533 | 14.273 | 14.8706 | 11.1175 | 0 | -0.003 | 0.0008 | 0.0043 | 0.0014 | -0.0001 | 0.0199 | -0.005 | 0.0038 | -360.1927 | 17.4151 | -360.4327 | 17.6451 | -360.7773 | 18.1728 | -360.8666 | 17.5978 | -352.6198 | 18.7292 | -352.6075 | 16.7807
12:36 | 4588 | 42.2095 | 202.4549 | 449.8407 | 456.6794 | -16.5281 | -40.6534 | 11.1382 | 7.9463 | 2.0886 | 0.6271 | 3.0049 | -0.9773 | 11.7042 | 4.6841 | 0.6159 | 0.6601 | 0.9616 | 0.7413 | -129.482 | -0.0351 | 5.5427 | 1.762 | -2.9858 | -1.4707 | 4.4119 |  | 3.1736 | 0.0812 | 4.0081 | 3.3642 | 3.3358 | 1.0756 | 10.7612 | 14.2757 | 14.8697 | 11.1074 | -0.0001 | -0.0042 | 0.0013 | 0.004 | 0.0013 | 0 | 0.0114 | -0.0116 | -0.004 | -360.1835 | 17.4295 | -360.4789 | 17.682 | -360.8327 | 18.1399 | -360.7989 | 17.5794 | -352.6106 | 18.7189 | -352.6567 | 16.8176
12:36 | 4589 | 42.2056 | 202.4375 | 449.843 | 456.7127 | -16.4903 | -40.6012 | 11.2015 | 7.8912 | 2.0853 | 0.4494 | 2.9158 | -0.9866 | 11.7312 | 4.6935 | 0.6168 | 0.6637 | 0.9642 | 0.7436 | -129.5178 | -0.1338 | 5.6176 | 1.7355 | -2.9986 | -1.4168 | 4.4579 |  | 3.1407 | 0.0551 | 4.0092 | 3.3664 | 3.3358 | 1.0781 | 10.7488 | 14.2563 | 14.8446 | 11.1086 | -0.0006 | -0.0028 | 0.0002 | 0.0036 | 0.0009 | -0.0006 | 0.0057 | -0.0013 | -0.0063 | -360.1773 | 17.3802 | -360.4266 | 17.6594 | -360.8143 | 18.183 | -360.8789 | 17.5876 | -352.6167 | 18.682 | -352.5675 | 16.7971
12:36 | 4590 | 42.115 | 202.2799 | 449.6967 | 456.5689 | -16.4707 | -40.6685 | 11.2016 | 7.8956 | 2.1173 | 0.3705 | 2.9981 | -0.9775 | 11.6321 | 4.6869 | 0.6182 | 0.6611 | 0.9613 | 0.7421 | -129.4502 | -0.1004 | 5.6233 | 1.6245 | -3.1479 | -1.3934 | 4.3424 |  | 3.2709 | 0.032 | 4.0093 | 3.3648 | 3.3395 | 1.0787 | 10.7302 | 14.2324 | 14.8232 | 11.0717 | 0.0004 | -0.0031 | 0.0008 | 0.0036 | 0.0007 | -0.0006 | 0.007 | -0.0023 | -0.013 | -360.2235 | 17.4377 | -360.4666 | 17.6533 | -360.7743 | 18.142 | -360.7958 | 17.5896 | -352.6475 | 18.7353 | -352.6906 | 16.7807
12:36 | 4591 | 42.1725 | 202.3958 | 449.6476 | 456.5763 | -16.4662 | -40.6824 | 11.1273 | 7.8616 | 2.1026 | 0.4604 | 2.995 | -0.9948 | 11.721 | 4.797 | 0.6175 | 0.6609 | 0.9623 | 0.7419 | -129.5328 | -0.068 | 5.597 | 1.6833 | -3.102 | -1.4324 | 4.3776 |  | 3.214 | 0.0937 | 4.0081 | 3.3651 | 3.3347 | 1.0767 | 10.751 | 14.2591 | 14.8621 | 11.0634 | 0.0001 | -0.003 | 0.0009 | 0.0035 | 0.0004 | -0.0008 | 0.025 | 0.0077 | -0.024 | -360.1004 | 17.3864 | -360.4358 | 17.6615 | -360.8358 | 18.1769 | -360.8143 | 17.5527 | -352.5921 | 18.6881 | -352.6167 | 16.8197
12:36 | 4592 | 42.1288 | 202.4017 | 449.6557 | 456.5264 | -16.4753 | -40.6783 | 11.012 | 7.8188 | 2.0639 | 0.4865 | 3.0003 | -0.9534 | 11.7135 | 4.6964 | 0.6165 | 0.6617 | 0.9626 | 0.7433 | -129.5052 | -0.0973 | 5.5476 | 1.7184 | -3.0863 | -1.4517 | 4.4387 |  | 3.1583 | 0.036 | 4.0077 | 3.3637 | 3.335 | 1.0784 | 10.7291 | 14.26 | 14.8324 | 11.0768 | -0.0001 | -0.0027 | 0.0003 | 0.0035 | 0.0011 | -0.0005 | 0.0132 | -0.0154 | -0.0169 | -360.2142 | 17.4048 | -360.4204 | 17.6245 | -360.7804 | 18.1584 | -360.842 | 17.604 | -352.626 | 18.7087 | -352.6106 | 16.7622
12:36 | 4593 | 42.166 | 202.318 | 449.7559 | 456.5467 | -16.548 | -40.728 | 10.9946 | 7.9377 | 2.1351 | 0.4852 | 3.1296 | -0.9584 | 11.7293 | 4.7651 | 0.618 | 0.6634 | 0.9648 | 0.7451 | -129.4575 | -0.1877 | 5.565 | 1.6541 | -3.0619 | -1.3398 | 4.4434 |  | 3.2619 | 0.1132 | 4.0103 | 3.3648 | 3.3359 | 1.079 | 10.715 | 14.2465 | 14.8386 | 11.1139 | -0.0003 | -0.0027 | 0.0009 | 0.0038 | 0.0007 | -0.0004 | -0.0061 | -0.0128 | -0.0263 | -360.1558 | 17.4213 | -360.4696 | 17.6759 | -360.842 | 18.1296 | -360.7373 | 17.5424 | -352.5767 | 18.7066 | -352.669 | 16.8238
12:36 | 4594 | 42.1442 | 202.3258 | 449.7007 | 456.5288 | -16.5342 | -40.7556 | 11.0794 | 7.9088 | 2.127 | 0.542 | 3.1342 | -1.0223 | 11.6107 | 4.6767 | 0.6162 | 0.6601 | 0.9624 | 0.7404 | -129.483 | -0.1527 | 5.5411 | 1.7614 | -3.0302 | -1.3511 | 4.5205 |  | 3.2068 | 0.0802 | 4.01 | 3.3641 | 3.3358 | 1.0787 | 10.7718 | 14.2974 | 14.8778 | 11.0955 | 0.0004 | -0.0026 | 0.0007 | 0.0041 | 0.0004 | -0.0011 | 0.024 | -0.0215 | -0.0054 | -360.1342 | 17.3802 | -360.3681 | 17.6328 | -360.7989 | 18.181 | -360.8758 | 17.5814 | -352.5829 | 18.682 | -352.5644 | 16.7745
12:36 | 4595 | 42.1002 | 202.3366 | 449.7326 | 456.6035 | -16.4977 | -40.6734 | 11.0975 | 7.8973 | 2.0935 | 0.5979 | 3.1841 | -0.9684 | 11.5934 | 4.6095 | 0.6183 | 0.661 | 0.9639 | 0.741 | -129.4127 | -0.1859 | 5.5561 | 1.7243 | -3.1075 | -1.3609 | 4.4369 |  | 3.1933 | 0.0596 | 4.0104 | 3.3615 | 3.3367 | 1.0779 | 10.7706 | 14.279 | 14.8717 | 11.1056 | 0.0002 | -0.0029 | 0.0011 | 0.0043 | 0.0006 | 0 | 0.0028 | -0.0102 | -0.0288 | -360.1896 | 17.4295 | -360.4573 | 17.6389 | -360.7435 | 18.1296 | -360.8174 | 17.5794 | -352.6444 | 18.7312 | -352.669 | 16.7848
12:36 | 4596 | 42.207 | 202.3796 | 449.8163 | 456.6672 | -16.4579 | -40.5352 | 11.1757 | 7.8574 | 2.2242 | 0.5758 | 3.276 | -0.8898 | 11.745 | 4.7172 | 0.6169 | 0.6624 | 0.9607 | 0.7422 | -129.4398 | -0.1454 | 5.6037 | 1.6756 | -3.147 | -1.4645 | 4.3684 |  | 3.217 | 0.0396 | 4.0108 | 3.3607 | 3.336 | 1.0778 | 10.7094 | 14.2635 | 14.8191 | 11.0858 | -0.0002 | -0.0029 | 0.0008 | 0.0037 | 0.0011 | -0.0005 | -0.0051 | -0.0054 | -0.0311 | -360.0758 | 17.3843 | -360.4419 | 17.6759 | -360.845 | 18.1707 | -360.8143 | 17.5486 | -352.5613 | 18.6861 | -352.6413 | 16.8238
12:36 | 4597 | 42.1848 | 202.3841 | 449.8537 | 456.6127 | -16.4595 | -40.6637 | 11.1569 | 7.9422 | 2.2316 | 0.5776 | 3.2376 | -0.95 | 11.6652 | 4.64 | 0.6169 | 0.6576 | 0.9632 | 0.7416 | -129.4604 | -0.1998 | 5.5859 | 1.6677 | -3.0296 | -1.4428 | 4.4188 |  | 3.2218 | 0.1562 | 4.009 | 3.3622 | 3.3365 | 1.0771 | 10.7431 | 14.2272 | 14.8319 | 11.0454 | -0.0003 | -0.0024 | 0.0005 | 0.0033 | 0.0002 | -0.0003 | 0.0069 | -0.0058 | -0.0015 | -360.205 | 17.4007 | -360.4112 | 17.643 | -360.7712 | 18.1543 | -360.8789 | 17.604 | -352.6813 | 18.7025 | -352.6537 | 16.7724
12:36 | 4598 | 42.2353 | 202.4203 | 449.8367 | 456.6734 | -16.4309 | -40.733 | 11.1795 | 8.0031 | 2.2213 | 0.5678 | 3.2409 | -1.0895 | 11.6387 | 4.6518 | 0.6176 | 0.6618 | 0.9604 | 0.7419 | -129.5044 | -0.0805 | 5.6855 | 1.7434 | -2.9521 | -1.3969 | 4.4401 |  | 3.2748 | 0.2577 | 4.0102 | 3.3642 | 3.3355 | 1.0778 | 10.7291 | 14.2252 | 14.7966 | 11.0425 | 0 | -0.0029 | 0.0006 | 0.0039 | 0.0012 | -0.0002 | -0.0061 | -0.0029 | -0.0061 | -360.125 | 17.4336 | -360.4912 | 17.6882 | -360.8235 | 18.1502 | -360.7989 | 17.565 | -352.629 | 18.7189 | -352.6998 | 16.832
12:36 | 4599 | 42.2502 | 202.3946 | 449.8959 | 456.6979 | -16.4058 | -40.524 | 11.3022 | 8.0991 | 2.3265 | 0.4606 | 3.3045 | -1.0776 | 11.6657 | 4.594 | 0.6175 | 0.6621 | 0.9666 | 0.7419 | -129.4443 | -0.2105 | 5.5707 | 1.7423 | -2.9269 | -1.3747 | 4.4007 |  | 3.2925 | 0.2895 | 4.0087 | 3.3669 | 3.3365 | 1.0788 | 10.7476 | 14.2323 | 14.8164 | 11.0605 | 0.0004 | -0.0028 | 0.001 | 0.0035 | 0.0009 | 0.0001 | 0.0059 | 0.0028 | -0.0102 | -360.1896 | 17.3925 | -360.4327 | 17.68 | -360.8297 | 18.2036 | -360.9097 | 17.602 | -352.6567 | 18.6963 | -352.6198 | 16.8156
12:36 | 4600 | 42.2343 | 202.4163 | 449.9202 | 456.6891 | -16.4415 | -40.5455 | 11.2212 | 8.0206 | 2.4025 | 0.5884 | 3.3097 | -1.0598 | 11.6688 | 4.5863 | 0.6171 | 0.66 | 0.9657 | 0.7411 | -129.5279 | -0.1431 | 5.5846 | 1.7504 | -2.9995 | -1.3802 | 4.356 |  | 3.1996 | 0.2272 | 4.01 | 3.364 | 3.3365 | 1.0764 | 10.744 | 14.2579 | 14.8491 | 11.0739 | -0.0001 | -0.0026 | 0.0007 | 0.0042 | 0.0008 | -0.0007 | 0.0237 | -0.0076 | -0.0037 | -360.245 | 17.4541 | -360.4912 | 17.6779 | -360.8174 | 18.1543 | -360.8512 | 17.6143 | -352.709 | 18.7518 | -352.7121 | 16.8032
12:36 | 4601 | 42.1954 | 202.3783 | 449.7592 | 456.6573 | -16.4356 | -40.5903 | 11.2098 | 8.0664 | 2.2829 | 0.6316 | 3.3359 | -1.043 | 11.7586 | 4.5824 | 0.6165 | 0.6613 | 0.9628 | 0.7418 | -129.5296 | -0.1524 | 5.5405 | 1.7078 | -3.0913 | -1.4182 | 4.2698 |  | 3.3125 | 0.1664 | 4.0092 | 3.3657 | 3.34 | 1.0787 | 10.7648 | 14.2848 | 14.8659 | 11.1056 | -0.0003 | -0.0024 | 0.001 | 0.0042 | 0.0006 | -0.0003 | 0.0107 | -0.0075 | -0.0076 | -360.1127 | 17.4172 | -360.485 | 17.7169 | -360.8881 | 18.2015 | -360.842 | 17.5753 | -352.6106 | 18.7066 | -352.6813 | 16.8484
12:36 | 4602 | 42.1625 | 202.4258 | 449.8182 | 456.5987 | -16.4367 | -40.5934 | 11.1994 | 7.9949 | 2.3324 | 0.4596 | 3.3844 | -0.9885 | 11.7762 | 4.6654 | 0.6165 | 0.6627 | 0.9651 | 0.7433 | -129.4947 | -0.1494 | 5.5764 | 1.7494 | -3.1253 | -1.3932 | 4.3257 |  | 3.2836 | 0.2407 | 4.0099 | 3.3658 | 3.3357 | 1.0777 | 10.7844 | 14.3103 | 14.9092 | 11.0847 | 0.0002 | -0.0028 | 0.001 | 0.0044 | 0.0005 | -0.0003 | 0.0038 | -0.0087 | -0.0127 | -360.245 | 17.4377 | -360.4542 | 17.6553 | -360.8235 | 18.183 | -360.885 | 17.6204 | -352.6906 | 18.7312 | -352.6352 | 16.7786
12:36 | 4603 | 42.1682 | 202.4462 | 449.9752 | 456.6619 | -16.4104 | -40.601 | 11.0967 | 8.0285 | 2.3795 | 0.551 | 3.2734 | -1.0999 | 11.8074 | 4.6686 | 0.6168 | 0.6605 | 0.9648 | 0.741 | -129.4903 | -0.086 | 5.4945 | 1.7147 | -3.1807 | -1.3876 | 4.332 |  | 3.2378 | 0.2066 | 4.01 | 3.3635 | 3.3406 | 1.0784 | 10.7601 | 14.2802 | 14.8557 | 11.0951 | 0.0002 | -0.003 | 0.0005 | 0.0037 | 0.0014 | -0.0001 | 0.0227 | -0.0006 | -0.0094 | -360.1896 | 17.4315 | -360.525 | 17.6923 | -360.845 | 18.1522 | -360.805 | 17.5691 | -352.5767 | 18.7292 | -352.6906 | 16.8074
12:36 | 4604 | 42.1258 | 202.4691 | 449.7462 | 456.714 | -16.4106 | -40.6555 | 11.1694 | 7.9768 | 2.3328 | 0.5487 | 3.2583 | -1.098 | 11.7511 | 4.6173 | 0.6161 | 0.66 | 0.9631 | 0.7422 | -129.5186 | -0.1374 | 5.5217 | 1.674 | -3.1673 | -1.4918 | 4.2895 |  | 3.2345 | 0.2464 | 4.01 | 3.3675 | 3.3352 | 1.0781 | 10.7659 | 14.2744 | 14.8962 | 11.1183 | 0 | -0.0029 | 0.0008 | 0.0041 | 0.0007 | -0.0003 | 0.0034 | -0.0128 | 0.0006 | -360.1558 | 17.3823 | -360.4235 | 17.6677 | -360.8235 | 18.1933 | -360.845 | 17.5835 | -352.586 | 18.684 | -352.626 | 16.793
12:36 | 4605 | 42.1861 | 202.3831 | 449.8434 | 456.6906 | -16.4569 | -40.5923 | 11.0686 | 7.994 | 2.3045 | 0.7028 | 3.2497 | -0.9697 | 11.8106 | 4.6025 | 0.6168 | 0.6597 | 0.9608 | 0.7427 | -129.5265 | -0.2699 | 5.4989 | 1.7427 | -3.1359 | -1.5354 | 4.3399 |  | 3.2973 | 0.2937 | 4.0101 | 3.3667 | 3.3346 | 1.0769 | 10.7406 | 14.26 | 14.8266 | 11.0999 | -0.0004 | -0.0029 | 0.0003 | 0.0033 | 0.0009 | -0.0008 | 0.0098 | -0.0057 | -0.0006 | -360.2019 | 17.4315 | -360.4696 | 17.6594 | -360.7743 | 18.1379 | -360.8143 | 17.5896 | -352.6567 | 18.7271 | -352.666 | 16.7827
12:36 | 4606 | 42.0791 | 202.3416 | 449.7321 | 456.646 | -16.5241 | -40.6934 | 11.0373 | 7.9244 | 2.2442 | 0.6492 | 3.2281 | -0.8688 | 11.7542 | 4.6855 | 0.6167 | 0.6604 | 0.9628 | 0.7435 | -129.5433 | -0.1294 | 5.5005 | 1.8016 | -3.0632 | -1.4012 | 4.3566 |  | 3.2899 | 0.2541 | 4.0093 | 3.3653 | 3.3353 | 1.0777 | 10.7383 | 14.252 | 14.8249 | 11.0569 | -0.0001 | -0.0027 | 0.0008 | 0.0037 | 0.0003 | -0.0006 | -0.0081 | -0.008 | -0.0158 | -360.0942 | 17.3843 | -360.4296 | 17.6841 | -360.8389 | 18.1687 | -360.8081 | 17.5506 | -352.5398 | 18.682 | -352.6383 | 16.8217
12:36 | 4607 | 42.11 | 202.3536 | 449.7115 | 456.6353 | -16.5132 | -40.6321 | 11.0677 | 7.8844 | 2.2719 | 0.5935 | 3.2859 | -1.036 | 11.7345 | 4.6221 | 0.6172 | 0.662 | 0.9624 | 0.7431 | -129.5277 | -0.0487 | 5.5083 | 1.8714 | -3.0397 | -1.3231 | 4.4375 |  | 3.3127 | 0.3807 | 4.0095 | 3.3616 | 3.3341 | 1.0773 | 10.7152 | 14.2518 | 14.8239 | 11.0919 | 0 | -0.0035 | 0.0011 | 0.0037 | 0.0009 | -0.0006 | 0.014 | -0.0181 | 0.0069 | -360.205 | 17.3966 | -360.3989 | 17.6328 | -360.762 | 18.1543 | -360.8512 | 17.5978 | -352.626 | 18.6922 | -352.6075 | 16.7724
12:37 | 4608 | 42.2038 | 202.3677 | 449.7232 | 456.6347 | -16.4727 | -40.5559 | 11.1824 | 7.8859 | 2.3136 | 0.6265 | 3.3525 | -1.0325 | 11.6957 | 4.5846 | 0.6164 | 0.6608 | 0.9614 | 0.7431 | -129.5072 | -0.1002 | 5.5174 | 1.7642 | -3.068 | -1.2983 | 4.3793 |  | 3.2435 | 0.246 | 4.0087 | 3.3641 | 3.3381 | 1.0776 | 10.7232 | 14.2428 | 14.845 | 11.0822 | 0.0001 | -0.0031 | 0.0006 | 0.0042 | 0.0007 | -0.0004 | 0.0342 | -0.0176 | 0.0109 | -360.1373 | 17.4131 | -360.4542 | 17.6738 | -360.802 | 18.144 | -360.7804 | 17.5691 | -352.5798 | 18.7045 | -352.6444 | 16.8115
12:37 | 4609 | 42.1674 | 202.4288 | 449.9086 | 456.7612 | -16.4624 | -40.7015 | 11.2362 | 7.8337 | 2.3295 | 0.5736 | 3.291 | -0.9636 | 11.7224 | 4.6538 | 0.6164 | 0.6595 | 0.9624 | 0.7426 | -129.5584 | -0.1789 | 5.5339 | 1.7235 | -3.095 | -1.4929 | 4.3219 |  | 3.3202 | 0.2102 | 4.0084 | 3.3612 | 3.3375 | 1.0774 | 10.76 | 14.292 | 14.8752 | 11.0886 | -0.0002 | -0.0024 | 0.0015 | 0.0047 | 0.0012 | -0.0004 | 0.014 | -0.0049 | -0.0309 | -360.1404 | 17.3679 | -360.3927 | 17.6594 | -360.7835 | 18.1728 | -360.8512 | 17.5712 | -352.5644 | 18.6779 | -352.5736 | 16.7909
12:37 | 4610 | 42.1648 | 202.3654 | 449.8092 | 456.618 | -16.4535 | -40.6905 | 11.0908 | 7.8858 | 2.2542 | 0.5617 | 3.3546 | -0.8857 | 11.7468 | 4.6759 | 0.6169 | 0.659 | 0.9591 | 0.7405 | -129.5761 | -0.1163 | 5.5544 | 1.7625 | -3.0615 | -1.3771 | 4.3623 |  | 3.2785 | 0.2478 | 4.009 | 3.3639 | 3.3389 | 1.0768 | 10.7567 | 14.2708 | 14.8516 | 11.0861 | -0.0005 | -0.0028 | 0.0008 | 0.0042 | 0.001 | 0.0002 | 0.0186 | -0.0089 | -0.0047 | -360.1988 | 17.4254 | -360.4358 | 17.643 | -360.7712 | 18.1337 | -360.8235 | 17.5794 | -352.6444 | 18.7169 | -352.6537 | 16.7848
12:37 | 4611 | 42.1773 | 202.3372 | 449.7642 | 456.6933 | -16.4337 | -40.5156 | 11.2101 | 7.958 | 2.3357 | 0.7501 | 3.3096 | -0.9512 | 11.7269 | 4.7064 | 0.6171 | 0.6614 | 0.9579 | 0.7405 | -129.6089 | -0.0831 | 5.5719 | 1.7977 | -3.1029 | -1.3478 | 4.2973 |  | 3.3468 | 0.364 | 4.0092 | 3.3656 | 3.3396 | 1.0784 | 10.7718 | 14.28 | 14.8893 | 11.1071 | 0.0003 | -0.0029 | 0.0008 | 0.0041 | 0.0012 | -0.0006 | 0.0114 | -0.0097 | -0.0039 | -360.0973 | 17.3925 | -360.4266 | 17.6738 | -360.8112 | 18.1748 | -360.8266 | 17.5588 | -352.5521 | 18.6881 | -352.626 | 16.8135
12:37 | 4612 | 42.2006 | 202.3382 | 449.9091 | 456.7567 | -16.2776 | -40.4539 | 11.205 | 7.9392 | 2.3366 | 0.7404 | 3.3579 | -0.9285 | 11.7652 | 4.7197 | 0.619 | 0.6605 | 0.96 | 0.7395 | -129.5146 | -0.0301 | 5.5843 | 1.7732 | -3.0861 | -1.3915 | 4.2812 |  | 3.3314 | 0.3138 | 4.0097 | 3.3613 | 3.3339 | 1.0774 | 10.7394 | 14.288 | 14.8679 | 11.1096 | 0 | -0.0031 | 0.0007 | 0.0036 | 0.0008 | -0.0002 | -0.0041 | -0.0022 | 0.0145 | -360.1527 | 17.4048 | -360.4204 | 17.641 | -360.7712 | 18.1645 | -360.842 | 17.5855 | -352.6413 | 18.7066 | -352.6413 | 16.793
12:37 | 4613 | 42.2168 | 202.4437 | 450.0347 | 456.801 | -16.3628 | -40.576 | 11.2059 | 7.9474 | 2.2921 | 0.7729 | 3.3803 | -0.9597 | 11.7487 | 4.6427 | 0.6185 | 0.6628 | 0.9647 | 0.7419 | -129.5431 | -0.1093 | 5.6432 | 1.8072 | -3.0888 | -1.3342 | 4.2754 |  | 3.1826 | 0.4127 | 4.0091 | 3.3638 | 3.3362 | 1.077 | 10.7625 | 14.2766 | 14.8689 | 11.0919 | -0.0001 | -0.0026 | 0.0004 | 0.0036 | 0.0008 | -0.0003 | 0.0033 | -0.016 | -0.022 | -360.1435 | 17.4007 | -360.4635 | 17.6882 | -360.8297 | 18.1707 | -360.8235 | 17.5773 | -352.6444 | 18.7128 | -352.6567 | 16.8217
12:37 | 4614 | 42.1358 | 202.4286 | 449.8782 | 456.6989 | -16.3263 | -40.5237 | 11.2736 | 7.9383 | 2.2778 | 0.8458 | 3.3612 | -0.9487 | 11.7577 | 4.7025 | 0.6176 | 0.6585 | 0.9641 | 0.7408 | -129.4581 | -0.1248 | 5.5979 | 1.8568 | -3.0347 | -1.4403 | 4.3731 |  | 3.2315 | 0.3536 | 4.0092 | 3.3652 | 3.3375 | 1.0786 | 10.7418 | 14.2438 | 14.8453 | 11.0836 | -0.0001 | -0.003 | 0.0008 | 0.0035 | 0.0006 | -0.0012 | 0.0004 | -0.0141 | -0.0314 | -360.1927 | 17.4048 | -360.4296 | 17.6697 | -360.8174 | 18.181 | -360.885 | 17.6081 | -352.6475 | 18.7066 | -352.6383 | 16.8094
12:37 | 4615 | 42.2218 | 202.4272 | 449.812 | 456.7076 | -16.1393 | -40.518 | 11.3839 | 7.916 | 2.3496 | 0.7829 | 3.392 | -0.9788 | 11.6911 | 4.6889 | 0.6181 | 0.6627 | 0.9635 | 0.7418 | -129.4616 | -0.0976 | 5.7545 | 1.7644 | -2.9565 | -1.3178 | 4.3457 |  | 3.2901 | 0.3947 | 4.0104 | 3.3646 | 3.3364 | 1.078 | 10.7359 | 14.2383 | 14.8475 | 11.0771 | 0.0001 | -0.0032 | 0.0013 | 0.0042 | 0.0007 | -0.0003 | 0.0121 | -0.0143 | -0.0181 | -360.1804 | 17.4213 | -360.4696 | 17.682 | -360.8143 | 18.1707 | -360.8204 | 17.5978 | -352.6321 | 18.721 | -352.6629 | 16.8279
12:37 | 4616 | 42.2498 | 202.3982 | 449.7819 | 456.6538 | -16.2021 | -40.5169 | 11.3043 | 7.9955 | 2.3652 | 0.7509 | 3.4059 | -0.9883 | 11.6768 | 4.5713 | 0.6173 | 0.6614 | 0.9645 | 0.7415 | -129.4297 | -0.091 | 5.6924 | 1.7316 | -2.9293 | -1.4054 | 4.4288 |  | 3.3131 | 0.4064 | 4.0099 | 3.3647 | 3.3367 | 1.0769 | 10.7475 | 14.2324 | 14.8348 | 11.0659 | 0.0003 | -0.003 | 0.0008 | 0.0039 | 0.0005 | -0.0009 | 0.0094 | -0.0061 | -0.0132 | -360.1896 | 17.4151 | -360.4727 | 17.682 | -360.842 | 18.1871 | -360.8481 | 17.6081 | -352.6475 | 18.721 | -352.6629 | 16.8176
12:37 | 4617 | 42.2572 | 202.4423 | 449.8749 | 456.6757 | -16.1964 | -40.5232 | 11.3249 | 7.9386 | 2.3581 | 0.65 | 3.367 | -1.0117 | 11.7113 | 4.5921 | 0.618 | 0.6607 | 0.9618 | 0.7411 | -129.4472 | -0.0944 | 5.7494 | 1.6778 | -2.949 | -1.2317 | 4.4546 |  | 3.1933 | 0.3396 | 4.0119 | 3.364 | 3.3373 | 1.0788 | 10.7255 | 14.2742 | 14.872 | 11.0897 | -0.0004 | -0.0027 | 0.0013 | 0.0047 | 0.0003 | -0.0001 | -0.0011 | -0.0036 | -0.0086 | -360.1742 | 17.4213 | -360.4666 | 17.6861 | -360.8204 | 18.1851 | -360.8512 | 17.5978 | -352.6413 | 18.7312 | -352.6783 | 16.8299
12:37 | 4618 | 42.1888 | 202.4148 | 449.8493 | 456.7704 | -16.173 | -40.4803 | 11.4601 | 7.8916 | 2.2798 | 0.6652 | 3.3692 | -1.0054 | 11.752 | 4.5492 | 0.6175 | 0.6623 | 0.9634 | 0.744 | -129.547 | -0.111 | 5.7494 | 1.6565 | -3.0239 | -1.4028 | 4.3752 |  | 3.204 | 0.3514 | 4.0106 | 3.3641 | 3.3348 | 1.0785 | 10.7602 | 14.2684 | 14.8662 | 11.0955 | -0.0001 | -0.0025 | 0.001 | 0.0041 | 0.001 | -0.0006 | -0.0046 | -0.0079 | 0.0055 | -360.1404 | 17.4151 | -360.4696 | 17.6944 | -360.8327 | 18.181 | -360.8666 | 17.5958 | -352.6444 | 18.7189 | -352.6567 | 16.8299
12:37 | 4619 | 42.2619 | 202.3738 | 449.8246 | 456.6476 | -16.2096 | -40.5448 | 11.3772 | 7.9148 | 2.2798 | 0.6867 | 3.3809 | -1.0226 | 11.7079 | 4.5695 | 0.6182 | 0.6628 | 0.966 | 0.7439 | -129.493 | -0.1883 | 5.6407 | 1.7723 | -3.1176 | -1.3705 | 4.4048 |  | 3.2164 | 0.2328 | 4.0086 | 3.363 | 3.3344 | 1.0776 | 10.7822 | 14.2788 | 14.8822 | 11.0944 | 0.0001 | -0.0029 | 0.0004 | 0.0033 | 0.0005 | -0.0002 | 0.008 | -0.0047 | -0.018 | -360.2419 | 17.4356 | -360.4758 | 17.6902 | -360.8358 | 18.1789 | -360.8481 | 17.6061 | -352.6629 | 18.7292 | -352.709 | 16.8217
12:37 | 4620 | 42.2011 | 202.4309 | 449.8184 | 456.7091 | -16.2139 | -40.4887 | 11.3675 | 7.8878 | 2.2149 | 0.6106 | 3.3985 | -0.9202 | 11.7727 | 4.6612 | 0.6181 | 0.6624 | 0.962 | 0.7438 | -129.5576 | -0.2046 | 5.6945 | 1.8247 | -3.0674 | -1.276 | 4.3842 |  | 3.2767 | 0.2022 | 4.0087 | 3.3613 | 3.34 | 1.0786 | 10.7428 | 14.2512 | 14.8673 | 11.0778 | 0.0005 | -0.0027 | 0.0009 | 0.004 | 0.0012 | 0 | -0.0054 | 0.0015 | -0.0197 | -360.1988 | 17.4213 | -360.4912 | 17.6923 | -360.8512 | 18.1851 | -360.8881 | 17.5999 | -352.6352 | 18.7169 | -352.669 | 16.8279
12:37 | 4621 | 42.1967 | 202.4078 | 449.8038 | 456.7022 | -16.229 | -40.4783 | 11.4739 | 7.9199 | 2.2323 | 0.5219 | 3.3775 | -0.985 | 11.7853 | 4.678 | 0.6159 | 0.6601 | 0.9622 | 0.7433 | -129.5501 | -0.221 | 5.6767 | 1.8682 | -3.043 | -1.3247 | 4.4739 |  | 3.232 | 0.2375 | 4.0089 | 3.3608 | 3.3349 | 1.0777 | 10.7532 | 14.2385 | 14.8601 | 11.0941 | 0 | -0.0026 | 0.0008 | 0.0036 | 0.0006 | -0.0001 | 0.0171 | -0.0029 | -0.0068 | -360.1958 | 17.4295 | -360.4542 | 17.6697 | -360.8327 | 18.181 | -360.8727 | 17.6102 | -352.6783 | 18.721 | -352.6567 | 16.8074
12:37 | 4622 | 42.1838 | 202.3424 | 449.6043 | 456.6703 | -16.2084 | -40.4637 | 11.3644 | 7.8435 | 2.1349 | 0.5517 | 3.4393 | -0.9552 | 11.7027 | 4.5921 | 0.6174 | 0.6617 | 0.9627 | 0.7432 | -129.5057 | -0.2685 | 5.7217 | 1.8236 | -3.0204 | -1.3674 | 4.4024 |  | 3.2371 | 0.2707 | 4.0085 | 3.363 | 3.3397 | 1.0788 | 10.7108 | 14.2351 | 14.8325 | 11.0714 | -0.0006 | -0.003 | 0.0001 | 0.0034 | 0.0008 | -0.0007 | 0.0205 | -0.0063 | 0.0129 | -360.1865 | 17.4397 | -360.4973 | 17.682 | -360.8481 | 18.1789 | -360.8235 | 17.5937 | -352.6198 | 18.7271 | -352.6998 | 16.8381
12:37 | 4623 | 42.1601 | 202.459 | 449.692 | 456.6946 | -16.269 | -40.5666 | 11.3246 | 7.8752 | 2.1546 | 0.5223 | 3.3828 | -1.0329 | 11.7009 | 4.5981 | 0.6163 | 0.6618 | 0.9595 | 0.7439 | -129.5981 | -0.2639 | 5.6399 | 1.8299 | -3.0568 | -1.2599 | 4.4612 |  | 3.1934 | 0.1117 | 4.0094 | 3.3628 | 3.3351 | 1.0765 | 10.7325 | 14.2289 | 14.8075 | 11.08 | -0.0002 | -0.0028 | 0.0011 | 0.0043 | 0.0007 | 0 | 0.0256 | -0.004 | 0.0014 | -360.1742 | 17.409 | -360.4481 | 17.6697 | -360.845 | 18.2056 | -360.8727 | 17.6122 | -352.6629 | 18.7004 | -352.6383 | 16.8238
12:37 | 4624 | 42.1895 | 202.441 | 449.6653 | 456.7076 | -16.2428 | -40.3905 | 11.4368 | 7.9034 | 2.2332 | 0.5601 | 3.3738 | -1.0955 | 11.6362 | 4.4906 | 0.6186 | 0.6641 | 0.9619 | 0.7432 | -129.5935 | -0.1278 | 5.6746 | 1.7427 | -3.0563 | -1.3102 | 4.4139 |  | 3.1744 | 0.2643 | 4.0077 | 3.3629 | 3.3345 | 1.0786 | 10.7325 | 14.2462 | 14.8365 | 11.0742 | 0.0002 | -0.0032 | 0.0004 | 0.0037 | 0.0009 | -0.0008 | 0.0028 | -0.0038 | 0.0001 | -360.2235 | 17.4377 | -360.4819 | 17.6779 | -360.8235 | 18.1687 | -360.8481 | 17.6081 | -352.6813 | 18.7436 | -352.6721 | 16.8115
12:37 | 4625 | 42.2349 | 202.481 | 449.8229 | 456.8121 | -16.2498 | -40.5795 | 11.4547 | 7.8926 | 2.1968 | 0.4559 | 3.3395 | -1.0441 | 11.6981 | 4.5349 | 0.6177 | 0.6624 | 0.9658 | 0.7447 | -129.6055 | -0.2533 | 5.6337 | 1.7599 | -3.0365 | -1.3184 | 4.3975 |  | 3.1671 | 0.2619 | 4.0078 | 3.3615 | 3.3347 | 1.0762 | 10.7498 | 14.2695 | 14.8549 | 11.0739 | -0.0002 | -0.003 | 0.0007 | 0.0041 | 0.0006 | -0.0008 | 0.0156 | -0.0087 | -0.0098 | -360.1404 | 17.4172 | -360.4696 | 17.6923 | -360.8881 | 18.1892 | -360.8881 | 17.5896 | -352.629 | 18.7066 | -352.6598 | 16.8423
12:37 | 4626 | 42.1982 | 202.4168 | 449.7911 | 456.7353 | -16.2844 | -40.5382 | 11.3711 | 7.8687 | 2.3177 | 0.6087 | 3.4012 | -0.9626 | 11.7365 | 4.6113 | 0.6173 | 0.6614 | 0.9653 | 0.7435 | -129.5636 | -0.1705 | 5.6265 | 1.7676 | -3.0431 | -1.2201 | 4.4336 |  | 3.1477 | 0.2067 | 4.0104 | 3.3608 | 3.3372 | 1.077 | 10.7925 | 14.2721 | 14.8714 | 11.0984 | -0.0002 | -0.0027 | 0.0011 | 0.0041 | 0.0008 | -0.0003 | 0.0145 | -0.0074 | -0.015 | -360.2173 | 17.4315 | -360.4481 | 17.6594 | -360.8112 | 18.1789 | -360.9004 | 17.6225 | -352.6567 | 18.7148 | -352.6475 | 16.7971
12:37 | 4627 | 42.1807 | 202.3721 | 449.6259 | 456.6418 | -16.327 | -40.4795 | 11.3682 | 7.8499 | 2.2521 | 0.5686 | 3.3516 | -1.0544 | 11.6388 | 4.5086 | 0.6176 | 0.6611 | 0.9619 | 0.7431 | -129.4928 | -0.1382 | 5.5925 | 1.7845 | -3.0101 | -1.3211 | 4.4499 |  | 3.1672 | 0.2653 | 4.0102 | 3.3661 | 3.3389 | 1.0782 | 10.7822 | 14.2788 | 14.8938 | 11.1349 | -0.0002 | -0.0031 | 0.0003 | 0.0032 | 0.0006 | -0.0007 | 0.0132 | -0.0203 | -0.0053 | -360.1835 | 17.4418 | -360.5096 | 17.6861 | -360.8574 | 18.1522 | -360.802 | 17.5999 | -352.666 | 18.7292 | -352.6906 | 16.8402
12:37 | 4628 | 42.192 | 202.4525 | 449.8526 | 456.7497 | -16.3239 | -40.5849 | 11.3437 | 7.87 | 2.1352 | 0.5544 | 3.2506 | -0.963 | 11.7024 | 4.6647 | 0.6176 | 0.6587 | 0.9616 | 0.7423 | -129.503 | 0.0104 | 5.6831 | 1.7981 | -3.0174 | -1.2011 | 4.5147 |  | 3.0971 | 0.2117 | 4.0085 | 3.3639 | 3.3394 | 1.0764 | 10.7589 | 14.2907 | 14.867 | 11.0937 | 0.0001 | -0.003 | 0.0013 | 0.0041 | 0.0005 | -0.0004 | 0.0029 | 0.003 | -0.0304 | -360.1988 | 17.4028 | -360.4419 | 17.682 | -360.842 | 18.1769 | -360.9097 | 17.6163 | -352.6198 | 18.6922 | -352.6444 | 16.8176
12:37 | 4629 | 42.0849 | 202.4929 | 449.7798 | 456.733 | -16.3264 | -40.5294 | 11.3719 | 7.8504 | 2.2424 | 0.542 | 3.368 | -1.0041 | 11.6662 | 4.5798 | 0.6169 | 0.661 | 0.9635 | 0.7417 | -129.479 | -0.1013 | 5.6741 | 1.8235 | -3.0286 | -1.2077 | 4.507 |  | 3.1097 | 0.1724 | 4.009 | 3.3632 | 3.3378 | 1.0788 | 10.7625 | 14.2649 | 14.8331 | 11.0865 | -0.0002 | -0.003 | 0.0011 | 0.004 | 0.0011 | -0.0007 | -0.0096 | -0.0064 | -0.0034 | -360.2388 | 17.4562 | -360.4912 | 17.68 | -360.8143 | 18.1255 | -360.8174 | 17.6081 | -352.6783 | 18.7456 | -352.709 | 16.8238
12:37 | 4630 | 42.3331 | 202.5297 | 449.9236 | 456.847 | -16.309 | -40.5698 | 11.2956 | 7.9126 | 2.3349 | 0.4417 | 3.4032 | -1.0471 | 11.6235 | 4.5892 | 0.6181 | 0.6602 | 0.9623 | 0.7415 | -129.5753 | -0.1356 | 5.6458 | 1.7853 | -3.0166 | -1.3517 | 4.4954 |  | 3.1211 | 0.0703 | 4.0084 | 3.3608 | 3.3335 | 1.0763 | 10.7499 | 14.2578 | 14.8481 | 11.0916 | -0.0002 | -0.0028 | 0.0005 | 0.0034 | 0.0005 | -0.0005 | 0.0032 | 0.0007 | -0.0072 | -360.1588 | 17.4048 | -360.4573 | 17.6861 | -360.9097 | 18.1769 | -360.8789 | 17.5835 | -352.6444 | 18.6881 | -352.6629 | 16.8299
12:37 | 4631 | 42.3208 | 202.5898 | 449.899 | 456.8898 | -16.3594 | -40.6327 | 11.4207 | 7.8877 | 2.3545 | 0.4964 | 3.3388 | -1.104 | 11.7033 | 4.613 | 0.6171 | 0.6587 | 0.9594 | 0.7408 | -129.5385 | -0.002 | 5.7232 | 1.6777 | -3.0783 | -1.2647 | 4.4539 |  | 3.174 | 0.1992 | 4.0106 | 3.3647 | 3.3377 | 1.0783 | 10.7117 | 14.2254 | 14.8045 | 11.0706 | -0.0001 | -0.0031 | 0.001 | 0.0044 | 0.001 | -0.0009 | 0.0098 | -0.0183 | -0.0144 | -360.2542 | 17.4418 | -360.4604 | 17.6594 | -360.7958 | 18.1296 | -360.8604 | 17.6163 | -352.6844 | 18.7271 | -352.6721 | 16.8156
12:37 | 4632 | 42.2579 | 202.475 | 449.9398 | 456.7937 | -16.307 | -40.6952 | 11.3068 | 7.8967 | 2.3314 | 0.6259 | 3.3854 | -1.1306 | 11.6134 | 4.5306 | 0.618 | 0.6613 | 0.9633 | 0.7416 | -129.4893 | -0.1019 | 5.689 | 1.7312 | -3.1802 | -1.3191 | 4.4441 |  | 3.1276 | 0.2465 | 4.008 | 3.3615 | 3.3394 | 1.0775 | 10.7568 | 14.2821 | 14.8784 | 11.0927 | 0.0004 | -0.0033 | 0.0005 | 0.0037 | 0.0005 | -0.0002 | 0.0178 | 0.0011 | 0.0086 | -360.1558 | 17.4151 | -360.485 | 17.6964 | -360.885 | 18.1604 | -360.8204 | 17.5794 | -352.5952 | 18.7045 | -352.669 | 16.8566
12:37 | 4633 | 42.3482 | 202.4045 | 449.8799 | 456.756 | -16.2708 | -40.7429 | 11.3316 | 7.9807 | 2.4075 | 0.6927 | 3.4544 | -1.1491 | 11.6832 | 4.5499 | 0.6179 | 0.6628 | 0.9624 | 0.7412 | -129.433 | -0.09 | 5.71 | 1.7809 | -3.0674 | -1.208 | 4.4663 |  | 3.1999 | 0.3215 | 4.0078 | 3.3623 | 3.3416 | 1.0784 | 10.7405 | 14.2372 | 14.8345 | 11.0818 | 0 | -0.0031 | 0.0007 | 0.0039 | 0.0014 | -0.0005 | 0.0024 | 0.0008 | -0.0146 | -360.1958 | 17.409 | -360.4419 | 17.6512 | -360.7989 | 18.1645 | -360.9004 | 17.643 | -352.6752 | 18.7025 | -352.6229 | 16.8115
12:37 | 4634 | 42.3341 | 202.4077 | 449.8893 | 456.7825 | -16.3462 | -40.6993 | 11.3967 | 8.0284 | 2.3898 | 0.6119 | 3.4564 | -1.0811 | 11.6419 | 4.5932 | 0.6182 | 0.6627 | 0.9622 | 0.7437 | -129.4595 | -0.1217 | 5.7333 | 1.8651 | -3.003 | -1.2118 | 4.4968 |  | 3.1576 | 0.2675 | 4.0079 | 3.3659 | 3.3425 | 1.078 | 10.7635 | 14.2665 | 14.8724 | 11.1038 | -0.0002 | -0.0025 | 0.0006 | 0.0037 | 0.0006 | -0.0003 | 0.0126 | -0.0124 | -0.0267 | -360.1711 | 17.4315 | -360.5066 | 17.6923 | -360.842 | 18.1358 | -360.8112 | 17.5958 | -352.6567 | 18.7312 | -352.6813 | 16.8546
12:37 | 4635 | 42.346 | 202.453 | 449.915 | 456.7555 | -16.2272 | -40.5431 | 11.452 | 8.0067 | 2.3186 | 0.6527 | 3.3781 | -1.0851 | 11.6967 | 4.5747 | 0.6183 | 0.6611 | 0.9612 | 0.7425 | -129.4131 | -0.0857 | 5.7605 | 1.8316 | -3.0177 | -1.2325 | 4.4078 |  | 3.1897 | 0.2891 | 4.0083 | 3.3652 | 3.3396 | 1.0756 | 10.781 | 14.3009 | 14.905 | 11.1161 | -0.0002 | -0.0028 | 0.0007 | 0.0034 | 0.0007 | -0.0006 | 0.0067 | -0.0133 | -0.011 | -360.1588 | 17.3946 | -360.4389 | 17.6574 | -360.8327 | 18.1892 | -360.8912 | 17.6307 | -352.6229 | 18.6799 | -352.6136 | 16.8238
12:37 | 4636 | 42.2914 | 202.5479 | 449.8696 | 456.7673 | -16.2881 | -40.6202 | 11.3095 | 7.9486 | 2.3283 | 0.7611 | 3.3717 | -0.9819 | 11.7462 | 4.5456 | 0.6173 | 0.6626 | 0.9626 | 0.7433 | -129.389 | -0.0396 | 5.762 | 1.7023 | -3.1023 | -1.3069 | 4.4389 |  | 3.2267 | 0.3374 | 4.0085 | 3.3611 | 3.3392 | 1.0774 | 10.7601 | 14.263 | 14.8625 | 11.0774 | 0.0005 | -0.0027 | 0.0008 | 0.0041 | 0.0006 | -0.0003 | 0.022 | -0.0078 | 0.004 | -360.2019 | 17.4562 | -360.4881 | 17.6697 | -360.805 | 18.1296 | -360.8389 | 17.6307 | -352.6813 | 18.7395 | -352.7029 | 16.8176
12:37 | 4637 | 42.3742 | 202.4889 | 449.8763 | 456.7671 | -16.2353 | -40.5974 | 11.3484 | 8.0264 | 2.3799 | 0.5813 | 3.3331 | -0.9934 | 11.7511 | 4.6517 | 0.6175 | 0.6636 | 0.9616 | 0.7445 | -129.4314 | -0.1867 | 5.7101 | 1.6728 | -2.9686 | -1.1856 | 4.4884 |  | 3.2532 | 0.2744 | 4.0089 | 3.3675 | 3.3405 | 1.0788 | 10.7498 | 14.2812 | 14.8849 | 11.1255 | 0.0002 | -0.0031 | 0.0007 | 0.0037 | 0.0007 | -0.0003 | 0.0091 | -0.0012 | -0.0211 | -360.1219 | 17.3925 | -360.4727 | 17.6985 | -360.8635 | 18.1769 | -360.8635 | 17.5876 | -352.626 | 18.6963 | -352.6413 | 16.8423
12:37 | 4638 | 42.3393 | 202.3769 | 449.8684 | 456.7503 | -16.2034 | -40.5491 | 11.3353 | 8.0248 | 2.3685 | 0.5617 | 3.3333 | -1.0139 | 11.7112 | 4.6552 | 0.6166 | 0.6601 | 0.9595 | 0.743 | -129.3922 | -0.1045 | 5.8042 | 1.6345 | -2.9987 | -1.2632 | 4.4205 |  | 3.1865 | 0.2652 | 4.0091 | 3.3632 | 3.3362 | 1.0776 | 10.7556 | 14.2579 | 14.8665 | 11.1085 | -0.0003 | -0.0025 | 0.0006 | 0.0043 | 0.0011 | -0.0004 | 0.0158 | -0.0012 | -0.0088 | -360.2388 | 17.4356 | -360.4358 | 17.6512 | -360.7866 | 18.144 | -360.8635 | 17.643 | -352.709 | 18.721 | -352.6506 | 16.8074
12:37 | 4639 | 42.2383 | 202.3682 | 449.7991 | 456.7723 | -16.216 | -40.6287 | 11.3337 | 7.9703 | 2.4552 | 0.7505 | 3.3195 | -1.0908 | 11.688 | 4.614 | 0.6171 | 0.6584 | 0.9621 | 0.743 | -129.4335 | -0.0498 | 5.8022 | 1.6927 | -3.0222 | -1.2522 | 4.453 |  | 3.2022 | 0.2683 | 4.0093 | 3.3632 | 3.3365 | 1.0781 | 10.7371 | 14.2625 | 14.8362 | 11.0786 | -0.0001 | -0.0027 | 0.0016 | 0.0051 | 0.0004 | -0.0008 | 0.0095 | -0.017 | -0.0038 | -360.1958 | 17.4254 | -360.5189 | 17.7128 | -360.8881 | 18.1379 | -360.8204 | 17.5999 | -352.6413 | 18.7169 | -352.6906 | 16.8566
12:37 | 4640 | 42.2503 | 202.3856 | 449.762 | 456.675 | -16.2592 | -40.6346 | 11.2595 | 8.0336 | 2.4117 | 0.7105 | 3.3181 | -0.9936 | 11.7439 | 4.6068 | 0.6169 | 0.6587 | 0.9627 | 0.7428 | -129.4852 | -0.0916 | 5.6878 | 1.8799 | -3.0466 | -1.3053 | 4.4257 |  | 3.1828 | 0.2121 | 4.0093 | 3.3659 | 3.3391 | 1.0774 | 10.7152 | 14.2404 | 14.8133 | 11.0742 | 0.0004 | -0.003 | 0.0006 | 0.0032 | 0.0007 | -0.0009 | 0.0178 | 0.0014 | -0.0022 | -360.1988 | 17.3905 | -360.4112 | 17.6574 | -360.8112 | 18.1748 | -360.9066 | 17.6348 | -352.6567 | 18.682 | -352.629 | 16.8032
12:37 | 4641 | 42.2894 | 202.408 | 449.7371 | 456.7345 | -16.2369 | -40.6019 | 11.282 | 7.8926 | 2.4682 | 0.6306 | 3.3381 | -1.002 | 11.7081 | 4.6726 | 0.6181 | 0.6615 | 0.9619 | 0.7432 | -129.5722 | -0.0965 | 5.7515 | 1.8687 | -2.9715 | -1.3324 | 4.4763 |  | 3.1888 | 0.1718 | 4.0104 | 3.3622 | 3.3383 | 1.0766 | 10.7268 | 14.2345 | 14.8123 | 11.0573 | -0.0001 | -0.0033 | 0.0008 | 0.0039 | 0.0005 | -0.0009 | 0.0246 | -0.0208 | 0.0004 | -360.2111 | 17.4562 | -360.5158 | 17.682 | -360.8358 | 18.1276 | -360.8204 | 17.6184 | -352.6906 | 18.7353 | -352.7029 | 16.832
12:37 | 4642 | 42.2984 | 202.4927 | 449.8053 | 456.7266 | -16.2456 | -40.6759 | 11.2336 | 7.9255 | 2.4289 | 0.6459 | 3.3293 | -1.0281 | 11.652 | 4.6936 | 0.6178 | 0.6551 | 0.9641 | 0.7438 | -129.4642 | -0.0091 | 5.7241 | 1.9243 | -2.9889 | -1.2557 | 4.4794 |  | 3.2114 | 0.219 | 4.0086 | 3.3626 | 3.338 | 1.0768 | 10.7371 | 14.2683 | 14.842 | 11.0843 | 0.0003 | -0.0025 | 0.001 | 0.0037 | 0.0008 | -0.0008 | 0.0058 | 0.0019 | -0.031 | -360.1404 | 17.3987 | -360.4604 | 17.6841 | -360.8635 | 18.181 | -360.8697 | 17.6081 | -352.6167 | 18.6861 | -352.6537 | 16.8443
12:37 | 4643 | 42.3551 | 202.4174 | 449.7753 | 456.8093 | -16.2347 | -40.5735 | 11.2667 | 7.9084 | 2.4373 | 0.655 | 3.2675 | -0.9947 | 11.6696 | 4.6173 | 0.6177 | 0.6583 | 0.9609 | 0.743 | -129.4548 | -0.0998 | 5.7099 | 1.9618 | -2.9794 | -1.2119 | 4.4772 |  | 3.2248 | 0.2299 | 4.0102 | 3.367 | 3.3369 | 1.0787 | 10.7302 | 14.2613 | 14.8406 | 11.0948 | -0.0004 | -0.0028 | 0.0008 | 0.0037 | 0.0006 | 0.0001 | 0.0206 | 0.0043 | -0.01 | -360.2481 | 17.4336 | -360.4604 | 17.6615 | -360.7804 | 18.1481 | -360.8604 | 17.6451 | -352.7029 | 18.7312 | -352.6444 | 16.8053
12:37 | 4644 | 42.323 | 202.3835 | 449.8431 | 456.8578 | -16.3072 | -40.5207 | 11.2464 | 7.8629 | 2.3513 | 0.6273 | 3.1942 | -0.9439 | 11.7111 | 4.6533 | 0.6166 | 0.6611 | 0.9652 | 0.7442 | -129.413 | 0.0125 | 5.6712 | 1.8871 | -2.938 | -1.2376 | 4.5341 |  | 3.1419 | 0.3178 | 4.0094 | 3.3627 | 3.3354 | 1.0798 | 10.7591 | 14.2613 | 14.858 | 11.0948 | 0 | -0.0028 | 0.0006 | 0.0039 | 0.0011 | -0.0005 | 0.025 | -0.0103 | -0.0174 | -360.1711 | 17.4356 | -360.5066 | 17.7169 | -360.8789 | 18.1584 | -360.8143 | 17.5999 | -352.6506 | 18.723 | -352.6906 | 16.8566
12:37 | 4645 | 42.2485 | 202.3611 | 449.8864 | 456.7505 | -16.3472 | -40.5485 | 11.2938 | 7.943 | 2.4133 | 0.7686 | 3.3005 | -1.042 | 11.688 | 4.5132 | 0.6171 | 0.6586 | 0.9631 | 0.7441 | -129.4626 | -0.0461 | 5.6965 | 1.8554 | -3.0334 | -1.203 | 4.5122 |  | 3.2783 | 0.239 | 4.0098 | 3.3633 | 3.3367 | 1.0784 | 10.7394 | 14.2821 | 14.861 | 11.0753 | 0 | -0.0032 | 0.0006 | 0.0043 | 0.0009 | 0.0004 | 0.0121 | -0.0174 | -0.0154 | -360.1804 | 17.4007 | -360.4296 | 17.6594 | -360.8143 | 18.1789 | -360.8758 | 17.6369 | -352.6506 | 18.682 | -352.589 | 16.8053
12:37 | 4646 | 42.3182 | 202.342 | 449.9179 | 456.7407 | -16.3562 | -40.71 | 11.3079 | 7.8371 | 2.4176 | 0.715 | 3.2846 | -1.0478 | 11.7531 | 4.5456 | 0.6187 | 0.6575 | 0.9632 | 0.7434 | -129.4426 | 0.0375 | 5.796 | 1.7973 | -3.0407 | -1.2684 | 4.4231 |  | 3.2431 | 0.228 | 4.0102 | 3.3633 | 3.3405 | 1.0792 | 10.7544 | 14.28 | 14.872 | 11.084 | -0.0002 | -0.0026 | 0.0006 | 0.0038 | 0.0012 | -0.0005 | 0.0122 | 0.0006 | -0.0154 | -360.2204 | 17.4623 | -360.5189 | 17.6985 | -360.8512 | 18.1317 | -360.8112 | 17.6061 | -352.6875 | 18.7374 | -352.7152 | 16.8361
12:37 | 4647 | 42.3455 | 202.4054 | 449.9444 | 456.8062 | -16.3523 | -40.6641 | 11.3458 | 7.9027 | 2.4622 | 0.7862 | 3.251 | -1.0228 | 11.7609 | 4.5236 | 0.6187 | 0.6605 | 0.9623 | 0.7436 | -129.4851 | -0.0159 | 5.7268 | 1.8269 | -3.0331 | -1.2714 | 4.4907 |  | 3.1597 | 0.247 | 4.0107 | 3.3617 | 3.3395 | 1.0792 | 10.766 | 14.2336 | 14.8304 | 11.0901 | -0.0003 | -0.0025 | 0.0008 | 0.0044 | 0.0007 | -0.0005 | 0.0046 | 0.0029 | 0.006 | -360.1281 | 17.3987 | -360.4389 | 17.6902 | -360.885 | 18.181 | -360.882 | 17.6102 | -352.5952 | 18.6861 | -352.6106 | 16.8361
12:37 | 4648 | 42.3538 | 202.4424 | 449.861 | 456.7385 | -16.3519 | -40.5966 | 11.2242 | 7.8893 | 2.4627 | 0.8203 | 3.331 | -0.9354 | 11.7992 | 4.5423 | 0.6177 | 0.6605 | 0.965 | 0.7435 | -129.4488 | 0.0138 | 5.7392 | 1.8388 | -3.1328 | -1.2561 | 4.4054 |  | 3.1757 | 0.2995 | 4.0107 | 3.3634 | 3.335 | 1.0783 | 10.7557 | 14.2346 | 14.8365 | 11.0742 | -0.0002 | -0.0031 | 0.0004 | 0.0034 | 0.001 | -0.0004 | 0.0175 | -0.0031 | -0.0134 | -360.245 | 17.45 | -360.4573 | 17.6492 | -360.7897 | 18.1276 | -360.8266 | 17.6286 | -352.709 | 18.721 | -352.6444 | 16.8012
12:37 | 4649 | 42.3657 | 202.4195 | 449.8495 | 456.7209 | -16.3116 | -40.5884 | 11.2426 | 7.8842 | 2.4541 | 0.8548 | 3.2662 | -0.9421 | 11.7458 | 4.5718 | 0.6168 | 0.6581 | 0.9624 | 0.7438 | -129.5302 | -0.0182 | 5.6262 | 1.8454 | -3.0172 | -1.2701 | 4.4358 |  | 3.1959 | 0.278 | 4.0115 | 3.3667 | 3.3369 | 1.078 | 10.7625 | 14.2708 | 14.8631 | 11.115 | 0.0002 | -0.0033 | 0.0011 | 0.004 | 0.0009 | -0.0008 | 0.0075 | -0.0015 | -0.0171 | -360.1281 | 17.411 | -360.4819 | 17.6923 | -360.885 | 18.1584 | -360.8143 | 17.5814 | -352.6044 | 18.6922 | -352.666 | 16.8443
12:37 | 4650 | 42.2798 | 202.4112 | 449.8344 | 456.7171 | -16.2519 | -40.6465 | 11.2519 | 7.7844 | 2.4003 | 0.8378 | 3.2761 | -0.8165 | 11.7218 | 4.6003 | 0.6165 | 0.6613 | 0.9651 | 0.7454 | -129.5388 | 0.0172 | 5.5708 | 1.9417 | -2.9585 | -1.2872 | 4.4634 |  | 3.1904 | 0.2805 | 4.0101 | 3.3676 | 3.3372 | 1.08 | 10.7557 | 14.2692 | 14.8354 | 11.0688 | -0.0004 | -0.0033 | 0.0009 | 0.0037 | 0.0004 | -0.0005 | 0.0002 | -0.0121 | -0.0206 | -360.205 | 17.4028 | -360.4327 | 17.641 | -360.7804 | 18.1543 | -360.882 | 17.6266 | -352.6413 | 18.6943 | -352.589 | 16.7807
12:37 | 4651 | 42.3625 | 202.3574 | 449.7021 | 456.727 | -16.2451 | -40.5662 | 11.3334 | 7.8056 | 2.3716 | 0.728 | 3.2264 | -0.9269 | 11.6951 | 4.5301 | 0.6177 | 0.6576 | 0.9631 | 0.7436 | -129.4963 | -0.0164 | 5.6823 | 1.9293 | -2.8494 | -1.3369 | 4.4318 |  | 3.2371 | 0.2651 | 4.0092 | 3.363 | 3.3377 | 1.0784 | 10.7671 | 14.2523 | 14.8618 | 11.1082 | -0.0002 | -0.0023 | 0.0009 | 0.0035 | 0.0014 | -0.0003 | 0.0131 | -0.0028 | -0.0289 | -360.1711 | 17.4336 | -360.485 | 17.6718 | -360.8266 | 18.1112 | -360.7681 | 17.5773 | -352.6198 | 18.7066 | -352.6875 | 16.8299
12:37 | 4652 | 42.3954 | 202.3195 | 449.748 | 456.7038 | -16.2717 | -40.5969 | 11.1686 | 7.8004 | 2.3065 | 0.6951 | 3.2364 | -0.9184 | 11.7408 | 4.6217 | 0.6179 | 0.663 | 0.9631 | 0.7445 | -129.4492 | -0.0102 | 5.6344 | 1.957 | -2.8981 | -1.37 | 4.4817 |  | 3.2553 | 0.3948 | 4.0105 | 3.3641 | 3.3376 | 1.0797 | 10.7578 | 14.2779 | 14.8714 | 11.1042 | -0.0001 | -0.0027 | 0.0011 | 0.0044 | 0.0008 | -0.0002 | 0.0082 | -0.0135 | -0.0094 | -360.1465 | 17.3802 | -360.405 | 17.6451 | -360.7989 | 18.1625 | -360.8789 | 17.5917 | -352.586 | 18.6594 | -352.589 | 16.8012
12:37 | 4653 | 42.2813 | 202.3795 | 449.8696 | 456.7723 | -16.3097 | -40.6712 | 11.2328 | 7.8822 | 2.3575 | 0.7095 | 3.3272 | -0.9723 | 11.6671 | 4.5232 | 0.6181 | 0.6618 | 0.9596 | 0.7446 | -129.4985 | 0.0215 | 5.7033 | 1.9932 | -2.9884 | -1.3054 | 4.3919 |  | 3.2249 | 0.3468 | 4.0099 | 3.3681 | 3.338 | 1.0778 | 10.7151 | 14.2868 | 14.8433 | 11.097 | 0.0001 | -0.0033 | 0.0007 | 0.0043 | 0.0011 | -0.0007 | 0.0177 | -0.0074 | 0.0065 | -360.205 | 17.4397 | -360.4481 | 17.6266 | -360.7558 | 18.1071 | -360.7927 | 17.5978 | -352.629 | 18.7066 | -352.6537 | 16.8012
12:37 | 4654 | 42.3898 | 202.3915 | 449.821 | 456.6798 | -16.1881 | -40.5338 | 11.2188 | 7.9373 | 2.3621 | 0.7835 | 3.2396 | -0.8751 | 11.7249 | 4.6315 | 0.618 | 0.6628 | 0.9653 | 0.7442 | -129.448 | 0.0314 | 5.7182 | 1.8737 | -2.9571 | -1.3537 | 4.4167 |  | 3.1582 | 0.3734 | 4.0111 | 3.3639 | 3.3367 | 1.079 | 10.7821 | 14.2791 | 14.8901 | 11.0879 | 0.0001 | -0.0028 | 0.0011 | 0.0041 | 0.0005 | -0.0005 | 0.0122 | -0.0009 | 0.002 | -360.0942 | 17.3782 | -360.4142 | 17.6718 | -360.842 | 18.1399 | -360.7989 | 17.5732 | -352.5244 | 18.6614 | -352.6383 | 16.8258
12:37 | 4655 | 42.3595 | 202.3581 | 449.8601 | 456.6814 | -16.2581 | -40.5508 | 11.2806 | 7.8904 | 2.3361 | 0.7605 | 3.2193 | -1.0311 | 11.6996 | 4.5728 | 0.6162 | 0.662 | 0.9601 | 0.7454 | -129.4821 | 0.058 | 5.6844 | 1.8822 | -2.9636 | -1.2911 | 4.4165 |  | 3.2305 | 0.4198 | 4.0104 | 3.3605 | 3.3337 | 1.0791 | 10.7292 | 14.2364 | 14.8118 | 11.0837 | -0.0007 | -0.0029 | 0.0004 | 0.0039 | 0.0009 | -0.0008 | 0.0212 | -0.0101 | -0.0131 | -360.1896 | 17.3884 | -360.4081 | 17.6061 | -360.7435 | 18.1296 | -360.8481 | 17.6184 | -352.6383 | 18.6799 | -352.5736 | 16.7807
12:37 | 4656 | 42.4024 | 202.3852 | 449.8314 | 456.6985 | -16.3764 | -40.6201 | 11.2145 | 7.8564 | 2.3015 | 0.5254 | 3.1723 | -1.0068 | 11.7622 | 4.5894 | 0.6173 | 0.6587 | 0.9597 | 0.7436 | -129.5363 | -0.019 | 5.5942 | 1.9142 | -2.9402 | -1.328 | 4.4081 |  | 3.2907 | 0.3142 | 4.0091 | 3.3647 | 3.3369 | 1.0799 | 10.7624 | 14.271 | 14.8758 | 11.0857 | -0.0001 | -0.0027 | 0.0004 | 0.0035 | 0.001 | 0.0001 | 0.0119 | -0.0165 | -0.0066 | -360.1435 | 17.4048 | -360.4573 | 17.6533 | -360.7927 | 18.1112 | -360.7466 | 17.5568 | -352.6106 | 18.6984 | -352.6506 | 16.8279
12:37 | 4657 | 42.4238 | 202.4385 | 449.8599 | 456.7642 | -16.3307 | -40.6626 | 11.2408 | 7.9694 | 2.4022 | 0.8651 | 3.2929 | -1.061 | 11.7286 | 4.5441 | 0.6187 | 0.6602 | 0.9648 | 0.7444 | -129.4477 | 0.0274 | 5.6074 | 1.888 | -2.9371 | -1.2991 | 4.374 |  | 3.203 | 0.2545 | 4.0086 | 3.3622 | 3.3391 | 1.0793 | 10.728 | 14.2124 | 14.7547 | 11.0472 | 0.0003 | -0.0031 | 0.0004 | 0.0036 | 0.0009 | -0.0006 | 0.0045 | -0.0088 | -0.0039 | -360.1188 | 17.3617 | -360.3835 | 17.6307 | -360.802 | 18.1543 | -360.8389 | 17.5855 | -352.5706 | 18.6614 | -352.5736 | 16.8012
12:37 | 4658 | 42.4281 | 202.4442 | 449.8372 | 456.7804 | -16.3423 | -40.6134 | 11.195 | 7.8987 | 2.4365 | 0.8431 | 3.2576 | -1.0339 | 11.7388 | 4.6223 | 0.6187 | 0.6615 | 0.9637 | 0.7447 | -129.5273 | -0.1199 | 5.5069 | 1.8389 | -3.0846 | -1.3972 | 4.3781 |  | 3.2544 | 0.3006 | 4.0094 | 3.3627 | 3.3387 | 1.0797 | 10.7568 | 14.2532 | 14.8379 | 11.11 | 0.0001 | -0.0037 | 0.0008 | 0.0038 | 0.0007 | -0.0003 | 0.009 | -0.0115 | 0.001 | -360.1773 | 17.4254 | -360.4389 | 17.641 | -360.7466 | 18.0988 | -360.802 | 17.5978 | -352.6537 | 18.7169 | -352.6383 | 16.795
12:37 | 4659 | 42.4322 | 202.4931 | 449.8049 | 456.7403 | -16.4701 | -40.742 | 11.0964 | 7.9275 | 2.3675 | 0.6767 | 3.2649 | -1.1203 | 11.7748 | 4.6469 | 0.6175 | 0.6597 | 0.9649 | 0.7448 | -129.4639 | -0.0023 | 5.6717 | 1.8603 | -3.0725 | -1.4431 | 4.411 |  | 3.2447 | 0.3033 | 4.0098 | 3.3626 | 3.3385 | 1.0791 | 10.7635 | 14.3072 | 14.8272 | 11.0861 | 0.0001 | -0.0022 | 0.0012 | 0.0044 | 0.0014 | -0.0001 | 0.0206 | 0.0005 | -0.0057 | -360.1342 | 17.3802 | -360.4389 | 17.6779 | -360.8481 | 18.1522 | -360.7989 | 17.5691 | -352.5706 | 18.6655 | -352.626 | 16.8402
12:37 | 4660 | 42.3537 | 202.4173 | 449.8091 | 456.723 | -16.407 | -40.7781 | 11.1466 | 7.8937 | 2.3295 | 0.6047 | 3.2268 | -1.0652 | 11.7912 | 4.5461 | 0.6175 | 0.6614 | 0.9653 | 0.7444 | -129.3078 | 0.0394 | 5.7173 | 1.8003 | -3.0825 | -1.3923 | 4.4509 |  | 3.2715 | 0.3541 | 4.0083 | 3.3659 | 3.3369 | 1.0775 | 10.8007 | 14.3149 | 14.8904 | 11.124 | -0.0001 | -0.0026 | 0.0003 | 0.0038 | 0.0003 | -0.0005 | 0.0146 | -0.0235 | 0.0035 | -360.2081 | 17.4131 | -360.405 | 17.6286 | -360.7681 | 18.142 | -360.8727 | 17.6369 | -352.6783 | 18.6943 | -352.6413 | 16.7889
12:37 | 4661 | 42.3952 | 202.3726 | 449.7944 | 456.7713 | -16.3683 | -40.8266 | 11.1505 | 7.9587 | 2.339 | 0.6607 | 3.2697 | -0.9702 | 11.7233 | 4.6052 | 0.6183 | 0.6603 | 0.9631 | 0.7453 | -129.4184 | -0.0259 | 5.7276 | 1.7375 | -3.1091 | -1.365 | 4.4068 |  | 3.2084 | 0.3391 | 4.0093 | 3.368 | 3.3406 | 1.0791 | 10.7751 | 14.2723 | 14.8956 | 11.098 | 0.0006 | -0.0026 | 0.001 | 0.0043 | 0.001 | -0.0002 | -0.0005 | -0.0116 | -0.0108 | -360.1404 | 17.4397 | -360.4912 | 17.6861 | -360.845 | 18.1379 | -360.7897 | 17.5835 | -352.6537 | 18.7128 | -352.706 | 16.8525
12:37 | 4662 | 42.4553 | 202.42 | 449.7985 | 456.7331 | -16.4379 | -40.8231 | 11.226 | 7.9617 | 2.3349 | 0.6523 | 3.2365 | -0.969 | 11.7381 | 4.6901 | 0.6173 | 0.6606 | 0.9607 | 0.7441 | -129.4737 | 0.0142 | 5.7296 | 1.5633 | -3.1441 | -1.3866 | 4.418 |  | 3.2355 | 0.3524 | 4.008 | 3.3638 | 3.3392 | 1.0778 | 10.7636 | 14.2836 | 14.8819 | 11.0814 | 0.0001 | -0.0029 | 0.001 | 0.004 | 0.0004 | -0.0008 | 0.0125 | -0.0218 | -0.0138 | -360.165 | 17.3987 | -360.4358 | 17.6738 | -360.842 | 18.1871 | -360.8912 | 17.6184 | -352.6167 | 18.684 | -352.629 | 16.8381
12:37 | 4663 | 42.4177 | 202.4146 | 449.8615 | 456.7229 | -16.3674 | -40.7473 | 11.2437 | 7.9853 | 2.2634 | 0.6562 | 3.2574 | -0.9726 | 11.8237 | 4.5964 | 0.6184 | 0.6591 | 0.9632 | 0.7436 | -129.4233 | -0.0301 | 5.7313 | 1.5537 | -3.1747 | -1.377 | 4.4588 |  | 3.314 | 0.4547 | 4.0085 | 3.366 | 3.3368 | 1.0796 | 10.7428 | 14.2627 | 14.8488 | 11.1071 | -0.0002 | -0.0024 | 0.0005 | 0.004 | 0.0004 | -0.0003 | 0.0124 | -0.0108 | -0.0003 | -360.2696 | 17.4459 | -360.485 | 17.6553 | -360.7681 | 18.1379 | -360.8574 | 17.6348 | -352.7121 | 18.7312 | -352.6721 | 16.8135
12:37 | 4664 | 42.3604 | 202.3729 | 449.803 | 456.6831 | -16.3834 | -40.6756 | 11.2286 | 7.8873 | 2.2767 | 0.6225 | 3.2763 | -0.9684 | 11.8907 | 4.6352 | 0.6173 | 0.6602 | 0.9629 | 0.7451 | -129.462 | -0.0226 | 5.6873 | 1.5664 | -2.9967 | -1.413 | 4.4477 |  | 3.2774 | 0.4141 | 4.0084 | 3.3666 | 3.3389 | 1.0795 | 10.759 | 14.2383 | 14.8475 | 11.0944 | -0.0001 | -0.0027 | 0.0008 | 0.0038 | 0.001 | -0.0008 | 0.0095 | -0.0012 | 0.0038 | -360.1342 | 17.4233 | -360.5066 | 17.7005 | -360.8974 | 18.1625 | -360.8204 | 17.5917 | -352.6075 | 18.7045 | -352.7029 | 16.8464
12:37 | 4665 | 42.3703 | 202.3841 | 449.8555 | 456.7309 | -16.3074 | -40.6338 | 11.239 | 7.808 | 2.2438 | 0.6169 | 3.1848 | -0.9236 | 11.8127 | 4.6623 | 0.6167 | 0.6574 | 0.961 | 0.7435 | -129.4576 | 0.0567 | 5.7367 | 1.6429 | -2.9992 | -1.4061 | 4.4782 |  | 3.2574 | 0.2895 | 4.009 | 3.3698 | 3.3376 | 1.0786 | 10.7245 | 14.2378 | 14.8606 | 11.0671 | 0 | -0.0033 | 0.0007 | 0.0036 | 0.0009 | -0.0004 | 0.0359 | -0.0001 | -0.0111 | -360.1958 | 17.4007 | -360.4142 | 17.6553 | -360.805 | 18.1625 | -360.885 | 17.6266 | -352.6383 | 18.6943 | -352.6136 | 16.8012
12:37 | 4666 | 42.396 | 202.3926 | 449.9854 | 456.7887 | -16.3191 | -40.6749 | 11.1961 | 7.9183 | 2.2315 | 0.527 | 3.2534 | -0.963 | 11.7695 | 4.5654 | 0.6167 | 0.6613 | 0.9637 | 0.745 | -129.4387 | -0.0556 | 5.704 | 1.6598 | -2.9465 | -1.264 | 4.5824 |  | 3.2443 | 0.3549 | 4.0085 | 3.3666 | 3.3384 | 1.0783 | 10.7405 | 14.2662 | 14.8645 | 11.0641 | 0.0007 | -0.0027 | 0.0011 | 0.0041 | 0.0009 | -0.0008 | 0.0219 | 0.0079 | -0.0026 | -360.1835 | 17.4377 | -360.4789 | 17.6697 | -360.7927 | 18.1091 | -360.8174 | 17.604 | -352.6136 | 18.7251 | -352.669 | 16.8094
12:37 | 4667 | 42.3958 | 202.356 | 449.9162 | 456.8521 | -16.3483 | -40.7894 | 11.2238 | 7.9733 | 2.1857 | 0.6745 | 3.2795 | -0.9154 | 11.7809 | 4.6005 | 0.6169 | 0.6614 | 0.965 | 0.7434 | -129.4248 | -0.0893 | 5.6571 | 1.709 | -3.0171 | -1.3779 | 4.5809 |  | 3.2795 | 0.3217 | 4.0081 | 3.366 | 3.335 | 1.0797 | 10.7429 | 14.2509 | 14.8246 | 11.0901 | -0.0002 | -0.0028 | 0.0007 | 0.004 | 0.0009 | 0.0001 | 0.0115 | -0.0072 | 0.0005 | -360.1281 | 17.3843 | -360.4142 | 17.6615 | -360.8481 | 18.1543 | -360.842 | 17.5773 | -352.5736 | 18.6696 | -352.6352 | 16.8197
12:38 | 4668 | 42.3804 | 202.4208 | 449.8279 | 456.772 | -16.3775 | -40.7022 | 11.2523 | 7.9448 | 2.2527 | 0.5873 | 3.2305 | -0.9336 | 11.7989 | 4.6468 | 0.6185 | 0.662 | 0.9649 | 0.7449 | -129.4001 | 0.0308 | 5.7119 | 1.4941 | -2.9214 | -1.2773 | 4.5854 |  | 3.2884 | 0.3268 | 4.0086 | 3.3646 | 3.3378 | 1.0781 | 10.752 | 14.2953 | 14.8598 | 11.0926 | -0.0001 | -0.0027 | 0.0008 | 0.004 | 0.001 | -0.0001 | 0.0042 | -0.0035 | -0.0171 | -360.2019 | 17.4069 | -360.4296 | 17.6204 | -360.7343 | 18.1255 | -360.8327 | 17.6204 | -352.629 | 18.682 | -352.5952 | 16.7827
12:38 | 4669 | 42.3215 | 202.4011 | 449.6868 | 456.7561 | -16.3012 | -40.7275 | 11.2921 | 7.8448 | 2.3045 | 0.663 | 3.2639 | -0.964 | 11.7926 | 4.5229 | 0.6176 | 0.6581 | 0.9649 | 0.7431 | -129.3863 | 0.0774 | 5.6675 | 1.5931 | -3.0046 | -1.3146 | 4.5156 |  | 3.3251 | 0.2311 | 4.0104 | 3.3654 | 3.3356 | 1.0796 | 10.7602 | 14.2916 | 14.8604 | 11.0955 | 0.0001 | -0.0029 | 0.0009 | 0.004 | 0.0008 | -0.0004 | -0.0072 | 0.0067 | -0.0233 | -360.1711 | 17.4007 | -360.4635 | 17.6677 | -360.7989 | 18.1112 | -360.7927 | 17.5773 | -352.5983 | 18.6881 | -352.666 | 16.8176
12:38 | 4670 | 42.4303 | 202.4123 | 449.7691 | 456.7105 | -16.4539 | -40.7927 | 11.1757 | 7.8834 | 2.283 | 0.6325 | 3.3277 | -1.0338 | 11.7345 | 4.5526 | 0.6172 | 0.6566 | 0.9625 | 0.7456 | -129.3494 | 0.1199 | 5.7726 | 1.7705 | -3.0024 | -1.3773 | 4.5225 |  | 3.245 | 0.1959 | 4.0085 | 3.3628 | 3.3389 | 1.079 | 10.7441 | 14.2925 | 14.8481 | 11.1031 | -0.0002 | -0.0031 | 0.0004 | 0.0035 | 0.0008 | -0.0004 | -0.0065 | -0.0041 | -0.016 | -360.1065 | 17.3802 | -360.3804 | 17.6369 | -360.8174 | 18.1543 | -360.8143 | 17.5855 | -352.5921 | 18.6655 | -352.589 | 16.8053
12:38 | 4671 | 42.48 | 202.4093 | 449.8813 | 456.6764 | -16.4858 | -40.7114 | 11.2559 | 7.8688 | 2.2263 | 0.5829 | 3.3031 | -0.9345 | 11.8041 | 4.5425 | 0.6169 | 0.659 | 0.966 | 0.7454 | -129.3374 | 0.0719 | 5.7544 | 1.8265 | -3.0731 | -1.2294 | 4.488 |  | 3.3104 | 0.2238 | 4.0101 | 3.3608 | 3.3375 | 1.078 | 10.7626 | 14.23 | 14.8436 | 11.0695 | -0.0001 | -0.0026 | 0.0003 | 0.0037 | 0.0009 | -0.0004 | 0.0277 | -0.01 | -0.0179 | -360.1373 | 17.4172 | -360.4204 | 17.6143 | -360.7343 | 18.1132 | -360.7835 | 17.602 | -352.6013 | 18.6922 | -352.5952 | 16.7848
12:38 | 4672 | 42.541 | 202.4786 | 449.9005 | 456.6964 | -16.4285 | -40.6015 | 11.1996 | 7.9194 | 2.2932 | 0.648 | 3.3223 | -0.9292 | 11.8439 | 4.5554 | 0.6172 | 0.6626 | 0.9671 | 0.7432 | -129.314 | 0.1245 | 5.8836 | 1.8136 | -3.076 | -1.3398 | 4.5277 |  | 3.3133 | 0.2315 | 4.01 | 3.3638 | 3.3346 | 1.0788 | 10.751 | 14.2705 | 14.861 | 11.0811 | -0.0008 | -0.0029 | 0.0012 | 0.0043 | 0.0004 | -0.0007 | 0.0138 | -0.0021 | -0.0088 | -360.085 | 17.3987 | -360.4481 | 17.6553 | -360.805 | 18.1296 | -360.7773 | 17.5794 | -352.5736 | 18.6902 | -352.6321 | 16.8156
12:38 | 4673 | 42.4515 | 202.5143 | 449.8512 | 456.7225 | -16.3805 | -40.6371 | 11.199 | 7.8983 | 2.2479 | 0.598 | 3.2976 | -1.0173 | 11.7572 | 4.5501 | 0.6176 | 0.6631 | 0.9642 | 0.745 | -129.2842 | 0.1115 | 5.8003 | 1.7831 | -3.0341 | -1.2596 | 4.5299 |  | 3.281 | 0.2185 | 4.0094 | 3.3628 | 3.3368 | 1.0786 | 10.7741 | 14.2591 | 14.8968 | 11.0865 | 0.0002 | -0.0031 | 0.0013 | 0.004 | 0.001 | -0.0006 | 0.0111 | -0.0077 | -0.01 | -360.1096 | 17.3864 | -360.4019 | 17.6204 | -360.805 | 18.1379 | -360.7927 | 17.5937 | -352.5767 | 18.6737 | -352.5767 | 16.795
12:38 | 4674 | 42.4963 | 202.4206 | 449.8308 | 456.7563 | -16.402 | -40.5702 | 11.2491 | 7.8868 | 2.2903 | 0.622 | 3.3082 | -1.0008 | 11.7622 | 4.5229 | 0.618 | 0.6608 | 0.9676 | 0.7428 | -129.3408 | 0.1075 | 5.7828 | 1.8514 | -3.0372 | -1.1763 | 4.5984 |  | 3.2406 | 0.2941 | 4.0104 | 3.3667 | 3.3374 | 1.0803 | 10.7232 | 14.2833 | 14.8392 | 11.088 | -0.0002 | -0.0034 | 0.0009 | 0.0042 | 0.0005 | -0.0005 | 0.0055 | -0.0102 | -0.0045 | -360.1496 | 17.4151 | -360.4266 | 17.6225 | -360.7497 | 18.1255 | -360.7927 | 17.5835 | -352.6198 | 18.6963 | -352.6106 | 16.8032
12:38 | 4675 | 42.4293 | 202.3518 | 449.8406 | 456.7188 | -16.4837 | -40.6837 | 11.2022 | 7.957 | 2.3119 | 0.6704 | 3.3651 | -0.998 | 11.7421 | 4.5859 | 0.6165 | 0.6618 | 0.9633 | 0.7439 | -129.3532 | 0.0904 | 5.737 | 1.7592 | -2.9431 | -1.2822 | 4.5787 |  | 3.2495 | 0.1653 | 4.0108 | 3.3638 | 3.3359 | 1.0771 | 10.7498 | 14.2812 | 14.856 | 11.0966 | -0.0002 | -0.0029 | 0.0007 | 0.0035 | 0.0009 | -0.0006 | 0.0125 | 0.0006 | -0.0075 | -360.1065 | 17.3946 | -360.4358 | 17.643 | -360.7743 | 18.1235 | -360.805 | 17.5773 | -352.5675 | 18.6696 | -352.6013 | 16.7991
12:38 | 4676 | 42.5119 | 202.4244 | 449.8231 | 456.6935 | -16.2546 | -40.402 | 11.458 | 7.8452 | 2.2744 | 0.6351 | 3.3226 | -0.9233 | 11.7802 | 4.612 | 0.6179 | 0.66 | 0.9638 | 0.7461 | -129.4057 | 0.163 | 5.683 | 1.79 | -2.9478 | -1.2128 | 4.5304 |  | 3.2655 | 0.2657 | 4.0097 | 3.3649 | 3.3364 | 1.0786 | 10.737 | 14.2802 | 14.8499 | 11.1067 | -0.0005 | -0.0031 | 0.0004 | 0.0039 | 0.0007 | -0.0004 | 0.0096 | -0.0138 | -0.0158 | -360.1311 | 17.3905 | -360.4142 | 17.6328 | -360.762 | 18.1255 | -360.805 | 17.5794 | -352.589 | 18.684 | -352.6013 | 16.7991
12:38 | 4677 | 42.6241 | 202.4189 | 449.9334 | 456.7556 | -16.1873 | -40.3865 | 11.3346 | 7.9248 | 2.262 | 0.6837 | 3.2967 | -0.8722 | 11.7696 | 4.5829 | 0.6164 | 0.6626 | 0.9634 | 0.7442 | -129.4006 | 0.1662 | 5.7456 | 1.6859 | -2.939 | -1.3354 | 4.513 |  | 3.2427 | 0.2376 | 4.0098 | 3.3631 | 3.3345 | 1.0795 | 10.7557 | 14.2635 | 14.8307 | 11.08 | 0.0002 | -0.0026 | 0.001 | 0.0041 | 0.0009 | -0.0007 | 0.0069 | -0.0181 | -0.0014 | -360.1465 | 17.4028 | -360.4019 | 17.6266 | -360.7589 | 18.1235 | -360.7927 | 17.5814 | -352.586 | 18.6758 | -352.6044 | 16.7991
12:38 | 4678 | 42.5611 | 202.3861 | 449.9251 | 456.7066 | -16.2388 | -40.4108 | 11.3796 | 7.9282 | 2.2695 | 0.6062 | 3.3269 | -0.875 | 11.786 | 4.552 | 0.6192 | 0.6599 | 0.9622 | 0.7447 | -129.3776 | 0.0412 | 5.7527 | 1.7158 | -3.0016 | -1.3097 | 4.5246 |  | 3.2325 | 0.2244 | 4.0111 | 3.3638 | 3.3369 | 1.0787 | 10.767 | 14.2931 | 14.8813 | 11.1016 | 0.0001 | -0.0027 | 0.0006 | 0.0037 | 0.0006 | 0.0004 | 0.0103 | -0.0059 | -0.0323 | -360.1219 | 17.3843 | -360.3958 | 17.6266 | -360.7466 | 18.1296 | -360.8143 | 17.5896 | -352.6075 | 18.6758 | -352.5983 | 16.8012
12:38 | 4679 | 42.5518 | 202.4739 | 449.9052 | 456.7531 | -16.2429 | -40.3565 | 11.3782 | 7.8694 | 2.3155 | 0.4519 | 3.1989 | -0.8635 | 11.8039 | 4.6003 | 0.6184 | 0.6604 | 0.9648 | 0.7437 | -129.3996 | 0.1011 | 5.7859 | 1.6497 | -2.9934 | -1.3354 | 4.4622 |  | 3.2558 | 0.1905 | 4.0108 | 3.364 | 3.337 | 1.0799 | 10.7626 | 14.2588 | 14.8194 | 11.1161 | -0.0005 | -0.003 | 0.0001 | 0.0034 | 0.0007 | -0.001 | 0.0091 | -0.0158 | 0.0065 | -360.1496 | 17.3946 | -360.3835 | 17.6286 | -360.7712 | 18.1173 | -360.7835 | 17.5896 | -352.6167 | 18.682 | -352.6136 | 16.8012
12:38 | 4680 | 42.6701 | 202.4462 | 449.9629 | 456.8053 | -16.1891 | -40.3034 | 11.4064 | 7.8642 | 2.3386 | 0.5709 | 3.2647 | -0.9778 | 11.8378 | 4.6553 | 0.6179 | 0.6586 | 0.9604 | 0.745 | -129.4895 | 0.1307 | 5.8102 | 1.6424 | -2.9351 | -1.2228 | 4.542 |  | 3.1558 | 0.2763 | 4.0095 | 3.3647 | 3.3349 | 1.0791 | 10.7082 | 14.2509 | 14.813 | 11.0786 | 0 | -0.0025 | 0.0014 | 0.0046 | 0.0003 | -0.0004 | 0.0106 | -0.0057 | -0.0023 | -360.1127 | 17.3966 | -360.3927 | 17.6369 | -360.7927 | 18.1358 | -360.7989 | 17.5691 | -352.5306 | 18.6737 | -352.6198 | 16.8135
12:38 | 4681 | 42.5014 | 202.367 | 449.9469 | 456.7425 | -16.1827 | -40.3801 | 11.4562 | 7.9088 | 2.3225 | 0.4725 | 3.2111 | -0.9921 | 11.7168 | 4.5091 | 0.6189 | 0.6592 | 0.9657 | 0.743 | -129.5181 | 0.2083 | 5.8692 | 1.6665 | -2.9361 | -1.1881 | 4.5333 |  | 3.1461 | 0.2585 | 4.0111 | 3.362 | 3.3369 | 1.0792 | 10.7532 | 14.279 | 14.889 | 11.1114 | 0 | -0.0028 | 0.0012 | 0.0039 | 0.001 | -0.0007 | -0.004 | -0.0088 | -0.0213 | -360.1435 | 17.3905 | -360.405 | 17.6163 | -360.7527 | 18.1317 | -360.8481 | 17.5937 | -352.6106 | 18.6717 | -352.6106 | 16.8012
12:38 | 4682 | 42.5651 | 202.5024 | 449.9451 | 456.7625 | -16.2051 | -40.3521 | 11.3519 | 7.9194 | 2.3488 | 0.5073 | 3.2856 | -1.0404 | 11.7953 | 4.4871 | 0.6175 | 0.6599 | 0.9629 | 0.7436 | -129.4872 | 0.271 | 5.8106 | 1.6941 | -2.918 | -1.272 | 4.5213 |  | 3.2701 | 0.2032 | 4.0084 | 3.3664 | 3.3345 | 1.079 | 10.7625 | 14.2882 | 14.8747 | 11.0919 | 0.0003 | -0.003 | 0.0005 | 0.0038 | 0.0002 | -0.0007 | -0.0047 | 0.0002 | -0.0084 | -360.1804 | 17.409 | -360.4296 | 17.6307 | -360.7373 | 18.105 | -360.7866 | 17.5937 | -352.626 | 18.6984 | -352.6136 | 16.7991
12:38 | 4683 | 42.4753 | 202.4071 | 449.966 | 456.7148 | -16.2417 | -40.4385 | 11.3549 | 7.9424 | 2.4598 | 0.5466 | 3.3037 | -0.9262 | 11.786 | 4.5974 | 0.6172 | 0.6576 | 0.9633 | 0.7442 | -129.4801 | 0.1955 | 5.7351 | 1.6929 | -2.9735 | -1.3481 | 4.4487 |  | 3.2286 | 0.1608 | 4.0097 | 3.3642 | 3.3368 | 1.0801 | 10.7775 | 14.2686 | 14.8499 | 11.1009 | 0.0006 | -0.0026 | 0.0011 | 0.0044 | 0.001 | -0.0002 | -0.002 | 0.0083 | 0.0025 | -360.1188 | 17.3823 | -360.4327 | 17.6451 | -360.805 | 18.1276 | -360.802 | 17.5712 | -352.5736 | 18.6758 | -352.6198 | 16.8238
12:38 | 4684 | 42.4594 | 202.4029 | 449.9997 | 456.7722 | -16.3236 | -40.387 | 11.3259 | 7.9596 | 2.3671 | 0.4892 | 3.2929 | -0.8523 | 11.8635 | 4.6559 | 0.6163 | 0.6576 | 0.9636 | 0.7436 | -129.5136 | 0.1648 | 5.8189 | 1.6447 | -2.9007 | -1.3743 | 4.4671 |  | 3.16 | 0.1413 | 4.0096 | 3.3652 | 3.3339 | 1.0799 | 10.751 | 14.2707 | 14.8679 | 11.0981 | -0.0004 | -0.0028 | 0.0003 | 0.0035 | 0.0006 | -0.0006 | 0.0179 | -0.007 | -0.0012 | -360.1188 | 17.3761 | -360.3712 | 17.6102 | -360.7712 | 18.1358 | -360.8512 | 17.5999 | -352.6013 | 18.6553 | -352.5644 | 16.8012
12:38 | 4685 | 42.5007 | 202.3781 | 450.016 | 456.7585 | -16.305 | -40.3547 | 11.3573 | 8.0667 | 2.3296 | 0.6481 | 3.3406 | -0.9276 | 11.7045 | 4.6109 | 0.6178 | 0.6593 | 0.9659 | 0.7443 | -129.4941 | 0.1442 | 5.7496 | 1.6345 | -2.9854 | -1.3156 | 4.5202 |  | 3.1682 | 0.1573 | 4.0096 | 3.3641 | 3.3398 | 1.0784 | 10.7279 | 14.253 | 14.8021 | 11.0699 | 0.0001 | -0.0022 | 0.0009 | 0.004 | 0.0006 | -0.0003 | 0.0198 | -0.0045 | -0.0171 | -360.1681 | 17.4151 | -360.4419 | 17.6286 | -360.7558 | 18.0988 | -360.7743 | 17.5835 | -352.6229 | 18.7107 | -352.6475 | 16.7991
12:38 | 4686 | 42.6299 | 202.5135 | 450.0418 | 456.8388 | -16.2621 | -40.334 | 11.4085 | 7.9925 | 2.4476 | 0.5469 | 3.2788 | -0.9313 | 11.7495 | 4.5267 | 0.6161 | 0.6589 | 0.9667 | 0.744 | -129.4702 | 0.0826 | 5.8072 | 1.6601 | -2.9852 | -1.344 | 4.5026 |  | 3.24 | 0.1455 | 4.0091 | 3.3618 | 3.3359 | 1.0798 | 10.7393 | 14.265 | 14.8574 | 11.0803 | 0.0004 | -0.0031 | 0.0008 | 0.0042 | 0.0007 | -0.0007 | 0.0085 | -0.0085 | -0.0235 | -360.0696 | 17.372 | -360.4204 | 17.6451 | -360.7927 | 18.1461 | -360.7866 | 17.5629 | -352.5583 | 18.6553 | -352.6198 | 16.8217
12:38 | 4687 | 42.5291 | 202.421 | 450.0007 | 456.7388 | -16.2911 | -40.2858 | 11.4304 | 8.0583 | 2.4645 | 0.5336 | 3.3575 | -1.0088 | 11.6707 | 4.5061 | 0.6189 | 0.6584 | 0.9687 | 0.7439 | -129.4594 | 0.1127 | 5.7938 | 1.6993 | -3.0619 | -1.2817 | 4.441 |  | 3.1824 | 0.1681 | 4.0089 | 3.3621 | 3.3368 | 1.0792 | 10.7279 | 14.2532 | 14.8552 | 11.0927 | 0.0002 | -0.0027 | 0.0007 | 0.0039 | 0.0006 | -0.0002 | 0.0082 | -0.0189 | -0.0106 | -360.205 | 17.3987 | -360.405 | 17.6081 | -360.7281 | 18.1296 | -360.8112 | 17.6163 | -352.626 | 18.6758 | -352.5983 | 16.7868
12:38 | 4688 | 42.5789 | 202.3923 | 449.9267 | 456.7163 | -16.2588 | -40.3865 | 11.4286 | 8.0322 | 2.4427 | 0.5494 | 3.3438 | -0.9161 | 11.7761 | 4.5264 | 0.6181 | 0.6606 | 0.9623 | 0.7428 | -129.5902 | 0.1003 | 5.7121 | 1.6613 | -2.9938 | -1.3054 | 4.4561 |  | 3.2008 | 0.2106 | 4.0099 | 3.3629 | 3.3365 | 1.0782 | 10.7464 | 14.2544 | 14.8682 | 11.0937 | -0.0003 | -0.0026 | 0.0015 | 0.0043 | 0.001 | -0.0006 | 0.0101 | -0.0042 | -0.0098 | -360.1342 | 17.411 | -360.4512 | 17.6451 | -360.7804 | 18.1029 | -360.7558 | 17.5568 | -352.589 | 18.6984 | -352.6537 | 16.8238
12:38 | 4689 | 42.5068 | 202.402 | 450.0339 | 456.8052 | -16.2866 | -40.3862 | 11.4016 | 8.0414 | 2.3814 | 0.4939 | 3.3081 | -0.8857 | 11.7567 | 4.6339 | 0.6189 | 0.6595 | 0.9629 | 0.7456 | -129.532 | 0.0756 | 5.6786 | 1.7485 | -2.9962 | -1.3118 | 4.423 |  | 3.132 | 0.2219 | 4.01 | 3.365 | 3.336 | 1.0793 | 10.7578 | 14.2779 | 14.9003 | 11.1331 | -0.0002 | -0.0025 | 0.0008 | 0.0041 | 0.001 | 0 | 0.024 | -0.0174 | -0.0184 | -360.1281 | 17.3699 | -360.3773 | 17.6369 | -360.7804 | 18.1522 | -360.8389 | 17.5835 | -352.5798 | 18.6614 | -352.5644 | 16.8135
12:38 | 4690 | 42.4893 | 202.4238 | 449.9896 | 456.7035 | -16.2664 | -40.2957 | 11.4213 | 8.057 | 2.3829 | 0.5695 | 3.362 | -0.8785 | 11.7967 | 4.485 | 0.6179 | 0.6597 | 0.963 | 0.7459 | -129.5177 | 0.1176 | 5.7585 | 1.8482 | -2.9481 | -1.2994 | 4.4544 |  | 3.1945 | 0.1961 | 4.0095 | 3.3652 | 3.3329 | 1.079 | 10.7371 | 14.2739 | 14.9046 | 11.1078 | 0.0002 | -0.0033 | 0.0004 | 0.0035 | 0.0007 | -0.0008 | 0.0132 | -0.0062 | -0.0251 | -360.1835 | 17.4069 | -360.4142 | 17.6081 | -360.7004 | 18.105 | -360.7927 | 17.5958 | -352.6321 | 18.6963 | -352.6136 | 16.7848
12:38 | 4691 | 42.5211 | 202.4119 | 450.0024 | 456.6986 | -16.225 | -40.4224 | 11.4597 | 8.0597 | 2.369 | 0.5813 | 3.3868 | -1.0341 | 11.6886 | 4.4848 | 0.6172 | 0.6638 | 0.9635 | 0.7455 | -129.5161 | 0.2292 | 5.778 | 1.8994 | -3.0578 | -1.2751 | 4.4229 |  | 3.2701 | 0.2674 | 4.0087 | 3.361 | 3.3369 | 1.0793 | 10.7498 | 14.2348 | 14.8318 | 11.1028 | 0.0001 | -0.0034 | 0.0005 | 0.0038 | 0.001 | 0.0001 | 0.0117 | 0.0012 | -0.0203 | -360.1127 | 17.4028 | -360.4358 | 17.6677 | -360.8266 | 18.1214 | -360.7835 | 17.565 | -352.589 | 18.6943 | -352.6444 | 16.8279
12:38 | 4692 | 42.629 | 202.3822 | 449.8797 | 456.7086 | -16.3029 | -40.3011 | 11.5131 | 8.0199 | 2.4152 | 0.56 | 3.3572 | -0.9642 | 11.6801 | 4.4686 | 0.6171 | 0.6601 | 0.9633 | 0.7442 | -129.4784 | 0.171 | 5.8522 | 2.0226 | -3.0191 | -1.321 | 4.5455 |  | 3.1674 | 0.1882 | 4.0092 | 3.3627 | 3.3347 | 1.0804 | 10.7798 | 14.3058 | 14.8884 | 11.1316 | 0.0001 | -0.0024 | 0.0006 | 0.0035 | 0.0009 | -0.0007 | 0.0167 | 0.0032 | -0.0163 | -360.1742 | 17.3802 | -360.365 | 17.6266 | -360.7804 | 18.1502 | -360.8327 | 17.5999 | -352.6136 | 18.6676 | -352.5675 | 16.7889
12:38 | 4693 | 42.6037 | 202.5018 | 450.0415 | 456.7132 | -16.2213 | -40.3206 | 11.5354 | 8.0018 | 2.3709 | 0.4904 | 3.299 | -1.0872 | 11.6682 | 4.5245 | 0.6176 | 0.6594 | 0.9606 | 0.7448 | -129.5353 | 0.3125 | 5.8733 | 1.8961 | -3.0303 | -1.3083 | 4.5571 |  | 3.2548 | 0.187 | 4.0107 | 3.3634 | 3.3375 | 1.0794 | 10.7061 | 14.2191 | 14.8466 | 11.0895 | -0.0005 | -0.003 | 0.0006 | 0.0041 | 0.0002 | -0.0005 | 0.0075 | -0.0021 | -0.0202 | -360.1804 | 17.4295 | -360.4604 | 17.6245 | -360.7497 | 18.1071 | -360.7773 | 17.5999 | -352.6383 | 18.7148 | -352.6475 | 16.7971
12:38 | 4694 | 42.6666 | 202.541 | 450.0871 | 456.6589 | -16.31 | -40.5124 | 11.5279 | 7.9942 | 2.3347 | 0.6244 | 3.376 | -1.0205 | 11.7869 | 4.5433 | 0.6181 | 0.6615 | 0.9654 | 0.7458 | -129.5369 | 0.2965 | 5.8051 | 1.8668 | -2.9945 | -1.3405 | 4.5207 |  | 3.2145 | 0.2526 | 4.0092 | 3.3632 | 3.3352 | 1.0798 | 10.7682 | 14.271 | 14.8237 | 11.0973 | 0.0003 | -0.0029 | 0.001 | 0.0039 | 0.0011 | -0.0002 | 0.0071 | -0.0094 | -0.0089 | -360.0788 | 17.3864 | -360.4296 | 17.6615 | -360.8481 | 18.144 | -360.7866 | 17.5691 | -352.5736 | 18.6799 | -352.6475 | 16.8361
12:38 | 4695 | 42.5913 | 202.4575 | 449.9693 | 456.6621 | -16.2865 | -40.5088 | 11.4658 | 7.9492 | 2.348 | 0.5336 | 3.4056 | -0.8847 | 11.7845 | 4.5674 | 0.6174 | 0.661 | 0.9621 | 0.744 | -129.4977 | 0.2906 | 5.8558 | 1.9245 | -2.8667 | -1.3012 | 4.5621 |  | 3.1689 | 0.2087 | 4.0102 | 3.3652 | 3.3395 | 1.0783 | 10.7498 | 14.2696 | 14.8502 | 11.0735 | 0 | -0.0031 | 0.0005 | 0.0039 | 0.0009 | -0.0003 | 0.0143 | -0.0119 | -0.0067 | -360.1742 | 17.372 | -360.3835 | 17.6102 | -360.7466 | 18.144 | -360.8389 | 17.604 | -352.6198 | 18.6717 | -352.5952 | 16.7909
12:38 | 4696 | 42.5793 | 202.4561 | 449.9236 | 456.6191 | -16.3192 | -40.4367 | 11.4362 | 8.0173 | 2.3835 | 0.5409 | 3.3396 | -0.8675 | 11.7407 | 4.5445 | 0.6177 | 0.6632 | 0.9613 | 0.7447 | -129.4644 | 0.2746 | 5.9187 | 1.8758 | -2.9367 | -1.2928 | 4.5608 |  | 3.1884 | 0.1405 | 4.009 | 3.3632 | 3.3333 | 1.0776 | 10.729 | 14.2834 | 14.8287 | 11.0645 | -0.0008 | -0.0032 | 0.0014 | 0.0041 | 0.0009 | -0.0002 | 0.0096 | -0.0178 | 0.01 | -360.1835 | 17.4233 | -360.4789 | 17.643 | -360.7773 | 18.0968 | -360.7681 | 17.5814 | -352.626 | 18.721 | -352.669 | 16.8258
12:38 | 4697 | 42.6221 | 202.4581 | 449.9847 | 456.7421 | -16.2536 | -40.5053 | 11.325 | 7.9634 | 2.3813 | 0.5587 | 3.2432 | -0.8471 | 11.8053 | 4.595 | 0.6182 | 0.6633 | 0.9652 | 0.7479 | -129.4199 | 0.2442 | 5.8988 | 1.8132 | -2.9864 | -1.2958 | 4.5267 |  | 3.2189 | 0.2138 | 4.0079 | 3.3621 | 3.3365 | 1.0784 | 10.7624 | 14.2653 | 14.8826 | 11.1027 | -0.0004 | -0.0026 | 0.0006 | 0.0037 | 0.0006 | -0.0009 | 0.0084 | -0.01 | -0.0077 | -360.0665 | 17.372 | -360.4019 | 17.6451 | -360.8327 | 18.1543 | -360.8297 | 17.5547 | -352.586 | 18.6655 | -352.6167 | 16.832
12:38 | 4698 | 42.5313 | 202.4557 | 449.927 | 456.7255 | -16.2711 | -40.4928 | 11.5219 | 8.0064 | 2.3889 | 0.6336 | 3.2881 | -0.865 | 11.8272 | 4.5782 | 0.6164 | 0.6623 | 0.9606 | 0.7445 | -129.5536 | 0.0641 | 5.8913 | 1.8045 | -2.9969 | -1.2922 | 4.545 |  | 3.2375 | 0.1457 | 4.0079 | 3.3632 | 3.3362 | 1.0772 | 10.7707 | 14.2554 | 14.8685 | 11.101 | -0.0005 | -0.0035 | 0.0003 | 0.0035 | 0.0002 | -0.0002 | 0.0062 | -0.0153 | -0.0224 | -360.1742 | 17.3987 | -360.3989 | 17.6061 | -360.7466 | 18.1296 | -360.8358 | 17.6204 | -352.6598 | 18.684 | -352.6136 | 16.8053
12:38 | 4699 | 42.6665 | 202.4376 | 450.0198 | 456.7981 | -16.4046 | -40.5301 | 11.3622 | 7.9585 | 2.3459 | 0.4093 | 3.3231 | -0.8663 | 11.806 | 4.6288 | 0.6175 | 0.6633 | 0.9597 | 0.7437 | -129.5886 | 0.165 | 5.8235 | 1.7528 | -2.926 | -1.3468 | 4.5723 |  | 3.307 | 0.2366 | 4.0082 | 3.3619 | 3.3363 | 1.0789 | 10.7324 | 14.264 | 14.8686 | 11.102 | 0.0001 | -0.0029 | 0.0007 | 0.004 | 0.0013 | -0.0006 | 0.0194 | -0.0034 | -0.0212 | -360.1588 | 17.4131 | -360.4573 | 17.6492 | -360.7743 | 18.105 | -360.7681 | 17.565 | -352.5983 | 18.7066 | -352.669 | 16.8402
12:38 | 4700 | 42.635 | 202.421 | 450.0369 | 456.7499 | -16.413 | -40.5402 | 11.3914 | 8.0588 | 2.4106 | 0.5755 | 3.4408 | -0.978 | 11.7267 | 4.5524 | 0.6177 | 0.6618 | 0.9636 | 0.7438 | -129.5069 | 0.1818 | 5.8296 | 1.8053 | -2.9865 | -1.2572 | 4.5297 |  | 3.2911 | 0.3065 | 4.0084 | 3.3628 | 3.3348 | 1.0799 | 10.7429 | 14.2508 | 14.8351 | 11.0789 | -0.0001 | -0.0027 | 0.0006 | 0.0038 | 0.0004 | -0.0002 | 0 | 0.0028 | -0.0139 | -360.1127 | 17.3638 | -360.4112 | 17.643 | -360.7927 | 18.1625 | -360.8512 | 17.5876 | -352.6044 | 18.6614 | -352.5952 | 16.8217
12:38 | 4701 | 42.5079 | 202.3612 | 449.8762 | 456.7208 | -16.4273 | -40.4983 | 11.3768 | 8.0974 | 2.362 | 0.5467 | 3.3955 | -0.9572 | 11.7901 | 4.606 | 0.6168 | 0.6603 | 0.9636 | 0.7431 | -129.4492 | 0.2012 | 5.8693 | 1.725 | -2.9469 | -1.3415 | 4.5804 |  | 3.3392 | 0.345 | 4.0082 | 3.3622 | 3.3342 | 1.0788 | 10.7383 | 14.2345 | 14.847 | 11.0746 | -0.0002 | -0.0027 | 0.0008 | 0.004 | 0.0013 | 0 | 0.0035 | 0.0005 | -0.0006 | -360.1865 | 17.4192 | -360.4204 | 17.6122 | -360.7558 | 18.1194 | -360.8512 | 17.604 | -352.6413 | 18.7004 | -352.6321 | 16.8115
12:38 | 4702 | 42.5874 | 202.4487 | 449.941 | 456.74 | -16.38 | -40.5608 | 11.361 | 8.0374 | 2.3632 | 0.524 | 3.3517 | -0.8038 | 11.735 | 4.6252 | 0.6172 | 0.6593 | 0.962 | 0.7441 | -129.5044 | 0.1915 | 5.9056 | 1.7477 | -2.9295 | -1.1828 | 4.6057 |  | 3.239 | 0.2589 | 4.0086 | 3.3647 | 3.3368 | 1.0767 | 10.737 | 14.2511 | 14.7967 | 11.0897 | 0.0005 | -0.0026 | 0.0009 | 0.0041 | 0.0004 | -0.0005 | 0.0226 | -0.0087 | -0.0104 | -360.1096 | 17.4028 | -360.485 | 17.6574 | -360.8389 | 18.1255 | -360.7958 | 17.5794 | -352.6044 | 18.7107 | -352.6783 | 16.8587
12:38 | 4703 | 42.507 | 202.4198 | 449.8875 | 456.6557 | -16.4075 | -40.5472 | 11.2394 | 7.9883 | 2.355 | 0.4905 | 3.3848 | -0.9299 | 11.6982 | 4.4853 | 0.6179 | 0.6612 | 0.9622 | 0.7428 | -129.5125 | 0.26 | 5.8944 | 1.7333 | -2.9343 | -1.2482 | 4.6003 |  | 3.2489 | 0.2742 | 4.0081 | 3.3619 | 3.3356 | 1.0791 | 10.7382 | 14.2984 | 14.8491 | 11.0681 | 0.0002 | -0.0032 | 0.0009 | 0.0036 | 0.0009 | -0.0005 | -0.0032 | -0.0164 | -0.0101 | -360.1342 | 17.3802 | -360.3773 | 17.6245 | -360.8081 | 18.1604 | -360.845 | 17.6061 | -352.6136 | 18.6676 | -352.6075 | 16.8258
12:38 | 4704 | 42.5213 | 202.3678 | 449.9237 | 456.722 | -16.4386 | -40.5733 | 11.2581 | 8.0173 | 2.3333 | 0.5901 | 3.3481 | -0.925 | 11.6552 | 4.5773 | 0.6174 | 0.6654 | 0.9605 | 0.744 | -129.6205 | 0.1241 | 5.8112 | 1.8277 | -2.9468 | -1.281 | 4.57 |  | 3.3151 | 0.2928 | 4.01 | 3.3649 | 3.3369 | 1.0798 | 10.7509 | 14.2766 | 14.8747 | 11.0861 | -0.0001 | -0.0027 | 0.0009 | 0.0038 | 0.0007 | -0.0004 | 0.008 | -0.0054 | 0.0052 | -360.1896 | 17.4295 | -360.4358 | 17.6184 | -360.7404 | 18.1091 | -360.8174 | 17.6061 | -352.6567 | 18.723 | -352.6567 | 16.8115
12:38 | 4705 | 42.5534 | 202.4024 | 449.9807 | 456.7678 | -16.471 | -40.5662 | 11.1918 | 8.0375 | 2.2926 | 0.5035 | 3.3423 | -0.9342 | 11.7126 | 4.4998 | 0.6182 | 0.6635 | 0.9595 | 0.7439 | -129.5349 | 0.207 | 5.8333 | 1.8619 | -2.8737 | -1.2271 | 4.5843 |  | 3.3261 | 0.2644 | 4.0106 | 3.3637 | 3.3369 | 1.078 | 10.7682 | 14.2594 | 14.8468 | 11.0915 | -0.0001 | -0.0023 | 0.0008 | 0.0034 | 0.001 | -0.0006 | 0.0111 | -0.0083 | -0.0234 | -360.1034 | 17.3946 | -360.4327 | 17.6389 | -360.8389 | 18.142 | -360.7927 | 17.5712 | -352.5921 | 18.6799 | -352.6567 | 16.8423
12:38 | 4706 | 42.5347 | 202.4384 | 449.8721 | 456.7212 | -16.5202 | -40.5489 | 11.2045 | 8.1112 | 2.3609 | 0.6652 | 3.5647 | -0.949 | 11.707 | 4.4668 | 0.6181 | 0.6633 | 0.9601 | 0.7438 | -129.5394 | 0.1562 | 5.8222 | 1.7727 | -2.9402 | -1.1983 | 4.5349 |  | 3.2964 | 0.2166 | 4.0095 | 3.3643 | 3.3369 | 1.0795 | 10.7371 | 14.2683 | 14.8246 | 11.067 | 0 | -0.0023 | 0.0005 | 0.0035 | 0.0009 | -0.0004 | 0.0183 | -0.0192 | -0.0103 | -360.1742 | 17.3843 | -360.3742 | 17.6122 | -360.7958 | 18.1461 | -360.8235 | 17.6102 | -352.6136 | 18.6717 | -352.6044 | 16.8074
12:38 | 4707 | 42.5521 | 202.4677 | 449.861 | 456.7867 | -16.4918 | -40.5136 | 11.275 | 8.0337 | 2.2597 | 0.6245 | 3.4908 | -0.955 | 11.6989 | 4.5667 | 0.6183 | 0.6624 | 0.9607 | 0.7456 | -129.5704 | 0.1486 | 5.8001 | 1.8388 | -2.9245 | -1.1882 | 4.6317 |  | 3.3094 | 0.2446 | 4.0088 | 3.3662 | 3.3379 | 1.079 | 10.7636 | 14.2893 | 14.8356 | 11.093 | 0.0003 | -0.0029 | 0.001 | 0.0044 | 0.0009 | -0.0006 | 0.0201 | -0.0075 | -0.0259 | -360.1773 | 17.4254 | -360.4266 | 17.6328 | -360.7712 | 18.1173 | -360.7835 | 17.5835 | -352.6136 | 18.6984 | -352.6229 | 16.8299
12:38 | 4708 | 42.5661 | 202.4153 | 449.8804 | 456.7578 | -16.6478 | -40.626 | 11.0857 | 7.9676 | 2.2743 | 0.6732 | 3.5454 | -0.9067 | 11.7032 | 4.5989 | 0.6199 | 0.6625 | 0.9624 | 0.7444 | -129.5499 | 0.0399 | 5.7751 | 1.6489 | -3.0057 | -1.3584 | 4.4814 |  | 3.2807 | 0.129 | 4.0081 | 3.3631 | 3.3368 | 1.0793 | 10.7395 | 14.2413 | 14.801 | 11.0761 | 0.0001 | -0.0029 | 0.0007 | 0.0041 | 0.001 | -0.0005 | 0.0184 | -0.0147 | 0.0055 | -360.1096 | 17.3782 | -360.3927 | 17.643 | -360.8112 | 18.1522 | -360.8081 | 17.5753 | -352.5521 | 18.6717 | -352.6321 | 16.834
12:38 | 4709 | 42.5391 | 202.3574 | 449.7977 | 456.7337 | -16.6222 | -40.6332 | 11.2385 | 8.0049 | 2.2809 | 0.5926 | 3.4984 | -0.9748 | 11.7487 | 4.6005 | 0.6189 | 0.6607 | 0.9622 | 0.7458 | -129.529 | 0.1023 | 5.7945 | 1.6719 | -2.9649 | -1.3064 | 4.5932 |  | 3.2 | 0.2205 | 4.0084 | 3.363 | 3.3357 | 1.0803 | 10.7579 | 14.2429 | 14.8461 | 11.0529 | 0 | -0.0023 | 0.0006 | 0.0039 | 0.0008 | 0.0002 | 0.009 | -0.0081 | -0.0083 | -360.1742 | 17.3966 | -360.3896 | 17.602 | -360.7466 | 18.1173 | -360.7897 | 17.5958 | -352.626 | 18.682 | -352.6167 | 16.8074
12:38 | 4710 | 42.4589 | 202.3658 | 449.8513 | 456.7445 | -16.5873 | -40.6064 | 11.2516 | 7.9757 | 2.1747 | 0.6349 | 3.4452 | -1.0698 | 11.6988 | 4.6131 | 0.6199 | 0.6637 | 0.9619 | 0.7452 | -129.6014 | 0.0359 | 5.6961 | 1.5818 | -2.9758 | -1.4179 | 4.5573 |  | 3.2921 | 0.2921 | 4.008 | 3.3642 | 3.3401 | 1.0788 | 10.721 | 14.2112 | 14.817 | 11.0577 | -0.0012 | -0.003 | 0.0009 | 0.0039 | 0.001 | -0.0009 | 0.0208 | -0.0127 | -0.0009 | -360.1435 | 17.3946 | -360.445 | 17.6471 | -360.7927 | 18.1153 | -360.7773 | 17.5753 | -352.5706 | 18.6799 | -352.6475 | 16.8423
12:38 | 4711 | 42.5119 | 202.4174 | 449.8299 | 456.797 | -16.5227 | -40.5517 | 11.3353 | 7.9801 | 2.303 | 0.5888 | 3.4864 | -0.9587 | 11.7643 | 4.6475 | 0.619 | 0.6633 | 0.9606 | 0.7433 | -129.6247 | 0.0115 | 5.6859 | 1.6695 | -3.0003 | -1.2856 | 4.5779 |  | 3.3099 | 0.1705 | 4.0096 | 3.3619 | 3.3389 | 1.0797 | 10.7602 | 14.2569 | 14.8604 | 11.1186 | 0.0003 | -0.0031 | 0.0011 | 0.0037 | 0.0006 | -0.0001 | 0.0036 | -0.0077 | -0.0149 | -360.1158 | 17.3699 | -360.3896 | 17.6204 | -360.7835 | 18.142 | -360.8235 | 17.5876 | -352.5798 | 18.6573 | -352.5952 | 16.8279
12:38 | 4712 | 42.4167 | 202.4482 | 449.9836 | 456.8159 | -16.5925 | -40.7155 | 11.2651 | 8.0113 | 2.302 | 0.6663 | 3.5172 | -1.0208 | 11.6639 | 4.556 | 0.6176 | 0.6625 | 0.9658 | 0.7438 | -129.5842 | 0.0018 | 5.6012 | 1.6505 | -3.0249 | -1.343 | 4.586 |  | 3.2621 | 0.0634 | 4.0106 | 3.3638 | 3.3413 | 1.0796 | 10.7394 | 14.2649 | 14.8679 | 11.1038 | 0.0001 | -0.0032 | 0.0012 | 0.0039 | 0.0012 | -0.0007 | 0.0169 | 0.0028 | -0.0159 | -360.1342 | 17.4151 | -360.4173 | 17.6204 | -360.7835 | 18.1173 | -360.7773 | 17.5978 | -352.6475 | 18.7025 | -352.6352 | 16.8238
12:38 | 4713 | 42.4503 | 202.4455 | 449.9714 | 456.8486 | -16.5762 | -40.6659 | 11.2351 | 8.0692 | 2.324 | 0.6782 | 3.5988 | -1.1004 | 11.6531 | 4.5416 | 0.6176 | 0.6618 | 0.9601 | 0.7447 | -129.4498 | 0.0174 | 5.7747 | 1.8814 | -3.0385 | -1.2989 | 4.5439 |  | 3.2177 | 0.1397 | 4.0086 | 3.3605 | 3.3377 | 1.079 | 10.7222 | 14.2471 | 14.8299 | 11.0761 | -0.0006 | -0.0028 | 0.0006 | 0.0035 | 0.0007 | -0.0002 | 0.0093 | -0.0063 | -0.0064 | -360.1034 | 17.3843 | -360.4389 | 17.6348 | -360.8081 | 18.144 | -360.805 | 17.5671 | -352.5767 | 18.6737 | -352.6383 | 16.8464
12:38 | 4714 | 42.5376 | 202.3595 | 449.898 | 456.7326 | -16.5736 | -40.7497 | 11.2523 | 7.9809 | 2.2845 | 0.7827 | 3.4321 | -1.0347 | 11.7625 | 4.5718 | 0.6182 | 0.663 | 0.9615 | 0.7419 | -129.5868 | 0.0385 | 5.7816 | 1.8523 | -2.9669 | -1.3218 | 4.6197 |  | 3.214 | 0.223 | 4.0078 | 3.3657 | 3.3394 | 1.0782 | 10.7764 | 14.2904 | 14.8185 | 11.1175 | -0.0004 | -0.003 | 0.0001 | 0.0032 | 0.0012 | -0.0004 | -0.0036 | -0.0084 | -0.0199 | -360.1619 | 17.3843 | -360.405 | 17.6184 | -360.7835 | 18.142 | -360.8297 | 17.6081 | -352.626 | 18.6779 | -352.6075 | 16.834
12:38 | 4715 | 42.4835 | 202.36 | 449.8101 | 456.7313 | -16.5857 | -40.7441 | 11.3216 | 7.9268 | 2.2696 | 0.6196 | 3.4609 | -1.0853 | 11.7415 | 4.6139 | 0.6182 | 0.6616 | 0.9636 | 0.7426 | -129.5031 | 0.1125 | 5.7023 | 1.9093 | -2.9657 | -1.3315 | 4.5716 |  | 3.1987 | 0.1192 | 4.0091 | 3.3654 | 3.338 | 1.0784 | 10.766 | 14.2799 | 14.8709 | 11.0959 | -0.0001 | -0.0033 | 0.0009 | 0.004 | 0.0008 | -0.0003 | -0.0013 | 0 | -0.0309 | -360.1681 | 17.4069 | -360.4266 | 17.6307 | -360.802 | 18.1153 | -360.802 | 17.5999 | -352.626 | 18.7004 | -352.6229 | 16.8423
12:38 | 4716 | 42.3882 | 202.3782 | 449.8422 | 456.7504 | -16.6215 | -40.6902 | 11.3143 | 7.9975 | 2.252 | 0.6223 | 3.4704 | -0.9963 | 11.7885 | 4.6166 | 0.6185 | 0.661 | 0.9625 | 0.7441 | -129.5072 | 0.1811 | 5.782 | 1.9221 | -2.9882 | -1.2329 | 4.5575 |  | 3.2184 | 0.2527 | 4.0084 | 3.3648 | 3.3403 | 1.0786 | 10.7637 | 14.2834 | 14.8229 | 11.0991 | -0.0001 | -0.0029 | 0.0006 | 0.0045 | 0.001 | -0.0006 | 0.0058 | -0.0052 | -0.0147 | -360.1281 | 17.3905 | -360.4142 | 17.6451 | -360.8143 | 18.1584 | -360.8297 | 17.5896 | -352.6075 | 18.6779 | -352.626 | 16.8505
12:38 | 4717 | 42.4769 | 202.3607 | 449.9004 | 456.7772 | -16.5481 | -40.6125 | 11.4502 | 8.0401 | 2.233 | 0.6666 | 3.3209 | -1.1424 | 11.6742 | 4.5313 | 0.6186 | 0.66 | 0.9653 | 0.7435 | -129.4734 | 0.2355 | 5.7794 | 1.8422 | -2.9632 | -1.2941 | 4.5993 |  | 3.1904 | 0.2185 | 4.0088 | 3.3639 | 3.3364 | 1.0781 | 10.7578 | 14.2895 | 14.8482 | 11.1273 | -0.0002 | -0.0026 | 0.0007 | 0.004 | 0.0006 | -0.0004 | 0.0137 | -0.0014 | -0.0057 | -360.1927 | 17.4048 | -360.4327 | 17.6225 | -360.7527 | 18.1255 | -360.842 | 17.6061 | -352.6075 | 18.6943 | -352.6444 | 16.8197
12:38 | 4718 | 42.4501 | 202.3779 | 449.8343 | 456.8351 | -16.5315 | -40.6522 | 11.3219 | 8.0769 | 2.3064 | 0.6721 | 3.2376 | -1.1182 | 11.7772 | 4.5633 | 0.6188 | 0.6594 | 0.9625 | 0.7437 | -129.4835 | 0.1771 | 5.8014 | 1.8836 | -2.9108 | -1.3698 | 4.675 |  | 3.2799 | 0.1812 | 4.0089 | 3.3679 | 3.3364 | 1.0789 | 10.7798 | 14.2477 | 14.8689 | 11.0803 | -0.0004 | -0.0026 | 0.0007 | 0.0041 | 0.0007 | -0.0005 | 0.0115 | -0.0016 | 0.0085 | -360.165 | 17.4131 | -360.4666 | 17.6553 | -360.842 | 18.1276 | -360.7897 | 17.5896 | -352.6352 | 18.7004 | -352.6537 | 16.8546
12:38 | 4719 | 42.4515 | 202.3686 | 449.9075 | 456.7265 | -16.6331 | -40.7008 | 11.2201 | 8.0684 | 2.4564 | 0.5988 | 3.2945 | -1.1511 | 11.7355 | 4.6188 | 0.6189 | 0.6614 | 0.9614 | 0.7417 | -129.5159 | 0.1631 | 5.7686 | 1.9805 | -2.8518 | -1.3321 | 4.6719 |  | 3.2442 | 0.1474 | 4.008 | 3.3665 | 3.3369 | 1.0785 | 10.7601 | 14.2628 | 14.8673 | 11.1183 | 0.0003 | -0.0032 | 0.0007 | 0.0036 | 0.0008 | -0.0004 | 0.0041 | -0.0069 | -0.0037 | -360.1742 | 17.3843 | -360.3989 | 17.6389 | -360.8174 | 18.1625 | -360.8512 | 17.602 | -352.6075 | 18.6696 | -352.6167 | 16.8381
12:38 | 4720 | 42.4773 | 202.3941 | 449.8832 | 456.7725 | -16.6652 | -40.6547 | 11.2545 | 8.1279 | 2.365 | 0.6832 | 3.2929 | -1.0864 | 11.7348 | 4.6088 | 0.6183 | 0.6562 | 0.9602 | 0.7429 | -129.4358 | 0.1492 | 5.7002 | 1.9357 | -2.8992 | -1.1996 | 4.6544 |  | 3.2301 | 0.2479 | 4.0096 | 3.3658 | 3.3363 | 1.0785 | 10.7718 | 14.28 | 14.8488 | 11.1129 | -0.0001 | -0.0032 | 0.0008 | 0.0036 | 0.0001 | -0.0008 | 0.0034 | -0.0013 | -0.0249 | -360.2142 | 17.4233 | -360.4635 | 17.6307 | -360.7958 | 18.1296 | -360.8512 | 17.6081 | -352.6598 | 18.7271 | -352.6444 | 16.8402
12:38 | 4721 | 42.5255 | 202.3713 | 449.8497 | 456.6867 | -16.5071 | -40.5439 | 11.363 | 7.9996 | 2.4254 | 0.5759 | 3.2804 | -1.14 | 11.7646 | 4.6788 | 0.6191 | 0.6618 | 0.9628 | 0.7451 | -129.58 | 0.0638 | 5.7214 | 1.9597 | -2.8367 | -1.2323 | 4.6174 |  | 3.267 | 0.2298 | 4.0089 | 3.3629 | 3.3353 | 1.0778 | 10.773 | 14.281 | 14.8491 | 11.0739 | -0.0004 | -0.0026 | 0.001 | 0.0039 | 0.0011 | -0.0003 | 0.0135 | -0.0174 | -0.0162 | -360.1527 | 17.3966 | -360.4512 | 17.6512 | -360.845 | 18.1481 | -360.8574 | 17.5937 | -352.5983 | 18.682 | -352.6506 | 16.8546
12:38 | 4722 | 42.5732 | 202.301 | 449.9054 | 456.6888 | -16.4829 | -40.4709 | 11.5204 | 8.0012 | 2.423 | 0.6182 | 3.3442 | -1.1749 | 11.6862 | 4.5761 | 0.6173 | 0.6611 | 0.9613 | 0.7445 | -129.6072 | 0.1101 | 5.7233 | 1.9803 | -2.9274 | -1.2193 | 4.5733 |  | 3.3248 | 0.162 | 4.0081 | 3.3661 | 3.3363 | 1.0786 | 10.7648 | 14.2673 | 14.859 | 11.106 | -0.0004 | -0.0027 | 0.0007 | 0.0038 | 0.0009 | -0.0003 | 0.0133 | -0.0082 | -0.0248 | -360.165 | 17.3987 | -360.4235 | 17.6286 | -360.802 | 18.1502 | -360.8727 | 17.6225 | -352.6352 | 18.6758 | -352.6444 | 16.8361
12:38 | 4723 | 42.4394 | 202.362 | 449.8657 | 456.7326 | -16.5081 | -40.4941 | 11.4341 | 8.0826 | 2.4043 | 0.7716 | 3.3026 | -1.1752 | 11.7326 | 4.6019 | 0.6169 | 0.6655 | 0.9589 | 0.7436 | -129.5471 | 0.0818 | 5.7572 | 1.9381 | -3.0202 | -1.2621 | 4.5708 |  | 3.2194 | 0.0965 | 4.009 | 3.3646 | 3.3375 | 1.0787 | 10.766 | 14.2916 | 14.8836 | 11.0666 | 0 | -0.0029 | 0.0009 | 0.0044 | 0.001 | -0.0006 | 0.0088 | -0.0118 | -0.0049 | -360.1773 | 17.4233 | -360.4789 | 17.6245 | -360.8204 | 18.1255 | -360.8143 | 17.5978 | -352.6629 | 18.7087 | -352.6906 | 16.8361
12:38 | 4724 | 42.4994 | 202.3831 | 449.9004 | 456.722 | -16.4796 | -40.5426 | 11.3826 | 8.1547 | 2.496 | 0.8178 | 3.3763 | -0.997 | 11.7082 | 4.6137 | 0.6182 | 0.6591 | 0.9627 | 0.742 | -129.5755 | 0.1865 | 5.7113 | 1.997 | -2.995 | -1.1987 | 4.5709 |  | 3.3576 | 0.1807 | 4.0087 | 3.3667 | 3.3392 | 1.0786 | 10.7314 | 14.2624 | 14.8525 | 11.102 | 0.0001 | -0.0033 | 0.001 | 0.0043 | 0.0006 | -0.0004 | -0.0045 | -0.0153 | -0.0024 | -360.1127 | 17.3802 | -360.4235 | 17.6286 | -360.8235 | 18.1543 | -360.842 | 17.5855 | -352.5829 | 18.6779 | -352.6506 | 16.8443
12:38 | 4725 | 42.5331 | 202.3848 | 449.9475 | 456.7175 | -16.4026 | -40.5101 | 11.3911 | 8.0591 | 2.3967 | 0.7215 | 3.2907 | -1.0488 | 11.8357 | 4.6841 | 0.6177 | 0.6619 | 0.9633 | 0.744 | -129.583 | 0.189 | 5.6476 | 1.8764 | -2.9398 | -1.2148 | 4.6143 |  | 3.2913 | 0.248 | 4.008 | 3.3655 | 3.3383 | 1.0782 | 10.7534 | 14.2612 | 14.8453 | 11.1125 | -0.0002 | -0.003 | 0.0007 | 0.004 | 0.0009 | -0.0009 | 0.0026 | -0.0098 | -0.0066 | -360.1773 | 17.409 | -360.3958 | 17.5958 | -360.765 | 18.1296 | -360.8297 | 17.6328 | -352.6629 | 18.6922 | -352.6229 | 16.8094
12:38 | 4726 | 42.6128 | 202.357 | 449.7931 | 456.6729 | -16.4275 | -40.5242 | 11.406 | 8.0474 | 2.3512 | 0.7243 | 3.2328 | -1.0658 | 11.7929 | 4.6599 | 0.6182 | 0.6637 | 0.9625 | 0.7452 | -129.5139 | 0.0979 | 5.6155 | 1.8569 | -2.9576 | -1.2899 | 4.6678 |  | 3.2235 | 0.1965 | 4.0071 | 3.3658 | 3.3342 | 1.0781 | 10.7729 | 14.287 | 14.8965 | 11.1024 | 0.0001 | -0.0025 | 0.0013 | 0.004 | 0.0008 | -0.0001 | 0.0074 | -0.0014 | -0.014 | -360.1711 | 17.4131 | -360.485 | 17.6369 | -360.7989 | 18.1255 | -360.802 | 17.5917 | -352.6475 | 18.7148 | -352.6967 | 16.8505
12:38 | 4727 | 42.5141 | 202.3482 | 449.8023 | 456.7041 | -16.4723 | -40.5707 | 11.3729 | 8.0817 | 2.3027 | 0.8226 | 3.2148 | -1.0815 | 11.7711 | 4.6374 | 0.6186 | 0.6624 | 0.9617 | 0.7444 | -129.632 | 0.1485 | 5.6535 | 1.8549 | -2.9866 | -1.2307 | 4.7073 |  | 3.26 | 0.1916 | 4.0069 | 3.3664 | 3.337 | 1.0787 | 10.7568 | 14.2707 | 14.8563 | 11.0923 | 0.0001 | -0.0028 | 0.0008 | 0.0035 | 0.0009 | -0.0007 | 0.0032 | -0.0057 | -0.021 | -360.1988 | 17.3802 | -360.3927 | 17.6184 | -360.8327 | 18.1769 | -360.8635 | 17.6081 | -352.6506 | 18.684 | -352.6075 | 16.8402
12:39 | 4728 | 42.5601 | 202.2814 | 449.9677 | 456.6484 | -16.4766 | -40.6001 | 11.4592 | 8.0918 | 2.2532 | 0.7083 | 3.2461 | -1.0765 | 11.7891 | 4.6345 | 0.618 | 0.6611 | 0.964 | 0.7428 | -129.5824 | 0.1843 | 5.6938 | 1.8993 | -3.0186 | -1.2019 | 4.628 |  | 3.2567 | 0.1876 | 4.0067 | 3.3608 | 3.3355 | 1.0782 | 10.7579 | 14.2718 | 14.8577 | 11.1107 | 0.0006 | -0.0026 | 0.0006 | 0.0035 | 0.0008 | -0.0003 | 0.0199 | -0.0146 | -0.003 | -360.2173 | 17.4377 | -360.4789 | 17.6184 | -360.7866 | 18.1358 | -360.8266 | 17.6328 | -352.6721 | 18.7251 | -352.6537 | 16.832
12:39 | 4729 | 42.6534 | 202.3342 | 449.8808 | 456.6674 | -16.4791 | -40.5278 | 11.397 | 8.0621 | 2.2924 | 0.7152 | 3.3506 | -1.1072 | 11.7809 | 4.6404 | 0.6188 | 0.6616 | 0.9627 | 0.745 | -129.6208 | 0.1776 | 5.6894 | 1.9054 | -3.0336 | -1.2367 | 4.6532 |  | 3.2708 | 0.1828 | 4.0067 | 3.3612 | 3.3388 | 1.0771 | 10.7498 | 14.2463 | 14.8433 | 11.0796 | -0.0003 | -0.0029 | 0.0006 | 0.004 | 0.0003 | -0.0005 | 0.0198 | -0.0016 | -0.0111 | -360.1711 | 17.4192 | -360.4942 | 17.6574 | -360.8727 | 18.1769 | -360.8297 | 17.5937 | -352.626 | 18.6984 | -352.6998 | 16.871
12:39 | 4730 | 42.5707 | 202.4201 | 449.8924 | 456.6748 | -16.5107 | -40.4866 | 11.441 | 8.1384 | 2.2541 | 0.7552 | 3.3679 | -1.0589 | 11.8206 | 4.5297 | 0.6187 | 0.6589 | 0.9627 | 0.7422 | -129.5403 | 0.1046 | 5.6758 | 1.9638 | -3.0223 | -1.1522 | 4.599 |  | 3.3824 | 0.1918 | 4.0087 | 3.3612 | 3.3369 | 1.08 | 10.7301 | 14.273 | 14.8359 | 11.106 | -0.0001 | -0.0023 | 0.0006 | 0.0036 | 0.0006 | -0.0009 | 0.0181 | -0.0077 | -0.0203 | -360.2111 | 17.4069 | -360.4112 | 17.6122 | -360.8112 | 18.1953 | -360.8943 | 17.6389 | -352.669 | 18.6861 | -352.6167 | 16.8279
12:39 | 4731 | 42.5111 | 202.2898 | 449.864 | 456.6479 | -16.4522 | -40.5109 | 11.4635 | 8.1198 | 2.2025 | 0.5474 | 3.2639 | -1.0871 | 11.8188 | 4.6012 | 0.6182 | 0.6621 | 0.9625 | 0.7439 | -129.56 | 0.2083 | 5.724 | 1.9183 | -3.0245 | -1.1714 | 4.6517 |  | 3.2295 | 0.2254 | 4.008 | 3.366 | 3.3367 | 1.0788 | 10.7705 | 14.2907 | 14.8554 | 11.1052 | 0.0002 | -0.0028 | 0.0013 | 0.0047 | 0.0006 | -0.0004 | 0.0184 | -0.0072 | -0.0287 | -360.2327 | 17.4521 | -360.5127 | 17.6389 | -360.8327 | 18.1481 | -360.8112 | 17.6204 | -352.666 | 18.7374 | -352.6906 | 16.8402
12:39 | 4732 | 42.5357 | 202.3844 | 449.9433 | 456.7584 | -16.5279 | -40.5579 | 11.5358 | 8.1702 | 2.2603 | 0.7037 | 3.3351 | -1.1148 | 11.7383 | 4.6038 | 0.6175 | 0.6587 | 0.9636 | 0.7436 | -129.5386 | 0.1874 | 5.7256 | 1.9137 | -3.0253 | -1.1591 | 4.6141 |  | 3.2987 | 0.2324 | 4.009 | 3.3638 | 3.3359 | 1.0788 | 10.7695 | 14.2892 | 14.8577 | 11.0876 | 0.0001 | -0.003 | 0.0006 | 0.0042 | 0.0009 | -0.0008 | 0.0073 | 0.0023 | -0.0192 | -360.1496 | 17.4048 | -360.4666 | 17.6471 | -360.882 | 18.1994 | -360.8697 | 17.6061 | -352.5983 | 18.6881 | -352.666 | 16.8546
12:39 | 4733 | 42.6492 | 202.4696 | 449.9039 | 456.8609 | -16.4947 | -40.5288 | 11.5169 | 8.192 | 2.3668 | 0.6053 | 3.3519 | -0.9972 | 11.7861 | 4.6288 | 0.6184 | 0.6631 | 0.9613 | 0.7436 | -129.5225 | 0.2176 | 5.7219 | 1.944 | -3.0356 | -1.087 | 4.6196 |  | 3.3132 | 0.1359 | 4.0088 | 3.3667 | 3.3392 | 1.0805 | 10.7776 | 14.2624 | 14.8293 | 11.0616 | -0.0001 | -0.003 | 0.0006 | 0.0033 | 0.0006 | -0.0002 | -0.0019 | -0.0058 | -0.007 | -360.2296 | 17.4151 | -360.4542 | 17.6163 | -360.7958 | 18.1728 | -360.8789 | 17.641 | -352.6967 | 18.7107 | -352.6537 | 16.8115
12:39 | 4734 | 42.6577 | 202.464 | 449.9444 | 456.8446 | -16.41 | -40.5706 | 11.4697 | 8.1979 | 2.4199 | 0.6926 | 3.3117 | -1.001 | 11.7903 | 4.662 | 0.6189 | 0.6617 | 0.9624 | 0.7435 | -129.5993 | 0.1842 | 5.7188 | 1.9829 | -3.0035 | -1.2336 | 4.5723 |  | 3.296 | 0.1771 | 4.0078 | 3.3647 | 3.3378 | 1.0791 | 10.7407 | 14.2772 | 14.8371 | 11.0656 | -0.0008 | -0.0028 | 0.0008 | 0.0037 | 0.0009 | -0.0007 | 0.0031 | -0.0082 | -0.0091 | -360.1865 | 17.4418 | -360.525 | 17.643 | -360.8358 | 18.1502 | -360.805 | 17.5794 | -352.6567 | 18.7292 | -352.6906 | 16.8505
12:39 | 4735 | 42.6868 | 202.4862 | 449.9776 | 456.8011 | -16.5127 | -40.5099 | 11.3221 | 8.1034 | 2.2579 | 0.6227 | 3.3626 | -0.977 | 11.8659 | 4.6494 | 0.6163 | 0.6617 | 0.9602 | 0.7427 | -129.5929 | 0.2498 | 5.6962 | 1.9033 | -2.9758 | -1.211 | 4.5892 |  | 3.3171 | 0.1388 | 4.0077 | 3.3697 | 3.3336 | 1.0795 | 10.7695 | 14.2892 | 14.8577 | 11.0876 | -0.0002 | -0.0027 | 0.0003 | 0.0033 | 0.0003 | -0.0004 | 0.005 | -0.007 | -0.0076 | -360.1465 | 17.3884 | -360.4266 | 17.6307 | -360.8512 | 18.1851 | -360.8481 | 17.5958 | -352.6167 | 18.6737 | -352.6136 | 16.8402
12:39 | 4736 | 42.5934 | 202.3858 | 450.047 | 456.7782 | -16.4822 | -40.4056 | 11.5112 | 8.1197 | 2.2912 | 0.6256 | 3.3374 | -1.0093 | 11.8794 | 4.6826 | 0.6177 | 0.6591 | 0.9601 | 0.7428 | -129.579 | 0.2736 | 5.8024 | 1.8665 | -2.8928 | -1.1968 | 4.7207 |  | 3.3106 | 0.1391 | 4.0085 | 3.3687 | 3.3382 | 1.0795 | 10.751 | 14.2705 | 14.8436 | 11.0984 | -0.0002 | -0.0034 | 0.0004 | 0.0034 | 0.001 | -0.0006 | 0.0057 | -0.0111 | -0.0058 | -360.1958 | 17.4233 | -360.4204 | 17.6102 | -360.7866 | 18.1687 | -360.8604 | 17.6163 | -352.6444 | 18.6943 | -352.6167 | 16.8115
12:39 | 4737 | 42.6441 | 202.4898 | 450.1026 | 456.8212 | -16.5029 | -40.4062 | 11.4977 | 8.1278 | 2.3332 | 0.6091 | 3.222 | -0.9879 | 11.9193 | 4.713 | 0.6187 | 0.6631 | 0.9625 | 0.7431 | -129.4901 | 0.2122 | 5.7788 | 1.7215 | -2.9522 | -1.1765 | 4.644 |  | 3.3519 | 0.1511 | 4.0082 | 3.3732 | 3.3345 | 1.0805 | 10.7487 | 14.2625 | 14.8478 | 11.1074 | -0.0002 | -0.0032 | 0.0006 | 0.004 | 0.0006 | -0.0002 | 0.0166 | 0.0028 | -0.0039 | -360.205 | 17.4356 | -360.4789 | 17.6512 | -360.8358 | 18.1317 | -360.7927 | 17.565 | -352.6136 | 18.7128 | -352.6967 | 16.8484
12:39 | 4738 | 42.643 | 202.4874 | 449.9917 | 456.8339 | -16.5247 | -40.4319 | 11.4211 | 8.0701 | 2.2508 | 0.5507 | 3.1991 | -0.9533 | 11.9847 | 4.7269 | 0.619 | 0.6618 | 0.959 | 0.7418 | -129.5014 | 0.195 | 5.7265 | 1.8485 | -2.9797 | -1.2263 | 4.6716 |  | 3.3814 | 0.34 | 4.0084 | 3.3684 | 3.3351 | 1.0796 | 10.7613 | 14.2756 | 14.857 | 11.0731 | -0.0002 | -0.0028 | 0.0008 | 0.004 | 0.0013 | -0.0005 | -0.0049 | -0.0051 | -0.0055 | -360.1465 | 17.3905 | -360.4266 | 17.6266 | -360.8543 | 18.1912 | -360.8635 | 17.5917 | -352.6198 | 18.6696 | -352.626 | 16.834
12:39 | 4739 | 42.6492 | 202.3956 | 449.8906 | 456.8885 | -16.4789 | -40.4308 | 11.4381 | 7.9834 | 2.2608 | 0.5048 | 3.1603 | -0.9182 | 11.9328 | 4.622 | 0.6193 | 0.6652 | 0.9598 | 0.7435 | -129.5525 | 0.1641 | 5.7472 | 1.6658 | -2.9553 | -1.2055 | 4.5903 |  | 3.3498 | 0.3638 | 4.0088 | 3.3692 | 3.3385 | 1.0797 | 10.781 | 14.3183 | 14.8703 | 11.1219 | -0.0006 | -0.0028 | 0.0007 | 0.0041 | 0.0006 | -0.0004 | 0.0116 | -0.0043 | -0.0121 | -360.2081 | 17.4254 | -360.4204 | 17.602 | -360.7712 | 18.1399 | -360.8574 | 17.6163 | -352.666 | 18.7045 | -352.6198 | 16.8032
12:39 | 4740 | 42.5932 | 202.4275 | 449.8341 | 456.7496 | -16.5083 | -40.4057 | 11.3004 | 7.9851 | 2.2758 | 0.4973 | 3.2242 | -0.9149 | 11.8823 | 4.7081 | 0.6177 | 0.6606 | 0.9611 | 0.7432 | -129.538 | 0.1007 | 5.6708 | 1.7896 | -2.8784 | -1.1648 | 4.6414 |  | 3.2994 | 0.284 | 4.009 | 3.368 | 3.3367 | 1.0802 | 10.789 | 14.2803 | 14.8857 | 11.1005 | 0.0005 | -0.0028 | 0.0009 | 0.0043 | 0.0004 | -0.0005 | 0.0026 | -0.007 | -0.0066 | -360.1465 | 17.4192 | -360.4912 | 17.6533 | -360.8389 | 18.1296 | -360.7773 | 17.5588 | -352.5829 | 18.7066 | -352.6721 | 16.8464
12:39 | 4741 | 42.6049 | 202.3948 | 449.7868 | 456.75 | -16.5193 | -40.3668 | 11.2886 | 7.9816 | 2.3706 | 0.5683 | 3.2864 | -0.8588 | 11.8229 | 4.7089 | 0.6185 | 0.663 | 0.9603 | 0.7426 | -129.6333 | 0.0555 | 5.6345 | 1.8816 | -2.8982 | -1.2098 | 4.6457 |  | 3.2758 | 0.2238 | 4.0085 | 3.3666 | 3.3387 | 1.0806 | 10.7753 | 14.2833 | 14.8277 | 11.1226 | -0.0004 | -0.0034 | 0.0008 | 0.0036 | 0.0009 | -0.0007 | 0.0092 | -0.0143 | -0.0014 | -360.1588 | 17.374 | -360.3989 | 17.6102 | -360.8235 | 18.1728 | -360.8389 | 17.5835 | -352.6013 | 18.6758 | -352.5829 | 16.8115
12:39 | 4742 | 42.582 | 202.3883 | 449.7863 | 456.8079 | -16.443 | -40.3622 | 11.3906 | 7.9953 | 2.4153 | 0.7308 | 3.272 | -0.8891 | 11.794 | 4.7352 | 0.6169 | 0.6602 | 0.957 | 0.7447 | -129.6391 | 0.1757 | 5.6773 | 1.9585 | -2.8902 | -1.1649 | 4.6564 |  | 3.2725 | 0.2538 | 4.0077 | 3.3635 | 3.335 | 1.0789 | 10.7637 | 14.2661 | 14.8403 | 11.0876 | -0.0001 | -0.0026 | 0.0009 | 0.0039 | 0.0008 | -0.0002 | 0.0044 | -0.0173 | 0.0065 | -360.1527 | 17.411 | -360.4266 | 17.5876 | -360.7158 | 18.1235 | -360.805 | 17.5876 | -352.6044 | 18.7066 | -352.5952 | 16.7889
12:39 | 4743 | 42.621 | 202.4527 | 449.8029 | 456.7878 | -16.4845 | -40.3015 | 11.3046 | 8.0331 | 2.4348 | 0.714 | 3.2696 | -0.8593 | 11.8551 | 4.7401 | 0.6176 | 0.6614 | 0.9606 | 0.7437 | -129.5971 | 0.1951 | 5.714 | 1.9263 | -2.914 | -1.0977 | 4.6397 |  | 3.2976 | 0.2422 | 4.0094 | 3.3652 | 3.3342 | 1.0795 | 10.7487 | 14.2508 | 14.8467 | 11.0789 | 0 | -0.0027 | 0.0012 | 0.0041 | 0.0006 | -0.0007 | 0.0097 | -0.0039 | -0.0193 | -360.1096 | 17.4069 | -360.4635 | 17.6369 | -360.8327 | 18.1337 | -360.7681 | 17.5424 | -352.5829 | 18.6902 | -352.6598 | 16.8484
12:39 | 4744 | 42.4949 | 202.4275 | 449.7496 | 456.8163 | -16.4074 | -40.3972 | 11.3943 | 8.0607 | 2.3668 | 0.6457 | 3.2869 | -0.8725 | 11.9276 | 4.7564 | 0.6187 | 0.6635 | 0.9644 | 0.7449 | -129.5697 | 0.2055 | 5.7018 | 1.757 | -2.821 | -1.0819 | 4.6467 |  | 3.2957 | 0.0896 | 4.0082 | 3.3653 | 3.3322 | 1.0793 | 10.7441 | 14.2578 | 14.8596 | 11.0916 | 0.0002 | -0.0031 | 0.0008 | 0.0037 | 0.0007 | -0.0004 | 0.0105 | -0.0204 | -0.0044 | -360.0973 | 17.3699 | -360.3558 | 17.5896 | -360.7681 | 18.1604 | -360.8389 | 17.5814 | -352.586 | 18.6655 | -352.5767 | 16.8094
12:39 | 4745 | 42.6425 | 202.4354 | 449.7688 | 456.806 | -16.5007 | -40.4051 | 11.3926 | 7.9696 | 2.4486 | 0.7546 | 3.2388 | -0.8264 | 11.9229 | 4.6845 | 0.6185 | 0.6634 | 0.96 | 0.7422 | -129.5509 | 0.2043 | 5.7368 | 1.8489 | -2.8399 | -1.0839 | 4.6373 |  | 3.3347 | 0.1899 | 4.0069 | 3.3687 | 3.338 | 1.0792 | 10.7498 | 14.2579 | 14.8491 | 11.1085 | 0.0004 | -0.003 | 0.0005 | 0.0042 | 0.0012 | -0.0006 | 0.0148 | 0.0072 | -0.0009 | -360.165 | 17.4131 | -360.4327 | 17.5937 | -360.7466 | 18.1173 | -360.7897 | 17.5835 | -352.629 | 18.7169 | -352.629 | 16.8053
12:39 | 4746 | 42.6081 | 202.4501 | 449.7483 | 456.7843 | -16.396 | -40.4402 | 11.3664 | 7.9975 | 2.3628 | 0.6516 | 3.3405 | -0.9163 | 11.922 | 4.704 | 0.6185 | 0.666 | 0.961 | 0.7446 | -129.4964 | 0.3216 | 5.6886 | 1.8251 | -2.8664 | -1.2259 | 4.5764 |  | 3.3452 | 0.131 | 4.0089 | 3.3663 | 3.3357 | 1.0808 | 10.7706 | 14.2616 | 14.8485 | 11.1056 | -0.0001 | -0.0027 | 0.0009 | 0.0041 | 0.0006 | 0 | -0.0033 | -0.0113 | -0.0193 | -360.0819 | 17.3905 | -360.4296 | 17.6389 | -360.8112 | 18.1625 | -360.7773 | 17.5547 | -352.5521 | 18.684 | -352.6321 | 16.8484
12:39 | 4747 | 42.578 | 202.5276 | 449.8541 | 456.7768 | -16.3182 | -40.3543 | 11.3275 | 7.9749 | 2.3256 | 0.6238 | 3.3372 | -0.9451 | 11.9156 | 4.6884 | 0.618 | 0.6643 | 0.9618 | 0.745 | -129.4987 | 0.2752 | 5.6942 | 1.7779 | -2.8688 | -1.2348 | 4.5577 |  | 3.3501 | 0.1472 | 4.01 | 3.3666 | 3.3372 | 1.0797 | 10.7474 | 14.2674 | 14.8543 | 11.0941 | -0.0001 | -0.0025 | 0.0003 | 0.0037 | 0.0012 | -0.0005 | 0.009 | -0.024 | -0.0065 | -360.1496 | 17.3802 | -360.3712 | 17.5876 | -360.762 | 18.1543 | -360.8266 | 17.6081 | -352.6106 | 18.6779 | -352.5736 | 16.8012
12:39 | 4748 | 42.702 | 202.4776 | 449.9329 | 456.8009 | -16.3743 | -40.2289 | 11.3506 | 8.075 | 2.3823 | 0.6994 | 3.2898 | -0.9584 | 11.8707 | 4.6377 | 0.6182 | 0.6617 | 0.9645 | 0.7459 | -129.5752 | 0.2404 | 5.6832 | 1.6725 | -2.8876 | -1.3056 | 4.6057 |  | 3.3134 | 0.1666 | 4.0099 | 3.3658 | 3.3333 | 1.0818 | 10.7754 | 14.2658 | 14.8497 | 11.0768 | 0.0001 | -0.0029 | 0.0006 | 0.0036 | 0.0001 | -0.0002 | 0.0233 | 0.0092 | -0.0152 | -360.1896 | 17.4233 | -360.4604 | 17.6184 | -360.7743 | 18.1235 | -360.7866 | 17.5814 | -352.6506 | 18.7251 | -352.669 | 16.8381
12:39 | 4749 | 42.6808 | 202.4944 | 449.9322 | 456.8102 | -16.4626 | -40.2257 | 11.3513 | 8.1326 | 2.372 | 0.626 | 3.2911 | -0.9867 | 11.8769 | 4.6636 | 0.6162 | 0.6616 | 0.9624 | 0.7447 | -129.4509 | 0.2129 | 5.7224 | 1.6442 | -2.8624 | -1.2043 | 4.643 |  | 3.2743 | 0.2207 | 4.0097 | 3.3672 | 3.3388 | 1.08 | 10.7776 | 14.2799 | 14.8362 | 11.0786 | 0.0003 | -0.003 | 0.0007 | 0.0031 | 0.0008 | -0.0006 | 0.0185 | 0.0059 | -0.0013 | -360.0819 | 17.3823 | -360.4419 | 17.6286 | -360.8389 | 18.1707 | -360.8297 | 17.5568 | -352.5613 | 18.684 | -352.6229 | 16.8607
12:39 | 4750 | 42.6517 | 202.4649 | 449.9332 | 456.8273 | -16.574 | -40.3522 | 11.4016 | 8.1145 | 2.3773 | 0.6701 | 3.3543 | -0.9494 | 11.8683 | 4.6428 | 0.6177 | 0.6632 | 0.9631 | 0.7444 | -129.4474 | 0.2032 | 5.7854 | 1.7015 | -2.9137 | -1.2714 | 4.5948 |  | 3.2344 | 0.1913 | 4.0097 | 3.3643 | 3.3372 | 1.0804 | 10.7625 | 14.2707 | 14.8042 | 11.0692 | -0.0002 | -0.0027 | 0.0013 | 0.0039 | 0.0008 | 0 | 0.0166 | -0.015 | -0.0096 | -360.1711 | 17.3987 | -360.4358 | 17.602 | -360.7712 | 18.1522 | -360.882 | 17.6184 | -352.6537 | 18.7107 | -352.6044 | 16.8217
12:39 | 4751 | 42.6085 | 202.4057 | 449.8037 | 456.8199 | -16.605 | -40.337 | 11.2358 | 8.0861 | 2.4054 | 0.6392 | 3.3626 | -0.9712 | 11.8677 | 4.7249 | 0.6178 | 0.6609 | 0.961 | 0.745 | -129.5296 | 0.1739 | 5.702 | 1.6809 | -2.8263 | -1.2451 | 4.5798 |  | 3.3051 | 0.1881 | 4.0089 | 3.363 | 3.3349 | 1.0785 | 10.7742 | 14.2647 | 14.8668 | 11.0927 | -0.0003 | -0.0027 | 0.0011 | 0.0039 | 0.0007 | -0.0007 | 0.0077 | 0.0045 | 0.0079 | -360.1835 | 17.4233 | -360.4666 | 17.6492 | -360.8235 | 18.1358 | -360.7866 | 17.5732 | -352.6413 | 18.723 | -352.6967 | 16.8607
12:39 | 4752 | 42.6592 | 202.4501 | 449.7237 | 456.7792 | -16.4985 | -40.3465 | 11.3247 | 8.0885 | 2.458 | 0.6424 | 3.3619 | -0.8385 | 11.9093 | 4.7043 | 0.6192 | 0.6626 | 0.9605 | 0.7448 | -129.4679 | 0.3528 | 5.7553 | 1.6808 | -2.8337 | -1.2394 | 4.5712 |  | 3.3856 | 0.2152 | 4.0094 | 3.3675 | 3.3383 | 1.0783 | 10.7867 | 14.3011 | 14.8482 | 11.0984 | 0.0007 | -0.0024 | 0.0009 | 0.0039 | 0.0007 | -0.0004 | 0.0213 | -0.004 | 0.0183 | -360.1496 | 17.3905 | -360.4358 | 17.6451 | -360.8604 | 18.1933 | -360.8512 | 17.5958 | -352.6352 | 18.6943 | -352.6475 | 16.8628
12:39 | 4753 | 42.7743 | 202.4819 | 449.8601 | 456.8794 | -16.5138 | -40.3644 | 11.2958 | 8.0244 | 2.4244 | 0.6049 | 3.323 | -0.9795 | 11.7864 | 4.6133 | 0.6206 | 0.6626 | 0.9649 | 0.7439 | -129.446 | 0.3239 | 5.8436 | 1.8348 | -2.8411 | -1.3049 | 4.5242 |  | 3.4205 | 0.2454 | 4.009 | 3.3665 | 3.3392 | 1.0799 | 10.7672 | 14.2635 | 14.8886 | 11.1031 | 0 | -0.0032 | 0.0009 | 0.0047 | 0.0006 | -0.0006 | 0.0242 | -0.0119 | 0.0104 | -360.2419 | 17.4356 | -360.4604 | 17.6184 | -360.7927 | 18.1461 | -360.8697 | 17.6163 | -352.6844 | 18.7374 | -352.6844 | 16.8299
12:39 | 4754 | 42.6931 | 202.4658 | 449.8431 | 456.8271 | -16.5034 | -40.3541 | 11.2733 | 7.984 | 2.4059 | 0.6744 | 3.3441 | -0.9211 | 11.7592 | 4.6186 | 0.6201 | 0.6615 | 0.9638 | 0.7436 | -129.4198 | 0.4104 | 5.8329 | 1.7962 | -2.7525 | -1.2041 | 4.5253 |  | 3.3807 | 0.2139 | 4.0086 | 3.3658 | 3.3394 | 1.0802 | 10.7462 | 14.2779 | 14.8714 | 11.0926 | 0 | -0.0028 | 0.0012 | 0.0043 | 0.0008 | -0.0008 | 0.0217 | -0.0075 | 0.0208 | -360.1711 | 17.4295 | -360.5219 | 17.6594 | -360.8635 | 18.1604 | -360.8297 | 17.5917 | -352.6198 | 18.7292 | -352.7213 | 16.8772
12:39 | 4755 | 42.7017 | 202.4042 | 449.7992 | 456.7768 | -16.4529 | -40.3148 | 11.2978 | 7.9782 | 2.3999 | 0.5625 | 3.2684 | -0.9178 | 11.8377 | 4.6549 | 0.6199 | 0.6628 | 0.9619 | 0.7447 | -129.4976 | 0.4078 | 5.8386 | 1.7662 | -2.7441 | -1.2905 | 4.5522 |  | 3.3467 | 0.214 | 4.0092 | 3.3683 | 3.3394 | 1.0796 | 10.7602 | 14.2567 | 14.8535 | 11.1074 | -0.0005 | -0.0027 | -0.0001 | 0.0036 | 0.0008 | -0.0002 | 0.0158 | 0.003 | 0 | -360.1742 | 17.4007 | -360.445 | 17.641 | -360.845 | 18.1892 | -360.9066 | 17.6143 | -352.626 | 18.7045 | -352.629 | 16.8464
12:39 | 4756 | 42.6433 | 202.4474 | 449.9207 | 456.7932 | -16.5771 | -40.3744 | 11.3171 | 7.9967 | 2.4111 | 0.5128 | 3.353 | -0.8872 | 11.9411 | 4.7578 | 0.6194 | 0.6641 | 0.9615 | 0.7452 | -129.4628 | 0.3121 | 5.7961 | 1.8128 | -2.8134 | -1.298 | 4.449 |  | 3.2768 | 0.2128 | 4.0075 | 3.3677 | 3.3426 | 1.0798 | 10.7673 | 14.2401 | 14.8228 | 11.075 | -0.0004 | -0.0032 | 0.0004 | 0.0036 | 0.0008 | -0.001 | 0.0157 | -0.0114 | -0.0016 | -360.2542 | 17.448 | -360.4635 | 17.6245 | -360.8235 | 18.1399 | -360.8389 | 17.6225 | -352.6844 | 18.7415 | -352.6752 | 16.834
12:39 | 4757 | 42.7129 | 202.5286 | 449.8816 | 456.8269 | -16.5859 | -40.4322 | 11.3869 | 8.1268 | 2.4634 | 0.5946 | 3.2593 | -0.8842 | 11.7599 | 4.6411 | 0.6198 | 0.6662 | 0.9613 | 0.7461 | -129.515 | 0.3512 | 5.8047 | 1.7791 | -2.81 | -1.2822 | 4.522 |  | 3.3076 | 0.1162 | 4.0092 | 3.3626 | 3.3394 | 1.0778 | 10.751 | 14.2707 | 14.8621 | 11.1038 | 0 | -0.0031 | 0.0011 | 0.0038 | 0.0008 | -0.0003 | 0.0242 | -0.0078 | -0.0273 | -360.1681 | 17.4192 | -360.5096 | 17.6697 | -360.8758 | 18.1789 | -360.8327 | 17.5835 | -352.5798 | 18.7271 | -352.666 | 16.8772
12:39 | 4758 | 42.6605 | 202.5727 | 449.8438 | 456.8346 | -16.529 | -40.5092 | 11.3833 | 8.0893 | 2.4728 | 0.5552 | 3.2957 | -0.8986 | 11.8651 | 4.7243 | 0.6197 | 0.6674 | 0.9624 | 0.7469 | -129.5099 | 0.2879 | 5.7284 | 1.7541 | -2.8483 | -1.2174 | 4.5637 |  | 3.3367 | 0.2766 | 4.0087 | 3.3672 | 3.3385 | 1.0801 | 10.7834 | 14.2567 | 14.8593 | 11.0901 | -0.0002 | -0.0028 | 0.0007 | 0.0038 | 0.001 | -0.0008 | 0.0234 | -0.0051 | -0.0028 | -360.2081 | 17.4028 | -360.4142 | 17.6204 | -360.8174 | 18.181 | -360.9004 | 17.6204 | -352.6413 | 18.7004 | -352.6075 | 16.8258
12:39 | 4759 | 42.685 | 202.5463 | 449.768 | 456.844 | -16.555 | -40.58 | 11.3372 | 8.104 | 2.4975 | 0.5998 | 3.2962 | -0.9114 | 11.8959 | 4.7198 | 0.6213 | 0.6609 | 0.9599 | 0.7457 | -129.4622 | 0.3357 | 5.7952 | 1.6791 | -2.8505 | -1.2181 | 4.5181 |  | 3.2818 | 0.2312 | 4.0093 | 3.3655 | 3.3353 | 1.08 | 10.7591 | 14.2785 | 14.8048 | 11.0721 | -0.0004 | -0.0026 | 0.0013 | 0.0043 | 0.0007 | 0.0002 | 0.0157 | 0.0001 | -0.0018 | -360.1835 | 17.4356 | -360.4973 | 17.6225 | -360.805 | 18.1502 | -360.8266 | 17.5958 | -352.666 | 18.7436 | -352.6752 | 16.8423
12:39 | 4760 | 42.6731 | 202.5515 | 449.8397 | 456.8139 | -16.5319 | -40.4863 | 11.3251 | 8.0614 | 2.4614 | 0.5333 | 3.2562 | -0.8891 | 11.9149 | 4.7111 | 0.6195 | 0.6653 | 0.9617 | 0.744 | -129.472 | 0.2402 | 5.7182 | 1.648 | -2.8654 | -1.2916 | 4.5395 |  | 3.2801 | 0.2224 | 4.0092 | 3.3688 | 3.3394 | 1.0802 | 10.7821 | 14.3137 | 14.8833 | 11.0941 | 0 | -0.0028 | 0.0007 | 0.004 | 0.0008 | -0.0008 | 0.0146 | -0.005 | 0.0014 | -360.1219 | 17.4028 | -360.4635 | 17.6471 | -360.8789 | 18.1748 | -360.8389 | 17.5732 | -352.5798 | 18.7025 | -352.6475 | 16.8546
12:39 | 4761 | 42.7285 | 202.4901 | 449.8288 | 456.7604 | -16.4798 | -40.6308 | 11.3334 | 8.0115 | 2.4018 | 0.4967 | 3.1768 | -0.9778 | 11.8894 | 4.7533 | 0.6183 | 0.6613 | 0.9614 | 0.7461 | -129.4654 | 0.2294 | 5.7862 | 1.6336 | -2.8823 | -1.2383 | 4.5409 |  | 3.2548 | 0.167 | 4.0097 | 3.3668 | 3.3417 | 1.0805 | 10.7903 | 14.2754 | 14.8734 | 11.085 | -0.0001 | -0.0033 | 0.0007 | 0.0039 | 0.0007 | 0.0003 | 0.0069 | 0.0064 | -0.0096 | -360.1804 | 17.4192 | -360.4266 | 17.6061 | -360.802 | 18.1522 | -360.8604 | 17.6184 | -352.666 | 18.7128 | -352.6075 | 16.8053
12:39 | 4762 | 42.7227 | 202.4863 | 449.6906 | 456.6679 | -16.4396 | -40.6056 | 11.2784 | 8.0942 | 2.4362 | 0.5658 | 3.2223 | -0.998 | 11.9256 | 4.6041 | 0.6184 | 0.661 | 0.9587 | 0.7439 | -129.4465 | 0.2074 | 5.8066 | 1.6665 | -2.8016 | -1.279 | 4.5609 |  | 3.3203 | 0.3798 | 4.0097 | 3.3631 | 3.3364 | 1.079 | 10.7914 | 14.2767 | 14.8642 | 11.1089 | 0.0003 | -0.0029 | 0.001 | 0.0044 | 0.001 | -0.0007 | -0.0002 | -0.0188 | -0.0053 | -360.1927 | 17.4295 | -360.485 | 17.6369 | -360.8174 | 18.1235 | -360.8081 | 17.5794 | -352.6075 | 18.7353 | -352.6813 | 16.8443
12:39 | 4763 | 42.7585 | 202.5832 | 449.8123 | 456.7645 | -16.3807 | -40.5773 | 11.3482 | 8.0801 | 2.4264 | 0.5091 | 3.2228 | -0.9808 | 11.9296 | 4.6059 | 0.6193 | 0.6653 | 0.959 | 0.7453 | -129.4875 | 0.274 | 5.7657 | 1.6517 | -2.8428 | -1.2019 | 4.5599 |  | 3.3011 | 0.2629 | 4.0094 | 3.3669 | 3.3402 | 1.0805 | 10.7833 | 14.2858 | 14.8836 | 11.1417 | -0.0001 | -0.0024 | 0.0004 | 0.0035 | 0.0008 | -0.0008 | 0.0039 | 0.005 | -0.0199 | -360.1681 | 17.3823 | -360.3989 | 17.6225 | -360.8358 | 18.183 | -360.8635 | 17.5773 | -352.6044 | 18.6861 | -352.6136 | 16.8361
12:39 | 4764 | 42.7613 | 202.5882 | 449.851 | 456.803 | -16.3945 | -40.5534 | 11.3196 | 8.0585 | 2.5132 | 0.6585 | 3.275 | -0.9862 | 11.8926 | 4.7585 | 0.6192 | 0.6617 | 0.9627 | 0.7449 | -129.5037 | 0.2502 | 5.8064 | 1.6439 | -2.7584 | -1.1574 | 4.5999 |  | 3.2872 | 0.1449 | 4.0095 | 3.3669 | 3.3371 | 1.0803 | 10.7684 | 14.2879 | 14.8436 | 11.0811 | -0.0001 | -0.0026 | 0.0007 | 0.0038 | 0.0009 | -0.0005 | 0.0118 | -0.0139 | -0.0097 | -360.1988 | 17.4213 | -360.4296 | 17.5835 | -360.7589 | 18.1337 | -360.805 | 17.5958 | -352.6506 | 18.7087 | -352.6167 | 16.8053
12:39 | 4765 | 42.7097 | 202.5696 | 449.7772 | 456.7525 | -16.4584 | -40.5672 | 11.3494 | 8.0464 | 2.5355 | 0.7511 | 3.2462 | -0.9621 | 11.8481 | 4.7584 | 0.6191 | 0.6641 | 0.9614 | 0.7462 | -129.5026 | 0.0865 | 5.6836 | 1.9131 | -2.746 | -1.2011 | 4.6548 |  | 3.3081 | 0.2851 | 4.0091 | 3.3653 | 3.3414 | 1.0793 | 10.7613 | 14.2696 | 14.8444 | 11.085 | 0.0002 | -0.0031 | 0.0013 | 0.0038 | 0.0009 | -0.0008 | 0.0088 | -0.0153 | -0.0091 | -360.0973 | 17.3987 | -360.4542 | 17.6245 | -360.8358 | 18.1358 | -360.7927 | 17.5527 | -352.546 | 18.6881 | -352.6506 | 16.8505
12:39 | 4766 | 42.7464 | 202.4959 | 449.742 | 456.7586 | -16.4901 | -40.5988 | 11.2681 | 8.035 | 2.5611 | 0.673 | 3.2724 | -0.8826 | 11.7703 | 4.6398 | 0.6192 | 0.6624 | 0.9575 | 0.7442 | -129.5088 | 0.1697 | 5.6507 | 1.9722 | -2.7276 | -1.1192 | 4.6458 |  | 3.293 | 0.2305 | 4.0096 | 3.3661 | 3.3394 | 1.0799 | 10.7764 | 14.2673 | 14.8648 | 11.0829 | -0.0001 | -0.0031 | 0.0013 | 0.0042 | 0.0009 | -0.0002 | 0.0143 | -0.0007 | -0.001 | -360.1496 | 17.3699 | -360.3619 | 17.5855 | -360.7743 | 18.1604 | -360.845 | 17.5896 | -352.5829 | 18.6635 | -352.5552 | 16.8032
12:39 | 4767 | 42.6732 | 202.4792 | 449.7957 | 456.7425 | -16.4513 | -40.6941 | 11.3213 | 8.0663 | 2.4204 | 0.6916 | 3.2673 | -0.9687 | 11.7981 | 4.6328 | 0.6186 | 0.6604 | 0.963 | 0.7452 | -129.5218 | 0.1124 | 5.6101 | 1.8575 | -2.7553 | -1.1812 | 4.5967 |  | 3.3119 | 0.294 | 4.0079 | 3.3681 | 3.3422 | 1.0797 | 10.7994 | 14.2852 | 14.8691 | 11.1045 | -0.0002 | -0.0025 | 0.0016 | 0.0043 | 0.0014 | 0 | 0.0207 | -0.0003 | 0.002 | -360.1865 | 17.4151 | -360.4542 | 17.6081 | -360.7681 | 18.1194 | -360.762 | 17.5732 | -352.6106 | 18.7169 | -352.6567 | 16.8299
12:39 | 4768 | 42.6402 | 202.5072 | 449.8036 | 456.7373 | -16.4717 | -40.601 | 11.278 | 8.0946 | 2.3794 | 0.6358 | 3.2283 | -0.9808 | 11.7742 | 4.617 | 0.6186 | 0.6614 | 0.9649 | 0.7442 | -129.5511 | 0.2501 | 5.694 | 1.9061 | -2.6893 | -1.1177 | 4.6026 |  | 3.3516 | 0.3103 | 4.0098 | 3.3671 | 3.3395 | 1.0808 | 10.7984 | 14.3067 | 14.8587 | 11.0988 | -0.0004 | -0.0029 | 0.0008 | 0.004 | 0.0007 | -0.0001 | 0.0197 | -0.0146 | 0.0024 | -360.1188 | 17.3617 | -360.4081 | 17.6122 | -360.8174 | 18.1563 | -360.8235 | 17.5568 | -352.549 | 18.6614 | -352.6044 | 16.8402
12:39 | 4769 | 42.7518 | 202.5533 | 449.8792 | 456.7431 | -16.4667 | -40.5558 | 11.3653 | 8.1411 | 2.2738 | 0.6423 | 3.1783 | -0.9175 | 11.7783 | 4.6715 | 0.62 | 0.6638 | 0.9653 | 0.7458 | -129.4955 | 0.2933 | 5.7078 | 1.9432 | -2.6846 | -1.0904 | 4.6769 |  | 3.3613 | 0.3696 | 4.0082 | 3.3626 | 3.3382 | 1.0793 | 10.7938 | 14.273 | 14.8417 | 11.0771 | 0.0005 | -0.0028 | 0.0003 | 0.0037 | 0.0007 | -0.0003 | 0.0051 | -0.0084 | -0.0248 | -360.1804 | 17.4028 | -360.4112 | 17.5835 | -360.7558 | 18.1255 | -360.8327 | 17.6061 | -352.6475 | 18.7004 | -352.5921 | 16.8074
12:39 | 4770 | 42.739 | 202.5733 | 449.8639 | 456.7165 | -16.3856 | -40.5416 | 11.3598 | 8.1436 | 2.2124 | 0.7021 | 3.2211 | -0.8651 | 11.804 | 4.6756 | 0.6192 | 0.6634 | 0.9629 | 0.7462 | -129.4179 | 0.2254 | 5.7792 | 1.9876 | -2.6222 | -1.1346 | 4.7416 |  | 3.405 | 0.3548 | 4.0085 | 3.3615 | 3.3369 | 1.0789 | 10.7591 | 14.244 | 14.8232 | 11.089 | 0.0002 | -0.0029 | 0.0009 | 0.0038 | 0.0009 | -0.0002 | 0.0068 | -0.0062 | -0.0209 | -360.1342 | 17.4028 | -360.4512 | 17.6286 | -360.8297 | 18.1255 | -360.7435 | 17.5568 | -352.5613 | 18.7025 | -352.6444 | 16.8505
12:39 | 4771 | 42.8438 | 202.6086 | 449.9154 | 456.7509 | -16.4554 | -40.5415 | 11.2884 | 8.1756 | 2.3018 | 0.9121 | 3.324 | -0.8006 | 11.8339 | 4.6881 | 0.6188 | 0.6621 | 0.9613 | 0.7448 | -129.4133 | 0.2619 | 5.728 | 1.868 | -2.7872 | -1.1636 | 4.6155 |  | 3.4188 | 0.266 | 4.0094 | 3.3693 | 3.3423 | 1.0791 | 10.7592 | 14.2726 | 14.8327 | 11.0667 | -0.0002 | -0.0025 | 0.0003 | 0.0033 | 0.0011 | -0.0007 | 0.0138 | -0.0134 | -0.0076 | -360.1588 | 17.3576 | -360.3496 | 17.5855 | -360.802 | 18.1748 | -360.8574 | 17.5958 | -352.6013 | 18.6635 | -352.5583 | 16.8156
12:39 | 4772 | 42.7284 | 202.5285 | 449.7937 | 456.7602 | -16.4801 | -40.4293 | 11.3046 | 8.2382 | 2.4069 | 0.7787 | 3.3077 | -0.933 | 11.8248 | 4.6266 | 0.6187 | 0.6624 | 0.963 | 0.7459 | -129.4426 | 0.2834 | 5.8071 | 1.8915 | -2.835 | -1.1268 | 4.6523 |  | 3.3788 | 0.2818 | 4.0084 | 3.3646 | 3.3396 | 1.0796 | 10.7626 | 14.2415 | 14.8136 | 11.0526 | -0.0004 | -0.0028 | 0.0005 | 0.0033 | 0.0009 | 0.0001 | 0.0043 | -0.0109 | -0.0341 | -360.1927 | 17.4192 | -360.4635 | 17.602 | -360.7527 | 18.1173 | -360.7897 | 17.5753 | -352.6198 | 18.721 | -352.6598 | 16.8238
12:39 | 4773 | 42.7481 | 202.5355 | 449.8749 | 456.826 | -16.5364 | -40.4047 | 11.3385 | 8.1782 | 2.2967 | 0.6169 | 3.2843 | -0.9162 | 11.8488 | 4.7003 | 0.6181 | 0.6628 | 0.9632 | 0.7456 | -129.4803 | 0.3171 | 5.817 | 1.8714 | -2.8246 | -1.2025 | 4.6091 |  | 3.3988 | 0.2707 | 4.0101 | 3.3642 | 3.3388 | 1.0796 | 10.7568 | 14.2707 | 14.8621 | 11.0749 | 0.0001 | -0.0028 | 0.0011 | 0.0037 | 0.0007 | -0.0012 | -0.0071 | -0.0093 | 0.0016 | -360.0788 | 17.3658 | -360.3958 | 17.6225 | -360.8266 | 18.1604 | -360.8081 | 17.5527 | -352.4998 | 18.6737 | -352.6044 | 16.8402
12:39 | 4774 | 42.6766 | 202.5124 | 449.8389 | 456.8072 | -16.4576 | -40.3857 | 11.4212 | 8.1145 | 2.2426 | 0.5483 | 3.2552 | -0.9985 | 11.7875 | 4.5187 | 0.6192 | 0.6625 | 0.9664 | 0.7459 | -129.4092 | 0.2843 | 5.7908 | 1.8176 | -2.7461 | -1.1299 | 4.6878 |  | 3.3404 | 0.3196 | 4.0098 | 3.3659 | 3.3402 | 1.0804 | 10.7776 | 14.2567 | 14.8651 | 11.0959 | 0.0002 | -0.0028 | 0.001 | 0.0037 | 0.0006 | -0.0004 | 0.0198 | -0.0186 | -0.0013 | -360.1773 | 17.4069 | -360.4081 | 17.5773 | -360.7527 | 18.1276 | -360.8358 | 17.5978 | -352.666 | 18.7004 | -352.589 | 16.8074
12:39 | 4775 | 42.7515 | 202.4777 | 449.9699 | 456.807 | -16.4143 | -40.3375 | 11.5 | 8.088 | 2.1541 | 0.6448 | 3.1823 | -0.9593 | 11.8391 | 4.632 | 0.6179 | 0.6588 | 0.9617 | 0.7462 | -129.5323 | 0.2362 | 5.8332 | 1.743 | -2.7705 | -1.1647 | 4.6686 |  | 3.3728 | 0.3001 | 4.0086 | 3.366 | 3.3396 | 1.079 | 10.8052 | 14.3082 | 14.9028 | 11.1222 | -0.0005 | -0.0025 | 0.0014 | 0.0045 | 0.0011 | -0.0002 | -0.0038 | 0.0015 | -0.0039 | -360.1311 | 17.4028 | -360.485 | 17.6184 | -360.805 | 18.1317 | -360.7743 | 17.5424 | -352.586 | 18.7169 | -352.666 | 16.8484
12:39 | 4776 | 42.6252 | 202.4784 | 449.946 | 456.7872 | -16.3864 | -40.248 | 11.5142 | 8.0811 | 2.2159 | 0.6596 | 3.2331 | -0.9352 | 11.8382 | 4.5433 | 0.6185 | 0.6619 | 0.962 | 0.7453 | -129.4957 | 0.1328 | 5.7521 | 1.6967 | -2.7141 | -1.2341 | 4.6681 |  | 3.3469 | 0.3999 | 4.0089 | 3.3651 | 3.3394 | 1.0785 | 10.796 | 14.3162 | 14.8755 | 11.0958 | 0 | -0.0022 | 0.0007 | 0.0045 | 0.0011 | -0.0002 | 0.0013 | 0.0009 | -0.0015 | -360.1281 | 17.3597 | -360.3804 | 17.5855 | -360.8112 | 18.1666 | -360.845 | 17.5835 | -352.6106 | 18.6635 | -352.5644 | 16.8217
12:39 | 4777 | 42.7097 | 202.4523 | 449.9203 | 456.7899 | -16.431 | -40.1743 | 11.5767 | 8.0811 | 2.2363 | 0.684 | 3.2552 | -0.9222 | 11.8991 | 4.6653 | 0.6191 | 0.6627 | 0.964 | 0.7454 | -129.4634 | 0.2375 | 5.8 | 1.7954 | -2.704 | -1.0819 | 4.8039 |  | 3.3185 | 0.2684 | 4.0098 | 3.3684 | 3.3416 | 1.0789 | 10.7915 | 14.3054 | 14.8563 | 11.1212 | 0.0001 | -0.0029 | 0.0004 | 0.004 | 0.0006 | -0.0004 | 0.0026 | -0.0016 | -0.0125 | -360.2358 | 17.4233 | -360.4481 | 17.5814 | -360.762 | 18.1112 | -360.8081 | 17.5835 | -352.6413 | 18.7148 | -352.626 | 16.8238
12:39 | 4778 | 42.7545 | 202.5123 | 449.8402 | 456.7351 | -16.4309 | -40.1705 | 11.4812 | 8.1255 | 2.1994 | 0.682 | 3.2665 | -0.8172 | 11.8804 | 4.6917 | 0.6185 | 0.6605 | 0.9623 | 0.7456 | -129.4771 | 0.2991 | 5.7534 | 1.9153 | -2.6501 | -1.0231 | 4.7978 |  | 3.2856 | 0.2382 | 4.0093 | 3.3651 | 3.3402 | 1.0782 | 10.7765 | 14.2496 | 14.8222 | 11.0836 | 0.0002 | -0.0031 | 0.0009 | 0.0044 | 0.0009 | -0.0005 | 0.017 | -0.0096 | -0.0126 | -360.0788 | 17.3884 | -360.4327 | 17.6266 | -360.8481 | 18.1584 | -360.7897 | 17.5568 | -352.549 | 18.6799 | -352.6413 | 16.8546
12:39 | 4779 | 42.7508 | 202.5394 | 449.8609 | 456.8315 | -16.4246 | -40.2782 | 11.5154 | 8.1173 | 2.2205 | 0.7413 | 3.2048 | -0.8234 | 11.8517 | 4.7425 | 0.6163 | 0.6578 | 0.956 | 0.7446 | -129.3893 | 0.3957 | 5.8269 | 1.929 | -2.7532 | -1.1109 | 4.7416 |  | 3.2618 | 0.3257 | 4.0096 | 3.3648 | 3.3429 | 1.0789 | 10.7765 | 14.2785 | 14.8106 | 11.0836 | -0.0004 | -0.0032 | 0.0007 | 0.0038 | 0.0007 | -0.0002 | 0.0031 | -0.0033 | 0.0041 | -360.1865 | 17.3761 | -360.3619 | 17.5794 | -360.725 | 18.1707 | -360.8635 | 17.5917 | -352.5798 | 18.6799 | -352.5583 | 16.8053
12:39 | 4780 | 42.807 | 202.5162 | 449.9653 | 456.8863 | -16.3753 | -40.2548 | 11.5646 | 8.1305 | 2.2203 | 0.7155 | 3.3178 | -0.8849 | 11.762 | 4.6454 | 0.6174 | 0.6634 | 0.9599 | 0.7456 | -129.436 | 0.2696 | 5.7494 | 1.9927 | -2.6744 | -1.0108 | 4.7305 |  | 3.2723 | 0.2887 | 4.0092 | 3.3645 | 3.3384 | 1.0785 | 10.7846 | 14.2576 | 14.8412 | 11.0573 | -0.0005 | -0.0029 | 0.0011 | 0.004 | 0.001 | -0.0007 | -0.0045 | -0.0095 | -0.0101 | -360.2173 | 17.4131 | -360.4327 | 17.6143 | -360.7835 | 18.1461 | -360.762 | 17.5753 | -352.5829 | 18.7107 | -352.6444 | 16.8361
12:39 | 4781 | 42.9042 | 202.5487 | 449.8455 | 456.8763 | -16.3923 | -40.2548 | 11.5193 | 8.074 | 2.1929 | 0.6197 | 3.2839 | -1.0007 | 11.7748 | 4.6331 | 0.6185 | 0.6608 | 0.9613 | 0.7456 | -129.4592 | 0.3078 | 5.83 | 1.9746 | -2.6594 | -1.0701 | 4.7657 |  | 3.2559 | 0.1773 | 4.0092 | 3.3671 | 3.3378 | 1.0786 | 10.7811 | 14.2775 | 14.8277 | 11.0706 | -0.0002 | -0.003 | 0.0009 | 0.0041 | 0.0006 | -0.0001 | 0.0219 | 0.0001 | -0.0148 | -360.1127 | 17.3535 | -360.3896 | 17.6204 | -360.8081 | 18.1912 | -360.802 | 17.5588 | -352.5275 | 18.6635 | -352.589 | 16.8402
12:39 | 4782 | 42.6863 | 202.3814 | 449.7708 | 456.7152 | -16.4642 | -40.2802 | 11.484 | 8.0085 | 2.2354 | 0.6834 | 3.2866 | -0.9647 | 11.8143 | 4.5595 | 0.619 | 0.6608 | 0.9627 | 0.7442 | -129.5067 | 0.2759 | 5.6987 | 2.0534 | -2.644 | -1.058 | 4.7381 |  | 3.3034 | 0.2077 | 4.0103 | 3.3669 | 3.3379 | 1.0787 | 10.7902 | 14.2929 | 14.8744 | 11.0789 | 0 | -0.0031 | 0.001 | 0.0037 | 0.0011 | -0.0004 | -0.0021 | -0.0218 | -0.0007 | -360.2081 | 17.3987 | -360.4266 | 17.5753 | -360.7281 | 18.1604 | -360.7958 | 17.5937 | -352.6537 | 18.6984 | -352.6136 | 16.8135
12:39 | 4783 | 42.7163 | 202.4566 | 449.869 | 456.7193 | -16.4836 | -40.2695 | 11.4445 | 7.9681 | 2.2699 | 0.7104 | 3.3563 | -0.8863 | 11.9386 | 4.7083 | 0.6186 | 0.6611 | 0.962 | 0.7446 | -129.4949 | 0.3318 | 5.7438 | 1.9875 | -2.765 | -1.0734 | 4.756 |  | 3.3442 | 0.2715 | 4.0092 | 3.3701 | 3.3382 | 1.0793 | 10.7753 | 14.2834 | 14.875 | 11.0876 | 0.0001 | -0.0026 | 0.0007 | 0.0042 | 0.0006 | 0 | 0.0052 | 0.0016 | 0.005 | -360.1311 | 17.3966 | -360.4512 | 17.6286 | -360.8327 | 18.1584 | -360.7743 | 17.5465 | -352.5644 | 18.6984 | -352.6352 | 16.8525
12:39 | 4784 | 42.6796 | 202.3659 | 449.8375 | 456.6658 | -16.4499 | -40.3209 | 11.4833 | 8.0195 | 2.1873 | 0.7253 | 3.3026 | -0.9117 | 11.8147 | 4.5705 | 0.6185 | 0.6615 | 0.9603 | 0.7442 | -129.4948 | 0.231 | 5.7388 | 1.9804 | -2.6958 | -1.0926 | 4.8051 |  | 3.2949 | 0.2659 | 4.0101 | 3.3677 | 3.3401 | 1.0793 | 10.796 | 14.3103 | 14.886 | 11.1367 | -0.0006 | -0.003 | 0.0009 | 0.0039 | 0.0006 | -0.0009 | 0.0101 | 0.0014 | -0.0181 | -360.1373 | 17.3597 | -360.3589 | 17.5917 | -360.7897 | 18.1953 | -360.8512 | 17.5753 | -352.589 | 18.6635 | -352.5798 | 16.8258
12:39 | 4785 | 42.6407 | 202.456 | 449.853 | 456.7119 | -16.4714 | -40.3055 | 11.4986 | 8.0318 | 2.2918 | 0.7778 | 3.3367 | -0.8621 | 11.8567 | 4.5924 | 0.6186 | 0.6598 | 0.9565 | 0.745 | -129.4243 | 0.3865 | 5.8891 | 1.956 | -2.8001 | -1.1217 | 4.6389 |  | 3.3626 | 0.2232 | 4.0102 | 3.3663 | 3.3398 | 1.0783 | 10.8134 | 14.3276 | 14.886 | 11.0789 | -0.0001 | -0.0027 | 0.0005 | 0.004 | 0.0009 | 0.0001 | 0.0033 | -0.0009 | -0.0031 | -360.1588 | 17.4315 | -360.4604 | 17.5999 | -360.7681 | 18.144 | -360.7589 | 17.5753 | -352.6321 | 18.721 | -352.6567 | 16.8279
12:39 | 4786 | 42.6136 | 202.4148 | 449.7958 | 456.6896 | -16.4769 | -40.3349 | 11.4234 | 8.0079 | 2.3213 | 0.685 | 3.3151 | -0.89 | 11.8355 | 4.6239 | 0.6193 | 0.6614 | 0.9623 | 0.7448 | -129.4514 | 0.3701 | 5.8445 | 1.9842 | -2.7075 | -1.0331 | 4.7139 |  | 3.3984 | 0.3299 | 4.0093 | 3.3668 | 3.3384 | 1.0801 | 10.7718 | 14.2914 | 14.8478 | 11.119 | 0.0002 | -0.0032 | 0.0007 | 0.004 | 0.0005 | -0.0006 | 0.0056 | -0.0066 | -0.0106 | -360.0911 | 17.3638 | -360.3958 | 17.6225 | -360.8297 | 18.1912 | -360.8266 | 17.5445 | -352.5398 | 18.6491 | -352.5952 | 16.8484
12:39 | 4787 | 42.7247 | 202.4095 | 449.8124 | 456.7463 | -16.4541 | -40.3346 | 11.4122 | 7.9927 | 2.3125 | 0.7015 | 3.3103 | -0.934 | 11.8637 | 4.5808 | 0.6188 | 0.6607 | 0.965 | 0.7453 | -129.4289 | 0.4486 | 5.931 | 2.0523 | -2.6779 | -1.061 | 4.7378 |  | 3.261 | 0.2327 | 4.01 | 3.3658 | 3.3401 | 1.0795 | 10.7822 | 14.2615 | 14.8764 | 11.0887 | 0 | -0.003 | 0.0008 | 0.0039 | 0.0009 | -0.0005 | -0.0005 | -0.0085 | -0.0219 | -360.1711 | 17.3987 | -360.4112 | 17.5773 | -360.7589 | 18.1645 | -360.8235 | 17.5814 | -352.6537 | 18.6963 | -352.5767 | 16.8156
12:40 | 4788 | 42.6987 | 202.4658 | 449.8646 | 456.7771 | -16.405 | -40.4001 | 11.3964 | 7.9632 | 2.3055 | 0.6638 | 3.2767 | -0.9554 | 11.7842 | 4.5367 | 0.6197 | 0.6628 | 0.9617 | 0.7443 | -129.3734 | 0.2987 | 5.7846 | 1.9192 | -2.7092 | -1.1147 | 4.5828 |  | 3.3895 | 0.3061 | 4.0104 | 3.3633 | 3.3368 | 1.0806 | 10.7927 | 14.2486 | 14.8334 | 11.088 | 0.0002 | -0.0025 | 0.0009 | 0.0036 | 0.0006 | -0.0007 | 0.0209 | -0.0104 | -0.0055 | -360.1281 | 17.4028 | -360.4635 | 17.6328 | -360.8081 | 18.1645 | -360.7589 | 17.5404 | -352.5798 | 18.6984 | -352.626 | 16.8587
12:40 | 4789 | 42.6867 | 202.5111 | 449.8264 | 456.789 | -16.394 | -40.3332 | 11.4235 | 7.9781 | 2.3246 | 0.7238 | 3.3079 | -1.0059 | 11.8305 | 4.6009 | 0.6185 | 0.6619 | 0.9643 | 0.7461 | -129.4496 | 0.2452 | 5.7889 | 1.8874 | -2.7342 | -1.2266 | 4.6107 |  | 3.3963 | 0.4265 | 4.0086 | 3.3657 | 3.3356 | 1.0802 | 10.7695 | 14.2429 | 14.7998 | 11.1049 | 0 | -0.0028 | 0.0016 | 0.0044 | 0.001 | -0.0003 | 0.0045 | 0.0018 | -0.0104 | -360.1127 | 17.3556 | -360.3465 | 17.5876 | -360.7866 | 18.1912 | -360.8543 | 17.5732 | -352.5952 | 18.6573 | -352.5798 | 16.8217
12:40 | 4790 | 42.7467 | 202.4665 | 449.7683 | 456.7127 | -16.4737 | -40.2214 | 11.4166 | 7.9415 | 2.3265 | 0.6953 | 3.2193 | -0.8902 | 11.8348 | 4.6203 | 0.6185 | 0.6605 | 0.9639 | 0.7449 | -129.4623 | 0.2011 | 5.8469 | 1.8686 | -2.775 | -1.2462 | 4.5483 |  | 3.3013 | 0.2988 | 4.0086 | 3.3665 | 3.3357 | 1.0788 | 10.7891 | 14.2802 | 14.8325 | 11.072 | 0.0004 | -0.0027 | 0.0009 | 0.0037 | 0.0006 | -0.0005 | 0.0071 | -0.002 | -0.0053 | -360.1773 | 17.4233 | -360.4696 | 17.6122 | -360.7527 | 18.1379 | -360.7743 | 17.5588 | -352.629 | 18.7292 | -352.6629 | 16.8381
12:40 | 4791 | 42.8241 | 202.536 | 449.855 | 456.7903 | -16.4262 | -40.3826 | 11.4147 | 8.0441 | 2.44 | 0.8593 | 3.3561 | -0.9251 | 11.8849 | 4.6126 | 0.6186 | 0.6605 | 0.9631 | 0.7461 | -129.3618 | 0.2874 | 5.8632 | 1.8909 | -2.7872 | -1.1421 | 4.6055 |  | 3.3562 | 0.2603 | 4.0101 | 3.3673 | 3.3379 | 1.0795 | 10.7695 | 14.3006 | 14.8334 | 11.0648 | 0 | -0.0031 | 0.0003 | 0.0037 | 0.001 | -0.0008 | 0.0046 | -0.0115 | 0.0028 | -360.0696 | 17.3556 | -360.3865 | 17.6184 | -360.8235 | 18.1933 | -360.805 | 17.5363 | -352.549 | 18.6799 | -352.6106 | 16.8505
12:40 | 4792 | 42.8574 | 202.5382 | 449.8653 | 456.789 | -16.5112 | -40.2659 | 11.3549 | 8 | 2.4273 | 0.809 | 3.2989 | -1.0197 | 11.8565 | 4.638 | 0.6191 | 0.6629 | 0.9574 | 0.7444 | -129.3951 | 0.2909 | 5.7851 | 1.9271 | -2.7067 | -1.1839 | 4.5769 |  | 3.2996 | 0.2527 | 4.0115 | 3.3686 | 3.3336 | 1.0785 | 10.8052 | 14.2733 | 14.867 | 11.0995 | -0.0003 | -0.0022 | 0.0006 | 0.0039 | 0.0009 | 0.0005 | 0.0057 | 0.007 | -0.0019 | -360.1681 | 17.3987 | -360.4019 | 17.5855 | -360.7712 | 18.1522 | -360.8235 | 17.5896 | -352.666 | 18.7148 | -352.6075 | 16.8135
12:40 | 4793 | 42.8313 | 202.4826 | 449.9098 | 456.7867 | -16.4264 | -40.2368 | 11.3422 | 8.0042 | 2.3998 | 0.7458 | 3.2574 | -0.9077 | 11.8695 | 4.6459 | 0.6188 | 0.6598 | 0.9587 | 0.744 | -129.3892 | 0.2974 | 5.7975 | 1.8616 | -2.7565 | -1.1698 | 4.5665 |  | 3.3407 | 0.2443 | 4.009 | 3.368 | 3.3392 | 1.0786 | 10.7903 | 14.2868 | 14.8607 | 11.097 | -0.0004 | -0.0026 | 0.0002 | 0.0038 | 0.0012 | -0.0007 | 0.0017 | -0.0137 | -0.0015 | -360.1219 | 17.3966 | -360.445 | 17.6286 | -360.8297 | 18.1604 | -360.8112 | 17.5363 | -352.6013 | 18.721 | -352.6598 | 16.8546
12:40 | 4794 | 42.9012 | 202.5297 | 449.9804 | 456.8644 | -16.4986 | -40.2446 | 11.3676 | 8.025 | 2.483 | 0.8383 | 3.4003 | -0.9065 | 11.8038 | 4.6382 | 0.6169 | 0.6591 | 0.9616 | 0.7443 | -129.4302 | 0.3246 | 5.7494 | 1.9047 | -2.7443 | -1.16 | 4.5277 |  | 3.3971 | 0.3385 | 4.0098 | 3.3647 | 3.3387 | 1.0789 | 10.7707 | 14.2612 | 14.8395 | 11.101 | 0.0003 | -0.0031 | 0.0012 | 0.0044 | 0.0006 | 0.0003 | 0.0005 | -0.0098 | -0.0012 | -360.1158 | 17.3597 | -360.3712 | 17.5896 | -360.7927 | 18.2056 | -360.8666 | 17.5712 | -352.589 | 18.6737 | -352.549 | 16.832
12:40 | 4795 | 42.7684 | 202.5145 | 449.7598 | 456.6824 | -16.5206 | -40.2078 | 11.413 | 8.0521 | 2.4923 | 0.7405 | 3.341 | -0.9872 | 11.8208 | 4.6646 | 0.6167 | 0.6604 | 0.9591 | 0.7441 | -129.394 | 0.2955 | 5.7691 | 1.9322 | -2.6841 | -1.1648 | 4.5997 |  | 3.4228 | 0.2331 | 4.0101 | 3.3672 | 3.3422 | 1.0796 | 10.7949 | 14.2975 | 14.8557 | 11.1009 | 0.0003 | -0.0027 | 0.0007 | 0.0036 | 0.0011 | -0.0007 | 0.0066 | -0.009 | 0.0051 | -360.1835 | 17.4274 | -360.4358 | 17.5896 | -360.7497 | 18.1399 | -360.7743 | 17.5712 | -352.6752 | 18.7333 | -352.6475 | 16.834
12:40 | 4796 | 42.6873 | 202.4646 | 449.7237 | 456.6981 | -16.4787 | -40.2448 | 11.4462 | 8.0933 | 2.3341 | 0.6921 | 3.2706 | -0.965 | 11.7468 | 4.6274 | 0.6185 | 0.6625 | 0.9623 | 0.7437 | -129.4099 | 0.3128 | 5.7573 | 1.8679 | -2.6595 | -1.0859 | 4.6166 |  | 3.4021 | 0.2753 | 4.0099 | 3.3641 | 3.3384 | 1.0781 | 10.7834 | 14.2913 | 14.8525 | 11.0789 | -0.0003 | -0.0025 | 0.0004 | 0.0036 | 0.0003 | -0.0007 | 0.0233 | -0.0147 | 0.0056 | -360.1281 | 17.372 | -360.4235 | 17.6204 | -360.8266 | 18.1871 | -360.8235 | 17.5465 | -352.5706 | 18.6984 | -352.626 | 16.8546
12:40 | 4797 | 42.8578 | 202.4535 | 449.6914 | 456.7597 | -16.464 | -40.2599 | 11.333 | 8.1615 | 2.3102 | 0.9466 | 3.3836 | -0.9209 | 11.8421 | 4.7308 | 0.6189 | 0.6644 | 0.9634 | 0.7438 | -129.4326 | 0.3424 | 5.7279 | 1.9115 | -2.7075 | -1.0735 | 4.6655 |  | 3.3647 | 0.2513 | 4.0097 | 3.3679 | 3.3397 | 1.0799 | 10.7626 | 14.2647 | 14.8205 | 11.0638 | -0.0004 | -0.0027 | 0.0013 | 0.0043 | 0.0009 | -0.0006 | -0.0019 | -0.01 | -0.0025 | -360.1742 | 17.3864 | -360.3958 | 17.5773 | -360.7558 | 18.183 | -360.8666 | 17.5978 | -352.6567 | 18.7025 | -352.6013 | 16.8217
12:40 | 4798 | 42.7488 | 202.4788 | 449.8347 | 456.7662 | -16.5923 | -40.2676 | 11.35 | 8.1182 | 2.3406 | 0.8265 | 3.3456 | -0.9217 | 11.8782 | 4.7679 | 0.6185 | 0.6656 | 0.966 | 0.7439 | -129.4814 | 0.2954 | 5.7491 | 1.8587 | -2.6729 | -1.1891 | 4.605 |  | 3.3725 | 0.3647 | 4.0093 | 3.3688 | 3.3394 | 1.0791 | 10.7533 | 14.2846 | 14.8475 | 11.1118 | 0.0002 | -0.0031 | 0.0009 | 0.004 | 0.001 | -0.0005 | 0.0057 | -0.009 | -0.0167 | -360.1435 | 17.4172 | -360.4696 | 17.6204 | -360.7927 | 18.142 | -360.7681 | 17.5445 | -352.6229 | 18.7312 | -352.666 | 16.8587
12:40 | 4799 | 42.8416 | 202.4131 | 449.8087 | 456.7117 | -16.5315 | -40.1273 | 11.3565 | 8.1776 | 2.4164 | 0.8621 | 3.3569 | -0.9982 | 11.793 | 4.6736 | 0.6187 | 0.6609 | 0.9643 | 0.7457 | -129.5051 | 0.2134 | 5.7468 | 1.9115 | -2.7581 | -1.1916 | 4.5131 |  | 3.4362 | 0.3363 | 4.0105 | 3.3668 | 3.3376 | 1.0821 | 10.8076 | 14.3043 | 14.8791 | 11.1139 | 0 | -0.003 | 0.0012 | 0.0042 | 0.0008 | -0.0004 | -0.0023 | -0.0133 | -0.0131 | -360.1558 | 17.3597 | -360.3865 | 17.6122 | -360.8235 | 18.2097 | -360.8789 | 17.5568 | -352.6075 | 18.6963 | -352.6198 | 16.8505
12:40 | 4800 | 42.8122 | 202.4568 | 449.8427 | 456.7997 | -16.5255 | -40.1859 | 11.2984 | 8.1707 | 2.3838 | 0.8636 | 3.2884 | -0.9931 | 11.7598 | 4.7096 | 0.6163 | 0.6624 | 0.962 | 0.7451 | -129.4169 | 0.3414 | 5.7895 | 1.8972 | -2.7027 | -1.1167 | 4.588 |  | 3.3783 | 0.2638 | 4.0101 | 3.3679 | 3.3371 | 1.0814 | 10.796 | 14.2987 | 14.8918 | 11.1078 | 0 | -0.0027 | 0.0007 | 0.0044 | 0.0009 | -0.0005 | 0.0112 | -0.0083 | -0.017 | -360.1681 | 17.4172 | -360.4358 | 17.5917 | -360.7589 | 18.1543 | -360.8358 | 17.5732 | -352.6906 | 18.7353 | -352.6413 | 16.8258
12:40 | 4801 | 42.8043 | 202.4782 | 449.7449 | 456.707 | -16.5609 | -40.2122 | 11.3506 | 8.1501 | 2.3594 | 0.9444 | 3.3381 | -0.9587 | 11.7526 | 4.5975 | 0.617 | 0.663 | 0.9618 | 0.7445 | -129.482 | 0.3676 | 5.8109 | 1.8293 | -2.621 | -1.13 | 4.6761 |  | 3.4183 | 0.2783 | 4.0108 | 3.3657 | 3.337 | 1.0806 | 10.7938 | 14.2902 | 14.858 | 11.1295 | -0.0006 | -0.0029 | 0.0009 | 0.004 | 0.0005 | -0.0008 | 0.0113 | -0.0074 | -0.0107 | -360.1342 | 17.409 | -360.5066 | 17.6594 | -360.8604 | 18.1871 | -360.8081 | 17.5342 | -352.6229 | 18.7353 | -352.6967 | 16.8751
12:40 | 4802 | 42.8774 | 202.5092 | 449.9057 | 456.689 | -16.4859 | -40.2387 | 11.3461 | 8.0663 | 2.2671 | 0.7807 | 3.2813 | -0.9146 | 11.8432 | 4.6218 | 0.6175 | 0.6626 | 0.9615 | 0.7448 | -129.5101 | 0.3116 | 5.745 | 1.8227 | -2.6232 | -1.0834 | 4.6541 |  | 3.3701 | 0.2917 | 4.0106 | 3.3668 | 3.3406 | 1.081 | 10.7672 | 14.2751 | 14.8423 | 11.0685 | 0 | -0.003 | 0.0008 | 0.0038 | 0.0011 | -0.0003 | 0.024 | -0.0103 | -0.0038 | -360.1619 | 17.3823 | -360.4112 | 17.6143 | -360.7897 | 18.2036 | -360.8758 | 17.5876 | -352.6598 | 18.7004 | -352.589 | 16.8299
12:40 | 4803 | 42.8243 | 202.4619 | 449.8212 | 456.7223 | -16.4013 | -40.1757 | 11.3504 | 8.0907 | 2.2426 | 0.7122 | 3.2476 | -0.9723 | 11.8672 | 4.6912 | 0.6184 | 0.6593 | 0.9626 | 0.7451 | -129.4945 | 0.2524 | 5.7283 | 1.9351 | -2.5772 | -1.1749 | 4.6364 |  | 3.384 | 0.3686 | 4.0093 | 3.3688 | 3.3386 | 1.0811 | 10.7637 | 14.2776 | 14.8461 | 11.0934 | 0 | -0.0032 | 0.0009 | 0.0035 | 0.0007 | -0.0002 | 0.0114 | -0.017 | -0.0079 | -360.1927 | 17.4397 | -360.5066 | 17.6266 | -360.8081 | 18.1604 | -360.8143 | 17.5712 | -352.6813 | 18.7641 | -352.6998 | 16.8484
12:40 | 4804 | 42.7305 | 202.4401 | 449.8945 | 456.7232 | -16.4821 | -40.2664 | 11.2948 | 8.0534 | 2.3912 | 0.8559 | 3.3741 | -1.0057 | 11.8533 | 4.6585 | 0.6178 | 0.6613 | 0.962 | 0.7446 | -129.5524 | 0.2617 | 5.7684 | 1.9343 | -2.6768 | -1.1779 | 4.6069 |  | 3.4368 | 0.396 | 4.0097 | 3.3704 | 3.3417 | 1.0799 | 10.7753 | 14.2717 | 14.8219 | 11.088 | -0.0003 | -0.0028 | 0.0008 | 0.0035 | 0.001 | -0.0008 | 0.0163 | 0.0001 | -0.0051 | -360.1065 | 17.3905 | -360.4542 | 17.6492 | -360.8574 | 18.2036 | -360.8512 | 17.5547 | -352.5983 | 18.7087 | -352.6598 | 16.871
12:40 | 4805 | 42.7022 | 202.4455 | 449.7435 | 456.6958 | -16.4361 | -40.2297 | 11.2952 | 8.104 | 2.4013 | 0.8059 | 3.4043 | -0.9666 | 11.7961 | 4.6346 | 0.6179 | 0.6654 | 0.9628 | 0.7448 | -129.4261 | 0.3483 | 5.7696 | 1.7949 | -2.656 | -1.3323 | 4.5883 |  | 3.3717 | 0.3495 | 4.0112 | 3.3661 | 3.3347 | 1.0806 | 10.7613 | 14.2698 | 14.8802 | 11.0962 | -0.0005 | -0.003 | 0.0012 | 0.0039 | 0.001 | -0.0001 | 0.0161 | -0.0087 | -0.0004 | -360.2419 | 17.4233 | -360.4204 | 17.604 | -360.8081 | 18.1953 | -360.885 | 17.6143 | -352.6906 | 18.7312 | -352.6475 | 16.8279
12:40 | 4806 | 42.7612 | 202.4714 | 449.7364 | 456.77 | -16.3913 | -40.2999 | 11.3317 | 7.9998 | 2.3051 | 0.8259 | 3.3626 | -0.9368 | 11.8969 | 4.776 | 0.6185 | 0.6634 | 0.9644 | 0.7457 | -129.4286 | 0.2719 | 5.8013 | 1.8866 | -2.653 | -1.0916 | 4.6366 |  | 3.4072 | 0.3208 | 4.0105 | 3.3688 | 3.3383 | 1.0801 | 10.7673 | 14.2923 | 14.8239 | 11.0862 | 0.0002 | -0.0027 | 0.0007 | 0.004 | 0.001 | -0.0007 | -0.0066 | -0.0102 | 0.0064 | -360.1773 | 17.4315 | -360.4973 | 17.6574 | -360.8789 | 18.1666 | -360.802 | 17.5588 | -352.6136 | 18.7456 | -352.709 | 16.871
12:40 | 4807 | 42.7611 | 202.5495 | 449.7995 | 456.8226 | -16.458 | -40.1651 | 11.327 | 8.1118 | 2.4025 | 0.8955 | 3.2608 | -0.8951 | 11.8629 | 4.8204 | 0.619 | 0.6608 | 0.9636 | 0.7447 | -129.4398 | 0.2774 | 5.8405 | 1.8697 | -2.7067 | -1.1698 | 4.637 |  | 3.5085 | 0.2844 | 4.0106 | 3.3651 | 3.3401 | 1.0814 | 10.7741 | 14.2766 | 14.8747 | 11.0977 | 0.0003 | -0.0028 | 0.0007 | 0.0039 | 0.0005 | -0.0004 | 0.0046 | -0.0112 | -0.006 | -360.1742 | 17.3946 | -360.4112 | 17.6307 | -360.8512 | 18.2364 | -360.9035 | 17.5937 | -352.6198 | 18.7087 | -352.6413 | 16.8484
12:40 | 4808 | 42.8083 | 202.5976 | 449.8525 | 456.8205 | -16.4806 | -40.2084 | 11.2973 | 8.1466 | 2.4007 | 1.0104 | 3.3321 | -0.9699 | 11.8884 | 4.7568 | 0.621 | 0.666 | 0.9613 | 0.745 | -129.4519 | 0.3226 | 5.8774 | 1.8217 | -2.7611 | -1.079 | 4.6728 |  | 3.4318 | 0.3752 | 4.0116 | 3.3655 | 3.3383 | 1.0804 | 10.7879 | 14.2849 | 14.8727 | 11.1341 | 0.0001 | -0.0028 | 0.0005 | 0.0039 | 0.0011 | -0.0005 | 0.0116 | -0.0038 | -0.0169 | -360.1835 | 17.4356 | -360.4696 | 17.6225 | -360.7835 | 18.1748 | -360.8512 | 17.5896 | -352.6752 | 18.7559 | -352.7029 | 16.8402
12:40 | 4809 | 42.7914 | 202.5155 | 449.8144 | 456.8126 | -16.4547 | -40.1462 | 11.4512 | 8.0795 | 2.4148 | 0.9891 | 3.2985 | -0.9106 | 11.9482 | 4.7075 | 0.6189 | 0.6639 | 0.9584 | 0.7454 | -129.3595 | 0.4081 | 5.8707 | 1.8241 | -2.7365 | -1.0629 | 4.6707 |  | 3.4088 | 0.4377 | 4.01 | 3.3662 | 3.3402 | 1.0813 | 10.796 | 14.3218 | 14.8744 | 11.102 | -0.0002 | -0.0025 | 0.0008 | 0.0041 | 0.0003 | -0.0003 | 0.0181 | -0.012 | 0.0157 | -360.205 | 17.4192 | -360.5189 | 17.6718 | -360.9097 | 18.1974 | -360.8481 | 17.5609 | -352.589 | 18.7477 | -352.6906 | 16.8854
12:40 | 4810 | 42.7739 | 202.4611 | 449.7781 | 456.8419 | -16.5359 | -40.2086 | 11.367 | 8.0651 | 2.437 | 0.9728 | 3.2711 | -0.8976 | 11.9266 | 4.7179 | 0.6183 | 0.6601 | 0.9592 | 0.744 | -129.3453 | 0.3238 | 5.8341 | 1.9207 | -2.741 | -1.0733 | 4.7189 |  | 3.4061 | 0.3103 | 4.0084 | 3.3662 | 3.3376 | 1.0792 | 10.7613 | 14.2756 | 14.8513 | 11.0904 | 0 | -0.0029 | 0.001 | 0.0041 | 0.0011 | -0.0004 | 0.0094 | -0.0099 | -0.0077 | -360.2081 | 17.4028 | -360.3927 | 17.6184 | -360.8327 | 18.2179 | -360.8974 | 17.6081 | -352.669 | 18.7292 | -352.6321 | 16.834
12:40 | 4811 | 42.8497 | 202.4808 | 449.7114 | 456.8315 | -16.4261 | -40.2649 | 11.3668 | 8.0246 | 2.4319 | 0.7783 | 3.3191 | -0.9212 | 11.8747 | 4.7055 | 0.6192 | 0.6628 | 0.9627 | 0.7454 | -129.3758 | 0.3004 | 5.8958 | 1.902 | -2.7201 | -1.123 | 4.7001 |  | 3.4121 | 0.4767 | 4.0109 | 3.3675 | 3.3365 | 1.0808 | 10.8029 | 14.2825 | 14.8642 | 11.0973 | 0.0003 | -0.0029 | 0.0007 | 0.0039 | 0.0007 | -0.0004 | 0.0074 | -0.0172 | -0.018 | -360.2296 | 17.4562 | -360.5189 | 17.6594 | -360.8358 | 18.1728 | -360.8327 | 17.5896 | -352.6844 | 18.7723 | -352.6967 | 16.8505
12:40 | 4812 | 42.8453 | 202.5265 | 449.7862 | 456.7785 | -16.4584 | -40.2847 | 11.4287 | 8.0413 | 2.4057 | 0.8217 | 3.2847 | -0.9921 | 11.7836 | 4.6996 | 0.6183 | 0.6618 | 0.9574 | 0.7443 | -129.343 | 0.2621 | 5.7987 | 1.8597 | -2.8283 | -1.1172 | 4.6789 |  | 3.4381 | 0.3699 | 4.01 | 3.3646 | 3.3385 | 1.0811 | 10.7822 | 14.2557 | 14.8185 | 11.0829 | 0.0003 | -0.0027 | 0.0005 | 0.0033 | 0.0007 | 0 | 0.0213 | 0.0082 | 0.004 | -360.1096 | 17.3966 | -360.4758 | 17.6656 | -360.885 | 18.2179 | -360.8697 | 17.5629 | -352.6044 | 18.721 | -352.6721 | 16.8628
12:40 | 4813 | 42.8736 | 202.4862 | 449.8666 | 456.7339 | -16.4405 | -40.2616 | 11.416 | 8.027 | 2.3607 | 0.9315 | 3.2559 | -1.007 | 11.7964 | 4.6031 | 0.6176 | 0.6583 | 0.9604 | 0.7463 | -129.428 | 0.2476 | 5.7336 | 1.9305 | -2.7924 | -1.0499 | 4.7457 |  | 3.5292 | 0.4072 | 4.0094 | 3.3628 | 3.3405 | 1.0807 | 10.7568 | 14.2763 | 14.8147 | 11.0869 | -0.0004 | -0.003 | 0.0006 | 0.0037 | 0.0009 | -0.0008 | 0.0049 | -0.0225 | -0.0094 | -360.2358 | 17.4315 | -360.4573 | 17.6143 | -360.7927 | 18.1892 | -360.8974 | 17.6143 | -352.6967 | 18.7374 | -352.6167 | 16.8197
12:40 | 4814 | 42.9197 | 202.5083 | 449.8537 | 456.7968 | -16.368 | -40.1891 | 11.5466 | 8.0553 | 2.4499 | 0.8602 | 3.2923 | -0.9859 | 11.8547 | 4.6696 | 0.6199 | 0.6549 | 0.9583 | 0.7432 | -129.4997 | 0.2834 | 5.78 | 1.9095 | -2.7983 | -0.9942 | 4.715 |  | 3.4987 | 0.3408 | 4.0089 | 3.3646 | 3.3397 | 1.0811 | 10.7487 | 14.2681 | 14.8235 | 11.0616 | 0.0001 | -0.0026 | 0.0009 | 0.0039 | 0.0011 | -0.0001 | 0.0093 | -0.0078 | -0.0016 | -360.1711 | 17.4397 | -360.5035 | 17.6574 | -360.8635 | 18.1748 | -360.802 | 17.5547 | -352.6383 | 18.7518 | -352.7029 | 16.871
12:40 | 4815 | 42.9141 | 202.4692 | 449.9029 | 456.8773 | -16.3526 | -40.2346 | 11.4308 | 8.0273 | 2.4053 | 0.7981 | 3.3427 | -0.9559 | 11.9045 | 4.7459 | 0.6193 | 0.6588 | 0.9575 | 0.7441 | -129.4921 | 0.301 | 5.6899 | 1.8621 | -2.8472 | -0.9517 | 4.7093 |  | 3.4272 | 0.3756 | 4.0094 | 3.3627 | 3.343 | 1.0811 | 10.7603 | 14.2797 | 14.8525 | 11.0674 | 0.0003 | -0.0033 | 0.0004 | 0.0038 | 0.0008 | -0.0007 | 0.013 | -0.0073 | -0.0123 | -360.1958 | 17.3884 | -360.4358 | 17.6225 | -360.8512 | 18.2302 | -360.9127 | 17.5917 | -352.629 | 18.7189 | -352.6013 | 16.832
12:40 | 4816 | 42.8858 | 202.4255 | 449.8094 | 456.7751 | -16.3338 | -40.2204 | 11.4115 | 7.994 | 2.3483 | 0.7583 | 3.3173 | -0.8631 | 11.8936 | 4.7747 | 0.6175 | 0.6628 | 0.9603 | 0.7436 | -129.4283 | 0.3099 | 5.6754 | 1.8186 | -2.842 | -1.0609 | 4.6355 |  | 3.4844 | 0.304 | 4.0107 | 3.3654 | 3.3384 | 1.0799 | 10.7776 | 14.2799 | 14.8767 | 11.1132 | 0.0001 | -0.0028 | 0.0008 | 0.0042 | 0.0005 | -0.0005 | 0.0031 | -0.0157 | -0.0291 | -360.1988 | 17.4521 | -360.4789 | 17.6163 | -360.8112 | 18.1687 | -360.8297 | 17.5978 | -352.6752 | 18.762 | -352.6721 | 16.8279
12:40 | 4817 | 42.9019 | 202.4794 | 449.826 | 456.886 | -16.3711 | -40.227 | 11.4173 | 8.0277 | 2.4247 | 0.8788 | 3.3578 | -0.9773 | 11.8672 | 4.7549 | 0.6184 | 0.6638 | 0.9627 | 0.7442 | -129.5342 | 0.2086 | 5.679 | 1.8544 | -2.8319 | -1.0484 | 4.6404 |  | 3.4315 | 0.2285 | 4.0103 | 3.3685 | 3.341 | 1.0823 | 10.7544 | 14.2859 | 14.8152 | 11.0778 | -0.0002 | -0.0025 | 0.0009 | 0.0039 | 0.0018 | -0.0002 | 0.0067 | -0.0029 | -0.0175 | -360.1435 | 17.4131 | -360.5035 | 17.6492 | -360.9035 | 18.2056 | -360.8358 | 17.5609 | -352.6044 | 18.721 | -352.6537 | 16.8689
12:40 | 4818 | 43.0505 | 202.5099 | 449.8925 | 456.8182 | -16.4897 | -40.2244 | 11.3819 | 8.009 | 2.3482 | 0.8362 | 3.3121 | -1.0227 | 11.8469 | 4.75 | 0.618 | 0.665 | 0.9643 | 0.7443 | -129.4634 | 0.3373 | 5.7074 | 1.7986 | -2.9074 | -1.0832 | 4.6274 |  | 3.425 | 0.2931 | 4.0096 | 3.3661 | 3.3416 | 1.0808 | 10.7879 | 14.3021 | 14.8717 | 11.1056 | -0.0004 | -0.0029 | 0.0012 | 0.0039 | 0.0006 | -0.0002 | 0.0043 | -0.0073 | -0.018 | -360.2265 | 17.411 | -360.4327 | 17.5999 | -360.7958 | 18.2097 | -360.885 | 17.604 | -352.6937 | 18.7292 | -352.6321 | 16.8217
12:40 | 4819 | 43.0653 | 202.5034 | 449.8584 | 456.8855 | -16.5611 | -40.1669 | 11.3403 | 7.9954 | 2.3574 | 0.9867 | 3.3558 | -0.9819 | 11.8655 | 4.7466 | 0.6185 | 0.6618 | 0.9634 | 0.7449 | -129.4583 | 0.2637 | 5.7109 | 1.8377 | -2.8443 | -1.095 | 4.7193 |  | 3.4062 | 0.3366 | 4.009 | 3.3648 | 3.3411 | 1.0811 | 10.7904 | 14.2925 | 14.8712 | 11.0973 | 0.0002 | -0.003 | 0.0008 | 0.0041 | 0.0005 | -0.0006 | 0.0243 | -0.0083 | 0.0179 | -360.1835 | 17.4459 | -360.5127 | 17.6594 | -360.8912 | 18.1687 | -360.7989 | 17.5609 | -352.626 | 18.7641 | -352.7244 | 16.8587
12:40 | 4820 | 43.0617 | 202.4944 | 449.8827 | 456.9183 | -16.5354 | -40.257 | 11.3663 | 7.9664 | 2.286 | 0.904 | 3.3388 | -1.0426 | 11.7785 | 4.6276 | 0.6186 | 0.6635 | 0.9621 | 0.7463 | -129.4031 | 0.2806 | 5.7947 | 1.7721 | -2.769 | -1.0219 | 4.7131 |  | 3.3772 | 0.3146 | 4.0077 | 3.3644 | 3.3401 | 1.0802 | 10.7754 | 14.2947 | 14.8382 | 11.0768 | 0.0002 | -0.0031 | 0.0008 | 0.0034 | 0.0007 | -0.0004 | 0.0061 | 0.0014 | -0.008 | -360.1588 | 17.4028 | -360.4358 | 17.6204 | -360.8512 | 18.2323 | -360.9127 | 17.5937 | -352.6229 | 18.7148 | -352.5952 | 16.8402
12:40 | 4821 | 42.9466 | 202.4647 | 449.8529 | 456.8581 | -16.5406 | -40.2048 | 11.358 | 8.0961 | 2.2735 | 0.9658 | 3.3751 | -0.9875 | 11.7789 | 4.7383 | 0.6178 | 0.6641 | 0.9628 | 0.7464 | -129.456 | 0.2655 | 5.7303 | 1.8168 | -2.641 | -1.0949 | 4.7073 |  | 3.4837 | 0.327 | 4.0093 | 3.3671 | 3.3385 | 1.0804 | 10.7869 | 14.2773 | 14.8497 | 11.0941 | -0.0003 | -0.0029 | 0.0007 | 0.0036 | 0.0006 | -0.0009 | 0.0075 | -0.0192 | -0.0179 | -360.2081 | 17.448 | -360.4942 | 17.6122 | -360.8174 | 18.1728 | -360.8358 | 17.5855 | -352.6844 | 18.7661 | -352.6937 | 16.832
12:40 | 4822 | 42.9569 | 202.4527 | 449.886 | 456.7613 | -16.5503 | -40.1365 | 11.3439 | 8.0743 | 2.2352 | 1.0369 | 3.3381 | -0.9605 | 11.8864 | 4.6508 | 0.6188 | 0.6611 | 0.9642 | 0.7432 | -129.3995 | 0.3295 | 5.7461 | 1.8519 | -2.7745 | -1.0806 | 4.6927 |  | 3.4816 | 0.3697 | 4.0086 | 3.3675 | 3.3396 | 1.0814 | 10.7626 | 14.2646 | 14.8079 | 11.0757 | -0.0003 | -0.0029 | 0.0005 | 0.0038 | 0.0005 | -0.0003 | 0.0088 | -0.0097 | 0.0032 | -360.1742 | 17.4069 | -360.4727 | 17.6553 | -360.8789 | 18.2118 | -360.8543 | 17.5588 | -352.5952 | 18.7312 | -352.6783 | 16.8689
12:40 | 4823 | 43.0198 | 202.391 | 449.9428 | 456.7966 | -16.626 | -40.1056 | 11.3171 | 8.0414 | 2.2349 | 0.8839 | 3.3456 | -0.9538 | 11.8369 | 4.7098 | 0.6197 | 0.6622 | 0.9628 | 0.7461 | -129.4399 | 0.3073 | 5.7548 | 1.8355 | -2.6876 | -1.0147 | 4.7568 |  | 3.4719 | 0.4799 | 4.009 | 3.3655 | 3.3398 | 1.082 | 10.7742 | 14.2821 | 14.8089 | 11.0695 | 0 | -0.0032 | 0.0008 | 0.0038 | 0.0007 | -0.0005 | 0.0036 | -0.0029 | 0.0052 | -360.2265 | 17.409 | -360.4358 | 17.6061 | -360.7804 | 18.2056 | -360.8943 | 17.6143 | -352.6967 | 18.7312 | -352.6044 | 16.8176
12:40 | 4824 | 42.9737 | 202.448 | 449.9167 | 456.7654 | -16.5946 | -40.2557 | 11.4175 | 8.0253 | 2.2613 | 0.9767 | 3.2734 | -0.9043 | 11.88 | 4.7119 | 0.6181 | 0.6625 | 0.9625 | 0.7461 | -129.5052 | 0.2947 | 5.865 | 1.8686 | -2.726 | -1.0967 | 4.6682 |  | 3.4606 | 0.4907 | 4.0083 | 3.364 | 3.3394 | 1.0795 | 10.7822 | 14.2673 | 14.8475 | 11.0887 | 0.0003 | -0.0029 | 0.001 | 0.0045 | 0.001 | -0.0004 | 0.0103 | -0.0082 | -0.0035 | -360.1711 | 17.4541 | -360.5281 | 17.6492 | -360.8727 | 18.1707 | -360.7989 | 17.5671 | -352.6321 | 18.7538 | -352.7183 | 16.8628
12:40 | 4825 | 42.8287 | 202.383 | 449.8728 | 456.6975 | -16.5032 | -40.1463 | 11.4637 | 7.9897 | 2.3212 | 0.8498 | 3.2901 | -0.9163 | 11.8528 | 4.7433 | 0.6177 | 0.6619 | 0.9622 | 0.7457 | -129.5227 | 0.2647 | 5.7055 | 1.9231 | -2.8651 | -1.2266 | 4.6212 |  | 3.4884 | 0.4623 | 4.0109 | 3.3631 | 3.3408 | 1.0807 | 10.8041 | 14.2836 | 14.8645 | 11.0988 | -0.0004 | -0.0027 | 0.0008 | 0.0037 | 0.0007 | -0.0002 | -0.0016 | -0.0035 | 0.0041 | -360.1681 | 17.3946 | -360.4481 | 17.6369 | -360.8635 | 18.2241 | -360.8758 | 17.5855 | -352.6321 | 18.721 | -352.629 | 16.8443
12:40 | 4826 | 42.9359 | 202.4447 | 449.9348 | 456.7696 | -16.6026 | -40.164 | 11.368 | 8.0537 | 2.2791 | 0.8944 | 3.283 | -0.8933 | 11.8041 | 4.7558 | 0.6173 | 0.6607 | 0.9632 | 0.7457 | -129.5035 | 0.2612 | 5.7321 | 1.8676 | -2.8308 | -1.1327 | 4.6635 |  | 3.4517 | 0.3706 | 4.0107 | 3.3665 | 3.34 | 1.0802 | 10.7973 | 14.2938 | 14.8331 | 11.0981 | 0 | -0.0022 | 0.0006 | 0.004 | 0.0013 | -0.0006 | 0.0146 | -0.011 | -0.0094 | -360.2142 | 17.4439 | -360.4912 | 17.6143 | -360.7897 | 18.1687 | -360.8327 | 17.5958 | -352.6906 | 18.7579 | -352.6537 | 16.834
12:40 | 4827 | 42.8739 | 202.4406 | 449.7956 | 456.7654 | -16.6917 | -40.1263 | 11.335 | 8.0763 | 2.3382 | 0.8138 | 3.364 | -0.9236 | 11.9065 | 4.7777 | 0.6169 | 0.6601 | 0.9589 | 0.7462 | -129.4914 | 0.2617 | 5.7954 | 1.921 | -2.7701 | -1.1301 | 4.7284 |  | 3.4243 | 0.4219 | 4.009 | 3.3675 | 3.3397 | 1.0808 | 10.7891 | 14.2916 | 14.8257 | 11.1013 | -0.0001 | -0.0031 | 0.0013 | 0.0039 | 0.0008 | 0.0002 | 0.0076 | -0.0213 | -0.0182 | -360.1711 | 17.4254 | -360.5066 | 17.6615 | -360.8727 | 18.2036 | -360.802 | 17.5527 | -352.6352 | 18.7353 | -352.6598 | 16.8792
12:40 | 4828 | 42.9842 | 202.5782 | 449.8443 | 456.7649 | -16.6621 | -40.1872 | 11.3827 | 8.0951 | 2.3173 | 0.7813 | 3.3639 | -0.9132 | 11.8594 | 4.7201 | 0.619 | 0.6626 | 0.9611 | 0.7458 | -129.4712 | 0.3057 | 5.6978 | 1.9107 | -2.8317 | -1.1183 | 4.5946 |  | 3.4429 | 0.3961 | 4.0106 | 3.3702 | 3.343 | 1.0812 | 10.7787 | 14.2754 | 14.856 | 11.085 | 0.0003 | -0.0031 | 0.0008 | 0.0037 | 0.0009 | -0.0005 | 0.0158 | -0.0001 | -0.0174 | -360.2173 | 17.4048 | -360.4019 | 17.6061 | -360.805 | 18.2179 | -360.9004 | 17.6061 | -352.6567 | 18.7128 | -352.6167 | 16.8217
12:40 | 4829 | 42.9462 | 202.4967 | 449.8782 | 456.7338 | -16.649 | -40.3073 | 11.348 | 8.0963 | 2.2783 | 0.6979 | 3.3666 | -0.9255 | 11.9078 | 4.7026 | 0.6173 | 0.665 | 0.9597 | 0.7451 | -129.4389 | 0.2766 | 5.7619 | 1.8911 | -2.8276 | -1.2021 | 4.5928 |  | 3.4771 | 0.3836 | 4.0096 | 3.3663 | 3.3356 | 1.0799 | 10.7661 | 14.2391 | 14.8572 | 11.0735 | -0.0001 | -0.0028 | 0.0005 | 0.0039 | 0 | -0.0005 | 0.0081 | -0.0146 | -0.0066 | -360.2265 | 17.4439 | -360.5189 | 17.643 | -360.8266 | 18.1748 | -360.8143 | 17.5712 | -352.6598 | 18.7703 | -352.6906 | 16.8464
12:40 | 4830 | 43.0354 | 202.6103 | 449.8985 | 456.7719 | -16.5944 | -40.2428 | 11.3581 | 8.1506 | 2.2287 | 0.843 | 3.3418 | -0.8915 | 11.8539 | 4.7617 | 0.6182 | 0.6609 | 0.9597 | 0.7462 | -129.428 | 0.284 | 5.6978 | 1.7185 | -2.8655 | -1.131 | 4.6153 |  | 3.4551 | 0.3824 | 4.0087 | 3.3673 | 3.339 | 1.0805 | 10.7603 | 14.2508 | 14.8351 | 11.0616 | -0.0003 | -0.0027 | 0.0013 | 0.0042 | 0.001 | -0.0008 | 0.0065 | -0.0172 | -0.0123 | -360.1311 | 17.4007 | -360.4604 | 17.6451 | -360.8635 | 18.2282 | -360.8358 | 17.565 | -352.586 | 18.7148 | -352.6537 | 16.8628
12:40 | 4831 | 42.9726 | 202.3377 | 449.9048 | 456.7377 | -16.5832 | -40.1338 | 11.4445 | 8.1582 | 2.3174 | 0.711 | 3.3563 | -0.9697 | 11.8436 | 4.7467 | 0.6177 | 0.6613 | 0.9596 | 0.7438 | -129.343 | 0.4214 | 5.8423 | 1.8732 | -2.8711 | -1.1567 | 4.6158 |  | 3.5251 | 0.4414 | 4.0098 | 3.3676 | 3.3388 | 1.0812 | 10.7383 | 14.2751 | 14.8191 | 11.0973 | 0.0002 | -0.003 | 0.0007 | 0.0038 | 0.0005 | -0.0008 | 0.0124 | -0.0067 | 0.0002 | -360.2512 | 17.4254 | -360.4358 | 17.6163 | -360.8143 | 18.2159 | -360.8727 | 17.6122 | -352.6813 | 18.7374 | -352.629 | 16.8197
12:40 | 4832 | 42.9404 | 202.359 | 449.9111 | 456.6739 | -16.5779 | -40.2214 | 11.3502 | 8.116 | 2.3512 | 0.659 | 3.3059 | -0.9979 | 11.8225 | 4.745 | 0.6176 | 0.6618 | 0.9616 | 0.7451 | -129.4004 | 0.3467 | 5.7349 | 1.9025 | -2.9181 | -1.0984 | 4.5855 |  | 3.4247 | 0.3696 | 4.0095 | 3.3656 | 3.3419 | 1.0809 | 10.7903 | 14.2753 | 14.8433 | 11.1028 | 0.0003 | -0.0029 | 0.0009 | 0.0041 | 0.0011 | -0.0004 | 0.009 | -0.0069 | -0.0188 | -360.1958 | 17.4274 | -360.5158 | 17.6677 | -360.8604 | 18.181 | -360.8112 | 17.5629 | -352.6229 | 18.7579 | -352.7306 | 16.8566
12:40 | 4833 | 42.9255 | 202.4371 | 449.9234 | 456.6643 | -16.6013 | -40.2359 | 11.3414 | 8.0939 | 2.2468 | 0.5508 | 3.2907 | -1.0593 | 11.8466 | 4.7586 | 0.618 | 0.6612 | 0.9611 | 0.7459 | -129.4306 | 0.2709 | 5.6468 | 1.9021 | -2.8436 | -1.2148 | 4.5712 |  | 3.3758 | 0.3766 | 4.0092 | 3.3667 | 3.3392 | 1.0817 | 10.8029 | 14.3233 | 14.8837 | 11.1197 | 0 | -0.0024 | 0.0012 | 0.0041 | 0.0008 | -0.0006 | 0.0266 | 0.0013 | -0.0028 | -360.1527 | 17.4028 | -360.4204 | 17.6348 | -360.8481 | 18.2569 | -360.8943 | 17.5855 | -352.6229 | 18.723 | -352.6383 | 16.8381
12:40 | 4834 | 42.9185 | 202.3946 | 449.8628 | 456.6711 | -16.5922 | -40.2202 | 11.384 | 8.1246 | 2.274 | 0.719 | 3.31 | -1.0245 | 11.8263 | 4.7697 | 0.6192 | 0.6641 | 0.9604 | 0.7459 | -129.4567 | 0.3173 | 5.62 | 1.922 | -2.8414 | -1.1375 | 4.6821 |  | 3.331 | 0.3401 | 4.0112 | 3.3679 | 3.3391 | 1.0802 | 10.8065 | 14.3088 | 14.842 | 11.1074 | -0.0004 | -0.0026 | 0.0006 | 0.0035 | 0.0008 | -0.0004 | 0.0077 | -0.0075 | -0.008 | -360.2173 | 17.4521 | -360.4789 | 17.6266 | -360.8081 | 18.2097 | -360.8174 | 17.5937 | -352.7152 | 18.76 | -352.6875 | 16.8299
12:40 | 4835 | 42.7623 | 202.3374 | 449.8797 | 456.6283 | -16.4482 | -40.158 | 11.4716 | 8.1603 | 2.3213 | 0.6923 | 3.3327 | -0.9107 | 11.8842 | 4.7344 | 0.6177 | 0.6607 | 0.9621 | 0.7453 | -129.4891 | 0.273 | 5.729 | 1.9303 | -2.8475 | -1.0895 | 4.6878 |  | 3.3223 | 0.2924 | 4.0087 | 3.365 | 3.335 | 1.0804 | 10.7938 | 14.273 | 14.8532 | 11.106 | 0.0002 | -0.0028 | 0.0006 | 0.0037 | 0.0007 | -0.0003 | -0.0005 | 0.0031 | 0.0194 | -360.1311 | 17.4131 | -360.5096 | 17.6656 | -360.8974 | 18.222 | -360.845 | 17.5588 | -352.6075 | 18.7312 | -352.6906 | 16.8669
12:40 | 4836 | 42.8609 | 202.3486 | 449.8455 | 456.7164 | -16.3897 | -40.1772 | 11.5529 | 8.109 | 2.2613 | 0.6658 | 3.2673 | -0.9661 | 11.7395 | 4.7105 | 0.6182 | 0.66 | 0.9609 | 0.743 | -129.5072 | 0.2177 | 5.6771 | 1.8842 | -2.785 | -1.1508 | 4.6081 |  | 3.3539 | 0.3386 | 4.008 | 3.3657 | 3.3389 | 1.0819 | 10.7972 | 14.2941 | 14.8816 | 11.0915 | 0.0001 | -0.0029 | 0.0005 | 0.0034 | 0.0006 | -0.0003 | 0.0222 | -0.004 | -0.0166 | -360.1804 | 17.4192 | -360.4204 | 17.6204 | -360.8112 | 18.2302 | -360.8666 | 17.604 | -352.6813 | 18.723 | -352.6229 | 16.834
12:40 | 4837 | 42.9157 | 202.4357 | 449.9742 | 456.8385 | -16.4631 | -40.1882 | 11.5256 | 8.094 | 2.3608 | 0.6996 | 3.2832 | -0.9723 | 11.8496 | 4.7037 | 0.6186 | 0.6627 | 0.9561 | 0.7444 | -129.4947 | 0.3753 | 5.7008 | 1.9722 | -2.6786 | -1.0915 | 4.6122 |  | 3.4268 | 0.3849 | 4.009 | 3.3663 | 3.3428 | 1.081 | 10.7454 | 14.241 | 14.822 | 11.0768 | -0.0003 | -0.003 | 0.0002 | 0.0039 | 0.0006 | -0.0011 | 0.0046 | -0.0084 | -0.0215 | -360.1896 | 17.4521 | -360.5096 | 17.6512 | -360.8604 | 18.1953 | -360.7958 | 17.5588 | -352.629 | 18.7682 | -352.7152 | 16.8587
12:40 | 4838 | 42.9286 | 202.3725 | 449.9515 | 456.7806 | -16.3965 | -40.1049 | 11.5175 | 8.13 | 2.3629 | 0.8227 | 3.2907 | -0.9046 | 11.8586 | 4.6574 | 0.6175 | 0.6639 | 0.9602 | 0.7455 | -129.5326 | 0.3532 | 5.6813 | 1.8498 | -2.7682 | -1.0961 | 4.5944 |  | 3.3945 | 0.3266 | 4.0105 | 3.3684 | 3.3382 | 1.0819 | 10.7671 | 14.2581 | 14.856 | 11.0619 | 0.0001 | -0.0023 | 0.0012 | 0.0041 | 0.0008 | 0.0001 | 0.0064 | -0.0002 | 0.0072 | -360.1619 | 17.4007 | -360.445 | 17.6389 | -360.8666 | 18.2446 | -360.8758 | 17.5794 | -352.6352 | 18.7087 | -352.629 | 16.8566
12:40 | 4839 | 42.9777 | 202.3862 | 449.9075 | 456.829 | -16.4507 | -40.2638 | 11.5136 | 8.1626 | 2.4529 | 0.7611 | 3.3021 | -0.9693 | 11.8249 | 4.6857 | 0.6185 | 0.6631 | 0.9606 | 0.746 | -129.4866 | 0.3249 | 5.6385 | 1.8194 | -2.8056 | -1.138 | 4.6876 |  | 3.5129 | 0.3961 | 4.0096 | 3.3685 | 3.3429 | 1.0814 | 10.78 | 14.2761 | 14.8079 | 11.0873 | -0.0002 | -0.0027 | 0.0007 | 0.0039 | 0.0011 | -0.0006 | 0.0146 | 0.0124 | -0.0121 | -360.2512 | 17.4562 | -360.4912 | 17.6143 | -360.8204 | 18.1994 | -360.8481 | 17.5732 | -352.6629 | 18.762 | -352.669 | 16.8443
12:40 | 4840 | 42.9432 | 202.3735 | 450.0465 | 456.7637 | -16.4358 | -40.2139 | 11.5046 | 8.1762 | 2.4279 | 0.7578 | 3.3206 | -0.9884 | 11.793 | 4.7381 | 0.6188 | 0.664 | 0.9617 | 0.7447 | -129.5554 | 0.3758 | 5.7676 | 1.954 | -2.8055 | -1.1536 | 4.7375 |  | 3.4272 | 0.2748 | 4.0102 | 3.3699 | 3.3407 | 1.0817 | 10.7903 | 14.2696 | 14.8734 | 11.1197 | 0.0002 | -0.0029 | 0.0003 | 0.0039 | 0.0012 | 0.0003 | 0.0097 | -0.0066 | -0.0041 | -360.1496 | 17.4131 | -360.5035 | 17.6615 | -360.8912 | 18.2138 | -360.8327 | 17.5465 | -352.6106 | 18.7292 | -352.6721 | 16.871
12:40 | 4841 | 43.0422 | 202.3964 | 449.9787 | 456.7377 | -16.3787 | -40.3046 | 11.3816 | 8.1372 | 2.4824 | 0.8249 | 3.3428 | -0.8971 | 11.8047 | 4.6785 | 0.6192 | 0.6631 | 0.9564 | 0.7443 | -129.6025 | 0.4636 | 5.7976 | 1.9454 | -2.7866 | -1.0203 | 4.7467 |  | 3.4825 | 0.2759 | 4.0085 | 3.3675 | 3.3417 | 1.0814 | 10.8122 | 14.2803 | 14.8683 | 11.1005 | -0.0001 | -0.0029 | 0.0009 | 0.0041 | 0.0013 | -0.0005 | 0.0138 | -0.0073 | -0.0102 | -360.2111 | 17.4151 | -360.4358 | 17.6204 | -360.8081 | 18.2261 | -360.9004 | 17.5937 | -352.6721 | 18.7189 | -352.6475 | 16.8279
12:40 | 4842 | 42.9869 | 202.2909 | 449.924 | 456.6861 | -16.5012 | -40.2483 | 11.398 | 8.1411 | 2.4721 | 0.7953 | 3.3415 | -0.8722 | 11.8095 | 4.7738 | 0.6177 | 0.6624 | 0.9608 | 0.7445 | -129.6129 | 0.406 | 5.7582 | 1.9553 | -2.7444 | -1.0697 | 4.712 |  | 3.484 | 0.263 | 4.0087 | 3.3653 | 3.3403 | 1.0814 | 10.8158 | 14.3295 | 14.9087 | 11.1457 | -0.0007 | -0.0027 | 0.0002 | 0.0034 | 0.0003 | -0.0002 | 0.0216 | 0.0049 | -0.0145 | -360.2204 | 17.4439 | -360.5281 | 17.6574 | -360.8389 | 18.1871 | -360.805 | 17.5568 | -352.6413 | 18.7723 | -352.6752 | 16.8484
12:40 | 4843 | 42.9149 | 202.3672 | 449.8874 | 456.6667 | -16.5524 | -40.2236 | 11.3675 | 8.0871 | 2.5317 | 0.7853 | 3.3431 | -0.7878 | 11.8519 | 4.8203 | 0.6187 | 0.6642 | 0.9628 | 0.7447 | -129.6828 | 0.3281 | 5.7897 | 1.904 | -2.7732 | -1.0984 | 4.665 |  | 3.4959 | 0.2182 | 4.009 | 3.3669 | 3.3392 | 1.0813 | 10.788 | 14.2962 | 14.8301 | 11.0771 | 0 | -0.0027 | 0.0011 | 0.0038 | 0.0008 | -0.0007 | 0.0214 | -0.0036 | -0.0223 | -360.1742 | 17.4028 | -360.4542 | 17.6492 | -360.8543 | 18.2446 | -360.8727 | 17.5609 | -352.6013 | 18.7312 | -352.6383 | 16.8566
12:40 | 4844 | 42.887 | 202.3936 | 449.9204 | 456.69 | -16.5678 | -40.2558 | 11.3386 | 8.1011 | 2.5193 | 0.8829 | 3.3369 | -0.8947 | 11.8501 | 4.7374 | 0.6194 | 0.6653 | 0.9603 | 0.7448 | -129.6721 | 0.2198 | 5.7672 | 1.9703 | -2.7135 | -1.0538 | 4.6991 |  | 3.5082 | 0.3568 | 4.0084 | 3.3661 | 3.3389 | 1.08 | 10.8076 | 14.287 | 14.8444 | 11.0908 | 0.0002 | -0.003 | 0.0011 | 0.0043 | 0.0008 | -0.0003 | 0.0122 | 0.0009 | -0.0176 | -360.245 | 17.4439 | -360.4727 | 17.6204 | -360.7866 | 18.2056 | -360.8635 | 17.5978 | -352.6721 | 18.7559 | -352.6567 | 16.8258
12:40 | 4845 | 42.8834 | 202.4497 | 449.8912 | 456.696 | -16.5659 | -40.2648 | 11.4253 | 8.06 | 2.5182 | 0.8194 | 3.3552 | -0.8889 | 11.7976 | 4.739 | 0.6182 | 0.6607 | 0.9631 | 0.7448 | -129.753 | 0.2507 | 5.7147 | 1.9868 | -2.727 | -0.9713 | 4.7181 |  | 3.4867 | 0.3494 | 4.01 | 3.3707 | 3.3416 | 1.0824 | 10.7453 | 14.2587 | 14.8415 | 11.0819 | 0 | -0.0031 | 0.0006 | 0.0041 | 0.0007 | -0.0005 | 0.0075 | -0.0163 | -0.0214 | -360.1527 | 17.4254 | -360.5189 | 17.6759 | -360.8881 | 18.2118 | -360.8389 | 17.5568 | -352.626 | 18.7518 | -352.6875 | 16.8669
12:40 | 4846 | 43.0323 | 202.4644 | 449.9252 | 456.6844 | -16.5306 | -40.2423 | 11.4968 | 8.1114 | 2.4727 | 0.9649 | 3.3181 | -0.9457 | 11.8376 | 4.7694 | 0.619 | 0.6609 | 0.961 | 0.7449 | -129.7234 | 0.2686 | 5.7722 | 1.9455 | -2.7741 | -1.037 | 4.6523 |  | 3.4346 | 0.2931 | 4.0091 | 3.3691 | 3.3441 | 1.08 | 10.7511 | 14.2646 | 14.8079 | 11.0641 | -0.0002 | -0.0028 | 0.0011 | 0.0041 | 0.0002 | -0.0012 | 0.0233 | -0.0036 | 0.0007 | -360.1804 | 17.3925 | -360.405 | 17.6307 | -360.7927 | 18.2302 | -360.9127 | 17.6061 | -352.6475 | 18.7271 | -352.5952 | 16.8217
12:40 | 4847 | 42.9841 | 202.3695 | 449.8009 | 456.632 | -16.5069 | -40.2559 | 11.4273 | 8.0943 | 2.4592 | 0.8618 | 3.3019 | -0.9037 | 11.8797 | 4.8416 | 0.6177 | 0.6611 | 0.9612 | 0.7458 | -129.6931 | 0.3754 | 5.733 | 1.932 | -2.8258 | -0.9814 | 4.6614 |  | 3.509 | 0.3091 | 4.0086 | 3.3673 | 3.3409 | 1.0811 | 10.7857 | 14.2996 | 14.8447 | 11.1038 | -0.0002 | -0.0024 | 0.0005 | 0.0042 | 0.0006 | -0.0003 | 0.005 | -0.0162 | -0.0068 | -360.2388 | 17.4562 | -360.5158 | 17.6492 | -360.8358 | 18.1912 | -360.8204 | 17.5876 | -352.6752 | 18.7744 | -352.6998 | 16.8505
12:41 | 4848 | 43.0422 | 202.4278 | 449.8162 | 456.6292 | -16.5589 | -40.1722 | 11.3767 | 8.105 | 2.4423 | 0.8331 | 3.3526 | -0.9101 | 11.9069 | 4.775 | 0.6184 | 0.6634 | 0.9582 | 0.7457 | -129.7506 | 0.2675 | 5.6875 | 1.9264 | -2.8376 | -1.1572 | 4.6886 |  | 3.3861 | 0.2587 | 4.0086 | 3.3662 | 3.341 | 1.0814 | 10.7857 | 14.2764 | 14.8621 | 11.0865 | 0 | -0.0034 | 0.0005 | 0.0034 | 0.0012 | -0.0005 | 0.0087 | 0 | -0.0139 | -360.1373 | 17.3987 | -360.4819 | 17.6677 | -360.8727 | 18.2405 | -360.8727 | 17.5712 | -352.5952 | 18.7312 | -352.6475 | 16.8587
12:41 | 4849 | 42.9393 | 202.4429 | 449.7557 | 456.624 | -16.513 | -40.1951 | 11.3667 | 8.1016 | 2.3873 | 0.8713 | 3.3003 | -1.0263 | 11.785 | 4.6534 | 0.6191 | 0.6665 | 0.963 | 0.7462 | -129.7291 | 0.4082 | 5.7313 | 1.8248 | -2.9073 | -1.1055 | 4.5739 |  | 3.5293 | 0.3342 | 4.01 | 3.369 | 3.3407 | 1.081 | 10.7925 | 14.3244 | 14.8377 | 11.1153 | 0.0002 | -0.003 | 0.0011 | 0.0039 | 0.0006 | -0.0002 | -0.0043 | -0.0053 | -0.0135 | -360.2481 | 17.4377 | -360.4358 | 17.6225 | -360.805 | 18.2036 | -360.8727 | 17.6061 | -352.7029 | 18.7538 | -352.6444 | 16.8135
12:41 | 4850 | 42.9978 | 202.4447 | 449.8578 | 456.6522 | -16.6079 | -40.3641 | 11.2364 | 8.1702 | 2.4363 | 1.0414 | 3.2857 | -0.9171 | 11.8594 | 4.7034 | 0.6193 | 0.6625 | 0.9628 | 0.7477 | -129.7024 | 0.3855 | 5.815 | 1.8563 | -2.8397 | -1.1008 | 4.5656 |  | 3.4572 | 0.3668 | 4.0087 | 3.3663 | 3.3393 | 1.0823 | 10.8168 | 14.2965 | 14.8959 | 11.1284 | -0.0001 | -0.0025 | 0.0006 | 0.0034 | 0.0007 | -0.0003 | 0.0116 | -0.0158 | -0.0145 | -360.1742 | 17.4336 | -360.5096 | 17.6594 | -360.8666 | 18.2077 | -360.8143 | 17.5465 | -352.6167 | 18.7497 | -352.706 | 16.8628
12:41 | 4851 | 42.9833 | 202.4976 | 449.8775 | 456.6959 | -16.5763 | -40.3381 | 11.2985 | 8.1491 | 2.4958 | 0.9143 | 3.2465 | -0.9026 | 11.8932 | 4.6934 | 0.6177 | 0.6618 | 0.9621 | 0.7457 | -129.7039 | 0.535 | 5.7993 | 1.8549 | -2.8737 | -1.0856 | 4.6574 |  | 3.5254 | 0.3856 | 4.0096 | 3.3671 | 3.3363 | 1.0804 | 10.7811 | 14.289 | 14.8855 | 11.0995 | -0.0005 | -0.0029 | 0.0008 | 0.004 | 0.0004 | -0.0004 | 0 | -0.0074 | -0.0012 | -360.1958 | 17.3905 | -360.4019 | 17.6184 | -360.8235 | 18.2467 | -360.885 | 17.5753 | -352.6567 | 18.7107 | -352.6167 | 16.8279
12:41 | 4852 | 42.9557 | 202.486 | 450.0082 | 456.6619 | -16.5476 | -40.3427 | 11.3674 | 8.2173 | 2.4686 | 1.0091 | 3.3822 | -0.8535 | 11.8818 | 4.7286 | 0.618 | 0.6601 | 0.9637 | 0.7453 | -129.7554 | 0.4677 | 5.7848 | 1.8906 | -2.8612 | -1.157 | 4.6171 |  | 3.5194 | 0.3182 | 4.0081 | 3.3661 | 3.335 | 1.0804 | 10.8018 | 14.2815 | 14.8871 | 11.0843 | 0.0001 | -0.0026 | 0.0008 | 0.0041 | 0.0009 | -0.0002 | 0.0277 | -0.0127 | -0.0029 | -360.2327 | 17.4521 | -360.5035 | 17.6369 | -360.8174 | 18.1933 | -360.8358 | 17.5691 | -352.7183 | 18.7764 | -352.7029 | 16.834
12:41 | 4853 | 42.974 | 202.4377 | 449.8893 | 456.7318 | -16.3914 | -40.2223 | 11.4324 | 8.0773 | 2.4502 | 1.0991 | 3.3068 | -0.7821 | 11.8958 | 4.7713 | 0.6183 | 0.6603 | 0.9609 | 0.7448 | -129.7417 | 0.3503 | 5.7136 | 1.8896 | -2.8173 | -1.0998 | 4.5393 |  | 3.463 | 0.3796 | 4.0088 | 3.3655 | 3.3386 | 1.0823 | 10.7638 | 14.2947 | 14.8497 | 11.0941 | 0 | -0.0033 | 0.0006 | 0.0039 | 0.0001 | -0.0003 | 0.0058 | -0.0011 | -0.0171 | -360.1496 | 17.4048 | -360.4758 | 17.6533 | -360.885 | 18.2364 | -360.8389 | 17.5465 | -352.5829 | 18.7374 | -352.6567 | 16.8751
12:41 | 4854 | 43.0104 | 202.443 | 450.021 | 456.7986 | -16.4073 | -40.0765 | 11.469 | 8.0988 | 2.4451 | 1.0099 | 3.3399 | -0.8384 | 11.9221 | 4.7218 | 0.6185 | 0.6613 | 0.9583 | 0.7449 | -129.7361 | 0.3314 | 5.7345 | 1.8429 | -2.8257 | -1.128 | 4.51 |  | 3.4044 | 0.3192 | 4.0085 | 3.3658 | 3.3398 | 1.0815 | 10.7499 | 14.2576 | 14.8354 | 11.0688 | -0.0001 | -0.0029 | 0.0011 | 0.0041 | 0.0007 | -0.0013 | 0.0171 | -0.0049 | -0.0036 | -360.2111 | 17.4151 | -360.4604 | 17.6245 | -360.7773 | 18.2261 | -360.9251 | 17.6102 | -352.6967 | 18.7497 | -352.6198 | 16.8197
12:41 | 4855 | 43.047 | 202.4729 | 449.9531 | 456.6834 | -16.3766 | -40.0681 | 11.5011 | 8.0212 | 2.4046 | 0.7815 | 3.2246 | -0.8145 | 11.8974 | 4.7484 | 0.6173 | 0.6601 | 0.9595 | 0.7454 | -129.7757 | 0.3997 | 5.6978 | 1.7628 | -2.8705 | -1.1453 | 4.519 |  | 3.4874 | 0.2631 | 4.0089 | 3.3665 | 3.3399 | 1.0815 | 10.7544 | 14.2569 | 14.8372 | 11.084 | 0.0001 | -0.0023 | 0.0009 | 0.0042 | 0.0004 | -0.0006 | 0.0165 | -0.0071 | -0.0014 | -360.1865 | 17.4377 | -360.5127 | 17.6574 | -360.8758 | 18.1912 | -360.8235 | 17.5629 | -352.6321 | 18.7723 | -352.7183 | 16.8587
12:41 | 4856 | 43.0693 | 202.4708 | 450.0261 | 456.7104 | -16.4003 | -40.0742 | 11.4842 | 8.1276 | 2.3835 | 0.7215 | 3.2111 | -0.8821 | 11.8428 | 4.7186 | 0.6178 | 0.6648 | 0.9592 | 0.7469 | -129.7457 | 0.4071 | 5.7258 | 1.8083 | -2.8744 | -1.2467 | 4.5377 |  | 3.4097 | 0.197 | 4.0097 | 3.3699 | 3.3387 | 1.0827 | 10.8099 | 14.3126 | 14.8598 | 11.1099 | 0.0001 | -0.0031 | 0.0006 | 0.0034 | 0.0007 | -0.0008 | -0.0048 | -0.0058 | 0.0049 | -360.1711 | 17.3946 | -360.4327 | 17.6348 | -360.8666 | 18.2569 | -360.9158 | 17.5814 | -352.626 | 18.7251 | -352.6229 | 16.8484
12:41 | 4857 | 42.9567 | 202.4196 | 449.8071 | 456.7201 | -16.5187 | -40.2004 | 11.3427 | 8.1459 | 2.4517 | 0.8464 | 3.3145 | -0.9177 | 11.8171 | 4.6953 | 0.617 | 0.6633 | 0.9624 | 0.7466 | -129.7187 | 0.4801 | 5.7885 | 1.7954 | -2.771 | -1.2202 | 4.5103 |  | 3.461 | 0.3836 | 4.0094 | 3.3668 | 3.3399 | 1.0812 | 10.7926 | 14.2893 | 14.8471 | 11.093 | 0.0004 | -0.0029 | 0.001 | 0.0037 | 0.0006 | -0.0004 | 0.0072 | -0.0189 | -0.0177 | -360.2235 | 17.45 | -360.485 | 17.6225 | -360.8235 | 18.1953 | -360.8297 | 17.5814 | -352.6813 | 18.7785 | -352.6937 | 16.8381
12:41 | 4858 | 43.0111 | 202.4826 | 449.9096 | 456.756 | -16.4792 | -40.2847 | 11.3875 | 8.1313 | 2.5313 | 0.7586 | 3.3594 | -0.8397 | 11.8672 | 4.7824 | 0.6179 | 0.6607 | 0.9611 | 0.7469 | -129.7358 | 0.4137 | 5.6652 | 1.8532 | -2.8164 | -1.0794 | 4.5343 |  | 3.415 | 0.3186 | 4.0101 | 3.3671 | 3.3394 | 1.0804 | 10.811 | 14.314 | 14.8854 | 11.1106 | 0.0001 | -0.0028 | 0.0001 | 0.0029 | 0.0005 | -0.0004 | 0.0094 | 0.0084 | -0.0166 | -360.1311 | 17.4172 | -360.4819 | 17.6677 | -360.8943 | 18.2118 | -360.8389 | 17.5486 | -352.6106 | 18.7497 | -352.6906 | 16.8751
12:41 | 4859 | 42.9747 | 202.4621 | 449.8572 | 456.7462 | -16.4171 | -40.2573 | 11.4205 | 8.131 | 2.5632 | 0.9118 | 3.3056 | -0.8496 | 11.9162 | 4.7397 | 0.6181 | 0.665 | 0.9631 | 0.7459 | -129.7159 | 0.3482 | 5.7476 | 1.6688 | -2.8104 | -1.1252 | 4.574 |  | 3.5394 | 0.2947 | 4.0087 | 3.3656 | 3.341 | 1.0816 | 10.7672 | 14.2809 | 14.8423 | 11.0858 | -0.0002 | -0.0021 | 0.0009 | 0.0037 | 0.001 | -0.0007 | 0.0053 | 0.001 | -0.0151 | -360.205 | 17.4131 | -360.4389 | 17.6266 | -360.8174 | 18.2364 | -360.9004 | 17.5999 | -352.669 | 18.7312 | -352.6167 | 16.8402
12:41 | 4860 | 42.9553 | 202.4979 | 449.9655 | 456.8048 | -16.4314 | -40.1735 | 11.3998 | 8.1392 | 2.3947 | 0.8761 | 3.2813 | -0.8322 | 11.8533 | 4.708 | 0.6185 | 0.6636 | 0.9622 | 0.7462 | -129.7537 | 0.3593 | 5.7468 | 1.737 | -2.7651 | -1.1167 | 4.5407 |  | 3.4525 | 0.2833 | 4.0088 | 3.364 | 3.3382 | 1.0805 | 10.7868 | 14.272 | 14.8298 | 11.0872 | -0.0001 | -0.0028 | 0.0011 | 0.0045 | 0.0006 | 0.0003 | 0.0111 | -0.0134 | -0.0104 | -360.1927 | 17.4459 | -360.5127 | 17.6512 | -360.8266 | 18.1974 | -360.802 | 17.5629 | -352.6383 | 18.7723 | -352.666 | 16.8607
12:41 | 4861 | 43.0111 | 202.412 | 449.8792 | 456.8031 | -16.3644 | -40.261 | 11.4574 | 8.0132 | 2.413 | 0.8606 | 3.3281 | -0.8511 | 11.8405 | 4.7493 | 0.6184 | 0.6659 | 0.9581 | 0.7456 | -129.6501 | 0.3818 | 5.7288 | 1.7115 | -2.7768 | -1.1481 | 4.5829 |  | 3.5117 | 0.4086 | 4.01 | 3.3655 | 3.3398 | 1.0806 | 10.7556 | 14.2695 | 14.8723 | 11.1085 | 0.0004 | -0.0027 | 0.0005 | 0.004 | 0.0012 | -0.0006 | 0.0154 | 0.0013 | -0.0051 | -360.1865 | 17.4048 | -360.4481 | 17.6471 | -360.8789 | 18.2364 | -360.8635 | 17.5773 | -352.586 | 18.7292 | -352.6444 | 16.8546
12:41 | 4862 | 43.0175 | 202.3755 | 449.846 | 456.8015 | -16.4486 | -40.1763 | 11.3987 | 8.1377 | 2.4122 | 0.9085 | 3.3377 | -0.8413 | 11.8794 | 4.7183 | 0.6181 | 0.6627 | 0.96 | 0.7458 | -129.7005 | 0.2879 | 5.826 | 1.7999 | -2.7251 | -1.1734 | 4.5952 |  | 3.47 | 0.404 | 4.0101 | 3.3698 | 3.3395 | 1.0816 | 10.7672 | 14.2346 | 14.8365 | 11.0627 | -0.0001 | -0.0028 | 0.0016 | 0.0049 | 0.0005 | -0.0003 | 0.0128 | -0.0037 | -0.0198 | -360.2204 | 17.4459 | -360.4758 | 17.6204 | -360.8081 | 18.2056 | -360.8943 | 17.5937 | -352.6967 | 18.76 | -352.6721 | 16.8299
12:41 | 4863 | 43.0063 | 202.4909 | 449.8771 | 456.7533 | -16.5279 | -40.1514 | 11.3462 | 8.1419 | 2.3191 | 0.9086 | 3.3273 | -0.8875 | 11.8881 | 4.8387 | 0.6192 | 0.6589 | 0.9621 | 0.7461 | -129.5734 | 0.4523 | 5.8608 | 1.8106 | -2.6752 | -1.1161 | 4.5874 |  | 3.4624 | 0.3257 | 4.0107 | 3.3678 | 3.3364 | 1.0804 | 10.7844 | 14.2931 | 14.835 | 11.0785 | -0.0002 | -0.0027 | 0.0012 | 0.0041 | 0.0015 | -0.0004 | 0.0134 | 0.0012 | -0.0038 | -360.1619 | 17.4295 | -360.5066 | 17.6697 | -360.8912 | 18.2036 | -360.8358 | 17.5629 | -352.6229 | 18.7579 | -352.6998 | 16.8751
12:41 | 4864 | 43.0312 | 202.5233 | 450.0233 | 456.8091 | -16.4888 | -40.1556 | 11.4398 | 8.082 | 2.3579 | 0.8575 | 3.2881 | -0.8834 | 11.9526 | 4.7678 | 0.6184 | 0.6594 | 0.9579 | 0.7435 | -129.5635 | 0.362 | 5.8779 | 1.8281 | -2.7575 | -1.1625 | 4.6066 |  | 3.4497 | 0.3326 | 4.0101 | 3.3675 | 3.3398 | 1.0815 | 10.7614 | 14.2867 | 14.8481 | 11.0858 | -0.0002 | -0.0028 | 0.0004 | 0.0036 | 0.0005 | -0.0006 | 0.0038 | -0.014 | -0.0083 | -360.1742 | 17.3884 | -360.4142 | 17.6307 | -360.8358 | 18.2344 | -360.8912 | 17.5855 | -352.6413 | 18.7353 | -352.6136 | 16.8443
12:41 | 4865 | 43.0359 | 202.5862 | 449.9882 | 456.8804 | -16.4619 | -40.2472 | 11.4744 | 8.1405 | 2.4027 | 0.8228 | 3.3141 | -0.7508 | 11.9741 | 4.7805 | 0.6176 | 0.6609 | 0.9596 | 0.7445 | -129.719 | 0.4098 | 5.877 | 1.7209 | -2.8085 | -1.1612 | 4.5449 |  | 3.4218 | 0.1876 | 4.0099 | 3.3683 | 3.3399 | 1.0815 | 10.8007 | 14.303 | 14.8651 | 11.0959 | 0 | -0.0034 | 0.0008 | 0.0036 | 0.0012 | -0.0007 | -0.0022 | -0.0042 | -0.0027 | -360.2481 | 17.4439 | -360.5035 | 17.6389 | -360.8174 | 18.1871 | -360.8235 | 17.5773 | -352.6813 | 18.7826 | -352.6875 | 16.8443
12:41 | 4866 | 42.9819 | 202.5378 | 449.9797 | 456.868 | -16.4097 | -40.1741 | 11.4472 | 8.1193 | 2.4485 | 0.8832 | 3.3499 | -0.7164 | 11.9187 | 4.7291 | 0.6177 | 0.6636 | 0.966 | 0.7449 | -129.7191 | 0.4084 | 5.8755 | 1.9115 | -2.9071 | -1.1637 | 4.6014 |  | 3.5306 | 0.3379 | 4.0103 | 3.3678 | 3.3397 | 1.0802 | 10.8122 | 14.3033 | 14.8615 | 11.1183 | -0.0001 | -0.0028 | 0.001 | 0.0035 | 0.0009 | -0.0003 | 0.0237 | 0.0038 | 0.0077 | -360.1527 | 17.4028 | -360.4481 | 17.6471 | -360.8635 | 18.2323 | -360.8574 | 17.565 | -352.6198 | 18.7312 | -352.6598 | 16.8587
12:41 | 4867 | 43.015 | 202.5223 | 449.9658 | 456.7924 | -16.3852 | -40.185 | 11.5199 | 8.0848 | 2.386 | 0.8658 | 3.3086 | -0.7643 | 11.9178 | 4.7626 | 0.6196 | 0.66 | 0.9617 | 0.7455 | -129.6298 | 0.4121 | 5.7183 | 1.9597 | -2.7962 | -1.1661 | 4.6324 |  | 3.492 | 0.237 | 4.0093 | 3.3672 | 3.3405 | 1.0804 | 10.7868 | 14.2834 | 14.8634 | 11.0702 | -0.0003 | -0.0025 | 0.0009 | 0.0041 | 0.0008 | -0.0005 | -0.0053 | -0.0137 | -0.0171 | -360.2327 | 17.4172 | -360.445 | 17.6102 | -360.8081 | 18.2097 | -360.8758 | 17.5999 | -352.6721 | 18.7538 | -352.6321 | 16.8299
12:41 | 4868 | 43.0065 | 202.4956 | 449.976 | 456.9055 | -16.4575 | -40.1838 | 11.4839 | 8.1226 | 2.3876 | 0.7166 | 3.3041 | -0.7857 | 11.8999 | 4.7889 | 0.6187 | 0.6622 | 0.9651 | 0.7445 | -129.6506 | 0.4233 | 5.662 | 1.9776 | -2.765 | -1.0531 | 4.6781 |  | 3.4404 | 0.2614 | 4.0081 | 3.3693 | 3.3386 | 1.0813 | 10.7903 | 14.3043 | 14.8734 | 11.1082 | -0.0004 | -0.0029 | 0.001 | 0.0045 | 0.0009 | -0.0006 | 0.0058 | -0.0001 | -0.0124 | -360.1711 | 17.4295 | -360.5158 | 17.6492 | -360.8543 | 18.2118 | -360.8204 | 17.565 | -352.6413 | 18.7559 | -352.6967 | 16.8669
12:41 | 4869 | 43.0456 | 202.5765 | 449.9387 | 456.9028 | -16.5693 | -40.1379 | 11.4916 | 8.1056 | 2.4163 | 0.808 | 3.3386 | -0.8149 | 11.908 | 4.755 | 0.6182 | 0.6603 | 0.9642 | 0.7467 | -129.6743 | 0.4487 | 5.6876 | 1.9941 | -2.7592 | -1.1025 | 4.6839 |  | 3.4653 | 0.4189 | 4.0096 | 3.3695 | 3.3379 | 1.0823 | 10.8191 | 14.3279 | 14.8997 | 11.107 | 0.0003 | -0.003 | 0.001 | 0.004 | 0.0009 | -0.0004 | 0.0178 | 0.0012 | -0.0076 | -360.1465 | 17.3925 | -360.4142 | 17.6143 | -360.8204 | 18.2364 | -360.8912 | 17.5753 | -352.6229 | 18.7271 | -352.6413 | 16.8443
12:41 | 4870 | 42.9859 | 202.5935 | 449.9119 | 456.7568 | -16.4965 | -40.1828 | 11.4827 | 8.1283 | 2.4903 | 0.8139 | 3.4022 | -0.8896 | 11.918 | 4.6908 | 0.6173 | 0.6584 | 0.9605 | 0.7457 | -129.6177 | 0.3845 | 5.5993 | 1.9828 | -2.759 | -1.0758 | 4.6524 |  | 3.4217 | 0.3814 | 4.0084 | 3.3696 | 3.3401 | 1.0811 | 10.7962 | 14.2809 | 14.8828 | 11.0973 | -0.0005 | -0.0034 | 0.0007 | 0.0038 | 0.001 | -0.0003 | 0.0085 | -0.0076 | -0.0028 | -360.2388 | 17.4459 | -360.4666 | 17.6184 | -360.7866 | 18.1933 | -360.842 | 17.5835 | -352.6783 | 18.7661 | -352.6844 | 16.8464
12:41 | 4871 | 43.0879 | 202.5384 | 449.9065 | 456.9223 | -16.4483 | -40.1229 | 11.468 | 8.1419 | 2.5278 | 0.9038 | 3.4674 | -0.8875 | 11.985 | 4.8471 | 0.6184 | 0.6619 | 0.9621 | 0.7464 | -129.5582 | 0.4087 | 5.5683 | 1.8568 | -2.7749 | -1.1898 | 4.6316 |  | 3.4174 | 0.2192 | 4.0098 | 3.3694 | 3.3414 | 1.0815 | 10.781 | 14.2489 | 14.8356 | 11.0468 | 0.0001 | -0.0024 | 0.0009 | 0.0037 | 0.0008 | -0.0001 | 0.0065 | -0.0152 | -0.0015 | -360.1219 | 17.3925 | -360.445 | 17.6348 | -360.8297 | 18.2138 | -360.8481 | 17.5568 | -352.6075 | 18.7353 | -352.6506 | 16.8525
12:41 | 4872 | 43.1431 | 202.5549 | 449.9423 | 456.9735 | -16.4511 | -40.0817 | 11.4236 | 8.0883 | 2.4852 | 0.8368 | 3.4015 | -0.8802 | 11.9321 | 4.7922 | 0.6179 | 0.6592 | 0.9618 | 0.7455 | -129.6473 | 0.4109 | 5.5607 | 1.9898 | -2.76 | -1.132 | 4.6262 |  | 3.458 | 0.1978 | 4.0102 | 3.3721 | 3.3403 | 1.0815 | 10.8019 | 14.2867 | 14.8307 | 11.1031 | -0.0002 | -0.0028 | 0.0006 | 0.0036 | 0.0012 | -0.0005 | 0.0097 | -0.0109 | 0.0112 | -360.1681 | 17.4028 | -360.4142 | 17.5978 | -360.7897 | 18.1994 | -360.8543 | 17.5917 | -352.666 | 18.7292 | -352.6321 | 16.8279
12:41 | 4873 | 42.9939 | 202.4521 | 449.8398 | 456.9157 | -16.4075 | -40.0602 | 11.4318 | 8.0772 | 2.3833 | 0.7582 | 3.3422 | -0.8262 | 11.935 | 4.7426 | 0.6179 | 0.6633 | 0.9651 | 0.7457 | -129.6705 | 0.3736 | 5.6161 | 1.9989 | -2.7514 | -1.0913 | 4.6741 |  | 3.481 | 0.3637 | 4.0101 | 3.3729 | 3.3424 | 1.0817 | 10.8111 | 14.2905 | 14.8601 | 11.0883 | 0.0004 | -0.0031 | 0.0008 | 0.0039 | 0.0008 | 0.0001 | 0.0103 | 0.0002 | -0.0056 | -360.1619 | 17.3987 | -360.4266 | 17.6081 | -360.7712 | 18.1769 | -360.7743 | 17.5506 | -352.6352 | 18.7271 | -352.6321 | 16.8381
12:41 | 4874 | 43.0584 | 202.5267 | 450.0736 | 456.9809 | -16.4512 | -40.1619 | 11.4882 | 7.9636 | 2.4602 | 0.7643 | 3.3504 | -0.9137 | 11.8667 | 4.7104 | 0.6184 | 0.6655 | 0.9633 | 0.7455 | -129.6117 | 0.2947 | 5.6432 | 1.9269 | -2.682 | -1.0302 | 4.7035 |  | 3.4974 | 0.3713 | 4.0096 | 3.3663 | 3.3414 | 1.0817 | 10.7892 | 14.2567 | 14.8593 | 11.0959 | 0.0004 | -0.0028 | 0.0007 | 0.0039 | 0.0011 | -0.0007 | 0.0155 | -0.0115 | -0.0067 | -360.1219 | 17.3761 | -360.3896 | 17.6225 | -360.7927 | 18.2077 | -360.8358 | 17.5424 | -352.6044 | 18.7025 | -352.5952 | 16.8361
12:41 | 4875 | 42.9763 | 202.435 | 449.9309 | 456.7946 | -16.4455 | -40.1375 | 11.4096 | 7.9658 | 2.4573 | 0.7209 | 3.2672 | -0.8227 | 11.9685 | 4.7782 | 0.6201 | 0.6659 | 0.9615 | 0.7465 | -129.6816 | 0.2948 | 5.6452 | 1.8676 | -2.7944 | -1.1441 | 4.5728 |  | 3.4906 | 0.4274 | 4.0102 | 3.3676 | 3.34 | 1.081 | 10.809 | 14.2644 | 14.8126 | 11.0992 | -0.0004 | -0.0031 | 0.0007 | 0.0038 | 0.0003 | -0.0005 | 0.0244 | -0.0013 | 0.0061 | -360.1742 | 17.3946 | -360.3927 | 17.602 | -360.7527 | 18.1769 | -360.805 | 17.5568 | -352.626 | 18.7251 | -352.6136 | 16.8156
12:41 | 4876 | 42.9497 | 202.3506 | 449.8815 | 456.8475 | -16.4823 | -40.2277 | 11.4338 | 7.9397 | 2.4013 | 0.7598 | 3.2321 | -0.9202 | 11.9613 | 4.765 | 0.6197 | 0.6615 | 0.9639 | 0.7474 | -129.6759 | 0.3768 | 5.6881 | 1.8882 | -2.7735 | -1.1937 | 4.6423 |  | 3.5253 | 0.3328 | 4.0108 | 3.3693 | 3.3422 | 1.0801 | 10.8097 | 14.3015 | 14.8572 | 11.1204 | 0.0001 | -0.0021 | 0.0013 | 0.0045 | 0.001 | -0.0007 | 0.0066 | 0.0006 | -0.0048 | -360.125 | 17.3925 | -360.4358 | 17.6369 | -360.8081 | 18.1789 | -360.7804 | 17.5383 | -352.5952 | 18.723 | -352.6383 | 16.8423
12:41 | 4877 | 42.9585 | 202.4212 | 450.0481 | 456.8988 | -16.4512 | -40.1278 | 11.505 | 8.1402 | 2.5161 | 0.7143 | 3.3216 | -0.8598 | 12.0298 | 4.8613 | 0.6189 | 0.6601 | 0.9597 | 0.7448 | -129.6986 | 0.294 | 5.6652 | 1.8707 | -2.768 | -1.1159 | 4.578 |  | 3.497 | 0.3685 | 4.0099 | 3.3668 | 3.3405 | 1.0827 | 10.8157 | 14.2836 | 14.8761 | 11.1103 | 0.0002 | -0.0029 | 0.0005 | 0.0038 | 0.0008 | 0.0002 | 0.0194 | -0.001 | -0.0022 | -360.1311 | 17.3699 | -360.3742 | 17.6184 | -360.7866 | 18.2036 | -360.802 | 17.5506 | -352.5952 | 18.7025 | -352.5983 | 16.8381
12:41 | 4878 | 42.9567 | 202.5131 | 449.9934 | 456.7816 | -16.4107 | -40.1463 | 11.5196 | 8.1248 | 2.5098 | 0.8433 | 3.3681 | -0.8188 | 11.9467 | 4.7611 | 0.6186 | 0.6656 | 0.9638 | 0.7468 | -129.6839 | 0.2433 | 5.5766 | 1.8706 | -2.7878 | -1.3038 | 4.6409 |  | 3.5652 | 0.4338 | 4.0099 | 3.3669 | 3.3385 | 1.0825 | 10.8088 | 14.2882 | 14.8689 | 11.0861 | 0.0002 | -0.0027 | 0.0008 | 0.0037 | 0.0012 | -0.0006 | 0.0358 | -0.0157 | 0.0108 | -360.2019 | 17.3987 | -360.4235 | 17.6122 | -360.7373 | 18.1851 | -360.7989 | 17.5547 | -352.6075 | 18.7312 | -352.6167 | 16.8279
12:41 | 4879 | 42.9487 | 202.3724 | 449.9937 | 456.8174 | -16.4315 | -40.084 | 11.5014 | 8.1338 | 2.4019 | 0.8167 | 3.327 | -0.867 | 11.8593 | 4.7322 | 0.6193 | 0.6634 | 0.9613 | 0.7464 | -129.7247 | 0.3856 | 5.699 | 1.9133 | -2.8103 | -1.1812 | 4.6363 |  | 3.5507 | 0.4536 | 4.0089 | 3.3678 | 3.3365 | 1.0815 | 10.7972 | 14.2883 | 14.8816 | 11.1089 | 0.0001 | -0.0025 | 0.0011 | 0.0042 | 0.0004 | -0.0005 | 0.0065 | -0.0126 | -0.0141 | -360.1096 | 17.3905 | -360.3927 | 17.6328 | -360.8081 | 18.1871 | -360.802 | 17.5404 | -352.5644 | 18.7107 | -352.6136 | 16.8381
12:41 | 4880 | 42.9595 | 202.3885 | 449.9225 | 456.7743 | -16.4091 | -40.0864 | 11.425 | 8.0403 | 2.3895 | 0.7715 | 3.2494 | -0.7983 | 12.0132 | 4.6853 | 0.6195 | 0.6629 | 0.9605 | 0.7453 | -129.7424 | 0.3023 | 5.57 | 1.9026 | -2.7609 | -1.0879 | 4.6469 |  | 3.4849 | 0.3403 | 4.0104 | 3.3667 | 3.3371 | 1.0817 | 10.8008 | 14.2796 | 14.8398 | 11.1024 | -0.0002 | -0.0027 | 0.0002 | 0.0031 | 0.0005 | -0.0007 | 0.0159 | -0.0021 | -0.0264 | -360.1927 | 17.4048 | -360.4142 | 17.6245 | -360.7866 | 18.1892 | -360.8543 | 17.5691 | -352.6352 | 18.7128 | -352.5921 | 16.8217
12:41 | 4881 | 42.9932 | 202.457 | 449.921 | 456.8204 | -16.5157 | -40.1982 | 11.3478 | 8.0447 | 2.4768 | 0.76 | 3.3337 | -0.8575 | 12.0242 | 4.7321 | 0.6189 | 0.6637 | 0.9615 | 0.7447 | -129.7661 | 0.238 | 5.5289 | 1.8337 | -2.8311 | -1.2275 | 4.5834 |  | 3.4638 | 0.2146 | 4.0103 | 3.3665 | 3.3361 | 1.0821 | 10.7625 | 14.2591 | 14.8042 | 11.0518 | 0.0003 | -0.0028 | 0.0009 | 0.0036 | 0.0011 | -0.0005 | 0.0306 | 0.0013 | -0.0049 | -360.1711 | 17.411 | -360.4573 | 17.6471 | -360.8174 | 18.1912 | -360.7958 | 17.5568 | -352.6044 | 18.7395 | -352.629 | 16.8258
12:41 | 4882 | 42.998 | 202.4509 | 449.9862 | 456.8095 | -16.5104 | -40.2727 | 11.4822 | 8.0622 | 2.4605 | 0.7654 | 3.3122 | -0.8576 | 12.0435 | 4.7939 | 0.6182 | 0.6625 | 0.9615 | 0.7462 | -129.7186 | 0.2772 | 5.5813 | 1.8343 | -2.8189 | -1.1391 | 4.6482 |  | 3.4669 | 0.2238 | 4.0109 | 3.3708 | 3.3404 | 1.0821 | 10.7973 | 14.2763 | 14.8842 | 11.0927 | 0.0002 | -0.0033 | 0.0006 | 0.004 | 0.0009 | -0.0003 | 0.0032 | -0.0136 | -0.0114 | -360.1804 | 17.4028 | -360.445 | 17.6492 | -360.8604 | 18.2118 | -360.8697 | 17.5671 | -352.5983 | 18.7353 | -352.6506 | 16.8361
12:41 | 4883 | 42.9682 | 202.4883 | 449.9356 | 456.7877 | -16.4721 | -40.2385 | 11.3714 | 8.0435 | 2.4274 | 0.775 | 3.2743 | -0.732 | 12.0347 | 4.7556 | 0.6194 | 0.6612 | 0.9587 | 0.7445 | -129.7086 | 0.3188 | 5.6354 | 1.9072 | -2.7289 | -1.0749 | 4.6212 |  | 3.5242 | 0.1845 | 4.0084 | 3.3681 | 3.3386 | 1.081 | 10.7844 | 14.2698 | 14.8339 | 11.0962 | 0.0003 | -0.002 | 0.0004 | 0.0039 | 0.0011 | -0.0002 | 0.0198 | -0.0046 | 0.0115 | -360.2019 | 17.4274 | -360.4296 | 17.643 | -360.8297 | 18.2015 | -360.8543 | 17.5732 | -352.6598 | 18.7395 | -352.6413 | 16.8381
12:41 | 4884 | 43.0363 | 202.446 | 449.9079 | 456.7537 | -16.479 | -40.1765 | 11.4406 | 8.029 | 2.4837 | 0.8055 | 3.2596 | -0.8303 | 11.9183 | 4.7083 | 0.6184 | 0.6618 | 0.9589 | 0.7448 | -129.6813 | 0.3275 | 5.6215 | 1.9024 | -2.7371 | -1.0903 | 4.6192 |  | 3.5541 | 0.1449 | 4.0107 | 3.3676 | 3.3388 | 1.0815 | 10.7914 | 14.2766 | 14.8747 | 11.1092 | -0.0005 | -0.0027 | 0.0007 | 0.0042 | 0.0007 | -0.0002 | 0.0223 | -0.0124 | -0.0105 | -360.1988 | 17.4131 | -360.485 | 17.682 | -360.8604 | 18.22 | -360.8666 | 17.5773 | -352.6229 | 18.7436 | -352.6721 | 16.8566
12:41 | 4885 | 43.0435 | 202.5209 | 449.9602 | 456.8298 | -16.5168 | -40.2191 | 11.4397 | 8.0015 | 2.4762 | 0.7945 | 3.3453 | -0.7031 | 11.8532 | 4.7066 | 0.6185 | 0.6593 | 0.9583 | 0.7443 | -129.6378 | 0.309 | 5.5399 | 1.8937 | -2.6624 | -1.101 | 4.677 |  | 3.4698 | 0.0958 | 4.0088 | 3.3664 | 3.3377 | 1.0818 | 10.8169 | 14.2846 | 14.8475 | 11.0829 | -0.0003 | -0.0031 | 0.0004 | 0.0035 | 0.0014 | 0 | -0.0055 | -0.006 | -0.0184 | -360.2235 | 17.4213 | -360.4542 | 17.6574 | -360.8297 | 18.2241 | -360.8727 | 17.5814 | -352.6198 | 18.7415 | -352.669 | 16.8546
12:41 | 4886 | 43.0121 | 202.4256 | 449.9936 | 456.8387 | -16.4499 | -40.2446 | 11.3175 | 8.0379 | 2.4925 | 0.847 | 3.3455 | -0.767 | 11.8747 | 4.735 | 0.6188 | 0.6581 | 0.9626 | 0.7438 | -129.7028 | 0.2738 | 5.4858 | 1.8924 | -2.6694 | -1.1303 | 4.558 |  | 3.5079 | 0.2262 | 4.0099 | 3.3691 | 3.3404 | 1.0811 | 10.7694 | 14.272 | 14.8645 | 11.0872 | 0.0001 | -0.0032 | 0.0009 | 0.004 | 0.0009 | -0.0002 | 0.0021 | -0.0176 | -0.0041 | -360.2081 | 17.4295 | -360.4758 | 17.6759 | -360.8204 | 18.2118 | -360.8635 | 17.5753 | -352.6444 | 18.7579 | -352.6567 | 16.8587
12:41 | 4887 | 43.0618 | 202.4507 | 449.991 | 456.8621 | -16.4966 | -40.1783 | 11.3654 | 7.9486 | 2.5063 | 0.9308 | 3.3359 | -0.8262 | 11.9107 | 4.735 | 0.6183 | 0.6605 | 0.9633 | 0.7454 | -129.6194 | 0.3257 | 5.5777 | 1.8992 | -2.7346 | -1.2009 | 4.4888 |  | 3.3719 | 0.1962 | 4.0103 | 3.3684 | 3.3366 | 1.0827 | 10.7916 | 14.2877 | 14.8194 | 11.0815 | -0.0003 | -0.0028 | 0.0006 | 0.0037 | 0.0012 | -0.0007 | -0.0062 | -0.0078 | 0.0034 | -360.1865 | 17.4131 | -360.4635 | 17.6553 | -360.8081 | 18.2261 | -360.842 | 17.5712 | -352.6352 | 18.7374 | -352.6444 | 16.8628
12:41 | 4888 | 42.9647 | 202.4296 | 449.952 | 456.8453 | -16.3998 | -40.189 | 11.518 | 7.9717 | 2.4771 | 0.9385 | 3.2841 | -0.8574 | 11.8692 | 4.7561 | 0.6188 | 0.6638 | 0.9642 | 0.7477 | -129.6059 | 0.474 | 5.5596 | 1.9004 | -2.748 | -1.1138 | 4.5681 |  | 3.5156 | 0.1979 | 4.011 | 3.3677 | 3.3373 | 1.0822 | 10.8018 | 14.287 | 14.8618 | 11.1139 | -0.0002 | -0.0028 | 0.0011 | 0.0039 | 0.0008 | 0 | -0.0024 | -0.004 | -0.0126 | -360.165 | 17.4028 | -360.4666 | 17.6512 | -360.8297 | 18.1994 | -360.8512 | 17.5753 | -352.6352 | 18.7436 | -352.6598 | 16.8464
12:41 | 4889 | 43.0806 | 202.4603 | 449.9559 | 456.9091 | -16.5094 | -40.3025 | 11.4022 | 8.0345 | 2.4732 | 0.6764 | 3.2479 | -0.8779 | 11.8049 | 4.6297 | 0.6197 | 0.6617 | 0.9637 | 0.7449 | -129.6191 | 0.3834 | 5.5992 | 1.8538 | -2.7738 | -1.2281 | 4.5273 |  | 3.5287 | 0.2842 | 4.0101 | 3.3667 | 3.3401 | 1.0817 | 10.7996 | 14.2555 | 14.8638 | 11.1179 | 0 | -0.003 | 0.0011 | 0.0041 | 0.0011 | -0.001 | 0.0042 | -0.0235 | 0.0019 | -360.1804 | 17.411 | -360.4389 | 17.6594 | -360.8297 | 18.2077 | -360.8604 | 17.5671 | -352.6167 | 18.7374 | -352.6537 | 16.8505
12:41 | 4890 | 43.047 | 202.3701 | 449.8915 | 456.8196 | -16.4999 | -40.2629 | 11.4157 | 7.9228 | 2.3757 | 0.7726 | 3.2274 | -0.8529 | 11.8872 | 4.7372 | 0.6192 | 0.6636 | 0.9625 | 0.7449 | -129.6228 | 0.3159 | 5.6067 | 1.852 | -2.7569 | -1.0724 | 4.5617 |  | 3.5724 | 0.2128 | 4.011 | 3.366 | 3.3389 | 1.0813 | 10.7637 | 14.295 | 14.8171 | 11.0934 | 0.0002 | -0.0032 | 0.0006 | 0.004 | 0.0007 | -0.0002 | 0.0023 | -0.008 | -0.0216 | -360.1435 | 17.4007 | -360.4173 | 17.6328 | -360.7897 | 18.2036 | -360.8358 | 17.5486 | -352.6136 | 18.7333 | -352.626 | 16.8361
12:41 | 4891 | 43.0825 | 202.4504 | 449.8913 | 456.7587 | -16.4885 | -40.2379 | 11.4546 | 8.0296 | 2.4026 | 0.9112 | 3.2096 | -0.7763 | 11.8505 | 4.7858 | 0.6171 | 0.6574 | 0.9647 | 0.744 | -129.6182 | 0.29 | 5.5776 | 2.044 | -2.646 | -1.0432 | 4.637 |  | 3.517 | 0.2324 | 4.0108 | 3.3686 | 3.3372 | 1.0814 | 10.788 | 14.2846 | 14.859 | 11.1118 | -0.0003 | -0.0033 | 0.0008 | 0.0041 | 0.001 | -0.0005 | -0.0028 | -0.0093 | -0.0157 | -360.125 | 17.3905 | -360.4266 | 17.6245 | -360.762 | 18.1994 | -360.802 | 17.5486 | -352.5829 | 18.7169 | -352.6352 | 16.834
12:41 | 4892 | 43.1041 | 202.4024 | 449.8439 | 456.8258 | -16.4465 | -40.3291 | 11.4073 | 8.0222 | 2.4094 | 1.0747 | 3.2838 | -0.805 | 11.8706 | 4.715 | 0.6184 | 0.6616 | 0.9592 | 0.7456 | -129.6599 | 0.2991 | 5.5445 | 2.0204 | -2.6267 | -0.9805 | 4.6264 |  | 3.4775 | 0.2103 | 4.0113 | 3.3676 | 3.3386 | 1.0816 | 10.7903 | 14.2984 | 14.8549 | 11.0912 | -0.0004 | -0.0029 | 0.0007 | 0.0036 | 0.0005 | -0.0009 | 0.0069 | 0.0006 | -0.0032 | -360.1435 | 17.3864 | -360.4296 | 17.641 | -360.7681 | 18.1912 | -360.8358 | 17.5506 | -352.5952 | 18.7169 | -352.629 | 16.832
12:41 | 4893 | 43.0972 | 202.3959 | 449.9199 | 456.8586 | -16.4517 | -40.3684 | 11.3564 | 8.0261 | 2.43 | 0.9818 | 3.2683 | -0.8153 | 11.9535 | 4.7639 | 0.6209 | 0.6639 | 0.9601 | 0.7454 | -129.5983 | 0.3322 | 5.5787 | 2.0015 | -2.643 | -1.054 | 4.6254 |  | 3.5519 | 0.222 | 4.0081 | 3.3637 | 3.3402 | 1.0819 | 10.7983 | 14.2837 | 14.8887 | 11.0926 | 0.0002 | -0.0029 | 0.0008 | 0.0041 | 0.0007 | -0.0003 | 0.0079 | -0.0246 | -0.0073 | -360.1311 | 17.3946 | -360.3927 | 17.6286 | -360.7897 | 18.1912 | -360.805 | 17.5547 | -352.5983 | 18.721 | -352.6013 | 16.834
12:41 | 4894 | 43.064 | 202.4843 | 449.8843 | 456.9883 | -16.4159 | -40.3306 | 11.4649 | 8.029 | 2.3938 | 1.004 | 3.2679 | -0.8152 | 11.9621 | 4.8065 | 0.6197 | 0.6622 | 0.9602 | 0.7442 | -129.5852 | 0.3439 | 5.5836 | 1.9028 | -2.6547 | -1.0299 | 4.6491 |  | 3.4743 | 0.2338 | 4.009 | 3.3662 | 3.3394 | 1.0809 | 10.8204 | 14.2764 | 14.8447 | 11.0923 | -0.0001 | -0.0034 | 0.001 | 0.0039 | 0.0012 | -0.0003 | 0.0013 | -0.0077 | -0.0212 | -360.1527 | 17.4048 | -360.4173 | 17.6286 | -360.7743 | 18.1851 | -360.7989 | 17.5404 | -352.5521 | 18.723 | -352.6136 | 16.8279
12:41 | 4895 | 43.1477 | 202.4447 | 449.9099 | 456.8658 | -16.4276 | -40.2664 | 11.4445 | 8.0882 | 2.4387 | 1.0669 | 3.3598 | -0.7891 | 12.0197 | 4.7323 | 0.6207 | 0.6605 | 0.9592 | 0.7461 | -129.6574 | 0.3441 | 5.6008 | 1.8425 | -2.7483 | -0.9311 | 4.6135 |  | 3.5174 | 0.209 | 4.0089 | 3.3682 | 3.3384 | 1.0822 | 10.7846 | 14.2751 | 14.8075 | 11.0973 | 0 | -0.0028 | 0.0009 | 0.0037 | 0.0005 | -0.0004 | 0.0128 | 0.009 | -0.0201 | -360.1619 | 17.3905 | -360.4142 | 17.6286 | -360.7743 | 18.2056 | -360.8235 | 17.5486 | -352.6044 | 18.7128 | -352.5983 | 16.8238
12:41 | 4896 | 43.164 | 202.4194 | 449.9018 | 456.7575 | -16.3874 | -40.3222 | 11.4913 | 8.0663 | 2.4012 | 1.0162 | 3.278 | -0.8279 | 11.9639 | 4.7317 | 0.6198 | 0.6602 | 0.9616 | 0.7456 | -129.6524 | 0.3943 | 5.5978 | 1.8681 | -2.8147 | -1.1046 | 4.6292 |  | 3.5133 | 0.2827 | 4.0092 | 3.3709 | 3.3382 | 1.0829 | 10.7787 | 14.2926 | 14.826 | 11.0739 | -0.0003 | -0.0024 | 0.0009 | 0.0033 | 0.0011 | -0.0005 | 0.0062 | -0.0101 | -0.0249 | -360.1588 | 17.4028 | -360.4296 | 17.6348 | -360.7897 | 18.181 | -360.8297 | 17.5527 | -352.6013 | 18.721 | -352.6075 | 16.8279
12:41 | 4897 | 43.1806 | 202.4146 | 449.9367 | 456.7946 | -16.4541 | -40.3634 | 11.4848 | 8.0268 | 2.3468 | 0.9445 | 3.2746 | -0.8268 | 11.912 | 4.7218 | 0.6195 | 0.6632 | 0.9614 | 0.7463 | -129.62 | 0.4287 | 5.6056 | 1.8745 | -2.7752 | -1.0934 | 4.619 |  | 3.4927 | 0.3437 | 4.0081 | 3.3708 | 3.3398 | 1.0816 | 10.7615 | 14.2692 | 14.8239 | 11.0688 | -0.0003 | -0.0028 | 0.0007 | 0.004 | 0.0005 | -0.0003 | 0.002 | -0.0065 | -0.0091 | -360.2142 | 17.3946 | -360.4266 | 17.6492 | -360.805 | 18.2056 | -360.8358 | 17.5547 | -352.5983 | 18.7169 | -352.6136 | 16.8258
12:41 | 4898 | 43.2233 | 202.4935 | 449.9262 | 456.8232 | -16.4356 | -40.4148 | 11.4352 | 8.0606 | 2.4491 | 1.0409 | 3.2755 | -0.8696 | 11.8805 | 4.7479 | 0.6191 | 0.6628 | 0.9636 | 0.7452 | -129.7215 | 0.3943 | 5.4961 | 1.7707 | -2.8561 | -1.1881 | 4.5671 |  | 3.4741 | 0.3327 | 4.0089 | 3.3684 | 3.3383 | 1.083 | 10.7764 | 14.2788 | 14.8706 | 11.106 | 0.0004 | -0.0031 | 0.0006 | 0.0041 | 0.001 | -0.0005 | 0.0026 | -0.012 | -0.0172 | -360.1588 | 17.409 | -360.4358 | 17.6245 | -360.7866 | 18.2159 | -360.8666 | 17.565 | -352.6013 | 18.723 | -352.626 | 16.8094
12:41 | 4899 | 43.2071 | 202.5311 | 449.9772 | 456.9316 | -16.4081 | -40.3217 | 11.4423 | 8.0213 | 2.4425 | 1.0141 | 3.3295 | -0.7839 | 11.9751 | 4.8023 | 0.6192 | 0.6619 | 0.9605 | 0.7452 | -129.6832 | 0.2771 | 5.5817 | 1.8114 | -2.7894 | -1.1044 | 4.6229 |  | 3.581 | 0.3007 | 4.0085 | 3.368 | 3.335 | 1.0818 | 10.7821 | 14.2733 | 14.8612 | 11.0937 | 0.0001 | -0.003 | 0.0011 | 0.004 | 0.0004 | -0.0002 | 0.0148 | 0.0016 | -0.0159 | -360.1958 | 17.4213 | -360.4789 | 17.6512 | -360.8235 | 18.1974 | -360.8297 | 17.5671 | -352.626 | 18.7497 | -352.6813 | 16.834
12:41 | 4900 | 43.1785 | 202.3638 | 449.8773 | 456.8665 | -16.5058 | -40.273 | 11.4131 | 7.9972 | 2.3526 | 0.8847 | 3.3201 | -0.7828 | 12.0007 | 4.8014 | 0.6202 | 0.6616 | 0.9615 | 0.745 | -129.6103 | 0.2439 | 5.5673 | 1.8622 | -2.7363 | -1.0413 | 4.6529 |  | 3.5583 | 0.25 | 4.0098 | 3.3708 | 3.3417 | 1.0817 | 10.7499 | 14.2807 | 14.8354 | 11.1093 | 0.0001 | -0.0024 | 0.0006 | 0.0041 | 0.0006 | -0.0011 | 0.01 | -0.0112 | -0.0123 | -360.1804 | 17.4007 | -360.4296 | 17.6574 | -360.8358 | 18.2323 | -360.8758 | 17.565 | -352.5798 | 18.7189 | -352.6413 | 16.8258
12:41 | 4901 | 43.1779 | 202.467 | 449.9477 | 456.8614 | -16.5047 | -40.2664 | 11.3738 | 8.0636 | 2.4016 | 1.0262 | 3.3836 | -0.7921 | 11.9978 | 4.7453 | 0.619 | 0.6629 | 0.9608 | 0.7443 | -129.6732 | 0.3037 | 5.5293 | 1.9112 | -2.7864 | -1.0693 | 4.6383 |  | 3.5036 | 0.3025 | 4.0099 | 3.3704 | 3.3388 | 1.0832 | 10.811 | 14.2965 | 14.9017 | 11.0937 | -0.0003 | -0.0027 | 0.0009 | 0.0034 | 0.0007 | -0.0003 | 0.0194 | 0.0023 | -0.021 | -360.205 | 17.4213 | -360.445 | 17.6471 | -360.8081 | 18.2241 | -360.8604 | 17.5937 | -352.6752 | 18.7395 | -352.6352 | 16.8156
12:41 | 4902 | 43.1567 | 202.3955 | 450.0196 | 456.7923 | -16.5031 | -40.3132 | 11.3661 | 8.1016 | 2.4189 | 1.0706 | 3.3444 | -0.7322 | 11.9428 | 4.7107 | 0.6184 | 0.6622 | 0.9602 | 0.7445 | -129.7123 | 0.4389 | 5.5419 | 1.8868 | -2.7725 | -1.1056 | 4.6335 |  | 3.5673 | 0.2783 | 4.0095 | 3.3666 | 3.3382 | 1.0818 | 10.8031 | 14.2821 | 14.8726 | 11.1042 | 0.0003 | -0.0027 | 0.001 | 0.0034 | 0.0007 | -0.0009 | 0.0088 | -0.0079 | -0.0151 | -360.2019 | 17.4397 | -360.4942 | 17.6697 | -360.8358 | 18.1912 | -360.7681 | 17.5568 | -352.6537 | 18.7682 | -352.6875 | 16.8423
12:41 | 4903 | 43.1851 | 202.4657 | 449.9237 | 456.9034 | -16.4397 | -40.3095 | 11.3972 | 8.0934 | 2.4751 | 0.9411 | 3.3487 | -0.7543 | 11.9626 | 4.7206 | 0.6214 | 0.6642 | 0.9664 | 0.745 | -129.6843 | 0.4544 | 5.636 | 1.8893 | -2.7649 | -1.0551 | 4.6833 |  | 3.5696 | 0.1526 | 4.0092 | 3.3671 | 3.339 | 1.0814 | 10.7522 | 14.2715 | 14.8324 | 11.1172 | -0.0001 | -0.0029 | 0.0007 | 0.004 | 0.0004 | -0.0008 | 0.001 | -0.0185 | 0.0074 | -360.1588 | 17.4028 | -360.4481 | 17.6594 | -360.8666 | 18.2528 | -360.8974 | 17.5712 | -352.6321 | 18.7148 | -352.6383 | 16.8402
12:41 | 4904 | 43.2105 | 202.3899 | 449.931 | 456.8813 | -16.4364 | -40.2562 | 11.4245 | 8.1173 | 2.4997 | 0.8914 | 3.4049 | -0.8422 | 11.8917 | 4.7571 | 0.6199 | 0.667 | 0.9633 | 0.7469 | -129.6918 | 0.3898 | 5.5087 | 1.9484 | -2.7967 | -1.018 | 4.7051 |  | 3.6238 | 0.1884 | 4.009 | 3.3674 | 3.3411 | 1.0814 | 10.8076 | 14.2929 | 14.8628 | 11.0847 | -0.0002 | -0.0025 | 0.0006 | 0.0038 | 0.0007 | -0.0006 | 0.0037 | -0.0082 | 0.0124 | -360.2235 | 17.4315 | -360.4635 | 17.6328 | -360.7989 | 18.2036 | -360.885 | 17.5896 | -352.6721 | 18.7538 | -352.6321 | 16.8135
12:41 | 4905 | 43.2592 | 202.4498 | 449.9423 | 456.8013 | -16.4691 | -40.2792 | 11.408 | 8.1385 | 2.4932 | 0.9418 | 3.4397 | -0.8678 | 11.8958 | 4.7699 | 0.6201 | 0.6656 | 0.962 | 0.7449 | -129.6011 | 0.4544 | 5.4755 | 2.0373 | -2.8494 | -1.1214 | 4.5573 |  | 3.5883 | 0.2334 | 4.0099 | 3.3678 | 3.3386 | 1.0808 | 10.7662 | 14.2505 | 14.8388 | 11.0681 | -0.0003 | -0.0025 | 0.0005 | 0.0038 | 0.0009 | -0.0004 | 0.0034 | -0.0037 | -0.0008 | -360.1835 | 17.4233 | -360.5158 | 17.7026 | -360.882 | 18.2077 | -360.8235 | 17.5445 | -352.6506 | 18.7579 | -352.706 | 16.871
12:41 | 4906 | 43.1683 | 202.4338 | 449.9135 | 456.8062 | -16.447 | -40.2398 | 11.4294 | 8.108 | 2.5483 | 1.0642 | 3.4702 | -0.8082 | 11.9418 | 4.7972 | 0.6201 | 0.6629 | 0.9601 | 0.7449 | -129.5675 | 0.4469 | 5.574 | 2.0602 | -2.7626 | -1.0115 | 4.7144 |  | 3.5936 | 0.3131 | 4.0092 | 3.367 | 3.3387 | 1.081 | 10.7557 | 14.2576 | 14.8528 | 11.0804 | 0 | -0.0034 | 0.0008 | 0.004 | 0.0013 | -0.0001 | 0.0008 | -0.0127 | -0.007 | -360.1711 | 17.4048 | -360.3958 | 17.6369 | -360.8297 | 18.2344 | -360.8974 | 17.5896 | -352.6598 | 18.7251 | -352.6444 | 16.8258
12:41 | 4907 | 43.2516 | 202.4397 | 449.9439 | 456.9013 | -16.3974 | -40.2692 | 11.4792 | 8.099 | 2.5456 | 0.9035 | 3.3667 | -0.7683 | 12.0409 | 4.8875 | 0.6211 | 0.6613 | 0.964 | 0.7444 | -129.5844 | 0.4596 | 5.5736 | 2.0845 | -2.7139 | -1.0643 | 4.682 |  | 3.5928 | 0.2418 | 4.0096 | 3.3675 | 3.3396 | 1.0802 | 10.7811 | 14.2833 | 14.8797 | 11.1111 | 0 | -0.0032 | 0.0004 | 0.0037 | 0.0007 | -0.0006 | 0.0037 | -0.0208 | -0.0036 | -360.2265 | 17.4521 | -360.5096 | 17.6656 | -360.805 | 18.1933 | -360.8266 | 17.5691 | -352.6844 | 18.7805 | -352.706 | 16.8402
12:42 | 4908 | 43.1947 | 202.5362 | 450.046 | 456.9782 | -16.4735 | -40.2885 | 11.4068 | 8.0523 | 2.5628 | 0.9646 | 3.3667 | -0.8405 | 11.9383 | 4.8365 | 0.6192 | 0.664 | 0.9679 | 0.7446 | -129.5771 | 0.5341 | 5.6678 | 2.0084 | -2.7749 | -1.1206 | 4.6144 |  | 3.5887 | 0.1985 | 4.0098 | 3.3669 | 3.3391 | 1.0786 | 10.7846 | 14.2634 | 14.8528 | 11.0862 | -0.0004 | -0.0028 | 0.0006 | 0.0036 | 0.0007 | 0.0003 | 0.0201 | -0.013 | -0.0193 | -360.1188 | 17.372 | -360.4173 | 17.6697 | -360.8604 | 18.2241 | -360.8666 | 17.5404 | -352.586 | 18.7045 | -352.6352 | 16.8443
12:42 | 4909 | 43.0534 | 202.4055 | 449.9024 | 456.8313 | -16.4422 | -40.2836 | 11.4749 | 8.2144 | 2.5813 | 0.8757 | 3.4262 | -0.8237 | 11.9417 | 4.7684 | 0.6207 | 0.662 | 0.967 | 0.7432 | -129.6258 | 0.412 | 5.5183 | 2.0216 | -2.7827 | -1.0592 | 4.693 |  | 3.5991 | 0.2194 | 4.0102 | 3.3696 | 3.3403 | 1.0835 | 10.7557 | 14.2693 | 14.8307 | 11.0742 | -0.0002 | -0.0027 | 0.0014 | 0.0041 | 0.0011 | -0.0007 | 0.0055 | -0.0146 | -0.0142 | -360.165 | 17.3987 | -360.4112 | 17.6102 | -360.7343 | 18.1912 | -360.8235 | 17.5753 | -352.6567 | 18.7189 | -352.6044 | 16.8032
12:42 | 4910 | 43.1367 | 202.4285 | 449.8984 | 456.8157 | -16.4083 | -40.2245 | 11.5489 | 8.1662 | 2.5894 | 0.8951 | 3.3891 | -0.8567 | 11.9266 | 4.8123 | 0.6209 | 0.6639 | 0.9658 | 0.7459 | -129.6786 | 0.4378 | 5.4767 | 1.9257 | -2.8542 | -1.1333 | 4.6 |  | 3.5594 | 0.2398 | 4.0103 | 3.3673 | 3.3408 | 1.0825 | 10.781 | 14.2834 | 14.8692 | 11.1049 | 0.0003 | -0.0028 | 0.001 | 0.0039 | 0.0003 | -0.0002 | 0.0212 | -0.0011 | -0.0001 | -360.1373 | 17.3946 | -360.4542 | 17.6492 | -360.8358 | 18.1789 | -360.7743 | 17.5219 | -352.5706 | 18.721 | -352.669 | 16.8443
12:42 | 4911 | 43.1165 | 202.4527 | 449.901 | 456.8861 | -16.3136 | -40.1034 | 11.5716 | 8.1333 | 2.5288 | 0.8465 | 3.3766 | -0.8571 | 11.96 | 4.7958 | 0.6204 | 0.6649 | 0.9655 | 0.7452 | -129.6761 | 0.4763 | 5.5346 | 1.7764 | -2.834 | -1.0789 | 4.5708 |  | 3.6232 | 0.2314 | 4.0099 | 3.3672 | 3.3404 | 1.0813 | 10.7672 | 14.2809 | 14.8481 | 11.0858 | -0.0001 | -0.0032 | 0.0005 | 0.0039 | 0.0008 | -0.0007 | 0.0112 | -0.0008 | 0.0021 | -360.1219 | 17.3576 | -360.3558 | 17.6061 | -360.7743 | 18.22 | -360.8512 | 17.5547 | -352.589 | 18.6881 | -352.549 | 16.8074
12:42 | 4912 | 43.1685 | 202.4649 | 449.9852 | 456.8869 | -16.4555 | -40.158 | 11.579 | 8.11 | 2.4786 | 0.9297 | 3.3919 | -0.8031 | 11.9821 | 4.761 | 0.6182 | 0.665 | 0.9655 | 0.7449 | -129.6917 | 0.3798 | 5.5137 | 1.8903 | -2.6859 | -1.0616 | 4.6121 |  | 3.6169 | 0.2266 | 4.0102 | 3.3658 | 3.3416 | 1.0817 | 10.7972 | 14.2766 | 14.8747 | 11.0861 | -0.0002 | -0.0025 | 0.0008 | 0.0035 | 0.0008 | -0.0004 | 0.0202 | -0.0112 | -0.0096 | -360.1742 | 17.4274 | -360.4604 | 17.6245 | -360.7527 | 18.1625 | -360.802 | 17.5588 | -352.6106 | 18.7436 | -352.6598 | 16.8074
12:42 | 4913 | 43.0157 | 202.4881 | 449.8381 | 456.9192 | -16.4115 | -40.2072 | 11.6354 | 8.0392 | 2.4826 | 0.8896 | 3.4161 | -0.7499 | 12.0842 | 4.7339 | 0.6209 | 0.6629 | 0.9655 | 0.7454 | -129.6081 | 0.3535 | 5.5904 | 1.8758 | -2.7335 | -1.0474 | 4.5975 |  | 3.5691 | 0.2716 | 4.0091 | 3.3695 | 3.3394 | 1.0818 | 10.8295 | 14.315 | 14.8973 | 11.1468 | -0.0003 | -0.0026 | 0.0004 | 0.0039 | 0.0009 | -0.0009 | 0.0084 | -0.0238 | -0.0182 | -360.0911 | 17.3782 | -360.4327 | 17.6677 | -360.882 | 18.2138 | -360.7927 | 17.528 | -352.5213 | 18.7045 | -352.6075 | 16.8464
12:42 | 4914 | 43.075 | 202.4702 | 449.9209 | 456.9303 | -16.4666 | -40.2915 | 11.4941 | 8.1395 | 2.5262 | 0.8393 | 3.4329 | -0.8386 | 11.9785 | 4.6873 | 0.6199 | 0.6664 | 0.964 | 0.7462 | -129.7037 | 0.3888 | 5.5353 | 1.8969 | -2.607 | -1.0748 | 4.7047 |  | 3.5191 | 0.3066 | 4.0107 | 3.3717 | 3.3421 | 1.0824 | 10.7856 | 14.2939 | 14.8516 | 11.1266 | 0 | -0.0028 | 0.0008 | 0.0042 | 0.0007 | -0.0007 | 0.0292 | -0.014 | -0.0009 | -360.1958 | 17.409 | -360.4081 | 17.6266 | -360.8081 | 18.2179 | -360.9035 | 17.5855 | -352.6383 | 18.7189 | -352.6198 | 16.8094
12:42 | 4915 | 43.1508 | 202.4958 | 449.9544 | 456.9756 | -16.4093 | -40.2458 | 11.4913 | 8.1033 | 2.4457 | 0.7457 | 3.3686 | -0.8489 | 12.0209 | 4.7125 | 0.6205 | 0.6647 | 0.9603 | 0.7446 | -129.6773 | 0.356 | 5.5426 | 1.8183 | -2.7298 | -1.123 | 4.66 |  | 3.6026 | 0.3305 | 4.0084 | 3.3662 | 3.3362 | 1.0818 | 10.8065 | 14.2799 | 14.8304 | 11.0959 | 0 | -0.0035 | 0.0006 | 0.0038 | 0.0008 | -0.0006 | 0.0085 | -0.0073 | 0.0173 | -360.2111 | 17.4336 | -360.5189 | 17.6697 | -360.845 | 18.1851 | -360.7958 | 17.5506 | -352.626 | 18.7497 | -352.6937 | 16.8505
12:42 | 4916 | 43.1842 | 202.5305 | 449.9539 | 456.98 | -16.2926 | -40.0377 | 11.6272 | 8.1489 | 2.5361 | 0.7703 | 3.4619 | -0.8208 | 11.976 | 4.7953 | 0.6191 | 0.6656 | 0.9623 | 0.7464 | -129.6921 | 0.3792 | 5.5222 | 1.8524 | -2.7234 | -1.2289 | 4.6461 |  | 3.6015 | 0.3509 | 4.0099 | 3.3684 | 3.3388 | 1.0824 | 10.7823 | 14.267 | 14.8453 | 11.1125 | -0.0001 | -0.0027 | 0.0006 | 0.0038 | 0.0007 | -0.0005 | 0.0173 | -0.0107 | 0.0101 | -360.1527 | 17.4069 | -360.4358 | 17.6759 | -360.8758 | 18.2385 | -360.8697 | 17.565 | -352.629 | 18.7312 | -352.6167 | 16.8464
12:42 | 4917 | 43.2769 | 202.6667 | 449.8594 | 456.8744 | -16.2894 | -40.0572 | 11.6168 | 8.0837 | 2.4501 | 0.9362 | 3.4105 | -0.8438 | 12.0368 | 4.7707 | 0.6191 | 0.6613 | 0.9643 | 0.7457 | -129.7667 | 0.3405 | 5.5595 | 1.8927 | -2.7114 | -1.2 | 4.6632 |  | 3.5745 | 0.3102 | 4.0108 | 3.3688 | 3.3411 | 1.081 | 10.759 | 14.2673 | 14.8359 | 11.0713 | -0.0001 | -0.0024 | 0.0015 | 0.0041 | 0.0003 | -0.0002 | 0.0176 | -0.0178 | 0.0069 | -360.2388 | 17.4356 | -360.4481 | 17.643 | -360.8235 | 18.2097 | -360.8635 | 17.5917 | -352.6567 | 18.7477 | -352.6752 | 16.8197
12:42 | 4918 | 43.1466 | 202.6162 | 449.8924 | 456.8808 | -16.2723 | -39.9958 | 11.681 | 8.0677 | 2.4832 | 0.8393 | 3.3163 | -0.7965 | 12.0716 | 4.7755 | 0.6214 | 0.6641 | 0.9645 | 0.7453 | -129.6692 | 0.4909 | 5.6182 | 1.918 | -2.7375 | -1.1089 | 4.6699 |  | 3.5569 | 0.29 | 4.0101 | 3.3715 | 3.3373 | 1.0813 | 10.7856 | 14.2882 | 14.8342 | 11.0919 | 0.0002 | -0.0028 | 0.0009 | 0.0039 | 0.001 | -0.0003 | 0.0217 | 0.0027 | -0.0192 | -360.1711 | 17.4295 | -360.5312 | 17.6882 | -360.8512 | 18.2159 | -360.845 | 17.5609 | -352.6352 | 18.7477 | -352.6998 | 16.8648
12:42 | 4919 | 43.1464 | 202.6059 | 449.9652 | 456.9601 | -16.2906 | -39.9943 | 11.6867 | 8.0447 | 2.4223 | 0.8356 | 3.3604 | -0.8341 | 12.1057 | 4.7741 | 0.6181 | 0.6584 | 0.9615 | 0.7461 | -129.6488 | 0.5248 | 5.6137 | 1.9105 | -2.7243 | -1.0599 | 4.692 |  | 3.5012 | 0.2237 | 4.0089 | 3.367 | 3.3405 | 1.0807 | 10.8272 | 14.2954 | 14.9014 | 11.1038 | 0.0004 | -0.0027 | 0.0012 | 0.0043 | 0.0007 | -0.0002 | 0.005 | -0.0013 | 0.014 | -360.1681 | 17.3966 | -360.4512 | 17.6574 | -360.8266 | 18.222 | -360.8574 | 17.5773 | -352.6383 | 18.7292 | -352.6475 | 16.8258
12:42 | 4920 | 43.1385 | 202.4628 | 449.9591 | 456.8792 | -16.3133 | -40.0398 | 11.6354 | 8.0434 | 2.4736 | 0.9432 | 3.369 | -0.7466 | 12.0886 | 4.73 | 0.6203 | 0.6631 | 0.9623 | 0.7469 | -129.678 | 0.4433 | 5.6312 | 1.8513 | -2.6849 | -0.9896 | 4.6445 |  | 3.5314 | 0.1491 | 4.01 | 3.3667 | 3.3373 | 1.0824 | 10.7914 | 14.2882 | 14.8805 | 11.115 | -0.0003 | -0.0029 | 0.0012 | 0.0038 | 0.0013 | -0.0005 | 0.012 | -0.01 | -0.0034 | -360.205 | 17.4356 | -360.4696 | 17.6594 | -360.802 | 18.2077 | -360.845 | 17.5773 | -352.6413 | 18.7579 | -352.6752 | 16.834
12:42 | 4921 | 43.1742 | 202.4091 | 449.8184 | 456.8599 | -16.2818 | -40.051 | 11.6412 | 8.0311 | 2.476 | 0.9763 | 3.3532 | -0.8546 | 12.0809 | 4.7931 | 0.6186 | 0.6623 | 0.9673 | 0.7456 | -129.6623 | 0.4365 | 5.6157 | 1.9527 | -2.7268 | -1.0019 | 4.7046 |  | 3.4696 | 0.2268 | 4.0091 | 3.3655 | 3.3407 | 1.0821 | 10.8134 | 14.2871 | 14.8686 | 11.1251 | -0.0002 | -0.0024 | 0.0006 | 0.0041 | 0.0012 | 0.0003 | 0.0044 | -0.0116 | 0.0087 | -360.1404 | 17.409 | -360.4512 | 17.6492 | -360.8174 | 18.2097 | -360.842 | 17.565 | -352.629 | 18.7271 | -352.6598 | 16.8423
12:42 | 4922 | 43.1743 | 202.5389 | 449.9133 | 456.8024 | -16.3296 | -40.0747 | 11.6724 | 8.0738 | 2.5585 | 1.0932 | 3.4468 | -0.8408 | 12.0537 | 4.7515 | 0.6196 | 0.6599 | 0.9651 | 0.7464 | -129.6682 | 0.339 | 5.5541 | 1.8547 | -2.8189 | -1.0706 | 4.6492 |  | 3.5191 | 0.197 | 4.0092 | 3.3635 | 3.34 | 1.0812 | 10.7754 | 14.2369 | 14.8324 | 11.0768 | -0.0003 | -0.0028 | 0.0008 | 0.0039 | 0.001 | -0.0008 | 0.0052 | 0.0002 | -0.0047 | -360.1988 | 17.4007 | -360.4573 | 17.6492 | -360.7989 | 18.2138 | -360.8358 | 17.5732 | -352.6352 | 18.7353 | -352.6413 | 16.8361
12:42 | 4923 | 43.1881 | 202.618 | 449.9231 | 456.9283 | -16.3396 | -40.1696 | 11.6214 | 8.0179 | 2.4376 | 0.909 | 3.3558 | -0.8987 | 12.0021 | 4.7381 | 0.621 | 0.6648 | 0.9666 | 0.7462 | -129.6372 | 0.3395 | 5.5215 | 1.871 | -2.742 | -1.0402 | 4.7517 |  | 3.5414 | 0.2672 | 4.0098 | 3.3648 | 3.3384 | 1.0827 | 10.7927 | 14.289 | 14.8566 | 11.1111 | 0 | -0.0031 | 0.0004 | 0.0035 | 0.0005 | -0.0006 | 0.0077 | -0.0013 | 0.0027 | -360.1588 | 17.3966 | -360.4358 | 17.6492 | -360.7773 | 18.1974 | -360.8204 | 17.5527 | -352.626 | 18.7353 | -352.6537 | 16.8361
12:42 | 4924 | 43.2473 | 202.5532 | 449.9494 | 456.9428 | -16.3309 | -40.1158 | 11.6419 | 7.9212 | 2.4466 | 0.8767 | 3.2717 | -0.8776 | 12.0661 | 4.789 | 0.6198 | 0.663 | 0.9651 | 0.7468 | -129.5782 | 0.3886 | 5.6235 | 1.8731 | -2.8052 | -1.0521 | 4.6601 |  | 3.5313 | 0.2513 | 4.0089 | 3.3647 | 3.3384 | 1.0836 | 10.7521 | 14.2718 | 14.8577 | 11.0991 | 0.0003 | -0.0029 | 0.0006 | 0.0041 | 0.0014 | -0.0004 | 0.0138 | -0.0049 | -0.0103 | -360.1496 | 17.3864 | -360.4173 | 17.6369 | -360.7804 | 18.2036 | -360.802 | 17.5609 | -352.6136 | 18.7025 | -352.6106 | 16.8197
12:42 | 4925 | 43.2625 | 202.5216 | 449.983 | 456.8971 | -16.309 | -40.1779 | 11.5119 | 7.8814 | 2.4441 | 0.942 | 3.2824 | -0.9401 | 12.073 | 4.797 | 0.6188 | 0.6597 | 0.9641 | 0.7454 | -129.5509 | 0.3628 | 5.5392 | 1.8916 | -2.804 | -1.163 | 4.6672 |  | 3.5553 | 0.3342 | 4.0092 | 3.3641 | 3.3361 | 1.0824 | 10.7846 | 14.2578 | 14.8249 | 11.08 | -0.0001 | -0.0026 | 0.0014 | 0.004 | 0.0006 | -0.0003 | -0.0002 | -0.0064 | -0.009 | -360.1558 | 17.3925 | -360.3896 | 17.6328 | -360.7897 | 18.1892 | -360.7743 | 17.5547 | -352.6106 | 18.7189 | -352.6229 | 16.8053
12:42 | 4926 | 43.2651 | 202.501 | 449.8223 | 456.8512 | -16.364 | -40.2613 | 11.483 | 7.9286 | 2.4959 | 1.0129 | 3.3694 | -0.8545 | 12.0182 | 4.7756 | 0.6186 | 0.6625 | 0.9614 | 0.7442 | -129.5865 | 0.4399 | 5.4932 | 1.9014 | -2.8062 | -1.1013 | 4.6229 |  | 3.5892 | 0.2268 | 4.0093 | 3.3654 | 3.3392 | 1.083 | 10.7555 | 14.2873 | 14.8581 | 11.0901 | 0.0002 | -0.0024 | 0.0013 | 0.0042 | 0.0014 | -0.0001 | 0.006 | -0.011 | -0.0101 | -360.1558 | 17.4007 | -360.4389 | 17.6677 | -360.7989 | 18.1789 | -360.7681 | 17.5342 | -352.5767 | 18.7169 | -352.6813 | 16.8402
12:42 | 4927 | 43.3202 | 202.5628 | 449.9659 | 456.9541 | -16.3349 | -40.2356 | 11.4985 | 8.0192 | 2.4707 | 0.9337 | 3.3968 | -0.9111 | 11.9876 | 4.7165 | 0.6185 | 0.6642 | 0.9686 | 0.7463 | -129.5658 | 0.4383 | 5.5269 | 1.8489 | -2.8043 | -1.0564 | 4.6604 |  | 3.5378 | 0.216 | 4.0095 | 3.3652 | 3.3376 | 1.0823 | 10.795 | 14.2741 | 14.8651 | 11.0843 | -0.0001 | -0.0032 | 0.0003 | 0.0036 | 0.0008 | -0.0003 | 0.0037 | -0.0166 | 0.0019 | -360.1342 | 17.3597 | -360.3835 | 17.641 | -360.7835 | 18.2159 | -360.8174 | 17.5609 | -352.5767 | 18.6902 | -352.5736 | 16.8074
12:42 | 4928 | 43.342 | 202.7147 | 450.0584 | 456.9363 | -16.3407 | -40.2325 | 11.5131 | 8.0076 | 2.4511 | 1.0512 | 3.3839 | -0.9381 | 12.0024 | 4.7502 | 0.6182 | 0.662 | 0.9653 | 0.7463 | -129.4434 | 0.4156 | 5.5864 | 1.8331 | -2.797 | -1.1054 | 4.6732 |  | 3.559 | 0.3066 | 4.0106 | 3.3651 | 3.3399 | 1.0812 | 10.7949 | 14.3147 | 14.8546 | 11.0897 | 0 | -0.0032 | 0.001 | 0.0041 | 0.0007 | -0.0006 | -0.0026 | -0.0012 | -0.0068 | -360.1958 | 17.4151 | -360.4481 | 17.6328 | -360.765 | 18.1707 | -360.7773 | 17.5506 | -352.6044 | 18.7312 | -352.6229 | 16.8053
12:42 | 4929 | 43.3038 | 202.6285 | 450.0474 | 456.9417 | -16.3544 | -40.3343 | 11.3986 | 8.0981 | 2.4237 | 0.9612 | 3.4178 | -0.938 | 11.9654 | 4.6855 | 0.6176 | 0.6649 | 0.9612 | 0.7452 | -129.3401 | 0.4014 | 5.519 | 1.7991 | -2.7791 | -1.0499 | 4.6894 |  | 3.4902 | 0.2712 | 4.0102 | 3.3675 | 3.3392 | 1.0825 | 10.7834 | 14.2681 | 14.8409 | 11.0732 | -0.0004 | -0.0027 | 0.0002 | 0.0034 | 0.0014 | -0.0007 | 0.0265 | -0.001 | -0.0106 | -360.0881 | 17.3782 | -360.4204 | 17.6677 | -360.8112 | 18.2015 | -360.7958 | 17.526 | -352.5613 | 18.6922 | -352.6321 | 16.8484
12:42 | 4930 | 43.3201 | 202.624 | 449.9993 | 456.8938 | -16.3269 | -40.3664 | 11.5085 | 8.1056 | 2.4078 | 0.9258 | 3.4503 | -0.9725 | 12.072 | 4.6708 | 0.6188 | 0.6633 | 0.9642 | 0.7467 | -129.3844 | 0.4154 | 5.529 | 1.8199 | -2.762 | -1.1121 | 4.665 |  | 3.6241 | 0.3475 | 4.0094 | 3.3616 | 3.3364 | 1.0825 | 10.7707 | 14.2843 | 14.8337 | 11.0952 | -0.0007 | -0.0028 | 0.0006 | 0.0037 | 0.0008 | -0.0002 | 0.0145 | -0.0123 | 0.0134 | -360.1711 | 17.3823 | -360.3865 | 17.6184 | -360.722 | 18.1994 | -360.8543 | 17.5794 | -352.626 | 18.6963 | -352.5583 | 16.7889
12:42 | 4931 | 43.4457 | 202.6477 | 450.1801 | 457.0716 | -16.2857 | -40.2616 | 11.4604 | 8.1746 | 2.4265 | 0.9906 | 3.4217 | -1.0268 | 11.9685 | 4.6968 | 0.6185 | 0.6656 | 0.9616 | 0.7456 | -129.2747 | 0.5221 | 5.5927 | 1.8932 | -2.7998 | -1.0534 | 4.6421 |  | 3.6007 | 0.3093 | 4.0097 | 3.3643 | 3.337 | 1.0807 | 10.7776 | 14.28 | 14.843 | 11.084 | 0.0003 | -0.003 | 0.0013 | 0.0043 | 0.0014 | -0.0006 | 0.0191 | -0.0138 | 0.0131 | -360.1681 | 17.4213 | -360.4696 | 17.6615 | -360.802 | 18.1563 | -360.7497 | 17.5383 | -352.6044 | 18.7189 | -352.6475 | 16.834
12:42 | 4932 | 43.3018 | 202.5412 | 449.9595 | 456.9598 | -16.2346 | -40.3528 | 11.4484 | 8.1966 | 2.4498 | 0.9799 | 3.3615 | -0.9468 | 11.919 | 4.6285 | 0.6197 | 0.6659 | 0.9631 | 0.7458 | -129.3174 | 0.5001 | 5.6533 | 1.8144 | -2.7087 | -1.0148 | 4.6861 |  | 3.6054 | 0.2961 | 4.0087 | 3.3636 | 3.3372 | 1.0809 | 10.7638 | 14.2772 | 14.8603 | 11.0656 | -0.0001 | -0.0033 | 0.0007 | 0.0036 | 0.0002 | -0.0005 | 0.007 | 0.0047 | -0.0348 | -360.1404 | 17.3638 | -360.3927 | 17.6636 | -360.8143 | 18.1933 | -360.842 | 17.5383 | -352.5429 | 18.684 | -352.5952 | 16.8238
12:42 | 4933 | 43.2509 | 202.5095 | 449.9783 | 456.9324 | -16.3113 | -40.2917 | 11.4975 | 8.1003 | 2.4627 | 0.944 | 3.3791 | -0.9943 | 11.941 | 4.6893 | 0.6189 | 0.6666 | 0.9606 | 0.7456 | -129.237 | 0.5159 | 5.6767 | 1.8352 | -2.723 | -0.9263 | 4.7467 |  | 3.5624 | 0.3071 | 4.0097 | 3.3657 | 3.3354 | 1.0834 | 10.7753 | 14.295 | 14.8461 | 11.128 | -0.0003 | -0.0025 | 0.0011 | 0.0039 | 0.0011 | -0.0005 | 0.0111 | 0.0063 | -0.0082 | -360.1988 | 17.411 | -360.4112 | 17.6143 | -360.7373 | 18.1522 | -360.8174 | 17.5671 | -352.6352 | 18.7148 | -352.589 | 16.795
12:42 | 4934 | 43.3303 | 202.5574 | 450.0778 | 456.8842 | -16.3393 | -40.3158 | 11.4859 | 8.0634 | 2.4991 | 0.9557 | 3.3752 | -0.9375 | 11.932 | 4.6634 | 0.6195 | 0.6643 | 0.9556 | 0.7444 | -129.2163 | 0.528 | 5.7181 | 1.8791 | -2.6313 | -0.9911 | 4.7196 |  | 3.6295 | 0.3899 | 4.0102 | 3.365 | 3.3362 | 1.0813 | 10.811 | 14.2908 | 14.9028 | 11.0933 | -0.0002 | -0.0027 | 0.0011 | 0.0037 | 0.0005 | 0.0001 | 0.0172 | 0.006 | -0.0052 | -360.0973 | 17.3905 | -360.4819 | 17.6779 | -360.8389 | 18.1789 | -360.8112 | 17.5198 | -352.5736 | 18.7087 | -352.6567 | 16.8484
12:42 | 4935 | 43.2652 | 202.6159 | 450.011 | 456.9726 | -16.336 | -40.3897 | 11.4223 | 8.1388 | 2.4252 | 0.9452 | 3.3505 | -0.9848 | 11.9126 | 4.6997 | 0.6195 | 0.6655 | 0.9584 | 0.7427 | -129.291 | 0.4406 | 5.6879 | 1.9477 | -2.6744 | -0.9851 | 4.6959 |  | 3.5714 | 0.4482 | 4.009 | 3.3618 | 3.3387 | 1.0821 | 10.7857 | 14.3169 | 14.8389 | 11.1154 | 0.0003 | -0.0027 | 0.0003 | 0.0034 | 0.0008 | -0.0009 | 0.0089 | 0.0019 | -0.0125 | -360.165 | 17.3699 | -360.365 | 17.6348 | -360.7681 | 18.1994 | -360.8666 | 17.5691 | -352.6075 | 18.6881 | -352.5644 | 16.7971
12:42 | 4936 | 43.2869 | 202.6172 | 449.8952 | 456.9292 | -16.353 | -40.3575 | 11.4226 | 8.0689 | 2.4983 | 1.0215 | 3.3696 | -0.9271 | 11.9787 | 4.7653 | 0.6197 | 0.6684 | 0.9667 | 0.7451 | -129.4019 | 0.452 | 5.6292 | 1.7644 | -2.6686 | -1.0895 | 4.5629 |  | 3.5876 | 0.4434 | 4.0097 | 3.3629 | 3.3356 | 1.082 | 10.8052 | 14.3082 | 14.9028 | 11.1222 | 0.0004 | -0.0026 | 0.0007 | 0.0043 | 0.001 | 0 | 0.0299 | -0.0109 | -0.0116 | -360.1742 | 17.4336 | -360.4727 | 17.6759 | -360.7927 | 18.1502 | -360.7712 | 17.565 | -352.6229 | 18.7415 | -352.6506 | 16.8238
12:42 | 4937 | 43.2667 | 202.5681 | 449.9338 | 456.9102 | -16.3856 | -40.3899 | 11.3113 | 8.0508 | 2.4737 | 0.8756 | 3.4141 | -0.9463 | 12.0296 | 4.6636 | 0.6195 | 0.6663 | 0.9618 | 0.7443 | -129.3904 | 0.4083 | 5.6339 | 1.9153 | -2.7714 | -1.1558 | 4.4738 |  | 3.6762 | 0.3937 | 4.0099 | 3.3648 | 3.3355 | 1.0833 | 10.7915 | 14.2821 | 14.8957 | 11.1158 | -0.0004 | -0.0029 | 0.0002 | 0.0034 | 0.001 | -0.001 | 0.0321 | -0.0181 | -0.0263 | -360.1496 | 17.3864 | -360.4573 | 17.68 | -360.8143 | 18.1892 | -360.8297 | 17.5342 | -352.5583 | 18.7066 | -352.6167 | 16.8423
12:42 | 4938 | 43.2766 | 202.6486 | 449.895 | 456.9343 | -16.3725 | -40.379 | 11.3604 | 8.0585 | 2.4773 | 0.9673 | 3.3522 | -1.0084 | 11.9507 | 4.714 | 0.6202 | 0.6669 | 0.96 | 0.7447 | -129.4472 | 0.5143 | 5.6282 | 1.9839 | -2.8356 | -1.1967 | 4.5519 |  | 3.7292 | 0.3632 | 4.0091 | 3.3669 | 3.3389 | 1.0821 | 10.7857 | 14.2879 | 14.8494 | 11.0927 | -0.0003 | -0.0026 | 0.0007 | 0.0039 | 0.0004 | -0.0006 | 0.0257 | -0.0147 | -0.0126 | -360.1865 | 17.4007 | -360.4296 | 17.6512 | -360.7743 | 18.1851 | -360.8697 | 17.5835 | -352.6475 | 18.7148 | -352.6013 | 16.8012
12:42 | 4939 | 43.3157 | 202.6621 | 449.9868 | 456.9981 | -16.3164 | -40.3259 | 11.2908 | 8.0661 | 2.4868 | 1.0189 | 3.3024 | -1.0458 | 11.9825 | 4.6972 | 0.6199 | 0.6633 | 0.961 | 0.7456 | -129.3931 | 0.4533 | 5.6074 | 1.8418 | -2.7983 | -1.2762 | 4.5269 |  | 3.6269 | 0.4006 | 4.0101 | 3.3653 | 3.3405 | 1.0834 | 10.7822 | 14.2382 | 14.829 | 11.0486 | 0.0003 | -0.0027 | 0.0009 | 0.0042 | 0.0006 | -0.0006 | 0.0112 | -0.0047 | 0.0022 | -360.1558 | 17.4131 | -360.4942 | 17.6964 | -360.8327 | 18.1748 | -360.7927 | 17.5506 | -352.6136 | 18.7292 | -352.6721 | 16.8423
12:42 | 4940 | 43.2382 | 202.6776 | 449.9544 | 456.9706 | -16.3963 | -40.3955 | 11.2929 | 8.0698 | 2.4028 | 1.0126 | 3.3202 | -0.9816 | 11.9472 | 4.6953 | 0.6194 | 0.6642 | 0.9639 | 0.7442 | -129.3781 | 0.3908 | 5.6415 | 1.7572 | -2.8 | -1.1251 | 4.6437 |  | 3.5857 | 0.3804 | 4.0099 | 3.3644 | 3.3382 | 1.082 | 10.7881 | 14.2554 | 14.8627 | 11.101 | 0.0003 | -0.0032 | 0.0008 | 0.0035 | 0.0004 | -0.0007 | 0.0227 | 0.0009 | 0.004 | -360.1496 | 17.3802 | -360.4296 | 17.6636 | -360.8143 | 18.2138 | -360.8389 | 17.5732 | -352.6075 | 18.7004 | -352.5952 | 16.8238
12:42 | 4941 | 43.2309 | 202.583 | 450.0064 | 456.9731 | -16.382 | -40.3782 | 11.2547 | 8.0864 | 2.4118 | 1.0232 | 3.3377 | -0.835 | 11.9541 | 4.679 | 0.6194 | 0.6666 | 0.9628 | 0.7435 | -129.351 | 0.3964 | 5.6769 | 1.9413 | -2.7981 | -1.1348 | 4.6183 |  | 3.6032 | 0.3553 | 4.0097 | 3.3654 | 3.3369 | 1.0813 | 10.7463 | 14.2661 | 14.8403 | 11.0991 | 0.0003 | -0.0025 | 0.0009 | 0.0042 | 0.0003 | -0.0005 | -0.0072 | -0.0027 | -0.0146 | -360.2204 | 17.4315 | -360.4512 | 17.682 | -360.7743 | 18.181 | -360.8389 | 17.5794 | -352.6167 | 18.7374 | -352.6506 | 16.8217
12:42 | 4942 | 43.2899 | 202.66 | 450.006 | 456.9049 | -16.3845 | -40.3088 | 11.2858 | 8.1044 | 2.3401 | 1.0923 | 3.3201 | -0.8783 | 11.9303 | 4.7807 | 0.6198 | 0.6656 | 0.9589 | 0.7453 | -129.356 | 0.3363 | 5.559 | 2.043 | -2.7566 | -1.086 | 4.6655 |  | 3.6082 | 0.3415 | 4.0099 | 3.3655 | 3.342 | 1.0825 | 10.7856 | 14.2535 | 14.8458 | 11.0977 | 0.0001 | -0.0023 | 0.0008 | 0.0038 | 0.0009 | -0.0007 | 0.0163 | -0.0177 | -0.0088 | -360.1342 | 17.4069 | -360.4635 | 17.6964 | -360.8543 | 18.1933 | -360.8297 | 17.5609 | -352.5552 | 18.7148 | -352.629 | 16.834
12:42 | 4943 | 43.2895 | 202.6815 | 450.055 | 456.8884 | -16.3955 | -40.3155 | 11.298 | 8.0634 | 2.4333 | 1.1201 | 3.324 | -0.832 | 11.9633 | 4.8247 | 0.6198 | 0.6584 | 0.9614 | 0.7433 | -129.3582 | 0.455 | 5.5809 | 2.0134 | -2.8046 | -1.1298 | 4.6118 |  | 3.6235 | 0.2939 | 4.01 | 3.3621 | 3.3415 | 1.0816 | 10.7775 | 14.2686 | 14.8383 | 11.0894 | 0.0004 | -0.0026 | 0.0004 | 0.0034 | 0.0012 | 0.0005 | 0.0015 | 0.0057 | 0.0026 | -360.1958 | 17.4151 | -360.445 | 17.682 | -360.8112 | 18.1953 | -360.8481 | 17.5855 | -352.6413 | 18.7107 | -352.6352 | 16.8258
12:42 | 4944 | 43.236 | 202.6064 | 449.913 | 456.8842 | -16.3156 | -40.2727 | 11.4009 | 8.1476 | 2.3324 | 1.0754 | 3.3587 | -0.9164 | 11.9599 | 4.7686 | 0.6199 | 0.6624 | 0.9593 | 0.745 | -129.2325 | 0.4977 | 5.7116 | 1.8711 | -2.8622 | -1.134 | 4.5919 |  | 3.5434 | 0.2876 | 4.0109 | 3.3646 | 3.3403 | 1.0806 | 10.7718 | 14.3031 | 14.8488 | 11.084 | 0.0002 | -0.0029 | 0.0007 | 0.0039 | 0.001 | -0.0006 | 0.0123 | -0.0182 | -0.0159 | -360.1865 | 17.4233 | -360.4635 | 17.6985 | -360.8204 | 18.183 | -360.8143 | 17.5671 | -352.6198 | 18.7189 | -352.6136 | 16.832
12:42 | 4945 | 43.2325 | 202.7157 | 450.011 | 456.9294 | -16.2507 | -40.3477 | 11.3876 | 8.1247 | 2.2676 | 1.0286 | 3.2952 | -0.7943 | 12.0399 | 4.758 | 0.62 | 0.6645 | 0.9602 | 0.743 | -129.3592 | 0.4314 | 5.6691 | 1.8156 | -2.8275 | -1.2754 | 4.5589 |  | 3.6516 | 0.3216 | 4.0115 | 3.3628 | 3.3394 | 1.083 | 10.8087 | 14.3114 | 14.8526 | 11.0973 | 0.0001 | -0.0024 | 0.0005 | 0.0036 | 0.0007 | 0 | 0.0133 | -0.0024 | -0.0342 | -360.205 | 17.411 | -360.4696 | 17.6985 | -360.8204 | 18.2015 | -360.8697 | 17.5855 | -352.6198 | 18.7271 | -352.6567 | 16.834
12:42 | 4946 | 43.2645 | 202.6894 | 449.9431 | 456.8611 | -16.3149 | -40.3172 | 11.3819 | 8.0264 | 2.1864 | 0.973 | 3.4517 | -0.7835 | 11.9845 | 4.7815 | 0.6194 | 0.6642 | 0.9618 | 0.7433 | -129.3999 | 0.3093 | 5.6539 | 1.7702 | -2.78 | -1.2534 | 4.4545 |  | 3.5835 | 0.4197 | 4.009 | 3.3615 | 3.3372 | 1.0808 | 10.7904 | 14.2693 | 14.8481 | 11.0916 | -0.0005 | -0.0027 | 0.0006 | 0.0037 | 0.0007 | -0.0005 | 0.0314 | -0.0112 | -0.0209 | -360.2019 | 17.4233 | -360.4604 | 17.7026 | -360.8266 | 18.1851 | -360.845 | 17.5896 | -352.6013 | 18.7169 | -352.666 | 16.8423
12:42 | 4947 | 43.2042 | 202.6043 | 449.9599 | 456.8679 | -16.3507 | -40.0793 | 11.4339 | 8.0537 | 2.1706 | 1.0884 | 3.5068 | -0.7699 | 11.9132 | 4.6647 | 0.619 | 0.6657 | 0.9616 | 0.7443 | -129.4151 | 0.3354 | 5.6003 | 1.8353 | -2.7972 | -1.2138 | 4.5394 |  | 3.6214 | 0.3977 | 4.0096 | 3.3639 | 3.3397 | 1.0808 | 10.7938 | 14.2671 | 14.829 | 11.0717 | 0 | -0.0023 | 0.0013 | 0.0041 | 0.0003 | -0.0006 | 0.0117 | -0.0006 | -0.0117 | -360.165 | 17.4356 | -360.4789 | 17.7231 | -360.8512 | 18.2036 | -360.8389 | 17.5937 | -352.626 | 18.7107 | -352.6567 | 16.8484
12:42 | 4948 | 43.3016 | 202.7204 | 450.0735 | 456.9946 | -16.4249 | -40.0473 | 11.4702 | 8.035 | 2.1589 | 1.0688 | 3.5052 | -0.8293 | 11.9951 | 4.7058 | 0.6191 | 0.663 | 0.9638 | 0.7442 | -129.3406 | 0.4661 | 5.7215 | 1.8524 | -2.7556 | -1.2515 | 4.5589 |  | 3.6506 | 0.5283 | 4.0111 | 3.3663 | 3.3385 | 1.0818 | 10.7973 | 14.2533 | 14.8679 | 11.0923 | 0.0002 | -0.0031 | 0.0017 | 0.0042 | 0.0012 | -0.0003 | 0.0141 | 0.006 | -0.0052 | -360.1773 | 17.4233 | -360.4696 | 17.7026 | -360.802 | 18.2015 | -360.882 | 17.5794 | -352.6444 | 18.7292 | -352.6567 | 16.8402
12:42 | 4949 | 43.4216 | 202.6685 | 450.0157 | 457.001 | -16.3381 | -40.0763 | 11.4503 | 7.9826 | 2.1766 | 1.054 | 3.4782 | -0.8415 | 12.0439 | 4.7398 | 0.6206 | 0.6606 | 0.9636 | 0.7432 | -129.3382 | 0.5369 | 5.6413 | 1.9041 | -2.719 | -1.0838 | 4.5406 |  | 3.5908 | 0.4538 | 4.0093 | 3.3625 | 3.3358 | 1.0805 | 10.8077 | 14.2753 | 14.8549 | 11.097 | -0.0002 | -0.0033 | 0.0007 | 0.0039 | 0.0006 | -0.0005 | 0.0043 | -0.0092 | 0.0066 | -360.1988 | 17.4439 | -360.5035 | 17.7005 | -360.845 | 18.1974 | -360.8543 | 17.5773 | -352.6321 | 18.7374 | -352.6783 | 16.8464
12:42 | 4950 | 43.4359 | 202.6988 | 450.088 | 456.973 | -16.3693 | -40.0958 | 11.4231 | 8.0454 | 2.3044 | 1.1114 | 3.5967 | -0.8748 | 12.0227 | 4.6869 | 0.6191 | 0.6632 | 0.9639 | 0.7441 | -129.352 | 0.5379 | 5.7462 | 1.9629 | -2.7237 | -1.1258 | 4.5829 |  | 3.6051 | 0.4863 | 4.01 | 3.3626 | 3.3396 | 1.0816 | 10.7729 | 14.2987 | 14.857 | 11.1078 | -0.0004 | -0.0026 | 0.0011 | 0.0039 | 0.0012 | -0.0003 | 0.0024 | -0.0115 | -0.0051 | -360.2019 | 17.4151 | -360.4635 | 17.6964 | -360.8266 | 18.1933 | -360.8574 | 17.5876 | -352.6013 | 18.7169 | -352.6383 | 16.834
12:42 | 4951 | 43.2077 | 202.5903 | 449.9499 | 456.9771 | -16.4708 | -40.1246 | 11.5283 | 8.0965 | 2.2832 | 1.0223 | 3.4538 | -0.8567 | 12.0533 | 4.7076 | 0.6187 | 0.6604 | 0.9611 | 0.7447 | -129.4394 | 0.5508 | 5.6603 | 2.0738 | -2.6251 | -1.126 | 4.601 |  | 3.5882 | 0.4944 | 4.0107 | 3.3627 | 3.3379 | 1.0826 | 10.7846 | 14.2751 | 14.8365 | 11.0685 | 0 | -0.0031 | 0.0004 | 0.0035 | 0.0008 | -0.0004 | -0.0079 | -0.0073 | -0.0189 | -360.1865 | 17.4315 | -360.4758 | 17.6923 | -360.7958 | 18.1871 | -360.8327 | 17.5876 | -352.6567 | 18.7374 | -352.6567 | 16.8361
12:42 | 4952 | 43.2874 | 202.6444 | 450.0697 | 456.9434 | -16.4218 | -40.1955 | 11.49 | 8.0337 | 2.3108 | 0.9933 | 3.2462 | -0.9612 | 11.9913 | 4.7655 | 0.6205 | 0.662 | 0.9649 | 0.7438 | -129.3579 | 0.6112 | 5.7268 | 2.0803 | -2.6749 | -1.0277 | 4.5981 |  | 3.563 | 0.5644 | 4.01 | 3.3654 | 3.336 | 1.0822 | 10.7671 | 14.287 | 14.8212 | 11.0966 | 0.0004 | -0.0028 | 0.0011 | 0.0044 | 0.0009 | -0.0006 | 0.0185 | -0.0242 | -0.0089 | -360.1465 | 17.4131 | -360.4758 | 17.6902 | -360.842 | 18.1974 | -360.8481 | 17.5671 | -352.6167 | 18.7066 | -352.669 | 16.8402
12:42 | 4953 | 43.3414 | 202.7162 | 450.1707 | 457.0803 | -16.3856 | -40.1824 | 11.4023 | 8.0466 | 2.333 | 0.965 | 3.3282 | -0.8821 | 11.899 | 4.7141 | 0.6206 | 0.6648 | 0.9605 | 0.7437 | -129.4667 | 0.4254 | 5.5533 | 2.0958 | -2.6864 | -1.0369 | 4.518 |  | 3.5607 | 0.4575 | 4.0078 | 3.3662 | 3.3357 | 1.0821 | 10.7719 | 14.2739 | 14.8467 | 11.102 | 0.0002 | -0.0029 | 0.0006 | 0.0038 | 0.0008 | -0.0009 | 0.0205 | -0.0148 | -0.021 | -360.1804 | 17.4028 | -360.4481 | 17.682 | -360.7989 | 18.1871 | -360.8727 | 17.5753 | -352.6598 | 18.7066 | -352.6506 | 16.8156
12:42 | 4954 | 43.3327 | 202.6424 | 450.1338 | 457.032 | -16.476 | -40.215 | 11.5261 | 7.9806 | 2.3216 | 0.9557 | 3.2544 | -0.9497 | 11.9115 | 4.7039 | 0.6202 | 0.6607 | 0.9626 | 0.7439 | -129.4325 | 0.4634 | 5.6752 | 2.104 | -2.6772 | -1.1129 | 4.5725 |  | 3.5624 | 0.4021 | 4.0079 | 3.3639 | 3.3367 | 1.0808 | 10.7799 | 14.2936 | 14.8494 | 11.0811 | -0.0007 | -0.0027 | 0.0006 | 0.0037 | 0.0008 | -0.0001 | 0.0249 | 0.0101 | 0.0022 | -360.1896 | 17.411 | -360.4727 | 17.6861 | -360.7712 | 18.1645 | -360.8266 | 17.5629 | -352.6413 | 18.7189 | -352.6721 | 16.8238
12:42 | 4955 | 43.3942 | 202.7574 | 450.1912 | 457.0445 | -16.4082 | -40.1785 | 11.5054 | 7.9825 | 2.3291 | 0.9512 | 3.2935 | -0.8447 | 11.8588 | 4.7114 | 0.6205 | 0.6631 | 0.9617 | 0.7443 | -129.4723 | 0.5134 | 5.6273 | 2.1492 | -2.706 | -1.1705 | 4.638 |  | 3.6301 | 0.3341 | 4.0098 | 3.3644 | 3.3385 | 1.0821 | 10.7752 | 14.2604 | 14.8587 | 11.093 | -0.0002 | -0.0029 | 0.001 | 0.004 | 0.0012 | -0.0009 | 0.0016 | -0.0097 | -0.0097 | -360.1281 | 17.3823 | -360.4173 | 17.6841 | -360.8143 | 18.1933 | -360.8358 | 17.565 | -352.5829 | 18.6902 | -352.629 | 16.8238
12:42 | 4956 | 43.375 | 202.6865 | 450.0878 | 456.9723 | -16.3993 | -40.2028 | 11.5205 | 8.0528 | 2.4397 | 0.9681 | 3.2938 | -0.7944 | 11.9096 | 4.7139 | 0.6195 | 0.6599 | 0.9616 | 0.7437 | -129.445 | 0.5138 | 5.6389 | 2.1145 | -2.8098 | -1.0647 | 4.5826 |  | 3.589 | 0.3235 | 4.0098 | 3.3641 | 3.3404 | 1.0824 | 10.8181 | 14.2742 | 14.8836 | 11.1244 | 0.0001 | -0.0033 | 0.0011 | 0.0039 | 0.0008 | -0.0002 | 0.0065 | 0.0054 | -0.0192 | -360.1773 | 17.4151 | -360.4204 | 17.6636 | -360.7897 | 18.1645 | -360.845 | 17.5855 | -352.669 | 18.721 | -352.6075 | 16.8012
12:42 | 4957 | 43.4296 | 202.7489 | 450.2272 | 457.0475 | -16.3216 | -40.1606 | 11.4643 | 7.9869 | 2.4059 | 0.9711 | 3.2955 | -0.7493 | 12.0109 | 4.7303 | 0.62 | 0.6641 | 0.9604 | 0.7454 | -129.4632 | 0.5268 | 5.6096 | 2.1094 | -2.7519 | -1.0864 | 4.5298 |  | 3.6237 | 0.316 | 4.0109 | 3.3621 | 3.3407 | 1.0828 | 10.8064 | 14.2744 | 14.8788 | 11.1009 | 0.0005 | -0.0028 | 0.0013 | 0.0042 | 0.0011 | -0.0005 | 0.0064 | 0.0006 | 0.0036 | -360.1681 | 17.4069 | -360.4819 | 17.6902 | -360.802 | 18.1687 | -360.8143 | 17.5547 | -352.5952 | 18.7148 | -352.6629 | 16.8299
12:42 | 4958 | 43.3736 | 202.6489 | 450.0641 | 456.9476 | -16.4676 | -40.2447 | 11.4058 | 7.9398 | 2.4042 | 0.9374 | 3.2384 | -0.8527 | 11.9912 | 4.823 | 0.6192 | 0.6629 | 0.9619 | 0.7454 | -129.507 | 0.5349 | 5.5947 | 2.2264 | -2.7693 | -1.1037 | 4.6855 |  | 3.6214 | 0.4022 | 4.0105 | 3.3661 | 3.3365 | 1.0828 | 10.796 | 14.2698 | 14.886 | 11.1367 | -0.0002 | -0.0026 | 0.0005 | 0.0041 | 0.0006 | -0.0002 | 0.0197 | -0.0124 | -0.0183 | -360.1342 | 17.3802 | -360.4327 | 17.6779 | -360.7958 | 18.2056 | -360.8543 | 17.5691 | -352.5983 | 18.6922 | -352.6167 | 16.8238
12:42 | 4959 | 43.4012 | 202.6841 | 450.0903 | 456.9748 | -16.4192 | -40.2007 | 11.4651 | 8.0058 | 2.41 | 0.9814 | 3.297 | -0.8672 | 12.0177 | 4.776 | 0.6197 | 0.6597 | 0.9601 | 0.7429 | -129.4305 | 0.5925 | 5.7055 | 2.1214 | -2.7403 | -1.086 | 4.6221 |  | 3.5387 | 0.3759 | 4.0089 | 3.3668 | 3.3371 | 1.0834 | 10.7867 | 14.2779 | 14.8598 | 11.1099 | -0.0002 | -0.0024 | 0.0002 | 0.0039 | 0.0013 | -0.0008 | 0.0044 | 0.0027 | -0.0024 | -360.1927 | 17.4131 | -360.405 | 17.6615 | -360.7435 | 18.1584 | -360.8174 | 17.5753 | -352.629 | 18.723 | -352.6229 | 16.795
12:42 | 4960 | 43.4459 | 202.732 | 450.1422 | 456.9539 | -16.3125 | -40.1594 | 11.495 | 7.9737 | 2.391 | 0.998 | 3.2764 | -0.9413 | 11.9528 | 4.8196 | 0.6197 | 0.6629 | 0.9615 | 0.7448 | -129.4858 | 0.5227 | 5.6047 | 2.1356 | -2.6529 | -1.1037 | 4.6496 |  | 3.5484 | 0.2971 | 4.0087 | 3.3669 | 3.3401 | 1.0824 | 10.7995 | 14.2904 | 14.8764 | 11.1175 | 0.0005 | -0.0028 | 0.0006 | 0.004 | -0.0001 | -0.0007 | 0.0315 | -0.0078 | -0.0289 | -360.1373 | 17.3966 | -360.4635 | 17.6985 | -360.8235 | 18.1748 | -360.7897 | 17.5547 | -352.589 | 18.7128 | -352.6506 | 16.8381
12:42 | 4961 | 43.4623 | 202.7398 | 450.146 | 456.9133 | -16.403 | -40.0666 | 11.4647 | 7.908 | 2.2579 | 0.8077 | 3.1878 | -0.8684 | 11.9303 | 4.8035 | 0.6203 | 0.6654 | 0.9617 | 0.7466 | -129.53 | 0.4512 | 5.6464 | 2.1744 | -2.6115 | -0.9715 | 4.6342 |  | 3.5932 | 0.3751 | 4.0106 | 3.3683 | 3.3384 | 1.0837 | 10.7776 | 14.2742 | 14.8372 | 11.084 | 0.0002 | -0.003 | 0.0008 | 0.0042 | 0.0012 | -0.0005 | 0.0175 | -0.0016 | -0.0076 | -360.1127 | 17.372 | -360.3742 | 17.6697 | -360.7927 | 18.1871 | -360.8389 | 17.5609 | -352.6075 | 18.684 | -352.5921 | 16.8115
12:42 | 4962 | 43.4174 | 202.6504 | 450.0803 | 456.8962 | -16.3493 | -40.0698 | 11.5169 | 7.9678 | 2.3866 | 0.8803 | 3.1916 | -0.8685 | 11.9543 | 4.7833 | 0.6189 | 0.6625 | 0.9606 | 0.7442 | -129.5422 | 0.4987 | 5.6541 | 2.1858 | -2.6293 | -0.9455 | 4.6657 |  | 3.5399 | 0.2792 | 4.0096 | 3.3677 | 3.3381 | 1.0831 | 10.7833 | 14.2686 | 14.8499 | 11.0894 | 0 | -0.0024 | 0.001 | 0.0039 | 0.0009 | -0.0003 | 0.0229 | -0.0029 | 0.0163 | -360.205 | 17.4233 | -360.4296 | 17.6594 | -360.7527 | 18.1522 | -360.7958 | 17.5671 | -352.629 | 18.7312 | -352.6229 | 16.7971
12:42 | 4963 | 43.4062 | 202.6455 | 450.1041 | 456.9448 | -16.3801 | -40.0639 | 11.5251 | 8.0163 | 2.377 | 0.9009 | 3.3048 | -0.8687 | 11.9713 | 4.8642 | 0.6199 | 0.6641 | 0.9633 | 0.7461 | -129.4934 | 0.4545 | 5.5815 | 2.1379 | -2.5959 | -0.9303 | 4.6498 |  | 3.6406 | 0.3199 | 4.0092 | 3.3673 | 3.3421 | 1.0819 | 10.7845 | 14.2695 | 14.8549 | 11.097 | -0.0002 | -0.0025 | 0.0013 | 0.0042 | 0.0007 | -0.0008 | -0.0041 | -0.0073 | -0.005 | -360.1373 | 17.3823 | -360.4481 | 17.6861 | -360.8081 | 18.1707 | -360.7958 | 17.5321 | -352.5613 | 18.6943 | -352.6475 | 16.8197
12:42 | 4964 | 43.3801 | 202.6511 | 450.0976 | 457.0273 | -16.3712 | -40.1629 | 11.4981 | 8.0417 | 2.3783 | 0.8777 | 3.2937 | -0.7988 | 11.9117 | 4.9267 | 0.62 | 0.6629 | 0.9614 | 0.7464 | -129.4926 | 0.4772 | 5.6101 | 2.0508 | -2.6803 | -1.076 | 4.6248 |  | 3.6192 | 0.3055 | 4.0113 | 3.3659 | 3.3374 | 1.0819 | 10.8018 | 14.2929 | 14.8686 | 11.1078 | 0.0002 | -0.0028 | 0.0009 | 0.0035 | 0.0011 | -0.0002 | 0.0068 | 0.0022 | -0.0078 | -360.1773 | 17.3905 | -360.4112 | 17.6512 | -360.7835 | 18.1707 | -360.8327 | 17.5814 | -352.6106 | 18.6861 | -352.5644 | 16.7889
12:42 | 4965 | 43.3725 | 202.5759 | 450.0773 | 456.9398 | -16.3385 | -40.0988 | 11.4667 | 8.0328 | 2.3655 | 0.903 | 3.2716 | -0.89 | 11.918 | 4.8038 | 0.6188 | 0.6656 | 0.9624 | 0.7452 | -129.4256 | 0.5631 | 5.7546 | 2.0443 | -2.6948 | -1.0223 | 4.6282 |  | 3.6055 | 0.3012 | 4.0091 | 3.3672 | 3.3391 | 1.0832 | 10.7834 | 14.2856 | 14.8535 | 11.1017 | 0 | -0.0032 | 0.0009 | 0.0035 | 0.0002 | -0.0005 | 0.008 | -0.0122 | -0.0074 | -360.1927 | 17.4172 | -360.4604 | 17.6677 | -360.7804 | 18.1481 | -360.7681 | 17.5465 | -352.6106 | 18.7189 | -352.6413 | 16.8074
12:42 | 4966 | 43.4047 | 202.622 | 450.0989 | 456.9864 | -16.3698 | -40.2288 | 11.4293 | 8.0363 | 2.3833 | 0.9629 | 3.2569 | -0.8547 | 11.8855 | 4.8024 | 0.6193 | 0.6604 | 0.9618 | 0.7453 | -129.4066 | 0.476 | 5.7086 | 2.0456 | -2.6291 | -1.0403 | 4.6763 |  | 3.6996 | 0.3673 | 4.0088 | 3.3685 | 3.3423 | 1.0839 | 10.7777 | 14.2738 | 14.8398 | 11.1082 | -0.0003 | -0.003 | 0.0004 | 0.0036 | 0.0007 | -0.0008 | 0.0142 | 0.0012 | 0.0042 | -360.125 | 17.3782 | -360.4266 | 17.6759 | -360.8235 | 18.1994 | -360.8358 | 17.5486 | -352.5613 | 18.6881 | -352.5921 | 16.8176
12:42 | 4967 | 43.3017 | 202.5177 | 450.0323 | 456.9537 | -16.4675 | -40.1606 | 11.4714 | 8.0412 | 2.4573 | 0.8852 | 3.2357 | -0.8989 | 11.9342 | 4.7398 | 0.621 | 0.6649 | 0.9643 | 0.7473 | -129.4255 | 0.5255 | 5.6763 | 1.9879 | -2.7391 | -0.981 | 4.6405 |  | 3.657 | 0.3652 | 4.0109 | 3.3656 | 3.3409 | 1.0841 | 10.7961 | 14.2754 | 14.8444 | 11.085 | 0.0001 | -0.0024 | 0.0003 | 0.0034 | 0.0006 | -0.0003 | -0.0057 | -0.0085 | -0.0319 | -360.205 | 17.4172 | -360.4173 | 17.6389 | -360.7681 | 18.1687 | -360.8327 | 17.5917 | -352.6721 | 18.721 | -352.5798 | 16.7848
12:43 | 4968 | 43.337 | 202.5606 | 449.989 | 457.0295 | -16.4696 | -40.1515 | 11.5886 | 8.0081 | 2.4696 | 0.9334 | 3.2003 | -0.8674 | 11.9714 | 4.7364 | 0.6219 | 0.6594 | 0.9624 | 0.7458 | -129.3787 | 0.5453 | 5.7292 | 2.0582 | -2.6802 | -0.9594 | 4.7213 |  | 3.6568 | 0.3603 | 4.0105 | 3.3665 | 3.3379 | 1.0821 | 10.7812 | 14.2656 | 14.8371 | 11.0945 | 0 | -0.0031 | 0.0005 | 0.0038 | 0.0006 | -0.0012 | 0.0011 | -0.0065 | 0.0036 | -360.2111 | 17.4254 | -360.5035 | 17.7067 | -360.8543 | 18.1728 | -360.805 | 17.5465 | -352.6075 | 18.7374 | -352.6844 | 16.8279
12:43 | 4969 | 43.3077 | 202.5553 | 450.0628 | 456.9758 | -16.4156 | -40.2241 | 11.5626 | 8.0627 | 2.5026 | 0.9845 | 3.2534 | -0.9276 | 11.9551 | 4.6646 | 0.621 | 0.6644 | 0.9604 | 0.7452 | -129.3683 | 0.4643 | 5.7476 | 2.0928 | -2.6906 | -0.9675 | 4.6337 |  | 3.6033 | 0.2721 | 4.0102 | 3.3668 | 3.3398 | 1.0824 | 10.7649 | 14.296 | 14.8117 | 11.1006 | 0.0002 | -0.003 | 0.0007 | 0.0038 | 0.0003 | -0.0005 | 0.0074 | 0.0088 | -0.0084 | -360.1373 | 17.4048 | -360.4389 | 17.6944 | -360.8604 | 18.22 | -360.8974 | 17.5773 | -352.6075 | 18.7004 | -352.6198 | 16.8238
12:43 | 4970 | 43.3249 | 202.591 | 450.1391 | 456.9714 | -16.3912 | -40.274 | 11.4946 | 8.0105 | 2.5469 | 1.0268 | 3.3589 | -0.8622 | 12.0119 | 4.6995 | 0.6204 | 0.6626 | 0.9622 | 0.7457 | -129.4188 | 0.4428 | 5.6633 | 2.0672 | -2.7562 | -0.98 | 4.5973 |  | 3.6326 | 0.2916 | 4.01 | 3.3656 | 3.3376 | 1.0827 | 10.7834 | 14.2625 | 14.8362 | 11.1132 | 0.0001 | -0.0026 | 0.0008 | 0.0039 | 0.0009 | -0.0009 | 0.0106 | 0.0062 | 0.0093 | -360.2388 | 17.4459 | -360.4758 | 17.6738 | -360.7897 | 18.1728 | -360.8512 | 17.5937 | -352.706 | 18.7497 | -352.669 | 16.8032
12:43 | 4971 | 43.3456 | 202.5902 | 450.087 | 456.911 | -16.4767 | -40.3391 | 11.467 | 8.0545 | 2.53 | 0.9518 | 3.2358 | -0.8938 | 11.954 | 4.7892 | 0.6204 | 0.6638 | 0.9604 | 0.7456 | -129.4619 | 0.5762 | 5.5681 | 1.9397 | -2.8637 | -1.1053 | 4.5001 |  | 3.6125 | 0.3037 | 4.0101 | 3.3663 | 3.3365 | 1.0826 | 10.7926 | 14.3067 | 14.8703 | 11.093 | -0.0004 | -0.0026 | 0.0011 | 0.0037 | 0.0007 | -0.0001 | 0.0191 | -0.0135 | -0.0014 | -360.1865 | 17.4315 | -360.4973 | 17.721 | -360.8974 | 18.2015 | -360.8235 | 17.5629 | -352.5952 | 18.723 | -352.706 | 16.8525
12:43 | 4972 | 43.4438 | 202.6823 | 450.1545 | 456.9738 | -16.4352 | -40.2402 | 11.4264 | 8.0584 | 2.5359 | 0.949 | 3.2591 | -0.9915 | 11.8885 | 4.6661 | 0.6193 | 0.6619 | 0.9605 | 0.7447 | -129.4501 | 0.5232 | 5.5896 | 1.8606 | -2.7652 | -1.2012 | 4.5766 |  | 3.6147 | 0.2845 | 4.0095 | 3.3641 | 3.3371 | 1.0828 | 10.7718 | 14.2684 | 14.8662 | 11.1129 | 0.0001 | -0.0028 | 0.001 | 0.0039 | 0.001 | -0.0008 | -0.0035 | -0.0045 | -0.0085 | -360.2296 | 17.4048 | -360.4173 | 17.6636 | -360.8143 | 18.222 | -360.8974 | 17.6061 | -352.6598 | 18.721 | -352.6198 | 16.8156
12:43 | 4973 | 43.4198 | 202.6189 | 450.0609 | 456.9256 | -16.3323 | -40.2053 | 11.5191 | 8.0364 | 2.5182 | 0.9768 | 3.2931 | -0.9681 | 11.9148 | 4.6373 | 0.62 | 0.6624 | 0.9623 | 0.7469 | -129.4951 | 0.5141 | 5.5337 | 1.8158 | -2.8225 | -1.2242 | 4.5858 |  | 3.6685 | 0.4039 | 4.0085 | 3.363 | 3.3378 | 1.0828 | 10.8089 | 14.2821 | 14.8842 | 11.1331 | -0.0003 | -0.0033 | 0.0008 | 0.0037 | 0.0005 | -0.0002 | -0.0042 | -0.0197 | -0.0163 | -360.2758 | 17.4521 | -360.5066 | 17.6923 | -360.8235 | 18.1748 | -360.8389 | 17.5917 | -352.6783 | 18.7723 | -352.706 | 16.8258
12:43 | 4974 | 43.3756 | 202.6357 | 450.0768 | 456.897 | -16.4413 | -40.0989 | 11.4784 | 8.0325 | 2.5226 | 0.8551 | 3.2894 | -1.0043 | 11.9331 | 4.7733 | 0.6179 | 0.6646 | 0.9616 | 0.7455 | -129.5294 | 0.4937 | 5.4951 | 1.8584 | -2.8178 | -1.1999 | 4.5278 |  | 3.611 | 0.3626 | 4.0098 | 3.363 | 3.3398 | 1.0835 | 10.7857 | 14.2707 | 14.8737 | 11.1154 | -0.0002 | -0.0029 | 0.0006 | 0.004 | 0.0008 | -0.0007 | 0.0086 | -0.0025 | -0.0205 | -360.1435 | 17.4028 | -360.4604 | 17.7026 | -360.8666 | 18.2179 | -360.8604 | 17.5671 | -352.6075 | 18.7025 | -352.6721 | 16.8546
12:43 | 4975 | 43.2589 | 202.6114 | 450.0477 | 456.8691 | -16.4592 | -40.1258 | 11.4669 | 8.0584 | 2.4562 | 0.9024 | 3.2523 | -0.9426 | 11.8932 | 4.669 | 0.619 | 0.6633 | 0.9614 | 0.7452 | -129.469 | 0.5328 | 5.5087 | 2.0164 | -2.7695 | -1.1604 | 4.5678 |  | 3.6444 | 0.4991 | 4.0092 | 3.3636 | 3.3389 | 1.0825 | 10.7788 | 14.252 | 14.8365 | 11.0685 | -0.0006 | -0.0027 | 0.0006 | 0.0041 | 0.0009 | -0.0003 | 0.0026 | -0.0068 | -0.0053 | -360.2358 | 17.4274 | -360.4327 | 17.6594 | -360.7958 | 18.2015 | -360.9004 | 17.6102 | -352.709 | 18.7395 | -352.6352 | 16.8032
12:43 | 4976 | 43.2884 | 202.563 | 450.0637 | 456.8478 | -16.4735 | -40.1352 | 11.4779 | 8.0912 | 2.4208 | 0.872 | 3.2634 | -0.8572 | 11.942 | 4.7365 | 0.6197 | 0.6601 | 0.9622 | 0.746 | -129.5271 | 0.4576 | 5.5757 | 2.0695 | -2.7502 | -0.9847 | 4.5489 |  | 3.6893 | 0.4556 | 4.0079 | 3.3662 | 3.3363 | 1.0842 | 10.7961 | 14.2985 | 14.8734 | 11.1082 | 0.0001 | -0.0027 | 0.0009 | 0.0044 | 0.0006 | 0 | 0.0117 | -0.0029 | -0.0053 | -360.1988 | 17.4336 | -360.4881 | 17.7005 | -360.842 | 18.1707 | -360.7989 | 17.5671 | -352.6537 | 18.7456 | -352.6998 | 16.8381
12:43 | 4977 | 43.3469 | 202.5913 | 450.0975 | 457.0093 | -16.531 | -40.1439 | 11.4648 | 8.0492 | 2.3556 | 0.7424 | 3.2535 | -0.9178 | 11.9292 | 4.7204 | 0.6194 | 0.6578 | 0.9598 | 0.7461 | -129.4742 | 0.5434 | 5.6011 | 2.2122 | -2.7231 | -0.9396 | 4.7416 |  | 3.7022 | 0.4399 | 4.0085 | 3.3629 | 3.3395 | 1.0825 | 10.8145 | 14.323 | 14.8526 | 11.1089 | 0.0001 | -0.0033 | 0.0009 | 0.0042 | 0.0008 | -0.0004 | 0.0146 | -0.0049 | -0.0098 | -360.1619 | 17.3884 | -360.4235 | 17.6841 | -360.842 | 18.2344 | -360.8974 | 17.5794 | -352.629 | 18.6984 | -352.626 | 16.832
12:43 | 4978 | 43.3126 | 202.5458 | 450.0308 | 456.9916 | -16.4803 | -40.1781 | 11.4703 | 8.0649 | 2.4513 | 0.8774 | 3.2809 | -0.9158 | 11.9074 | 4.6703 | 0.6209 | 0.664 | 0.9597 | 0.7433 | -129.4703 | 0.5591 | 5.5591 | 2.0966 | -2.6279 | -1.0073 | 4.6667 |  | 3.6072 | 0.3715 | 4.0086 | 3.3674 | 3.3379 | 1.084 | 10.7731 | 14.2632 | 14.8633 | 11.0981 | -0.0001 | -0.0029 | 0.0008 | 0.0037 | 0.0005 | -0.0004 | 0.0004 | -0.0126 | -0.0165 | -360.2019 | 17.4233 | -360.4604 | 17.6533 | -360.765 | 18.1748 | -360.8512 | 17.5896 | -352.666 | 18.7374 | -352.6752 | 16.7971
12:43 | 4979 | 43.4231 | 202.5232 | 450.0312 | 456.9499 | -16.5943 | -40.162 | 11.3551 | 8.0804 | 2.3335 | 0.9014 | 3.3147 | -0.8538 | 11.955 | 4.7271 | 0.6204 | 0.6628 | 0.9614 | 0.7451 | -129.4847 | 0.5451 | 5.5213 | 2.1378 | -2.6345 | -0.9851 | 4.6937 |  | 3.6977 | 0.4538 | 4.0105 | 3.366 | 3.3382 | 1.0815 | 10.8007 | 14.3033 | 14.8383 | 11.0951 | -0.0003 | -0.0025 | 0.0011 | 0.004 | 0.0012 | -0.0004 | 0.0078 | -0.0012 | -0.0196 | -360.1588 | 17.4172 | -360.4789 | 17.7087 | -360.8666 | 18.1912 | -360.7897 | 17.5424 | -352.6106 | 18.7333 | -352.6967 | 16.8484
12:43 | 4980 | 43.4021 | 202.6158 | 450.0824 | 456.8783 | -16.5153 | -40.1463 | 11.4403 | 8.0488 | 2.3381 | 0.7914 | 3.2843 | -0.8538 | 11.9768 | 4.8122 | 0.6213 | 0.6619 | 0.9579 | 0.7455 | -129.4677 | 0.5287 | 5.448 | 1.9916 | -2.7331 | -1.0842 | 4.5897 |  | 3.7175 | 0.5094 | 4.0102 | 3.3679 | 3.3384 | 1.0825 | 10.8146 | 14.2997 | 14.9095 | 11.1266 | -0.0006 | -0.0034 | 0.0007 | 0.0034 | 0.0005 | -0.0005 | 0.0101 | -0.0057 | -0.0205 | -360.1865 | 17.3843 | -360.4019 | 17.6512 | -360.7835 | 18.2077 | -360.8758 | 17.5958 | -352.666 | 18.7045 | -352.6198 | 16.8012
12:43 | 4981 | 43.376 | 202.5289 | 450.0578 | 456.8828 | -16.5184 | -40.1132 | 11.4237 | 8.1098 | 2.3844 | 0.8037 | 3.2365 | -0.8146 | 11.9068 | 4.6862 | 0.6202 | 0.6642 | 0.9623 | 0.7452 | -129.5228 | 0.474 | 5.4515 | 2.041 | -2.6866 | -1.0095 | 4.6362 |  | 3.6935 | 0.6017 | 4.0093 | 3.3656 | 3.3377 | 1.0813 | 10.7913 | 14.3232 | 14.9058 | 11.1374 | 0.0005 | -0.003 | 0.0009 | 0.0041 | 0.0014 | -0.0005 | 0.009 | -0.0036 | -0.0089 | -360.2142 | 17.4295 | -360.4912 | 17.6718 | -360.7989 | 18.1645 | -360.8266 | 17.5773 | -352.6752 | 18.7477 | -352.6967 | 16.8176
12:43 | 4982 | 43.4385 | 202.4721 | 450.0505 | 456.9225 | -16.4376 | -40.1179 | 11.442 | 8.0879 | 2.2685 | 0.6727 | 3.1773 | -0.9273 | 11.8526 | 4.6586 | 0.62 | 0.6596 | 0.9632 | 0.7448 | -129.4996 | 0.5986 | 5.5694 | 2.0894 | -2.7092 | -1.051 | 4.6693 |  | 3.669 | 0.5062 | 4.0103 | 3.3653 | 3.3364 | 1.0821 | 10.7949 | 14.3091 | 14.8499 | 11.1009 | 0 | -0.0032 | 0.0007 | 0.004 | 0.0006 | 0 | 0.0242 | -0.0145 | -0.0124 | -360.1281 | 17.3843 | -360.4727 | 17.6985 | -360.8389 | 18.1851 | -360.8174 | 17.5506 | -352.5921 | 18.7004 | -352.6506 | 16.8443
12:43 | 4983 | 43.3579 | 202.4602 | 450.0305 | 456.9824 | -16.3644 | -40.2127 | 11.4276 | 8.1502 | 2.3028 | 0.6926 | 3.2554 | -0.8688 | 11.9155 | 4.6881 | 0.6198 | 0.6608 | 0.9623 | 0.7445 | -129.3819 | 0.5368 | 5.5197 | 2.0738 | -2.7167 | -1.0643 | 4.5985 |  | 3.6779 | 0.4161 | 4.01 | 3.368 | 3.3403 | 1.0834 | 10.8388 | 14.307 | 14.8898 | 11.1038 | -0.0001 | -0.0023 | 0.0011 | 0.0044 | 0.0007 | -0.0006 | -0.0034 | -0.0113 | -0.0146 | -360.1988 | 17.4007 | -360.3989 | 17.6451 | -360.762 | 18.1645 | -360.8943 | 17.602 | -352.7121 | 18.721 | -352.6229 | 16.7909
12:43 | 4984 | 43.4124 | 202.6134 | 450.0465 | 456.9979 | -16.3475 | -40.1912 | 11.4715 | 8.1824 | 2.3459 | 0.7303 | 3.2713 | -0.8648 | 11.9152 | 4.6928 | 0.6197 | 0.6648 | 0.9636 | 0.7447 | -129.4627 | 0.4513 | 5.6313 | 2.0885 | -2.7343 | -1.0209 | 4.6171 |  | 3.6816 | 0.4927 | 4.0103 | 3.3634 | 3.3363 | 1.0822 | 10.7891 | 14.2628 | 14.8094 | 11.0836 | 0.0002 | -0.0025 | 0.0003 | 0.0043 | 0.0006 | -0.0003 | 0.0128 | -0.0101 | 0.0088 | -360.1619 | 17.4213 | -360.4758 | 17.6861 | -360.8327 | 18.1379 | -360.7804 | 17.5445 | -352.6413 | 18.723 | -352.6721 | 16.8361
12:43 | 4985 | 43.436 | 202.5524 | 450.0294 | 456.9801 | -16.4052 | -40.2161 | 11.5257 | 8.1696 | 2.3237 | 0.753 | 3.2572 | -0.8064 | 11.9633 | 4.7304 | 0.6208 | 0.6624 | 0.9611 | 0.7448 | -129.4033 | 0.4518 | 5.6085 | 1.9761 | -2.5861 | -1.0289 | 4.6341 |  | 3.7079 | 0.4519 | 4.0111 | 3.3663 | 3.339 | 1.0833 | 10.7927 | 14.2715 | 14.8382 | 11.0883 | 0.0001 | -0.0029 | 0.0007 | 0.004 | 0.001 | -0.0006 | 0.0281 | -0.0029 | 0.0049 | -360.1435 | 17.3761 | -360.4081 | 17.6656 | -360.8235 | 18.1851 | -360.8789 | 17.5753 | -352.6136 | 18.6881 | -352.6075 | 16.8115
12:43 | 4986 | 43.393 | 202.5742 | 450.0404 | 456.9657 | -16.4055 | -40.2488 | 11.4845 | 8.1414 | 2.3702 | 0.7469 | 3.2867 | -0.8636 | 11.9688 | 4.7859 | 0.6208 | 0.6611 | 0.9638 | 0.7456 | -129.3769 | 0.4452 | 5.572 | 1.9587 | -2.7086 | -1.0905 | 4.556 |  | 3.7788 | 0.4978 | 4.0102 | 3.3664 | 3.3382 | 1.0835 | 10.773 | 14.2463 | 14.8549 | 11.1201 | 0.0004 | -0.0029 | 0.0006 | 0.0035 | 0.0009 | -0.0003 | 0.0065 | -0.0191 | -0.0149 | -360.2019 | 17.4192 | -360.4081 | 17.6471 | -360.7435 | 18.1317 | -360.8204 | 17.5835 | -352.6537 | 18.7312 | -352.629 | 16.7889
12:43 | 4987 | 43.4027 | 202.6149 | 450.0097 | 456.8976 | -16.3355 | -40.2466 | 11.4804 | 8.0892 | 2.3376 | 0.8149 | 3.2804 | -0.9174 | 11.9371 | 4.7343 | 0.6184 | 0.66 | 0.9615 | 0.7443 | -129.4279 | 0.3942 | 5.5148 | 1.9748 | -2.6509 | -1.0873 | 4.631 |  | 3.7489 | 0.5602 | 4.0117 | 3.3646 | 3.3356 | 1.083 | 10.7695 | 14.2718 | 14.8229 | 11.0876 | -0.0003 | -0.0027 | 0.0012 | 0.0042 | 0.0009 | -0.0001 | 0.0039 | -0.0163 | -0.0108 | -360.1311 | 17.3884 | -360.4419 | 17.6944 | -360.8389 | 18.1481 | -360.8174 | 17.5445 | -352.589 | 18.7107 | -352.6413 | 16.8402
12:43 | 4988 | 43.4066 | 202.6359 | 450.0835 | 456.9697 | -16.3408 | -40.2384 | 11.4583 | 8.1019 | 2.3869 | 0.7528 | 3.3335 | -0.9388 | 11.9118 | 4.722 | 0.6203 | 0.66 | 0.9625 | 0.7469 | -129.3724 | 0.4475 | 5.5448 | 2.0747 | -2.7421 | -1.2077 | 4.5445 |  | 3.7872 | 0.6316 | 4.0117 | 3.363 | 3.3372 | 1.0838 | 10.7846 | 14.2693 | 14.8481 | 11.1089 | -0.0001 | -0.0025 | 0.0014 | 0.004 | 0.0011 | -0.0004 | 0.0043 | -0.0035 | -0.0173 | -360.1804 | 17.3699 | -360.3527 | 17.643 | -360.7589 | 18.1625 | -360.8697 | 17.5876 | -352.5983 | 18.6902 | -352.5521 | 16.7786
12:43 | 4989 | 43.4022 | 202.5951 | 449.9383 | 456.8759 | -16.4401 | -40.3071 | 11.4445 | 8.1382 | 2.4129 | 0.8024 | 3.3341 | -0.9363 | 11.9739 | 4.7455 | 0.6192 | 0.6584 | 0.9642 | 0.7472 | -129.4634 | 0.5683 | 5.5081 | 2.043 | -2.6998 | -1.0151 | 4.5552 |  | 3.7426 | 0.5701 | 4.0116 | 3.3689 | 3.3388 | 1.0834 | 10.7706 | 14.2846 | 14.8243 | 11.0713 | 0.0001 | -0.0028 | 0.0004 | 0.0037 | 0.001 | 0 | 0.0039 | -0.0143 | -0.0205 | -360.1496 | 17.4131 | -360.4266 | 17.6697 | -360.7681 | 18.1276 | -360.7497 | 17.5712 | -352.6229 | 18.7271 | -352.6321 | 16.8074
12:43 | 4990 | 43.4213 | 202.5391 | 450.0688 | 456.9039 | -16.431 | -40.2078 | 11.3682 | 8.168 | 2.4908 | 0.9161 | 3.2979 | -1.0024 | 12.0168 | 4.6774 | 0.6188 | 0.6551 | 0.9638 | 0.7449 | -129.4977 | 0.5794 | 5.5037 | 2.0022 | -2.8304 | -0.9842 | 4.5518 |  | 3.7671 | 0.6383 | 4.0119 | 3.3667 | 3.3369 | 1.0834 | 10.7995 | 14.2963 | 14.8659 | 11.1172 | 0.0005 | -0.0025 | 0.0004 | 0.0038 | 0.0008 | -0.0007 | 0.0087 | -0.0028 | 0.0086 | -360.1588 | 17.374 | -360.405 | 17.6738 | -360.8266 | 18.1645 | -360.845 | 17.5691 | -352.5583 | 18.6943 | -352.6075 | 16.8053
12:43 | 4991 | 43.4796 | 202.5743 | 450.0363 | 456.9181 | -16.5074 | -40.2039 | 11.3899 | 8.1451 | 2.478 | 0.8594 | 3.2298 | -0.9556 | 11.9858 | 4.7547 | 0.6201 | 0.6603 | 0.9643 | 0.7458 | -129.4413 | 0.6298 | 5.5747 | 2.046 | -2.8305 | -1.0355 | 4.5442 |  | 3.785 | 0.6184 | 4.0097 | 3.3662 | 3.3371 | 1.0839 | 10.8204 | 14.2996 | 14.9084 | 11.1038 | -0.0002 | -0.0029 | 0.0008 | 0.0038 | 0.0004 | -0.0005 | -0.0058 | 0.0057 | -0.0057 | -360.1527 | 17.4028 | -360.405 | 17.641 | -360.7404 | 18.1399 | -360.8174 | 17.5876 | -352.5829 | 18.7066 | -352.6013 | 16.7889
12:43 | 4992 | 43.3997 | 202.5449 | 450.0387 | 456.953 | -16.4214 | -40.2062 | 11.4432 | 8.1576 | 2.5591 | 0.8924 | 3.2561 | -0.8665 | 11.9609 | 4.7402 | 0.6185 | 0.6567 | 0.9621 | 0.7442 | -129.4249 | 0.5481 | 5.5989 | 1.965 | -2.8216 | -1.1678 | 4.531 |  | 3.732 | 0.4975 | 4.0104 | 3.3626 | 3.3371 | 1.0835 | 10.7776 | 14.2972 | 14.8535 | 11.119 | -0.0003 | -0.0027 | 0.0005 | 0.0041 | 0.0011 | -0.001 | 0.0167 | -0.012 | 0.0016 | -360.1527 | 17.4028 | -360.4573 | 17.6882 | -360.7712 | 18.1399 | -360.7897 | 17.5609 | -352.6044 | 18.7148 | -352.6383 | 16.8197
12:43 | 4993 | 43.4469 | 202.5151 | 450.0712 | 456.9644 | -16.4428 | -40.2105 | 11.4961 | 8.0667 | 2.4097 | 0.8359 | 3.1326 | -0.906 | 11.9943 | 4.87 | 0.62 | 0.6617 | 0.9622 | 0.746 | -129.4714 | 0.5741 | 5.5514 | 1.928 | -2.7498 | -1.1876 | 4.5706 |  | 3.7573 | 0.534 | 4.009 | 3.3634 | 3.3347 | 1.0839 | 10.7776 | 14.2739 | 14.8409 | 11.102 | 0 | -0.0031 | 0.0009 | 0.0041 | 0.0006 | -0.0002 | 0.0016 | -0.0057 | -0.0051 | -360.165 | 17.3802 | -360.3865 | 17.6594 | -360.7927 | 18.1563 | -360.8235 | 17.5753 | -352.5736 | 18.6799 | -352.589 | 16.7909
12:43 | 4994 | 43.4641 | 202.5188 | 450.0509 | 456.9055 | -16.3544 | -40.2017 | 11.5323 | 8.1184 | 2.4334 | 0.9009 | 3.1755 | -0.9037 | 11.9565 | 4.7237 | 0.6188 | 0.6615 | 0.9603 | 0.7464 | -129.4554 | 0.5324 | 5.6992 | 2.0274 | -2.7268 | -1.1067 | 4.5635 |  | 3.7339 | 0.5638 | 4.0097 | 3.3661 | 3.3391 | 1.0843 | 10.7961 | 14.2753 | 14.8781 | 11.1028 | 0.0001 | -0.0033 | 0.0007 | 0.0034 | 0.0014 | -0.0006 | 0.0113 | -0.0144 | -0.0015 | -360.1404 | 17.409 | -360.4296 | 17.6677 | -360.7804 | 18.144 | -360.7927 | 17.5671 | -352.626 | 18.7107 | -352.6383 | 16.8094
12:43 | 4995 | 43.5011 | 202.573 | 450.1592 | 456.9604 | -16.3729 | -40.0617 | 11.6059 | 8.0411 | 2.4643 | 0.8752 | 3.2241 | -0.9995 | 11.9548 | 4.7761 | 0.6194 | 0.663 | 0.9607 | 0.7455 | -129.431 | 0.6002 | 5.6193 | 1.9567 | -2.8541 | -1.0196 | 4.5855 |  | 3.7435 | 0.6002 | 4.0103 | 3.3674 | 3.3428 | 1.0843 | 10.7603 | 14.2681 | 14.8409 | 11.102 | -0.0001 | -0.0028 | 0.0007 | 0.0036 | 0.0006 | -0.0006 | 0.0063 | -0.0227 | -0.0081 | -360.1311 | 17.3884 | -360.4235 | 17.6677 | -360.7897 | 18.1461 | -360.8235 | 17.5609 | -352.5767 | 18.684 | -352.5952 | 16.8074
12:43 | 4996 | 43.425 | 202.4753 | 450.0897 | 456.9475 | -16.443 | -40.1472 | 11.588 | 8.0948 | 2.4431 | 0.6797 | 3.1684 | -1.0572 | 11.941 | 4.7381 | 0.6197 | 0.6637 | 0.9622 | 0.7474 | -129.3593 | 0.6342 | 5.6198 | 2.0028 | -2.8696 | -1.1701 | 4.5127 |  | 3.7896 | 0.6024 | 4.0091 | 3.3663 | 3.342 | 1.0837 | 10.773 | 14.2462 | 14.8249 | 11.0685 | -0.0002 | -0.0025 | 0.0008 | 0.0036 | 0.0006 | -0.0005 | -0.0069 | -0.0158 | -0.008 | -360.1558 | 17.4048 | -360.4296 | 17.6718 | -360.8081 | 18.1461 | -360.8266 | 17.5773 | -352.5706 | 18.6779 | -352.6444 | 16.8094
12:43 | 4997 | 43.4887 | 202.5412 | 450.0337 | 456.9402 | -16.4258 | -40.1576 | 11.535 | 8.1669 | 2.4753 | 0.788 | 3.2151 | -1.0225 | 11.9048 | 4.6482 | 0.6187 | 0.6598 | 0.9583 | 0.7452 | -129.3795 | 0.603 | 5.7454 | 2.1089 | -2.8543 | -1.1331 | 4.5858 |  | 3.6877 | 0.5278 | 4.0092 | 3.3684 | 3.3401 | 1.0847 | 10.8041 | 14.272 | 14.8761 | 11.1334 | -0.0002 | -0.0031 | 0.0003 | 0.0039 | 0.0006 | -0.0003 | 0.0127 | -0.0125 | -0.0222 | -360.1558 | 17.3966 | -360.4327 | 17.6636 | -360.7927 | 18.1358 | -360.7835 | 17.565 | -352.6167 | 18.6861 | -352.6106 | 16.8012
12:43 | 4998 | 43.5926 | 202.5832 | 450.0413 | 456.9764 | -16.457 | -40.2225 | 11.6801 | 8.1219 | 2.5362 | 0.8598 | 3.1887 | -1.0918 | 11.8794 | 4.605 | 0.6185 | 0.6613 | 0.9569 | 0.7458 | -129.3487 | 0.5954 | 5.6833 | 2.0816 | -2.8367 | -1.1076 | 4.5659 |  | 3.7418 | 0.488 | 4.0098 | 3.3679 | 3.3383 | 1.0838 | 10.7961 | 14.3101 | 14.8444 | 11.0908 | 0.0002 | -0.0031 | 0.0008 | 0.004 | 0.0005 | -0.0007 | 0.0178 | -0.0018 | -0.0029 | -360.1558 | 17.3966 | -360.405 | 17.6553 | -360.765 | 18.1522 | -360.8327 | 17.5691 | -352.5798 | 18.684 | -352.5829 | 16.7909
12:43 | 4999 | 43.6453 | 202.5822 | 449.9983 | 456.9416 | -16.4177 | -40.1763 | 11.5993 | 8.2283 | 2.4344 | 0.7301 | 3.2911 | -0.9333 | 11.9178 | 4.6848 | 0.6204 | 0.6632 | 0.9582 | 0.7465 | -129.3611 | 0.6635 | 5.6058 | 2.0038 | -2.7491 | -1.0742 | 4.5722 |  | 3.7318 | 0.5579 | 4.0105 | 3.365 | 3.3397 | 1.0833 | 10.8307 | 14.3046 | 14.8986 | 11.1363 | -0.0002 | -0.0028 | 0.001 | 0.0042 | 0.0013 | -0.0003 | 0.0127 | -0.0122 | -0.0124 | -360.1496 | 17.3987 | -360.4296 | 17.6615 | -360.7589 | 18.1296 | -360.7897 | 17.5609 | -352.6044 | 18.6963 | -352.6229 | 16.8053
12:43 | 5000 | 43.5937 | 202.5928 | 450.0754 | 456.9583 | -16.4296 | -40.1243 | 11.5234 | 8.1611 | 2.3761 | 0.7657 | 3.2175 | -0.8784 | 11.9993 | 4.8007 | 0.6202 | 0.66 | 0.9611 | 0.7459 | -129.403 | 0.6265 | 5.5863 | 1.9874 | -2.762 | -1.1019 | 4.5271 |  | 3.7555 | 0.5899 | 4.0077 | 3.3645 | 3.3371 | 1.0831 | 10.7869 | 14.2948 | 14.845 | 11.1226 | -0.0005 | -0.0025 | 0.0003 | 0.0033 | 0.0006 | -0.0004 | 0.007 | 0.0042 | -0.0223 | -360.1773 | 17.3884 | -360.4142 | 17.6615 | -360.7866 | 18.1563 | -360.7989 | 17.5671 | -352.5706 | 18.6902 | -352.6321 | 16.793
12:43 | 5001 | 43.5612 | 202.5916 | 449.9904 | 456.9078 | -16.3919 | -40.0838 | 11.477 | 8.1992 | 2.3259 | 0.8484 | 3.2689 | -0.9174 | 11.96 | 4.7254 | 0.6193 | 0.6562 | 0.9587 | 0.7449 | -129.4623 | 0.5109 | 5.5523 | 1.9988 | -2.8317 | -1.0311 | 4.5711 |  | 3.7052 | 0.5658 | 4.0086 | 3.369 | 3.3397 | 1.0839 | 10.8227 | 14.2848 | 14.8601 | 11.1518 | 0 | -0.0031 | 0.001 | 0.0038 | 0.0012 | 0 | 0.0017 | -0.0044 | -0.0016 | -360.1742 | 17.3864 | -360.3773 | 17.6451 | -360.7558 | 18.1522 | -360.8358 | 17.5958 | -352.5829 | 18.6799 | -352.5736 | 16.7827
12:43 | 5002 | 43.5014 | 202.5348 | 450.032 | 456.9691 | -16.3852 | -40.0812 | 11.5189 | 8.1322 | 2.3804 | 0.8475 | 3.3365 | -0.8912 | 11.9498 | 4.7443 | 0.6187 | 0.6627 | 0.968 | 0.7454 | -129.3942 | 0.5032 | 5.5007 | 1.9398 | -2.7921 | -1.111 | 4.442 |  | 3.6606 | 0.5463 | 4.0095 | 3.3646 | 3.3392 | 1.0837 | 10.7879 | 14.2905 | 14.8717 | 11.1114 | 0.0002 | -0.003 | 0.0004 | 0.0035 | 0.0004 | -0.0003 | -0.0039 | -0.0016 | 0.0005 | -360.1742 | 17.4192 | -360.4389 | 17.6553 | -360.7989 | 18.1296 | -360.7835 | 17.5773 | -352.6106 | 18.7066 | -352.6352 | 16.795
12:43 | 5003 | 43.5996 | 202.6235 | 449.9814 | 456.9983 | -16.3301 | -40.1349 | 11.5394 | 8.145 | 2.3582 | 0.8888 | 3.4425 | -0.7994 | 11.9364 | 4.7117 | 0.6196 | 0.6581 | 0.9609 | 0.7457 | -129.3178 | 0.5281 | 5.5487 | 1.9698 | -2.7712 | -1.0893 | 4.5321 |  | 3.7755 | 0.4705 | 4.0093 | 3.3646 | 3.3416 | 1.0844 | 10.7673 | 14.2634 | 14.8759 | 11.0688 | 0.0001 | -0.003 | 0.001 | 0.004 | 0.0008 | -0.0008 | 0.0214 | -0.0073 | -0.0071 | -360.1188 | 17.3843 | -360.4142 | 17.68 | -360.8327 | 18.1707 | -360.8143 | 17.565 | -352.5829 | 18.6717 | -352.6106 | 16.8032
12:43 | 5004 | 43.6203 | 202.6408 | 450.0824 | 457.0169 | -16.3564 | -40.1709 | 11.4903 | 8.1224 | 2.3939 | 0.8242 | 3.497 | -0.869 | 11.9266 | 4.7136 | 0.6197 | 0.6607 | 0.9653 | 0.7454 | -129.3376 | 0.5707 | 5.5564 | 1.8695 | -2.8484 | -1.3703 | 4.5 |  | 3.7341 | 0.4283 | 4.0103 | 3.3639 | 3.3427 | 1.0831 | 10.7695 | 14.2601 | 14.8334 | 11.0822 | -0.0002 | -0.0028 | 0.0012 | 0.0039 | 0.0006 | -0.0003 | 0.0149 | -0.0081 | -0.0081 | -360.2204 | 17.4172 | -360.4235 | 17.6533 | -360.7773 | 18.1502 | -360.8389 | 17.6184 | -352.6475 | 18.6922 | -352.6167 | 16.7807
12:43 | 5005 | 43.6732 | 202.6219 | 449.9752 | 457.052 | -16.3425 | -39.971 | 11.5963 | 8.1515 | 2.3563 | 0.7917 | 3.4799 | -0.9876 | 11.9279 | 4.736 | 0.6194 | 0.6634 | 0.9615 | 0.7466 | -129.4262 | 0.5733 | 5.5024 | 1.8652 | -2.7942 | -1.3457 | 4.4722 |  | 3.741 | 0.4299 | 4.0106 | 3.3625 | 3.3401 | 1.084 | 10.8191 | 14.3337 | 14.8708 | 11.1244 | 0.0001 | -0.0027 | 0.0009 | 0.0039 | 0.0009 | -0.0017 | -0.0043 | -0.0175 | -0.0268 | -360.1373 | 17.4336 | -360.485 | 17.7026 | -360.842 | 18.142 | -360.7743 | 17.5671 | -352.6198 | 18.7087 | -352.6875 | 16.8299
12:43 | 5006 | 43.6107 | 202.6235 | 449.9962 | 457.0468 | -16.3327 | -40.052 | 11.5671 | 8.1589 | 2.4182 | 0.8419 | 3.4274 | -0.932 | 11.916 | 4.7288 | 0.6195 | 0.6628 | 0.9629 | 0.7448 | -129.3439 | 0.516 | 5.6241 | 1.8262 | -2.7398 | -1.1939 | 4.4892 |  | 3.6688 | 0.4689 | 4.0111 | 3.3672 | 3.3413 | 1.0849 | 10.7868 | 14.2718 | 14.8519 | 11.1049 | 0.0003 | -0.003 | 0.0014 | 0.0044 | 0.0006 | -0.0003 | 0.0236 | -0.0198 | -0.0157 | -360.165 | 17.3987 | -360.4204 | 17.6738 | -360.8512 | 18.183 | -360.8943 | 17.6102 | -352.6136 | 18.6717 | -352.6321 | 16.8012
12:43 | 5007 | 43.6308 | 202.5865 | 449.9311 | 457.0014 | -16.2957 | -39.9763 | 11.563 | 8.1365 | 2.3351 | 0.9091 | 3.4811 | -0.9723 | 11.9964 | 4.8064 | 0.6196 | 0.6598 | 0.9645 | 0.7452 | -129.3867 | 0.5825 | 5.6281 | 1.6613 | -2.7621 | -1.279 | 4.4889 |  | 3.6749 | 0.4188 | 4.0102 | 3.3657 | 3.3414 | 1.0845 | 10.7704 | 14.2968 | 14.8865 | 11.1334 | 0.0004 | -0.0026 | 0.001 | 0.0043 | 0.0016 | -0.0003 | 0.011 | -0.006 | -0.003 | -360.2481 | 17.4336 | -360.4512 | 17.6738 | -360.7773 | 18.144 | -360.8574 | 17.6081 | -352.669 | 18.7189 | -352.6475 | 16.7889
12:43 | 5008 | 43.648 | 202.494 | 449.9865 | 456.9429 | -16.2449 | -40.0082 | 11.5752 | 8.1392 | 2.3172 | 0.7696 | 3.5153 | -0.9891 | 11.954 | 4.6736 | 0.6186 | 0.6621 | 0.962 | 0.7455 | -129.3004 | 0.6103 | 5.7022 | 1.711 | -2.7592 | -1.1508 | 4.5251 |  | 3.6662 | 0.4011 | 4.0099 | 3.3675 | 3.3421 | 1.0831 | 10.7695 | 14.2544 | 14.8624 | 11.1111 | -0.0003 | -0.0026 | 0.0006 | 0.0037 | 0.0007 | 0 | 0.0188 | -0.0101 | -0.0094 | -360.1742 | 17.4233 | -360.5189 | 17.7231 | -360.8666 | 18.1666 | -360.8081 | 17.5629 | -352.6167 | 18.7189 | -352.6906 | 16.8423
12:43 | 5009 | 43.6314 | 202.6768 | 450.0797 | 456.9902 | -16.3118 | -40.0652 | 11.5256 | 8.1219 | 2.3173 | 0.774 | 3.496 | -0.848 | 11.8933 | 4.6745 | 0.6204 | 0.662 | 0.9637 | 0.7458 | -129.353 | 0.5892 | 5.7128 | 1.7282 | -2.7785 | -1.0373 | 4.5518 |  | 3.7351 | 0.494 | 4.0101 | 3.3622 | 3.3398 | 1.0845 | 10.7547 | 14.2677 | 14.8088 | 11.0801 | -0.0002 | -0.0032 | 0.0008 | 0.0035 | 0.0006 | -0.0001 | 0.0118 | -0.0103 | -0.0298 | -360.1958 | 17.3987 | -360.3927 | 17.6594 | -360.7958 | 18.1892 | -360.8912 | 17.604 | -352.629 | 18.6799 | -352.589 | 16.793
12:43 | 5010 | 43.5965 | 202.621 | 450.1426 | 456.9467 | -16.2521 | -40.0024 | 11.6255 | 8.0823 | 2.2872 | 0.8442 | 3.4279 | -0.8762 | 11.9381 | 4.7394 | 0.619 | 0.6606 | 0.9612 | 0.744 | -129.4003 | 0.5939 | 5.6447 | 1.8188 | -2.8022 | -1.0184 | 4.5519 |  | 3.7436 | 0.5534 | 4.0092 | 3.3625 | 3.337 | 1.0837 | 10.7775 | 14.257 | 14.8325 | 11.0489 | 0.0006 | -0.0027 | 0.0015 | 0.004 | 0.0006 | -0.0007 | 0.0183 | -0.0031 | -0.0006 | -360.2327 | 17.4397 | -360.5004 | 17.6882 | -360.805 | 18.1358 | -360.8143 | 17.5937 | -352.6167 | 18.7169 | -352.6783 | 16.8012
12:43 | 5011 | 43.6294 | 202.5714 | 450.0094 | 457.0032 | -16.2904 | -40.0921 | 11.5474 | 8.1517 | 2.2004 | 0.7101 | 3.4291 | -0.9446 | 11.9727 | 4.7205 | 0.62 | 0.6637 | 0.9646 | 0.7432 | -129.3321 | 0.6618 | 5.6721 | 1.7296 | -2.8636 | -1.2275 | 4.4543 |  | 3.7405 | 0.4263 | 4.0097 | 3.3629 | 3.3358 | 1.0832 | 10.757 | 14.2293 | 14.792 | 11.0541 | -0.0002 | -0.0032 | 0.0007 | 0.0036 | 0.0008 | -0.0004 | 0.0074 | -0.0104 | -0.0207 | -360.0973 | 17.3905 | -360.445 | 17.6944 | -360.842 | 18.1666 | -360.8235 | 17.5547 | -352.5921 | 18.682 | -352.6321 | 16.8197
12:43 | 5012 | 43.5627 | 202.6147 | 450.0458 | 456.9986 | -16.2774 | -40.2035 | 11.4599 | 8.2063 | 2.2739 | 0.737 | 3.3908 | -0.9955 | 11.9321 | 4.8155 | 0.6204 | 0.6617 | 0.9611 | 0.7453 | -129.4153 | 0.5051 | 5.6782 | 1.7297 | -2.8038 | -1.2096 | 4.4483 |  | 3.7812 | 0.5754 | 4.01 | 3.3646 | 3.3392 | 1.0834 | 10.7499 | 14.2462 | 14.8539 | 11.0858 | 0.0001 | -0.0021 | 0.0013 | 0.0043 | 0.001 | -0.0004 | 0.0276 | -0.003 | -0.0009 | -360.2265 | 17.3905 | -360.4019 | 17.6471 | -360.765 | 18.1604 | -360.8789 | 17.6081 | -352.626 | 18.6758 | -352.6013 | 16.7807
12:43 | 5013 | 43.6099 | 202.571 | 450.0831 | 456.9813 | -16.5083 | -40.2997 | 11.287 | 8.208 | 2.3125 | 0.8123 | 3.5304 | -0.9096 | 12.0587 | 4.821 | 0.6201 | 0.6635 | 0.9613 | 0.7449 | -129.3368 | 0.6072 | 5.6937 | 1.9686 | -2.801 | -1.1992 | 4.5465 |  | 3.7596 | 0.4082 | 4.0109 | 3.3603 | 3.3352 | 1.084 | 10.803 | 14.265 | 14.8458 | 11.1092 | -0.0001 | -0.0026 | 0.0006 | 0.0038 | 0.0001 | -0.0006 | 0.0105 | -0.0136 | -0.0085 | -360.1804 | 17.411 | -360.4727 | 17.6882 | -360.7866 | 18.1194 | -360.7589 | 17.5671 | -352.6013 | 18.7128 | -352.629 | 16.8135
12:43 | 5014 | 43.6083 | 202.6102 | 450.1015 | 457.0628 | -16.4055 | -40.2585 | 11.4653 | 8.1903 | 2.3182 | 0.8008 | 3.4607 | -0.8873 | 11.9981 | 4.7991 | 0.6203 | 0.6628 | 0.9626 | 0.7452 | -129.2804 | 0.6509 | 5.7529 | 1.9874 | -2.8575 | -1.1474 | 4.5821 |  | 3.7401 | 0.4005 | 4.0092 | 3.365 | 3.3403 | 1.0833 | 10.8215 | 14.3123 | 14.8808 | 11.1165 | 0.0001 | -0.0029 | 0.0005 | 0.0039 | 0.0008 | -0.0006 | 0.0124 | -0.0072 | -0.0204 | -360.1127 | 17.3823 | -360.4173 | 17.6759 | -360.8174 | 18.1707 | -360.842 | 17.5671 | -352.6106 | 18.6737 | -352.5983 | 16.8032
12:43 | 5015 | 43.4819 | 202.4599 | 449.9921 | 457.0322 | -16.3701 | -40.1736 | 11.4786 | 8.1572 | 2.2925 | 0.9321 | 3.4304 | -0.8746 | 11.9581 | 4.7433 | 0.6189 | 0.6627 | 0.9609 | 0.7456 | -129.3188 | 0.6119 | 5.6569 | 1.8598 | -2.8496 | -1.082 | 4.521 |  | 3.7644 | 0.5678 | 4.0091 | 3.3638 | 3.3384 | 1.0842 | 10.8017 | 14.3106 | 14.9055 | 11.1359 | 0.0004 | -0.003 | 0.0007 | 0.0038 | 0.0007 | -0.0001 | 0.0043 | -0.0083 | 0.0032 | -360.205 | 17.3966 | -360.4173 | 17.6533 | -360.7589 | 18.1358 | -360.842 | 17.5937 | -352.586 | 18.6984 | -352.6044 | 16.7868
12:43 | 5016 | 43.5896 | 202.6043 | 450.0635 | 457.0806 | -16.3453 | -40.2671 | 11.4287 | 8.1101 | 2.3139 | 0.7953 | 3.4256 | -0.9352 | 11.9322 | 4.8021 | 0.6189 | 0.6632 | 0.9657 | 0.7453 | -129.3323 | 0.6815 | 5.6079 | 1.9361 | -2.8849 | -1.1638 | 4.5309 |  | 3.7637 | 0.4498 | 4.0093 | 3.3654 | 3.3389 | 1.0839 | 10.8134 | 14.339 | 14.9312 | 11.1428 | -0.0007 | -0.003 | 0.0006 | 0.0034 | 0.0008 | -0.0008 | 0.0064 | -0.0061 | 0.0028 | -360.1311 | 17.4028 | -360.4696 | 17.68 | -360.8297 | 18.144 | -360.7743 | 17.5773 | -352.5583 | 18.6922 | -352.6475 | 16.8135
12:43 | 5017 | 43.5788 | 202.625 | 450.064 | 456.9467 | -16.3453 | -40.1969 | 11.4276 | 8.1313 | 2.3572 | 0.8548 | 3.424 | -0.9008 | 11.9704 | 4.828 | 0.621 | 0.6643 | 0.9623 | 0.7458 | -129.3266 | 0.6643 | 5.6271 | 1.9925 | -2.8986 | -1.2284 | 4.4878 |  | 3.767 | 0.5296 | 4.0097 | 3.366 | 3.3369 | 1.0828 | 10.7742 | 14.2763 | 14.8494 | 11.1042 | -0.0001 | -0.0026 | 0.0006 | 0.0036 | 0.0003 | -0.0005 | 0.0131 | -0.0059 | -0.0201 | -360.1588 | 17.3905 | -360.4019 | 17.6574 | -360.7743 | 18.1687 | -360.8081 | 17.5732 | -352.5798 | 18.684 | -352.626 | 16.8032
12:43 | 5018 | 43.6515 | 202.5648 | 450.0399 | 457.0276 | -16.3865 | -40.1651 | 11.4927 | 8.1484 | 2.3968 | 0.7479 | 3.4704 | -0.8539 | 11.9452 | 4.8022 | 0.6191 | 0.6621 | 0.9607 | 0.747 | -129.276 | 0.7098 | 5.629 | 1.9891 | -2.8527 | -1.1449 | 4.5855 |  | 3.7022 | 0.4471 | 4.0095 | 3.3641 | 3.3381 | 1.0825 | 10.7673 | 14.2634 | 14.8354 | 11.0862 | 0.0002 | -0.0033 | 0.0011 | 0.0041 | 0.0008 | -0.0009 | 0.0078 | -0.0178 | 0.0097 | -360.1496 | 17.4048 | -360.4266 | 17.6636 | -360.7558 | 18.1461 | -360.8081 | 17.5712 | -352.5829 | 18.6963 | -352.6044 | 16.7991
12:43 | 5019 | 43.6114 | 202.6186 | 450.0529 | 456.9589 | -16.3956 | -40.2366 | 11.3286 | 8.0906 | 2.3692 | 0.8463 | 3.4776 | -0.8565 | 11.9972 | 4.8142 | 0.6215 | 0.6662 | 0.9613 | 0.7468 | -129.3035 | 0.7361 | 5.714 | 2.0071 | -2.8122 | -1.0883 | 4.6149 |  | 3.7385 | 0.4344 | 4.0107 | 3.3645 | 3.3385 | 1.084 | 10.7616 | 14.2747 | 14.8333 | 11.1042 | -0.0003 | -0.0033 | 0.0004 | 0.0036 | 0.0001 | -0.0007 | 0.012 | -0.0215 | -0.0097 | -360.125 | 17.3946 | -360.4081 | 17.6656 | -360.7743 | 18.1461 | -360.8235 | 17.5794 | -352.5736 | 18.6902 | -352.5921 | 16.7991
12:43 | 5020 | 43.6567 | 202.5423 | 450.1309 | 456.9336 | -16.4518 | -40.2792 | 11.4086 | 8.087 | 2.3763 | 0.8555 | 3.4129 | -0.9996 | 11.9482 | 4.7564 | 0.6204 | 0.6607 | 0.9627 | 0.7477 | -129.3946 | 0.6962 | 5.711 | 1.9511 | -2.7884 | -1.1444 | 4.5678 |  | 3.6561 | 0.5014 | 4.0101 | 3.3648 | 3.3412 | 1.0848 | 10.7683 | 14.2707 | 14.8447 | 11.0807 | -0.0005 | -0.0027 | 0.0013 | 0.0047 | 0.0014 | -0.0004 | 0.0097 | 0.0009 | -0.0025 | -360.1404 | 17.3966 | -360.4173 | 17.6533 | -360.7681 | 18.1399 | -360.8204 | 17.5835 | -352.5829 | 18.6943 | -352.589 | 16.7868
12:43 | 5021 | 43.6524 | 202.6236 | 450.0182 | 456.999 | -16.4354 | -40.1807 | 11.35 | 8.192 | 2.3724 | 0.8512 | 3.4349 | -1.0267 | 11.9592 | 4.8252 | 0.6209 | 0.6612 | 0.9609 | 0.7465 | -129.3535 | 0.6711 | 5.7309 | 1.9352 | -2.7487 | -0.9882 | 4.6825 |  | 3.6861 | 0.4336 | 4.0088 | 3.3637 | 3.3394 | 1.0831 | 10.7579 | 14.2601 | 14.8219 | 11.0591 | -0.0004 | -0.0028 | 0.0005 | 0.0039 | 0.0006 | -0.0004 | 0.0111 | -0.0136 | 0.0012 | -360.1219 | 17.4007 | -360.4512 | 17.6718 | -360.7558 | 18.1276 | -360.7835 | 17.5773 | -352.586 | 18.6963 | -352.6629 | 16.8156
12:43 | 5022 | 43.661 | 202.5609 | 449.958 | 457.0217 | -16.496 | -40.2679 | 11.3986 | 8.1428 | 2.4801 | 0.9155 | 3.4769 | -1.0152 | 11.9409 | 4.8039 | 0.6219 | 0.6637 | 0.9638 | 0.746 | -129.2906 | 0.7781 | 5.802 | 1.9042 | -2.7758 | -1.073 | 4.6488 |  | 3.6607 | 0.3961 | 4.0107 | 3.3622 | 3.3411 | 1.0837 | 10.8122 | 14.2745 | 14.8625 | 11.1063 | 0.0004 | -0.0026 | 0.0006 | 0.004 | 0.0012 | -0.0003 | 0.0156 | -0.0099 | 0.0034 | -360.1404 | 17.3782 | -360.4142 | 17.6656 | -360.7927 | 18.1461 | -360.8297 | 17.5753 | -352.6229 | 18.6861 | -352.6352 | 16.7971
12:43 | 5023 | 43.6463 | 202.5439 | 449.9427 | 456.9668 | -16.4381 | -40.2016 | 11.3631 | 8.182 | 2.4705 | 0.905 | 3.5123 | -0.9805 | 12.0179 | 4.8335 | 0.6206 | 0.661 | 0.9629 | 0.7455 | -129.2841 | 0.6547 | 5.7969 | 1.9355 | -2.7733 | -1.1628 | 4.619 |  | 3.7282 | 0.3668 | 4.0089 | 3.368 | 3.3428 | 1.0839 | 10.8065 | 14.3031 | 14.8662 | 11.1244 | -0.0001 | -0.003 | 0.0009 | 0.0039 | 0.0011 | -0.0004 | 0.0093 | -0.0022 | -0.0211 | -360.1342 | 17.3966 | -360.4019 | 17.6594 | -360.7497 | 18.1563 | -360.8389 | 17.6061 | -352.6167 | 18.6902 | -352.6044 | 16.7909
12:43 | 5024 | 43.625 | 202.5861 | 449.9148 | 456.9319 | -16.4225 | -40.2127 | 11.4294 | 8.1743 | 2.4086 | 0.8322 | 3.479 | -0.9313 | 11.9401 | 4.841 | 0.6178 | 0.6629 | 0.9598 | 0.7465 | -129.2776 | 0.6767 | 5.7325 | 1.9175 | -2.7539 | -1.0893 | 4.6117 |  | 3.6373 | 0.3805 | 4.0103 | 3.3654 | 3.3392 | 1.0826 | 10.7984 | 14.2951 | 14.8935 | 11.1045 | -0.0002 | -0.0026 | 0.0007 | 0.0036 | 0.0009 | -0.0001 | 0.0168 | 0.0096 | -0.01 | -360.1865 | 17.4254 | -360.4512 | 17.68 | -360.8112 | 18.1481 | -360.765 | 17.5835 | -352.6444 | 18.723 | -352.669 | 16.8135
12:43 | 5025 | 43.7026 | 202.5835 | 450.0153 | 457.0084 | -16.4484 | -40.2103 | 11.4252 | 8.0656 | 2.4421 | 0.7603 | 3.3951 | -1.0474 | 11.91 | 4.7606 | 0.6204 | 0.6628 | 0.9645 | 0.7471 | -129.3039 | 0.63 | 5.6814 | 1.9232 | -2.832 | -1.181 | 4.614 |  | 3.5808 | 0.2834 | 4.0092 | 3.366 | 3.3341 | 1.0833 | 10.7949 | 14.2569 | 14.8604 | 11.1013 | -0.0004 | -0.0029 | 0.0009 | 0.0038 | 0.0009 | -0.0004 | 0.0013 | -0.0143 | -0.0148 | -360.1342 | 17.3966 | -360.4635 | 17.7046 | -360.8543 | 18.1769 | -360.8574 | 17.5753 | -352.6198 | 18.6943 | -352.6721 | 16.834
12:43 | 5026 | 43.6898 | 202.6473 | 450.0536 | 457.0453 | -16.4315 | -40.1939 | 11.4627 | 8.0594 | 2.3829 | 0.7498 | 3.4574 | -0.9333 | 11.9799 | 4.8319 | 0.619 | 0.6591 | 0.9602 | 0.7463 | -129.2716 | 0.5877 | 5.7841 | 1.9452 | -2.8339 | -1.1094 | 4.6804 |  | 3.628 | 0.3841 | 4.0106 | 3.3683 | 3.34 | 1.0834 | 10.7787 | 14.287 | 14.8328 | 11.1024 | 0.0001 | -0.0028 | 0.0012 | 0.0039 | 0.0005 | -0.0003 | 0.0046 | -0.0041 | -0.0035 | -360.2388 | 17.4213 | -360.4419 | 17.6574 | -360.7712 | 18.1604 | -360.8604 | 17.6307 | -352.6844 | 18.723 | -352.6475 | 16.795
12:43 | 5027 | 43.6366 | 202.6151 | 450.0324 | 456.9982 | -16.4019 | -40.1704 | 11.5048 | 8.1737 | 2.4141 | 0.8707 | 3.4621 | -0.9182 | 11.9791 | 4.8748 | 0.6208 | 0.6613 | 0.9615 | 0.745 | -129.3459 | 0.5923 | 5.7158 | 1.9773 | -2.812 | -1.1497 | 4.6604 |  | 3.7327 | 0.3519 | 4.0108 | 3.3633 | 3.3398 | 1.0834 | 10.7637 | 14.2718 | 14.8461 | 11.0934 | 0.0005 | -0.003 | 0.0009 | 0.0041 | 0.0013 | -0.0005 | 0.0101 | 0.0001 | -0.0092 | -360.1988 | 17.4192 | -360.4942 | 17.7026 | -360.8543 | 18.1522 | -360.7958 | 17.5753 | -352.6321 | 18.7271 | -352.706 | 16.8381
12:44 | 5028 | 43.7064 | 202.5936 | 449.9465 | 457.0658 | -16.4363 | -40.1638 | 11.4956 | 8.0777 | 2.3066 | 0.6891 | 3.439 | -1.0681 | 12.0236 | 4.836 | 0.6213 | 0.6633 | 0.9628 | 0.7488 | -129.3347 | 0.5919 | 5.6808 | 2.0316 | -2.7658 | -1.0873 | 4.6409 |  | 3.6799 | 0.3781 | 4.0095 | 3.364 | 3.3387 | 1.0824 | 10.7463 | 14.2603 | 14.8519 | 11.1049 | 0.0001 | -0.0027 | 0.0015 | 0.0049 | 0.001 | -0.0002 | 0.0151 | -0.0094 | -0.0042 | -360.1835 | 17.3905 | -360.445 | 17.6902 | -360.8635 | 18.2056 | -360.882 | 17.5999 | -352.6413 | 18.6861 | -352.6506 | 16.8258
12:44 | 5029 | 43.6854 | 202.6442 | 449.893 | 456.9852 | -16.4746 | -40.278 | 11.4838 | 8.1808 | 2.352 | 0.8451 | 3.4837 | -1.0551 | 12.0247 | 4.847 | 0.62 | 0.6618 | 0.9631 | 0.7464 | -129.3555 | 0.5391 | 5.6187 | 2.0175 | -2.7962 | -1.0159 | 4.6529 |  | 3.6871 | 0.4056 | 4.0085 | 3.3629 | 3.3379 | 1.0851 | 10.7902 | 14.2988 | 14.8465 | 11.1016 | 0 | -0.0023 | 0.001 | 0.0042 | 0.0009 | -0.0008 | -0.0053 | 0.004 | 0.0106 | -360.245 | 17.4418 | -360.4758 | 17.643 | -360.7897 | 18.1584 | -360.8574 | 17.6163 | -352.7029 | 18.7312 | -352.6752 | 16.8094
12:44 | 5030 | 43.6395 | 202.6272 | 450.0079 | 456.9945 | -16.4989 | -40.1942 | 11.4356 | 8.0652 | 2.3583 | 0.7858 | 3.3645 | -0.9864 | 12.0198 | 4.874 | 0.6204 | 0.6621 | 0.9578 | 0.7459 | -129.4166 | 0.5854 | 5.5399 | 1.9749 | -2.8142 | -1.1393 | 4.5542 |  | 3.6329 | 0.4492 | 4.0094 | 3.3636 | 3.3401 | 1.0835 | 10.8007 | 14.2741 | 14.8651 | 11.1132 | 0.0002 | -0.0027 | 0.0004 | 0.0038 | 0.0003 | -0.0006 | 0.0095 | -0.0054 | -0.0208 | -360.1835 | 17.4315 | -360.5158 | 17.7026 | -360.8881 | 18.1707 | -360.8235 | 17.5835 | -352.629 | 18.7251 | -352.7244 | 16.8464
12:44 | 5031 | 43.667 | 202.5646 | 449.9351 | 456.9981 | -16.5392 | -40.2893 | 11.4787 | 8.1271 | 2.4153 | 0.7791 | 3.4651 | -1.0382 | 11.9224 | 4.7825 | 0.619 | 0.6672 | 0.9597 | 0.7461 | -129.4421 | 0.5666 | 5.611 | 1.8636 | -2.8525 | -1.1477 | 4.6266 |  | 3.6969 | 0.4037 | 4.0091 | 3.3638 | 3.3406 | 1.0834 | 10.7822 | 14.2787 | 14.8522 | 11.089 | 0.0004 | -0.0027 | 0.0012 | 0.0042 | 0.0008 | -0.0008 | 0.0309 | -0.0021 | 0.0036 | -360.2019 | 17.3987 | -360.4142 | 17.6677 | -360.8574 | 18.1994 | -360.9097 | 17.6081 | -352.6721 | 18.6943 | -352.6136 | 16.8135
12:44 | 5032 | 43.6787 | 202.5216 | 450.0547 | 456.9871 | -16.4891 | -40.1695 | 11.6203 | 8.0515 | 2.4178 | 0.8359 | 3.4814 | -0.9997 | 11.9895 | 4.8104 | 0.62 | 0.6621 | 0.9608 | 0.7468 | -129.3415 | 0.616 | 5.7698 | 1.9486 | -2.9032 | -1.2366 | 4.5252 |  | 3.6511 | 0.3914 | 4.008 | 3.3636 | 3.3408 | 1.0847 | 10.7856 | 14.2766 | 14.8747 | 11.0861 | 0.0001 | -0.003 | 0.0009 | 0.0036 | 0.0009 | -0.0001 | 0.0079 | -0.0119 | -0.0013 | -360.2296 | 17.4439 | -360.4789 | 17.6718 | -360.7804 | 18.1399 | -360.8481 | 17.6143 | -352.6537 | 18.7415 | -352.6721 | 16.8032
12:44 | 5033 | 43.6408 | 202.5678 | 450.1126 | 456.955 | -16.3881 | -40.1602 | 11.5838 | 8.1028 | 2.41 | 0.8388 | 3.4424 | -0.946 | 11.9696 | 4.8074 | 0.6198 | 0.6647 | 0.9597 | 0.7464 | -129.441 | 0.5007 | 5.6338 | 1.9979 | -2.7989 | -1.1366 | 4.5831 |  | 3.7238 | 0.4214 | 4.0096 | 3.3693 | 3.3427 | 1.0847 | 10.7812 | 14.2772 | 14.8545 | 11.0887 | -0.0003 | -0.0025 | 0.0009 | 0.0036 | 0.0007 | -0.0005 | 0.0029 | -0.0048 | -0.0146 | -360.1558 | 17.4213 | -360.525 | 17.7149 | -360.8758 | 18.1625 | -360.8266 | 17.5794 | -352.6136 | 18.723 | -352.7029 | 16.8464
12:44 | 5034 | 43.7187 | 202.5856 | 450.131 | 457.0862 | -16.475 | -40.1264 | 11.5504 | 8.0955 | 2.5087 | 0.9213 | 3.4132 | -1.0035 | 11.8877 | 4.7858 | 0.6197 | 0.6612 | 0.9577 | 0.7463 | -129.4119 | 0.6055 | 5.6756 | 2.007 | -2.7686 | -1.2346 | 4.5394 |  | 3.621 | 0.3773 | 4.0097 | 3.3656 | 3.339 | 1.0831 | 10.7822 | 14.273 | 14.8475 | 11.106 | -0.0003 | -0.0031 | 0.0012 | 0.0041 | 0.0012 | 0 | 0.0049 | -0.0143 | -0.0013 | -360.2142 | 17.3966 | -360.405 | 17.6533 | -360.7958 | 18.183 | -360.8974 | 17.6245 | -352.6506 | 18.6963 | -352.6044 | 16.8074
12:44 | 5035 | 43.7489 | 202.5942 | 450.1091 | 457.0897 | -16.4215 | -40.1401 | 11.5242 | 8.0373 | 2.4784 | 0.8435 | 3.4194 | -0.9495 | 11.9371 | 4.8222 | 0.6193 | 0.6649 | 0.9622 | 0.7449 | -129.3344 | 0.6542 | 5.6629 | 1.9918 | -2.8263 | -1.2023 | 4.5806 |  | 3.7096 | 0.4676 | 4.0089 | 3.3649 | 3.3418 | 1.0831 | 10.7626 | 14.2705 | 14.8379 | 11.0753 | 0.0002 | -0.0031 | 0.001 | 0.004 | 0.0004 | -0.0007 | -0.0056 | -0.0018 | -0.0058 | -360.2111 | 17.4521 | -360.5066 | 17.6738 | -360.8174 | 18.1337 | -360.8327 | 17.6102 | -352.6875 | 18.7477 | -352.706 | 16.8156
12:44 | 5036 | 43.7053 | 202.5992 | 450.0686 | 457.049 | -16.4875 | -40.2298 | 11.4355 | 8.0334 | 2.4862 | 0.7642 | 3.3286 | -0.921 | 11.94 | 4.8119 | 0.6189 | 0.6638 | 0.9582 | 0.7459 | -129.4528 | 0.6444 | 5.6535 | 2.0708 | -2.7367 | -1.1395 | 4.6126 |  | 3.7242 | 0.4061 | 4.01 | 3.3607 | 3.3369 | 1.0825 | 10.8054 | 14.2901 | 14.8511 | 11.0952 | -0.0001 | -0.0029 | 0.0006 | 0.0039 | 0.0007 | -0.001 | 0.0135 | -0.0026 | -0.0175 | -360.1373 | 17.409 | -360.4758 | 17.7026 | -360.8727 | 18.1707 | -360.8204 | 17.5855 | -352.5921 | 18.6984 | -352.6906 | 16.8464
12:44 | 5037 | 43.7388 | 202.5792 | 450.0989 | 457.0594 | -16.4524 | -40.267 | 11.4625 | 7.9505 | 2.4172 | 0.6423 | 3.2597 | -0.8708 | 11.9307 | 4.7333 | 0.6195 | 0.6645 | 0.9604 | 0.7467 | -129.3287 | 0.7011 | 5.7577 | 2.0986 | -2.692 | -1.0891 | 4.6088 |  | 3.7238 | 0.3127 | 4.0088 | 3.364 | 3.3387 | 1.0827 | 10.781 | 14.2834 | 14.8634 | 11.0934 | -0.0003 | -0.0026 | 0.0009 | 0.004 | 0.0005 | -0.0003 | 0.0218 | -0.0151 | -0.0218 | -360.2388 | 17.4048 | -360.4358 | 17.6533 | -360.802 | 18.1728 | -360.9035 | 17.643 | -352.6752 | 18.7045 | -352.6136 | 16.795
12:44 | 5038 | 43.682 | 202.6077 | 450.1057 | 457.0269 | -16.4816 | -40.2426 | 11.4128 | 8.0049 | 2.4937 | 0.7442 | 3.3008 | -0.8611 | 11.9817 | 4.7687 | 0.6204 | 0.6641 | 0.9603 | 0.7466 | -129.3804 | 0.6985 | 5.8339 | 2.0724 | -2.775 | -1.1031 | 4.6103 |  | 3.7297 | 0.3679 | 4.0089 | 3.365 | 3.3392 | 1.0849 | 10.8122 | 14.3322 | 14.8846 | 11.1125 | -0.0002 | -0.0027 | 0.0005 | 0.0035 | 0.0008 | -0.0007 | 0.012 | -0.0106 | -0.0163 | -360.2081 | 17.4582 | -360.4912 | 17.6861 | -360.8389 | 18.1379 | -360.802 | 17.6143 | -352.6783 | 18.7477 | -352.6998 | 16.8197
12:44 | 5039 | 43.7102 | 202.6135 | 450.0764 | 457.0242 | -16.606 | -40.238 | 11.3946 | 8.0407 | 2.4258 | 0.7624 | 3.3458 | -0.8791 | 12.0062 | 4.8094 | 0.6203 | 0.6637 | 0.9609 | 0.7453 | -129.3452 | 0.7429 | 5.718 | 2.1761 | -2.722 | -1.043 | 4.6761 |  | 3.6721 | 0.4102 | 4.0091 | 3.3652 | 3.3377 | 1.0843 | 10.7973 | 14.288 | 14.8563 | 11.1038 | 0 | -0.0031 | 0.0007 | 0.0039 | 0.0008 | -0.0001 | 0.0031 | -0.0052 | -0.0245 | -360.0973 | 17.4048 | -360.4696 | 17.7005 | -360.882 | 18.1789 | -360.8512 | 17.5855 | -352.586 | 18.7025 | -352.6752 | 16.834
12:44 | 5040 | 43.6408 | 202.5651 | 449.9744 | 456.9479 | -16.5174 | -40.2154 | 11.3675 | 8.0431 | 2.4421 | 0.8987 | 3.4018 | -0.8009 | 11.9751 | 4.8911 | 0.6203 | 0.6643 | 0.9608 | 0.7471 | -129.2958 | 0.7098 | 5.6342 | 2.0901 | -2.6729 | -1.0526 | 4.6107 |  | 3.7128 | 0.4207 | 4.0076 | 3.3634 | 3.3399 | 1.084 | 10.8273 | 14.3067 | 14.8935 | 11.1277 | -0.0001 | -0.003 | 0.001 | 0.0039 | 0.0009 | -0.0007 | 0.0141 | -0.0108 | -0.0082 | -360.2173 | 17.4213 | -360.4389 | 17.6636 | -360.8112 | 18.1666 | -360.922 | 17.6348 | -352.6906 | 18.7107 | -352.6198 | 16.7971
12:44 | 5041 | 43.6449 | 202.5452 | 450.0643 | 457.0022 | -16.4955 | -40.2369 | 11.3819 | 8.0386 | 2.4216 | 0.7716 | 3.3573 | -0.8228 | 12.0498 | 4.8857 | 0.62 | 0.6653 | 0.9604 | 0.7479 | -129.2578 | 0.7276 | 5.7054 | 2.0879 | -2.6818 | -1.1008 | 4.6638 |  | 3.7117 | 0.3881 | 4.0088 | 3.3665 | 3.3408 | 1.0839 | 10.8007 | 14.3145 | 14.8651 | 11.1017 | -0.0004 | -0.0026 | 0.0007 | 0.0038 | 0 | -0.0006 | -0.0095 | -0.0125 | 0.0046 | -360.205 | 17.4418 | -360.4912 | 17.6738 | -360.8204 | 18.1379 | -360.7989 | 17.6081 | -352.6537 | 18.7374 | -352.6875 | 16.8156
12:44 | 5042 | 43.7376 | 202.581 | 450.025 | 457.0575 | -16.5986 | -40.2838 | 11.2705 | 8.1402 | 2.452 | 0.7356 | 3.4087 | -0.8614 | 11.9805 | 4.8341 | 0.6194 | 0.6654 | 0.9605 | 0.7476 | -129.3029 | 0.7394 | 5.6583 | 2.0932 | -2.666 | -1.1654 | 4.6271 |  | 3.5787 | 0.3564 | 4.0098 | 3.3611 | 3.3362 | 1.0833 | 10.8099 | 14.2778 | 14.8587 | 11.0988 | -0.0003 | -0.0029 | 0.0014 | 0.0041 | 0.0011 | -0.0003 | 0.0105 | -0.0083 | -0.0171 | -360.1373 | 17.411 | -360.4696 | 17.6985 | -360.8727 | 18.1687 | -360.8389 | 17.604 | -352.6167 | 18.7045 | -352.6783 | 16.8238
12:44 | 5043 | 43.6992 | 202.6276 | 450.0692 | 456.9746 | -16.517 | -40.2433 | 11.3584 | 8.0954 | 2.4347 | 0.7381 | 3.4143 | -0.9001 | 12.0043 | 4.8523 | 0.6195 | 0.6616 | 0.9597 | 0.7451 | -129.302 | 0.7646 | 5.7768 | 1.9757 | -2.6386 | -1.1152 | 4.619 |  | 3.6585 | 0.4768 | 4.0095 | 3.3664 | 3.3388 | 1.084 | 10.7707 | 14.2729 | 14.8638 | 11.1006 | 0.0001 | -0.0031 | 0.0003 | 0.0035 | 0.0007 | -0.0004 | 0.0099 | -0.0101 | -0.0131 | -360.2142 | 17.4192 | -360.4573 | 17.6718 | -360.7866 | 18.144 | -360.8789 | 17.641 | -352.6783 | 18.7128 | -352.6383 | 16.7909
12:44 | 5044 | 43.6588 | 202.5735 | 450.12 | 457.0134 | -16.526 | -40.216 | 11.3836 | 8.0367 | 2.3755 | 0.7243 | 3.3563 | -0.834 | 11.9816 | 4.8143 | 0.6205 | 0.6623 | 0.9646 | 0.7478 | -129.2717 | 0.7423 | 5.8418 | 2.0354 | -2.6353 | -1.1632 | 4.6756 |  | 3.5687 | 0.3686 | 4.0096 | 3.3669 | 3.3351 | 1.0833 | 10.7753 | 14.2718 | 14.8634 | 11.1049 | 0 | -0.0034 | 0.0008 | 0.0039 | 0.0011 | -0.0006 | 0.0234 | -0.0045 | -0.0078 | -360.2235 | 17.4295 | -360.4727 | 17.6861 | -360.8266 | 18.1296 | -360.7835 | 17.6061 | -352.6106 | 18.7189 | -352.6752 | 16.8115
12:44 | 5045 | 43.7346 | 202.5914 | 449.9678 | 457.0068 | -16.4213 | -40.1554 | 11.3076 | 8.1304 | 2.4466 | 0.9709 | 3.4173 | -0.9567 | 11.9389 | 4.7513 | 0.6195 | 0.6601 | 0.9616 | 0.7468 | -129.2241 | 0.865 | 5.8122 | 2.0161 | -2.6179 | -0.9944 | 4.6616 |  | 3.5193 | 0.3961 | 4.0085 | 3.3653 | 3.3394 | 1.0849 | 10.7579 | 14.2833 | 14.8277 | 11.088 | -0.0003 | -0.0026 | 0.0007 | 0.0041 | 0.0009 | -0.0006 | 0.0087 | -0.0124 | -0.0154 | -360.1404 | 17.3946 | -360.4419 | 17.6841 | -360.8389 | 18.1625 | -360.8512 | 17.5937 | -352.589 | 18.6963 | -352.669 | 16.8074
12:44 | 5046 | 43.7451 | 202.5721 | 449.9888 | 457.0875 | -16.442 | -40.1787 | 11.4334 | 8.1165 | 2.52 | 0.8734 | 3.4151 | -0.9307 | 12.0582 | 4.8332 | 0.6219 | 0.6627 | 0.9602 | 0.7475 | -129.2449 | 0.7968 | 5.7813 | 2.0352 | -2.6012 | -0.9755 | 4.6593 |  | 3.6186 | 0.4311 | 4.0093 | 3.3687 | 3.3382 | 1.084 | 10.7649 | 14.2843 | 14.828 | 11.1067 | -0.0002 | -0.0028 | 0.0001 | 0.0032 | 0.0006 | -0.0008 | 0.0068 | -0.0125 | -0.0293 | -360.2142 | 17.4131 | -360.4573 | 17.641 | -360.7835 | 18.1399 | -360.8327 | 17.6184 | -352.6567 | 18.7004 | -352.6167 | 16.7909
12:44 | 5047 | 43.6883 | 202.5613 | 449.9943 | 456.9697 | -16.5235 | -40.269 | 11.4077 | 8.151 | 2.4232 | 0.7799 | 3.401 | -0.8829 | 11.9861 | 4.8627 | 0.6203 | 0.6629 | 0.9624 | 0.7461 | -129.2783 | 0.787 | 5.8272 | 2.0347 | -2.6172 | -1.0272 | 4.6811 |  | 3.761 | 0.5036 | 4.0089 | 3.369 | 3.3442 | 1.084 | 10.7915 | 14.2822 | 14.8505 | 11.0865 | 0 | -0.003 | 0.0009 | 0.004 | 0.0012 | -0.0003 | -0.0006 | 0.0004 | -0.0268 | -360.1896 | 17.4295 | -360.4819 | 17.6718 | -360.8235 | 18.142 | -360.805 | 17.5999 | -352.5952 | 18.7004 | -352.6506 | 16.8156
12:44 | 5048 | 43.7065 | 202.6218 | 449.9069 | 456.957 | -16.4587 | -40.215 | 11.4157 | 8.0266 | 2.3484 | 0.8113 | 3.3551 | -0.999 | 11.9648 | 4.7564 | 0.6187 | 0.6655 | 0.9622 | 0.7482 | -129.2746 | 0.835 | 5.882 | 1.981 | -2.7608 | -1.0937 | 4.6105 |  | 3.6566 | 0.4531 | 4.0083 | 3.3657 | 3.339 | 1.0853 | 10.7878 | 14.3141 | 14.8633 | 11.0929 | 0.0004 | -0.0028 | 0.0011 | 0.0038 | 0.0011 | 0 | -0.0035 | -0.0142 | -0.022 | -360.1681 | 17.4069 | -360.4604 | 17.6636 | -360.8297 | 18.1604 | -360.8543 | 17.6122 | -352.6106 | 18.6881 | -352.6383 | 16.8074
12:44 | 5049 | 43.6624 | 202.5835 | 450.0364 | 456.9911 | -16.5476 | -40.2024 | 11.4453 | 8.081 | 2.5354 | 0.9215 | 3.4635 | -1.0309 | 11.891 | 4.7288 | 0.6193 | 0.6629 | 0.9617 | 0.7461 | -129.3319 | 0.807 | 5.8357 | 2.0199 | -2.6069 | -1.0972 | 4.6535 |  | 3.6452 | 0.4493 | 4.0103 | 3.3699 | 3.3406 | 1.0851 | 10.7985 | 14.2715 | 14.8671 | 11.0883 | -0.0003 | -0.0026 | 0.0008 | 0.0036 | 0.0008 | -0.0009 | 0.0033 | -0.021 | -0.0068 | -360.1927 | 17.4254 | -360.4727 | 17.6594 | -360.7989 | 18.1461 | -360.8358 | 17.6184 | -352.6229 | 18.7025 | -352.6598 | 16.8012
12:44 | 5050 | 43.718 | 202.57 | 450.0104 | 457.0439 | -16.5186 | -40.176 | 11.395 | 8.0529 | 2.5136 | 0.8162 | 3.3654 | -0.9707 | 11.9757 | 4.826 | 0.6195 | 0.6614 | 0.9623 | 0.7458 | -129.3251 | 0.7761 | 5.8384 | 2.0129 | -2.6287 | -1.135 | 4.6544 |  | 3.6907 | 0.4697 | 4.009 | 3.3657 | 3.3359 | 1.0837 | 10.789 | 14.3094 | 14.8925 | 11.1175 | -0.0003 | -0.0023 | 0.0011 | 0.0041 | 0.0007 | -0.0002 | -0.0036 | -0.0124 | -0.0044 | -360.2111 | 17.4213 | -360.5035 | 17.7046 | -360.8666 | 18.1461 | -360.8297 | 17.6143 | -352.6506 | 18.7087 | -352.666 | 16.8238
12:44 | 5051 | 43.6837 | 202.5399 | 450.0188 | 457.0329 | -16.3939 | -40.1188 | 11.5153 | 7.9873 | 2.457 | 0.9446 | 3.3659 | -0.8733 | 12.0024 | 4.8028 | 0.6192 | 0.6588 | 0.9589 | 0.7456 | -129.3704 | 0.6229 | 5.7282 | 2.0053 | -2.6241 | -0.9793 | 4.7228 |  | 3.6961 | 0.4341 | 4.0076 | 3.3656 | 3.3384 | 1.0833 | 10.8054 | 14.2844 | 14.8695 | 11.1006 | 0 | -0.003 | 0.0006 | 0.0037 | 0.0009 | -0.0011 | 0.0156 | 0.0123 | -0.024 | -360.1988 | 17.4151 | -360.4573 | 17.6759 | -360.842 | 18.1543 | -360.8574 | 17.6143 | -352.629 | 18.7169 | -352.6598 | 16.8115
12:44 | 5052 | 43.7195 | 202.6011 | 449.9528 | 457.0198 | -16.3808 | -40.1596 | 11.4369 | 8.0303 | 2.4156 | 0.869 | 3.3362 | -0.9184 | 11.9186 | 4.7515 | 0.6195 | 0.6605 | 0.9633 | 0.7462 | -129.3045 | 0.7129 | 5.798 | 1.9936 | -2.6685 | -1.0793 | 4.666 |  | 3.7001 | 0.4127 | 4.0087 | 3.3679 | 3.3405 | 1.0844 | 10.7835 | 14.2678 | 14.8214 | 11.1028 | 0 | -0.0032 | 0.0004 | 0.0037 | 0.0006 | -0.0004 | 0.0017 | -0.009 | 0.0083 | -360.1711 | 17.4254 | -360.4819 | 17.6677 | -360.805 | 18.1522 | -360.8789 | 17.6143 | -352.6629 | 18.7169 | -352.6629 | 16.8176
12:44 | 5053 | 43.7675 | 202.632 | 449.9416 | 457.036 | -16.2691 | -40.0148 | 11.5387 | 8.0325 | 2.3587 | 0.9104 | 3.3202 | -0.9555 | 11.9455 | 4.8099 | 0.6188 | 0.6623 | 0.9623 | 0.7472 | -129.3245 | 0.6939 | 5.813 | 2.0461 | -2.6934 | -1.0714 | 4.7156 |  | 3.6945 | 0.4541 | 4.0088 | 3.3651 | 3.3367 | 1.0835 | 10.7787 | 14.2523 | 14.8444 | 11.0966 | 0.0002 | -0.0029 | 0.0009 | 0.004 | 0.001 | -0.0007 | 0.0132 | -0.0206 | -0.0202 | -360.1773 | 17.4295 | -360.4758 | 17.682 | -360.8235 | 18.1522 | -360.8543 | 17.6143 | -352.6383 | 18.721 | -352.6598 | 16.8279
12:44 | 5054 | 43.7277 | 202.5984 | 449.9594 | 456.9885 | -16.3221 | -39.9637 | 11.5274 | 8.041 | 2.3221 | 0.8226 | 3.2703 | -0.9183 | 11.9323 | 4.8397 | 0.6196 | 0.6634 | 0.9588 | 0.7454 | -129.3797 | 0.6843 | 5.6566 | 2.0159 | -2.6656 | -1.0699 | 4.6669 |  | 3.606 | 0.4229 | 4.0082 | 3.363 | 3.3375 | 1.0823 | 10.7615 | 14.2459 | 14.8459 | 11.0692 | -0.0004 | -0.0027 | 0.0006 | 0.0038 | 0.0004 | -0.0003 | 0.0086 | 0.0027 | -0.002 | -360.2019 | 17.4295 | -360.4604 | 17.6677 | -360.8143 | 18.1584 | -360.8481 | 17.6266 | -352.6444 | 18.7148 | -352.6537 | 16.8115
12:44 | 5055 | 43.7546 | 202.6099 | 449.9897 | 457.0271 | -16.265 | -39.9848 | 11.4642 | 8.0399 | 2.2721 | 0.8537 | 3.3287 | -0.9177 | 11.9566 | 4.8965 | 0.6208 | 0.6646 | 0.9641 | 0.7474 | -129.2585 | 0.7895 | 5.7662 | 2.1264 | -2.6421 | -0.9545 | 4.6569 |  | 3.6517 | 0.4238 | 4.0088 | 3.3702 | 3.3387 | 1.0865 | 10.7707 | 14.2729 | 14.829 | 11.0544 | 0.0001 | -0.0027 | 0.0008 | 0.0038 | 0.0013 | -0.0004 | 0.0049 | 0.0096 | 0.0146 | -360.1681 | 17.4356 | -360.5066 | 17.6841 | -360.8389 | 18.1543 | -360.8666 | 17.6122 | -352.6567 | 18.7148 | -352.6629 | 16.8279
12:44 | 5056 | 43.8001 | 202.6918 | 450.1097 | 457.0115 | -16.3537 | -40.0478 | 11.497 | 8.0065 | 2.3214 | 0.8817 | 3.3202 | -0.9388 | 11.9729 | 4.9059 | 0.6186 | 0.6634 | 0.9595 | 0.745 | -129.3844 | 0.8108 | 5.7917 | 2.0677 | -2.5819 | -1.0123 | 4.6478 |  | 3.6385 | 0.3491 | 4.0087 | 3.3664 | 3.3375 | 1.0848 | 10.7881 | 14.2727 | 14.8395 | 11.0952 | 0.0004 | -0.003 | 0.001 | 0.0039 | 0.0007 | -0.0002 | 0.0217 | -0.0024 | -0.0033 | -360.1773 | 17.411 | -360.4604 | 17.6902 | -360.8266 | 18.1687 | -360.8666 | 17.6225 | -352.6444 | 18.7066 | -352.6598 | 16.8238
12:44 | 5057 | 43.77 | 202.6964 | 450.0762 | 457.0673 | -16.328 | -40.0858 | 11.5334 | 7.9806 | 2.3388 | 0.9236 | 3.3258 | -0.8574 | 11.8489 | 4.7485 | 0.6185 | 0.663 | 0.9586 | 0.7465 | -129.3213 | 0.7268 | 5.709 | 2.0259 | -2.7088 | -1.0944 | 4.5799 |  | 3.7093 | 0.4522 | 4.0095 | 3.3701 | 3.3396 | 1.0846 | 10.8146 | 14.3055 | 14.8631 | 11.1323 | -0.0003 | -0.0026 | 0.0008 | 0.0036 | 0.001 | 0 | 0.0041 | -0.0235 | -0.0301 | -360.2204 | 17.4336 | -360.4881 | 17.6841 | -360.8512 | 18.1502 | -360.8543 | 17.6348 | -352.6567 | 18.7292 | -352.6506 | 16.8094
12:44 | 5058 | 43.7658 | 202.6933 | 450.0033 | 456.9985 | -16.3652 | -40.0893 | 11.5197 | 8.0066 | 2.3668 | 0.9359 | 3.4056 | -0.8843 | 11.9101 | 4.7897 | 0.6181 | 0.664 | 0.9601 | 0.7447 | -129.3246 | 0.7473 | 5.8072 | 1.999 | -2.687 | -1.0062 | 4.6418 |  | 3.6614 | 0.5581 | 4.0079 | 3.3657 | 3.3415 | 1.0843 | 10.7822 | 14.2673 | 14.8359 | 11.0944 | 0 | -0.0024 | 0.0005 | 0.0039 | 0.0008 | -0.0005 | 0.0073 | -0.0201 | -0.0016 | -360.1865 | 17.4274 | -360.5066 | 17.7108 | -360.8266 | 18.1604 | -360.8574 | 17.602 | -352.6198 | 18.7271 | -352.7029 | 16.8402
12:44 | 5059 | 43.7576 | 202.6182 | 449.9434 | 457.0239 | -16.2973 | -40.0835 | 11.5157 | 7.9659 | 2.2986 | 0.7893 | 3.2629 | -0.9071 | 11.9427 | 4.8248 | 0.6202 | 0.6624 | 0.964 | 0.7466 | -129.3254 | 0.7487 | 5.7342 | 2.0547 | -2.6438 | -0.9224 | 4.6815 |  | 3.6592 | 0.5483 | 4.0069 | 3.3675 | 3.341 | 1.0857 | 10.8238 | 14.3264 | 14.8673 | 11.1183 | -0.0001 | -0.0027 | 0.0007 | 0.0037 | 0.0006 | 0 | 0.002 | -0.0135 | 0.002 | -360.2019 | 17.4048 | -360.4542 | 17.6902 | -360.805 | 18.1625 | -360.8666 | 17.6184 | -352.6537 | 18.7128 | -352.6537 | 16.8238
12:44 | 5060 | 43.7545 | 202.6667 | 450.0519 | 457.0101 | -16.2955 | -40.104 | 11.5038 | 7.9909 | 2.3095 | 0.6819 | 3.2104 | -0.9132 | 11.9756 | 4.8206 | 0.62 | 0.663 | 0.961 | 0.7447 | -129.2771 | 0.7137 | 5.693 | 1.9638 | -2.6402 | -1.0309 | 4.6044 |  | 3.6342 | 0.43 | 4.0084 | 3.3656 | 3.3375 | 1.0837 | 10.795 | 14.2799 | 14.8304 | 11.0901 | 0.0001 | -0.0034 | 0.0005 | 0.0038 | 0.0007 | -0.001 | 0.0261 | 0.0009 | -0.0031 | -360.2265 | 17.4336 | -360.4573 | 17.6677 | -360.8081 | 18.1461 | -360.8697 | 17.6204 | -352.6937 | 18.7271 | -352.6567 | 16.8053
12:44 | 5061 | 43.7853 | 202.6975 | 450.0027 | 457.005 | -16.4042 | -40.3414 | 11.4069 | 8.0637 | 2.3536 | 0.8688 | 3.3213 | -0.9701 | 11.8996 | 4.82 | 0.6191 | 0.6628 | 0.9594 | 0.7441 | -129.3491 | 0.6749 | 5.7723 | 1.9767 | -2.7298 | -1.0312 | 4.6513 |  | 3.7333 | 0.4725 | 4.0087 | 3.3677 | 3.3391 | 1.0842 | 10.7822 | 14.2671 | 14.829 | 11.1064 | 0 | -0.003 | 0.0006 | 0.0036 | 0.0005 | -0.0002 | 0.0162 | -0.0142 | -0.0014 | -360.1619 | 17.4233 | -360.5035 | 17.7046 | -360.8389 | 18.1481 | -360.8174 | 17.5958 | -352.6229 | 18.721 | -352.6844 | 16.8381
12:44 | 5062 | 43.778 | 202.6064 | 450.0064 | 457.0701 | -16.3996 | -40.2005 | 11.3853 | 8.008 | 2.3241 | 0.8202 | 3.2856 | -0.9672 | 11.9542 | 4.7745 | 0.6173 | 0.6645 | 0.9648 | 0.7459 | -129.2822 | 0.6716 | 5.7158 | 2.0151 | -2.6372 | -1.0457 | 4.68 |  | 3.7077 | 0.4717 | 4.009 | 3.3651 | 3.3385 | 1.0846 | 10.7684 | 14.2647 | 14.8379 | 11.0927 | -0.0002 | -0.0026 | 0.0009 | 0.0039 | 0.0009 | -0.0008 | 0.012 | -0.0046 | -0.0084 | -360.1988 | 17.3966 | -360.4204 | 17.6882 | -360.8389 | 18.1707 | -360.8789 | 17.6184 | -352.6629 | 18.7004 | -352.669 | 16.832
12:44 | 5063 | 43.8102 | 202.6079 | 449.9367 | 457.0852 | -16.4744 | -40.3703 | 11.3476 | 8.0154 | 2.3158 | 0.9241 | 3.3645 | -0.8324 | 11.9525 | 4.7902 | 0.619 | 0.6633 | 0.9629 | 0.7458 | -129.2707 | 0.7088 | 5.7622 | 2.0576 | -2.5848 | -0.9983 | 4.725 |  | 3.7155 | 0.4627 | 4.0094 | 3.367 | 3.3377 | 1.084 | 10.7949 | 14.28 | 14.8315 | 11.1129 | -0.0004 | -0.0031 | 0.0012 | 0.0045 | 0.0005 | -0.0005 | 0.019 | -0.0203 | 0.0081 | -360.1865 | 17.4254 | -360.4419 | 17.6636 | -360.7835 | 18.1337 | -360.8697 | 17.6143 | -352.6475 | 18.721 | -352.6413 | 16.7991
12:44 | 5064 | 43.707 | 202.5876 | 449.9792 | 457.0253 | -16.4357 | -40.3497 | 11.5444 | 7.9953 | 2.2272 | 0.8647 | 3.3602 | -0.8478 | 11.9707 | 4.8128 | 0.6182 | 0.6635 | 0.9596 | 0.7467 | -129.273 | 0.7234 | 5.7616 | 2.1065 | -2.5778 | -1.0293 | 4.7317 |  | 3.7221 | 0.4367 | 4.0071 | 3.3684 | 3.3426 | 1.0845 | 10.7742 | 14.2879 | 14.8552 | 11.0984 | 0.0001 | -0.003 | 0.0007 | 0.0042 | 0.0009 | -0.0007 | 0.0172 | -0.0188 | 0.0039 | -360.1496 | 17.4233 | -360.5035 | 17.6985 | -360.8666 | 18.1337 | -360.8389 | 17.604 | -352.6106 | 18.7169 | -352.669 | 16.8381
12:44 | 5065 | 43.7647 | 202.5845 | 449.9454 | 457.0544 | -16.3938 | -40.3171 | 11.4021 | 8.0049 | 2.2423 | 0.8323 | 3.313 | -0.8552 | 12.0177 | 4.8225 | 0.6186 | 0.6612 | 0.961 | 0.7466 | -129.2236 | 0.7111 | 5.5685 | 2.0845 | -2.6283 | -1.099 | 4.6075 |  | 3.6898 | 0.4779 | 4.0081 | 3.3669 | 3.3382 | 1.0843 | 10.8145 | 14.2883 | 14.8816 | 11.1146 | 0.0003 | -0.0026 | 0.0005 | 0.0038 | 0.0003 | -0.0002 | 0.0143 | -0.0095 | 0.0026 | -360.1835 | 17.3925 | -360.405 | 17.6533 | -360.8204 | 18.1584 | -360.8604 | 17.6225 | -352.669 | 18.6943 | -352.6444 | 16.8115
12:44 | 5066 | 43.7959 | 202.6582 | 449.9796 | 457.0903 | -16.4126 | -40.3225 | 11.4409 | 8.0364 | 2.277 | 0.8507 | 3.348 | -0.8331 | 11.9561 | 4.7691 | 0.6182 | 0.6613 | 0.9624 | 0.7458 | -129.2217 | 0.6587 | 5.5902 | 2.0685 | -2.6624 | -1.0321 | 4.6118 |  | 3.6268 | 0.533 | 4.0091 | 3.3654 | 3.3358 | 1.0836 | 10.8019 | 14.2693 | 14.8539 | 11.0973 | -0.0006 | -0.0029 | 0.0006 | 0.0041 | 0.0009 | -0.0008 | 0.0247 | -0.0084 | -0.0252 | -360.2111 | 17.4295 | -360.4635 | 17.6533 | -360.7712 | 18.1358 | -360.8297 | 17.6143 | -352.6813 | 18.7395 | -352.7029 | 16.8053
12:44 | 5067 | 43.8505 | 202.6483 | 450.0334 | 457.0458 | -16.447 | -40.3316 | 11.5346 | 8.1176 | 2.3366 | 0.778 | 3.4432 | -0.8755 | 12.0404 | 4.8906 | 0.6186 | 0.6602 | 0.9594 | 0.747 | -129.2059 | 0.6022 | 5.5877 | 2.0565 | -2.5935 | -1.0597 | 4.6296 |  | 3.636 | 0.43 | 4.0095 | 3.3665 | 3.3395 | 1.0851 | 10.8087 | 14.2825 | 14.8758 | 11.1204 | -0.0002 | -0.0026 | 0.0006 | 0.0035 | 0.0011 | 0 | 0.0048 | -0.0223 | -0.0077 | -360.1404 | 17.4069 | -360.4789 | 17.6985 | -360.845 | 18.1481 | -360.8297 | 17.5855 | -352.6167 | 18.7128 | -352.6998 | 16.8361
12:44 | 5068 | 43.7342 | 202.5725 | 449.9918 | 457.0031 | -16.3955 | -40.2779 | 11.3578 | 8.0778 | 2.3476 | 0.8137 | 3.3387 | -0.9125 | 11.9762 | 4.9057 | 0.6196 | 0.6681 | 0.9601 | 0.7485 | -129.3201 | 0.6055 | 5.5978 | 2.043 | -2.5972 | -1.0946 | 4.6834 |  | 3.5717 | 0.4733 | 4.008 | 3.3664 | 3.337 | 1.0842 | 10.7707 | 14.2844 | 14.8406 | 11.0833 | 0.0002 | -0.0031 | 0.0009 | 0.0043 | 0.0008 | -0.0007 | 0.0231 | -0.0065 | 0 | -360.1927 | 17.3987 | -360.3958 | 17.6471 | -360.8112 | 18.1625 | -360.9035 | 17.6307 | -352.6721 | 18.7045 | -352.6383 | 16.8053
12:44 | 5069 | 43.7424 | 202.5747 | 449.9923 | 456.9819 | -16.3739 | -40.1223 | 11.4838 | 8.0274 | 2.3106 | 0.8735 | 3.3151 | -0.9253 | 12.0153 | 4.8431 | 0.6189 | 0.6658 | 0.9637 | 0.7465 | -129.2302 | 0.6522 | 5.6492 | 2.0353 | -2.5959 | -1.0469 | 4.6573 |  | 3.6318 | 0.4614 | 4.0075 | 3.3652 | 3.3387 | 1.0848 | 10.7707 | 14.2612 | 14.8511 | 11.1125 | -0.0001 | -0.003 | 0.0005 | 0.0037 | 0.001 | -0.0005 | 0.0144 | -0.0239 | -0.0229 | -360.1804 | 17.4315 | -360.4789 | 17.6718 | -360.8081 | 18.1317 | -360.8143 | 17.6122 | -352.6813 | 18.7292 | -352.7121 | 16.8197
12:44 | 5070 | 43.7278 | 202.5858 | 450.0506 | 457.0481 | -16.3547 | -40.1592 | 11.4329 | 8.0177 | 2.3107 | 0.7641 | 3.3337 | -0.8591 | 12.0826 | 4.8951 | 0.6176 | 0.6647 | 0.9592 | 0.7477 | -129.2684 | 0.694 | 5.6393 | 2.1071 | -2.5783 | -0.9803 | 4.7316 |  | 3.597 | 0.4433 | 4.008 | 3.3651 | 3.34 | 1.0846 | 10.7798 | 14.2478 | 14.8237 | 11.0742 | -0.0001 | -0.0024 | 0.0011 | 0.0037 | 0.0014 | 0.0003 | 0.0182 | -0.0014 | -0.0025 | -360.1065 | 17.3966 | -360.4542 | 17.682 | -360.845 | 18.1604 | -360.8297 | 17.5855 | -352.5983 | 18.6984 | -352.6967 | 16.8402
12:44 | 5071 | 43.6904 | 202.6378 | 449.9165 | 457.0809 | -16.3569 | -40.1957 | 11.3296 | 8.0118 | 2.2987 | 0.7683 | 3.3643 | -0.8701 | 12.0012 | 4.8082 | 0.6182 | 0.6603 | 0.9585 | 0.7481 | -129.3166 | 0.7264 | 5.6864 | 2.1403 | -2.5204 | -0.9188 | 4.731 |  | 3.6304 | 0.4776 | 4.0083 | 3.3667 | 3.3405 | 1.0853 | 10.8135 | 14.2637 | 14.8549 | 11.1085 | -0.0001 | -0.0026 | 0.0005 | 0.0037 | 0.0011 | -0.0007 | 0.0054 | -0.0089 | -0.0149 | -360.1896 | 17.3987 | -360.4235 | 17.6389 | -360.7835 | 18.1543 | -360.882 | 17.6328 | -352.6475 | 18.7004 | -352.6383 | 16.8053
12:44 | 5072 | 43.6515 | 202.6654 | 450.0364 | 457.0455 | -16.4316 | -40.1781 | 11.3347 | 8.0336 | 2.3481 | 0.7439 | 3.3957 | -0.8524 | 12.0424 | 4.8362 | 0.6191 | 0.6637 | 0.9578 | 0.7474 | -129.3138 | 0.6648 | 5.7029 | 2.1295 | -2.6447 | -0.892 | 4.6914 |  | 3.6159 | 0.5923 | 4.0099 | 3.3676 | 3.3366 | 1.0858 | 10.7821 | 14.279 | 14.889 | 11.0594 | 0.0003 | -0.003 | 0.0006 | 0.0036 | 0.0008 | -0.0002 | 0.0258 | -0.0048 | -0.0045 | -360.1835 | 17.4233 | -360.4604 | 17.6677 | -360.7958 | 18.1255 | -360.7989 | 17.5896 | -352.6506 | 18.7333 | -352.6721 | 16.8258
12:44 | 5073 | 43.6722 | 202.6501 | 449.9604 | 457.0447 | -16.447 | -40.1203 | 11.3319 | 8.1015 | 2.3232 | 0.7979 | 3.3365 | -0.8547 | 11.9869 | 4.8764 | 0.6186 | 0.6637 | 0.961 | 0.748 | -129.2865 | 0.6355 | 5.7648 | 2.1542 | -2.5371 | -0.9478 | 4.775 |  | 3.6412 | 0.445 | 4.0092 | 3.3653 | 3.3378 | 1.0851 | 10.8007 | 14.2684 | 14.8604 | 11.0897 | 0.0001 | -0.0029 | 0.0008 | 0.004 | 0.001 | -0.0006 | 0.0099 | -0.0145 | -0.0191 | -360.1281 | 17.3884 | -360.445 | 17.6738 | -360.842 | 18.1666 | -360.845 | 17.5835 | -352.6136 | 18.6922 | -352.6598 | 16.832
12:44 | 5074 | 43.747 | 202.6562 | 450.0473 | 457.042 | -16.4951 | -40.1166 | 11.3321 | 8.0862 | 2.2551 | 0.759 | 3.319 | -0.8541 | 12.0562 | 4.8922 | 0.6189 | 0.6594 | 0.9602 | 0.7474 | -129.2728 | 0.6558 | 5.7063 | 1.9668 | -2.5849 | -0.9442 | 4.7066 |  | 3.664 | 0.3845 | 4.0094 | 3.3677 | 3.3369 | 1.0835 | 10.7569 | 14.2876 | 14.8473 | 11.0934 | -0.0003 | -0.0025 | 0.0005 | 0.0036 | 0.0001 | -0.0007 | 0.0179 | -0.0092 | -0.0194 | -360.2296 | 17.409 | -360.4142 | 17.6471 | -360.7681 | 18.1358 | -360.8789 | 17.6348 | -352.6937 | 18.7169 | -352.6475 | 16.7909
12:44 | 5075 | 43.7253 | 202.6784 | 450.009 | 457.0547 | -16.4071 | -40.1154 | 11.5742 | 8.0533 | 2.2293 | 0.6762 | 3.3485 | -0.9198 | 11.9406 | 4.8406 | 0.6188 | 0.6603 | 0.9599 | 0.7462 | -129.2412 | 0.7118 | 5.6384 | 1.8986 | -2.6244 | -0.9654 | 4.7082 |  | 3.6476 | 0.36 | 4.0084 | 3.3621 | 3.3376 | 1.0856 | 10.7764 | 14.273 | 14.8532 | 11.106 | -0.0002 | -0.0026 | 0.001 | 0.0042 | 0.0011 | -0.0004 | 0.0176 | -0.0102 | 0.009 | -360.165 | 17.4274 | -360.485 | 17.6697 | -360.8112 | 18.1296 | -360.7897 | 17.5876 | -352.6506 | 18.7292 | -352.6906 | 16.8299
12:44 | 5076 | 43.6853 | 202.5931 | 449.9875 | 457.0519 | -16.4414 | -40.1359 | 11.4933 | 8.0762 | 2.275 | 0.7395 | 3.403 | -0.9088 | 11.9777 | 4.8261 | 0.6177 | 0.6623 | 0.9611 | 0.7463 | -129.2377 | 0.6437 | 5.6723 | 2.1028 | -2.6178 | -0.98 | 4.7256 |  | 3.7211 | 0.4663 | 4.01 | 3.368 | 3.3403 | 1.0852 | 10.7996 | 14.2902 | 14.8638 | 11.1006 | 0.0004 | -0.0025 | 0.0007 | 0.0041 | 0.0004 | -0.0004 | 0.016 | -0.0143 | -0.007 | -360.1742 | 17.3864 | -360.405 | 17.6738 | -360.8543 | 18.1687 | -360.8635 | 17.5937 | -352.6136 | 18.6902 | -352.6321 | 16.8238
12:44 | 5077 | 43.6885 | 202.6587 | 450.0182 | 457.074 | -16.4272 | -40.0897 | 11.4043 | 8.1462 | 2.3 | 0.793 | 3.3642 | -0.8672 | 12.0219 | 4.8707 | 0.6195 | 0.6657 | 0.9625 | 0.7476 | -129.2161 | 0.6533 | 5.6661 | 2.0328 | -2.6588 | -0.9869 | 4.6953 |  | 3.7925 | 0.4103 | 4.0092 | 3.3673 | 3.3414 | 1.0858 | 10.7673 | 14.2576 | 14.8586 | 11.1093 | 0.0002 | -0.0032 | 0.0008 | 0.0043 | 0.0015 | -0.0007 | 0.0018 | -0.0023 | -0.012 | -360.245 | 17.4233 | -360.4358 | 17.6471 | -360.7989 | 18.1214 | -360.8727 | 17.643 | -352.6813 | 18.721 | -352.6413 | 16.7909
12:44 | 5078 | 43.702 | 202.6929 | 450.0614 | 457.1076 | -16.3418 | -40.0591 | 11.4714 | 8.1231 | 2.3402 | 0.7433 | 3.3762 | -0.9281 | 12.0118 | 4.788 | 0.6178 | 0.6589 | 0.961 | 0.7473 | -129.2646 | 0.6195 | 5.6788 | 2.0621 | -2.7235 | -0.9356 | 4.6028 |  | 3.6992 | 0.4159 | 4.0095 | 3.3661 | 3.3406 | 1.0844 | 10.7914 | 14.2535 | 14.8342 | 11.0746 | -0.0001 | -0.0027 | 0.0006 | 0.0033 | 0.0008 | 0 | -0.0053 | -0.0096 | -0.0095 | -360.1773 | 17.4274 | -360.5066 | 17.68 | -360.8327 | 18.1317 | -360.802 | 17.5958 | -352.6229 | 18.7251 | -352.6967 | 16.8423
12:44 | 5079 | 43.7998 | 202.6801 | 450.0589 | 457.1634 | -16.3634 | -40.1513 | 11.4034 | 8.1474 | 2.4145 | 0.811 | 3.3334 | -0.8977 | 12.0189 | 4.8567 | 0.6173 | 0.6608 | 0.9618 | 0.7475 | -129.2542 | 0.7229 | 5.705 | 2.0301 | -2.6352 | -0.9812 | 4.6599 |  | 3.6479 | 0.3477 | 4.0103 | 3.3674 | 3.3401 | 1.0848 | 10.7962 | 14.2403 | 14.8296 | 11.1035 | -0.0001 | -0.0022 | 0.0006 | 0.0035 | 0.0008 | -0.0006 | 0.0096 | -0.0161 | -0.0115 | -360.1711 | 17.3905 | -360.4512 | 17.6636 | -360.8512 | 18.1748 | -360.8912 | 17.6122 | -352.6352 | 18.6881 | -352.6106 | 16.8381
12:44 | 5080 | 43.7642 | 202.6116 | 450.0925 | 457.1331 | -16.3489 | -40.0303 | 11.4904 | 8.1023 | 2.3187 | 0.8127 | 3.307 | -0.7864 | 12.0652 | 4.8554 | 0.6188 | 0.6641 | 0.9668 | 0.7483 | -129.1961 | 0.7811 | 5.6679 | 1.9798 | -2.6931 | -1.003 | 4.6218 |  | 3.6826 | 0.3359 | 4.0094 | 3.3675 | 3.3405 | 1.0861 | 10.7822 | 14.2555 | 14.829 | 11.0486 | 0.0001 | -0.0028 | 0.001 | 0.0039 | 0.0007 | -0.0003 | 0.0129 | -0.0081 | -0.0024 | -360.2419 | 17.4356 | -360.4666 | 17.6163 | -360.7681 | 18.1276 | -360.8358 | 17.643 | -352.6937 | 18.723 | -352.6506 | 16.8032
12:44 | 5081 | 43.7855 | 202.5394 | 450.098 | 457.1542 | -16.4668 | -40.1423 | 11.3937 | 8.0966 | 2.3617 | 0.8849 | 3.3796 | -0.8797 | 11.9825 | 4.8113 | 0.6193 | 0.6636 | 0.9638 | 0.7479 | -129.226 | 0.7417 | 5.6495 | 1.8954 | -2.8002 | -1.0289 | 4.6554 |  | 3.6755 | 0.2673 | 4.0104 | 3.3658 | 3.3392 | 1.0837 | 10.8042 | 14.2892 | 14.8634 | 11.1107 | 0.0001 | -0.0031 | 0.001 | 0.004 | 0.0007 | -0.0003 | 0.0095 | -0.0085 | -0.0156 | -360.1435 | 17.4254 | -360.5066 | 17.6759 | -360.8481 | 18.1481 | -360.7989 | 17.5896 | -352.6198 | 18.7128 | -352.6967 | 16.8587
12:44 | 5082 | 43.7689 | 202.6312 | 450.0752 | 457.1226 | -16.3221 | -40.1497 | 11.4231 | 8.0879 | 2.4218 | 0.8935 | 3.4024 | -0.9407 | 11.898 | 4.9161 | 0.6192 | 0.6632 | 0.9626 | 0.7467 | -129.2515 | 0.8374 | 5.7016 | 1.899 | -2.7902 | -1.0813 | 4.6253 |  | 3.6988 | 0.3478 | 4.0091 | 3.3688 | 3.3405 | 1.085 | 10.8008 | 14.2913 | 14.8814 | 11.0905 | -0.0003 | -0.0031 | 0.0008 | 0.004 | 0.0007 | -0.0004 | 0.0142 | -0.0035 | -0.0005 | -360.1681 | 17.3987 | -360.4266 | 17.6348 | -360.8327 | 18.183 | -360.9004 | 17.6245 | -352.6537 | 18.6902 | -352.6352 | 16.8197
12:44 | 5083 | 43.8007 | 202.6673 | 450.0692 | 457.0374 | -16.5146 | -40.0951 | 11.3932 | 8.0384 | 2.4462 | 0.8054 | 3.3681 | -0.8822 | 12.0178 | 4.8623 | 0.6205 | 0.6671 | 0.9649 | 0.7488 | -129.2052 | 0.9298 | 5.7445 | 1.9311 | -2.784 | -1.0265 | 4.6285 |  | 3.6868 | 0.3487 | 4.0097 | 3.367 | 3.3407 | 1.086 | 10.7844 | 14.3046 | 14.835 | 11.1363 | -0.0006 | -0.0027 | 0.0011 | 0.0045 | 0.0008 | 0 | 0.0049 | -0.008 | 0.0027 | -360.2327 | 17.4439 | -360.4819 | 17.6307 | -360.7989 | 18.1255 | -360.8512 | 17.6225 | -352.666 | 18.7353 | -352.6998 | 16.8238
12:44 | 5084 | 43.8329 | 202.7084 | 450.1034 | 457.0327 | -16.4605 | -40.0733 | 11.4334 | 8.0893 | 2.4404 | 0.7277 | 3.307 | -0.9027 | 11.9997 | 4.8153 | 0.6181 | 0.6608 | 0.9641 | 0.7479 | -129.2502 | 0.8053 | 5.7136 | 1.8928 | -2.783 | -1.1577 | 4.6166 |  | 3.6337 | 0.3699 | 4.0096 | 3.3643 | 3.3415 | 1.083 | 10.8065 | 14.2974 | 14.8488 | 11.1129 | 0.0001 | -0.0027 | 0.0008 | 0.0042 | 0.0006 | -0.0006 | 0.0027 | -0.0074 | -0.0197 | -360.1588 | 17.4172 | -360.4942 | 17.6841 | -360.882 | 18.144 | -360.8389 | 17.5917 | -352.5952 | 18.7066 | -352.7183 | 16.8607
12:44 | 5085 | 43.7981 | 202.6825 | 450.159 | 457.0958 | -16.4377 | -40.1105 | 11.484 | 8.0054 | 2.3333 | 0.8079 | 3.3831 | -0.9812 | 11.934 | 4.7361 | 0.6195 | 0.6627 | 0.9647 | 0.7481 | -129.1465 | 0.7278 | 5.7788 | 1.8967 | -2.7868 | -1.0569 | 4.5803 |  | 3.6259 | 0.3735 | 4.0085 | 3.3672 | 3.3396 | 1.0843 | 10.8053 | 14.2963 | 14.8369 | 11.0998 | 0.0002 | -0.0033 | 0.001 | 0.0043 | 0.0006 | 0.0001 | 0.0106 | -0.008 | -0.0313 | -360.1958 | 17.3987 | -360.405 | 17.6348 | -360.8358 | 18.1666 | -360.8912 | 17.6286 | -352.6075 | 18.682 | -352.6321 | 16.8115
12:44 | 5086 | 43.8505 | 202.6881 | 450.1731 | 457.1371 | -16.4368 | -40.1441 | 11.4026 | 8.0134 | 2.2983 | 0.8854 | 3.3856 | -0.8902 | 11.9795 | 4.8944 | 0.6198 | 0.6649 | 0.9643 | 0.7479 | -129.1706 | 0.7509 | 5.7211 | 1.9258 | -2.6827 | -0.9888 | 4.5648 |  | 3.7167 | 0.4031 | 4.0093 | 3.3707 | 3.3418 | 1.0842 | 10.7995 | 14.2848 | 14.8717 | 11.1287 | 0 | -0.0027 | 0.001 | 0.0037 | 0.0007 | -0.0012 | -0.0017 | -0.0074 | -0.0136 | -360.2265 | 17.4439 | -360.4942 | 17.6369 | -360.8081 | 18.1296 | -360.8174 | 17.6204 | -352.6875 | 18.7312 | -352.669 | 16.8217
12:44 | 5087 | 43.7978 | 202.66 | 450.1339 | 457.0993 | -16.489 | -40.2634 | 11.3344 | 8.0908 | 2.3283 | 0.9484 | 3.4489 | -0.8475 | 12.0206 | 4.8258 | 0.6195 | 0.6666 | 0.9623 | 0.7466 | -129.3055 | 0.7482 | 5.7024 | 1.8969 | -2.6224 | -0.9854 | 4.5904 |  | 3.7515 | 0.452 | 4.0087 | 3.3661 | 3.3366 | 1.0851 | 10.7822 | 14.3076 | 14.8638 | 11.0948 | -0.0005 | -0.003 | 0.0003 | 0.0034 | 0.0006 | -0.0001 | 0.0099 | -0.0111 | 0.0007 | -360.1558 | 17.4131 | -360.4758 | 17.6697 | -360.885 | 18.1687 | -360.8327 | 17.5835 | -352.5952 | 18.6902 | -352.6721 | 16.8484
12:45 | 5088 | 43.7684 | 202.588 | 450.1739 | 457.1048 | -16.4662 | -40.1606 | 11.4533 | 8.0838 | 2.3145 | 0.9081 | 3.4192 | -0.9505 | 11.967 | 4.877 | 0.619 | 0.6645 | 0.9616 | 0.7459 | -129.2999 | 0.8013 | 5.6773 | 1.9013 | -2.6202 | -0.9524 | 4.6359 |  | 3.5659 | 0.3742 | 4.0093 | 3.3673 | 3.3401 | 1.0833 | 10.7418 | 14.2726 | 14.8269 | 11.0898 | -0.0002 | -0.003 | 0.0006 | 0.0037 | 0.0011 | -0.001 | 0.0022 | -0.0005 | -0.0204 | -360.2111 | 17.4069 | -360.4235 | 17.6163 | -360.8204 | 18.1481 | -360.8543 | 17.6328 | -352.666 | 18.6922 | -352.6167 | 16.7909
12:45 | 5089 | 43.7052 | 202.6134 | 450.128 | 457.2076 | -16.4882 | -40.104 | 11.3969 | 8.1059 | 2.3121 | 1.0236 | 3.4118 | -0.897 | 12.0123 | 4.8589 | 0.6194 | 0.6622 | 0.9622 | 0.7478 | -129.3749 | 0.7956 | 5.6541 | 1.8723 | -2.638 | -0.9803 | 4.6483 |  | 3.6038 | 0.3265 | 4.0101 | 3.3704 | 3.3425 | 1.0838 | 10.7915 | 14.2533 | 14.8563 | 11.0981 | 0 | -0.0034 | 0.0005 | 0.0034 | 0.0007 | -0.0002 | -0.0014 | -0.0073 | -0.0077 | -360.2204 | 17.4315 | -360.4819 | 17.643 | -360.8174 | 18.1153 | -360.8112 | 17.5999 | -352.6413 | 18.721 | -352.6813 | 16.8176
12:45 | 5090 | 43.708 | 202.5545 | 450.1914 | 457.0838 | -16.5003 | -40.1508 | 11.3979 | 8.0396 | 2.3053 | 0.8875 | 3.3838 | -0.9011 | 11.9579 | 4.8603 | 0.6208 | 0.6672 | 0.9602 | 0.7477 | -129.3574 | 0.7881 | 5.7108 | 1.9852 | -2.5784 | -0.912 | 4.7608 |  | 3.6319 | 0.4613 | 4.0104 | 3.3675 | 3.3422 | 1.0848 | 10.8019 | 14.2635 | 14.877 | 11.0916 | -0.0001 | -0.0029 | 0.0005 | 0.0042 | 0.001 | -0.0004 | 0.0162 | -0.0079 | -0.0119 | -360.0911 | 17.3884 | -360.4296 | 17.6471 | -360.8543 | 18.1604 | -360.8297 | 17.5794 | -352.5675 | 18.6758 | -352.6383 | 16.8238
12:45 | 5091 | 43.7976 | 202.5435 | 450.1196 | 457.079 | -16.4641 | -40.0957 | 11.4137 | 8.1251 | 2.4047 | 0.8845 | 3.4239 | -0.9741 | 11.9621 | 4.8228 | 0.6194 | 0.664 | 0.9628 | 0.7487 | -129.3608 | 0.7206 | 5.7118 | 1.9376 | -2.613 | -1.0069 | 4.7265 |  | 3.6014 | 0.3436 | 4.0095 | 3.3652 | 3.3406 | 1.083 | 10.7821 | 14.2733 | 14.8206 | 11.0764 | -0.0005 | -0.0025 | 0.001 | 0.0043 | 0.0006 | -0.0004 | 0.0126 | -0.0118 | -0.0012 | -360.1865 | 17.4172 | -360.4235 | 17.604 | -360.7743 | 18.1337 | -360.8727 | 17.6266 | -352.6752 | 18.7045 | -352.5767 | 16.7868
12:45 | 5092 | 43.7115 | 202.5454 | 450.1594 | 457.0442 | -16.4407 | -40.0895 | 11.3576 | 8.1571 | 2.3673 | 0.8578 | 3.338 | -0.9267 | 11.9458 | 4.7799 | 0.6204 | 0.6603 | 0.9587 | 0.7477 | -129.4215 | 0.7385 | 5.6918 | 1.8734 | -2.6898 | -0.9978 | 4.6446 |  | 3.6142 | 0.3042 | 4.0087 | 3.3684 | 3.3427 | 1.083 | 10.7902 | 14.3045 | 14.8513 | 11.102 | 0.0002 | -0.0025 | 0.0011 | 0.0037 | 0.0008 | -0.0002 | 0.0296 | -0.0183 | 0 | -360.1588 | 17.4439 | -360.5004 | 17.6389 | -360.8266 | 18.1235 | -360.7743 | 17.5835 | -352.6321 | 18.7148 | -352.6752 | 16.8197
12:45 | 5093 | 43.8424 | 202.5191 | 450.1365 | 457.1252 | -16.3833 | -40.0855 | 11.3975 | 8.0932 | 2.3873 | 0.7901 | 3.3508 | -0.9416 | 11.9607 | 4.7732 | 0.6202 | 0.6641 | 0.9574 | 0.7474 | -129.3155 | 0.7601 | 5.7092 | 1.9745 | -2.6276 | -1.0846 | 4.6475 |  | 3.5894 | 0.4247 | 4.0097 | 3.3678 | 3.3424 | 1.086 | 10.7937 | 14.3137 | 14.8948 | 11.123 | 0.0003 | -0.0029 | 0.0007 | 0.0036 | 0.0008 | -0.0005 | 0.0052 | -0.0019 | -0.0096 | -360.1158 | 17.372 | -360.4112 | 17.6266 | -360.8235 | 18.1604 | -360.8389 | 17.5896 | -352.5829 | 18.6655 | -352.589 | 16.8258
12:45 | 5094 | 43.8147 | 202.4847 | 450.0826 | 457.0376 | -16.4292 | -40.1837 | 11.3484 | 8.022 | 2.3004 | 0.8288 | 3.2512 | -0.9165 | 11.9816 | 4.8679 | 0.6195 | 0.6675 | 0.9591 | 0.7466 | -129.3095 | 0.8168 | 5.7454 | 2.0079 | -2.5595 | -0.9955 | 4.7199 |  | 3.6581 | 0.4675 | 4.009 | 3.3663 | 3.3421 | 1.0852 | 10.7729 | 14.2813 | 14.8744 | 11.1193 | 0.0001 | -0.0028 | 0.0006 | 0.0035 | 0.0008 | -0.0004 | 0.0212 | -0.0056 | -0.0223 | -360.2111 | 17.4213 | -360.4266 | 17.6081 | -360.762 | 18.1173 | -360.8297 | 17.6163 | -352.6567 | 18.7045 | -352.626 | 16.7868
12:45 | 5095 | 43.8373 | 202.4784 | 450.2518 | 457.0625 | -16.4493 | -40.1758 | 11.2726 | 8.0164 | 2.3465 | 0.7454 | 3.4676 | -0.948 | 12.0254 | 4.8541 | 0.6199 | 0.6627 | 0.9627 | 0.7479 | -129.305 | 0.8151 | 5.8203 | 1.9417 | -2.6452 | -0.9328 | 4.675 |  | 3.6233 | 0.3631 | 4.0093 | 3.3694 | 3.3401 | 1.0847 | 10.7949 | 14.3033 | 14.8846 | 11.072 | -0.0001 | -0.0025 | 0.0006 | 0.0039 | 0.0006 | -0.0006 | 0.0221 | 0.0033 | -0.0027 | -360.1404 | 17.4192 | -360.4758 | 17.643 | -360.8543 | 18.1214 | -360.7404 | 17.5691 | -352.5644 | 18.6984 | -352.6537 | 16.8238
12:45 | 5096 | 43.8466 | 202.4968 | 450.1288 | 457.0395 | -16.4711 | -40.2336 | 11.2586 | 8.0111 | 2.3386 | 0.7864 | 3.4093 | -0.8962 | 12.0082 | 4.8243 | 0.6205 | 0.6642 | 0.9615 | 0.7501 | -129.351 | 0.8627 | 5.6808 | 2.0196 | -2.6439 | -0.9453 | 4.6541 |  | 3.7064 | 0.3097 | 4.0087 | 3.3657 | 3.3391 | 1.0857 | 10.7696 | 14.26 | 14.8324 | 11.0768 | 0 | -0.0028 | 0.0007 | 0.0038 | 0.0003 | -0.0009 | 0.0026 | -0.0067 | -0.0087 | -360.1004 | 17.3679 | -360.3865 | 17.6245 | -360.8112 | 18.1625 | -360.8543 | 17.5917 | -352.6013 | 18.6717 | -352.589 | 16.8012
12:45 | 5097 | 43.9126 | 202.4976 | 450.0811 | 457.0611 | -16.5652 | -40.265 | 11.2639 | 8.0459 | 2.426 | 0.7612 | 3.3945 | -0.959 | 11.9764 | 4.9052 | 0.6212 | 0.6651 | 0.9617 | 0.7478 | -129.3606 | 0.7786 | 5.6843 | 1.9733 | -2.6692 | -1.112 | 4.6401 |  | 3.6421 | 0.2714 | 4.0093 | 3.3675 | 3.3382 | 1.0841 | 10.7614 | 14.2925 | 14.8249 | 11.1147 | 0 | -0.0032 | 0.0008 | 0.004 | 0.0008 | -0.0008 | 0.0138 | -0.0083 | -0.0294 | -360.2019 | 17.411 | -360.4419 | 17.5978 | -360.7497 | 18.1091 | -360.7835 | 17.602 | -352.6321 | 18.7066 | -352.6229 | 16.7786
12:45 | 5098 | 43.7244 | 202.4591 | 450.0828 | 456.9315 | -16.4196 | -40.1059 | 11.3238 | 8.0789 | 2.4142 | 0.8167 | 3.3291 | -0.9877 | 11.998 | 4.8242 | 0.62 | 0.6651 | 0.9618 | 0.7472 | -129.3572 | 0.7938 | 5.6998 | 1.9815 | -2.7314 | -0.9971 | 4.618 |  | 3.6989 | 0.3278 | 4.0118 | 3.3683 | 3.3394 | 1.0847 | 10.7765 | 14.2613 | 14.8406 | 11.1121 | 0.0005 | -0.0026 | 0.0009 | 0.0039 | 0.0008 | 0 | 0.0053 | -0.0165 | -0.0015 | -360.1127 | 17.4028 | -360.4696 | 17.6512 | -360.8327 | 18.1276 | -360.7866 | 17.5691 | -352.5644 | 18.6922 | -352.629 | 16.8258
12:45 | 5099 | 43.7671 | 202.5019 | 449.9943 | 456.9067 | -16.4857 | -40.1415 | 11.2735 | 8.0369 | 2.3058 | 0.7967 | 3.3094 | -0.9753 | 11.9814 | 4.7263 | 0.6198 | 0.6662 | 0.96 | 0.7484 | -129.37 | 0.8419 | 5.74 | 1.8688 | -2.7559 | -1.1287 | 4.6528 |  | 3.7009 | 0.4132 | 4.0108 | 3.3698 | 3.3389 | 1.0851 | 10.7822 | 14.2673 | 14.8417 | 11.0944 | -0.0003 | -0.0026 | 0.0012 | 0.0043 | 0.0009 | -0.0009 | -0.0045 | -0.0016 | -0.0304 | -360.1527 | 17.372 | -360.3804 | 17.6143 | -360.7835 | 18.1522 | -360.8574 | 17.5999 | -352.6167 | 18.6655 | -352.5706 | 16.7848
12:45 | 5100 | 43.7889 | 202.5192 | 450.0663 | 456.9606 | -16.4646 | -40.0682 | 11.3189 | 8.0466 | 2.242 | 0.7798 | 3.2928 | -0.8485 | 12.0109 | 4.7468 | 0.6205 | 0.6624 | 0.9609 | 0.7473 | -129.3166 | 0.7977 | 5.7169 | 1.7721 | -2.8541 | -1.1508 | 4.5162 |  | 3.7286 | 0.383 | 4.0101 | 3.3665 | 3.3419 | 1.0836 | 10.8099 | 14.2953 | 14.9003 | 11.0926 | 0.0001 | -0.0022 | 0.0008 | 0.0039 | 0.0006 | 0.0001 | 0.0104 | -0.0115 | -0.0032 | -360.1896 | 17.4233 | -360.4573 | 17.6184 | -360.7527 | 18.1009 | -360.7866 | 17.5855 | -352.6167 | 18.7169 | -352.6506 | 16.793
12:45 | 5101 | 43.8275 | 202.4659 | 450.0921 | 457.0195 | -16.4213 | -40.078 | 11.3992 | 8.0513 | 2.2739 | 0.7748 | 3.2923 | -0.8874 | 11.9919 | 4.8401 | 0.6198 | 0.6673 | 0.9657 | 0.7465 | -129.2838 | 0.816 | 5.7825 | 1.8733 | -2.8218 | -1.0103 | 4.5863 |  | 3.6484 | 0.4009 | 4.0096 | 3.3639 | 3.3405 | 1.0836 | 10.7799 | 14.2822 | 14.8794 | 11.0865 | 0.0002 | -0.0029 | 0.0004 | 0.0039 | 0.0007 | -0.0009 | 0.0106 | -0.0005 | -0.0366 | -360.085 | 17.3761 | -360.4358 | 17.643 | -360.8327 | 18.1379 | -360.802 | 17.565 | -352.5644 | 18.6758 | -352.6598 | 16.8238
12:45 | 5102 | 43.7772 | 202.5641 | 450.0232 | 457.0421 | -16.4822 | -40.271 | 11.4102 | 8.068 | 2.3469 | 0.7938 | 3.3791 | -1.0148 | 11.9667 | 4.7923 | 0.62 | 0.6664 | 0.9662 | 0.7482 | -129.2849 | 0.8123 | 5.7121 | 1.9687 | -2.7406 | -1.1196 | 4.5774 |  | 3.6647 | 0.358 | 4.0096 | 3.3648 | 3.3405 | 1.0843 | 10.8065 | 14.2914 | 14.842 | 11.1306 | -0.0001 | -0.0031 | 0.0013 | 0.0039 | 0.0007 | -0.0002 | -0.0056 | -0.004 | -0.0299 | -360.1158 | 17.3658 | -360.3465 | 17.5937 | -360.7497 | 18.1502 | -360.8481 | 17.5999 | -352.6167 | 18.6614 | -352.5613 | 16.795
12:45 | 5103 | 43.7939 | 202.6065 | 450.1488 | 457.0674 | -16.4716 | -40.2013 | 11.3205 | 8.0423 | 2.3578 | 0.8449 | 3.3173 | -0.9616 | 12.018 | 4.9114 | 0.6204 | 0.663 | 0.9632 | 0.7472 | -129.1978 | 0.8206 | 5.6656 | 1.8928 | -2.7313 | -1.0667 | 4.6071 |  | 3.7273 | 0.46 | 4.0111 | 3.3669 | 3.3405 | 1.0848 | 10.7914 | 14.2824 | 14.8458 | 11.0861 | -0.0003 | -0.0025 | 0.0004 | 0.0032 | 0.0014 | 0 | 0.0259 | -0.0072 | -0.0079 | -360.1311 | 17.411 | -360.4512 | 17.6328 | -360.7712 | 18.0988 | -360.7743 | 17.5814 | -352.6106 | 18.7169 | -352.6229 | 16.8156
12:45 | 5104 | 43.8054 | 202.6144 | 450.0672 | 457.0422 | -16.4872 | -40.3219 | 11.2956 | 8.0697 | 2.2813 | 0.8547 | 3.29 | -0.9667 | 12.0773 | 4.9066 | 0.6205 | 0.6599 | 0.9622 | 0.7481 | -129.261 | 0.9014 | 5.6715 | 1.9031 | -2.6881 | -1.0067 | 4.5559 |  | 3.7634 | 0.4011 | 4.0112 | 3.3703 | 3.3429 | 1.0851 | 10.7489 | 14.2386 | 14.7788 | 11.0804 | -0.0007 | -0.0029 | 0.0006 | 0.0039 | 0.0004 | -0.0008 | 0.0166 | -0.0129 | -0.0188 | -360.0696 | 17.372 | -360.4235 | 17.6348 | -360.8112 | 18.1379 | -360.8266 | 17.5629 | -352.5306 | 18.6717 | -352.6229 | 16.8361
12:45 | 5105 | 43.7445 | 202.6837 | 450.1798 | 457.0811 | -16.5124 | -40.2278 | 11.2863 | 8.1318 | 2.3299 | 0.9567 | 3.4176 | -1.0247 | 12.0759 | 4.8469 | 0.619 | 0.6641 | 0.9634 | 0.7461 | -129.2415 | 0.9056 | 5.6923 | 1.9502 | -2.7296 | -1.0416 | 4.6081 |  | 3.6782 | 0.4002 | 4.0109 | 3.3677 | 3.34 | 1.0838 | 10.7833 | 14.2974 | 14.8488 | 11.1013 | 0 | -0.0031 | 0.0008 | 0.0043 | 0.0008 | -0.0004 | 0.0173 | -0.012 | 0.0129 | -360.1619 | 17.374 | -360.3681 | 17.5999 | -360.7466 | 18.1358 | -360.8574 | 17.6081 | -352.6383 | 18.6799 | -352.5644 | 16.7909
12:45 | 5106 | 43.8029 | 202.5602 | 450.042 | 457.0775 | -16.5069 | -40.1935 | 11.3305 | 8.1617 | 2.3951 | 0.7678 | 3.3393 | -0.9615 | 12.0672 | 4.8936 | 0.619 | 0.6614 | 0.9644 | 0.747 | -129.2692 | 0.8876 | 5.7273 | 1.897 | -2.7883 | -1.087 | 4.6213 |  | 3.6825 | 0.4491 | 4.0108 | 3.3654 | 3.339 | 1.0838 | 10.7546 | 14.2853 | 14.8109 | 11.0678 | 0.0001 | -0.0034 | 0.0007 | 0.0039 | 0.0008 | -0.0007 | 0.0103 | -0.005 | -0.0133 | -360.1065 | 17.409 | -360.4573 | 17.6389 | -360.7897 | 18.1071 | -360.765 | 17.5712 | -352.6229 | 18.7148 | -352.6537 | 16.834
12:45 | 5107 | 43.8427 | 202.6695 | 450.1912 | 457.0486 | -16.473 | -40.1553 | 11.3111 | 8.0869 | 2.3369 | 0.7553 | 3.2476 | -0.9926 | 12.0385 | 4.7989 | 0.6202 | 0.6635 | 0.9623 | 0.7469 | -129.2217 | 0.923 | 5.6017 | 1.8813 | -2.8042 | -0.9794 | 4.6355 |  | 3.7035 | 0.4835 | 4.0111 | 3.3662 | 3.3399 | 1.0846 | 10.8019 | 14.2926 | 14.8839 | 11.097 | -0.0001 | -0.0028 | 0.0014 | 0.0046 | 0.0007 | -0.0002 | 0.0193 | -0.004 | -0.0113 | -360.1065 | 17.3679 | -360.4112 | 17.6451 | -360.8143 | 18.1604 | -360.8327 | 17.5671 | -352.586 | 18.6758 | -352.6167 | 16.8381
12:45 | 5108 | 43.8609 | 202.6743 | 450.1435 | 457.0273 | -16.4436 | -40.1575 | 11.3276 | 8.0671 | 2.404 | 0.7659 | 3.4165 | -0.9351 | 12.0679 | 4.9005 | 0.6193 | 0.6614 | 0.9636 | 0.7482 | -129.2798 | 0.8411 | 5.5996 | 1.7459 | -2.8284 | -1.008 | 4.5597 |  | 3.7738 | 0.5429 | 4.0104 | 3.3666 | 3.3405 | 1.0841 | 10.8236 | 14.3212 | 14.8657 | 11.1399 | 0.0001 | -0.0023 | 0.0011 | 0.0041 | 0.0009 | -0.0004 | 0.011 | -0.0137 | -0.0114 | -360.1988 | 17.3966 | -360.4204 | 17.6143 | -360.7404 | 18.1276 | -360.845 | 17.6102 | -352.706 | 18.7004 | -352.6198 | 16.8074
12:45 | 5109 | 43.8765 | 202.6073 | 450.2106 | 457.0339 | -16.3829 | -40.0574 | 11.4306 | 8.0005 | 2.3119 | 0.7657 | 3.3795 | -1.0344 | 12.0168 | 4.8957 | 0.62 | 0.6628 | 0.9631 | 0.7477 | -129.2091 | 0.8703 | 5.679 | 1.7455 | -2.7657 | -0.877 | 4.615 |  | 3.7752 | 0.502 | 4.0109 | 3.3634 | 3.3404 | 1.0837 | 10.8216 | 14.2717 | 14.8855 | 11.1342 | -0.0001 | -0.0029 | 0.0003 | 0.0035 | 0.0004 | -0.0006 | -0.0005 | -0.0081 | -0.0199 | -360.1127 | 17.409 | -360.4727 | 17.6512 | -360.7958 | 18.1132 | -360.8143 | 17.5629 | -352.5983 | 18.7189 | -352.6875 | 16.8464
12:45 | 5110 | 43.905 | 202.6633 | 450.1977 | 457.0079 | -16.4661 | -40.1876 | 11.4004 | 8.0762 | 2.3071 | 0.7279 | 3.3235 | -0.9665 | 12.0401 | 4.911 | 0.6199 | 0.6626 | 0.9639 | 0.747 | -129.266 | 0.8571 | 5.6417 | 1.7709 | -2.7282 | -0.9782 | 4.6752 |  | 3.7028 | 0.5438 | 4.01 | 3.3668 | 3.3381 | 1.0848 | 10.8007 | 14.3033 | 14.8673 | 11.124 | 0 | -0.003 | 0.0006 | 0.0037 | 0.0011 | -0.0007 | 0.0047 | -0.0085 | -0.0039 | -360.1096 | 17.3802 | -360.3835 | 17.6451 | -360.8358 | 18.1769 | -360.8758 | 17.5937 | -352.5921 | 18.6717 | -352.6136 | 16.8381
12:45 | 5111 | 43.9265 | 202.7229 | 450.1417 | 457.0656 | -16.4242 | -40.1811 | 11.4637 | 8.0401 | 2.2575 | 0.7419 | 3.3377 | -0.941 | 12.042 | 4.7851 | 0.6207 | 0.6616 | 0.9641 | 0.746 | -129.2184 | 0.8005 | 5.6207 | 1.8212 | -2.6981 | -0.9713 | 4.6659 |  | 3.7446 | 0.5938 | 4.0108 | 3.3645 | 3.3399 | 1.0838 | 10.8054 | 14.2902 | 14.8753 | 11.1006 | -0.0007 | -0.0031 | 0 | 0.0037 | 0.0006 | -0.0002 | 0.0174 | -0.0142 | -0.0087 | -360.2173 | 17.4274 | -360.4327 | 17.6307 | -360.7989 | 18.1214 | -360.8297 | 17.6102 | -352.6937 | 18.7148 | -352.6506 | 16.8238
12:45 | 5112 | 43.8288 | 202.6252 | 450.127 | 457.0793 | -16.4196 | -40.2563 | 11.4354 | 8.1159 | 2.2476 | 0.8128 | 3.3714 | -0.8804 | 12.0174 | 4.779 | 0.6205 | 0.6642 | 0.9655 | 0.7478 | -129.1762 | 0.7767 | 5.7097 | 1.8559 | -2.7378 | -0.9415 | 4.6465 |  | 3.758 | 0.5633 | 4.0101 | 3.3662 | 3.3374 | 1.0833 | 10.7765 | 14.2899 | 14.8269 | 11.084 | -0.0006 | -0.0026 | 0.0007 | 0.0038 | 0.001 | -0.0006 | 0.0284 | -0.0053 | -0.004 | -360.1773 | 17.4172 | -360.4881 | 17.6718 | -360.8604 | 18.1358 | -360.7989 | 17.5835 | -352.6475 | 18.7251 | -352.6906 | 16.8648
12:45 | 5113 | 43.8779 | 202.6492 | 450.1459 | 457.0697 | -16.3923 | -40.1766 | 11.4182 | 8.092 | 2.2947 | 0.9423 | 3.3951 | -0.9098 | 12.0341 | 4.8814 | 0.6217 | 0.6647 | 0.9623 | 0.7485 | -129.1972 | 0.7452 | 5.7176 | 1.7983 | -2.7263 | -1.022 | 4.6142 |  | 3.715 | 0.5775 | 4.0116 | 3.3651 | 3.3376 | 1.0839 | 10.7614 | 14.2463 | 14.8202 | 11.0739 | 0.0001 | -0.0031 | 0.0013 | 0.0042 | 0.0007 | -0.0003 | 0.0058 | -0.01 | 0.0036 | -360.2019 | 17.3843 | -360.4173 | 17.6348 | -360.8235 | 18.1728 | -360.9189 | 17.6225 | -352.666 | 18.6902 | -352.6352 | 16.8176
12:45 | 5114 | 43.8743 | 202.6248 | 450.1178 | 457.0885 | -16.4203 | -40.1374 | 11.358 | 8.0784 | 2.4287 | 0.9091 | 3.3805 | -0.9519 | 12.0881 | 4.792 | 0.6193 | 0.6622 | 0.9605 | 0.747 | -129.3007 | 0.8134 | 5.5759 | 1.6337 | -2.7233 | -0.9617 | 4.6199 |  | 3.8009 | 0.5223 | 4.0105 | 3.367 | 3.3384 | 1.0839 | 10.8111 | 14.3079 | 14.8717 | 11.0998 | 0.0004 | -0.0028 | 0.0008 | 0.004 | 0.0007 | -0.0007 | 0.017 | -0.0032 | -0.0079 | -360.2512 | 17.4459 | -360.4973 | 17.6492 | -360.8081 | 18.1214 | -360.8266 | 17.6143 | -352.6998 | 18.7292 | -352.6752 | 16.8258
12:45 | 5115 | 43.8596 | 202.6289 | 450.1388 | 457.0946 | -16.4461 | -40.2256 | 11.4421 | 8.0289 | 2.3265 | 1.0128 | 3.428 | -0.9902 | 12.0944 | 4.9356 | 0.6201 | 0.6611 | 0.9629 | 0.7467 | -129.3186 | 0.8272 | 5.6497 | 1.6865 | -2.6553 | -0.9964 | 4.6397 |  | 3.8121 | 0.4887 | 4.0114 | 3.3641 | 3.338 | 1.0829 | 10.7695 | 14.2603 | 14.8287 | 11.0991 | 0.0001 | -0.0026 | 0.0008 | 0.0039 | 0.0011 | 0.0001 | 0.0106 | -0.0205 | -0.0229 | -360.1619 | 17.409 | -360.485 | 17.682 | -360.8912 | 18.1522 | -360.8297 | 17.5917 | -352.6136 | 18.7045 | -352.6844 | 16.8689
12:45 | 5116 | 43.8217 | 202.6849 | 450.0652 | 456.9927 | -16.4818 | -40.2232 | 11.4202 | 7.9402 | 2.3548 | 0.7584 | 3.4015 | -1.0058 | 12.0746 | 4.8379 | 0.6196 | 0.6604 | 0.9623 | 0.7466 | -129.1993 | 1.0081 | 5.6847 | 1.7212 | -2.6245 | -0.9416 | 4.663 |  | 3.7942 | 0.4726 | 4.0107 | 3.3648 | 3.3406 | 1.0839 | 10.8283 | 14.3316 | 14.8933 | 11.1561 | -0.0001 | -0.0024 | 0.0012 | 0.0042 | 0.0011 | -0.0003 | 0.0229 | -0.0054 | -0.0125 | -360.1588 | 17.3987 | -360.3927 | 17.6328 | -360.7989 | 18.1645 | -360.882 | 17.6307 | -352.6444 | 18.6881 | -352.6044 | 16.8238
12:45 | 5117 | 43.9291 | 202.6398 | 450.1465 | 456.9795 | -16.4703 | -40.1696 | 11.411 | 7.9972 | 2.2939 | 0.795 | 3.3588 | -1.0074 | 11.9895 | 4.8704 | 0.6191 | 0.657 | 0.9627 | 0.7474 | -129.1989 | 0.8189 | 5.6125 | 1.7435 | -2.7294 | -0.9644 | 4.7076 |  | 3.7504 | 0.4288 | 4.0112 | 3.3659 | 3.3418 | 1.0847 | 10.8099 | 14.324 | 14.9166 | 11.1334 | 0.0004 | -0.0024 | 0.0006 | 0.0034 | 0.0005 | -0.0004 | 0.0188 | -0.0135 | -0.0095 | -360.2111 | 17.4521 | -360.5004 | 17.6615 | -360.8266 | 18.1235 | -360.8266 | 17.6081 | -352.6844 | 18.7497 | -352.7152 | 16.8484
12:45 | 5118 | 43.8618 | 202.6493 | 450.0524 | 456.9972 | -16.4792 | -40.2016 | 11.379 | 8.031 | 2.2321 | 0.8135 | 3.3202 | -0.9782 | 11.9663 | 4.8353 | 0.6206 | 0.6639 | 0.9614 | 0.7458 | -129.2187 | 0.9069 | 5.6441 | 1.5798 | -2.7234 | -1.0862 | 4.6016 |  | 3.7819 | 0.5081 | 4.0107 | 3.3641 | 3.3387 | 1.0829 | 10.8018 | 14.2638 | 14.8734 | 11.0908 | 0.0003 | -0.003 | 0.001 | 0.0044 | 0.0007 | -0.0001 | 0.0081 | -0.0108 | -0.0086 | -360.1034 | 17.3987 | -360.4758 | 17.6615 | -360.8727 | 18.1666 | -360.8481 | 17.5978 | -352.629 | 18.6902 | -352.6567 | 16.8525
12:45 | 5119 | 43.8516 | 202.6687 | 450.1556 | 457.113 | -16.4856 | -40.154 | 11.4524 | 8.0106 | 2.3108 | 0.8774 | 3.4624 | -0.966 | 11.9599 | 4.7992 | 0.6216 | 0.6616 | 0.9622 | 0.7475 | -129.2166 | 0.9783 | 5.6112 | 1.5894 | -2.7234 | -1.0998 | 4.6295 |  | 3.7772 | 0.5606 | 4.0102 | 3.3662 | 3.3418 | 1.0845 | 10.7821 | 14.279 | 14.8659 | 11.0941 | 0.0004 | -0.0024 | 0.0008 | 0.0041 | 0.0009 | -0.0008 | 0.0158 | 0.0024 | -0.0074 | -360.2235 | 17.4192 | -360.4358 | 17.6307 | -360.7773 | 18.1645 | -360.8881 | 17.6369 | -352.706 | 18.7128 | -352.6075 | 16.8197
12:45 | 5120 | 43.9142 | 202.5632 | 450.2267 | 457.071 | -16.5983 | -40.2153 | 11.3397 | 8.0812 | 2.2965 | 0.9592 | 3.3485 | -1.0549 | 11.9653 | 4.8011 | 0.6203 | 0.664 | 0.9639 | 0.7478 | -129.2166 | 0.8904 | 5.6605 | 1.6778 | -2.7327 | -1.1239 | 4.677 |  | 3.7513 | 0.6951 | 4.0111 | 3.367 | 3.3401 | 1.0839 | 10.7696 | 14.2773 | 14.8382 | 11.071 | -0.0005 | -0.0027 | 0.0007 | 0.0038 | 0.0003 | -0.0005 | 0.0079 | 0.0063 | -0.0092 | -360.1804 | 17.4356 | -360.5096 | 17.6738 | -360.8481 | 18.1276 | -360.8081 | 17.5794 | -352.6537 | 18.7292 | -352.7121 | 16.8587
12:45 | 5121 | 43.956 | 202.6328 | 450.1295 | 457.0878 | -16.5271 | -40.1674 | 11.3609 | 8.0355 | 2.277 | 0.9156 | 3.3472 | -0.9766 | 11.9595 | 4.8957 | 0.6201 | 0.6619 | 0.9634 | 0.7492 | -129.2291 | 0.902 | 5.6717 | 1.7575 | -2.6918 | -1.0761 | 4.7363 |  | 3.7331 | 0.5923 | 4.0107 | 3.3656 | 3.3362 | 1.0841 | 10.7776 | 14.2335 | 14.8525 | 11.0905 | -0.0003 | -0.003 | 0.0011 | 0.0042 | 0.0011 | -0.0012 | 0.0132 | -0.014 | -0.0034 | -360.1988 | 17.4069 | -360.4235 | 17.6615 | -360.8666 | 18.1769 | -360.885 | 17.6143 | -352.6136 | 18.6984 | -352.6537 | 16.8464
12:45 | 5122 | 43.8968 | 202.5704 | 450.1513 | 457.01 | -16.4232 | -40.1391 | 11.3573 | 8.1123 | 2.3077 | 0.8267 | 3.3943 | -0.9882 | 11.9575 | 4.9057 | 0.6203 | 0.6649 | 0.9625 | 0.7475 | -129.2468 | 0.868 | 5.6283 | 1.7629 | -2.6624 | -0.983 | 4.7203 |  | 3.8037 | 0.5804 | 4.0112 | 3.362 | 3.34 | 1.0836 | 10.7845 | 14.2349 | 14.8386 | 11.0793 | 0.0008 | -0.0025 | 0.001 | 0.0042 | 0.0009 | -0.0001 | 0.008 | -0.0032 | -0.012 | -360.2481 | 17.4315 | -360.4635 | 17.6369 | -360.7743 | 18.144 | -360.845 | 17.6204 | -352.6998 | 18.7353 | -352.6629 | 16.8258
12:45 | 5123 | 43.8504 | 202.5858 | 450.1122 | 457.0221 | -16.3263 | -39.9979 | 11.4491 | 8.1829 | 2.3609 | 0.8396 | 3.3548 | -0.9476 | 11.8758 | 4.8262 | 0.6205 | 0.6627 | 0.9625 | 0.748 | -129.2756 | 0.9492 | 5.5893 | 1.8193 | -2.7144 | -1.0566 | 4.6849 |  | 3.7919 | 0.6096 | 4.0109 | 3.3632 | 3.3405 | 1.0857 | 10.7891 | 14.2858 | 14.8025 | 11.1129 | -0.0001 | -0.0031 | 0.0007 | 0.004 | 0.0012 | -0.0003 | 0.0122 | -0.0168 | 0.0065 | -360.1588 | 17.4315 | -360.5343 | 17.68 | -360.8481 | 18.1502 | -360.8358 | 17.5937 | -352.6444 | 18.7169 | -352.7029 | 16.8587
12:45 | 5124 | 43.8391 | 202.6336 | 450.1391 | 457.0438 | -16.388 | -40.0268 | 11.5405 | 8.1182 | 2.3371 | 0.8859 | 3.5002 | -0.9759 | 11.911 | 4.8156 | 0.6197 | 0.664 | 0.9624 | 0.7463 | -129.3335 | 0.8394 | 5.5849 | 1.8228 | -2.6584 | -1.2411 | 4.6781 |  | 3.8402 | 0.6862 | 4.0114 | 3.3637 | 3.3419 | 1.0838 | 10.8249 | 14.2987 | 14.8744 | 11.1193 | -0.0003 | -0.0028 | 0.0013 | 0.004 | 0.0009 | -0.0004 | 0.0119 | -0.0014 | -0.0138 | -360.1958 | 17.3884 | -360.4142 | 17.641 | -360.8266 | 18.1707 | -360.8974 | 17.6245 | -352.6567 | 18.6984 | -352.626 | 16.8279
12:45 | 5125 | 43.9239 | 202.6547 | 450.0107 | 457.0078 | -16.2961 | -40.0092 | 11.519 | 8.0931 | 2.2844 | 0.8014 | 3.479 | -0.9912 | 11.9876 | 4.777 | 0.62 | 0.6613 | 0.9605 | 0.747 | -129.4 | 0.8381 | 5.6372 | 1.803 | -2.7045 | -1.0868 | 4.6245 |  | 3.8134 | 0.5833 | 4.0087 | 3.3626 | 3.3356 | 1.0848 | 10.7961 | 14.2984 | 14.8897 | 11.1085 | -0.0003 | -0.0027 | 0.0006 | 0.0036 | 0.0012 | -0.0003 | 0.022 | -0.0049 | 0.0019 | -360.2819 | 17.4521 | -360.4758 | 17.6471 | -360.8235 | 18.1337 | -360.7989 | 17.6225 | -352.6752 | 18.7477 | -352.6998 | 16.8402
12:45 | 5126 | 43.8739 | 202.5912 | 449.9931 | 456.9497 | -16.3089 | -39.9799 | 11.4747 | 8.0623 | 2.3706 | 0.8869 | 3.5557 | -1.0092 | 11.9538 | 4.7752 | 0.6197 | 0.6618 | 0.9628 | 0.747 | -129.2417 | 0.8089 | 5.6412 | 1.7642 | -2.7101 | -0.9896 | 4.6598 |  | 3.7784 | 0.5453 | 4.0108 | 3.3635 | 3.3408 | 1.0855 | 10.7973 | 14.2705 | 14.8726 | 11.1158 | -0.0002 | -0.0031 | 0.0005 | 0.0039 | 0.0007 | -0.0005 | 0.0138 | -0.0034 | -0.0223 | -360.1496 | 17.3946 | -360.4573 | 17.6677 | -360.8543 | 18.1666 | -360.8666 | 17.5978 | -352.6075 | 18.7066 | -352.6598 | 16.8505
12:45 | 5127 | 43.9277 | 202.5833 | 449.9861 | 457.0261 | -16.361 | -39.9301 | 11.5679 | 8.0554 | 2.3321 | 0.9453 | 3.5336 | -0.9563 | 11.9548 | 4.8321 | 0.6186 | 0.6639 | 0.9671 | 0.7464 | -129.2769 | 0.8051 | 5.5889 | 1.6763 | -2.6842 | -1.0425 | 4.595 |  | 3.8144 | 0.5007 | 4.0106 | 3.3641 | 3.3397 | 1.0844 | 10.7696 | 14.3005 | 14.8497 | 11.1057 | -0.0001 | -0.0031 | 0.0006 | 0.0037 | 0.0007 | -0.0009 | 0.0015 | -0.0139 | -0.0229 | -360.2081 | 17.4131 | -360.4296 | 17.6225 | -360.7989 | 18.1563 | -360.8943 | 17.6369 | -352.6783 | 18.7169 | -352.6537 | 16.8156
12:45 | 5128 | 43.8387 | 202.6516 | 450.0322 | 457.0151 | -16.3382 | -39.9496 | 11.5102 | 8.0442 | 2.3671 | 0.8096 | 3.5566 | -0.9514 | 11.9347 | 4.7761 | 0.6187 | 0.6634 | 0.9656 | 0.7459 | -129.2926 | 0.8962 | 5.664 | 1.7053 | -2.6877 | -1.0215 | 4.5773 |  | 3.7841 | 0.5703 | 4.0105 | 3.3663 | 3.3416 | 1.0849 | 10.7962 | 14.2751 | 14.8075 | 11.1089 | -0.0006 | -0.003 | 0.0008 | 0.0037 | 0.0009 | -0.0007 | 0.0132 | -0.008 | -0.0039 | -360.1958 | 17.4192 | -360.485 | 17.6553 | -360.8358 | 18.142 | -360.8081 | 17.5917 | -352.6783 | 18.7292 | -352.6844 | 16.8484
12:45 | 5129 | 43.8581 | 202.6157 | 450.0062 | 457.1354 | -16.3104 | -39.8208 | 11.5499 | 8.0264 | 2.3526 | 0.7454 | 3.514 | -1.0247 | 11.8621 | 4.8295 | 0.6181 | 0.6623 | 0.9652 | 0.7445 | -129.1957 | 0.9617 | 5.7095 | 1.8322 | -2.7071 | -0.9904 | 4.6466 |  | 3.8026 | 0.6396 | 4.0086 | 3.3624 | 3.3383 | 1.0848 | 10.7798 | 14.2882 | 14.8689 | 11.1035 | -0.0001 | -0.0025 | 0.0011 | 0.0044 | 0.0007 | -0.0008 | 0.0274 | -0.019 | 0.0019 | -360.1804 | 17.3864 | -360.4204 | 17.6307 | -360.8512 | 18.1728 | -360.8758 | 17.604 | -352.6321 | 18.6963 | -352.6352 | 16.8402
12:45 | 5130 | 43.9135 | 202.5731 | 450.0152 | 456.9949 | -16.3676 | -39.8482 | 11.5161 | 8.0661 | 2.3378 | 0.7763 | 3.549 | -0.9333 | 11.9393 | 4.8041 | 0.6194 | 0.662 | 0.9631 | 0.7459 | -129.1815 | 0.8728 | 5.6388 | 1.8406 | -2.6845 | -1.0922 | 4.6418 |  | 3.7727 | 0.6193 | 4.0104 | 3.3636 | 3.3417 | 1.0852 | 10.7972 | 14.2766 | 14.8458 | 11.1035 | 0 | -0.0034 | 0.0006 | 0.0036 | 0.001 | -0.0006 | 0.0229 | -0.0141 | 0.0025 | -360.2019 | 17.4213 | -360.4389 | 17.6122 | -360.7927 | 18.1337 | -360.845 | 17.6143 | -352.706 | 18.7374 | -352.6475 | 16.8238
12:45 | 5131 | 43.9405 | 202.635 | 450.0895 | 456.9879 | -16.3921 | -39.8183 | 11.4792 | 8.0076 | 2.3649 | 0.7757 | 3.4831 | -0.9868 | 11.9173 | 4.7429 | 0.619 | 0.6614 | 0.9619 | 0.7458 | -129.244 | 0.9341 | 5.6082 | 1.8211 | -2.6682 | -0.9532 | 4.6218 |  | 3.8053 | 0.5771 | 4.0113 | 3.3652 | 3.3392 | 1.0845 | 10.7683 | 14.2707 | 14.8447 | 11.0576 | 0.0002 | -0.0031 | 0.0012 | 0.0039 | 0.0008 | -0.0002 | 0.0116 | -0.0109 | 0.0131 | -360.1527 | 17.3966 | -360.4542 | 17.6492 | -360.842 | 18.1337 | -360.8204 | 17.5896 | -352.589 | 18.7087 | -352.6721 | 16.8443
12:45 | 5132 | 43.948 | 202.6131 | 450.0526 | 457.0146 | -16.3211 | -39.9005 | 11.4821 | 8.0286 | 2.3365 | 0.8154 | 3.4734 | -0.8687 | 12.037 | 4.818 | 0.62 | 0.6622 | 0.9674 | 0.7463 | -129.1703 | 0.8917 | 5.6908 | 1.8422 | -2.7067 | -1.0367 | 4.6352 |  | 3.8074 | 0.5704 | 4.0117 | 3.3618 | 3.3394 | 1.0835 | 10.7937 | 14.2848 | 14.8659 | 11.1345 | -0.0003 | -0.003 | 0.0006 | 0.0035 | 0.0012 | -0.0008 | 0.0046 | -0.0152 | -0.0226 | -360.1865 | 17.3946 | -360.4389 | 17.6143 | -360.7835 | 18.1481 | -360.8727 | 17.6122 | -352.6383 | 18.684 | -352.6044 | 16.8197
12:45 | 5133 | 43.9079 | 202.6557 | 450.1276 | 457.0956 | -16.3756 | -39.9003 | 11.4255 | 8.1004 | 2.4145 | 0.8148 | 3.5537 | -0.9968 | 11.9806 | 4.7616 | 0.6209 | 0.6611 | 0.9638 | 0.7465 | -129.2565 | 0.897 | 5.6709 | 1.8103 | -2.6902 | -1.0269 | 4.636 |  | 3.7533 | 0.4787 | 4.012 | 3.3644 | 3.3423 | 1.0838 | 10.8076 | 14.2812 | 14.8502 | 11.1139 | -0.0004 | -0.0028 | 0.0007 | 0.0035 | 0.0007 | 0 | 0.0051 | 0.0023 | -0.0064 | -360.1342 | 17.409 | -360.4542 | 17.643 | -360.7958 | 18.1235 | -360.8204 | 17.5835 | -352.666 | 18.7251 | -352.6844 | 16.8402
12:45 | 5134 | 43.8512 | 202.5986 | 450.0824 | 456.9054 | -16.2593 | -39.8255 | 11.431 | 8.0981 | 2.4104 | 0.8376 | 3.5528 | -1.0073 | 11.9886 | 4.7491 | 0.62 | 0.6648 | 0.9629 | 0.7466 | -129.2606 | 0.8624 | 5.7051 | 1.833 | -2.6697 | -1.0248 | 4.6816 |  | 3.7483 | 0.5539 | 4.0115 | 3.3655 | 3.3409 | 1.084 | 10.7903 | 14.287 | 14.8502 | 11.1024 | 0.0001 | -0.0029 | 0.0009 | 0.0042 | 0.0009 | -0.0008 | 0.0181 | -0.003 | 0.0018 | -360.1435 | 17.3699 | -360.4142 | 17.6266 | -360.8174 | 18.1584 | -360.8512 | 17.5876 | -352.6075 | 18.6861 | -352.629 | 16.832
12:45 | 5135 | 43.8726 | 202.5682 | 450.0025 | 456.9768 | -16.2749 | -39.8602 | 11.4526 | 8.0698 | 2.3614 | 0.754 | 3.5232 | -0.9911 | 12.0084 | 4.856 | 0.6204 | 0.6615 | 0.9633 | 0.7449 | -129.1781 | 0.8823 | 5.7204 | 2.0126 | -2.6217 | -0.8859 | 4.6557 |  | 3.816 | 0.3704 | 4.013 | 3.3645 | 3.3406 | 1.0825 | 10.7961 | 14.2695 | 14.8491 | 11.1143 | 0.0003 | -0.0029 | 0.0007 | 0.004 | 0.0007 | -0.0002 | 0.0083 | 0 | -0.0048 | -360.1496 | 17.4213 | -360.4204 | 17.6102 | -360.7743 | 18.1214 | -360.8081 | 17.6061 | -352.6598 | 18.7128 | -352.6598 | 16.8217
12:45 | 5136 | 43.8232 | 202.6182 | 450.0211 | 456.9505 | -16.257 | -39.8576 | 11.5574 | 8.0894 | 2.4046 | 0.6642 | 3.5007 | -0.9872 | 12.0277 | 4.894 | 0.6201 | 0.6598 | 0.9651 | 0.7451 | -129.1766 | 0.8729 | 5.6403 | 2.0233 | -2.5709 | -0.9994 | 4.6576 |  | 3.7858 | 0.3535 | 4.0114 | 3.3649 | 3.3415 | 1.0842 | 10.7717 | 14.2861 | 14.8162 | 11.0774 | 0.0001 | -0.0024 | 0.0006 | 0.0035 | 0.0012 | -0.0006 | 0.0128 | -0.0201 | 0.0116 | -360.1065 | 17.3987 | -360.4296 | 17.6328 | -360.845 | 18.1522 | -360.8174 | 17.5835 | -352.6013 | 18.6963 | -352.6721 | 16.8402
12:45 | 5137 | 43.9409 | 202.6169 | 450.0859 | 456.9727 | -16.2971 | -39.9645 | 11.454 | 7.9919 | 2.3817 | 0.6725 | 3.4933 | -1.0131 | 12.0775 | 4.9414 | 0.6194 | 0.6635 | 0.9642 | 0.7455 | -129.1944 | 0.9283 | 5.6151 | 1.9497 | -2.6505 | -0.948 | 4.6568 |  | 3.8044 | 0.3372 | 4.0101 | 3.3639 | 3.3397 | 1.0833 | 10.7615 | 14.275 | 14.8412 | 11.0862 | -0.0003 | -0.0029 | 0.0007 | 0.0035 | 0.0003 | -0.001 | 0.0044 | -0.0073 | 0.0015 | -360.165 | 17.4028 | -360.4142 | 17.5978 | -360.7866 | 18.1461 | -360.8358 | 17.602 | -352.6198 | 18.7045 | -352.626 | 16.8094
12:45 | 5138 | 43.9716 | 202.6186 | 450.011 | 456.963 | -16.4006 | -39.8563 | 11.5129 | 8.0424 | 2.3976 | 0.7057 | 3.5016 | -1.0313 | 12.0148 | 4.9406 | 0.6206 | 0.6625 | 0.9606 | 0.7448 | -129.1973 | 0.8525 | 5.6878 | 2.045 | -2.6132 | -0.8895 | 4.7389 |  | 3.723 | 0.3078 | 4.0118 | 3.3649 | 3.343 | 1.0845 | 10.7764 | 14.2962 | 14.8301 | 11.0944 | -0.0002 | -0.0031 | 0.0005 | 0.0033 | 0.0008 | -0.0006 | 0.0202 | -0.0084 | -0.0134 | -360.1711 | 17.411 | -360.445 | 17.6245 | -360.7835 | 18.1399 | -360.7989 | 17.5876 | -352.6136 | 18.721 | -352.6937 | 16.8299
12:45 | 5139 | 43.9316 | 202.6619 | 449.8782 | 456.8587 | -16.5028 | -39.9688 | 11.4798 | 8.0227 | 2.3895 | 0.6983 | 3.4245 | -1.0258 | 11.9082 | 4.8242 | 0.6196 | 0.6626 | 0.9631 | 0.7455 | -129.1073 | 0.8907 | 5.6824 | 2.0677 | -2.6078 | -0.9018 | 4.7216 |  | 3.7767 | 0.3817 | 4.0118 | 3.3613 | 3.3395 | 1.0842 | 10.7684 | 14.2763 | 14.8436 | 11.0753 | 0.0002 | -0.0027 | 0.0006 | 0.0041 | 0.0006 | -0.0004 | 0.0091 | 0.0013 | -0.0285 | -360.1435 | 17.3782 | -360.3927 | 17.6081 | -360.7866 | 18.1399 | -360.8143 | 17.5896 | -352.5829 | 18.6861 | -352.6537 | 16.8217
12:45 | 5140 | 43.9712 | 202.5651 | 450.016 | 456.8532 | -16.4943 | -39.9161 | 11.4196 | 8.0555 | 2.4717 | 0.8273 | 3.4501 | -1.0156 | 11.9802 | 4.8525 | 0.6181 | 0.665 | 0.9619 | 0.7458 | -129.1512 | 0.9161 | 5.6635 | 2.0072 | -2.6214 | -0.9547 | 4.6946 |  | 3.8222 | 0.4045 | 4.0106 | 3.3648 | 3.3397 | 1.0844 | 10.7742 | 14.2819 | 14.8426 | 11.0988 | -0.0003 | -0.0029 | 0.0011 | 0.0039 | 0.001 | -0.0002 | 0.0132 | -0.0176 | -0.0171 | -360.1619 | 17.3864 | -360.4142 | 17.604 | -360.7835 | 18.1399 | -360.8204 | 17.5876 | -352.626 | 18.6963 | -352.6229 | 16.8156
12:45 | 5141 | 43.977 | 202.6701 | 449.9902 | 456.9473 | -16.5065 | -39.9051 | 11.4946 | 8.0241 | 2.4202 | 0.7535 | 3.438 | -0.9749 | 12.0326 | 5.0001 | 0.6181 | 0.6649 | 0.963 | 0.7466 | -129.1405 | 0.9859 | 5.7856 | 1.8551 | -2.5491 | -0.953 | 4.7097 |  | 3.8433 | 0.4356 | 4.0118 | 3.3659 | 3.3382 | 1.0845 | 10.7647 | 14.2849 | 14.8612 | 11.0821 | 0.0002 | -0.0022 | 0.0011 | 0.0039 | 0.001 | -0.0003 | 0.007 | -0.0141 | 0.0181 | -360.125 | 17.3782 | -360.4112 | 17.602 | -360.762 | 18.1543 | -360.7958 | 17.5671 | -352.5583 | 18.6799 | -352.6229 | 16.8156
12:45 | 5142 | 44.0743 | 202.6797 | 449.9833 | 457.0006 | -16.4914 | -40.101 | 11.4329 | 8.029 | 2.361 | 0.7007 | 3.3949 | -1.0454 | 12.0264 | 5.0501 | 0.62 | 0.6637 | 0.9658 | 0.746 | -129.1628 | 0.9154 | 5.6297 | 1.9646 | -2.4666 | -0.8503 | 4.6778 |  | 3.9159 | 0.4153 | 4.0129 | 3.3663 | 3.338 | 1.084 | 10.8111 | 14.3021 | 14.8775 | 11.1403 | 0.0003 | -0.0027 | 0.0008 | 0.0044 | 0.0005 | -0.0003 | 0.0104 | 0.0019 | 0.011 | -360.1711 | 17.3925 | -360.4266 | 17.5978 | -360.7712 | 18.1502 | -360.8174 | 17.5629 | -352.5644 | 18.6963 | -352.6013 | 16.8094
12:45 | 5143 | 44.0505 | 202.6699 | 449.9238 | 456.9579 | -16.463 | -40.0446 | 11.4272 | 8.0602 | 2.4453 | 0.7521 | 3.426 | -1.0587 | 12.0523 | 4.926 | 0.6217 | 0.6635 | 0.9642 | 0.7464 | -129.1475 | 0.8492 | 5.613 | 2.0523 | -2.5378 | -0.9181 | 4.7342 |  | 3.8493 | 0.4364 | 4.0116 | 3.3613 | 3.341 | 1.0842 | 10.7637 | 14.2775 | 14.845 | 11.1111 | 0.0002 | -0.0027 | 0.0005 | 0.0041 | 0.0011 | -0.0007 | 0.0221 | -0.0072 | -0.0196 | -360.1619 | 17.3925 | -360.4142 | 17.604 | -360.7773 | 18.144 | -360.7897 | 17.5773 | -352.5952 | 18.6984 | -352.6044 | 16.8053
12:45 | 5144 | 44.0416 | 202.7114 | 449.9991 | 456.947 | -16.5032 | -40.0109 | 11.3935 | 8.094 | 2.4098 | 0.7019 | 3.4345 | -0.9738 | 12.0116 | 4.9752 | 0.6208 | 0.6622 | 0.9616 | 0.7453 | -129.1548 | 0.9445 | 5.6573 | 2.0595 | -2.5851 | -0.9558 | 4.72 |  | 3.8654 | 0.4385 | 4.0114 | 3.3623 | 3.338 | 1.0859 | 10.8319 | 14.3113 | 14.8458 | 11.1323 | -0.0002 | -0.0027 | 0.0008 | 0.0038 | 0 | -0.0008 | 0.0256 | -0.0077 | 0.0106 | -360.1435 | 17.4007 | -360.4573 | 17.6163 | -360.7958 | 18.1502 | -360.7743 | 17.565 | -352.6075 | 18.6984 | -352.6506 | 16.8238
12:45 | 5145 | 44.0122 | 202.6716 | 449.9807 | 456.8533 | -16.4229 | -39.9146 | 11.4284 | 8.1246 | 2.3825 | 0.7491 | 3.4366 | -1.1054 | 12.0292 | 4.9032 | 0.6209 | 0.6613 | 0.9644 | 0.7464 | -129.1751 | 0.9346 | 5.6043 | 1.9635 | -2.6746 | -1.1281 | 4.6877 |  | 3.8496 | 0.4306 | 4.0112 | 3.3623 | 3.3403 | 1.0848 | 10.7939 | 14.2959 | 14.8511 | 11.1125 | -0.0007 | -0.0025 | 0.0008 | 0.0041 | 0.0008 | -0.0004 | 0.0142 | -0.0158 | 0.0026 | -360.1558 | 17.3761 | -360.3989 | 17.6163 | -360.7927 | 18.1625 | -360.8174 | 17.5691 | -352.586 | 18.6902 | -352.5952 | 16.8074
12:45 | 5146 | 43.9988 | 202.676 | 449.9958 | 456.8686 | -16.5014 | -40.0003 | 11.5288 | 8.0915 | 2.3982 | 0.7741 | 3.4686 | -0.977 | 12.0676 | 4.8793 | 0.62 | 0.661 | 0.9611 | 0.7464 | -129.1503 | 0.8132 | 5.5745 | 1.8456 | -2.6164 | -0.9601 | 4.6998 |  | 3.8953 | 0.5609 | 4.0103 | 3.366 | 3.3411 | 1.0846 | 10.7637 | 14.2718 | 14.8403 | 11.0934 | 0.0002 | -0.0027 | 0.0011 | 0.0038 | 0.0007 | -0.0004 | 0.0121 | 0.0012 | -0.0055 | -360.2019 | 17.4233 | -360.4358 | 17.604 | -360.7835 | 18.1461 | -360.805 | 17.5876 | -352.6567 | 18.7107 | -352.629 | 16.8053
12:45 | 5147 | 44.0432 | 202.6625 | 450.1465 | 456.9611 | -16.4017 | -39.9283 | 11.5392 | 8.1456 | 2.4181 | 0.7102 | 3.433 | -0.9779 | 11.9438 | 4.9344 | 0.62 | 0.66 | 0.9617 | 0.746 | -129.269 | 0.7553 | 5.5674 | 1.8728 | -2.5304 | -0.9724 | 4.6776 |  | 3.8396 | 0.6189 | 4.0128 | 3.3653 | 3.3432 | 1.0864 | 10.7939 | 14.2726 | 14.8095 | 11.0898 | 0.0001 | -0.0035 | 0.0009 | 0.0039 | 0.001 | -0.0007 | 0.0145 | -0.0148 | -0.003 | -360.0881 | 17.3884 | -360.4512 | 17.6451 | -360.8266 | 18.1543 | -360.8174 | 17.5527 | -352.5675 | 18.7107 | -352.6444 | 16.834
12:46 | 5148 | 44.0596 | 202.6767 | 450.0329 | 456.9827 | -16.4812 | -40.0003 | 11.4496 | 8.0613 | 2.3554 | 0.7426 | 3.3911 | -1.0953 | 12.031 | 4.9881 | 0.6203 | 0.6606 | 0.9648 | 0.7457 | -129.2512 | 0.7598 | 5.6781 | 2.1279 | -2.4933 | -1.0553 | 4.756 |  | 3.7344 | 0.4819 | 4.0098 | 3.3624 | 3.3387 | 1.0851 | 10.7939 | 14.2727 | 14.8569 | 11.1125 | 0 | -0.0029 | 0.0006 | 0.0038 | 0.0006 | 0.0001 | 0.0059 | -0.0067 | -0.0093 | -360.2204 | 17.411 | -360.4542 | 17.6204 | -360.7927 | 18.1522 | -360.845 | 17.6102 | -352.6383 | 18.7169 | -352.6075 | 16.7991
12:46 | 5149 | 43.9777 | 202.5971 | 449.9952 | 456.9918 | -16.5084 | -40.0318 | 11.4754 | 8.0606 | 2.3705 | 0.6939 | 3.3874 | -1.0674 | 12.0244 | 4.9206 | 0.6201 | 0.6601 | 0.9632 | 0.7453 | -129.2304 | 0.881 | 5.6304 | 2.1294 | -2.5134 | -0.9873 | 4.7224 |  | 3.8432 | 0.5351 | 4.0118 | 3.362 | 3.3416 | 1.0841 | 10.781 | 14.2718 | 14.8519 | 11.1049 | -0.0004 | -0.0029 | 0.0008 | 0.0042 | 0.0011 | -0.0007 | 0.0081 | -0.0045 | -0.0147 | -360.1711 | 17.4254 | -360.4696 | 17.6389 | -360.8358 | 18.1461 | -360.7743 | 17.5712 | -352.6321 | 18.7395 | -352.666 | 16.8299
12:46 | 5150 | 43.9952 | 202.5352 | 450.0241 | 456.9971 | -16.511 | -40.0691 | 11.4745 | 8.0768 | 2.4066 | 0.7935 | 3.3973 | -1.012 | 11.999 | 4.8856 | 0.6196 | 0.6595 | 0.9662 | 0.7452 | -129.1782 | 0.7889 | 5.7057 | 2.0499 | -2.5419 | -0.9613 | 4.6938 |  | 3.8589 | 0.5659 | 4.0115 | 3.3635 | 3.3426 | 1.085 | 10.8238 | 14.2975 | 14.8673 | 11.0951 | 0.0001 | -0.0031 | 0.0013 | 0.0045 | 0.0008 | -0.0002 | 0.0101 | 0.0054 | -0.0226 | -360.1496 | 17.3864 | -360.4296 | 17.6369 | -360.8174 | 18.1933 | -360.8789 | 17.5814 | -352.5767 | 18.6963 | -352.5921 | 16.8176
12:46 | 5151 | 44.0115 | 202.6568 | 450.0582 | 457.1401 | -16.4792 | -39.9689 | 11.4662 | 8.0854 | 2.3448 | 0.8239 | 3.4155 | -0.9405 | 12.0068 | 4.8273 | 0.6203 | 0.6616 | 0.9622 | 0.7453 | -129.1682 | 0.8852 | 5.6634 | 1.9829 | -2.5755 | -0.9037 | 4.7114 |  | 3.8538 | 0.5394 | 4.0112 | 3.3653 | 3.3432 | 1.0866 | 10.7972 | 14.2997 | 14.8631 | 11.1266 | 0.0003 | -0.0032 | 0.0006 | 0.0038 | 0.0011 | -0.0003 | 0.0138 | -0.0088 | -0.0115 | -360.2512 | 17.4459 | -360.4696 | 17.6122 | -360.805 | 18.1399 | -360.7958 | 17.5978 | -352.6721 | 18.7436 | -352.6567 | 16.8094
12:46 | 5152 | 43.9797 | 202.6403 | 450.1382 | 457.1051 | -16.4884 | -39.9858 | 11.5335 | 8.0522 | 2.3767 | 0.9366 | 3.4577 | -0.9118 | 11.9943 | 4.8655 | 0.6193 | 0.66 | 0.9673 | 0.7459 | -129.2086 | 0.9271 | 5.6464 | 1.8752 | -2.584 | -0.9819 | 4.6486 |  | 3.8186 | 0.5115 | 4.0108 | 3.3603 | 3.3375 | 1.0841 | 10.8204 | 14.2996 | 14.8794 | 11.1327 | -0.0003 | -0.003 | 0.0008 | 0.0034 | 0.0008 | -0.0006 | 0.0162 | 0.0004 | -0.0208 | -360.1311 | 17.3823 | -360.445 | 17.6492 | -360.8697 | 18.183 | -360.8297 | 17.5568 | -352.5613 | 18.7004 | -352.6721 | 16.8546
12:46 | 5153 | 43.9559 | 202.5907 | 450.1231 | 457.0614 | -16.446 | -39.9632 | 11.5092 | 8.02 | 2.4134 | 0.7965 | 3.392 | -0.8936 | 12.0835 | 4.9933 | 0.62 | 0.6596 | 0.9651 | 0.7457 | -129.1803 | 0.8335 | 5.7723 | 1.9117 | -2.7076 | -0.9563 | 4.6444 |  | 3.7938 | 0.4087 | 4.0112 | 3.3644 | 3.3383 | 1.0841 | 10.7949 | 14.2858 | 14.8778 | 11.0609 | -0.0004 | -0.0025 | 0.0005 | 0.0038 | 0.0007 | -0.0001 | 0.0011 | 0.0088 | -0.0241 | -360.2481 | 17.4233 | -360.4481 | 17.6122 | -360.7866 | 18.1789 | -360.8635 | 17.6286 | -352.6875 | 18.7292 | -352.6413 | 16.8074
12:46 | 5154 | 43.9545 | 202.5936 | 449.9952 | 457.0511 | -16.4669 | -39.8938 | 11.5419 | 7.9969 | 2.3237 | 0.6866 | 3.3642 | -0.9374 | 11.9984 | 4.9288 | 0.6183 | 0.6597 | 0.9641 | 0.7447 | -129.1499 | 0.8127 | 5.7061 | 1.9587 | -2.6878 | -0.9562 | 4.6805 |  | 3.8095 | 0.388 | 4.0119 | 3.3623 | 3.3383 | 1.0856 | 10.7857 | 14.2996 | 14.8968 | 11.1154 | -0.0004 | -0.003 | 0.0005 | 0.0036 | 0.0008 | -0.001 | 0.0045 | -0.0043 | -0.0222 | -360.1988 | 17.4418 | -360.5035 | 17.6553 | -360.845 | 18.144 | -360.7866 | 17.5794 | -352.6506 | 18.7415 | -352.6752 | 16.8587
12:46 | 5155 | 43.9782 | 202.6152 | 449.8995 | 457.0525 | -16.4777 | -39.8958 | 11.5145 | 8.0453 | 2.3465 | 0.7072 | 3.3913 | -0.8207 | 12.0613 | 4.9097 | 0.6179 | 0.6636 | 0.9624 | 0.7473 | -129.1463 | 0.8458 | 5.648 | 1.9434 | -2.6085 | -0.9779 | 4.7275 |  | 3.8562 | 0.4671 | 4.0107 | 3.3621 | 3.3367 | 1.0851 | 10.7857 | 14.2764 | 14.8505 | 11.0865 | 0.0002 | -0.0028 | 0.0009 | 0.0039 | 0.0007 | -0.0004 | -0.0051 | -0.0056 | -0.0074 | -360.1896 | 17.3864 | -360.4481 | 17.6389 | -360.8604 | 18.2056 | -360.885 | 17.5999 | -352.6229 | 18.7025 | -352.6198 | 16.8505
12:46 | 5156 | 43.9264 | 202.5526 | 450.052 | 457.0385 | -16.5558 | -39.947 | 11.4813 | 7.9949 | 2.314 | 0.7239 | 3.3439 | -0.9352 | 11.9895 | 4.9521 | 0.6187 | 0.6606 | 0.9627 | 0.7456 | -129.1831 | 0.8494 | 5.7403 | 1.9531 | -2.6364 | -0.9401 | 4.7728 |  | 3.8433 | 0.5004 | 4.0111 | 3.3627 | 3.3417 | 1.0859 | 10.8007 | 14.257 | 14.8615 | 11.0951 | 0.0004 | -0.0028 | 0.0009 | 0.0038 | 0.0012 | -0.0004 | 0.0231 | -0.0094 | -0.0269 | -360.2635 | 17.448 | -360.4758 | 17.6328 | -360.7897 | 18.142 | -360.845 | 17.6061 | -352.6906 | 18.7559 | -352.6475 | 16.8238
12:46 | 5157 | 43.9958 | 202.5757 | 450.0008 | 456.9927 | -16.5137 | -39.8977 | 11.5155 | 8.0187 | 2.3511 | 0.7047 | 3.3481 | -0.9282 | 11.958 | 4.9196 | 0.6184 | 0.6627 | 0.9642 | 0.7458 | -129.2192 | 0.8411 | 5.7008 | 1.9084 | -2.7232 | -0.9994 | 4.677 |  | 3.7217 | 0.4615 | 4.0107 | 3.3599 | 3.3385 | 1.0854 | 10.8064 | 14.2803 | 14.8973 | 11.1121 | -0.0001 | -0.0025 | 0.0008 | 0.0039 | 0.0008 | -0.0002 | 0.0129 | -0.0119 | -0.016 | -360.1588 | 17.4131 | -360.5004 | 17.682 | -360.8943 | 18.1851 | -360.802 | 17.5691 | -352.5952 | 18.7169 | -352.6875 | 16.8772
12:46 | 5158 | 44.0494 | 202.5123 | 450.1154 | 457.0613 | -16.4941 | -39.9097 | 11.5656 | 8.101 | 2.3444 | 0.7366 | 3.376 | -0.9309 | 11.9687 | 4.8654 | 0.6201 | 0.6617 | 0.9648 | 0.7471 | -129.2134 | 0.9338 | 5.6752 | 1.8427 | -2.7646 | -1.0385 | 4.7029 |  | 3.7741 | 0.3907 | 4.0109 | 3.3664 | 3.3418 | 1.0853 | 10.7972 | 14.2939 | 14.8631 | 11.115 | 0.0002 | -0.0024 | 0.0005 | 0.0041 | 0.0011 | -0.0007 | 0.0263 | 0.0016 | -0.0181 | -360.2173 | 17.411 | -360.4296 | 17.6266 | -360.7835 | 18.1892 | -360.8789 | 17.6286 | -352.6875 | 18.7251 | -352.6106 | 16.8258
12:46 | 5159 | 44.0032 | 202.5074 | 450.1262 | 457.1297 | -16.4244 | -40.017 | 11.4982 | 8.0421 | 2.3294 | 0.7469 | 3.3654 | -0.8055 | 11.9883 | 4.9392 | 0.6185 | 0.6598 | 0.9661 | 0.7454 | -129.2414 | 0.9196 | 5.6771 | 1.9063 | -2.7785 | -1.0084 | 4.6831 |  | 3.8068 | 0.3998 | 4.0113 | 3.3648 | 3.3415 | 1.085 | 10.7903 | 14.2928 | 14.827 | 11.1139 | 0.0002 | -0.003 | 0.0009 | 0.004 | 0.0006 | -0.0001 | 0.0057 | -0.0208 | -0.0272 | -360.2111 | 17.4418 | -360.4942 | 17.6553 | -360.8297 | 18.1543 | -360.8204 | 17.5978 | -352.666 | 18.7477 | -352.706 | 16.8587
12:46 | 5160 | 44.0641 | 202.4403 | 450.1174 | 457.0563 | -16.4715 | -40.0467 | 11.4982 | 8.0115 | 2.3342 | 0.7185 | 3.446 | -0.8701 | 11.9806 | 4.7937 | 0.6171 | 0.6587 | 0.9635 | 0.744 | -129.3144 | 0.8511 | 5.4718 | 1.9132 | -2.7441 | -1.0144 | 4.7559 |  | 3.7062 | 0.4452 | 4.0106 | 3.3648 | 3.339 | 1.0855 | 10.7856 | 14.265 | 14.8631 | 11.115 | 0.0003 | -0.0029 | 0.0004 | 0.0036 | 0.001 | -0.0007 | 0.0351 | -0.0137 | -0.009 | -360.1496 | 17.4131 | -360.445 | 17.6594 | -360.8727 | 18.1994 | -360.8481 | 17.5917 | -352.6075 | 18.7087 | -352.6444 | 16.8628
12:46 | 5161 | 44.0656 | 202.5282 | 450.1326 | 457.0994 | -16.5937 | -40.1203 | 11.3164 | 7.9886 | 2.3036 | 0.6682 | 3.2632 | -0.9636 | 11.9461 | 4.827 | 0.6202 | 0.6597 | 0.9651 | 0.7444 | -129.4375 | 0.8214 | 5.4928 | 1.9733 | -2.711 | -1.0019 | 4.6801 |  | 3.7846 | 0.4146 | 4.0106 | 3.3652 | 3.339 | 1.0858 | 10.773 | 14.2693 | 14.8539 | 11.08 | -0.0004 | -0.0029 | 0.0008 | 0.0034 | 0.0005 | -0.0003 | 0.0282 | -0.0102 | -0.0238 | -360.2111 | 17.4172 | -360.4604 | 17.6163 | -360.7927 | 18.1769 | -360.8912 | 17.6266 | -352.6752 | 18.7374 | -352.6537 | 16.834
12:46 | 5162 | 44.0866 | 202.5462 | 450.207 | 457.1915 | -16.6083 | -40.0972 | 11.2843 | 7.9605 | 2.3955 | 0.7168 | 3.2192 | -0.9594 | 11.9429 | 4.7859 | 0.6187 | 0.6566 | 0.964 | 0.7449 | -129.3794 | 0.8127 | 5.5461 | 1.9773 | -2.7219 | -1.0328 | 4.705 |  | 3.8586 | 0.5048 | 4.0113 | 3.3616 | 3.3408 | 1.0866 | 10.7546 | 14.2622 | 14.7704 | 11.0504 | -0.0003 | -0.0027 | 0.001 | 0.0035 | 0.0008 | -0.0006 | -0.0027 | -0.0079 | -0.0205 | -360.1496 | 17.4048 | -360.5004 | 17.6697 | -360.8543 | 18.181 | -360.8112 | 17.5732 | -352.6229 | 18.7271 | -352.6937 | 16.8772
12:46 | 5163 | 44.0945 | 202.5965 | 450.1123 | 457.1063 | -16.5563 | -40.0498 | 11.2666 | 7.9765 | 2.3378 | 0.8125 | 3.2113 | -0.9292 | 11.9739 | 4.8186 | 0.6188 | 0.6649 | 0.9652 | 0.745 | -129.2744 | 0.9269 | 5.676 | 1.9414 | -2.7309 | -1.1178 | 4.5716 |  | 3.8247 | 0.4173 | 4.0113 | 3.3649 | 3.3406 | 1.0858 | 10.7821 | 14.2963 | 14.8485 | 11.0998 | 0.0003 | -0.0028 | 0.0006 | 0.0036 | 0.001 | -0.0004 | 0.0134 | -0.017 | -0.0137 | -360.1865 | 17.4069 | -360.4327 | 17.6184 | -360.8112 | 18.1666 | -360.8635 | 17.6061 | -352.6475 | 18.7333 | -352.626 | 16.8299
12:46 | 5164 | 44.1373 | 202.6121 | 450.1069 | 457.1428 | -16.6425 | -40.0933 | 11.325 | 7.9863 | 2.3939 | 0.8375 | 3.2495 | -0.8984 | 11.956 | 4.8457 | 0.6183 | 0.6618 | 0.9643 | 0.7452 | -129.2471 | 0.9426 | 5.582 | 2.0171 | -2.5722 | -0.9826 | 4.7128 |  | 3.7879 | 0.4683 | 4.0097 | 3.3621 | 3.3398 | 1.0847 | 10.7961 | 14.2637 | 14.8376 | 11.0739 | 0.0001 | -0.003 | 0.0006 | 0.0041 | 0.0006 | -0.0006 | 0.0226 | -0.0184 | -0.0103 | -360.1435 | 17.411 | -360.4573 | 17.6471 | -360.8327 | 18.1707 | -360.842 | 17.5855 | -352.6413 | 18.7251 | -352.6813 | 16.8648
12:46 | 5165 | 44.0736 | 202.611 | 450.1305 | 457.1354 | -16.5937 | -39.9847 | 11.3544 | 7.992 | 2.3862 | 0.792 | 3.2446 | -0.9094 | 11.9107 | 4.8393 | 0.6185 | 0.661 | 0.9643 | 0.7433 | -129.2261 | 0.912 | 5.6429 | 1.9877 | -2.6053 | -1.041 | 4.7113 |  | 3.7756 | 0.4512 | 4.0092 | 3.3636 | 3.3415 | 1.0858 | 10.8006 | 14.2861 | 14.8799 | 11.1294 | 0.0003 | -0.0022 | 0.0008 | 0.0042 | 0.0007 | -0.0004 | 0.025 | -0.005 | -0.0146 | -360.1435 | 17.4007 | -360.4419 | 17.6266 | -360.8081 | 18.1604 | -360.8327 | 17.5917 | -352.6198 | 18.7128 | -352.626 | 16.8402
12:46 | 5166 | 44.0002 | 202.5956 | 450.0158 | 457.1247 | -16.666 | -40.1301 | 11.3045 | 8.0535 | 2.3551 | 0.7875 | 3.2113 | -0.8441 | 11.9899 | 4.9222 | 0.6205 | 0.664 | 0.9626 | 0.746 | -129.278 | 0.875 | 5.6538 | 2.0516 | -2.4825 | -0.9822 | 4.7411 |  | 3.8843 | 0.4276 | 4.011 | 3.3646 | 3.3362 | 1.0836 | 10.8111 | 14.3137 | 14.8427 | 11.0998 | -0.0002 | -0.0025 | 0.0004 | 0.004 | 0.0005 | 0 | 0.0254 | 0.0029 | -0.014 | -360.1742 | 17.3966 | -360.4081 | 17.6122 | -360.7897 | 18.1543 | -360.842 | 17.5855 | -352.6106 | 18.7066 | -352.6383 | 16.8381
12:46 | 5167 | 44.0201 | 202.5859 | 450.0723 | 457.1379 | -16.5973 | -40.0779 | 11.3029 | 8.0526 | 2.363 | 0.8916 | 3.2055 | -0.8985 | 11.9659 | 4.8733 | 0.6176 | 0.6596 | 0.9656 | 0.7453 | -129.2646 | 0.9436 | 5.678 | 2.0096 | -2.5444 | -0.9759 | 4.7479 |  | 3.8755 | 0.5259 | 4.0112 | 3.363 | 3.3364 | 1.0838 | 10.8089 | 14.2647 | 14.8379 | 11.1158 | 0.0001 | -0.0028 | 0.0008 | 0.0039 | 0.0009 | -0.0009 | 0.0198 | 0.0079 | -0.0055 | -360.1588 | 17.409 | -360.4419 | 17.6225 | -360.802 | 18.1379 | -360.7989 | 17.5712 | -352.6106 | 18.7045 | -352.6413 | 16.8402
12:46 | 5168 | 43.9959 | 202.6932 | 450.0467 | 457.1025 | -16.6288 | -40.1101 | 11.368 | 7.9936 | 2.3985 | 0.7656 | 3.186 | -0.8708 | 12.0955 | 4.9339 | 0.6185 | 0.6627 | 0.9646 | 0.7443 | -129.2039 | 0.9161 | 5.6415 | 2.0703 | -2.5608 | -0.9342 | 4.8076 |  | 3.8463 | 0.5226 | 4.0109 | 3.3648 | 3.3393 | 1.0848 | 10.7996 | 14.2554 | 14.8337 | 11.101 | 0 | -0.0033 | 0.0009 | 0.0034 | 0.0005 | -0.0006 | 0.0139 | 0.0006 | -0.004 | -360.1096 | 17.3823 | -360.3865 | 17.6081 | -360.7835 | 18.1563 | -360.8112 | 17.5712 | -352.5706 | 18.6922 | -352.626 | 16.834
12:46 | 5169 | 43.9622 | 202.6388 | 450.146 | 457.106 | -16.5755 | -40.1215 | 11.3506 | 8.043 | 2.4089 | 0.7503 | 3.2259 | -1.0119 | 11.9696 | 4.7891 | 0.6189 | 0.6637 | 0.9631 | 0.7435 | -129.1174 | 0.9554 | 5.6928 | 2.0227 | -2.4514 | -0.9527 | 4.7157 |  | 3.8329 | 0.3743 | 4.0113 | 3.3611 | 3.3343 | 1.0843 | 10.7765 | 14.296 | 14.8522 | 11.1237 | -0.0005 | -0.0029 | 0.0011 | 0.004 | 0.0011 | -0.0011 | 0.0004 | -0.0029 | -0.0268 | -360.2019 | 17.411 | -360.4235 | 17.6122 | -360.762 | 18.1379 | -360.7927 | 17.5835 | -352.6198 | 18.7169 | -352.6198 | 16.8258
12:46 | 5170 | 44.1265 | 202.6967 | 450.1549 | 457.2496 | -16.559 | -40.1252 | 11.3237 | 8.0593 | 2.3477 | 0.7634 | 3.1872 | -1.0396 | 12.0033 | 4.7998 | 0.6198 | 0.6658 | 0.9606 | 0.7457 | -129.2562 | 0.8747 | 5.5456 | 2.1207 | -2.6091 | -0.9772 | 4.7363 |  | 3.8244 | 0.459 | 4.0122 | 3.36 | 3.3383 | 1.0856 | 10.7602 | 14.2683 | 14.8593 | 11.0959 | -0.0003 | -0.0027 | 0.0011 | 0.0038 | 0.0006 | -0.0004 | 0.0263 | 0.0028 | 0.0008 | -360.1034 | 17.3823 | -360.4173 | 17.6348 | -360.8174 | 18.1461 | -360.7927 | 17.5506 | -352.5583 | 18.6943 | -352.6167 | 16.8381
12:46 | 5171 | 44.046 | 202.6639 | 450.0157 | 457.1093 | -16.5045 | -40.0716 | 11.3608 | 8.0475 | 2.4314 | 0.8525 | 3.2232 | -1.0301 | 12.0145 | 4.8158 | 0.6188 | 0.6627 | 0.9606 | 0.7451 | -129.2727 | 0.8443 | 5.6903 | 2.0684 | -2.5181 | -0.8972 | 4.7573 |  | 3.8296 | 0.3545 | 4.0126 | 3.3654 | 3.3375 | 1.0861 | 10.7776 | 14.2684 | 14.8488 | 11.1302 | -0.0002 | -0.003 | 0.0007 | 0.0037 | 0.0013 | -0.0007 | 0.0196 | -0.0166 | -0.0074 | -360.2019 | 17.3966 | -360.3865 | 17.5937 | -360.7835 | 18.1522 | -360.842 | 17.602 | -352.629 | 18.7045 | -352.6013 | 16.8012
12:46 | 5172 | 44.1247 | 202.7029 | 450.1394 | 457.1012 | -16.5593 | -40.0778 | 11.3444 | 8.0516 | 2.4677 | 0.8209 | 3.1647 | -1.0063 | 12.0621 | 4.849 | 0.6188 | 0.6625 | 0.9627 | 0.7448 | -129.2816 | 0.7914 | 5.6945 | 2.1257 | -2.5257 | -1.0102 | 4.6978 |  | 3.8882 | 0.5156 | 4.009 | 3.3613 | 3.3373 | 1.0842 | 10.7684 | 14.2705 | 14.8494 | 11.0984 | 0.0003 | -0.0029 | 0.0009 | 0.0042 | 0.0005 | -0.0001 | 0.0217 | -0.0062 | -0.0065 | -360.1865 | 17.4151 | -360.4635 | 17.643 | -360.8143 | 18.1337 | -360.7527 | 17.5568 | -352.5921 | 18.7189 | -352.6629 | 16.8546
12:46 | 5173 | 44.2021 | 202.7252 | 450.1173 | 457.1792 | -16.4998 | -40.0118 | 11.4407 | 8.05 | 2.48 | 0.8434 | 3.1987 | -1.0006 | 11.9657 | 4.8563 | 0.6185 | 0.6616 | 0.9621 | 0.7453 | -129.2566 | 0.8673 | 5.5495 | 2.0891 | -2.4615 | -1.0173 | 4.7703 |  | 3.9386 | 0.4766 | 4.0121 | 3.3648 | 3.3416 | 1.0841 | 10.8227 | 14.3137 | 14.8659 | 11.1172 | -0.0001 | -0.0033 | 0.0008 | 0.0039 | 0.0008 | -0.0006 | -0.0011 | -0.0196 | -0.0183 | -360.1311 | 17.3884 | -360.4266 | 17.6163 | -360.8235 | 18.2015 | -360.922 | 17.5937 | -352.5983 | 18.682 | -352.6044 | 16.8381
12:46 | 5174 | 44.0298 | 202.6552 | 450.065 | 457.203 | -16.5371 | -40.0388 | 11.5482 | 8.0639 | 2.4351 | 0.8673 | 3.1324 | -0.9806 | 11.9885 | 4.911 | 0.6203 | 0.6619 | 0.9639 | 0.745 | -129.2522 | 0.824 | 5.5564 | 2.0816 | -2.4775 | -0.9614 | 4.7607 |  | 3.842 | 0.4092 | 4.0097 | 3.3646 | 3.3389 | 1.0856 | 10.8238 | 14.3091 | 14.873 | 11.1067 | -0.0002 | -0.0025 | 0.0002 | 0.0036 | 0.0008 | -0.0005 | 0.004 | 0.0063 | -0.0302 | -360.2111 | 17.4439 | -360.4635 | 17.6369 | -360.7927 | 18.1522 | -360.842 | 17.6081 | -352.6844 | 18.7415 | -352.669 | 16.8402
12:46 | 5175 | 43.9997 | 202.6125 | 449.9907 | 457.0933 | -16.5094 | -40.0538 | 11.4501 | 8.0712 | 2.3841 | 0.9536 | 3.2109 | -1.0046 | 12.0108 | 4.8202 | 0.6196 | 0.6601 | 0.9651 | 0.7457 | -129.1739 | 0.9533 | 5.6191 | 2.0925 | -2.515 | -0.943 | 4.8707 |  | 3.8549 | 0.5097 | 4.0102 | 3.3639 | 3.3388 | 1.086 | 10.7777 | 14.2794 | 14.833 | 11.0739 | -0.0001 | -0.0032 | 0.0005 | 0.0035 | 0.0006 | -0.0007 | 0.005 | -0.0133 | -0.0069 | -360.1342 | 17.409 | -360.4666 | 17.6677 | -360.8943 | 18.1994 | -360.8297 | 17.5794 | -352.586 | 18.6984 | -352.6598 | 16.8854
12:46 | 5176 | 44.0457 | 202.583 | 450.1679 | 457.1319 | -16.5463 | -39.9752 | 11.487 | 8.0797 | 2.4299 | 0.8707 | 3.1697 | -0.9747 | 12.0425 | 4.9467 | 0.6206 | 0.6616 | 0.966 | 0.7466 | -129.2987 | 0.9073 | 5.5342 | 2.0383 | -2.5021 | -0.9306 | 4.81 |  | 3.839 | 0.4128 | 4.0108 | 3.3642 | 3.3389 | 1.0862 | 10.7926 | 14.2893 | 14.8703 | 11.1219 | 0.0002 | -0.0032 | 0.001 | 0.0038 | 0.0009 | -0.0005 | -0.0012 | 0.0009 | -0.0305 | -360.2235 | 17.411 | -360.4296 | 17.6245 | -360.8112 | 18.1789 | -360.8974 | 17.6225 | -352.6721 | 18.7128 | -352.6136 | 16.8299
12:46 | 5177 | 44.0541 | 202.6072 | 450.1547 | 457.1081 | -16.4828 | -40.0215 | 11.4565 | 7.989 | 2.4072 | 0.8357 | 3.2296 | -1.0841 | 12.0581 | 4.8551 | 0.6184 | 0.6589 | 0.9646 | 0.7447 | -129.2095 | 0.911 | 5.5321 | 1.9328 | -2.4982 | -0.9631 | 4.7846 |  | 3.817 | 0.4721 | 4.0113 | 3.3661 | 3.341 | 1.0855 | 10.7788 | 14.2578 | 14.8307 | 11.1089 | 0 | -0.0028 | 0.001 | 0.0036 | 0.0003 | -0.0009 | 0.012 | -0.0098 | -0.0068 | -360.2019 | 17.448 | -360.5189 | 17.6656 | -360.8543 | 18.1522 | -360.8081 | 17.5814 | -352.6136 | 18.7477 | -352.706 | 16.8772
12:46 | 5178 | 44.1172 | 202.6145 | 450.1029 | 457.0712 | -16.5042 | -39.9815 | 11.4985 | 7.95 | 2.4282 | 0.7339 | 3.1248 | -0.9804 | 12.0865 | 4.8374 | 0.6195 | 0.6624 | 0.967 | 0.7456 | -129.201 | 1.0005 | 5.6565 | 1.8371 | -2.5527 | -1.1013 | 4.6831 |  | 3.8671 | 0.4929 | 4.0106 | 3.3627 | 3.3447 | 1.0842 | 10.788 | 14.273 | 14.8475 | 11.1118 | -0.0002 | -0.0026 | 0.0015 | 0.0041 | 0.0009 | -0.0005 | -0.0074 | -0.0188 | -0.0046 | -360.165 | 17.3946 | -360.4235 | 17.6533 | -360.8697 | 18.2036 | -360.8912 | 17.5999 | -352.6475 | 18.6881 | -352.629 | 16.8648
12:46 | 5179 | 44.0778 | 202.6044 | 450.1347 | 457.1018 | -16.53 | -40.0321 | 11.4662 | 7.9229 | 2.3876 | 0.7879 | 3.0946 | -0.9461 | 12.0664 | 4.8556 | 0.6191 | 0.6602 | 0.967 | 0.7463 | -129.2675 | 0.8973 | 5.6143 | 1.9133 | -2.6073 | -1.048 | 4.756 |  | 3.8773 | 0.4264 | 4.0114 | 3.3619 | 3.3416 | 1.0849 | 10.7937 | 14.2791 | 14.8438 | 11.0706 | 0.0001 | -0.0026 | 0.0009 | 0.0039 | 0.0011 | 0 | 0.0175 | -0.0197 | -0.0097 | -360.2235 | 17.4274 | -360.4666 | 17.6184 | -360.7927 | 18.1563 | -360.8389 | 17.6102 | -352.6783 | 18.7312 | -352.669 | 16.834
12:46 | 5180 | 44.1123 | 202.6224 | 450.1449 | 457.0899 | -16.4812 | -40.0663 | 11.3671 | 7.9512 | 2.427 | 0.7968 | 3.1353 | -0.9797 | 11.9414 | 4.7586 | 0.6191 | 0.661 | 0.9649 | 0.746 | -129.3207 | 0.8446 | 5.6236 | 1.8873 | -2.5719 | -1.0068 | 4.6822 |  | 3.8629 | 0.471 | 4.0108 | 3.363 | 3.34 | 1.0857 | 10.8007 | 14.3031 | 14.8836 | 11.0955 | 0.0003 | -0.003 | 0.0007 | 0.0039 | 0.0009 | -0.0004 | -0.0043 | -0.0104 | -0.0093 | -360.1034 | 17.4048 | -360.5189 | 17.6615 | -360.8727 | 18.1748 | -360.8266 | 17.5671 | -352.6136 | 18.7148 | -352.7121 | 16.8854
12:46 | 5181 | 44.1854 | 202.6332 | 450.2189 | 457.182 | -16.5012 | -39.9501 | 11.4439 | 7.9964 | 2.4 | 0.8396 | 3.0974 | -0.9625 | 11.9459 | 4.7484 | 0.62 | 0.6599 | 0.9638 | 0.7442 | -129.2708 | 0.9001 | 5.5626 | 1.9588 | -2.5393 | -1.0099 | 4.704 |  | 3.9091 | 0.4877 | 4.0121 | 3.3634 | 3.3407 | 1.0866 | 10.8134 | 14.2928 | 14.8734 | 11.1082 | 0 | -0.0026 | 0.0009 | 0.0042 | 0.0007 | -0.0001 | 0.0032 | -0.0172 | 0.0018 | -360.1742 | 17.3864 | -360.4173 | 17.6102 | -360.8112 | 18.181 | -360.8758 | 17.602 | -352.6537 | 18.6943 | -352.6106 | 16.8402
12:46 | 5182 | 44.0664 | 202.5189 | 450.1777 | 457.0735 | -16.5323 | -40.029 | 11.4303 | 7.8934 | 2.4007 | 0.777 | 3.0365 | -0.9281 | 11.9664 | 4.7901 | 0.6196 | 0.664 | 0.9632 | 0.7448 | -129.2817 | 0.9584 | 5.5459 | 2.0028 | -2.6165 | -1.0153 | 4.6984 |  | 3.8985 | 0.537 | 4.012 | 3.3622 | 3.3405 | 1.0839 | 10.7776 | 14.2741 | 14.8593 | 11.1017 | 0 | -0.0025 | 0 | 0.0036 | 0.0007 | -0.0007 | 0.0057 | -0.0144 | -0.0268 | -360.2388 | 17.4377 | -360.4973 | 17.6204 | -360.8081 | 18.142 | -360.8266 | 17.5896 | -352.6383 | 18.7436 | -352.706 | 16.8566
12:46 | 5183 | 44.0644 | 202.5504 | 450.029 | 457.0934 | -16.581 | -40.0704 | 11.4116 | 7.9556 | 2.4191 | 0.8522 | 3.1131 | -0.9248 | 11.9628 | 4.7554 | 0.6199 | 0.6619 | 0.9648 | 0.7458 | -129.3042 | 1.0265 | 5.6111 | 1.9091 | -2.6179 | -1.0488 | 4.7414 |  | 3.8982 | 0.4558 | 4.0103 | 3.3642 | 3.3371 | 1.0841 | 10.765 | 14.261 | 14.8327 | 11.0898 | -0.0001 | -0.0027 | 0.0004 | 0.0041 | 0.0006 | 0.0002 | 0.0017 | -0.0082 | 0.0011 | -360.1158 | 17.3884 | -360.4512 | 17.6307 | -360.8635 | 18.181 | -360.842 | 17.5712 | -352.6106 | 18.6984 | -352.666 | 16.8772
12:46 | 5184 | 44.0998 | 202.5735 | 450.077 | 457.1188 | -16.516 | -39.9832 | 11.389 | 7.9592 | 2.3855 | 0.789 | 3.1903 | -0.9673 | 11.9976 | 4.8494 | 0.6206 | 0.6612 | 0.9647 | 0.7454 | -129.3114 | 0.9737 | 5.6362 | 1.8543 | -2.6245 | -1.0433 | 4.6095 |  | 3.8567 | 0.5508 | 4.0101 | 3.3667 | 3.3392 | 1.0847 | 10.7845 | 14.2581 | 14.8386 | 11.0966 | 0.0006 | -0.0029 | 0.0011 | 0.0039 | 0.0013 | -0.0002 | 0.0147 | -0.0039 | -0.0024 | -360.2173 | 17.4192 | -360.4419 | 17.602 | -360.7989 | 18.1604 | -360.8604 | 17.6163 | -352.6813 | 18.7169 | -352.6167 | 16.8381
12:46 | 5185 | 44.0982 | 202.5936 | 450.0774 | 457.1682 | -16.5753 | -40.0269 | 11.3697 | 7.8957 | 2.3729 | 0.8701 | 3.1684 | -0.9425 | 11.9461 | 4.7153 | 0.6202 | 0.6624 | 0.9638 | 0.7459 | -129.3612 | 0.8777 | 5.5388 | 1.8679 | -2.6576 | -1.0671 | 4.6416 |  | 3.8942 | 0.5284 | 4.0121 | 3.3667 | 3.3398 | 1.0853 | 10.8031 | 14.2704 | 14.8484 | 11.093 | -0.0001 | -0.003 | 0.0012 | 0.0039 | 0.0007 | -0.0003 | 0.0057 | -0.0168 | 0.0012 | -360.1465 | 17.4028 | -360.4542 | 17.6389 | -360.8358 | 18.1687 | -360.8174 | 17.5753 | -352.626 | 18.7066 | -352.6752 | 16.8648
12:46 | 5186 | 44.1906 | 202.6655 | 450.1031 | 457.183 | -16.5006 | -40.0009 | 11.3981 | 7.8779 | 2.4323 | 0.8118 | 3.1206 | -0.9504 | 11.9893 | 4.7829 | 0.6209 | 0.6628 | 0.9625 | 0.7448 | -129.2914 | 1.0074 | 5.5727 | 1.8958 | -2.6598 | -1.0554 | 4.7083 |  | 3.9415 | 0.5689 | 4.0115 | 3.3622 | 3.3412 | 1.0841 | 10.7729 | 14.2407 | 14.8386 | 11.0619 | 0 | -0.0022 | 0.0014 | 0.0042 | 0.0009 | -0.0004 | 0.0139 | -0.0163 | 0.0121 | -360.1527 | 17.3946 | -360.4327 | 17.6184 | -360.8204 | 18.181 | -360.8666 | 17.5978 | -352.6321 | 18.6963 | -352.6383 | 16.8505
12:46 | 5187 | 44.1044 | 202.6305 | 449.9901 | 457.1049 | -16.5449 | -40.0135 | 11.4366 | 7.9476 | 2.4686 | 0.8646 | 3.1089 | -1.0398 | 11.987 | 4.8707 | 0.6213 | 0.6613 | 0.9631 | 0.7447 | -129.3296 | 0.8917 | 5.5703 | 1.9365 | -2.6757 | -0.9159 | 4.7162 |  | 3.9301 | 0.534 | 4.0112 | 3.3646 | 3.3402 | 1.0857 | 10.7903 | 14.2754 | 14.8849 | 11.1197 | 0 | -0.0026 | 0.001 | 0.0041 | 0.0007 | -0.0007 | 0.0218 | -0.0014 | 0.008 | -360.1958 | 17.411 | -360.4542 | 17.6307 | -360.8143 | 18.1851 | -360.8297 | 17.5896 | -352.6321 | 18.7189 | -352.6444 | 16.8587
12:46 | 5188 | 44.0102 | 202.5201 | 450.0319 | 457.0758 | -16.3634 | -39.8322 | 11.5594 | 7.9956 | 2.4783 | 0.7605 | 3.1275 | -1.0087 | 11.8944 | 4.8973 | 0.6203 | 0.6626 | 0.9613 | 0.7449 | -129.3303 | 0.8562 | 5.4635 | 2.0019 | -2.5819 | -0.905 | 4.817 |  | 3.9349 | 0.5171 | 4.0115 | 3.3644 | 3.344 | 1.0843 | 10.8204 | 14.2994 | 14.8436 | 11.1215 | 0 | -0.0031 | 0.0002 | 0.0037 | 0.0007 | -0.0003 | 0.0128 | -0.0163 | 0.0052 | -360.1527 | 17.3946 | -360.4389 | 17.6184 | -360.8204 | 18.1933 | -360.8266 | 17.5794 | -352.6413 | 18.7066 | -352.6537 | 16.8546
12:46 | 5189 | 44.0644 | 202.5368 | 450.0705 | 457.1433 | -16.3741 | -39.8533 | 11.4759 | 7.9004 | 2.449 | 0.6037 | 3.0412 | -1.0311 | 11.859 | 4.8335 | 0.6207 | 0.6603 | 0.9632 | 0.7455 | -129.429 | 0.7612 | 5.505 | 1.9761 | -2.5599 | -0.9494 | 4.7419 |  | 3.8932 | 0.5193 | 4.0112 | 3.3635 | 3.3422 | 1.0843 | 10.8041 | 14.3184 | 14.8829 | 11.0926 | 0.0002 | -0.0027 | 0.001 | 0.0044 | 0.0008 | -0.0005 | 0.0008 | -0.0088 | -0.0193 | -360.1435 | 17.3884 | -360.3989 | 17.6122 | -360.802 | 18.1953 | -360.8389 | 17.5794 | -352.6229 | 18.6943 | -352.6321 | 16.8484
12:46 | 5190 | 44.1975 | 202.5523 | 450.1495 | 457.1767 | -16.3006 | -39.8809 | 11.5779 | 7.9067 | 2.3499 | 0.5796 | 2.975 | -0.9381 | 11.8766 | 4.8593 | 0.6213 | 0.6627 | 0.9642 | 0.7469 | -129.3807 | 0.8992 | 5.611 | 2.0194 | -2.6199 | -0.8891 | 4.7485 |  | 3.7889 | 0.4934 | 4.0099 | 3.3622 | 3.3384 | 1.0849 | 10.8078 | 14.2923 | 14.8528 | 11.0977 | -0.0004 | -0.003 | 0.0003 | 0.0032 | 0.0001 | -0.0007 | 0.0127 | -0.0035 | -0.0183 | -360.1804 | 17.3987 | -360.4389 | 17.5958 | -360.7466 | 18.1851 | -360.8543 | 17.5814 | -352.6413 | 18.7128 | -352.6229 | 16.8361
12:46 | 5191 | 44.1075 | 202.6079 | 450.1643 | 457.1911 | -16.2934 | -39.8553 | 11.5405 | 7.9034 | 2.4714 | 0.6902 | 3.0569 | -0.954 | 11.8428 | 4.9107 | 0.6204 | 0.6622 | 0.9625 | 0.7475 | -129.3988 | 0.9022 | 5.6078 | 1.9807 | -2.6181 | -1.0626 | 4.7472 |  | 3.8096 | 0.5162 | 4.0103 | 3.3641 | 3.3411 | 1.0849 | 10.7915 | 14.288 | 14.8679 | 11.1038 | -0.0003 | -0.0026 | 0.0008 | 0.0034 | 0.0012 | -0.0006 | 0.0094 | -0.014 | -0.0176 | -360.1373 | 17.3905 | -360.4512 | 17.6328 | -360.8235 | 18.1953 | -360.8174 | 17.5712 | -352.5952 | 18.7107 | -352.669 | 16.8669
12:46 | 5192 | 44.1922 | 202.6086 | 450.1801 | 457.2009 | -16.3499 | -40.0029 | 11.4627 | 8.0233 | 2.4286 | 0.6862 | 3.17 | -0.951 | 11.9377 | 4.8131 | 0.6198 | 0.6586 | 0.9659 | 0.7475 | -129.2731 | 0.918 | 5.4624 | 2.0424 | -2.6524 | -0.971 | 4.6879 |  | 3.8517 | 0.5718 | 4.0114 | 3.3652 | 3.3435 | 1.0843 | 10.7857 | 14.2705 | 14.8379 | 11.1042 | 0 | -0.0033 | 0.0016 | 0.0042 | 0.0005 | -0.0001 | 0.0164 | -0.0126 | -0.0118 | -360.1158 | 17.3658 | -360.3896 | 17.604 | -360.7866 | 18.1994 | -360.8574 | 17.5712 | -352.6352 | 18.6779 | -352.5736 | 16.8361
12:46 | 5193 | 44.1329 | 202.5067 | 450.1862 | 457.1754 | -16.4519 | -40.1139 | 11.4216 | 8.0031 | 2.4064 | 0.6603 | 3.1046 | -1.0488 | 11.9449 | 4.8524 | 0.6206 | 0.6606 | 0.9656 | 0.7462 | -129.3486 | 0.838 | 5.4367 | 2.0257 | -2.6068 | -1.0276 | 4.7575 |  | 3.8591 | 0.5514 | 4.0108 | 3.3637 | 3.3417 | 1.0859 | 10.7904 | 14.275 | 14.8354 | 11.0573 | 0.0001 | -0.0028 | 0.0007 | 0.0037 | 0.0008 | -0.0006 | 0.0007 | -0.0055 | -0.007 | -360.1527 | 17.4213 | -360.4666 | 17.6061 | -360.7527 | 18.1625 | -360.7897 | 17.565 | -352.6506 | 18.723 | -352.6721 | 16.8402
12:46 | 5194 | 44.0947 | 202.5338 | 450.2304 | 457.1739 | -16.3938 | -39.9442 | 11.4162 | 7.9963 | 2.4669 | 0.7298 | 3.1261 | -1.0138 | 11.9406 | 4.9277 | 0.6216 | 0.662 | 0.9667 | 0.7465 | -129.3069 | 0.9093 | 5.5313 | 2.0305 | -2.5835 | -1.0961 | 4.7531 |  | 3.8477 | 0.4855 | 4.0113 | 3.3622 | 3.3374 | 1.086 | 10.7914 | 14.2594 | 14.8353 | 11.1089 | -0.0002 | -0.0025 | 0.0012 | 0.0041 | 0.0009 | 0.0001 | -0.0074 | -0.009 | -0.0187 | -360.1004 | 17.3658 | -360.4112 | 17.6348 | -360.8266 | 18.1912 | -360.8174 | 17.5363 | -352.5306 | 18.6779 | -352.6075 | 16.8587
12:46 | 5195 | 44.1068 | 202.5574 | 450.2079 | 457.1344 | -16.4319 | -40.097 | 11.3837 | 8.0684 | 2.4797 | 0.6796 | 3.1264 | -1.0002 | 11.936 | 4.8802 | 0.6208 | 0.6585 | 0.963 | 0.7474 | -129.1894 | 1.0433 | 5.5813 | 2.0548 | -2.5564 | -1.0755 | 4.6899 |  | 3.798 | 0.4602 | 4.0109 | 3.364 | 3.3412 | 1.0859 | 10.7915 | 14.2589 | 14.8379 | 11.11 | -0.0005 | -0.003 | 0.0007 | 0.0038 | 0.0011 | -0.0007 | 0.0194 | -0.0144 | -0.0164 | -360.2019 | 17.3864 | -360.3773 | 17.5855 | -360.7435 | 18.181 | -360.8389 | 17.5753 | -352.6198 | 18.6861 | -352.5767 | 16.8217
12:46 | 5196 | 44.091 | 202.5793 | 450.1785 | 457.0763 | -16.4093 | -40.0521 | 11.4915 | 8.0267 | 2.5364 | 0.6914 | 3.1271 | -0.9522 | 11.9991 | 4.9962 | 0.621 | 0.6643 | 0.963 | 0.747 | -129.2495 | 0.8603 | 5.4637 | 2.0121 | -2.5289 | -1.2063 | 4.6407 |  | 3.8716 | 0.5785 | 4.011 | 3.3633 | 3.341 | 1.0854 | 10.8226 | 14.308 | 14.8843 | 11.0995 | 0.0001 | -0.0029 | 0.0006 | 0.004 | 0.0013 | 0.0003 | 0.0179 | 0.0008 | -0.0137 | -360.1527 | 17.4069 | -360.4666 | 17.6266 | -360.7835 | 18.1481 | -360.722 | 17.5465 | -352.589 | 18.7066 | -352.6629 | 16.8525
12:46 | 5197 | 44.0824 | 202.5764 | 450.1653 | 457.0953 | -16.3532 | -39.8752 | 11.5342 | 8.02 | 2.4591 | 0.6251 | 3.0364 | -0.8842 | 12.0088 | 4.9395 | 0.62 | 0.6616 | 0.963 | 0.7471 | -129.267 | 0.9187 | 5.587 | 2.079 | -2.4484 | -0.9972 | 4.7327 |  | 3.801 | 0.5234 | 4.0108 | 3.3601 | 3.3389 | 1.087 | 10.7972 | 14.2824 | 14.8689 | 11.1092 | -0.0002 | -0.0033 | 0.0008 | 0.0042 | 0.0008 | -0.0008 | 0.0211 | -0.0164 | -0.0134 | -360.1158 | 17.3535 | -360.3712 | 17.602 | -360.802 | 18.2118 | -360.8481 | 17.5609 | -352.5767 | 18.6696 | -352.5767 | 16.8443
12:46 | 5198 | 44.1125 | 202.5347 | 450.0772 | 457.0575 | -16.3037 | -39.9608 | 11.5113 | 7.9516 | 2.4094 | 0.5536 | 3.04 | -0.8701 | 11.9963 | 4.9428 | 0.62 | 0.6642 | 0.9627 | 0.7478 | -129.2636 | 0.82 | 5.5468 | 2.0041 | -2.5122 | -1.0948 | 4.6388 |  | 3.8868 | 0.5597 | 4.0107 | 3.3618 | 3.3383 | 1.0856 | 10.8111 | 14.3019 | 14.888 | 11.1291 | -0.0002 | -0.0028 | 0.0006 | 0.0039 | 0.0009 | -0.0001 | -0.0014 | -0.0111 | -0.0072 | -360.205 | 17.4151 | -360.4173 | 17.5814 | -360.7189 | 18.1399 | -360.7897 | 17.5671 | -352.629 | 18.7169 | -352.6013 | 16.8115
12:46 | 5199 | 44.1832 | 202.6522 | 450.0043 | 457.1061 | -16.3276 | -40.0277 | 11.5149 | 7.9123 | 2.3721 | 0.5695 | 3.0308 | -0.957 | 11.9891 | 4.9946 | 0.6207 | 0.6628 | 0.9655 | 0.7473 | -129.3256 | 0.8714 | 5.4988 | 1.942 | -2.5969 | -1.0686 | 4.6256 |  | 3.8805 | 0.4941 | 4.0122 | 3.3655 | 3.3384 | 1.085 | 10.7937 | 14.2848 | 14.8543 | 11.0825 | 0 | -0.0027 | 0.001 | 0.0035 | 0.001 | -0.0004 | 0.0085 | -0.0139 | -0.0212 | -360.1004 | 17.3884 | -360.4204 | 17.641 | -360.845 | 18.1892 | -360.8081 | 17.5424 | -352.5552 | 18.7066 | -352.6229 | 16.8587
12:46 | 5200 | 44.1822 | 202.597 | 450.1566 | 457.0439 | -16.3738 | -39.966 | 11.5427 | 7.8712 | 2.3336 | 0.5893 | 3.0916 | -0.978 | 11.9404 | 4.8989 | 0.6209 | 0.6635 | 0.9632 | 0.7474 | -129.3039 | 0.8474 | 5.5926 | 2.0345 | -2.6046 | -1.0283 | 4.7015 |  | 3.842 | 0.4596 | 4.0114 | 3.3655 | 3.3413 | 1.0855 | 10.7903 | 14.2812 | 14.8907 | 11.0908 | 0.0002 | -0.0027 | 0.0011 | 0.004 | 0.0007 | -0.0005 | 0.0056 | 0.0015 | -0.0078 | -360.1711 | 17.3679 | -360.3435 | 17.5876 | -360.7343 | 18.1892 | -360.845 | 17.5753 | -352.6106 | 18.6881 | -352.5767 | 16.8012
12:46 | 5201 | 44.1429 | 202.6731 | 450.0002 | 457.0694 | -16.4208 | -39.958 | 11.4826 | 7.9183 | 2.3833 | 0.6427 | 3.1768 | -0.866 | 11.9943 | 4.897 | 0.6208 | 0.6604 | 0.9638 | 0.7475 | -129.293 | 0.7993 | 5.5342 | 1.8899 | -2.6105 | -1.1132 | 4.5916 |  | 3.8993 | 0.4049 | 4.01 | 3.3601 | 3.3388 | 1.086 | 10.7683 | 14.2533 | 14.8389 | 11.1154 | 0.0006 | -0.0029 | 0.0012 | 0.0038 | 0.0008 | -0.0005 | 0.0081 | -0.0232 | -0.0073 | -360.1496 | 17.4151 | -360.4727 | 17.6225 | -360.7958 | 18.1481 | -360.765 | 17.5547 | -352.6044 | 18.7436 | -352.6475 | 16.8423
12:46 | 5202 | 44.1659 | 202.6716 | 449.9446 | 457.0213 | -16.4572 | -39.9985 | 11.4412 | 7.8933 | 2.3752 | 0.7497 | 3.1036 | -0.9383 | 12.0491 | 4.831 | 0.6195 | 0.66 | 0.9632 | 0.7472 | -129.2611 | 0.8772 | 5.5921 | 1.7802 | -2.5634 | -1.1404 | 4.6993 |  | 3.8088 | 0.4829 | 4.0116 | 3.3646 | 3.3436 | 1.0854 | 10.7591 | 14.2554 | 14.828 | 11.0836 | -0.0002 | -0.0026 | 0.0004 | 0.0038 | 0.001 | -0.0008 | 0.0088 | -0.0011 | 0.0148 | -360.1034 | 17.3597 | -360.3958 | 17.6266 | -360.8266 | 18.2077 | -360.8389 | 17.5424 | -352.5675 | 18.6881 | -352.5921 | 16.8484
12:46 | 5203 | 44.1417 | 202.6495 | 450.1266 | 457.1013 | -16.4468 | -40.052 | 11.5592 | 7.8919 | 2.3953 | 0.648 | 3.2151 | -0.9599 | 12.1135 | 4.8797 | 0.6218 | 0.6606 | 0.9634 | 0.7472 | -129.2716 | 0.8501 | 5.5564 | 1.6937 | -2.5301 | -1.2316 | 4.6133 |  | 3.888 | 0.4498 | 4.0102 | 3.3653 | 3.3398 | 1.0841 | 10.7995 | 14.2963 | 14.8833 | 11.1172 | -0.0003 | -0.0024 | 0.0006 | 0.0039 | 0.0005 | -0.0005 | 0.0056 | -0.0074 | 0.0058 | -360.2265 | 17.4151 | -360.4173 | 17.5937 | -360.7435 | 18.1728 | -360.8297 | 17.5937 | -352.6321 | 18.7271 | -352.6106 | 16.8176
12:46 | 5204 | 44.2222 | 202.6563 | 450.0988 | 457.1115 | -16.472 | -39.9019 | 11.5003 | 8.0019 | 2.3509 | 0.6143 | 3.2161 | -0.9375 | 12.0683 | 4.9511 | 0.6209 | 0.6618 | 0.9667 | 0.7458 | -129.2361 | 0.9505 | 5.5994 | 2.0139 | -2.5014 | -1.0357 | 4.6685 |  | 3.8947 | 0.5108 | 4.0107 | 3.3655 | 3.3416 | 1.0843 | 10.7962 | 14.252 | 14.8365 | 11.1147 | 0.0001 | -0.003 | 0.0007 | 0.0038 | 0.0011 | -0.0007 | 0.0108 | -0.0005 | -0.012 | -360.1927 | 17.4151 | -360.4819 | 17.6574 | -360.8789 | 18.1851 | -360.7989 | 17.5527 | -352.5952 | 18.7271 | -352.6629 | 16.8751
12:46 | 5205 | 44.1887 | 202.697 | 450.0328 | 457.0772 | -16.4201 | -39.9684 | 11.5038 | 7.9466 | 2.3943 | 0.6338 | 3.1766 | -0.954 | 12.0572 | 4.9278 | 0.62 | 0.6599 | 0.9627 | 0.7459 | -129.2854 | 0.9584 | 5.6657 | 1.9194 | -2.5028 | -1.1435 | 4.6208 |  | 3.8442 | 0.486 | 4.011 | 3.363 | 3.3425 | 1.0857 | 10.7754 | 14.2889 | 14.8729 | 11.1057 | 0.0001 | -0.0029 | 0.0008 | 0.004 | 0.0005 | -0.0001 | 0.0128 | -0.0011 | -0.0008 | -360.1404 | 17.3966 | -360.4296 | 17.6245 | -360.8174 | 18.2282 | -360.8666 | 17.5835 | -352.629 | 18.6963 | -352.5952 | 16.8525
12:46 | 5206 | 44.0295 | 202.6216 | 450.0151 | 457.0635 | -16.4665 | -39.948 | 11.5962 | 7.9088 | 2.3408 | 0.6478 | 3.0391 | -0.93 | 12.0298 | 4.8997 | 0.6217 | 0.6633 | 0.967 | 0.748 | -129.3018 | 0.9098 | 5.5883 | 1.9357 | -2.725 | -1.2104 | 4.6647 |  | 3.8879 | 0.5718 | 4.0116 | 3.3669 | 3.3403 | 1.086 | 10.7949 | 14.2744 | 14.8383 | 11.1067 | -0.0001 | -0.0028 | 0.0011 | 0.0038 | 0.0013 | -0.0002 | 0.0036 | 0.0027 | -0.0144 | -360.2512 | 17.4439 | -360.4881 | 17.6328 | -360.8204 | 18.1748 | -360.8297 | 17.5917 | -352.6783 | 18.7579 | -352.6752 | 16.8402
12:46 | 5207 | 44.2104 | 202.6571 | 450.0626 | 457.1448 | -16.5075 | -39.9678 | 11.5614 | 8.0186 | 2.3719 | 0.6049 | 3.1045 | -0.9825 | 12.038 | 4.9088 | 0.621 | 0.6609 | 0.9657 | 0.7487 | -129.3087 | 0.9264 | 5.6049 | 2.0029 | -2.6751 | -1.1118 | 4.7342 |  | 3.872 | 0.5405 | 4.0102 | 3.3674 | 3.3433 | 1.0858 | 10.7742 | 14.2588 | 14.8542 | 11.0468 | -0.0004 | -0.0025 | 0.0006 | 0.0037 | 0.0004 | -0.0003 | 0.0077 | -0.0063 | -0.0061 | -360.1558 | 17.409 | -360.4666 | 17.6533 | -360.8666 | 18.22 | -360.8512 | 17.565 | -352.6198 | 18.7189 | -352.6752 | 16.8792
12:47 | 5208 | 44.1061 | 202.6444 | 449.9902 | 457.0802 | -16.5459 | -40.1112 | 11.4867 | 8.09 | 2.4262 | 0.7317 | 3.2937 | -0.9886 | 11.9949 | 4.8668 | 0.6207 | 0.6633 | 0.9648 | 0.7511 | -129.2965 | 1.0009 | 5.5615 | 2.0633 | -2.643 | -1.2018 | 4.7236 |  | 3.8327 | 0.5485 | 4.0119 | 3.3639 | 3.3384 | 1.087 | 10.773 | 14.2406 | 14.8086 | 11.0854 | 0.0006 | -0.0024 | 0.0012 | 0.0043 | 0.0006 | -0.0004 | 0.0152 | -0.0166 | -0.0115 | -360.2358 | 17.4356 | -360.4666 | 17.6389 | -360.8112 | 18.1912 | -360.8727 | 17.6081 | -352.706 | 18.7538 | -352.6629 | 16.8525
12:47 | 5209 | 44.0807 | 202.5952 | 449.9514 | 457.0212 | -16.566 | -40.0412 | 11.5096 | 7.9772 | 2.3869 | 0.6411 | 3.3047 | -0.9714 | 12.0535 | 4.9163 | 0.6207 | 0.6618 | 0.9637 | 0.7484 | -129.2202 | 0.9165 | 5.5595 | 2.0329 | -2.6471 | -1.0751 | 4.7473 |  | 3.9196 | 0.6296 | 4.0104 | 3.3673 | 3.3378 | 1.0862 | 10.7684 | 14.2646 | 14.8426 | 11.0815 | 0 | -0.0031 | 0.0009 | 0.0037 | 0.0008 | -0.0002 | 0.0121 | -0.0031 | -0.0196 | -360.1773 | 17.4172 | -360.4789 | 17.6512 | -360.8666 | 18.2015 | -360.8512 | 17.5671 | -352.6229 | 18.7353 | -352.6721 | 16.8813
12:47 | 5210 | 44.041 | 202.5374 | 449.992 | 457.119 | -16.5079 | -40.0137 | 11.4809 | 7.9764 | 2.3476 | 0.7073 | 3.3141 | -0.9383 | 12.0163 | 4.9703 | 0.6209 | 0.6629 | 0.9662 | 0.7488 | -129.3087 | 0.8841 | 5.6667 | 2.1062 | -2.6861 | -1.0082 | 4.7954 |  | 3.8554 | 0.5303 | 4.0115 | 3.3683 | 3.3442 | 1.0849 | 10.7856 | 14.2652 | 14.8584 | 11.1146 | 0 | -0.0027 | 0.0008 | 0.004 | 0.0008 | -0.0007 | 0.0105 | -0.0155 | -0.0104 | -360.2019 | 17.4254 | -360.4573 | 17.6266 | -360.8358 | 18.1953 | -360.8697 | 17.5958 | -352.6598 | 18.7312 | -352.6444 | 16.8423
12:47 | 5211 | 44.0138 | 202.5714 | 450.0337 | 457.0674 | -16.4824 | -39.9613 | 11.4722 | 7.9641 | 2.3404 | 0.5631 | 3.2737 | -0.895 | 12.0268 | 4.9056 | 0.6193 | 0.6622 | 0.9625 | 0.7484 | -129.2414 | 0.9141 | 5.612 | 2.0403 | -2.5978 | -1.0209 | 4.7951 |  | 3.8895 | 0.4549 | 4.0108 | 3.366 | 3.3413 | 1.0851 | 10.8087 | 14.3058 | 14.8769 | 11.1143 | -0.0003 | -0.0025 | 0.0006 | 0.0039 | 0.001 | -0.0003 | 0.0091 | 0.0016 | -0.0163 | -360.1927 | 17.411 | -360.4881 | 17.6471 | -360.8235 | 18.1871 | -360.845 | 17.5609 | -352.6413 | 18.7436 | -352.6998 | 16.8731
12:47 | 5212 | 44.1412 | 202.6905 | 449.9726 | 457.1325 | -16.6029 | -40.0103 | 11.5383 | 7.9708 | 2.3971 | 0.5871 | 3.3186 | -0.8745 | 11.9947 | 4.9095 | 0.6198 | 0.6607 | 0.966 | 0.7485 | -129.1308 | 1.0207 | 5.7238 | 2.0113 | -2.5926 | -1.0902 | 4.7693 |  | 3.8431 | 0.4621 | 4.0114 | 3.3641 | 3.3433 | 1.0845 | 10.8076 | 14.287 | 14.8791 | 11.1082 | -0.0002 | -0.0029 | 0.0002 | 0.0034 | 0.0008 | -0.0006 | -0.0006 | 0.0027 | -0.0168 | -360.1835 | 17.4048 | -360.4389 | 17.6184 | -360.805 | 18.1871 | -360.8358 | 17.5609 | -352.6352 | 18.7189 | -352.6567 | 16.8566
12:47 | 5213 | 44.22 | 202.714 | 450.0355 | 457.1348 | -16.5248 | -39.9695 | 11.5989 | 7.965 | 2.3656 | 0.6327 | 3.3254 | -0.8383 | 12.0245 | 4.8571 | 0.6201 | 0.6581 | 0.9634 | 0.7491 | -129.1302 | 0.9904 | 5.6792 | 2.0386 | -2.6239 | -1.005 | 4.6921 |  | 3.8401 | 0.6157 | 4.0095 | 3.3636 | 3.3366 | 1.0851 | 10.7868 | 14.2545 | 14.8403 | 11.1165 | 0.0003 | -0.0031 | 0.0009 | 0.0042 | 0.001 | -0.0005 | 0.0161 | -0.0076 | -0.0059 | -360.1158 | 17.3966 | -360.4481 | 17.6061 | -360.7927 | 18.181 | -360.8389 | 17.5629 | -352.6013 | 18.6984 | -352.6321 | 16.8484
12:47 | 5214 | 44.1865 | 202.6491 | 450.1454 | 457.1498 | -16.5068 | -39.9263 | 11.6095 | 7.8338 | 2.3165 | 0.562 | 3.2967 | -0.7874 | 11.9992 | 4.9096 | 0.6199 | 0.6609 | 0.9647 | 0.7476 | -129.1787 | 0.9643 | 5.6484 | 2.0867 | -2.607 | -1.0125 | 4.7026 |  | 3.8936 | 0.5785 | 4.0103 | 3.367 | 3.3368 | 1.0846 | 10.8295 | 14.3324 | 14.9204 | 11.1352 | 0.0001 | -0.0028 | 0.0009 | 0.004 | 0.0005 | -0.0001 | 0.0051 | -0.0201 | -0.0173 | -360.1188 | 17.3823 | -360.4389 | 17.6184 | -360.7958 | 18.181 | -360.802 | 17.5465 | -352.586 | 18.7066 | -352.6352 | 16.8628
12:47 | 5215 | 44.1007 | 202.5809 | 450.2104 | 457.1067 | -16.4156 | -39.906 | 11.5807 | 7.8599 | 2.405 | 0.5599 | 3.2694 | -1.0049 | 11.9303 | 4.8659 | 0.6206 | 0.6626 | 0.9641 | 0.7476 | -129.1971 | 0.87 | 5.5702 | 2.117 | -2.6524 | -1.0091 | 4.7415 |  | 3.8482 | 0.475 | 4.0115 | 3.3659 | 3.3411 | 1.0868 | 10.7914 | 14.2939 | 14.8805 | 11.1092 | -0.0004 | -0.0027 | 0.0012 | 0.004 | 0.0009 | -0.001 | 0.0052 | -0.0154 | -0.0082 | -360.1311 | 17.3802 | -360.3865 | 17.6081 | -360.7589 | 18.181 | -360.8327 | 17.5671 | -352.5829 | 18.6902 | -352.5829 | 16.834
12:47 | 5216 | 44.147 | 202.5701 | 450.0678 | 457.085 | -16.458 | -39.9597 | 11.5158 | 7.9607 | 2.3845 | 0.5193 | 3.2897 | -1.0061 | 11.9953 | 4.9235 | 0.6216 | 0.6615 | 0.9646 | 0.7481 | -129.1908 | 0.922 | 5.7668 | 1.9833 | -2.619 | -1.0352 | 4.6428 |  | 3.8517 | 0.4931 | 4.0109 | 3.3647 | 3.3428 | 1.0858 | 10.7788 | 14.252 | 14.8365 | 11.0627 | -0.0002 | -0.0032 | 0.0016 | 0.0045 | 0.0003 | -0.0002 | 0.0019 | -0.0161 | -0.0133 | -360.1588 | 17.4007 | -360.4389 | 17.6122 | -360.762 | 18.1687 | -360.7804 | 17.5445 | -352.6106 | 18.7087 | -352.6136 | 16.8443
12:47 | 5217 | 44.142 | 202.5883 | 450.1568 | 457.194 | -16.5554 | -39.9807 | 11.4926 | 7.9989 | 2.4507 | 0.5898 | 3.3096 | -0.944 | 11.887 | 4.88 | 0.6199 | 0.6588 | 0.9646 | 0.7483 | -129.2084 | 0.9312 | 5.6465 | 1.7755 | -2.6668 | -1.0697 | 4.6117 |  | 3.979 | 0.6493 | 4.0116 | 3.3655 | 3.3406 | 1.0876 | 10.7844 | 14.2929 | 14.8628 | 11.0789 | 0.0004 | -0.0029 | 0.0011 | 0.0036 | 0.0008 | -0.0009 | 0.016 | 0.0031 | -0.007 | -360.1127 | 17.3782 | -360.4019 | 17.6102 | -360.7958 | 18.2015 | -360.7989 | 17.5527 | -352.5613 | 18.6922 | -352.6013 | 16.8423
12:47 | 5218 | 44.1521 | 202.639 | 450.0927 | 457.1987 | -16.5768 | -40.0367 | 11.4722 | 7.8985 | 2.5091 | 0.7059 | 3.2557 | -0.856 | 12.0041 | 4.9597 | 0.6193 | 0.6633 | 0.962 | 0.7478 | -129.1138 | 0.8544 | 5.6322 | 1.8457 | -2.6081 | -1.0204 | 4.6705 |  | 3.9916 | 0.6152 | 4.0098 | 3.3665 | 3.3385 | 1.0845 | 10.7638 | 14.2947 | 14.8266 | 11.0826 | -0.0002 | -0.0033 | 0.0007 | 0.004 | 0.0006 | -0.0008 | 0.0018 | 0.002 | -0.0077 | -360.1742 | 17.4048 | -360.4389 | 17.5876 | -360.762 | 18.1748 | -360.7897 | 17.5691 | -352.6506 | 18.7148 | -352.5952 | 16.8176
12:47 | 5219 | 44.067 | 202.6402 | 449.9348 | 457.1174 | -16.522 | -39.9486 | 11.4671 | 7.9464 | 2.503 | 0.6347 | 3.3413 | -0.9533 | 11.9925 | 4.8906 | 0.6203 | 0.6614 | 0.9631 | 0.7474 | -129.108 | 0.8954 | 5.6809 | 1.7592 | -2.6222 | -1.132 | 4.7363 |  | 3.9496 | 0.6322 | 4.0102 | 3.3689 | 3.3386 | 1.086 | 10.773 | 14.2637 | 14.8665 | 11.097 | -0.0003 | -0.0024 | 0.0007 | 0.0043 | 0.0011 | -0.0008 | 0.0157 | -0.0192 | -0.0071 | -360.1096 | 17.411 | -360.4635 | 17.641 | -360.8389 | 18.1851 | -360.7989 | 17.5445 | -352.5675 | 18.7148 | -352.6506 | 16.8689
12:47 | 5220 | 44.2014 | 202.5995 | 450.0497 | 457.2051 | -16.5945 | -40.044 | 11.4805 | 7.9752 | 2.5863 | 0.7101 | 3.3834 | -0.9353 | 11.9168 | 4.8416 | 0.6207 | 0.6626 | 0.9658 | 0.7463 | -129.1519 | 0.9155 | 5.6711 | 1.8534 | -2.6327 | -1.0452 | 4.7279 |  | 3.9943 | 0.592 | 4.0115 | 3.3651 | 3.3396 | 1.0859 | 10.7776 | 14.2858 | 14.8488 | 11.0955 | -0.0001 | -0.0026 | 0.0006 | 0.0038 | 0.0007 | -0.0006 | 0.0188 | -0.0108 | -0.0098 | -360.1988 | 17.3843 | -360.3958 | 17.602 | -360.7958 | 18.2036 | -360.8697 | 17.5937 | -352.6352 | 18.7004 | -352.5706 | 16.8238
12:47 | 5221 | 44.1639 | 202.61 | 450.1408 | 457.1588 | -16.6578 | -40.0858 | 11.4513 | 7.9676 | 2.4685 | 0.6885 | 3.4813 | -0.8349 | 12.0011 | 4.877 | 0.62 | 0.6645 | 0.9663 | 0.7475 | -129.1614 | 0.9186 | 5.6588 | 1.8958 | -2.6266 | -1.0625 | 4.7424 |  | 3.9108 | 0.6574 | 4.0109 | 3.3624 | 3.3365 | 1.0862 | 10.7695 | 14.3064 | 14.8508 | 11.0995 | -0.0003 | -0.0032 | 0.0008 | 0.004 | 0.0007 | -0.0003 | -0.0001 | -0.0105 | -0.0207 | -360.2204 | 17.4377 | -360.5066 | 17.6451 | -360.842 | 18.1707 | -360.7897 | 17.5506 | -352.6506 | 18.7497 | -352.7029 | 16.8525
12:47 | 5222 | 44.1579 | 202.5998 | 450.1291 | 457.1631 | -16.6381 | -40.1398 | 11.3888 | 7.9036 | 2.3376 | 0.6308 | 3.4056 | -0.9695 | 11.9957 | 4.8519 | 0.6187 | 0.667 | 0.964 | 0.7467 | -129.1712 | 0.939 | 5.6988 | 1.8091 | -2.6865 | -1.1215 | 4.712 |  | 3.9214 | 0.5244 | 4.0119 | 3.3632 | 3.3375 | 1.0855 | 10.8365 | 14.2815 | 14.8813 | 11.1074 | 0.0003 | -0.0027 | 0.0011 | 0.0038 | 0.0007 | -0.0005 | -0.009 | 0.001 | -0.0254 | -360.1527 | 17.3884 | -360.4235 | 17.6307 | -360.8574 | 18.22 | -360.885 | 17.5671 | -352.5798 | 18.7004 | -352.5921 | 16.8546
12:47 | 5223 | 44.1501 | 202.5796 | 450.1418 | 457.0812 | -16.5685 | -40.0614 | 11.335 | 7.9153 | 2.4168 | 0.644 | 3.4075 | -0.9101 | 11.9329 | 4.8292 | 0.6202 | 0.6601 | 0.9605 | 0.7463 | -129.2169 | 0.9378 | 5.7274 | 1.9189 | -2.6109 | -1.0995 | 4.7674 |  | 3.9469 | 0.4859 | 4.0126 | 3.3657 | 3.3393 | 1.0864 | 10.7984 | 14.2717 | 14.8624 | 11.1053 | -0.0001 | -0.0024 | 0.0005 | 0.0035 | 0.0006 | -0.0005 | 0.0048 | -0.0155 | -0.0311 | -360.2327 | 17.4295 | -360.4881 | 17.6143 | -360.7773 | 18.1748 | -360.8481 | 17.5814 | -352.666 | 18.7436 | -352.6321 | 16.8217
12:47 | 5224 | 44.1629 | 202.5841 | 450.0874 | 457.0803 | -16.658 | -39.9988 | 11.3764 | 7.8187 | 2.463 | 0.5861 | 3.3766 | -0.9049 | 11.9652 | 4.8712 | 0.6198 | 0.6614 | 0.9625 | 0.7467 | -129.1995 | 0.9556 | 5.7313 | 1.9309 | -2.6078 | -1.0516 | 4.7804 |  | 3.8861 | 0.4995 | 4.0115 | 3.3659 | 3.3383 | 1.0851 | 10.8019 | 14.2926 | 14.8723 | 11.0739 | -0.001 | -0.0025 | 0.001 | 0.004 | 0.0007 | -0.0003 | 0.0004 | -0.0132 | -0.0188 | -360.1681 | 17.4254 | -360.5066 | 17.6677 | -360.8666 | 18.1953 | -360.8143 | 17.5547 | -352.5921 | 18.7292 | -352.6506 | 16.8792
12:47 | 5225 | 44.2156 | 202.6431 | 450.1286 | 457.153 | -16.5431 | -40.0777 | 11.4482 | 8.0184 | 2.4304 | 0.7742 | 3.5262 | -0.89 | 12.0124 | 4.9188 | 0.6218 | 0.6612 | 0.9664 | 0.7484 | -129.1418 | 0.9835 | 5.7796 | 2.0227 | -2.5827 | -0.9656 | 4.7705 |  | 3.9366 | 0.6244 | 4.0101 | 3.3661 | 3.3384 | 1.0859 | 10.7556 | 14.2579 | 14.8433 | 11.0796 | 0.0003 | -0.0031 | 0.0009 | 0.0035 | 0.0007 | -0.0003 | 0.009 | -0.0097 | -0.023 | -360.1958 | 17.4028 | -360.4204 | 17.6122 | -360.7897 | 18.2179 | -360.8697 | 17.6081 | -352.6721 | 18.7045 | -352.5983 | 16.832
12:47 | 5226 | 44.2004 | 202.5712 | 450.1849 | 457.115 | -16.5238 | -39.9688 | 11.3965 | 8.0258 | 2.5066 | 0.7512 | 3.4233 | -0.9288 | 12.0312 | 4.9298 | 0.6208 | 0.6642 | 0.9655 | 0.748 | -129.125 | 1.0687 | 5.7127 | 1.9817 | -2.6568 | -1.051 | 4.6797 |  | 3.8809 | 0.5802 | 4.0109 | 3.3665 | 3.3374 | 1.0863 | 10.7604 | 14.2621 | 14.833 | 11.0739 | 0.0001 | -0.003 | 0.0005 | 0.0038 | 0.0008 | -0.0008 | 0.0016 | 0.007 | -0.0256 | -360.1773 | 17.4521 | -360.5096 | 17.6451 | -360.8389 | 18.1748 | -360.7897 | 17.5732 | -352.6598 | 18.76 | -352.7121 | 16.8628
12:47 | 5227 | 44.2249 | 202.6005 | 450.0504 | 457.142 | -16.5155 | -39.9844 | 11.566 | 8.0471 | 2.5499 | 0.8796 | 3.5567 | -0.8551 | 12.0536 | 4.9494 | 0.6206 | 0.664 | 0.9624 | 0.7474 | -129.1697 | 1.1092 | 5.5561 | 1.9887 | -2.5888 | -0.9807 | 4.7551 |  | 3.8497 | 0.5679 | 4.0122 | 3.3638 | 3.342 | 1.087 | 10.7972 | 14.2824 | 14.8631 | 11.115 | -0.0002 | -0.0025 | 0.0008 | 0.0044 | 0.0009 | -0.0001 | 0.0136 | -0.0107 | -0.0125 | -360.1558 | 17.4048 | -360.4635 | 17.643 | -360.882 | 18.2364 | -360.8789 | 17.5814 | -352.5983 | 18.7107 | -352.6629 | 16.8628
12:47 | 5228 | 44.2635 | 202.5608 | 450.1133 | 457.0621 | -16.5584 | -39.979 | 11.4915 | 7.9921 | 2.4647 | 0.7276 | 3.4209 | -0.7813 | 12.0673 | 4.9414 | 0.6201 | 0.6629 | 0.9654 | 0.7478 | -129.2909 | 1.0434 | 5.648 | 2.0188 | -2.5869 | -1.0028 | 4.7582 |  | 3.8976 | 0.5599 | 4.0124 | 3.3653 | 3.34 | 1.0858 | 10.7707 | 14.2901 | 14.8743 | 11.101 | -0.0003 | -0.003 | 0.0005 | 0.0034 | 0.0008 | -0.0007 | 0.0207 | -0.0006 | -0.0177 | -360.2204 | 17.4356 | -360.4758 | 17.6245 | -360.7743 | 18.1933 | -360.8512 | 17.5978 | -352.6937 | 18.7436 | -352.629 | 16.8443
12:47 | 5229 | 44.2265 | 202.5922 | 450.0734 | 457.1159 | -16.5327 | -40.0431 | 11.5283 | 7.9442 | 2.5393 | 0.7538 | 3.3587 | -0.9241 | 12.0942 | 4.9505 | 0.6199 | 0.6651 | 0.964 | 0.7471 | -129.2818 | 1.0747 | 5.7246 | 1.9932 | -2.5749 | -0.9588 | 4.7162 |  | 3.8231 | 0.4724 | 4.0115 | 3.3642 | 3.3351 | 1.0856 | 10.7672 | 14.2578 | 14.8249 | 11.0916 | 0.0003 | -0.0029 | 0.001 | 0.004 | 0.0004 | -0.0001 | 0.0092 | 0.0079 | -0.0018 | -360.1742 | 17.4274 | -360.5127 | 17.6636 | -360.8574 | 18.2015 | -360.8512 | 17.5732 | -352.6475 | 18.7374 | -352.6906 | 16.8854
12:47 | 5230 | 44.2428 | 202.6131 | 450.1152 | 457.1008 | -16.4933 | -40.0139 | 11.4577 | 7.9447 | 2.578 | 0.7394 | 3.3924 | -0.99 | 12.0041 | 4.8444 | 0.6204 | 0.661 | 0.967 | 0.7458 | -129.24 | 1.1193 | 5.7063 | 2.0347 | -2.5823 | -0.973 | 4.7404 |  | 3.8646 | 0.5629 | 4.0109 | 3.3627 | 3.3391 | 1.0855 | 10.7961 | 14.287 | 14.856 | 11.1197 | 0 | -0.0032 | 0.0011 | 0.0039 | 0.001 | -0.0007 | 0.0241 | -0.0151 | -0.0147 | -360.1773 | 17.3946 | -360.4266 | 17.6307 | -360.8266 | 18.2261 | -360.8912 | 17.5896 | -352.6598 | 18.7066 | -352.626 | 16.8505
12:47 | 5231 | 44.3003 | 202.5393 | 450.137 | 457.1518 | -16.5207 | -39.9022 | 11.4388 | 7.9955 | 2.5811 | 0.8064 | 3.4971 | -0.947 | 12.0161 | 4.8592 | 0.6206 | 0.6639 | 0.9672 | 0.7485 | -129.2303 | 1.1329 | 5.6858 | 2.0575 | -2.4829 | -0.9359 | 4.7818 |  | 3.8981 | 0.5723 | 4.0125 | 3.3679 | 3.3425 | 1.0865 | 10.8111 | 14.3251 | 14.9053 | 11.1118 | -0.0005 | -0.0028 | 0.0009 | 0.0037 | 0.0006 | -0.0003 | 0.0223 | -0.0083 | -0.0171 | -360.2111 | 17.4439 | -360.5219 | 17.6512 | -360.8358 | 18.183 | -360.8143 | 17.5712 | -352.6752 | 18.7497 | -352.6721 | 16.8731
12:47 | 5232 | 44.2353 | 202.5453 | 450.0771 | 457.0689 | -16.5471 | -39.9232 | 11.571 | 8.0108 | 2.5621 | 0.7669 | 3.3955 | -0.9517 | 11.9747 | 4.8775 | 0.6187 | 0.6644 | 0.9638 | 0.7465 | -129.208 | 1.0579 | 5.6322 | 1.9977 | -2.6045 | -1.0106 | 4.7143 |  | 3.9001 | 0.5955 | 4.0123 | 3.3663 | 3.3431 | 1.0852 | 10.7868 | 14.295 | 14.8692 | 11.1165 | -0.0002 | -0.0025 | 0.0012 | 0.0041 | 0.0012 | -0.0006 | 0.0003 | 0.0042 | -0.0048 | -360.1865 | 17.3966 | -360.4604 | 17.6451 | -360.8266 | 18.2077 | -360.8574 | 17.5917 | -352.6537 | 18.7128 | -352.6321 | 16.8669
12:47 | 5233 | 44.2214 | 202.5417 | 450.1483 | 457.1439 | -16.5714 | -40.0238 | 11.4462 | 8.0782 | 2.5306 | 0.7609 | 3.4593 | -0.9918 | 11.9048 | 4.7665 | 0.6214 | 0.6644 | 0.9653 | 0.7475 | -129.2135 | 1.0957 | 5.5989 | 1.9624 | -2.6195 | -1.1648 | 4.7292 |  | 3.9024 | 0.5341 | 4.0105 | 3.3642 | 3.3386 | 1.0851 | 10.7835 | 14.2911 | 14.8804 | 11.1255 | -0.0002 | -0.0032 | 0.0001 | 0.0034 | 0.0003 | -0.0007 | 0.0146 | -0.0178 | -0.0081 | -360.2235 | 17.4213 | -360.485 | 17.6594 | -360.8081 | 18.1974 | -360.8543 | 17.5876 | -352.6752 | 18.7395 | -352.6598 | 16.8648
12:47 | 5234 | 44.2251 | 202.5689 | 450.0967 | 457.1567 | -16.566 | -40.114 | 11.4582 | 7.9599 | 2.4317 | 0.7672 | 3.2626 | -0.9517 | 12.0253 | 4.8992 | 0.6196 | 0.6608 | 0.9619 | 0.7475 | -129.2079 | 1.0151 | 5.6587 | 1.9334 | -2.5858 | -1.0016 | 4.7578 |  | 3.8473 | 0.3669 | 4.0106 | 3.3626 | 3.3386 | 1.085 | 10.7891 | 14.2744 | 14.8673 | 11.0836 | 0.0004 | -0.0027 | 0.0007 | 0.004 | 0.0008 | -0.0004 | -0.0058 | -0.0184 | 0.0004 | -360.1988 | 17.4295 | -360.4973 | 17.6492 | -360.8297 | 18.1871 | -360.845 | 17.5753 | -352.6229 | 18.7333 | -352.6567 | 16.8669
12:47 | 5235 | 44.2442 | 202.4762 | 450.1224 | 457.1071 | -16.5577 | -40.0593 | 11.4625 | 8.0351 | 2.4248 | 0.6671 | 3.1797 | -1.0045 | 11.9633 | 4.856 | 0.6205 | 0.663 | 0.964 | 0.7481 | -129.2124 | 1.0009 | 5.6908 | 1.7598 | -2.6695 | -1.0205 | 4.6898 |  | 3.8834 | 0.5053 | 4.0121 | 3.3679 | 3.3378 | 1.0875 | 10.7731 | 14.2748 | 14.8286 | 11.1097 | -0.0001 | -0.0031 | 0.0006 | 0.0044 | 0.0007 | -0.0009 | -0.0017 | -0.0022 | 0.0033 | -360.1896 | 17.4069 | -360.4819 | 17.6492 | -360.8543 | 18.22 | -360.8481 | 17.5794 | -352.6383 | 18.7292 | -352.6567 | 16.871
12:47 | 5236 | 44.2974 | 202.5936 | 450.0776 | 457.1829 | -16.6331 | -40.067 | 11.4397 | 8.1231 | 2.4762 | 0.7699 | 3.1888 | -0.9515 | 12.0397 | 4.9299 | 0.6215 | 0.6622 | 0.9664 | 0.7463 | -129.2291 | 0.9881 | 5.6146 | 1.7846 | -2.6036 | -1.0461 | 4.7004 |  | 3.9094 | 0.6228 | 4.012 | 3.3679 | 3.3397 | 1.0878 | 10.7926 | 14.2778 | 14.8645 | 11.1103 | -0.0003 | -0.0025 | 0.0006 | 0.0037 | 0.0007 | -0.0005 | -0.0004 | -0.0015 | 0.0007 | -360.2204 | 17.4274 | -360.4758 | 17.641 | -360.805 | 18.2056 | -360.8174 | 17.5896 | -352.6444 | 18.7456 | -352.669 | 16.8566
12:47 | 5237 | 44.354 | 202.6151 | 450.1397 | 457.1834 | -16.503 | -39.9491 | 11.5834 | 8.069 | 2.4226 | 0.865 | 3.1422 | -0.9527 | 12.0386 | 4.8308 | 0.6216 | 0.6623 | 0.9616 | 0.7485 | -129.2397 | 0.9413 | 5.5763 | 1.7876 | -2.565 | -1.0362 | 4.7659 |  | 3.8824 | 0.5679 | 4.0126 | 3.3681 | 3.3444 | 1.0862 | 10.7683 | 14.2708 | 14.8226 | 11.0746 | 0 | -0.0027 | 0.0008 | 0.0037 | 0.0009 | -0.0008 | 0.0032 | -0.004 | -0.011 | -360.1865 | 17.4172 | -360.4881 | 17.6677 | -360.8297 | 18.2077 | -360.8512 | 17.5609 | -352.629 | 18.7312 | -352.706 | 16.8854
12:47 | 5238 | 44.2935 | 202.4851 | 450.1655 | 457.1685 | -16.5431 | -39.9285 | 11.4762 | 8.0217 | 2.3824 | 0.9582 | 3.1901 | -1.0026 | 12.0253 | 4.9077 | 0.6212 | 0.6657 | 0.9649 | 0.7477 | -129.2092 | 1.0069 | 5.6619 | 1.8665 | -2.6391 | -1.0272 | 4.7818 |  | 3.9699 | 0.561 | 4.0115 | 3.367 | 3.3396 | 1.0849 | 10.7995 | 14.2962 | 14.8764 | 11.1349 | 0 | -0.0032 | 0.0007 | 0.0035 | 0.0006 | -0.0006 | 0.0185 | -0.0005 | -0.0107 | -360.1404 | 17.3905 | -360.4542 | 17.641 | -360.8266 | 18.2364 | -360.8666 | 17.5937 | -352.626 | 18.6963 | -352.6383 | 16.8628
12:47 | 5239 | 44.2517 | 202.5458 | 450.1067 | 457.0388 | -16.4573 | -40.0386 | 11.5016 | 8.0174 | 2.3138 | 0.918 | 3.1489 | -1.0127 | 12.0223 | 4.8721 | 0.6217 | 0.6635 | 0.9635 | 0.7476 | -129.3258 | 0.9578 | 5.5207 | 1.9 | -2.6355 | -1.0588 | 4.7116 |  | 3.9846 | 0.5911 | 4.0126 | 3.3667 | 3.3442 | 1.0872 | 10.7914 | 14.3057 | 14.8874 | 11.132 | 0.0003 | -0.0025 | 0.0008 | 0.0036 | 0.0008 | -0.0007 | 0.0195 | 0.0042 | 0.0002 | -360.2358 | 17.4397 | -360.5004 | 17.6369 | -360.8143 | 18.1892 | -360.805 | 17.5814 | -352.6937 | 18.7518 | -352.6967 | 16.8607
12:47 | 5240 | 44.3451 | 202.5962 | 450.1687 | 457.0995 | -16.4576 | -40.0359 | 11.4734 | 7.9151 | 2.1749 | 0.6426 | 3.188 | -1.0481 | 11.9715 | 4.8435 | 0.6233 | 0.6677 | 0.9637 | 0.7484 | -129.3338 | 0.9704 | 5.5165 | 1.9744 | -2.5518 | -1.128 | 4.7046 |  | 3.9659 | 0.6159 | 4.0108 | 3.3636 | 3.3419 | 1.0873 | 10.8066 | 14.3086 | 14.8814 | 11.0789 | -0.0006 | -0.0028 | 0.0004 | 0.0036 | 0.0004 | -0.0003 | 0 | 0.0015 | -0.0117 | -360.1311 | 17.3761 | -360.4666 | 17.6615 | -360.8512 | 18.2261 | -360.8389 | 17.5506 | -352.5921 | 18.7025 | -352.669 | 16.8895
12:47 | 5241 | 44.259 | 202.5332 | 450.1385 | 457.1503 | -16.5183 | -39.9932 | 11.4366 | 8.0261 | 2.2903 | 0.8139 | 3.1784 | -1.0257 | 12.0087 | 4.8491 | 0.621 | 0.6645 | 0.9643 | 0.7477 | -129.3202 | 0.9962 | 5.5725 | 1.9025 | -2.5909 | -1.0252 | 4.6576 |  | 3.8987 | 0.5593 | 4.0112 | 3.3664 | 3.3408 | 1.0864 | 10.7799 | 14.2705 | 14.8842 | 11.0695 | 0.0001 | -0.0027 | 0.0011 | 0.0045 | 0.0009 | -0.0004 | 0.0106 | -0.0103 | 0.0098 | -360.2081 | 17.4069 | -360.4204 | 17.604 | -360.7866 | 18.2118 | -360.8666 | 17.604 | -352.6752 | 18.7148 | -352.6321 | 16.8443
12:47 | 5242 | 44.3037 | 202.5635 | 450.0965 | 457.156 | -16.5344 | -40.0419 | 11.5116 | 8.0083 | 2.273 | 0.7256 | 3.1356 | -1 | 12.0612 | 4.8752 | 0.6222 | 0.6602 | 0.9608 | 0.7466 | -129.2219 | 0.9299 | 5.5986 | 2.0046 | -2.5327 | -1.0209 | 4.8336 |  | 3.8704 | 0.4965 | 4.0115 | 3.3659 | 3.3397 | 1.0875 | 10.7833 | 14.2569 | 14.843 | 11.1071 | 0.0004 | -0.0034 | 0.0008 | 0.0042 | 0.0006 | -0.0001 | 0.014 | -0.0114 | -0.0074 | -360.1004 | 17.409 | -360.4973 | 17.6533 | -360.8327 | 18.1912 | -360.7773 | 17.5404 | -352.629 | 18.7271 | -352.6813 | 16.8854
12:47 | 5243 | 44.3746 | 202.6408 | 450.1064 | 457.1197 | -16.544 | -40.0551 | 11.5667 | 8.006 | 2.2595 | 0.6484 | 3.1601 | -1.0583 | 12.0718 | 4.8705 | 0.6213 | 0.6606 | 0.9619 | 0.7476 | -129.2084 | 0.9362 | 5.5993 | 1.8833 | -2.5917 | -1.0607 | 4.7508 |  | 3.967 | 0.5572 | 4.011 | 3.3661 | 3.34 | 1.0873 | 10.7556 | 14.287 | 14.8502 | 11.0908 | 0.0001 | -0.0026 | 0.001 | 0.0047 | 0.0009 | -0.0008 | 0.0067 | 0.0008 | 0.007 | -360.1188 | 17.3679 | -360.4019 | 17.6163 | -360.8174 | 18.2467 | -360.8758 | 17.5773 | -352.6136 | 18.6902 | -352.6075 | 16.8587
12:47 | 5244 | 44.2906 | 202.5418 | 450.12 | 457.0576 | -16.5578 | -40.0015 | 11.5178 | 8.0811 | 2.3145 | 0.7275 | 3.2211 | -1.0475 | 11.9644 | 4.8243 | 0.6219 | 0.6649 | 0.9629 | 0.7482 | -129.2093 | 0.9975 | 5.6207 | 1.8871 | -2.5593 | -0.9881 | 4.7583 |  | 3.8658 | 0.6096 | 4.0112 | 3.3637 | 3.3385 | 1.0869 | 10.7937 | 14.2618 | 14.8496 | 11.111 | 0.0001 | -0.0023 | 0.001 | 0.004 | 0.0005 | -0.0003 | 0.0181 | -0.0095 | -0.0034 | -360.1773 | 17.4151 | -360.4512 | 17.604 | -360.7373 | 18.1789 | -360.7989 | 17.5691 | -352.6537 | 18.7251 | -352.6598 | 16.8402
12:47 | 5245 | 44.287 | 202.5593 | 450.1566 | 457.1321 | -16.5531 | -39.9683 | 11.5374 | 7.9955 | 2.3969 | 0.7033 | 3.1688 | -0.9383 | 12.0771 | 4.9075 | 0.6211 | 0.663 | 0.9631 | 0.7481 | -129.2611 | 0.9745 | 5.5218 | 1.8751 | -2.5719 | -1.1249 | 4.7671 |  | 3.9079 | 0.6454 | 4.0124 | 3.3703 | 3.3385 | 1.0865 | 10.7869 | 14.2948 | 14.8797 | 11.1168 | 0.0001 | -0.0027 | 0.0004 | 0.0037 | 0.0008 | -0.001 | 0.0063 | 0.007 | -0.0049 | -360.1435 | 17.3946 | -360.4512 | 17.6492 | -360.8389 | 18.1912 | -360.805 | 17.5342 | -352.5736 | 18.6963 | -352.6629 | 16.8813
12:47 | 5246 | 44.2992 | 202.5546 | 450.1071 | 457.1039 | -16.6068 | -39.9487 | 11.5239 | 8.1039 | 2.3901 | 0.5659 | 3.2562 | -0.8813 | 12.0788 | 4.9332 | 0.621 | 0.6641 | 0.9629 | 0.7486 | -129.2575 | 0.9763 | 5.6254 | 1.8901 | -2.5614 | -1.0688 | 4.7517 |  | 3.8565 | 0.6353 | 4.0111 | 3.367 | 3.3391 | 1.0871 | 10.8052 | 14.3023 | 14.8901 | 11.1226 | 0.0005 | -0.0028 | 0.0008 | 0.004 | 0.0005 | -0.0003 | 0.0095 | -0.0033 | -0.0037 | -360.1188 | 17.3638 | -360.3496 | 17.5978 | -360.7435 | 18.2159 | -360.845 | 17.5609 | -352.5798 | 18.6676 | -352.5644 | 16.834
12:47 | 5247 | 44.3531 | 202.7088 | 450.1317 | 457.2453 | -16.5121 | -39.9761 | 11.4687 | 8.0874 | 2.3767 | 0.5853 | 3.1335 | -0.8921 | 12.0253 | 4.9683 | 0.6213 | 0.6645 | 0.9625 | 0.7486 | -129.2765 | 0.9762 | 5.625 | 1.957 | -2.4905 | -0.9988 | 4.7496 |  | 3.8913 | 0.7121 | 4.0109 | 3.3654 | 3.3378 | 1.087 | 10.8052 | 14.2907 | 14.8785 | 11.1226 | 0 | -0.0027 | 0.0006 | 0.0038 | 0.0007 | -0.0004 | 0.0012 | -0.0005 | -0.008 | -360.1804 | 17.4233 | -360.4512 | 17.6081 | -360.7527 | 18.1687 | -360.7835 | 17.5527 | -352.629 | 18.7251 | -352.6567 | 16.8484
12:47 | 5248 | 44.3348 | 202.6356 | 450.1224 | 457.2011 | -16.5066 | -39.9852 | 11.4837 | 8.111 | 2.3685 | 0.7065 | 3.1559 | -0.8421 | 12.0751 | 4.9174 | 0.621 | 0.6659 | 0.9636 | 0.7464 | -129.303 | 1.0048 | 5.6039 | 1.8971 | -2.5538 | -1.0336 | 4.7199 |  | 3.8677 | 0.5922 | 4.0119 | 3.3692 | 3.3382 | 1.0861 | 10.7614 | 14.2693 | 14.8249 | 11.08 | -0.0004 | -0.0025 | 0.0006 | 0.0038 | 0.0011 | -0.0004 | 0.0153 | -0.0084 | -0.0127 | -360.0973 | 17.3699 | -360.3958 | 17.6245 | -360.7989 | 18.2056 | -360.7866 | 17.526 | -352.5367 | 18.682 | -352.6352 | 16.8607
12:47 | 5249 | 44.3595 | 202.5896 | 450.2148 | 457.1645 | -16.5009 | -39.9646 | 11.514 | 8.0571 | 2.4082 | 0.7318 | 3.1437 | -0.8416 | 12.1521 | 5.0335 | 0.6219 | 0.6664 | 0.9606 | 0.7459 | -129.251 | 1.0152 | 5.5674 | 1.941 | -2.5769 | -1.0178 | 4.7742 |  | 3.9217 | 0.5519 | 4.0106 | 3.3647 | 3.3356 | 1.0864 | 10.7984 | 14.2836 | 14.8587 | 11.0872 | -0.0004 | -0.003 | 0.0012 | 0.0044 | 0.0012 | 0.0003 | 0.0165 | -0.0085 | -0.0094 | -360.1927 | 17.3843 | -360.3742 | 17.5855 | -360.7312 | 18.1994 | -360.8266 | 17.5753 | -352.6136 | 18.7066 | -352.6044 | 16.8217
12:47 | 5250 | 44.3253 | 202.6013 | 450.1079 | 457.1762 | -16.4383 | -40.0038 | 11.5339 | 8.1125 | 2.4743 | 0.7898 | 3.0872 | -0.9188 | 12.0426 | 4.9128 | 0.6205 | 0.6667 | 0.9639 | 0.7468 | -129.2569 | 0.9689 | 5.6405 | 1.9006 | -2.5659 | -1.0882 | 4.7125 |  | 3.9048 | 0.555 | 4.0118 | 3.3666 | 3.3405 | 1.0871 | 10.7696 | 14.2541 | 14.8371 | 11.0887 | -0.0001 | -0.0031 | 0.0004 | 0.0038 | 0.0006 | -0.0009 | 0.0061 | -0.0168 | 0.0049 | -360.1311 | 17.4069 | -360.4235 | 17.6143 | -360.7866 | 18.1707 | -360.7435 | 17.5383 | -352.5983 | 18.7189 | -352.6352 | 16.8587
12:47 | 5251 | 44.2675 | 202.5612 | 450.0855 | 457.1692 | -16.4637 | -40.003 | 11.5222 | 8.1253 | 2.4723 | 0.6542 | 3.1331 | -0.9374 | 12.021 | 4.899 | 0.6202 | 0.6629 | 0.9578 | 0.7466 | -129.2668 | 0.9904 | 5.5847 | 1.9424 | -2.5602 | -1.0316 | 4.6925 |  | 3.9761 | 0.5016 | 4.0113 | 3.366 | 3.3412 | 1.088 | 10.7834 | 14.2739 | 14.8467 | 11.0847 | 0.0003 | -0.0027 | 0.001 | 0.0043 | 0.0004 | -0.0003 | 0.0054 | -0.0053 | -0.0035 | -360.0788 | 17.3638 | -360.405 | 17.6204 | -360.805 | 18.22 | -360.8266 | 17.5321 | -352.546 | 18.6902 | -352.5736 | 16.8484
12:47 | 5252 | 44.2933 | 202.5298 | 450.1552 | 457.1425 | -16.3506 | -39.9119 | 11.5857 | 8.0817 | 2.4259 | 0.6172 | 3.108 | -0.8641 | 12.0016 | 4.9432 | 0.6201 | 0.6642 | 0.9641 | 0.746 | -129.261 | 0.9472 | 5.6306 | 1.9763 | -2.6037 | -1.0859 | 4.7375 |  | 3.9122 | 0.5236 | 4.0111 | 3.3675 | 3.3404 | 1.0877 | 10.7602 | 14.2569 | 14.8257 | 11.084 | -0.0001 | -0.0025 | 0.0008 | 0.0036 | 0.0012 | -0.0004 | 0.0074 | 0.0007 | -0.017 | -360.1742 | 17.3864 | -360.405 | 17.5917 | -360.7035 | 18.1789 | -360.7866 | 17.5609 | -352.6167 | 18.7169 | -352.6075 | 16.8197
12:47 | 5253 | 44.3117 | 202.5586 | 450.1483 | 457.1393 | -16.4086 | -39.9878 | 11.5576 | 8.1231 | 2.4462 | 0.6637 | 3.1483 | -0.903 | 12.0135 | 4.9546 | 0.6206 | 0.6637 | 0.9643 | 0.7461 | -129.135 | 0.9668 | 5.6707 | 1.9094 | -2.6427 | -1.071 | 4.7653 |  | 3.901 | 0.5782 | 4.0106 | 3.3641 | 3.3364 | 1.0855 | 10.7614 | 14.2751 | 14.8249 | 11.1089 | 0 | -0.0024 | 0.0002 | 0.0033 | 0.0003 | -0.0007 | 0.021 | -0.0036 | 0.0164 | -360.1496 | 17.372 | -360.4389 | 17.6328 | -360.805 | 18.1994 | -360.7958 | 17.528 | -352.5675 | 18.7004 | -352.6229 | 16.8587
12:47 | 5254 | 44.3823 | 202.5576 | 450.2183 | 457.2314 | -16.4446 | -39.9734 | 11.5222 | 8.0266 | 2.4117 | 0.6796 | 3.0646 | -0.9042 | 11.9649 | 4.8075 | 0.6205 | 0.6645 | 0.9587 | 0.7451 | -129.2532 | 0.9873 | 5.5801 | 1.9776 | -2.5484 | -0.9542 | 4.8136 |  | 3.8607 | 0.6017 | 4.0101 | 3.3636 | 3.3407 | 1.0852 | 10.7661 | 14.2624 | 14.8467 | 11.1078 | 0.0004 | -0.0029 | 0.0007 | 0.0038 | 0.0012 | -0.0007 | 0.0261 | -0.0086 | -0.0104 | -360.1588 | 17.3802 | -360.3865 | 17.5917 | -360.7527 | 18.1953 | -360.8235 | 17.5568 | -352.6013 | 18.6922 | -352.5798 | 16.834
12:47 | 5255 | 44.3803 | 202.5641 | 450.1725 | 457.173 | -16.4976 | -40.1048 | 11.387 | 8.0384 | 2.4431 | 0.6472 | 3.1324 | -0.847 | 11.9377 | 4.8662 | 0.621 | 0.6673 | 0.9615 | 0.7461 | -129.3054 | 0.9772 | 5.5055 | 2.0523 | -2.6144 | -0.9977 | 4.8347 |  | 3.9234 | 0.7907 | 4.0136 | 3.3684 | 3.3459 | 1.0884 | 10.8261 | 14.3058 | 14.8769 | 11.0969 | 0 | -0.003 | 0.0005 | 0.0036 | 0.0009 | 0.0003 | 0.0151 | -0.0022 | 0.011 | -360.1373 | 17.3925 | -360.4235 | 17.6225 | -360.7989 | 18.181 | -360.7804 | 17.5424 | -352.5552 | 18.7107 | -352.626 | 16.8505
12:47 | 5256 | 44.3214 | 202.5717 | 450.1696 | 457.1724 | -16.4859 | -39.9278 | 11.4884 | 8.0035 | 2.3942 | 0.5577 | 3.0713 | -0.9405 | 11.8738 | 4.8506 | 0.6218 | 0.6627 | 0.9623 | 0.7484 | -129.2824 | 0.9418 | 5.5206 | 1.997 | -2.6112 | -1.0152 | 4.8018 |  | 3.9456 | 0.7259 | 4.0107 | 3.3675 | 3.3413 | 1.0862 | 10.7893 | 14.2796 | 14.8398 | 11.0793 | -0.0004 | -0.0028 | 0.0007 | 0.0038 | 0.0008 | -0.0007 | 0.0152 | -0.002 | -0.0156 | -360.1558 | 17.3884 | -360.4019 | 17.6102 | -360.7712 | 18.2015 | -360.7835 | 17.5547 | -352.5583 | 18.6943 | -352.6013 | 16.8423
12:47 | 5257 | 44.3436 | 202.51 | 450.1624 | 457.078 | -16.4441 | -39.9399 | 11.5649 | 8.0276 | 2.4582 | 0.6717 | 3.1251 | -0.8912 | 11.9476 | 4.8723 | 0.6213 | 0.6623 | 0.9628 | 0.7476 | -129.232 | 1.0415 | 5.5234 | 1.9034 | -2.6243 | -0.9757 | 4.8035 |  | 3.9386 | 0.7102 | 4.009 | 3.3667 | 3.3395 | 1.0868 | 10.8065 | 14.2858 | 14.872 | 11.0897 | -0.0004 | -0.0026 | 0.001 | 0.0043 | 0.0007 | -0.0001 | 0.0123 | -0.0023 | -0.0017 | -360.1588 | 17.3864 | -360.4327 | 17.602 | -360.765 | 18.2036 | -360.8174 | 17.5547 | -352.5983 | 18.7148 | -352.6106 | 16.8279
12:47 | 5258 | 44.3121 | 202.447 | 450.0627 | 457.1205 | -16.4601 | -40.039 | 11.4922 | 7.9821 | 2.4406 | 0.4954 | 3.1385 | -0.8377 | 12.0311 | 4.9514 | 0.6212 | 0.6631 | 0.9624 | 0.7467 | -129.2928 | 0.9817 | 5.6092 | 1.9302 | -2.6014 | -0.9447 | 4.7812 |  | 3.9594 | 0.6034 | 4.0102 | 3.3647 | 3.3379 | 1.0865 | 10.811 | 14.2965 | 14.8727 | 11.1226 | 0.0001 | -0.0028 | 0.0006 | 0.0037 | 0.0008 | -0.0008 | 0.0073 | -0.0092 | -0.0026 | -360.1804 | 17.4069 | -360.4358 | 17.6143 | -360.7804 | 18.2015 | -360.7989 | 17.5588 | -352.5829 | 18.7045 | -352.589 | 16.8381
12:47 | 5259 | 44.3715 | 202.4684 | 450.1541 | 457.079 | -16.3757 | -39.9918 | 11.5609 | 7.9812 | 2.4575 | 0.5455 | 3.1813 | -0.8729 | 12.0106 | 4.8724 | 0.621 | 0.6647 | 0.9619 | 0.7466 | -129.2795 | 1.0377 | 5.624 | 1.8846 | -2.6207 | -0.9705 | 4.8236 |  | 3.8816 | 0.4373 | 4.0124 | 3.3631 | 3.3403 | 1.0874 | 10.7788 | 14.2576 | 14.8296 | 11.1093 | 0.0002 | -0.0031 | 0.0006 | 0.0041 | 0.0006 | -0.0007 | 0.0276 | -0.0144 | 0.0099 | -360.1835 | 17.4007 | -360.4296 | 17.6307 | -360.7958 | 18.2015 | -360.8327 | 17.5527 | -352.5798 | 18.7169 | -352.626 | 16.8423
12:47 | 5260 | 44.45 | 202.4896 | 450.1213 | 457.1263 | -16.453 | -39.8584 | 11.5469 | 7.9621 | 2.3402 | 0.533 | 3.1407 | -0.938 | 11.98 | 4.9002 | 0.6221 | 0.6623 | 0.9628 | 0.7483 | -129.2552 | 0.9484 | 5.5654 | 1.9097 | -2.5632 | -0.9505 | 4.7616 |  | 3.8237 | 0.4757 | 4.0106 | 3.3677 | 3.3362 | 1.0867 | 10.7914 | 14.2824 | 14.8458 | 11.115 | -0.0001 | -0.0028 | 0.001 | 0.0039 | 0.001 | -0.0003 | 0.0165 | -0.006 | -0.0103 | -360.1958 | 17.4007 | -360.445 | 17.6143 | -360.7773 | 18.2077 | -360.8235 | 17.5609 | -352.6075 | 18.7107 | -352.6198 | 16.834
12:47 | 5261 | 44.4087 | 202.5694 | 450.1577 | 457.0976 | -16.3737 | -39.9165 | 11.4906 | 7.9878 | 2.396 | 0.6032 | 3.1381 | -1.0813 | 11.8815 | 4.8272 | 0.6208 | 0.6617 | 0.9618 | 0.7481 | -129.1681 | 0.9781 | 5.5696 | 1.8422 | -2.6437 | -1.0237 | 4.7145 |  | 3.8964 | 0.4959 | 4.0108 | 3.3682 | 3.3398 | 1.0864 | 10.7846 | 14.2693 | 14.8365 | 11.1031 | 0 | -0.0026 | 0.0004 | 0.0034 | 0.001 | -0.0006 | 0.02 | -0.0087 | -0.0129 | -360.1896 | 17.4131 | -360.4296 | 17.6389 | -360.8235 | 18.1912 | -360.802 | 17.5465 | -352.5952 | 18.7251 | -352.6321 | 16.8525
12:47 | 5262 | 44.3986 | 202.5915 | 450.1285 | 457.0434 | -16.3652 | -39.9609 | 11.486 | 8.0298 | 2.4208 | 0.7104 | 3.178 | -0.9639 | 12.0387 | 4.943 | 0.6211 | 0.666 | 0.964 | 0.7478 | -129.1309 | 0.8601 | 5.587 | 1.9017 | -2.6567 | -1.0671 | 4.7961 |  | 3.9044 | 0.5797 | 4.0102 | 3.369 | 3.3355 | 1.0857 | 10.788 | 14.2498 | 14.8232 | 11.1006 | 0 | -0.0029 | 0.0009 | 0.004 | 0.0008 | -0.0002 | 0.0065 | 0.0006 | 0.0044 | -360.1896 | 17.3987 | -360.4296 | 17.6286 | -360.8358 | 18.2179 | -360.8358 | 17.5609 | -352.6044 | 18.7107 | -352.6167 | 16.8443
12:47 | 5263 | 44.3872 | 202.607 | 450.211 | 457.0274 | -16.3901 | -40.0055 | 11.478 | 8.0166 | 2.4626 | 0.7963 | 3.1881 | -0.9453 | 11.9031 | 4.8947 | 0.6219 | 0.6673 | 0.9608 | 0.7482 | -129.158 | 0.937 | 5.6051 | 1.8477 | -2.6149 | -1.0526 | 4.8342 |  | 3.9314 | 0.5037 | 4.0097 | 3.3634 | 3.3388 | 1.0869 | 10.781 | 14.2893 | 14.8529 | 11.0872 | 0.0001 | -0.003 | 0.0009 | 0.0041 | 0.0008 | -0.0006 | 0.0067 | 0.0047 | -0.0059 | -360.2142 | 17.4274 | -360.4696 | 17.6122 | -360.805 | 18.2097 | -360.8327 | 17.5814 | -352.6444 | 18.7415 | -352.6537 | 16.8279
12:47 | 5264 | 44.3897 | 202.6865 | 450.2341 | 457.0126 | -16.3611 | -40.0652 | 11.5096 | 7.9721 | 2.376 | 0.7573 | 3.1086 | -0.9373 | 11.9452 | 4.84 | 0.6223 | 0.6668 | 0.9654 | 0.749 | -129.1681 | 0.9222 | 5.6586 | 1.931 | -2.6422 | -1.0994 | 4.7964 |  | 3.9064 | 0.5414 | 4.01 | 3.3723 | 3.341 | 1.0864 | 10.7973 | 14.2994 | 14.8494 | 11.0869 | -0.0007 | -0.0031 | 0.0006 | 0.0042 | 0.0007 | -0.0001 | 0.0053 | 0.0061 | -0.006 | -360.1711 | 17.4213 | -360.5219 | 17.6718 | -360.8574 | 18.2241 | -360.8266 | 17.5568 | -352.6044 | 18.7415 | -352.6844 | 16.8751
12:47 | 5265 | 44.4825 | 202.6051 | 450.2012 | 456.9788 | -16.4547 | -40.0741 | 11.5081 | 7.9501 | 2.4305 | 0.5854 | 3.1025 | -0.9535 | 12.0006 | 4.8969 | 0.6209 | 0.6632 | 0.9625 | 0.7497 | -129.1954 | 0.9735 | 5.7108 | 1.8766 | -2.7037 | -1.0243 | 4.7979 |  | 3.9933 | 0.549 | 4.012 | 3.3655 | 3.3392 | 1.0885 | 10.8052 | 14.314 | 14.8796 | 11.128 | 0 | -0.0021 | 0.0014 | 0.0048 | 0.0016 | -0.0004 | 0.0111 | -0.0072 | -0.0039 | -360.2019 | 17.3966 | -360.4142 | 17.6286 | -360.8266 | 18.2282 | -360.8697 | 17.5835 | -352.6475 | 18.721 | -352.5798 | 16.8443
12:47 | 5266 | 44.307 | 202.5961 | 450.088 | 456.917 | -16.3771 | -40.0381 | 11.6372 | 7.9184 | 2.2873 | 0.4811 | 3.114 | -1.035 | 12.0016 | 4.8896 | 0.6211 | 0.6662 | 0.9596 | 0.749 | -129.2562 | 0.9986 | 5.6503 | 2.0188 | -2.6317 | -0.9473 | 4.8468 |  | 3.9598 | 0.4873 | 4.0094 | 3.3673 | 3.3386 | 1.0883 | 10.7694 | 14.3009 | 14.8529 | 11.1103 | -0.0001 | -0.0029 | 0.0008 | 0.0041 | 0.0004 | -0.0001 | 0.0198 | -0.0016 | -0.002 | -360.2111 | 17.4459 | -360.5004 | 17.6307 | -360.7958 | 18.2036 | -360.8235 | 17.5855 | -352.6813 | 18.7661 | -352.6567 | 16.8546
12:47 | 5267 | 44.3938 | 202.5859 | 449.9849 | 456.9923 | -16.4074 | -40.0459 | 11.5776 | 8.0457 | 2.4427 | 0.672 | 3.1601 | -0.9922 | 12.0037 | 4.959 | 0.6202 | 0.667 | 0.9605 | 0.7494 | -129.2375 | 1.0045 | 5.5881 | 1.9805 | -2.6143 | -0.9378 | 4.8142 |  | 3.9806 | 0.6213 | 4.0103 | 3.3665 | 3.3399 | 1.0867 | 10.8169 | 14.2963 | 14.8833 | 11.1403 | 0 | -0.0032 | 0.0004 | 0.0039 | 0.0015 | -0.0003 | 0.0059 | -0.018 | -0.002 | -360.1188 | 17.3905 | -360.4666 | 17.6492 | -360.8297 | 18.2405 | -360.8512 | 17.5486 | -352.6229 | 18.721 | -352.6752 | 16.8689
12:48 | 5268 | 44.435 | 202.611 | 450.1407 | 456.8993 | -16.4621 | -40.0041 | 11.5667 | 8.0805 | 2.3851 | 0.6962 | 3.1675 | -0.97 | 11.9584 | 4.8555 | 0.6205 | 0.664 | 0.962 | 0.7486 | -129.2359 | 0.948 | 5.5256 | 2.0954 | -2.6777 | -0.9872 | 4.8208 |  | 3.9669 | 0.5759 | 4.0102 | 3.371 | 3.3409 | 1.0876 | 10.7995 | 14.2502 | 14.8554 | 11.1168 | 0.0003 | -0.0028 | 0.0011 | 0.0039 | 0.0007 | -0.0004 | 0.0091 | -0.0057 | 0.0003 | -360.1711 | 17.409 | -360.4327 | 17.602 | -360.7773 | 18.22 | -360.8697 | 17.5855 | -352.6629 | 18.7292 | -352.6044 | 16.8258
12:48 | 5269 | 44.4082 | 202.6177 | 450.1203 | 456.9258 | -16.4466 | -40.0066 | 11.5138 | 8.0485 | 2.3294 | 0.6316 | 3.0466 | -1.0428 | 12.031 | 4.9086 | 0.6189 | 0.6642 | 0.9607 | 0.7486 | -129.3029 | 0.9732 | 5.6214 | 2.0485 | -2.6567 | -0.9736 | 4.8419 |  | 4.0381 | 0.6568 | 4.0101 | 3.3688 | 3.3385 | 1.0877 | 10.8111 | 14.3135 | 14.888 | 11.106 | -0.0001 | -0.0028 | 0.0007 | 0.0034 | 0.001 | -0.0006 | -0.0011 | 0.0015 | 0.0036 | -360.165 | 17.4151 | -360.4604 | 17.6389 | -360.8174 | 18.1933 | -360.765 | 17.5383 | -352.6075 | 18.7353 | -352.6998 | 16.8648
12:48 | 5270 | 44.4583 | 202.5918 | 450.236 | 456.9713 | -16.4329 | -39.9731 | 11.5007 | 8.0384 | 2.3361 | 0.6615 | 3.0776 | -1.0517 | 11.9737 | 4.88 | 0.6221 | 0.6687 | 0.96 | 0.7477 | -129.1828 | 0.9975 | 5.6355 | 2.1008 | -2.619 | -1.0336 | 4.8532 |  | 4.0058 | 0.6442 | 4.01 | 3.3658 | 3.3377 | 1.0868 | 10.7511 | 14.2646 | 14.8194 | 11.093 | 0.0004 | -0.0027 | 0.0009 | 0.0043 | 0.0006 | -0.0006 | 0.0158 | -0.0166 | -0.015 | -360.1465 | 17.3679 | -360.3742 | 17.6102 | -360.8112 | 18.2261 | -360.8604 | 17.5588 | -352.5921 | 18.6963 | -352.5952 | 16.8361
12:48 | 5271 | 44.4561 | 202.6137 | 450.0776 | 456.9973 | -16.4429 | -40.0184 | 11.5332 | 7.9926 | 2.2837 | 0.6669 | 3.0822 | -1.0588 | 12.0155 | 4.9586 | 0.621 | 0.666 | 0.9636 | 0.7495 | -129.2128 | 1.0203 | 5.6091 | 2.1177 | -2.6234 | -0.902 | 4.8696 |  | 4.0136 | 0.8002 | 4.0096 | 3.3645 | 3.3414 | 1.0879 | 10.7695 | 14.2717 | 14.8219 | 11.0937 | 0.0004 | -0.003 | 0.001 | 0.004 | 0.0009 | -0.0003 | 0.0077 | 0.0072 | 0.001 | -360.205 | 17.4131 | -360.4296 | 17.5917 | -360.7066 | 18.181 | -360.805 | 17.5609 | -352.629 | 18.7353 | -352.626 | 16.8176
12:48 | 5272 | 44.3886 | 202.6528 | 450.1065 | 456.8921 | -16.4196 | -39.9281 | 11.5655 | 7.9846 | 2.4051 | 0.6051 | 3.1296 | -0.9788 | 12.0604 | 4.9733 | 0.6222 | 0.6673 | 0.9619 | 0.7482 | -129.2124 | 1.0089 | 5.6426 | 2.0476 | -2.6929 | -0.918 | 4.8522 |  | 3.9943 | 0.7771 | 4.0105 | 3.3677 | 3.3407 | 1.0879 | 10.7846 | 14.2925 | 14.8481 | 11.08 | -0.0002 | -0.0028 | 0.0007 | 0.0041 | 0.0009 | -0.0005 | 0.0019 | -0.009 | -0.0117 | -360.0911 | 17.3761 | -360.445 | 17.6307 | -360.8112 | 18.2097 | -360.7712 | 17.5157 | -352.5675 | 18.7025 | -352.6413 | 16.8587
12:48 | 5273 | 44.419 | 202.697 | 450.0629 | 456.9084 | -16.4311 | -39.8991 | 11.5235 | 8.0589 | 2.4892 | 0.6918 | 3.2275 | -1.0157 | 11.9218 | 4.9183 | 0.6208 | 0.6667 | 0.9604 | 0.7485 | -129.2285 | 1.0611 | 5.6259 | 1.979 | -2.6539 | -0.9626 | 4.8723 |  | 4.0896 | 0.7899 | 4.0097 | 3.3661 | 3.3416 | 1.0886 | 10.7684 | 14.2763 | 14.8436 | 11.0927 | -0.0006 | -0.0026 | 0.0012 | 0.0043 | 0.0006 | -0.0002 | 0.0157 | 0.0012 | -0.0093 | -360.1527 | 17.3782 | -360.365 | 17.5835 | -360.7589 | 18.1912 | -360.8266 | 17.5712 | -352.6352 | 18.6984 | -352.5829 | 16.8012
12:48 | 5274 | 44.3922 | 202.6731 | 450.041 | 456.8808 | -16.5195 | -39.9625 | 11.5383 | 8.1588 | 2.4668 | 0.7984 | 3.1454 | -1.0544 | 11.9482 | 4.8584 | 0.6208 | 0.6676 | 0.9622 | 0.7493 | -129.1563 | 0.9787 | 5.5533 | 1.9772 | -2.7111 | -0.9963 | 4.8331 |  | 3.9831 | 0.8398 | 4.0114 | 3.3669 | 3.3377 | 1.087 | 10.8064 | 14.3034 | 14.8625 | 11.1237 | 0.0001 | -0.0023 | 0.001 | 0.0043 | 0.0013 | 0 | 0.0131 | -0.0153 | -0.0166 | -360.1373 | 17.411 | -360.4727 | 17.6245 | -360.7743 | 18.1666 | -360.7404 | 17.526 | -352.5829 | 18.7271 | -352.6413 | 16.8443
12:48 | 5275 | 44.3547 | 202.6008 | 450.1353 | 456.9594 | -16.3941 | -39.9796 | 11.6143 | 8.0199 | 2.4307 | 0.6945 | 3.1254 | -1.0141 | 11.996 | 4.9396 | 0.6224 | 0.6657 | 0.9624 | 0.7492 | -129.1634 | 0.9505 | 5.4848 | 1.9679 | -2.7886 | -1.0683 | 4.7469 |  | 4.0064 | 0.8781 | 4.0112 | 3.3716 | 3.3395 | 1.0882 | 10.7914 | 14.2882 | 14.84 | 11.0977 | 0.0003 | -0.003 | 0.001 | 0.0035 | 0.0007 | -0.0004 | 0.0065 | -0.0031 | -0.0214 | -360.1004 | 17.372 | -360.3681 | 17.6307 | -360.8235 | 18.2159 | -360.8481 | 17.5506 | -352.5706 | 18.684 | -352.5583 | 16.8279
12:48 | 5276 | 44.3799 | 202.6705 | 450.1496 | 456.9861 | -16.4626 | -40.0287 | 11.5931 | 8.0227 | 2.4391 | 0.7536 | 3.1187 | -1.0126 | 11.9747 | 4.8235 | 0.621 | 0.6638 | 0.9623 | 0.7489 | -129.1785 | 0.9431 | 5.5205 | 2.0286 | -2.7055 | -1.0051 | 4.7418 |  | 4.0245 | 0.8099 | 4.0103 | 3.3649 | 3.339 | 1.0863 | 10.7638 | 14.2772 | 14.8255 | 11.0656 | -0.0004 | -0.0031 | 0.0004 | 0.0038 | 0.0008 | -0.0006 | 0.0264 | -0.0022 | -0.0063 | -360.1804 | 17.411 | -360.4296 | 17.5978 | -360.7312 | 18.1728 | -360.8143 | 17.5732 | -352.6413 | 18.7292 | -352.6013 | 16.8074
12:48 | 5277 | 44.5295 | 202.6244 | 450.1812 | 457.0177 | -16.5272 | -39.9336 | 11.5409 | 8.0477 | 2.4204 | 0.6388 | 3.1973 | -1.0068 | 11.9199 | 4.917 | 0.6204 | 0.6651 | 0.9645 | 0.7502 | -129.2289 | 0.9096 | 5.4818 | 1.9561 | -2.7778 | -1.1727 | 4.7342 |  | 4.0477 | 0.767 | 4.0123 | 3.3701 | 3.3414 | 1.0881 | 10.8204 | 14.2997 | 14.8921 | 11.1208 | -0.0004 | -0.0028 | 0.0007 | 0.0035 | 0.0006 | -0.0004 | 0.0012 | -0.0049 | -0.0033 | -360.1311 | 17.4007 | -360.485 | 17.6574 | -360.8604 | 18.2097 | -360.7804 | 17.5301 | -352.586 | 18.7128 | -352.6906 | 16.8587
12:48 | 5278 | 44.4773 | 202.6512 | 450.1501 | 456.9429 | -16.4787 | -39.9543 | 11.5217 | 8.0644 | 2.4635 | 0.6902 | 3.2128 | -0.9425 | 11.9285 | 4.8797 | 0.6218 | 0.6637 | 0.9613 | 0.7483 | -129.1543 | 0.9069 | 5.5653 | 1.9636 | -2.6781 | -0.9723 | 4.8289 |  | 4.0488 | 0.7391 | 4.0123 | 3.3685 | 3.3455 | 1.0882 | 10.8078 | 14.269 | 14.817 | 11.0808 | -0.0005 | -0.0029 | 0.0007 | 0.0039 | 0.0007 | -0.0012 | -0.0021 | 0.0076 | -0.0111 | -360.1588 | 17.3905 | -360.4019 | 17.5999 | -360.7989 | 18.2282 | -360.8943 | 17.5896 | -352.6352 | 18.7107 | -352.5644 | 16.8053
12:48 | 5279 | 44.484 | 202.6384 | 450.2612 | 456.9391 | -16.502 | -39.8994 | 11.5697 | 8.0929 | 2.4709 | 0.7053 | 3.1602 | -1.0983 | 11.8459 | 4.8798 | 0.621 | 0.6666 | 0.9665 | 0.7501 | -129.1905 | 0.9555 | 5.4538 | 1.9557 | -2.7329 | -0.9754 | 4.738 |  | 4.106 | 0.664 | 4.0125 | 3.368 | 3.3413 | 1.0869 | 10.7707 | 14.2671 | 14.8406 | 11.0833 | 0.0002 | -0.0029 | 0.0014 | 0.0044 | 0.0008 | -0.0001 | -0.0003 | -0.0187 | -0.0121 | -360.1927 | 17.4521 | -360.5127 | 17.6574 | -360.8174 | 18.1974 | -360.845 | 17.5609 | -352.6598 | 18.76 | -352.6752 | 16.8505
12:48 | 5280 | 44.4114 | 202.5263 | 450.2218 | 457.0026 | -16.4142 | -39.9055 | 11.5501 | 8.077 | 2.4772 | 0.7042 | 3.1624 | -1.0521 | 11.9109 | 4.9032 | 0.6194 | 0.6661 | 0.9632 | 0.7488 | -129.2293 | 0.9772 | 5.5346 | 2.0327 | -2.642 | -0.8769 | 4.8602 |  | 4.0832 | 0.727 | 4.0102 | 3.3694 | 3.3378 | 1.0868 | 10.7914 | 14.2708 | 14.8458 | 11.1092 | 0.0002 | -0.0029 | 0.0009 | 0.0041 | 0.0013 | -0.0008 | 0.0282 | -0.0237 | -0.0124 | -360.1373 | 17.3864 | -360.4389 | 17.6594 | -360.8635 | 18.2487 | -360.8727 | 17.5609 | -352.5952 | 18.7189 | -352.6413 | 16.8566
12:48 | 5281 | 44.4227 | 202.5581 | 450.1621 | 456.9657 | -16.5092 | -39.8907 | 11.5074 | 8.1129 | 2.4345 | 0.582 | 3.1489 | -1.0229 | 11.9214 | 4.9894 | 0.6209 | 0.6625 | 0.9618 | 0.7477 | -129.2076 | 0.9448 | 5.5655 | 2.0148 | -2.7154 | -0.9363 | 4.8509 |  | 4.0778 | 0.7287 | 4.012 | 3.3662 | 3.3376 | 1.0875 | 10.7961 | 14.2754 | 14.8386 | 11.1024 | -0.0008 | -0.003 | 0.0012 | 0.0047 | 0.0005 | -0.0005 | 0.0129 | -0.0128 | -0.0073 | -360.2265 | 17.4274 | -360.4635 | 17.6266 | -360.7897 | 18.2179 | -360.885 | 17.5999 | -352.6906 | 18.7436 | -352.6444 | 16.832
12:48 | 5282 | 44.3417 | 202.5814 | 450.0908 | 456.9033 | -16.4651 | -39.8171 | 11.5434 | 8.0554 | 2.4058 | 0.6886 | 3.0447 | -1.102 | 11.8998 | 4.9067 | 0.6198 | 0.662 | 0.9633 | 0.7486 | -129.214 | 1.0272 | 5.5116 | 1.9487 | -2.6872 | -0.9503 | 4.7176 |  | 4.0015 | 0.732 | 4.0104 | 3.3677 | 3.338 | 1.0872 | 10.7958 | 14.2993 | 14.8845 | 11.1294 | 0.0002 | -0.0025 | 0.0009 | 0.0041 | 0.0013 | 0.0001 | 0.0068 | -0.0006 | -0.0097 | -360.1804 | 17.4315 | -360.485 | 17.6779 | -360.842 | 18.2056 | -360.802 | 17.5506 | -352.6321 | 18.7538 | -352.7121 | 16.8669
12:48 | 5283 | 44.4548 | 202.678 | 450.0941 | 457.0236 | -16.5351 | -39.8087 | 11.5364 | 8.0769 | 2.4215 | 0.7225 | 3.0574 | -1.0933 | 11.8103 | 4.8297 | 0.6204 | 0.6656 | 0.9638 | 0.747 | -129.2269 | 0.9762 | 5.5334 | 1.7971 | -2.6846 | -1.0404 | 4.7906 |  | 3.9274 | 0.6872 | 4.0096 | 3.3686 | 3.3376 | 1.0871 | 10.8041 | 14.3011 | 14.8829 | 11.1157 | -0.0002 | -0.0033 | 0.0005 | 0.0037 | 0.0013 | -0.0002 | 0.0226 | -0.0116 | 0.0047 | -360.1681 | 17.3802 | -360.3958 | 17.6389 | -360.8327 | 18.2549 | -360.885 | 17.5773 | -352.6444 | 18.7087 | -352.6167 | 16.8443
12:48 | 5284 | 44.4651 | 202.6901 | 450.0598 | 456.9692 | -16.5455 | -39.8818 | 11.4363 | 8.0928 | 2.5167 | 0.7932 | 3.1539 | -1.1714 | 11.8931 | 4.8089 | 0.6204 | 0.663 | 0.9603 | 0.7481 | -129.1816 | 1.0528 | 5.5491 | 1.8075 | -2.7453 | -1.0106 | 4.7998 |  | 3.989 | 0.6179 | 4.0096 | 3.3636 | 3.3377 | 1.0869 | 10.7789 | 14.2517 | 14.8459 | 11.0692 | -0.0002 | -0.003 | 0.0006 | 0.0036 | 0.0004 | -0.0005 | 0.0065 | -0.0071 | -0.0026 | -360.1896 | 17.4213 | -360.445 | 17.6225 | -360.7435 | 18.1892 | -360.8358 | 17.5712 | -352.6537 | 18.7559 | -352.6567 | 16.8217
12:48 | 5285 | 44.5729 | 202.6752 | 450.1125 | 457.0687 | -16.6062 | -40.0273 | 11.2871 | 8.0859 | 2.5083 | 0.7639 | 3.128 | -1.0923 | 11.8901 | 4.9042 | 0.6208 | 0.6652 | 0.9627 | 0.7488 | -129.2654 | 1.0239 | 5.6069 | 1.9066 | -2.7053 | -1.0601 | 4.7437 |  | 3.9223 | 0.6808 | 4.0106 | 3.3644 | 3.3375 | 1.0883 | 10.7695 | 14.2661 | 14.8403 | 11.0587 | -0.0003 | -0.0028 | 0.0009 | 0.0041 | 0.0008 | -0.0007 | 0.0188 | 0.0104 | -0.0019 | -360.085 | 17.3925 | -360.4573 | 17.6636 | -360.8512 | 18.2077 | -360.7897 | 17.5363 | -352.5952 | 18.7148 | -352.6475 | 16.8566
12:48 | 5286 | 44.6567 | 202.6897 | 450.1303 | 457.0651 | -16.5208 | -39.8942 | 11.3908 | 8.0134 | 2.4925 | 0.6679 | 3.1391 | -1.157 | 11.7956 | 4.726 | 0.6207 | 0.667 | 0.9621 | 0.7488 | -129.3487 | 0.9818 | 5.4826 | 1.878 | -2.7223 | -1.005 | 4.7756 |  | 4.0352 | 0.6647 | 4.0115 | 3.3661 | 3.3442 | 1.0875 | 10.7569 | 14.2529 | 14.8473 | 11.0703 | -0.0001 | -0.0026 | 0.0004 | 0.004 | 0.0001 | -0.0005 | 0.0179 | -0.0088 | -0.0097 | -360.1281 | 17.3658 | -360.3527 | 17.6081 | -360.762 | 18.2118 | -360.845 | 17.565 | -352.6013 | 18.6943 | -352.5706 | 16.8074
12:48 | 5287 | 44.5205 | 202.7116 | 450.1016 | 457.0098 | -16.5167 | -39.8805 | 11.3963 | 7.9901 | 2.4083 | 0.6753 | 3.1156 | -1.1913 | 11.9394 | 4.921 | 0.6217 | 0.6661 | 0.9614 | 0.7477 | -129.3087 | 1.0109 | 5.608 | 1.861 | -2.6562 | -1.0737 | 4.744 |  | 3.9876 | 0.6774 | 4.011 | 3.3668 | 3.3376 | 1.0868 | 10.7579 | 14.2544 | 14.8277 | 11.0706 | 0.0003 | -0.0031 | 0.0009 | 0.0038 | 0.0013 | -0.0008 | 0.0059 | -0.0125 | -0.0147 | -360.1681 | 17.4254 | -360.445 | 17.6328 | -360.762 | 18.1666 | -360.7773 | 17.5465 | -352.6198 | 18.7415 | -352.6444 | 16.8238
12:48 | 5288 | 44.5049 | 202.7285 | 450.1409 | 456.9499 | -16.4997 | -39.9086 | 11.3668 | 8.0256 | 2.4151 | 0.7478 | 3.1049 | -1.0513 | 11.9594 | 5.0128 | 0.6203 | 0.6691 | 0.9648 | 0.7481 | -129.205 | 1.1164 | 5.5994 | 1.9234 | -2.687 | -1.0433 | 4.7817 |  | 3.9464 | 0.6509 | 4.0094 | 3.3678 | 3.3401 | 1.088 | 10.8088 | 14.2822 | 14.8679 | 11.0865 | 0.0003 | -0.0031 | 0.0006 | 0.004 | 0.0005 | -0.0004 | 0.0138 | -0.0069 | -0.003 | -360.0911 | 17.372 | -360.4142 | 17.6348 | -360.8143 | 18.2118 | -360.7866 | 17.528 | -352.5367 | 18.6943 | -352.626 | 16.8464
12:48 | 5289 | 44.62 | 202.7464 | 450.0939 | 457.0478 | -16.496 | -39.9175 | 11.327 | 7.9614 | 2.416 | 0.6591 | 3.1285 | -0.961 | 11.905 | 4.8721 | 0.6202 | 0.6634 | 0.9598 | 0.7488 | -129.2175 | 0.9827 | 5.5554 | 1.9501 | -2.6679 | -1.0795 | 4.7643 |  | 3.9486 | 0.6519 | 4.0095 | 3.3663 | 3.3417 | 1.0878 | 10.8007 | 14.3033 | 14.8615 | 11.1125 | 0.0002 | -0.0023 | 0.0007 | 0.0041 | 0.0009 | -0.0005 | 0.0078 | -0.0143 | -0.0155 | -360.1342 | 17.3823 | -360.3773 | 17.6122 | -360.762 | 18.2056 | -360.845 | 17.565 | -352.626 | 18.7025 | -352.5675 | 16.8074
12:48 | 5290 | 44.5656 | 202.6974 | 450.1317 | 456.9872 | -16.4738 | -39.9004 | 11.4663 | 8.0364 | 2.4165 | 0.6484 | 3.1542 | -0.9208 | 11.9871 | 4.8969 | 0.6208 | 0.6644 | 0.9664 | 0.7482 | -129.2177 | 1.1403 | 5.5636 | 1.9517 | -2.6538 | -1 | 4.8299 |  | 3.989 | 0.6999 | 4.0087 | 3.3675 | 3.3401 | 1.0876 | 10.7855 | 14.3058 | 14.8537 | 11.1085 | 0 | -0.0023 | 0.0013 | 0.0041 | 0.0004 | -0.0002 | 0.0206 | 0.0037 | -0.0192 | -360.1527 | 17.4213 | -360.4789 | 17.6307 | -360.7958 | 18.1728 | -360.7743 | 17.5342 | -352.6044 | 18.7251 | -352.6383 | 16.8402
12:48 | 5291 | 44.476 | 202.5873 | 450.0206 | 456.8917 | -16.5286 | -39.8797 | 11.4275 | 8.0379 | 2.4309 | 0.637 | 3.0961 | -1.0062 | 11.8725 | 4.8784 | 0.619 | 0.6664 | 0.9644 | 0.7486 | -129.2188 | 1.0511 | 5.5927 | 1.9939 | -2.6205 | -1.0359 | 4.812 |  | 3.9488 | 0.6884 | 4.0092 | 3.3677 | 3.3402 | 1.087 | 10.8007 | 14.3031 | 14.9067 | 11.1071 | 0.0002 | -0.0028 | 0.0006 | 0.0039 | 0.0006 | -0.0008 | 0.0245 | -0.0239 | 0.0035 | -360.1373 | 17.3761 | -360.4142 | 17.6348 | -360.8327 | 18.2097 | -360.8235 | 17.5404 | -352.586 | 18.7004 | -352.5829 | 16.832
12:48 | 5292 | 44.4673 | 202.6564 | 450.1061 | 456.9948 | -16.5353 | -39.8247 | 11.438 | 8.0244 | 2.3888 | 0.6411 | 3.0962 | -0.9649 | 11.9234 | 4.9496 | 0.6198 | 0.6632 | 0.9649 | 0.7475 | -129.1809 | 1.084 | 5.596 | 2.0084 | -2.558 | -0.9537 | 4.8388 |  | 3.9536 | 0.6329 | 4.0089 | 3.366 | 3.3384 | 1.0866 | 10.773 | 14.2693 | 14.8423 | 11.0858 | 0.0004 | -0.0029 | 0.0009 | 0.0036 | 0.0007 | -0.0005 | 0.011 | 0.0012 | -0.0076 | -360.1835 | 17.4069 | -360.4327 | 17.6184 | -360.762 | 18.1953 | -360.842 | 17.5753 | -352.6167 | 18.7292 | -352.6044 | 16.8012
12:48 | 5293 | 44.551 | 202.7189 | 450.0909 | 457.0315 | -16.5558 | -39.8234 | 11.4229 | 7.9446 | 2.3593 | 0.5828 | 3.1119 | -0.9782 | 11.9141 | 4.8872 | 0.6211 | 0.6634 | 0.9667 | 0.7489 | -129.1851 | 1.0722 | 5.6233 | 1.9986 | -2.6248 | -1.0603 | 4.7822 |  | 3.9656 | 0.7357 | 4.011 | 3.3636 | 3.3397 | 1.0882 | 10.7638 | 14.2773 | 14.8266 | 11.0826 | -0.0004 | -0.0027 | 0.0007 | 0.0041 | 0.0007 | -0.0011 | 0.0133 | -0.0024 | -0.0132 | -360.1711 | 17.4192 | -360.5066 | 17.6779 | -360.8543 | 18.1974 | -360.7897 | 17.5527 | -352.6044 | 18.7374 | -352.6813 | 16.8566
12:48 | 5294 | 44.4862 | 202.6268 | 450.1036 | 457.0122 | -16.5559 | -39.9546 | 11.5017 | 7.9834 | 2.3895 | 0.6488 | 3.116 | -1.0126 | 11.8813 | 4.9491 | 0.6225 | 0.6626 | 0.9656 | 0.7482 | -129.2006 | 1.0929 | 5.6034 | 1.9648 | -2.6179 | -1.0356 | 4.7947 |  | 3.9002 | 0.6751 | 4.0119 | 3.3688 | 3.3397 | 1.0876 | 10.7327 | 14.234 | 14.8149 | 11.0642 | -0.0004 | -0.0026 | 0.0008 | 0.0042 | 0.0008 | -0.0003 | 0.0194 | -0.003 | -0.023 | -360.1927 | 17.3946 | -360.405 | 17.6594 | -360.845 | 18.2282 | -360.8604 | 17.5691 | -352.6136 | 18.7128 | -352.6229 | 16.832
12:48 | 5295 | 44.4414 | 202.6389 | 450.1589 | 457.0153 | -16.4845 | -39.7936 | 11.4975 | 7.9341 | 2.4466 | 0.6217 | 3.0268 | -0.9278 | 11.9959 | 5.0216 | 0.6216 | 0.6629 | 0.964 | 0.7487 | -129.0786 | 1.24 | 5.7021 | 1.815 | -2.5899 | -1.0677 | 4.91 |  | 3.9997 | 0.7165 | 4.0106 | 3.3651 | 3.3369 | 1.0881 | 10.7534 | 14.2612 | 14.8106 | 11.0663 | 0.0001 | -0.0031 | 0.0012 | 0.0043 | 0.0009 | -0.0006 | -0.0096 | -0.0029 | 0.0005 | -360.2419 | 17.4377 | -360.4789 | 17.6492 | -360.802 | 18.2015 | -360.845 | 17.5835 | -352.6752 | 18.7538 | -352.6537 | 16.8258
12:48 | 5296 | 44.442 | 202.6105 | 450.1118 | 456.8993 | -16.4966 | -39.8388 | 11.4931 | 7.9859 | 2.5371 | 0.8374 | 3.095 | -1.0191 | 11.9185 | 4.953 | 0.6209 | 0.6609 | 0.9651 | 0.7472 | -129.1466 | 1.1858 | 5.7101 | 1.8145 | -2.5852 | -1.1264 | 4.8471 |  | 3.9934 | 0.6579 | 4.0096 | 3.3656 | 3.3397 | 1.0878 | 10.7833 | 14.2974 | 14.8257 | 11.0724 | 0.0008 | -0.0028 | 0.0007 | 0.0038 | 0.0008 | -0.0005 | 0.0195 | -0.0088 | -0.0075 | -360.1835 | 17.4069 | -360.4819 | 17.682 | -360.8943 | 18.2261 | -360.8389 | 17.5547 | -352.6075 | 18.7292 | -352.6598 | 16.8731
12:48 | 5297 | 44.4626 | 202.6521 | 450.1749 | 456.999 | -16.4106 | -39.9073 | 11.417 | 7.967 | 2.4781 | 0.8628 | 3.0755 | -1.0564 | 11.8692 | 4.9435 | 0.6217 | 0.6606 | 0.9649 | 0.7493 | -129.1243 | 1.2336 | 5.7735 | 1.712 | -2.6003 | -0.9715 | 4.838 |  | 4.0567 | 0.6776 | 4.0104 | 3.3684 | 3.3381 | 1.0875 | 10.7833 | 14.3089 | 14.8488 | 11.1013 | -0.0001 | -0.003 | 0.0008 | 0.0038 | 0.0005 | 0 | 0.0184 | -0.01 | 0.0036 | -360.205 | 17.4131 | -360.4358 | 17.6492 | -360.8143 | 18.2282 | -360.8574 | 17.604 | -352.6629 | 18.7353 | -352.6352 | 16.8299
12:48 | 5298 | 44.5376 | 202.7141 | 450.0835 | 457.0004 | -16.548 | -39.8313 | 11.4012 | 8.0046 | 2.3736 | 0.897 | 3.0925 | -0.999 | 11.9534 | 4.9225 | 0.6191 | 0.6667 | 0.9659 | 0.7496 | -129.0612 | 1.2116 | 5.7205 | 1.6873 | -2.5676 | -1.0196 | 4.8367 |  | 3.928 | 0.6434 | 4.0106 | 3.3647 | 3.3379 | 1.0876 | 10.8018 | 14.3043 | 14.8791 | 11.1024 | -0.0006 | -0.0027 | 0.0011 | 0.0038 | 0.0015 | -0.0004 | 0.0189 | -0.0078 | 0.0094 | -360.1681 | 17.4213 | -360.5189 | 17.6759 | -360.842 | 18.2097 | -360.7927 | 17.5609 | -352.6413 | 18.7477 | -352.6937 | 16.8587
12:48 | 5299 | 44.5139 | 202.6907 | 450.1358 | 456.9825 | -16.5649 | -39.817 | 11.4694 | 7.9523 | 2.2671 | 0.7835 | 2.9964 | -1.0185 | 11.8526 | 4.843 | 0.6195 | 0.6658 | 0.9674 | 0.7493 | -129.0212 | 1.2034 | 5.7297 | 1.7215 | -2.5649 | -1.0709 | 4.8519 |  | 3.9718 | 0.7818 | 4.0103 | 3.366 | 3.3374 | 1.0871 | 10.8077 | 14.2982 | 14.8828 | 11.1493 | 0.0002 | -0.003 | 0.0001 | 0.0029 | 0.0006 | -0.0001 | 0.0249 | -0.0107 | -0.0211 | -360.1619 | 17.409 | -360.445 | 17.6677 | -360.8204 | 18.2344 | -360.8635 | 17.5917 | -352.6229 | 18.721 | -352.6413 | 16.8546
12:48 | 5300 | 44.5386 | 202.6968 | 450.167 | 456.9994 | -16.5637 | -39.7702 | 11.4129 | 7.951 | 2.3176 | 0.7595 | 3.0644 | -1.0295 | 11.9304 | 4.9129 | 0.6201 | 0.6631 | 0.962 | 0.7491 | -129.0611 | 1.2284 | 5.7421 | 1.74 | -2.4458 | -1.0629 | 4.8861 |  | 3.9685 | 0.7654 | 4.0111 | 3.3667 | 3.3389 | 1.0864 | 10.8227 | 14.2905 | 14.8311 | 11.0883 | 0 | -0.0029 | 0.0008 | 0.0037 | 0.0012 | -0.0005 | 0.0114 | -0.013 | -0.0069 | -360.2481 | 17.4336 | -360.4912 | 17.6533 | -360.7804 | 18.2056 | -360.845 | 17.5835 | -352.6783 | 18.7395 | -352.6598 | 16.8443
12:48 | 5301 | 44.6203 | 202.7033 | 450.1288 | 457.0298 | -16.5666 | -39.8354 | 11.4239 | 8.0081 | 2.3463 | 0.7963 | 3.0582 | -0.9804 | 11.9717 | 4.9179 | 0.6197 | 0.6613 | 0.964 | 0.749 | -129.0956 | 1.1901 | 5.7385 | 1.7938 | -2.4406 | -1.0058 | 4.8516 |  | 3.995 | 0.7446 | 4.0096 | 3.3649 | 3.3392 | 1.0869 | 10.7915 | 14.2764 | 14.8679 | 11.1038 | -0.0003 | -0.0029 | 0.0006 | 0.0036 | 0.0006 | -0.0004 | 0.0254 | -0.0149 | -0.0085 | -360.1588 | 17.4172 | -360.4881 | 17.6841 | -360.8666 | 18.2302 | -360.842 | 17.5547 | -352.6167 | 18.7189 | -352.6937 | 16.8813
12:48 | 5302 | 44.6318 | 202.6898 | 450.1216 | 456.9559 | -16.5751 | -39.8735 | 11.4767 | 7.884 | 2.3071 | 0.8421 | 3.09 | -0.9454 | 11.9632 | 4.9296 | 0.6213 | 0.665 | 0.9641 | 0.749 | -129.1314 | 1.2202 | 5.765 | 1.7566 | -2.4218 | -0.9701 | 4.8682 |  | 4.0171 | 0.7124 | 4.0109 | 3.3656 | 3.3371 | 1.0856 | 10.7661 | 14.2624 | 14.8814 | 11.0963 | -0.0005 | -0.0028 | 0.0004 | 0.0038 | 0.0013 | -0.0007 | 0.0003 | -0.0234 | -0.0083 | -360.1711 | 17.4131 | -360.4358 | 17.6451 | -360.8327 | 18.2138 | -360.8758 | 17.5876 | -352.6567 | 18.7312 | -352.6413 | 16.8505
12:48 | 5303 | 44.631 | 202.7063 | 450.23 | 457.1023 | -16.6252 | -39.8789 | 11.48 | 7.9488 | 2.3662 | 0.8313 | 3.1138 | -0.9656 | 11.9398 | 5.0473 | 0.6204 | 0.6653 | 0.964 | 0.7501 | -129.2208 | 1.2016 | 5.7534 | 1.7312 | -2.4218 | -0.9718 | 4.8568 |  | 3.9826 | 0.7064 | 4.0097 | 3.3647 | 3.3376 | 1.0874 | 10.7892 | 14.2683 | 14.8709 | 11.0728 | 0 | -0.0025 | 0.0006 | 0.0039 | 0.0005 | -0.0006 | 0.0136 | -0.0142 | 0.0053 | -360.2081 | 17.4418 | -360.5158 | 17.68 | -360.8358 | 18.2036 | -360.8143 | 17.5712 | -352.6629 | 18.7497 | -352.6875 | 16.8751
12:48 | 5304 | 44.6684 | 202.7042 | 450.2155 | 457.1508 | -16.5898 | -39.8931 | 11.3656 | 7.9977 | 2.3668 | 0.8258 | 3.0717 | -0.9477 | 11.9201 | 4.9812 | 0.6208 | 0.6641 | 0.9617 | 0.7496 | -129.1521 | 1.1515 | 5.7436 | 1.7713 | -2.3981 | -0.9555 | 4.8436 |  | 3.9845 | 0.6081 | 4.0101 | 3.3676 | 3.3391 | 1.0877 | 10.7822 | 14.2671 | 14.8406 | 11.0833 | 0.0003 | -0.0034 | 0.001 | 0.004 | 0.0009 | -0.0007 | 0.0119 | -0.0171 | 0.0082 | -360.1527 | 17.3966 | -360.4542 | 17.6594 | -360.8297 | 18.2261 | -360.8604 | 17.5671 | -352.6567 | 18.7107 | -352.6506 | 16.8546
12:48 | 5305 | 44.6445 | 202.6941 | 450.2375 | 457.0727 | -16.5454 | -39.8036 | 11.4177 | 8.0316 | 2.4323 | 0.7488 | 3.0955 | -0.9502 | 11.928 | 4.99 | 0.6211 | 0.6628 | 0.9603 | 0.7492 | -129.1983 | 1.1566 | 5.674 | 1.7507 | -2.448 | -1.0406 | 4.871 |  | 4.0096 | 0.6381 | 4.0099 | 3.3659 | 3.3376 | 1.0871 | 10.7902 | 14.2698 | 14.8686 | 11.1136 | 0.0001 | -0.0031 | 0.0011 | 0.004 | 0.0008 | -0.0002 | 0.0291 | 0.0022 | -0.0129 | -360.2573 | 17.4213 | -360.4666 | 17.6492 | -360.7989 | 18.2159 | -360.8697 | 17.5855 | -352.669 | 18.7456 | -352.6537 | 16.8299
12:48 | 5306 | 44.5621 | 202.6316 | 450.1759 | 457.0401 | -16.5578 | -39.7908 | 11.4512 | 8.0116 | 2.3653 | 0.7006 | 3.0471 | -0.997 | 11.9627 | 5.0457 | 0.619 | 0.6622 | 0.9654 | 0.7498 | -129.2438 | 1.1869 | 5.6809 | 1.9015 | -2.3635 | -1.0206 | 4.8305 |  | 3.8994 | 0.6324 | 4.0099 | 3.366 | 3.3401 | 1.0877 | 10.7706 | 14.279 | 14.8485 | 11.1403 | -0.0002 | -0.0024 | 0.0008 | 0.0041 | 0.0009 | -0.0007 | 0.0115 | -0.001 | -0.0161 | -360.1588 | 17.4233 | -360.4696 | 17.68 | -360.8481 | 18.2138 | -360.8297 | 17.5629 | -352.6321 | 18.7251 | -352.6598 | 16.8648
12:48 | 5307 | 44.5566 | 202.6501 | 450.0914 | 457.0444 | -16.5047 | -39.7441 | 11.4529 | 8.0728 | 2.4403 | 0.7183 | 3.0969 | -1.0202 | 12.0527 | 5.1421 | 0.6207 | 0.6649 | 0.9648 | 0.7498 | -129.1653 | 1.2751 | 5.7798 | 2.0182 | -2.3746 | -0.8868 | 4.9031 |  | 4.0386 | 0.6559 | 4.0107 | 3.3676 | 3.3396 | 1.0869 | 10.8042 | 14.3008 | 14.8924 | 11.0991 | -0.0004 | -0.003 | 0.0006 | 0.0035 | 0.001 | -0.0001 | 0.0227 | -0.0079 | -0.0317 | -360.1958 | 17.4007 | -360.4542 | 17.6574 | -360.8327 | 18.2344 | -360.8758 | 17.5814 | -352.629 | 18.7189 | -352.6167 | 16.8402
12:48 | 5308 | 44.5828 | 202.6103 | 450.212 | 457.1299 | -16.5043 | -39.7003 | 11.5652 | 8.0708 | 2.4811 | 0.6447 | 3.0516 | -0.8991 | 11.9894 | 5.0331 | 0.6202 | 0.6654 | 0.9635 | 0.7499 | -129.194 | 1.2755 | 5.7722 | 1.9483 | -2.3981 | -0.8947 | 4.8738 |  | 3.9734 | 0.5884 | 4.01 | 3.3643 | 3.3365 | 1.0871 | 10.8099 | 14.3011 | 14.8945 | 11.1042 | 0.0003 | -0.0029 | 0.0008 | 0.0044 | 0.0007 | -0.0002 | 0.0066 | -0.0029 | -0.0206 | -360.2358 | 17.4254 | -360.4789 | 17.6636 | -360.8174 | 18.2056 | -360.842 | 17.5732 | -352.6844 | 18.7497 | -352.6721 | 16.8279
12:48 | 5309 | 44.5747 | 202.6181 | 450.0544 | 457.0032 | -16.4603 | -39.6989 | 11.5037 | 8.108 | 2.5097 | 0.6737 | 3.0429 | -0.9155 | 11.9639 | 5.0085 | 0.6218 | 0.6689 | 0.9632 | 0.7496 | -129.0689 | 1.35 | 5.772 | 2.0788 | -2.5092 | -0.9668 | 4.8637 |  | 4.0086 | 0.6323 | 4.0097 | 3.3659 | 3.3426 | 1.0875 | 10.7453 | 14.253 | 14.8484 | 11.0815 | -0.0003 | -0.0029 | 0.0003 | 0.0038 | 0.0006 | -0.0007 | 0.0235 | -0.0134 | -0.0048 | -360.1804 | 17.4131 | -360.4666 | 17.6902 | -360.882 | 18.2261 | -360.8574 | 17.5588 | -352.6352 | 18.7333 | -352.6906 | 16.8628
12:48 | 5310 | 44.5587 | 202.6816 | 450.2191 | 457.1655 | -16.5198 | -39.7841 | 11.5631 | 8.1782 | 2.4504 | 0.7092 | 3.0965 | -0.9895 | 12.0532 | 4.9844 | 0.6201 | 0.6629 | 0.9624 | 0.7478 | -129.1418 | 1.3204 | 5.7751 | 2.1272 | -2.452 | -0.8618 | 4.989 |  | 3.9401 | 0.6474 | 4.0084 | 3.3682 | 3.3394 | 1.0876 | 10.7834 | 14.2856 | 14.8709 | 11.0786 | -0.0004 | -0.0028 | 0.0007 | 0.0039 | 0.0007 | -0.0001 | 0.0092 | -0.0086 | -0.016 | -360.1958 | 17.4048 | -360.4419 | 17.643 | -360.8327 | 18.2241 | -360.882 | 17.5917 | -352.666 | 18.7251 | -352.6352 | 16.8258
12:48 | 5311 | 44.4485 | 202.6345 | 450.1485 | 457.1286 | -16.421 | -39.706 | 11.5924 | 8.1168 | 2.4684 | 0.5795 | 3.0598 | -1.0158 | 12.0037 | 4.9981 | 0.621 | 0.6644 | 0.9645 | 0.75 | -129.1142 | 1.3244 | 5.65 | 2.1416 | -2.4387 | -0.8465 | 5.0094 |  | 3.9828 | 0.6623 | 4.0085 | 3.3661 | 3.3411 | 1.0876 | 10.7765 | 14.2554 | 14.8222 | 11.0779 | 0.0002 | -0.0027 | 0.0006 | 0.0039 | 0.001 | -0.0007 | 0.0006 | -0.013 | 0.0092 | -360.2142 | 17.4315 | -360.5158 | 17.6779 | -360.8266 | 18.2118 | -360.8174 | 17.5773 | -352.6413 | 18.76 | -352.6967 | 16.8546
12:48 | 5312 | 44.4961 | 202.681 | 450.2352 | 457.2193 | -16.4654 | -39.6904 | 11.6218 | 8.0738 | 2.4753 | 0.7145 | 3.0402 | -0.9477 | 11.996 | 4.9724 | 0.6203 | 0.6647 | 0.962 | 0.748 | -129.2029 | 1.2261 | 5.7744 | 2.0693 | -2.4852 | -0.9209 | 4.9454 |  | 4.0129 | 0.6171 | 4.0095 | 3.3647 | 3.338 | 1.0879 | 10.8204 | 14.2997 | 14.8689 | 11.1266 | 0.0001 | -0.0031 | 0.0003 | 0.0032 | 0.0007 | 0 | -0.0019 | -0.0071 | -0.0088 | -360.205 | 17.411 | -360.4358 | 17.6718 | -360.8789 | 18.2344 | -360.8389 | 17.5691 | -352.6167 | 18.721 | -352.6629 | 16.8505
12:48 | 5313 | 44.5496 | 202.7924 | 450.1546 | 457.2064 | -16.5054 | -39.6282 | 11.6684 | 8.0904 | 2.5522 | 0.7948 | 3.123 | -0.9598 | 11.9414 | 4.9883 | 0.6213 | 0.6652 | 0.9611 | 0.7503 | -129.1279 | 1.2655 | 5.694 | 2.0411 | -2.4907 | -0.881 | 5.0219 |  | 3.9524 | 0.6201 | 4.011 | 3.3673 | 3.3381 | 1.0867 | 10.7914 | 14.265 | 14.8805 | 11.0861 | 0.0004 | -0.0028 | 0.0011 | 0.004 | 0.001 | -0.0008 | -0.004 | -0.0092 | 0.0166 | -360.2296 | 17.4254 | -360.4389 | 17.6369 | -360.7958 | 18.2138 | -360.8697 | 17.604 | -352.6567 | 18.7333 | -352.6352 | 16.8197
12:48 | 5314 | 44.4911 | 202.7017 | 450.1782 | 457.1083 | -16.5233 | -39.6731 | 11.682 | 8.0237 | 2.5087 | 0.7282 | 3.0958 | -1.0339 | 11.9509 | 4.9164 | 0.6209 | 0.6629 | 0.9588 | 0.7502 | -129.1037 | 1.2049 | 5.6038 | 2.0442 | -2.5053 | -0.9419 | 4.9437 |  | 3.9863 | 0.5915 | 4.0104 | 3.367 | 3.3412 | 1.0868 | 10.8029 | 14.2999 | 14.8874 | 11.1262 | -0.0002 | -0.0027 | 0.0013 | 0.0038 | 0.0007 | -0.0002 | -0.0087 | -0.0027 | 0.017 | -360.1835 | 17.4172 | -360.5066 | 17.6841 | -360.845 | 18.2077 | -360.8143 | 17.5691 | -352.6506 | 18.7415 | -352.6629 | 16.8546
12:48 | 5315 | 44.5683 | 202.7267 | 450.0818 | 457.1361 | -16.4216 | -39.6456 | 11.774 | 8.0014 | 2.5531 | 0.8257 | 3.0474 | -1.0255 | 11.8801 | 4.8698 | 0.6213 | 0.666 | 0.9666 | 0.7498 | -129.0736 | 1.3059 | 5.6418 | 1.9181 | -2.5255 | -0.9618 | 4.8645 |  | 4.0257 | 0.6434 | 4.0091 | 3.3625 | 3.3355 | 1.0869 | 10.7926 | 14.2776 | 14.8519 | 11.0876 | 0 | -0.0025 | 0.0011 | 0.0041 | 0.0009 | -0.0008 | 0.0027 | -0.0065 | 0.0073 | -360.1527 | 17.3946 | -360.4266 | 17.6574 | -360.8512 | 18.2385 | -360.8574 | 17.5753 | -352.6167 | 18.7087 | -352.6321 | 16.8423
12:48 | 5316 | 44.517 | 202.7803 | 450.199 | 457.1309 | -16.3684 | -39.7533 | 11.8117 | 8.0063 | 2.5468 | 0.8321 | 3.0984 | -0.9634 | 11.979 | 4.9764 | 0.6199 | 0.6627 | 0.9606 | 0.7495 | -129.1009 | 1.2741 | 5.6929 | 2.0019 | -2.5331 | -1.0222 | 4.8556 |  | 4.05 | 0.6152 | 4.0101 | 3.3635 | 3.3385 | 1.0875 | 10.8181 | 14.2742 | 14.8488 | 11.1071 | 0.0002 | -0.003 | 0.0008 | 0.0043 | 0.0003 | -0.0005 | 0.0063 | -0.0142 | -0.0026 | -360.2665 | 17.4377 | -360.4758 | 17.6492 | -360.7835 | 18.2015 | -360.8481 | 17.5917 | -352.666 | 18.7497 | -352.6752 | 16.8279
12:48 | 5317 | 44.5564 | 202.7685 | 450.155 | 457.2012 | -16.421 | -39.6859 | 11.6645 | 7.99 | 2.626 | 0.9026 | 3.1246 | -0.9655 | 11.9417 | 4.9465 | 0.6214 | 0.6645 | 0.9637 | 0.7488 | -129.0676 | 1.1905 | 5.7445 | 1.9915 | -2.5622 | -0.9848 | 4.834 |  | 3.9847 | 0.6416 | 4.0109 | 3.3634 | 3.3391 | 1.0876 | 10.7881 | 14.267 | 14.8627 | 11.1067 | 0.0003 | -0.0027 | 0.0005 | 0.0039 | 0.0009 | -0.0008 | 0.0088 | -0.0113 | -0.0118 | -360.1619 | 17.4048 | -360.5096 | 17.6902 | -360.8543 | 18.2302 | -360.8543 | 17.5527 | -352.6136 | 18.7189 | -352.669 | 16.8607
12:48 | 5318 | 44.6407 | 202.7391 | 450.1749 | 457.1995 | -16.3518 | -39.7208 | 11.772 | 8.072 | 2.5388 | 0.8886 | 3.1789 | -1.0598 | 11.8914 | 4.9646 | 0.6209 | 0.6624 | 0.9649 | 0.7495 | -129.1289 | 1.253 | 5.6941 | 1.9732 | -2.5527 | -1.0647 | 4.8614 |  | 3.9614 | 0.523 | 4.0097 | 3.3666 | 3.3406 | 1.0874 | 10.7637 | 14.2834 | 14.8519 | 11.0818 | -0.0004 | -0.0024 | 0.0009 | 0.0041 | 0.0009 | -0.0003 | 0.0131 | -0.017 | -0.0068 | -360.2296 | 17.409 | -360.4389 | 17.6451 | -360.7989 | 18.2302 | -360.8881 | 17.5999 | -352.6567 | 18.7353 | -352.6229 | 16.8176
12:48 | 5319 | 44.546 | 202.784 | 450.1438 | 457.1407 | -16.3071 | -39.65 | 11.7649 | 8.1269 | 2.5663 | 0.7826 | 3.2054 | -0.9792 | 11.9948 | 5.0272 | 0.6213 | 0.6612 | 0.9609 | 0.7489 | -129.1211 | 1.2128 | 5.7845 | 1.965 | -2.6115 | -1.2101 | 4.8399 |  | 3.9914 | 0.6614 | 4.0091 | 3.3623 | 3.339 | 1.0871 | 10.7466 | 14.2247 | 14.8223 | 11.061 | -0.0004 | -0.003 | 0.0008 | 0.0042 | 0.001 | -0.0005 | 0.0006 | -0.0018 | 0.0039 | -360.1681 | 17.4336 | -360.485 | 17.6759 | -360.8327 | 18.1953 | -360.7989 | 17.565 | -352.6167 | 18.7456 | -352.709 | 16.8484
12:48 | 5320 | 44.5892 | 202.7311 | 450.1273 | 457.1615 | -16.2866 | -39.6306 | 11.7663 | 8.0818 | 2.4995 | 0.7966 | 3.1833 | -1.0072 | 11.981 | 4.9225 | 0.621 | 0.6617 | 0.9607 | 0.7481 | -129.1224 | 1.154 | 5.7441 | 1.9207 | -2.5321 | -1.074 | 4.7428 |  | 3.966 | 0.5533 | 4.0105 | 3.3659 | 3.3389 | 1.0884 | 10.8029 | 14.2941 | 14.8642 | 11.1146 | 0.0003 | -0.0026 | 0.0003 | 0.0033 | 0.0012 | -0.0004 | 0.0029 | -0.0229 | -0.0078 | -360.1804 | 17.3946 | -360.4573 | 17.6697 | -360.8604 | 18.2508 | -360.8727 | 17.5753 | -352.6044 | 18.7107 | -352.626 | 16.834
12:48 | 5321 | 44.6119 | 202.7699 | 450.1884 | 457.1146 | -16.4113 | -39.5785 | 11.6418 | 8.0287 | 2.4085 | 0.6988 | 3.1644 | -1.0058 | 11.9626 | 5.0157 | 0.621 | 0.6588 | 0.9612 | 0.7473 | -129.1656 | 1.2275 | 5.6582 | 1.9271 | -2.5737 | -1.0694 | 4.7909 |  | 4.0059 | 0.5589 | 4.0094 | 3.365 | 3.3351 | 1.0893 | 10.7754 | 14.26 | 14.844 | 11.071 | 0 | -0.0032 | 0.0009 | 0.0038 | 0.0004 | -0.0005 | 0.0196 | -0.0085 | -0.0184 | -360.2173 | 17.4397 | -360.4881 | 17.6348 | -360.7589 | 18.1953 | -360.8174 | 17.5855 | -352.6813 | 18.7477 | -352.6598 | 16.8135
12:48 | 5322 | 44.667 | 202.8451 | 450.1381 | 457.1421 | -16.4186 | -39.6424 | 11.6275 | 8.058 | 2.4081 | 0.6288 | 3.1373 | -1.0547 | 12.0075 | 4.9625 | 0.6196 | 0.6603 | 0.9611 | 0.748 | -129.1489 | 1.2554 | 5.6779 | 1.8372 | -2.5291 | -1.0579 | 4.8751 |  | 4.0035 | 0.5947 | 4.011 | 3.3657 | 3.3388 | 1.0879 | 10.7718 | 14.2567 | 14.8246 | 11.119 | -0.0001 | -0.0026 | 0.0005 | 0.0034 | 0.0017 | 0.0003 | 0.0222 | -0.0147 | -0.0019 | -360.1311 | 17.4131 | -360.4881 | 17.682 | -360.885 | 18.2241 | -360.8297 | 17.5445 | -352.6044 | 18.7251 | -352.6567 | 16.8525
12:48 | 5323 | 44.5683 | 202.7407 | 450.1457 | 457.1597 | -16.484 | -39.6248 | 11.6573 | 7.9688 | 2.4971 | 0.6658 | 3.1922 | -1.0825 | 12.0156 | 5.0017 | 0.6207 | 0.6617 | 0.9612 | 0.7466 | -129.1262 | 1.2598 | 5.7506 | 1.8527 | -2.5734 | -1.1457 | 4.8639 |  | 3.9847 | 0.5551 | 4.0105 | 3.3679 | 3.3371 | 1.0882 | 10.8132 | 14.3223 | 14.8545 | 11.124 | 0 | -0.0029 | 0.001 | 0.0038 | 0.0009 | 0.0001 | 0.0112 | -0.0024 | -0.0087 | -360.2019 | 17.3946 | -360.3989 | 17.6328 | -360.7897 | 18.2097 | -360.885 | 17.5896 | -352.669 | 18.7087 | -352.5798 | 16.8012
12:48 | 5324 | 44.5455 | 202.6734 | 450.1815 | 457.1546 | -16.3715 | -39.6365 | 11.6476 | 7.9742 | 2.5177 | 0.612 | 3.1055 | -1.0246 | 11.9723 | 4.9835 | 0.6202 | 0.6639 | 0.9612 | 0.7473 | -129.1179 | 1.3406 | 5.7369 | 1.8765 | -2.5555 | -0.9609 | 4.8459 |  | 3.97 | 0.5996 | 4.0095 | 3.3651 | 3.3383 | 1.0879 | 10.795 | 14.3088 | 14.9056 | 11.1479 | -0.0001 | -0.0031 | 0.0005 | 0.004 | 0.0006 | -0.0007 | 0.033 | -0.0165 | -0.0072 | -360.1988 | 17.4295 | -360.4881 | 17.6574 | -360.805 | 18.1851 | -360.7958 | 17.5486 | -352.626 | 18.7518 | -352.6813 | 16.8258
12:48 | 5325 | 44.5487 | 202.7392 | 450.2354 | 457.2175 | -16.4913 | -39.7451 | 11.5747 | 7.9047 | 2.4042 | 0.5182 | 3.0891 | -1.0657 | 11.9836 | 5.0087 | 0.6208 | 0.6625 | 0.9601 | 0.7468 | -129.1441 | 1.2277 | 5.7149 | 1.9822 | -2.4926 | -0.9601 | 4.8854 |  | 3.9663 | 0.59 | 4.0093 | 3.3677 | 3.3404 | 1.088 | 10.7879 | 14.2732 | 14.8369 | 11.0767 | 0.0002 | -0.0029 | 0.0008 | 0.0042 | 0.0006 | -0.0004 | 0.0102 | -0.0168 | -0.0081 | -360.1342 | 17.3679 | -360.4112 | 17.6512 | -360.8481 | 18.2302 | -360.8604 | 17.5568 | -352.589 | 18.6902 | -352.5952 | 16.8197
12:48 | 5326 | 44.4911 | 202.6507 | 450.1613 | 457.1286 | -16.4755 | -39.7481 | 11.6325 | 8.0248 | 2.4566 | 0.6023 | 3.1457 | -1.0645 | 11.854 | 4.9758 | 0.6207 | 0.6616 | 0.9593 | 0.7463 | -129.1146 | 1.1469 | 5.7421 | 1.9874 | -2.4708 | -0.9814 | 4.8358 |  | 3.9179 | 0.5278 | 4.0089 | 3.3677 | 3.3378 | 1.0869 | 10.8007 | 14.2741 | 14.8651 | 11.1074 | -0.0006 | -0.0029 | 0.0009 | 0.0038 | 0.0007 | -0.0013 | 0.0108 | 0.0015 | -0.0239 | -360.2173 | 17.4131 | -360.4112 | 17.604 | -360.7404 | 18.1687 | -360.8174 | 17.5773 | -352.6506 | 18.7333 | -352.6075 | 16.7827
12:48 | 5327 | 44.4576 | 202.6503 | 450.0984 | 457.1583 | -16.4717 | -39.7771 | 11.7057 | 8.0667 | 2.4253 | 0.6388 | 3.1377 | -1.1175 | 11.9133 | 4.9112 | 0.6225 | 0.6631 | 0.9614 | 0.7463 | -129.0975 | 1.2603 | 5.679 | 2.0828 | -2.4923 | -0.9549 | 4.8908 |  | 3.8929 | 0.6453 | 4.0099 | 3.366 | 3.3348 | 1.0877 | 10.7535 | 14.2898 | 14.8316 | 11.0902 | -0.0003 | -0.0028 | 0.0008 | 0.0041 | 0.0005 | -0.0002 | -0.0066 | -0.0106 | 0.0057 | -360.1342 | 17.3946 | -360.4573 | 17.6594 | -360.8543 | 18.1953 | -360.7835 | 17.5301 | -352.5675 | 18.7128 | -352.6506 | 16.832
12:49 | 5328 | 44.5312 | 202.6976 | 450.2583 | 457.2101 | -16.4282 | -39.7346 | 11.7022 | 8.0509 | 2.5265 | 0.7203 | 3.1755 | -1.0527 | 11.87 | 4.9424 | 0.6221 | 0.6646 | 0.964 | 0.7474 | -129.1219 | 1.2906 | 5.7467 | 2.0577 | -2.5298 | -1.0755 | 4.8668 |  | 3.9425 | 0.538 | 4.0112 | 3.3651 | 3.3387 | 1.0865 | 10.7498 | 14.2696 | 14.827 | 11.0908 | -0.0001 | -0.0034 | 0.0012 | 0.0039 | 0.0013 | -0.0007 | -0.0112 | -0.0229 | -0.0075 | -360.1681 | 17.3782 | -360.3742 | 17.6061 | -360.7527 | 18.2077 | -360.8635 | 17.5773 | -352.6229 | 18.6922 | -352.549 | 16.7786
12:49 | 5329 | 44.5128 | 202.6476 | 450.1635 | 457.1921 | -16.5141 | -39.7673 | 11.6727 | 8.1475 | 2.4438 | 0.7935 | 3.1811 | -1.076 | 11.9415 | 4.9873 | 0.6205 | 0.6638 | 0.9624 | 0.7472 | -129.205 | 1.2703 | 5.7243 | 2.0439 | -2.5123 | -0.9732 | 4.8772 |  | 3.9782 | 0.4862 | 4.0102 | 3.3687 | 3.3387 | 1.0883 | 10.7937 | 14.2963 | 14.8833 | 11.123 | 0.0004 | -0.0031 | 0.0009 | 0.0039 | 0.0008 | -0.0001 | -0.0041 | -0.0193 | -0.0179 | -360.1742 | 17.4213 | -360.485 | 17.641 | -360.7958 | 18.1604 | -360.7558 | 17.5404 | -352.6075 | 18.7497 | -352.6475 | 16.8156
12:49 | 5330 | 44.565 | 202.6745 | 450.1462 | 457.2212 | -16.465 | -39.775 | 11.6543 | 8.1993 | 2.4943 | 0.6793 | 3.2483 | -1.0594 | 11.947 | 4.93 | 0.6225 | 0.6655 | 0.9639 | 0.7479 | -129.2009 | 1.2227 | 5.6401 | 1.9971 | -2.5031 | -1.0621 | 4.8751 |  | 3.9016 | 0.3903 | 4.0091 | 3.3696 | 3.3384 | 1.0896 | 10.7741 | 14.265 | 14.8284 | 11.0572 | 0 | -0.0028 | 0.0011 | 0.004 | 0.0011 | 0.0001 | 0.0108 | -0.0029 | -0.0143 | -360.1096 | 17.3576 | -360.3835 | 17.6389 | -360.8081 | 18.22 | -360.8297 | 17.5424 | -352.5521 | 18.6881 | -352.5983 | 16.8053
12:49 | 5331 | 44.5628 | 202.6846 | 450.1607 | 457.1888 | -16.5041 | -39.7364 | 11.6413 | 8.0855 | 2.4211 | 0.6633 | 3.1952 | -0.9687 | 12.0194 | 4.9683 | 0.6218 | 0.6651 | 0.9663 | 0.7473 | -129.1328 | 1.1839 | 5.7005 | 2.0561 | -2.4842 | -1.0477 | 4.8935 |  | 4.0717 | 0.4773 | 4.0099 | 3.3677 | 3.339 | 1.0892 | 10.8169 | 14.279 | 14.8717 | 11.123 | -0.0003 | -0.0027 | 0.0005 | 0.0036 | 0.0012 | -0.0002 | 0.0097 | -0.0186 | -0.0097 | -360.1835 | 17.4151 | -360.4481 | 17.6081 | -360.7343 | 18.1645 | -360.7712 | 17.5568 | -352.6413 | 18.7436 | -352.5952 | 16.7848
12:49 | 5332 | 44.5562 | 202.727 | 450.1827 | 457.2064 | -16.5735 | -39.7659 | 11.5805 | 8.1009 | 2.4333 | 0.6082 | 3.1655 | -0.9764 | 12.0164 | 5.0974 | 0.6212 | 0.6668 | 0.9628 | 0.7491 | -129.069 | 1.2877 | 5.6659 | 2.1074 | -2.4907 | -1.0109 | 4.8749 |  | 4.0743 | 0.4629 | 4.0095 | 3.3656 | 3.3394 | 1.0875 | 10.8329 | 14.3245 | 14.8909 | 11.1265 | 0.0005 | -0.0023 | 0.0007 | 0.0042 | 0.0007 | 0.0002 | 0.0098 | -0.0127 | 0.0096 | -360.125 | 17.374 | -360.4173 | 17.6615 | -360.8297 | 18.2077 | -360.7681 | 17.5219 | -352.549 | 18.7025 | -352.6198 | 16.8258
12:49 | 5333 | 44.5764 | 202.6671 | 450.108 | 457.178 | -16.5731 | -39.7833 | 11.538 | 8.0598 | 2.5124 | 0.6761 | 3.2716 | -0.9462 | 11.9338 | 5.0392 | 0.6211 | 0.6649 | 0.9623 | 0.748 | -129.1333 | 1.2974 | 5.6911 | 2.1014 | -2.5014 | -0.8946 | 4.9361 |  | 4.0742 | 0.4804 | 4.0088 | 3.3694 | 3.3375 | 1.0896 | 10.7672 | 14.2926 | 14.8202 | 11.0739 | 0.0002 | -0.0032 | 0.0007 | 0.0042 | 0.0005 | -0.0007 | 0.0143 | 0.0007 | 0.0014 | -360.1865 | 17.3782 | -360.3742 | 17.6081 | -360.7373 | 18.1974 | -360.8235 | 17.5753 | -352.6598 | 18.7045 | -352.5706 | 16.7786
12:49 | 5334 | 44.5275 | 202.6208 | 450.2115 | 457.2235 | -16.5593 | -39.8451 | 11.5796 | 8.0837 | 2.4514 | 0.6491 | 3.2825 | -0.9865 | 11.881 | 5.0468 | 0.6213 | 0.6657 | 0.9629 | 0.7485 | -129.0947 | 1.2514 | 5.6498 | 2.1471 | -2.4004 | -0.9337 | 5.0128 |  | 3.989 | 0.5396 | 4.0087 | 3.3664 | 3.3394 | 1.0895 | 10.7926 | 14.2776 | 14.8229 | 11.0876 | -0.0001 | -0.0027 | 0.0011 | 0.0039 | 0.0009 | -0.0001 | 0.0043 | -0.0032 | -0.0174 | -360.1342 | 17.4213 | -360.4604 | 17.6574 | -360.7989 | 18.1645 | -360.7404 | 17.5321 | -352.5675 | 18.7312 | -352.6629 | 16.8238
12:49 | 5335 | 44.5204 | 202.6955 | 450.1523 | 457.2248 | -16.5113 | -39.8534 | 11.4851 | 8.1128 | 2.4487 | 0.7055 | 3.3036 | -0.999 | 11.9465 | 5.0116 | 0.6199 | 0.6591 | 0.9631 | 0.7478 | -129.1642 | 1.3515 | 5.7224 | 2.0637 | -2.438 | -0.9887 | 4.9856 |  | 3.974 | 0.5252 | 4.0089 | 3.3657 | 3.3378 | 1.0908 | 10.7753 | 14.2776 | 14.8229 | 11.1107 | -0.0004 | -0.0025 | 0.0007 | 0.0039 | 0.0012 | -0.0005 | 0.0147 | -0.0027 | -0.02 | -360.1465 | 17.3556 | -360.3742 | 17.6451 | -360.802 | 18.222 | -360.8512 | 17.5486 | -352.586 | 18.682 | -352.5675 | 16.8074
12:49 | 5336 | 44.5238 | 202.6956 | 450.2429 | 457.248 | -16.6079 | -39.9683 | 11.4678 | 8.1778 | 2.435 | 0.682 | 3.2475 | -0.957 | 11.9184 | 4.9939 | 0.62 | 0.6617 | 0.9623 | 0.747 | -129.0883 | 1.4086 | 5.6747 | 2.0162 | -2.4183 | -0.823 | 4.9567 |  | 3.9636 | 0.4812 | 4.0095 | 3.3662 | 3.3402 | 1.0882 | 10.7776 | 14.2508 | 14.8409 | 11.0847 | -0.0003 | -0.0029 | 0.0012 | 0.0038 | 0.0004 | -0.0008 | 0.004 | -0.0119 | 0.0006 | -360.1958 | 17.4254 | -360.4266 | 17.6328 | -360.7343 | 18.1604 | -360.7712 | 17.5609 | -352.6413 | 18.7333 | -352.6321 | 16.7909
12:49 | 5337 | 44.5309 | 202.6754 | 450.2353 | 457.2743 | -16.6424 | -39.8974 | 11.4483 | 8.2561 | 2.4584 | 0.6675 | 3.2561 | -0.9457 | 11.9599 | 5.0196 | 0.6204 | 0.6624 | 0.9609 | 0.7476 | -129.107 | 1.2589 | 5.6632 | 1.9839 | -2.3339 | -0.8679 | 4.98 |  | 3.9314 | 0.4285 | 4.009 | 3.366 | 3.3355 | 1.0881 | 10.7568 | 14.2705 | 14.8089 | 11.0695 | 0.0005 | -0.0029 | 0.0007 | 0.0038 | 0.001 | -0.0006 | 0.0058 | -0.013 | -0.0158 | -360.0973 | 17.374 | -360.4266 | 17.6759 | -360.8204 | 18.2056 | -360.8081 | 17.5239 | -352.5767 | 18.7148 | -352.6506 | 16.8443
12:49 | 5338 | 44.5645 | 202.5861 | 450.2433 | 457.2198 | -16.5279 | -39.775 | 11.5192 | 8.1925 | 2.454 | 0.7794 | 3.2653 | -0.9467 | 12.007 | 5.0261 | 0.6188 | 0.6628 | 0.9627 | 0.7482 | -129.1113 | 1.2627 | 5.7382 | 2.0355 | -2.3315 | -0.8475 | 4.9924 |  | 3.8913 | 0.5324 | 4.01 | 3.365 | 3.3367 | 1.0885 | 10.7625 | 14.2707 | 14.8389 | 11.0865 | -0.0001 | -0.0031 | 0.0011 | 0.004 | 0.001 | 0 | 0.0005 | -0.0044 | -0.0228 | -360.1865 | 17.3843 | -360.3989 | 17.6369 | -360.7589 | 18.1912 | -360.8758 | 17.5753 | -352.626 | 18.7107 | -352.6321 | 16.7991
12:49 | 5339 | 44.5597 | 202.6552 | 450.181 | 457.2125 | -16.5262 | -39.8381 | 11.5118 | 8.1091 | 2.4432 | 0.7218 | 3.1456 | -0.9684 | 11.989 | 5.0317 | 0.6199 | 0.6605 | 0.9589 | 0.7488 | -129.1285 | 1.3244 | 5.6842 | 2.0189 | -2.3619 | -0.9361 | 4.9898 |  | 3.9484 | 0.5346 | 4.0108 | 3.3664 | 3.3376 | 1.089 | 10.8007 | 14.2802 | 14.8846 | 11.1183 | 0 | -0.0021 | 0.0006 | 0.0038 | 0.001 | -0.0006 | 0.0087 | -0.0052 | -0.0033 | -360.165 | 17.4192 | -360.4789 | 17.6759 | -360.8235 | 18.1584 | -360.7897 | 17.5465 | -352.6198 | 18.7415 | -352.6783 | 16.8423
12:49 | 5340 | 44.6107 | 202.6097 | 450.2617 | 457.3076 | -16.5984 | -39.7874 | 11.533 | 8.1317 | 2.4538 | 0.666 | 3.2597 | -1.0441 | 11.9566 | 4.9797 | 0.621 | 0.6633 | 0.9611 | 0.7487 | -129.0478 | 1.3221 | 5.7111 | 2.1027 | -2.4129 | -0.9471 | 4.9456 |  | 3.9836 | 0.6488 | 4.0103 | 3.3668 | 3.3398 | 1.0879 | 10.8168 | 14.3023 | 14.9075 | 11.1284 | 0 | -0.0028 | 0.0003 | 0.0035 | 0.0011 | 0 | 0.0101 | -0.0121 | -0.0356 | -360.1004 | 17.3679 | -360.3989 | 17.6636 | -360.8266 | 18.2179 | -360.8574 | 17.5568 | -352.5983 | 18.6881 | -352.6106 | 16.834
12:49 | 5341 | 44.5785 | 202.6456 | 450.0908 | 457.311 | -16.5682 | -39.849 | 11.5402 | 8.1457 | 2.5332 | 0.73 | 3.2583 | -1.016 | 11.9961 | 5.052 | 0.6196 | 0.6604 | 0.9616 | 0.7479 | -129.1021 | 1.3015 | 5.759 | 2.1125 | -2.3923 | -0.8364 | 4.9658 |  | 4.0476 | 0.5713 | 4.0117 | 3.3679 | 3.342 | 1.0881 | 10.7834 | 14.2913 | 14.8814 | 11.1136 | -0.0003 | -0.0031 | 0.0007 | 0.0039 | 0.0011 | -0.0007 | -0.0007 | -0.0002 | -0.0105 | -360.1865 | 17.4172 | -360.445 | 17.6512 | -360.7527 | 18.1625 | -360.8235 | 17.5794 | -352.6383 | 18.7374 | -352.6383 | 16.8032
12:49 | 5342 | 44.59 | 202.6564 | 450.1877 | 457.2336 | -16.6153 | -39.8701 | 11.4845 | 8.0942 | 2.5356 | 0.7468 | 3.2562 | -1.0567 | 11.9389 | 4.9921 | 0.6197 | 0.6596 | 0.9635 | 0.7478 | -129.0464 | 1.3159 | 5.7451 | 2.0973 | -2.4309 | -0.7989 | 4.9611 |  | 3.9796 | 0.6049 | 4.0103 | 3.3637 | 3.3387 | 1.0892 | 10.7615 | 14.2632 | 14.817 | 11.075 | 0 | -0.0029 | 0.0006 | 0.0032 | 0.0009 | -0.0007 | 0.0245 | 0 | -0.0029 | -360.1496 | 17.3905 | -360.4419 | 17.6759 | -360.8389 | 18.1912 | -360.805 | 17.5342 | -352.6013 | 18.7107 | -352.6506 | 16.8423
12:49 | 5343 | 44.4807 | 202.4792 | 450.1407 | 457.1343 | -16.5388 | -39.715 | 11.6577 | 8.1234 | 2.5477 | 0.7898 | 3.2112 | -0.9725 | 11.9635 | 5.0334 | 0.62 | 0.6611 | 0.9569 | 0.7465 | -129.1042 | 1.1387 | 5.7115 | 2.1462 | -2.456 | -0.9008 | 4.9103 |  | 3.9992 | 0.6887 | 4.0119 | 3.3653 | 3.3397 | 1.089 | 10.7984 | 14.2545 | 14.8577 | 11.1049 | -0.0006 | -0.0026 | 0.0006 | 0.0034 | 0.0012 | -0.0003 | 0.0135 | -0.0084 | -0.0049 | -360.1311 | 17.3782 | -360.3896 | 17.6328 | -360.7712 | 18.183 | -360.8604 | 17.5814 | -352.6044 | 18.7148 | -352.6044 | 16.8115
12:49 | 5344 | 44.5668 | 202.6087 | 450.2506 | 457.1913 | -16.3821 | -39.7114 | 11.6664 | 8.1357 | 2.4885 | 0.7977 | 3.1908 | -1.0062 | 11.952 | 4.9745 | 0.6208 | 0.6631 | 0.9619 | 0.7494 | -129.118 | 1.2035 | 5.701 | 2.0933 | -2.4528 | -0.8601 | 5.0299 |  | 4.0025 | 0.6691 | 4.0112 | 3.3669 | 3.3419 | 1.0886 | 10.758 | 14.2658 | 14.8324 | 11.0652 | -0.0002 | -0.0028 | 0.0015 | 0.0044 | 0.0008 | -0.0006 | 0.0162 | -0.0037 | -0.0257 | -360.1188 | 17.3966 | -360.4419 | 17.6553 | -360.7927 | 18.1522 | -360.7835 | 17.5547 | -352.6198 | 18.7312 | -352.6321 | 16.8217
12:49 | 5345 | 44.4618 | 202.5791 | 450.0685 | 457.1948 | -16.4203 | -39.6917 | 11.6271 | 8.1525 | 2.4723 | 0.8179 | 3.1759 | -1 | 12.0047 | 4.9096 | 0.6199 | 0.6594 | 0.9606 | 0.7481 | -129.1495 | 1.2624 | 5.7114 | 2.0217 | -2.4241 | -0.8925 | 4.9591 |  | 4.0494 | 0.6606 | 4.0109 | 3.3647 | 3.3388 | 1.0878 | 10.7822 | 14.273 | 14.8243 | 11.0944 | 0.0001 | -0.0033 | 0.0009 | 0.0035 | 0.0008 | -0.0002 | 0.0052 | -0.0049 | -0.008 | -360.1219 | 17.3761 | -360.4112 | 17.641 | -360.805 | 18.1871 | -360.8297 | 17.5568 | -352.589 | 18.7045 | -352.626 | 16.8238
12:49 | 5346 | 44.5753 | 202.5934 | 450.1787 | 457.2126 | -16.4892 | -39.6977 | 11.6983 | 8.1837 | 2.5005 | 0.7819 | 3.1135 | -0.9655 | 11.9904 | 4.9175 | 0.6192 | 0.6642 | 0.963 | 0.7497 | -129.0551 | 1.2642 | 5.7868 | 1.9915 | -2.5226 | -0.9342 | 4.9454 |  | 4.0424 | 0.7168 | 4.0107 | 3.3677 | 3.3386 | 1.0887 | 10.7972 | 14.3171 | 14.8458 | 11.115 | 0 | -0.003 | 0.0004 | 0.0037 | 0.0014 | -0.0004 | 0.0054 | -0.0017 | 0.0082 | -360.1742 | 17.4069 | -360.4235 | 17.6307 | -360.7589 | 18.1604 | -360.7712 | 17.5671 | -352.6229 | 18.7271 | -352.6413 | 16.8217
12:49 | 5347 | 44.6367 | 202.5412 | 450.1341 | 457.1853 | -16.496 | -39.742 | 11.7056 | 8.1053 | 2.5242 | 0.7998 | 3.1319 | -1.039 | 11.9966 | 4.918 | 0.6203 | 0.6621 | 0.9586 | 0.749 | -129.1002 | 1.2584 | 5.6605 | 1.9792 | -2.4898 | -0.931 | 4.9856 |  | 4.1127 | 0.7637 | 4.0092 | 3.366 | 3.339 | 1.088 | 10.8065 | 14.2916 | 14.8546 | 11.1071 | -0.0005 | -0.003 | 0.0004 | 0.0035 | 0.0001 | -0.0003 | 0.0154 | -0.0048 | -0.0132 | -360.1158 | 17.3823 | -360.4204 | 17.6553 | -360.7835 | 18.1748 | -360.8081 | 17.5547 | -352.5829 | 18.7066 | -352.6136 | 16.8176
12:49 | 5348 | 44.6735 | 202.5654 | 450.1886 | 457.2306 | -16.439 | -39.7111 | 11.6438 | 8.0984 | 2.5869 | 0.7777 | 3.0584 | -1.0642 | 11.9783 | 4.9243 | 0.6191 | 0.6647 | 0.9621 | 0.7505 | -129.1377 | 1.2259 | 5.6834 | 2.0476 | -2.499 | -0.9082 | 4.8864 |  | 4.1068 | 0.7996 | 4.0091 | 3.3668 | 3.3399 | 1.0878 | 10.7833 | 14.3033 | 14.8152 | 11.0778 | -0.0001 | -0.0025 | 0.0004 | 0.0038 | 0.0009 | -0.0006 | 0.0043 | -0.0148 | -0.0186 | -360.1281 | 17.3925 | -360.3927 | 17.641 | -360.7927 | 18.1645 | -360.805 | 17.5753 | -352.5767 | 18.7025 | -352.5952 | 16.8197
12:49 | 5349 | 44.6607 | 202.6621 | 450.2388 | 457.2807 | -16.5035 | -39.7426 | 11.5593 | 8.1376 | 2.5291 | 0.764 | 3.1293 | -1.0838 | 11.8961 | 4.9793 | 0.6201 | 0.6611 | 0.9619 | 0.7495 | -129.0799 | 1.1886 | 5.5752 | 2.0141 | -2.4582 | -0.9198 | 4.8888 |  | 4.0012 | 0.6792 | 4.0103 | 3.366 | 3.3413 | 1.0879 | 10.7961 | 14.2985 | 14.8734 | 11.1082 | -0.0001 | -0.0031 | 0.0009 | 0.0039 | 0.0007 | -0.0004 | 0.0171 | -0.013 | -0.011 | -360.1281 | 17.3864 | -360.4081 | 17.6328 | -360.7712 | 18.1707 | -360.7958 | 17.5671 | -352.5706 | 18.7045 | -352.6044 | 16.8156
12:49 | 5350 | 44.6628 | 202.685 | 450.2967 | 457.242 | -16.5767 | -39.7833 | 11.5067 | 8.0977 | 2.4921 | 0.7997 | 3.14 | -0.9016 | 11.9611 | 4.9995 | 0.6179 | 0.6622 | 0.9624 | 0.7491 | -129.1331 | 1.234 | 5.6931 | 2.0551 | -2.407 | -0.9284 | 5.024 |  | 4.0025 | 0.6987 | 4.0088 | 3.3672 | 3.3391 | 1.0887 | 10.7729 | 14.2696 | 14.8386 | 11.0619 | -0.0003 | -0.0033 | 0.0013 | 0.0039 | 0.0012 | -0.0004 | 0.0239 | -0.0164 | 0.0025 | -360.1619 | 17.3843 | -360.3865 | 17.6389 | -360.7527 | 18.1687 | -360.8512 | 17.5712 | -352.589 | 18.7004 | -352.6044 | 16.8032
12:49 | 5351 | 44.6441 | 202.7083 | 450.2514 | 457.1553 | -16.544 | -39.6991 | 11.5636 | 8.0742 | 2.4648 | 0.7901 | 3.0687 | -0.9327 | 11.9741 | 4.9874 | 0.62 | 0.6629 | 0.9652 | 0.7485 | -129.198 | 1.2058 | 5.6717 | 1.8945 | -2.4709 | -0.9556 | 4.8758 |  | 3.9184 | 0.6712 | 4.0087 | 3.3646 | 3.339 | 1.0884 | 10.7741 | 14.2997 | 14.84 | 11.0919 | 0 | -0.0023 | 0.0009 | 0.0041 | 0.0007 | -0.0003 | 0.0138 | -0.0161 | -0.004 | -360.1342 | 17.3905 | -360.4327 | 17.6533 | -360.7743 | 18.1522 | -360.7804 | 17.5547 | -352.5706 | 18.7087 | -352.589 | 16.8176
12:49 | 5352 | 44.666 | 202.6389 | 450.2596 | 457.1544 | -16.5719 | -39.7983 | 11.6214 | 8.1355 | 2.5158 | 0.8342 | 3.1127 | -1.0188 | 12.0038 | 4.9701 | 0.6207 | 0.6632 | 0.9581 | 0.7496 | -129.2103 | 1.2242 | 5.7031 | 1.9389 | -2.3769 | -1.0097 | 4.8537 |  | 3.9818 | 0.6517 | 4.0088 | 3.3661 | 3.3352 | 1.09 | 10.7627 | 14.2702 | 14.8184 | 11.0876 | -0.0005 | -0.0028 | 0.0014 | 0.0042 | 0.0006 | -0.0008 | 0.0225 | -0.0105 | -0.0037 | -360.1004 | 17.3699 | -360.405 | 17.643 | -360.805 | 18.1871 | -360.7989 | 17.5506 | -352.5675 | 18.6902 | -352.6044 | 16.8197
12:49 | 5353 | 44.6518 | 202.5803 | 450.2435 | 457.1165 | -16.5145 | -39.7674 | 11.5929 | 7.9887 | 2.4404 | 0.7084 | 3.1057 | -1.056 | 11.93 | 4.9426 | 0.6201 | 0.6644 | 0.9597 | 0.75 | -129.0763 | 1.2998 | 5.737 | 1.9342 | -2.4124 | -1.0017 | 4.8385 |  | 3.9902 | 0.7823 | 4.0083 | 3.365 | 3.3345 | 1.0896 | 10.7741 | 14.2591 | 14.8679 | 11.0634 | 0.0001 | -0.0031 | 0.0008 | 0.0035 | 0.0007 | -0.0005 | 0.0115 | -0.0125 | -0.0281 | -360.1188 | 17.3905 | -360.3958 | 17.6245 | -360.7466 | 18.1769 | -360.8358 | 17.5794 | -352.6075 | 18.6984 | -352.5798 | 16.8032
12:49 | 5354 | 44.7425 | 202.6071 | 450.3158 | 457.186 | -16.5041 | -39.7283 | 11.5692 | 8.0062 | 2.4849 | 0.644 | 3.1498 | -0.9956 | 11.9971 | 4.9468 | 0.62 | 0.6601 | 0.9629 | 0.7495 | -129.1353 | 1.1692 | 5.5856 | 1.9423 | -2.4928 | -0.9751 | 4.9439 |  | 3.932 | 0.6365 | 4.0095 | 3.3652 | 3.3378 | 1.0886 | 10.7892 | 14.2741 | 14.8362 | 11.1017 | 0.0001 | -0.003 | 0.0002 | 0.0036 | 0.0009 | -0.0005 | 0.0205 | 0.0001 | 0.0107 | -360.1558 | 17.4028 | -360.4266 | 17.6553 | -360.7558 | 18.1399 | -360.7712 | 17.5527 | -352.6106 | 18.7066 | -352.6506 | 16.8176
12:49 | 5355 | 44.7433 | 202.5467 | 450.3156 | 457.1891 | -16.4892 | -39.6996 | 11.6054 | 8.0554 | 2.4633 | 0.7476 | 3.0778 | -0.9227 | 12.0273 | 5.0773 | 0.6204 | 0.6594 | 0.9624 | 0.7488 | -129.1464 | 1.2071 | 5.6741 | 2.0081 | -2.369 | -0.8661 | 4.9404 |  | 3.9224 | 0.5503 | 4.0098 | 3.3629 | 3.3377 | 1.0882 | 10.8053 | 14.2962 | 14.8996 | 11.106 | -0.0004 | -0.0028 | 0.0003 | 0.0038 | 0.0008 | -0.0005 | 0.0263 | -0.0131 | 0.0026 | -360.1496 | 17.3658 | -360.3835 | 17.6328 | -360.7958 | 18.2056 | -360.8327 | 17.5712 | -352.5983 | 18.6635 | -352.6075 | 16.8197
12:49 | 5356 | 44.7614 | 202.6031 | 450.3159 | 457.2334 | -16.4688 | -39.7396 | 11.5651 | 8.0712 | 2.4018 | 0.7963 | 3.0582 | -0.9397 | 11.9916 | 5.0785 | 0.6211 | 0.6608 | 0.9638 | 0.7498 | -129.1924 | 1.192 | 5.7227 | 1.9158 | -2.474 | -0.9126 | 4.8425 |  | 3.878 | 0.5729 | 4.0089 | 3.3657 | 3.3372 | 1.0875 | 10.751 | 14.2589 | 14.8436 | 11.0869 | 0.0002 | -0.0023 | 0.0005 | 0.0037 | 0.0005 | -0.0007 | 0.0127 | -0.0073 | -0.0205 | -360.2173 | 17.4192 | -360.4235 | 17.6286 | -360.725 | 18.142 | -360.7558 | 17.5773 | -352.6075 | 18.7271 | -352.6413 | 16.7909
12:49 | 5357 | 44.7631 | 202.603 | 450.2976 | 457.2477 | -16.4195 | -39.6875 | 11.6488 | 8.147 | 2.4272 | 0.7978 | 3.0935 | -0.8734 | 12.0495 | 5.0443 | 0.62 | 0.6635 | 0.961 | 0.7491 | -129.0738 | 1.2279 | 5.8123 | 1.9996 | -2.536 | -0.8975 | 4.9144 |  | 3.9594 | 0.5845 | 4.01 | 3.3648 | 3.3387 | 1.0884 | 10.7637 | 14.2659 | 14.8624 | 11.0822 | 0.0003 | -0.003 | 0.0005 | 0.0038 | 0.0006 | -0.0005 | 0.0084 | -0.0016 | -0.0029 | -360.0758 | 17.3699 | -360.4204 | 17.6553 | -360.8297 | 18.1769 | -360.7712 | 17.5506 | -352.5583 | 18.6676 | -352.6167 | 16.8279
12:49 | 5358 | 44.7207 | 202.6295 | 450.3114 | 457.1993 | -16.4681 | -39.8123 | 11.5785 | 8.053 | 2.3874 | 0.7123 | 3.1147 | -0.9484 | 12.0386 | 4.9971 | 0.6199 | 0.6626 | 0.9614 | 0.749 | -129.2251 | 1.1131 | 5.7991 | 1.9825 | -2.41 | -0.8509 | 4.8705 |  | 3.9597 | 0.4928 | 4.0107 | 3.3656 | 3.3419 | 1.0888 | 10.7995 | 14.2732 | 14.8717 | 11.0998 | 0.0004 | -0.0025 | 0.0012 | 0.0042 | 0.0009 | 0.0001 | 0.0144 | -0.0056 | -0.0292 | -360.1773 | 17.3884 | -360.3927 | 17.6204 | -360.725 | 18.1645 | -360.8327 | 17.5855 | -352.6198 | 18.6902 | -352.5767 | 16.7807
12:49 | 5359 | 44.8486 | 202.676 | 450.3524 | 457.2762 | -16.5837 | -39.8464 | 11.4567 | 8.0475 | 2.374 | 0.7575 | 3.0379 | -0.8865 | 12.0362 | 5.0073 | 0.6209 | 0.6603 | 0.964 | 0.7478 | -129.143 | 1.2169 | 5.7559 | 1.9611 | -2.3986 | -0.8529 | 4.9319 |  | 3.8866 | 0.4701 | 4.0099 | 3.3644 | 3.34 | 1.0883 | 10.7879 | 14.2963 | 14.8775 | 11.0998 | 0 | -0.0027 | 0.0007 | 0.0038 | 0.0008 | -0.001 | 0.0221 | -0.0163 | -0.0093 | -360.1127 | 17.4028 | -360.4573 | 17.6738 | -360.8112 | 18.1543 | -360.7497 | 17.5342 | -352.5706 | 18.7025 | -352.6444 | 16.8423
12:49 | 5360 | 44.785 | 202.6291 | 450.338 | 457.3037 | -16.528 | -39.823 | 11.4891 | 8.0882 | 2.3624 | 0.7432 | 3.097 | -0.9175 | 11.9949 | 4.9821 | 0.6218 | 0.6618 | 0.9633 | 0.7489 | -129.1358 | 1.2155 | 5.7216 | 1.9839 | -2.3617 | -0.8929 | 4.9117 |  | 3.9577 | 0.4833 | 4.0102 | 3.3672 | 3.3414 | 1.0878 | 10.8065 | 14.2627 | 14.8315 | 11.0955 | -0.0002 | -0.0022 | 0.0014 | 0.0041 | 0.0007 | 0.0001 | 0.0142 | -0.0177 | -0.0069 | -360.1281 | 17.3597 | -360.3404 | 17.6225 | -360.765 | 18.1953 | -360.8481 | 17.5753 | -352.5952 | 18.6696 | -352.549 | 16.795
12:49 | 5361 | 44.6886 | 202.7363 | 450.3426 | 457.1823 | -16.5352 | -39.8392 | 11.5049 | 8.0994 | 2.4483 | 0.7676 | 3.1394 | -0.9992 | 12.011 | 4.9897 | 0.6206 | 0.6617 | 0.9618 | 0.7484 | -129.0803 | 1.321 | 5.8404 | 1.9166 | -2.3566 | -0.9277 | 4.9227 |  | 3.9916 | 0.5134 | 4.0096 | 3.3647 | 3.337 | 1.0881 | 10.8007 | 14.2975 | 14.8673 | 11.0836 | 0 | -0.003 | 0.0008 | 0.004 | 0.0009 | -0.0008 | 0.0159 | -0.0132 | -0.0163 | -360.1804 | 17.4213 | -360.4696 | 17.6512 | -360.7712 | 18.1358 | -360.7804 | 17.5671 | -352.5983 | 18.7312 | -352.6413 | 16.793
12:49 | 5362 | 44.736 | 202.7606 | 450.3872 | 457.2981 | -16.5966 | -39.8611 | 11.4091 | 8.0635 | 2.3933 | 0.7508 | 3.0764 | -0.8351 | 12.0457 | 4.9253 | 0.621 | 0.6622 | 0.9637 | 0.7472 | -129.1377 | 1.296 | 5.7956 | 1.838 | -2.3101 | -0.8967 | 4.9171 |  | 3.9671 | 0.577 | 4.0096 | 3.3629 | 3.337 | 1.0879 | 10.7812 | 14.2656 | 14.8197 | 11.0945 | 0 | -0.0032 | 0.0005 | 0.0037 | 0.0007 | -0.0005 | 0.0049 | -0.0057 | -0.0183 | -360.0911 | 17.3617 | -360.405 | 17.6697 | -360.8358 | 18.1912 | -360.7897 | 17.5363 | -352.4967 | 18.6758 | -352.586 | 16.8217
12:49 | 5363 | 44.7868 | 202.6606 | 450.3175 | 457.2372 | -16.436 | -39.6649 | 11.5941 | 8.1092 | 2.4579 | 0.766 | 3.1345 | -0.9286 | 11.9805 | 4.8972 | 0.6205 | 0.6609 | 0.9594 | 0.7485 | -129.1669 | 1.2145 | 5.6223 | 1.8133 | -2.35 | -1.0095 | 4.8934 |  | 3.9319 | 0.4882 | 4.0091 | 3.3656 | 3.3419 | 1.0894 | 10.7647 | 14.2965 | 14.867 | 11.1052 | 0.0002 | -0.0026 | 0.0008 | 0.0041 | 0.0009 | -0.0006 | 0.0231 | -0.0087 | 0.0055 | -360.1927 | 17.3905 | -360.3958 | 17.6266 | -360.7466 | 18.1666 | -360.845 | 17.5835 | -352.6229 | 18.6963 | -352.5921 | 16.7766
12:49 | 5364 | 44.7171 | 202.6513 | 450.2259 | 457.1656 | -16.4409 | -39.6584 | 11.6127 | 8.1228 | 2.4892 | 0.7861 | 3.1133 | -0.9865 | 11.9822 | 5.0336 | 0.6207 | 0.6596 | 0.9591 | 0.7478 | -129.1552 | 1.2192 | 5.6879 | 1.7794 | -2.3146 | -0.8989 | 4.9486 |  | 3.9609 | 0.5625 | 4.0103 | 3.3677 | 3.3409 | 1.0898 | 10.7788 | 14.2518 | 14.8354 | 11.0919 | -0.0004 | -0.0029 | 0.0006 | 0.0036 | 0.0006 | -0.0005 | 0.002 | -0.0075 | -0.0056 | -360.1496 | 17.4048 | -360.4789 | 17.6697 | -360.8143 | 18.1522 | -360.7558 | 17.5404 | -352.5767 | 18.7169 | -352.6321 | 16.8176
12:49 | 5365 | 44.7334 | 202.6716 | 450.2245 | 457.1432 | -16.4812 | -39.6187 | 11.6885 | 8.0419 | 2.4285 | 0.788 | 3.0711 | -0.9372 | 11.9805 | 4.9508 | 0.6209 | 0.6639 | 0.9616 | 0.7487 | -129.1477 | 1.2775 | 5.6086 | 1.8301 | -2.3794 | -0.9591 | 4.8443 |  | 3.9182 | 0.5288 | 4.0108 | 3.3649 | 3.3419 | 1.0898 | 10.7615 | 14.2518 | 14.8528 | 11.0804 | 0 | -0.0028 | 0.0006 | 0.0038 | 0.001 | -0.0004 | 0.0057 | -0.0146 | -0.0054 | -360.1558 | 17.374 | -360.3896 | 17.6553 | -360.7927 | 18.183 | -360.8266 | 17.5629 | -352.5644 | 18.6799 | -352.5767 | 16.795
12:49 | 5366 | 44.7129 | 202.4947 | 450.1872 | 457.1165 | -16.4595 | -39.5848 | 11.7779 | 8.0485 | 2.3722 | 0.8323 | 3.0306 | -0.8857 | 12.056 | 5.0125 | 0.6214 | 0.6655 | 0.9682 | 0.7481 | -129.1961 | 1.2821 | 5.5924 | 1.9112 | -2.3253 | -0.9621 | 4.8323 |  | 4.0224 | 0.5023 | 4.0094 | 3.3643 | 3.3408 | 1.0883 | 10.7776 | 14.2799 | 14.8593 | 11.0901 | 0.0002 | -0.0031 | 0.0015 | 0.0042 | 0.0009 | -0.0003 | 0.0061 | -0.0053 | -0.0262 | -360.1835 | 17.409 | -360.4266 | 17.6266 | -360.7404 | 18.1604 | -360.7773 | 17.5794 | -352.6075 | 18.7066 | -352.6229 | 16.793
12:49 | 5367 | 44.6913 | 202.5457 | 450.0779 | 457.0492 | -16.5041 | -39.7622 | 11.8028 | 8.1119 | 2.4288 | 0.7815 | 3.1915 | -0.9585 | 12.0371 | 4.9812 | 0.6219 | 0.6671 | 0.9636 | 0.7487 | -129.2863 | 1.2036 | 5.523 | 1.8801 | -2.3164 | -0.9528 | 4.8703 |  | 4.072 | 0.5584 | 4.0104 | 3.3637 | 3.3402 | 1.0899 | 10.788 | 14.2498 | 14.858 | 11.0659 | -0.0004 | -0.0029 | 0.0007 | 0.0033 | 0.0008 | -0.0006 | 0.0255 | -0.003 | 0.0072 | -360.0881 | 17.3843 | -360.4358 | 17.6492 | -360.7897 | 18.1728 | -360.805 | 17.5506 | -352.5521 | 18.6902 | -352.6044 | 16.8074
12:49 | 5368 | 44.7067 | 202.6107 | 450.0781 | 457.1558 | -16.5354 | -39.7423 | 11.7753 | 8.133 | 2.4296 | 0.809 | 3.1539 | -0.9568 | 12.0595 | 4.9738 | 0.6222 | 0.6641 | 0.962 | 0.7476 | -129.2604 | 1.1933 | 5.5468 | 1.8668 | -2.2635 | -0.8341 | 4.8576 |  | 3.972 | 0.6115 | 4.0099 | 3.3668 | 3.3373 | 1.0884 | 10.7441 | 14.2578 | 14.8191 | 11.0569 | -0.0005 | -0.0027 | 0.0009 | 0.0039 | 0.0013 | 0 | 0.0191 | -0.0147 | -0.0161 | -360.1711 | 17.3946 | -360.405 | 17.641 | -360.7743 | 18.1687 | -360.8204 | 17.5773 | -352.589 | 18.7045 | -352.6167 | 16.793
12:49 | 5369 | 44.7672 | 202.6554 | 450.1309 | 457.1503 | -16.5414 | -39.6757 | 11.8019 | 8.0828 | 2.4218 | 0.6785 | 3.1249 | -0.9774 | 12.098 | 4.9222 | 0.6219 | 0.6627 | 0.9614 | 0.7468 | -129.3085 | 1.2046 | 5.5532 | 1.8083 | -2.4665 | -0.9128 | 4.8165 |  | 3.9966 | 0.5533 | 4.0108 | 3.3689 | 3.3372 | 1.0902 | 10.7961 | 14.281 | 14.8549 | 11.1374 | -0.0005 | -0.0029 | 0.0008 | 0.004 | 0.0006 | -0.0004 | 0.0076 | -0.018 | -0.0065 | -360.1681 | 17.3782 | -360.4235 | 17.6451 | -360.7589 | 18.1687 | -360.7897 | 17.5506 | -352.5613 | 18.6922 | -352.6198 | 16.8053
12:49 | 5370 | 44.7193 | 202.5736 | 450.3101 | 457.1164 | -16.3998 | -39.6713 | 11.7902 | 8.1043 | 2.4451 | 0.7449 | 3.1417 | -1.0761 | 11.9346 | 4.8018 | 0.6215 | 0.6657 | 0.9624 | 0.7496 | -129.2701 | 1.2273 | 5.5435 | 1.8181 | -2.4199 | -0.879 | 4.8661 |  | 4.1224 | 0.6615 | 4.0102 | 3.3672 | 3.3384 | 1.0897 | 10.7868 | 14.3125 | 14.8471 | 11.1277 | 0 | -0.003 | 0 | 0.0037 | 0.001 | -0.0004 | -0.0021 | -0.0122 | -0.0308 | -360.1342 | 17.3761 | -360.3896 | 17.6369 | -360.7743 | 18.1645 | -360.8112 | 17.5629 | -352.5583 | 18.6943 | -352.5798 | 16.7889
12:49 | 5371 | 44.7372 | 202.5778 | 450.1933 | 457.1747 | -16.4414 | -39.7141 | 11.8437 | 8.0849 | 2.3444 | 0.7387 | 3.0814 | -0.9465 | 12.0282 | 4.9526 | 0.6211 | 0.6597 | 0.9606 | 0.7509 | -129.3 | 1.2107 | 5.5451 | 1.8978 | -2.3859 | -0.9867 | 4.8428 |  | 4.0801 | 0.7382 | 4.0096 | 3.3658 | 3.3412 | 1.0894 | 10.7902 | 14.3046 | 14.8755 | 11.1363 | -0.0001 | -0.0031 | 0.0006 | 0.0041 | 0.0003 | -0.0004 | -0.0023 | -0.0101 | -0.02 | -360.1527 | 17.4028 | -360.4266 | 17.6512 | -360.7435 | 18.1543 | -360.7743 | 17.5588 | -352.629 | 18.7087 | -352.6413 | 16.8074
12:49 | 5372 | 44.7223 | 202.5129 | 450.068 | 457.0773 | -16.4328 | -39.7352 | 11.8085 | 8.129 | 2.4113 | 0.6722 | 3.0375 | -1.015 | 12.01 | 4.9058 | 0.6211 | 0.6622 | 0.962 | 0.7503 | -129.219 | 1.3867 | 5.6076 | 2.0258 | -2.3191 | -0.8326 | 4.867 |  | 4.0292 | 0.7056 | 4.0096 | 3.37 | 3.3358 | 1.0887 | 10.8065 | 14.2856 | 14.8593 | 11.1017 | -0.0004 | -0.0025 | 0.0008 | 0.004 | 0.0006 | -0.0007 | 0.0179 | -0.013 | -0.0038 | -360.0604 | 17.3679 | -360.3896 | 17.6512 | -360.802 | 18.1953 | -360.7897 | 17.5404 | -352.5952 | 18.6902 | -352.5983 | 16.8238
12:49 | 5373 | 44.696 | 202.503 | 450.0731 | 457.0469 | -16.505 | -39.7 | 11.6785 | 8.0222 | 2.3254 | 0.6074 | 2.979 | -0.9686 | 12.0084 | 4.9805 | 0.6216 | 0.6602 | 0.9618 | 0.7495 | -129.2601 | 1.2842 | 5.648 | 1.9541 | -2.4236 | -0.8414 | 4.8887 |  | 3.9937 | 0.735 | 4.0093 | 3.3671 | 3.3402 | 1.0898 | 10.8122 | 14.2917 | 14.8788 | 11.1183 | -0.0001 | -0.0032 | 0.0011 | 0.004 | 0.0008 | 0 | 0.0052 | -0.0039 | -0.0198 | -360.1988 | 17.3966 | -360.405 | 17.6286 | -360.7281 | 18.1543 | -360.8266 | 17.5855 | -352.6383 | 18.7148 | -352.626 | 16.7827
12:49 | 5374 | 44.7638 | 202.6558 | 450.2381 | 457.1903 | -16.3987 | -39.63 | 11.7429 | 8.1075 | 2.373 | 0.7169 | 3.0192 | -0.9856 | 12.0076 | 4.955 | 0.6204 | 0.6641 | 0.9625 | 0.7489 | -129.2799 | 1.2489 | 5.5522 | 1.9025 | -2.4827 | -0.917 | 4.8643 |  | 3.8984 | 0.6388 | 4.0105 | 3.37 | 3.3379 | 1.0889 | 10.7891 | 14.2802 | 14.8673 | 11.0894 | 0.0002 | -0.0031 | 0.0015 | 0.0042 | 0.0004 | -0.0009 | 0.0172 | -0.0045 | 0.0122 | -360.1127 | 17.3884 | -360.4696 | 17.6759 | -360.8481 | 18.1892 | -360.7835 | 17.5424 | -352.5767 | 18.6943 | -352.6783 | 16.8402
12:49 | 5375 | 44.7192 | 202.6476 | 450.3008 | 457.1771 | -16.4834 | -39.628 | 11.7021 | 8.0966 | 2.3694 | 0.7647 | 3.0315 | -1.0251 | 12.0411 | 4.8702 | 0.6218 | 0.6655 | 0.9632 | 0.7475 | -129.275 | 1.3358 | 5.6561 | 1.8439 | -2.4658 | -0.9256 | 4.8971 |  | 4.0016 | 0.7028 | 4.0092 | 3.3668 | 3.34 | 1.0879 | 10.8135 | 14.2926 | 14.8723 | 11.1259 | 0.0001 | -0.0029 | 0.0009 | 0.0039 | 0.0007 | -0.0003 | -0.0024 | -0.012 | -0.0143 | -360.1711 | 17.372 | -360.3804 | 17.6266 | -360.7466 | 18.1892 | -360.8727 | 17.5958 | -352.6136 | 18.6881 | -352.5552 | 16.7807
12:49 | 5376 | 44.7717 | 202.6642 | 450.2107 | 457.1003 | -16.4316 | -39.6485 | 11.6478 | 8.1032 | 2.5391 | 0.7339 | 3.1069 | -0.9759 | 12.1231 | 5.0018 | 0.6215 | 0.6642 | 0.9627 | 0.7492 | -129.2943 | 1.3119 | 5.5645 | 1.9489 | -2.5054 | -0.9528 | 4.8675 |  | 4.0039 | 0.7359 | 4.0114 | 3.3672 | 3.3392 | 1.0881 | 10.766 | 14.2567 | 14.8188 | 11.1017 | -0.0004 | -0.0027 | 0.0008 | 0.0037 | 0.0011 | -0.0009 | 0.0274 | -0.0073 | -0.0006 | -360.1681 | 17.4192 | -360.4789 | 17.6636 | -360.8081 | 18.1481 | -360.7589 | 17.5465 | -352.6075 | 18.721 | -352.6567 | 16.8156
12:49 | 5377 | 44.7958 | 202.6955 | 450.1494 | 457.0762 | -16.3888 | -39.6659 | 11.6761 | 8.0339 | 2.3689 | 0.7712 | 2.9863 | -0.97 | 12.0854 | 4.8739 | 0.6211 | 0.665 | 0.9613 | 0.7492 | -129.2631 | 1.2482 | 5.5888 | 1.9623 | -2.4138 | -0.9606 | 4.8808 |  | 3.9971 | 0.6675 | 4.011 | 3.3663 | 3.3382 | 1.0886 | 10.7879 | 14.2905 | 14.8717 | 11.1056 | -0.0004 | -0.0026 | 0.0008 | 0.0042 | 0.0008 | -0.0001 | 0.0216 | -0.0118 | 0.0089 | -360.0942 | 17.3658 | -360.3712 | 17.6492 | -360.8081 | 18.2138 | -360.8543 | 17.5671 | -352.5829 | 18.6676 | -352.586 | 16.8115
12:49 | 5378 | 44.7566 | 202.5845 | 450.192 | 457.0972 | -16.4577 | -39.6305 | 11.5787 | 7.9789 | 2.4254 | 0.7238 | 2.9641 | -0.9973 | 12.0767 | 4.8903 | 0.6216 | 0.6641 | 0.9602 | 0.7483 | -129.339 | 1.2209 | 5.5067 | 1.9993 | -2.4445 | -0.9247 | 4.9737 |  | 4.0304 | 0.6576 | 4.0105 | 3.3669 | 3.3391 | 1.0875 | 10.8018 | 14.3104 | 14.8813 | 11.0901 | 0.0001 | -0.003 | 0.0002 | 0.0038 | 0.0012 | -0.0001 | 0.0207 | -0.0083 | -0.0097 | -360.1527 | 17.409 | -360.4204 | 17.6266 | -360.7343 | 18.1502 | -360.7835 | 17.5732 | -352.6167 | 18.7128 | -352.629 | 16.795
12:49 | 5379 | 44.753 | 202.582 | 450.1651 | 457.0586 | -16.4765 | -39.5922 | 11.6502 | 8.0343 | 2.4506 | 0.7963 | 3.0449 | -0.9921 | 12.0688 | 4.8707 | 0.6205 | 0.6618 | 0.96 | 0.749 | -129.2562 | 1.2578 | 5.6176 | 1.9467 | -2.427 | -0.9018 | 4.9035 |  | 3.9298 | 0.6842 | 4.0098 | 3.3663 | 3.339 | 1.0887 | 10.7961 | 14.2928 | 14.8791 | 11.085 | 0.0002 | -0.003 | 0.0008 | 0.004 | 0.0009 | -0.0004 | 0.0089 | -0.0052 | 0.0026 | -360.1127 | 17.3761 | -360.4296 | 17.6779 | -360.8389 | 18.181 | -360.7773 | 17.5404 | -352.5398 | 18.6737 | -352.6167 | 16.8217
12:49 | 5380 | 44.7991 | 202.642 | 450.2029 | 457.2044 | -16.4422 | -39.5894 | 11.7281 | 8.0208 | 2.5482 | 0.7378 | 3.0729 | -1.0577 | 12.1191 | 4.8959 | 0.6214 | 0.6618 | 0.9593 | 0.7471 | -129.2833 | 1.2606 | 5.649 | 1.9278 | -2.503 | -1.0387 | 4.8468 |  | 3.9554 | 0.5833 | 4.0098 | 3.3694 | 3.3419 | 1.0888 | 10.7856 | 14.2882 | 14.8805 | 11.0977 | 0.0001 | -0.0023 | 0.0007 | 0.004 | 0.0009 | -0.0001 | 0.012 | -0.0096 | -0.0015 | -360.1711 | 17.3946 | -360.4081 | 17.6286 | -360.7312 | 18.1748 | -360.805 | 17.5814 | -352.586 | 18.682 | -352.586 | 16.793
12:49 | 5381 | 44.7645 | 202.6282 | 450.3028 | 457.211 | -16.4045 | -39.624 | 11.7382 | 8.0035 | 2.4686 | 0.8 | 3.123 | -1.0431 | 11.9791 | 4.9352 | 0.6209 | 0.6662 | 0.9636 | 0.7488 | -129.2528 | 1.2873 | 5.7058 | 1.8187 | -2.4946 | -0.9606 | 4.8126 |  | 3.8656 | 0.6068 | 4.0103 | 3.368 | 3.3358 | 1.0897 | 10.7788 | 14.2693 | 14.8481 | 11.1089 | -0.0001 | -0.0027 | 0.0009 | 0.0034 | 0.0008 | -0.0011 | 0.024 | -0.0175 | 0.0182 | -360.1281 | 17.4028 | -360.4666 | 17.6697 | -360.805 | 18.1358 | -360.762 | 17.5506 | -352.5736 | 18.7045 | -352.6506 | 16.8217
12:49 | 5382 | 44.7371 | 202.5335 | 450.2167 | 457.0951 | -16.4399 | -39.5566 | 11.6744 | 7.977 | 2.4158 | 0.7041 | 3.0662 | -1.0413 | 11.9709 | 4.9785 | 0.6219 | 0.6558 | 0.9582 | 0.748 | -129.2312 | 1.2042 | 5.6084 | 1.9902 | -2.4618 | -0.8456 | 4.9495 |  | 3.9533 | 0.6236 | 4.0097 | 3.3612 | 3.3347 | 1.09 | 10.7984 | 14.2778 | 14.8471 | 11.1161 | 0.0003 | -0.0026 | 0.0014 | 0.0045 | 0.0004 | -0.0002 | 0.011 | -0.0056 | -0.0197 | -360.1773 | 17.3782 | -360.4204 | 17.643 | -360.802 | 18.181 | -360.8143 | 17.5588 | -352.5798 | 18.6861 | -352.6013 | 16.8053
12:49 | 5383 | 44.6634 | 202.6504 | 450.2637 | 457.128 | -16.3869 | -39.7142 | 11.7348 | 7.9834 | 2.4678 | 0.5946 | 3.0565 | -1.0772 | 11.9475 | 4.8825 | 0.6217 | 0.663 | 0.9624 | 0.7491 | -129.2413 | 1.2165 | 5.7036 | 1.9907 | -2.494 | -0.8874 | 4.8395 |  | 3.931 | 0.5649 | 4.0111 | 3.3653 | 3.3365 | 1.089 | 10.7902 | 14.2813 | 14.8686 | 11.0962 | 0.0001 | -0.0028 | 0.0009 | 0.0038 | 0.0013 | -0.0005 | 0.0129 | -0.0026 | -0.0196 | -360.1804 | 17.4131 | -360.4666 | 17.6553 | -360.802 | 18.1769 | -360.8204 | 17.5732 | -352.6044 | 18.721 | -352.6352 | 16.8115
12:49 | 5384 | 44.6935 | 202.6199 | 450.2023 | 457.1523 | -16.4817 | -39.6813 | 11.6647 | 8.0065 | 2.456 | 0.6219 | 3.1313 | -0.9846 | 12.0432 | 4.9809 | 0.6229 | 0.6632 | 0.962 | 0.748 | -129.1846 | 1.3574 | 5.7581 | 2.0198 | -2.4995 | -0.9531 | 4.8955 |  | 4.0158 | 0.5553 | 4.0095 | 3.3657 | 3.3384 | 1.0902 | 10.7995 | 14.2732 | 14.8485 | 11.1114 | 0 | -0.0017 | 0.0007 | 0.0036 | 0.0005 | -0.0004 | 0.0183 | -0.0175 | 0.0059 | -360.1619 | 17.4007 | -360.4573 | 17.6636 | -360.8143 | 18.1994 | -360.8327 | 17.5732 | -352.5706 | 18.6881 | -352.626 | 16.8217
12:49 | 5385 | 44.5842 | 202.6088 | 450.0616 | 457.1204 | -16.3501 | -39.6027 | 11.6935 | 7.9969 | 2.5095 | 0.7543 | 3.0587 | -0.9802 | 12.0543 | 4.9597 | 0.6205 | 0.664 | 0.9631 | 0.7474 | -129.1693 | 1.2725 | 5.7592 | 1.9773 | -2.4439 | -1.0969 | 4.8351 |  | 3.9225 | 0.639 | 4.0089 | 3.3668 | 3.338 | 1.0882 | 10.7556 | 14.2695 | 14.8433 | 11.1143 | -0.0003 | -0.0024 | 0.0008 | 0.0042 | 0.0015 | -0.0007 | 0.0142 | -0.0014 | -0.0034 | -360.1865 | 17.409 | -360.4419 | 17.6656 | -360.7897 | 18.1933 | -360.8266 | 17.5855 | -352.6352 | 18.7066 | -352.6321 | 16.8074
12:49 | 5386 | 44.6088 | 202.5402 | 450.1009 | 456.997 | -16.4137 | -39.5871 | 11.7 | 7.9605 | 2.5176 | 0.6717 | 3.0383 | -1.1022 | 11.9924 | 4.9403 | 0.6199 | 0.6633 | 0.9641 | 0.7474 | -129.1952 | 1.2423 | 5.6647 | 2.0556 | -2.446 | -1.0134 | 4.9104 |  | 4.053 | 0.7149 | 4.0105 | 3.3681 | 3.3434 | 1.0898 | 10.7776 | 14.297 | 14.8409 | 11.102 | 0.0001 | -0.003 | 0.0001 | 0.0034 | 0.0005 | -0.0005 | 0.0123 | -0.0097 | -0.0211 | -360.1158 | 17.3966 | -360.4696 | 17.6861 | -360.8543 | 18.2015 | -360.8297 | 17.5609 | -352.5613 | 18.7045 | -352.6383 | 16.8238
12:49 | 5387 | 44.6616 | 202.6399 | 450.213 | 457.1211 | -16.3981 | -39.5385 | 11.732 | 7.9645 | 2.4693 | 0.6312 | 3.0337 | -1.0417 | 12.055 | 4.9473 | 0.6216 | 0.6613 | 0.9631 | 0.7491 | -129.2135 | 1.263 | 5.6536 | 2.0162 | -2.47 | -1.067 | 4.8537 |  | 3.971 | 0.5981 | 4.0103 | 3.3668 | 3.3396 | 1.0906 | 10.8077 | 14.252 | 14.8307 | 11.0858 | 0 | -0.0031 | 0.0009 | 0.0044 | 0.0011 | -0.0009 | -0.0015 | -0.0003 | -0.0186 | -360.1742 | 17.3946 | -360.4235 | 17.6697 | -360.8358 | 18.2036 | -360.8635 | 17.5937 | -352.6136 | 18.6984 | -352.586 | 16.8094
12:50 | 5388 | 44.7302 | 202.6994 | 450.1756 | 457.1915 | -16.4067 | -39.5915 | 11.6568 | 7.9215 | 2.412 | 0.6035 | 2.9904 | -1.0364 | 12.0948 | 5.018 | 0.6215 | 0.6605 | 0.9631 | 0.7488 | -129.1531 | 1.399 | 5.7532 | 1.9606 | -2.5629 | -1.009 | 4.926 |  | 3.9583 | 0.6497 | 4.0101 | 3.372 | 3.3392 | 1.0897 | 10.7788 | 14.2634 | 14.8412 | 11.0977 | -0.0002 | -0.0032 | 0.0006 | 0.0035 | 0.0005 | -0.0003 | -0.0019 | -0.012 | -0.0045 | -360.2142 | 17.448 | -360.5096 | 17.6738 | -360.8174 | 18.1687 | -360.8389 | 17.5999 | -352.6998 | 18.7477 | -352.666 | 16.8135
12:50 | 5389 | 44.7518 | 202.5634 | 450.1952 | 457.1015 | -16.5584 | -39.6334 | 11.5735 | 7.9674 | 2.5593 | 0.6089 | 3.0703 | -1.0492 | 12.0795 | 5.0477 | 0.6214 | 0.6616 | 0.9593 | 0.7488 | -129.2064 | 1.2838 | 5.6712 | 2.0668 | -2.5396 | -1.0083 | 4.828 |  | 3.982 | 0.7076 | 4.0105 | 3.3685 | 3.3377 | 1.0898 | 10.788 | 14.2788 | 14.8417 | 11.0771 | 0 | -0.0025 | 0.0009 | 0.0039 | 0.001 | -0.0004 | 0.0077 | -0.0055 | 0.0146 | -360.1311 | 17.3966 | -360.4542 | 17.7087 | -360.8697 | 18.2015 | -360.845 | 17.5794 | -352.5829 | 18.6963 | -352.6444 | 16.8402
12:50 | 5390 | 44.7618 | 202.6178 | 450.2441 | 457.2184 | -16.4771 | -39.6736 | 11.5561 | 7.9298 | 2.5684 | 0.566 | 3.0694 | -1.0116 | 12.0653 | 5.0599 | 0.6221 | 0.664 | 0.9668 | 0.7492 | -129.2328 | 1.2139 | 5.6461 | 1.8672 | -2.4459 | -1.0453 | 4.8588 |  | 3.9369 | 0.616 | 4.0106 | 3.3685 | 3.3382 | 1.0898 | 10.7845 | 14.2868 | 14.8723 | 11.0912 | 0.0001 | -0.003 | 0.0012 | 0.0041 | 0.0011 | 0.0001 | 0.0057 | -0.0054 | -0.0025 | -360.2296 | 17.4254 | -360.4604 | 17.6636 | -360.7712 | 18.1625 | -360.8697 | 17.6204 | -352.6813 | 18.7353 | -352.6383 | 16.7971
12:50 | 5391 | 44.767 | 202.6346 | 450.218 | 457.1563 | -16.4452 | -39.5579 | 11.654 | 7.9433 | 2.5597 | 0.6368 | 3.0683 | -0.9896 | 12.0834 | 5.0656 | 0.6222 | 0.6611 | 0.9668 | 0.7482 | -129.1866 | 1.3316 | 5.6458 | 1.7565 | -2.4489 | -0.9793 | 4.9487 |  | 3.9383 | 0.6217 | 4.011 | 3.365 | 3.3355 | 1.0885 | 10.7856 | 14.3055 | 14.8631 | 11.1208 | 0 | -0.0028 | 0.0009 | 0.004 | 0.0004 | -0.0005 | 0.0209 | -0.015 | -0.0084 | -360.1742 | 17.4295 | -360.5096 | 17.719 | -360.882 | 18.1789 | -360.7989 | 17.565 | -352.6106 | 18.7271 | -352.706 | 16.8669
12:50 | 5392 | 44.7737 | 202.665 | 450.2658 | 457.0429 | -16.4835 | -39.6885 | 11.5826 | 7.9006 | 2.4727 | 0.5248 | 2.9836 | -0.9754 | 12.0472 | 5.034 | 0.6221 | 0.6648 | 0.9628 | 0.747 | -129.2483 | 1.34 | 5.7154 | 1.761 | -2.4615 | -0.8804 | 4.9076 |  | 3.9784 | 0.6354 | 4.0094 | 3.3655 | 3.3373 | 1.0883 | 10.7915 | 14.2996 | 14.8389 | 11.0807 | -0.0002 | -0.0028 | 0.0005 | 0.0041 | 0.0007 | -0.0007 | 0.0115 | -0.008 | 0.0086 | -360.2081 | 17.409 | -360.4204 | 17.6615 | -360.8235 | 18.1892 | -360.885 | 17.6122 | -352.6413 | 18.6984 | -352.6075 | 16.8094
12:50 | 5393 | 44.7074 | 202.6529 | 450.2431 | 457.0863 | -16.4515 | -39.623 | 11.5701 | 7.8623 | 2.5192 | 0.5756 | 3.0246 | -0.8745 | 12.0228 | 5.0275 | 0.6204 | 0.6633 | 0.9649 | 0.7493 | -129.2943 | 1.3409 | 5.6357 | 1.8561 | -2.4803 | -0.9721 | 4.8273 |  | 4.0127 | 0.539 | 4.0104 | 3.3713 | 3.3374 | 1.0903 | 10.7972 | 14.3171 | 14.9095 | 11.1381 | -0.0007 | -0.0029 | 0.001 | 0.0045 | 0.0007 | -0.0001 | 0.0053 | -0.0058 | -0.0072 | -360.245 | 17.45 | -360.5096 | 17.6964 | -360.8358 | 18.1502 | -360.802 | 17.5958 | -352.6413 | 18.7497 | -352.7183 | 16.8402
12:50 | 5394 | 44.8209 | 202.7416 | 450.2274 | 457.0959 | -16.4969 | -39.5502 | 11.6077 | 7.9546 | 2.5976 | 0.6362 | 3.0824 | -0.8969 | 12.0521 | 5.0196 | 0.6202 | 0.6622 | 0.9629 | 0.747 | -129.2725 | 1.2833 | 5.707 | 1.8606 | -2.4613 | -0.9935 | 4.814 |  | 4.0265 | 0.5853 | 4.0089 | 3.3691 | 3.3372 | 1.0894 | 10.8145 | 14.2999 | 14.8642 | 11.1089 | 0.0001 | -0.003 | 0.0008 | 0.0041 | 0.0007 | -0.0009 | 0.004 | -0.0042 | -0.0139 | -360.1558 | 17.3987 | -360.4481 | 17.7046 | -360.885 | 18.1994 | -360.8604 | 17.5814 | -352.6075 | 18.7066 | -352.6475 | 16.8443
12:50 | 5395 | 44.7738 | 202.7801 | 450.2469 | 457.1428 | -16.5564 | -39.6652 | 11.6503 | 8.0557 | 2.5019 | 0.609 | 3.0706 | -0.9866 | 12.0078 | 5.0285 | 0.621 | 0.6617 | 0.9662 | 0.7489 | -129.1992 | 1.3263 | 5.7456 | 1.8907 | -2.3273 | -0.8882 | 4.8514 |  | 4.014 | 0.5943 | 4.0094 | 3.3702 | 3.3409 | 1.0899 | 10.8007 | 14.2856 | 14.8825 | 11.119 | -0.0003 | -0.0035 | 0.001 | 0.0044 | 0.0008 | -0.0001 | 0.0167 | 0.0109 | -0.0061 | -360.2235 | 17.4295 | -360.4573 | 17.6636 | -360.7743 | 18.1584 | -360.8697 | 17.6143 | -352.6906 | 18.7353 | -352.6444 | 16.7971
12:50 | 5396 | 44.7533 | 202.7012 | 450.2275 | 457.09 | -16.5068 | -39.6161 | 11.6479 | 8.0828 | 2.5405 | 0.7528 | 3.1516 | -0.9928 | 11.9894 | 5.0551 | 0.6208 | 0.6628 | 0.9607 | 0.7487 | -129.2114 | 1.2658 | 5.7114 | 1.9857 | -2.3059 | -0.9854 | 4.9004 |  | 4.0353 | 0.6092 | 4.0087 | 3.3673 | 3.3389 | 1.0892 | 10.8134 | 14.2871 | 14.8802 | 11.1309 | 0 | -0.0027 | 0.0011 | 0.0038 | 0.0009 | -0.0008 | 0.0135 | -0.0065 | -0.002 | -360.165 | 17.4274 | -360.5158 | 17.7169 | -360.8727 | 18.1687 | -360.8266 | 17.5876 | -352.6106 | 18.7312 | -352.6937 | 16.8505
12:50 | 5397 | 44.8291 | 202.6817 | 450.2098 | 457.1044 | -16.4906 | -39.6803 | 11.6572 | 7.9816 | 2.5041 | 0.6618 | 3.1485 | -1.0416 | 12.007 | 4.9257 | 0.6204 | 0.6626 | 0.9623 | 0.7489 | -129.1334 | 1.219 | 5.6564 | 2.0042 | -2.3041 | -0.8178 | 4.9691 |  | 3.9978 | 0.5631 | 4.0091 | 3.3695 | 3.3398 | 1.0886 | 10.8111 | 14.2905 | 14.8369 | 11.0998 | -0.0001 | -0.0026 | 0.0009 | 0.0034 | 0.0006 | -0.0004 | 0.0075 | 0.002 | -0.0217 | -360.1896 | 17.411 | -360.445 | 17.6738 | -360.8174 | 18.1789 | -360.8635 | 17.6184 | -352.626 | 18.7148 | -352.6383 | 16.8238
12:50 | 5398 | 44.8177 | 202.612 | 450.1961 | 457.1342 | -16.568 | -39.6212 | 11.6194 | 7.9575 | 2.4579 | 0.6955 | 3.1019 | -1.0362 | 12.0905 | 4.9341 | 0.6194 | 0.6595 | 0.9609 | 0.7489 | -129.119 | 1.3439 | 5.7016 | 1.9342 | -2.3147 | -0.8916 | 4.8881 |  | 3.9703 | 0.5791 | 4.0106 | 3.3667 | 3.34 | 1.0891 | 10.788 | 14.2904 | 14.8706 | 11.106 | 0.0001 | -0.003 | 0.0008 | 0.0037 | 0.0012 | -0.0004 | 0.0038 | -0.0076 | -0.0168 | -360.2173 | 17.4315 | -360.5035 | 17.6759 | -360.8174 | 18.1666 | -360.8266 | 17.604 | -352.6506 | 18.7395 | -352.6813 | 16.8299
12:50 | 5399 | 44.7592 | 202.7575 | 450.2654 | 457.1659 | -16.4433 | -39.4853 | 11.7612 | 8.0155 | 2.4912 | 0.6766 | 3.1347 | -1.0097 | 12.0363 | 4.888 | 0.6198 | 0.6582 | 0.9587 | 0.7479 | -129.1688 | 1.3277 | 5.7446 | 1.8499 | -2.3637 | -0.9123 | 4.9131 |  | 3.9691 | 0.531 | 4.0107 | 3.3678 | 3.3383 | 1.088 | 10.7683 | 14.2533 | 14.8389 | 11.0923 | 0.0002 | -0.0029 | 0.0008 | 0.0033 | 0.0005 | -0.0002 | 0.0253 | -0.0078 | -0.0017 | -360.1835 | 17.4131 | -360.4758 | 17.6677 | -360.8143 | 18.181 | -360.8481 | 17.604 | -352.669 | 18.7128 | -352.6567 | 16.8299
12:50 | 5400 | 44.8196 | 202.7718 | 450.3085 | 457.2593 | -16.4744 | -39.62 | 11.8338 | 8.0005 | 2.4585 | 0.7373 | 3.1705 | -0.9563 | 12.0728 | 4.9474 | 0.6213 | 0.6645 | 0.9649 | 0.7501 | -129.1279 | 1.2482 | 5.7886 | 1.7935 | -2.422 | -0.9694 | 4.9558 |  | 4.1028 | 0.5798 | 4.0108 | 3.3663 | 3.3395 | 1.0904 | 10.7661 | 14.2739 | 14.8583 | 11.0847 | -0.0001 | -0.0029 | 0.0006 | 0.0039 | 0.0007 | -0.0006 | 0.0121 | -0.0057 | -0.0316 | -360.1958 | 17.4069 | -360.4512 | 17.682 | -360.8297 | 18.1707 | -360.8204 | 17.6081 | -352.6506 | 18.7045 | -352.6598 | 16.834
12:50 | 5401 | 44.7236 | 202.8448 | 450.1359 | 457.1462 | -16.5039 | -39.5163 | 11.7451 | 7.9839 | 2.447 | 0.6432 | 3.1559 | -0.981 | 12.0991 | 5.0178 | 0.6202 | 0.6636 | 0.9639 | 0.7486 | -129.3216 | 1.2882 | 5.6026 | 1.7952 | -2.5088 | -0.9772 | 4.8496 |  | 3.8981 | 0.5945 | 4.0093 | 3.3677 | 3.3371 | 1.0894 | 10.7821 | 14.2616 | 14.8775 | 11.0998 | -0.0005 | -0.0026 | 0.0009 | 0.0043 | 0.001 | -0.0003 | 0.009 | -0.0107 | 0.0093 | -360.1773 | 17.4131 | -360.4666 | 17.6902 | -360.8574 | 18.1851 | -360.8297 | 17.5896 | -352.6198 | 18.7025 | -352.6567 | 16.8443
12:50 | 5402 | 44.708 | 202.6842 | 450.1435 | 457.0524 | -16.4321 | -39.4926 | 11.7674 | 8.0646 | 2.5139 | 0.6048 | 3.3821 | -0.985 | 12.0703 | 4.8615 | 0.6194 | 0.662 | 0.9571 | 0.7486 | -129.2075 | 1.237 | 5.5738 | 1.877 | -2.4862 | -0.9174 | 4.8539 |  | 3.9719 | 0.6204 | 4.0091 | 3.3657 | 3.3358 | 1.0897 | 10.8031 | 14.2821 | 14.8494 | 11.0984 | 0 | -0.0029 | 0.0003 | 0.0039 | 0.0008 | -0.0004 | -0.0005 | -0.0075 | -0.0108 | -360.1865 | 17.4007 | -360.4296 | 17.6574 | -360.805 | 18.1728 | -360.8543 | 17.6122 | -352.6567 | 18.7045 | -352.6321 | 16.8135
12:50 | 5403 | 44.7641 | 202.6941 | 450.2102 | 457.1214 | -16.4282 | -39.5 | 11.6472 | 8.0563 | 2.5804 | 0.7066 | 3.313 | -1.0096 | 12.0322 | 4.8825 | 0.6208 | 0.6634 | 0.9609 | 0.7485 | -129.314 | 1.254 | 5.5861 | 1.9656 | -2.5076 | -0.9637 | 4.869 |  | 4.051 | 0.617 | 4.0098 | 3.3668 | 3.3363 | 1.0901 | 10.7972 | 14.2766 | 14.8516 | 11.0919 | 0.0006 | -0.0023 | 0.0008 | 0.0045 | 0.0008 | -0.0004 | 0.0165 | -0.0025 | -0.0175 | -360.1773 | 17.4131 | -360.485 | 17.6861 | -360.8327 | 18.1502 | -360.8143 | 17.5896 | -352.6383 | 18.7148 | -352.6567 | 16.8279
12:50 | 5404 | 44.7657 | 202.6238 | 450.1864 | 457.0591 | -16.5374 | -39.6483 | 11.6107 | 8.0721 | 2.5512 | 0.6985 | 3.2899 | -0.9885 | 12.0109 | 4.8974 | 0.6202 | 0.6641 | 0.9621 | 0.7464 | -129.2642 | 1.3483 | 5.5807 | 1.952 | -2.6136 | -1.0545 | 4.8099 |  | 4.0163 | 0.6399 | 4.0086 | 3.3657 | 3.3377 | 1.0905 | 10.7775 | 14.2802 | 14.8557 | 11.1183 | 0.0004 | -0.0024 | 0.001 | 0.004 | 0.001 | -0.0001 | -0.0021 | -0.0049 | -0.0218 | -360.125 | 17.3946 | -360.4296 | 17.6718 | -360.8512 | 18.1769 | -360.8389 | 17.5855 | -352.6075 | 18.684 | -352.6506 | 16.834
12:50 | 5405 | 44.85 | 202.6542 | 450.2394 | 457.0772 | -16.5571 | -39.5911 | 11.6421 | 8.0685 | 2.4818 | 0.582 | 3.2718 | -0.9993 | 12.0323 | 4.8917 | 0.6207 | 0.6603 | 0.965 | 0.7487 | -129.1845 | 1.3531 | 5.6652 | 1.9335 | -2.5127 | -1.0616 | 4.8541 |  | 3.9901 | 0.6387 | 4.0091 | 3.3676 | 3.3379 | 1.0914 | 10.7731 | 14.2923 | 14.8239 | 11.0862 | -0.0005 | -0.0029 | 0.0006 | 0.0037 | 0.0006 | -0.0006 | 0.005 | 0.0069 | -0.0043 | -360.2081 | 17.3966 | -360.4296 | 17.6451 | -360.7589 | 18.1543 | -360.8543 | 17.6245 | -352.6444 | 18.7148 | -352.6167 | 16.795
12:50 | 5406 | 44.8953 | 202.6682 | 450.227 | 457.1244 | -16.4357 | -39.6238 | 11.6703 | 8.0536 | 2.4688 | 0.6263 | 3.3224 | -1.0089 | 11.9724 | 4.9096 | 0.621 | 0.6668 | 0.9607 | 0.7475 | -129.2779 | 1.2888 | 5.6572 | 1.9235 | -2.4618 | -1.1251 | 4.815 |  | 4.0517 | 0.5203 | 4.0104 | 3.3677 | 3.3386 | 1.0916 | 10.7891 | 14.2744 | 14.8673 | 11.1125 | 0.0002 | -0.0025 | 0.0007 | 0.0035 | 0.0005 | -0.0004 | 0.0178 | -0.0062 | -0.0019 | -360.1527 | 17.409 | -360.4789 | 17.7026 | -360.8481 | 18.1522 | -360.802 | 17.5773 | -352.6198 | 18.7107 | -352.6998 | 16.8464
12:50 | 5407 | 44.9602 | 202.6466 | 450.2559 | 457.122 | -16.5389 | -39.6355 | 11.6437 | 8.0035 | 2.4655 | 0.5997 | 3.3122 | -1.0007 | 12.0691 | 4.9261 | 0.6211 | 0.6635 | 0.963 | 0.7476 | -129.1749 | 1.2791 | 5.6323 | 1.9349 | -2.4552 | -0.9575 | 4.8914 |  | 3.9938 | 0.5406 | 4.0096 | 3.3693 | 3.3391 | 1.0903 | 10.7754 | 14.2889 | 14.844 | 11.1057 | 0.0001 | -0.0033 | 0.0012 | 0.0038 | 0.0009 | -0.0007 | 0.0084 | -0.0151 | -0.0168 | -360.205 | 17.374 | -360.3958 | 17.6492 | -360.7804 | 18.1687 | -360.882 | 17.604 | -352.6629 | 18.684 | -352.5798 | 16.7909
12:50 | 5408 | 44.8326 | 202.637 | 450.1225 | 457.1543 | -16.4121 | -39.6087 | 11.6028 | 8.0309 | 2.5323 | 0.6308 | 3.3596 | -0.9318 | 12.1067 | 4.9213 | 0.6213 | 0.6615 | 0.9625 | 0.7476 | -129.2392 | 1.2739 | 5.5274 | 1.9412 | -2.524 | -1.0377 | 4.9014 |  | 4.017 | 0.579 | 4.0095 | 3.3698 | 3.3407 | 1.0913 | 10.7579 | 14.295 | 14.8577 | 11.0934 | -0.0001 | -0.0028 | 0.0009 | 0.0045 | 0.0006 | -0.0001 | 0.0117 | -0.0146 | -0.0292 | -360.1681 | 17.4336 | -360.4666 | 17.682 | -360.7958 | 18.1358 | -360.7743 | 17.5876 | -352.626 | 18.7189 | -352.6721 | 16.8258
12:50 | 5409 | 44.8407 | 202.6047 | 450.2582 | 457.1215 | -16.4452 | -39.6929 | 11.6222 | 7.9614 | 2.5006 | 0.6055 | 3.3828 | -0.9333 | 12.0331 | 4.9594 | 0.6225 | 0.6631 | 0.9592 | 0.7466 | -129.2179 | 1.3145 | 5.5677 | 1.9451 | -2.5205 | -1.0601 | 4.8808 |  | 4.022 | 0.6232 | 4.0095 | 3.3704 | 3.3402 | 1.0917 | 10.7845 | 14.2521 | 14.8318 | 11.1085 | -0.0003 | -0.0027 | 0.0006 | 0.004 | 0.0011 | -0.0009 | 0.0081 | -0.0123 | 0.0027 | -360.0973 | 17.374 | -360.4173 | 17.6759 | -360.8143 | 18.1789 | -360.8666 | 17.5835 | -352.6136 | 18.6717 | -352.6106 | 16.832
12:50 | 5410 | 44.8592 | 202.6257 | 450.1754 | 457.1091 | -16.4548 | -39.6627 | 11.6963 | 8.0007 | 2.4925 | 0.6485 | 3.4249 | -0.9488 | 12.0722 | 5.0278 | 0.6219 | 0.6625 | 0.9639 | 0.7471 | -129.1877 | 1.352 | 5.705 | 1.9648 | -2.6206 | -0.9612 | 4.8705 |  | 4.0108 | 0.5691 | 4.0099 | 3.3681 | 3.3357 | 1.0898 | 10.803 | 14.3111 | 14.8679 | 11.1212 | -0.0004 | -0.0029 | 0.0007 | 0.004 | 0.0006 | -0.0005 | 0.0072 | -0.0119 | 0.0118 | -360.205 | 17.4274 | -360.4296 | 17.6369 | -360.7497 | 18.142 | -360.8266 | 17.6286 | -352.6721 | 18.7087 | -352.6383 | 16.795
12:50 | 5411 | 44.7679 | 202.6236 | 450.1406 | 457.0252 | -16.48 | -39.631 | 11.7414 | 8.0242 | 2.5184 | 0.6704 | 3.4443 | -1.0122 | 12.0314 | 4.8332 | 0.6212 | 0.6644 | 0.9611 | 0.7466 | -129.2633 | 1.3422 | 5.6707 | 1.9744 | -2.5744 | -0.9692 | 4.8986 |  | 3.9598 | 0.4874 | 4.0087 | 3.3722 | 3.3364 | 1.0909 | 10.7707 | 14.2671 | 14.8406 | 11.1006 | 0.0002 | -0.0029 | 0.0003 | 0.0038 | 0.001 | -0.0006 | 0.0139 | -0.002 | -0.0014 | -360.1373 | 17.4048 | -360.4758 | 17.7149 | -360.8697 | 18.1543 | -360.7866 | 17.565 | -352.5983 | 18.7087 | -352.6875 | 16.8525
12:50 | 5412 | 44.7563 | 202.5485 | 450.1162 | 457.0637 | -16.5226 | -39.7944 | 11.5874 | 8.0229 | 2.5604 | 0.7526 | 3.3905 | -0.9725 | 11.9989 | 4.9124 | 0.6216 | 0.6623 | 0.9667 | 0.7491 | -129.3546 | 1.2554 | 5.6713 | 1.6932 | -2.6401 | -0.917 | 4.9003 |  | 4.0388 | 0.6078 | 4.0092 | 3.3687 | 3.3335 | 1.0878 | 10.8181 | 14.2511 | 14.8546 | 11.1244 | -0.0002 | -0.0031 | 0.0009 | 0.0034 | 0.0008 | 0.0001 | 0.0102 | -0.0027 | -0.0207 | -360.1865 | 17.3638 | -360.3712 | 17.6553 | -360.7835 | 18.1748 | -360.8666 | 17.5937 | -352.6229 | 18.684 | -352.589 | 16.8053
12:50 | 5413 | 44.8963 | 202.6767 | 450.1573 | 457.1619 | -16.4479 | -39.7123 | 11.5447 | 8.0617 | 2.4858 | 0.6356 | 3.3677 | -0.9985 | 11.9398 | 4.8707 | 0.621 | 0.6605 | 0.9616 | 0.7472 | -129.2552 | 1.3175 | 5.6693 | 1.7411 | -2.5848 | -0.9569 | 4.8494 |  | 4.0272 | 0.5702 | 4.009 | 3.3666 | 3.3363 | 1.089 | 10.7659 | 14.2917 | 14.8267 | 11.0836 | -0.0001 | -0.0024 | 0.0008 | 0.0038 | 0.0012 | -0.0001 | 0.0164 | -0.0023 | -0.0036 | -360.1404 | 17.4336 | -360.4789 | 17.6677 | -360.8112 | 18.1255 | -360.7835 | 17.5978 | -352.6813 | 18.7169 | -352.6783 | 16.8074
12:50 | 5414 | 44.7866 | 202.6495 | 450.2386 | 457.1241 | -16.5276 | -39.6029 | 11.5921 | 8.0634 | 2.5358 | 0.7256 | 3.3594 | -1.0245 | 11.979 | 4.8393 | 0.6217 | 0.6634 | 0.9637 | 0.7471 | -129.2251 | 1.319 | 5.7577 | 1.8557 | -2.564 | -0.7759 | 4.8708 |  | 4.1044 | 0.5849 | 4.0102 | 3.3706 | 3.3375 | 1.0893 | 10.7892 | 14.303 | 14.8941 | 11.119 | -0.0002 | -0.003 | 0.001 | 0.0037 | 0.0005 | -0.0005 | 0.0023 | -0.0202 | -0.0032 | -360.1373 | 17.3802 | -360.4512 | 17.6861 | -360.8297 | 18.1707 | -360.8112 | 17.5712 | -352.5921 | 18.6779 | -352.6444 | 16.832
12:50 | 5415 | 44.92 | 202.6609 | 450.2313 | 457.153 | -16.5437 | -39.5604 | 11.7015 | 8.0511 | 2.4722 | 0.7579 | 3.2918 | -0.9705 | 11.997 | 4.8619 | 0.6203 | 0.6653 | 0.9647 | 0.7476 | -129.2215 | 1.2315 | 5.7055 | 1.9019 | -2.5132 | -0.8382 | 4.82 |  | 3.9791 | 0.5755 | 4.0086 | 3.3652 | 3.3358 | 1.0894 | 10.803 | 14.3055 | 14.8747 | 11.1323 | 0.0003 | -0.003 | 0.0008 | 0.0039 | 0.001 | -0.0002 | 0.0112 | -0.0076 | -0.0126 | -360.1896 | 17.4069 | -360.4112 | 17.6553 | -360.7804 | 18.1461 | -360.8912 | 17.6286 | -352.6752 | 18.6902 | -352.6444 | 16.8012
12:50 | 5416 | 44.8663 | 202.6922 | 450.3282 | 457.0932 | -16.5194 | -39.488 | 11.583 | 8.037 | 2.4016 | 0.7434 | 3.3669 | -1.0004 | 12.0087 | 4.8823 | 0.621 | 0.6607 | 0.9625 | 0.7485 | -129.2217 | 1.2713 | 5.648 | 1.8534 | -2.4703 | -0.8745 | 4.9004 |  | 3.9814 | 0.5863 | 4.0083 | 3.3662 | 3.3359 | 1.0885 | 10.7822 | 14.296 | 14.8348 | 11.0948 | 0 | -0.0032 | 0.0006 | 0.0041 | 0.0008 | -0.0004 | 0.0136 | -0.0018 | -0.0194 | -360.1773 | 17.4172 | -360.5004 | 17.6944 | -360.8481 | 18.1502 | -360.7989 | 17.5937 | -352.6352 | 18.7066 | -352.6875 | 16.8484
12:50 | 5417 | 45.0069 | 202.6989 | 450.171 | 457.1112 | -16.5484 | -39.5965 | 11.6076 | 8.0341 | 2.4292 | 0.6874 | 3.3465 | -1.0277 | 12.0998 | 4.888 | 0.6214 | 0.6609 | 0.9631 | 0.7485 | -129.2801 | 1.2942 | 5.6079 | 1.8823 | -2.4599 | -0.8854 | 4.8978 |  | 4.0406 | 0.6955 | 4.0101 | 3.3711 | 3.3387 | 1.0899 | 10.7914 | 14.2883 | 14.8353 | 11.1146 | -0.0003 | -0.0025 | 0.0009 | 0.0042 | 0.0009 | -0.0004 | 0.0086 | 0.0021 | -0.0072 | -360.1435 | 17.4028 | -360.4296 | 17.6697 | -360.8327 | 18.1687 | -360.8604 | 17.6122 | -352.6413 | 18.6922 | -352.6413 | 16.8197
12:50 | 5418 | 44.9197 | 202.6668 | 450.2385 | 457.1365 | -16.5595 | -39.6201 | 11.679 | 8.0459 | 2.5169 | 0.7768 | 3.2977 | -1.0207 | 12.0843 | 4.8825 | 0.6208 | 0.6606 | 0.9604 | 0.7475 | -129.2981 | 1.2569 | 5.6038 | 1.9535 | -2.4503 | -0.8396 | 4.8753 |  | 4.0553 | 0.5875 | 4.0101 | 3.3698 | 3.3378 | 1.0899 | 10.7948 | 14.3152 | 14.8694 | 11.1117 | -0.0001 | -0.0025 | 0.001 | 0.0044 | 0.0009 | -0.0004 | 0.0012 | -0.0131 | -0.0063 | -360.2142 | 17.4274 | -360.485 | 17.68 | -360.802 | 18.1645 | -360.8574 | 17.6081 | -352.6444 | 18.723 | -352.6813 | 16.8279
12:50 | 5419 | 44.8051 | 202.6139 | 450.0796 | 457.1334 | -16.5653 | -39.6608 | 11.6143 | 8.0312 | 2.4635 | 0.7113 | 3.3026 | -1.0162 | 12.1051 | 4.9406 | 0.6202 | 0.661 | 0.9627 | 0.7483 | -129.2233 | 1.2443 | 5.6064 | 2.0135 | -2.4691 | -0.8996 | 4.8867 |  | 4.0699 | 0.6688 | 4.011 | 3.3705 | 3.3356 | 1.0904 | 10.8076 | 14.2754 | 14.8734 | 11.1255 | 0.0002 | -0.0029 | 0.001 | 0.0038 | 0.0007 | -0.0005 | 0.0106 | -0.0088 | -0.0023 | -360.1742 | 17.4172 | -360.4696 | 17.6779 | -360.8266 | 18.1625 | -360.8327 | 17.604 | -352.6198 | 18.7169 | -352.6475 | 16.8217
12:50 | 5420 | 44.905 | 202.626 | 450.2065 | 457.0779 | -16.452 | -39.5674 | 11.7183 | 8.0494 | 2.457 | 0.6559 | 3.2622 | -1.0524 | 12.0213 | 4.8263 | 0.6205 | 0.663 | 0.9642 | 0.7492 | -129.2636 | 1.2544 | 5.6499 | 1.8859 | -2.4869 | -0.8755 | 4.8719 |  | 4.0516 | 0.5678 | 4.0095 | 3.3679 | 3.3419 | 1.0917 | 10.7763 | 14.2851 | 14.8738 | 11.1338 | 0.0001 | -0.0029 | 0.0012 | 0.004 | 0.0012 | -0.0004 | 0.0192 | -0.0073 | -0.0338 | -360.1988 | 17.4233 | -360.4789 | 17.6861 | -360.8481 | 18.1748 | -360.8543 | 17.6061 | -352.6321 | 18.7189 | -352.629 | 16.8279
12:50 | 5421 | 44.8755 | 202.67 | 450.2446 | 457.0807 | -16.5262 | -39.5815 | 11.5624 | 8.107 | 2.5087 | 0.5921 | 3.3365 | -1.1029 | 11.9491 | 4.8408 | 0.6217 | 0.6601 | 0.9626 | 0.7468 | -129.2072 | 1.269 | 5.5918 | 1.8748 | -2.45 | -0.708 | 4.9063 |  | 4.118 | 0.5909 | 4.0092 | 3.3648 | 3.335 | 1.0891 | 10.7994 | 14.2908 | 14.8564 | 11.0875 | 0 | -0.0023 | 0.0007 | 0.0035 | 0.0007 | 0.0004 | 0.0187 | -0.013 | 0.014 | -360.1988 | 17.4172 | -360.4758 | 17.6944 | -360.8358 | 18.181 | -360.8297 | 17.5917 | -352.6475 | 18.7169 | -352.6567 | 16.8381
12:50 | 5422 | 44.9395 | 202.7425 | 450.1803 | 457.1595 | -16.4758 | -39.5259 | 11.6353 | 8.0696 | 2.5123 | 0.6251 | 3.3696 | -1.0768 | 11.9707 | 4.9252 | 0.6217 | 0.6611 | 0.9615 | 0.7477 | -129.306 | 1.1774 | 5.6477 | 1.8297 | -2.4126 | -0.8067 | 4.9054 |  | 4.1669 | 0.6473 | 4.0097 | 3.3683 | 3.3359 | 1.0895 | 10.7858 | 14.2761 | 14.8426 | 11.0757 | -0.0002 | -0.0024 | 0.0008 | 0.004 | 0.001 | -0.0009 | 0.0107 | -0.016 | -0.0083 | -360.1958 | 17.4131 | -360.4666 | 17.6923 | -360.8081 | 18.1974 | -360.8666 | 17.6122 | -352.6567 | 18.7045 | -352.666 | 16.8217
12:50 | 5423 | 44.9591 | 202.6779 | 450.202 | 457.1417 | -16.5299 | -39.5723 | 11.6011 | 8.1042 | 2.5811 | 0.7813 | 3.3563 | -1.0631 | 11.9874 | 4.844 | 0.6209 | 0.657 | 0.9628 | 0.7471 | -129.2577 | 1.2705 | 5.5998 | 2.0129 | -2.3352 | -0.7939 | 4.8989 |  | 4.1212 | 0.6123 | 4.0101 | 3.3674 | 3.3391 | 1.092 | 10.7463 | 14.2429 | 14.8287 | 11.076 | 0.0005 | -0.0028 | 0.0013 | 0.0045 | 0.0009 | 0.0003 | 0.0091 | -0.0033 | -0.0033 | -360.1896 | 17.4213 | -360.4789 | 17.6841 | -360.8327 | 18.1604 | -360.8327 | 17.6061 | -352.6537 | 18.7128 | -352.6629 | 16.8238
12:50 | 5424 | 44.9536 | 202.6093 | 450.2945 | 457.0635 | -16.5329 | -39.5637 | 11.6994 | 8.1794 | 2.6172 | 0.853 | 3.2417 | -1.1053 | 11.9771 | 4.8129 | 0.621 | 0.6587 | 0.9623 | 0.7462 | -129.1732 | 1.3293 | 5.6085 | 2.0168 | -2.3465 | -0.7422 | 4.9663 |  | 4.0908 | 0.6 | 4.0086 | 3.3681 | 3.3389 | 1.0912 | 10.7915 | 14.2996 | 14.8679 | 11.1096 | 0.0001 | -0.0031 | 0.0004 | 0.0038 | 0.001 | -0.0008 | 0.0322 | -0.0198 | -0.0141 | -360.1681 | 17.4192 | -360.4727 | 17.7067 | -360.8697 | 18.1789 | -360.8481 | 17.5835 | -352.6229 | 18.7148 | -352.6752 | 16.8464
12:50 | 5425 | 44.9165 | 202.6427 | 450.1363 | 457.0061 | -16.5636 | -39.538 | 11.6509 | 8.1193 | 2.5197 | 0.6986 | 3.1978 | -1.1126 | 12.0649 | 4.8965 | 0.6206 | 0.6624 | 0.9653 | 0.7466 | -129.2277 | 1.3136 | 5.6744 | 2.0893 | -2.4721 | -0.7805 | 4.9411 |  | 4.1028 | 0.6551 | 4.0103 | 3.3674 | 3.3375 | 1.0906 | 10.7649 | 14.2554 | 14.8627 | 11.1125 | 0.0002 | -0.0027 | 0.0008 | 0.0043 | 0.0006 | -0.0008 | -0.0014 | 0.0057 | -0.0195 | -360.1896 | 17.4028 | -360.4296 | 17.6677 | -360.8389 | 18.1892 | -360.8604 | 17.6225 | -352.6475 | 18.6963 | -352.6136 | 16.8135
12:50 | 5426 | 44.8711 | 202.734 | 450.1888 | 457.075 | -16.5284 | -39.5907 | 11.7187 | 8.0875 | 2.529 | 0.7473 | 3.1822 | -1.024 | 12.1144 | 5.0162 | 0.6212 | 0.6618 | 0.9656 | 0.7469 | -129.2454 | 1.3393 | 5.6844 | 2.1479 | -2.4826 | -0.793 | 4.9665 |  | 4.0277 | 0.6319 | 4.0093 | 3.3679 | 3.3383 | 1.0908 | 10.7891 | 14.2859 | 14.8325 | 11.1125 | -0.0002 | -0.0023 | 0.0012 | 0.004 | 0.0012 | -0.0002 | 0.0095 | -0.004 | -0.0199 | -360.2235 | 17.45 | -360.5127 | 17.6697 | -360.8266 | 18.1584 | -360.8081 | 17.6204 | -352.6629 | 18.7333 | -352.6813 | 16.8299
12:50 | 5427 | 44.8916 | 202.6402 | 450.1464 | 457.0609 | -16.5548 | -39.5851 | 11.6145 | 8.1788 | 2.3808 | 0.7038 | 3.1632 | -1.1349 | 12.0571 | 4.9522 | 0.6215 | 0.6627 | 0.9628 | 0.7465 | -129.3137 | 1.3735 | 5.6174 | 2.1354 | -2.4666 | -0.7877 | 5.0546 |  | 4.0383 | 0.6292 | 4.0103 | 3.3636 | 3.3353 | 1.0918 | 10.7983 | 14.3068 | 14.8772 | 11.1099 | 0.0002 | -0.0024 | 0.0004 | 0.0034 | 0.0008 | -0.0007 | 0.0064 | -0.0064 | -0.0142 | -360.1527 | 17.3884 | -360.4481 | 17.6985 | -360.8727 | 18.1953 | -360.8697 | 17.5814 | -352.6229 | 18.6963 | -352.6444 | 16.8402
12:50 | 5428 | 44.9835 | 202.6461 | 450.2308 | 457.0971 | -16.5459 | -39.5403 | 11.6168 | 8.097 | 2.3924 | 0.5931 | 3.1173 | -1.0261 | 12.0781 | 4.9935 | 0.6216 | 0.6658 | 0.9629 | 0.7475 | -129.2855 | 1.2506 | 5.5182 | 2.0988 | -2.467 | -0.8013 | 4.9852 |  | 4.1045 | 0.7185 | 4.0089 | 3.3666 | 3.3378 | 1.0925 | 10.7684 | 14.2704 | 14.8194 | 11.0641 | 0.0001 | -0.003 | 0.0007 | 0.0037 | 0.0007 | -0.0002 | 0.0036 | -0.0149 | -0.0206 | -360.2327 | 17.4213 | -360.4542 | 17.6533 | -360.7866 | 18.181 | -360.9035 | 17.6389 | -352.7029 | 18.7169 | -352.6506 | 16.7971
12:50 | 5429 | 44.8723 | 202.6441 | 450.1269 | 457.0221 | -16.4712 | -39.4413 | 11.7514 | 8.1312 | 2.4058 | 0.6471 | 3.1118 | -1.0103 | 12.0394 | 4.9325 | 0.6214 | 0.6636 | 0.9629 | 0.7489 | -129.2143 | 1.2929 | 5.6126 | 1.9772 | -2.3753 | -0.8038 | 5.0015 |  | 4.0855 | 0.6056 | 4.0093 | 3.3657 | 3.34 | 1.0926 | 10.8064 | 14.2977 | 14.8567 | 11.0948 | -0.0003 | -0.0026 | 0.0011 | 0.0038 | 0.0011 | -0.0003 | -0.0024 | -0.0046 | -0.0213 | -360.1927 | 17.4356 | -360.5189 | 17.7108 | -360.8389 | 18.1645 | -360.8081 | 17.5835 | -352.6352 | 18.7189 | -352.6967 | 16.8484
12:50 | 5430 | 44.8965 | 202.6545 | 450.2105 | 457.0688 | -16.5171 | -39.5218 | 11.7232 | 8.1228 | 2.433 | 0.764 | 3.1746 | -1.0344 | 12.0372 | 4.9516 | 0.6224 | 0.6592 | 0.9612 | 0.7472 | -129.2135 | 1.4163 | 5.7516 | 1.9301 | -2.3955 | -0.7915 | 4.9625 |  | 4.1138 | 0.6023 | 4.0094 | 3.3696 | 3.3415 | 1.0922 | 10.7788 | 14.2809 | 14.8423 | 11.0742 | -0.0005 | -0.0028 | 0.0006 | 0.004 | 0.0004 | -0.0004 | 0.0081 | -0.0155 | -0.0289 | -360.1773 | 17.3987 | -360.4296 | 17.6964 | -360.8604 | 18.2015 | -360.9035 | 17.604 | -352.6198 | 18.7004 | -352.629 | 16.8217
12:50 | 5431 | 44.8935 | 202.6929 | 450.2403 | 457.063 | -16.5232 | -39.4544 | 11.7427 | 8.1297 | 2.4722 | 0.7529 | 3.177 | -0.9749 | 12.0036 | 4.9819 | 0.6219 | 0.6666 | 0.9666 | 0.7477 | -129.2513 | 1.4514 | 5.6236 | 1.8784 | -2.3346 | -0.8141 | 4.95 |  | 4.0529 | 0.488 | 4.0094 | 3.3632 | 3.339 | 1.0916 | 10.7718 | 14.2625 | 14.8709 | 11.1074 | -0.0001 | -0.0031 | 0.0009 | 0.0045 | 0.0011 | -0.0006 | 0.0036 | -0.0126 | -0.0206 | -360.2419 | 17.4418 | -360.4696 | 17.6594 | -360.7897 | 18.1543 | -360.8481 | 17.6184 | -352.6813 | 18.7292 | -352.6567 | 16.8032
12:50 | 5432 | 44.8564 | 202.633 | 450.181 | 457.0377 | -16.5354 | -39.5 | 11.6563 | 8.1573 | 2.4863 | 0.7246 | 3.1675 | -0.9782 | 12.0204 | 4.9447 | 0.6216 | 0.6654 | 0.9623 | 0.7471 | -129.1697 | 1.5136 | 5.766 | 1.9229 | -2.2255 | -0.7627 | 5.0772 |  | 4.0455 | 0.5744 | 4.0104 | 3.3655 | 3.3408 | 1.0904 | 10.8053 | 14.279 | 14.8659 | 11.0998 | 0.0004 | -0.0029 | 0.0004 | 0.0038 | 0.0008 | -0.0003 | 0.016 | -0.0061 | 0.008 | -360.1527 | 17.4254 | -360.5281 | 17.7108 | -360.8727 | 18.1728 | -360.8081 | 17.5753 | -352.6629 | 18.7148 | -352.6752 | 16.8484
12:50 | 5433 | 44.8876 | 202.641 | 450.1758 | 457.0314 | -16.5313 | -39.5178 | 11.684 | 8.0799 | 2.5099 | 0.6197 | 3.1413 | -0.989 | 12.0963 | 5.0141 | 0.6213 | 0.6623 | 0.9654 | 0.7473 | -129.1503 | 1.4178 | 5.7678 | 2.008 | -2.3003 | -0.7655 | 4.9642 |  | 4.0827 | 0.6218 | 4.0088 | 3.3678 | 3.339 | 1.0908 | 10.7847 | 14.2922 | 14.8228 | 11.0634 | -0.0004 | -0.003 | 0.0001 | 0.0037 | 0.001 | -0.0005 | 0.0047 | -0.0149 | -0.0157 | -360.1742 | 17.3966 | -360.4419 | 17.6759 | -360.8512 | 18.1994 | -360.8543 | 17.604 | -352.6136 | 18.6902 | -352.6198 | 16.8197
12:50 | 5434 | 44.9256 | 202.7713 | 450.2281 | 457.1208 | -16.4973 | -39.468 | 11.6748 | 8.0944 | 2.476 | 0.644 | 3.1132 | -1.1024 | 11.9684 | 4.9184 | 0.6218 | 0.6614 | 0.9663 | 0.7469 | -129.1457 | 1.3459 | 5.7562 | 2.0687 | -2.3443 | -0.7463 | 4.9685 |  | 4.0787 | 0.5802 | 4.0089 | 3.3684 | 3.3387 | 1.0919 | 10.7879 | 14.2618 | 14.8206 | 11.0879 | -0.0001 | -0.0025 | 0.001 | 0.0038 | 0.0007 | -0.0003 | 0.0056 | -0.0189 | -0.0152 | -360.2727 | 17.4397 | -360.4696 | 17.6574 | -360.7897 | 18.1645 | -360.8666 | 17.6163 | -352.6567 | 18.7251 | -352.6413 | 16.7971
12:50 | 5435 | 44.9589 | 202.7286 | 450.2069 | 457.1035 | -16.4576 | -39.5518 | 11.6818 | 8.0259 | 2.476 | 0.6942 | 3.1477 | -1.1166 | 11.9856 | 4.9089 | 0.6221 | 0.662 | 0.9618 | 0.7452 | -129.2046 | 1.385 | 5.7626 | 2.0741 | -2.4016 | -1.0954 | 4.9645 |  | 4.0595 | 0.5947 | 4.0095 | 3.3669 | 3.339 | 1.092 | 10.7962 | 14.2635 | 14.8481 | 11.0916 | 0.0001 | -0.0029 | 0.0002 | 0.0032 | 0.0009 | -0.0006 | 0.0109 | -0.0192 | -0.0059 | -360.1558 | 17.4254 | -360.5189 | 17.6944 | -360.8635 | 18.1728 | -360.8266 | 17.5958 | -352.626 | 18.721 | -352.7121 | 16.8464
12:50 | 5436 | 44.9835 | 202.6583 | 450.2249 | 457.0614 | -16.5191 | -39.5496 | 11.6587 | 7.9875 | 2.5494 | 0.6211 | 3.166 | -0.9852 | 12.0586 | 4.8896 | 0.6232 | 0.6651 | 0.9617 | 0.7471 | -129.2372 | 1.3444 | 5.6666 | 2.0329 | -2.3739 | -0.9034 | 5.0077 |  | 3.9768 | 0.5541 | 4.009 | 3.3671 | 3.3403 | 1.0918 | 10.7742 | 14.2879 | 14.8668 | 11.0984 | 0.0001 | -0.0033 | 0.0008 | 0.0036 | 0.0003 | -0.0007 | 0.0132 | -0.0085 | -0.0153 | -360.2173 | 17.409 | -360.4296 | 17.6615 | -360.842 | 18.1748 | -360.8635 | 17.6225 | -352.6629 | 18.7107 | -352.6229 | 16.8115
12:50 | 5437 | 44.9135 | 202.6295 | 450.1755 | 457.0506 | -16.5413 | -39.4299 | 11.6229 | 7.8982 | 2.4684 | 0.5712 | 3.0518 | -1.056 | 12.1502 | 4.9646 | 0.6217 | 0.6607 | 0.9622 | 0.7473 | -129.154 | 1.4285 | 5.77 | 2.0762 | -2.3883 | -0.8833 | 4.9944 |  | 3.9688 | 0.5504 | 4.0089 | 3.365 | 3.3354 | 1.0932 | 10.7775 | 14.2861 | 14.8741 | 11.1179 | 0 | -0.0026 | 0.0013 | 0.0039 | 0.001 | -0.0004 | -0.0005 | -0.0085 | 0.0001 | -360.2296 | 17.4356 | -360.4758 | 17.6656 | -360.8204 | 18.1707 | -360.8697 | 17.6081 | -352.6629 | 18.7333 | -352.6752 | 16.8238
12:50 | 5438 | 44.9784 | 202.7192 | 450.173 | 457.0618 | -16.521 | -39.4878 | 11.666 | 7.9416 | 2.4346 | 0.6335 | 3.1112 | -1.008 | 12.0689 | 4.9154 | 0.6225 | 0.6618 | 0.9631 | 0.7485 | -129.0781 | 1.4788 | 5.8716 | 2.0273 | -2.4387 | -0.9138 | 4.9852 |  | 3.984 | 0.6461 | 4.0103 | 3.3681 | 3.3376 | 1.0926 | 10.7742 | 14.2993 | 14.8368 | 11.0873 | -0.0004 | -0.0028 | 0.0002 | 0.0041 | 0.0005 | -0.0005 | 0.0144 | -0.0042 | -0.0051 | -360.1588 | 17.4048 | -360.4942 | 17.6902 | -360.845 | 18.1645 | -360.8604 | 17.5999 | -352.6167 | 18.7066 | -352.6383 | 16.8176
12:50 | 5439 | 44.8761 | 202.6912 | 450.0869 | 456.9995 | -16.5131 | -39.4948 | 11.7181 | 7.9315 | 2.4705 | 0.7619 | 3.1058 | -0.953 | 12.126 | 4.9329 | 0.6225 | 0.6641 | 0.961 | 0.7473 | -129.2039 | 1.4383 | 5.7436 | 2.0436 | -2.4327 | -0.9028 | 4.9596 |  | 4.0254 | 0.6013 | 4.0097 | 3.3694 | 3.3384 | 1.0912 | 10.7693 | 14.2665 | 14.8319 | 11.1153 | 0 | -0.0028 | 0.0013 | 0.0044 | 0.001 | -0.0001 | 0.0175 | -0.0051 | 0.0173 | -360.2142 | 17.4151 | -360.445 | 17.6656 | -360.8204 | 18.1543 | -360.8204 | 17.602 | -352.6229 | 18.7148 | -352.6537 | 16.8135
12:50 | 5440 | 44.9595 | 202.6848 | 450.1056 | 457.0019 | -16.5768 | -39.4879 | 11.7309 | 8.067 | 2.5589 | 0.7379 | 3.1127 | -0.9721 | 12.1086 | 4.9241 | 0.6226 | 0.66 | 0.9649 | 0.7496 | -129.1723 | 1.3855 | 5.7736 | 1.9887 | -2.4243 | -0.9212 | 5.0036 |  | 4.1292 | 0.6708 | 4.0098 | 3.3693 | 3.338 | 1.0908 | 10.7821 | 14.2674 | 14.8659 | 11.0941 | 0.0003 | -0.003 | 0.0006 | 0.0038 | 0.0005 | -0.0005 | 0.0128 | -0.0078 | -0.017 | -360.1158 | 17.4028 | -360.4635 | 17.6677 | -360.805 | 18.1379 | -360.7927 | 17.5671 | -352.6136 | 18.7148 | -352.669 | 16.8217
12:50 | 5441 | 44.9378 | 202.7336 | 450.1742 | 457.0038 | -16.6579 | -39.459 | 11.6416 | 8.03 | 2.6137 | 0.7359 | 3.1166 | -0.942 | 12.1449 | 4.9343 | 0.6203 | 0.6606 | 0.9579 | 0.7465 | -129.1077 | 1.4544 | 5.8475 | 1.9605 | -2.3905 | -0.9028 | 4.9632 |  | 4.0816 | 0.6401 | 4.0089 | 3.3659 | 3.335 | 1.0927 | 10.773 | 14.2925 | 14.8307 | 11.0858 | -0.0002 | -0.0031 | 0.0003 | 0.0036 | 0.0003 | -0.0005 | 0.0223 | -0.0005 | -0.023 | -360.1096 | 17.3864 | -360.4081 | 17.6574 | -360.8235 | 18.1543 | -360.8266 | 17.5753 | -352.5952 | 18.6902 | -352.6198 | 16.8094
12:50 | 5442 | 44.9535 | 202.6745 | 450.0329 | 457.008 | -16.6756 | -39.5621 | 11.6627 | 8.032 | 2.5767 | 0.726 | 3.1106 | -0.9974 | 12.1386 | 4.9376 | 0.622 | 0.6642 | 0.9611 | 0.748 | -129.1431 | 1.4006 | 5.8076 | 2.0061 | -2.4328 | -0.8616 | 4.9444 |  | 4.0344 | 0.6338 | 4.01 | 3.3668 | 3.3372 | 1.0926 | 10.8122 | 14.2977 | 14.8799 | 11.1063 | 0 | -0.0025 | 0.0007 | 0.0037 | 0.0009 | -0.0007 | 0.0063 | -0.0043 | -0.0084 | -360.1742 | 17.3987 | -360.4081 | 17.6163 | -360.7466 | 18.1276 | -360.8081 | 17.6163 | -352.629 | 18.6922 | -352.6044 | 16.7786
12:50 | 5443 | 45.0009 | 202.6825 | 450.1497 | 457.0276 | -16.6353 | -39.4965 | 11.6934 | 8.0057 | 2.5878 | 0.6728 | 3.0905 | -0.9755 | 12.2023 | 4.9424 | 0.6219 | 0.6635 | 0.9629 | 0.7485 | -129.1648 | 1.4723 | 5.8092 | 2.0299 | -2.3403 | -0.8036 | 5.0287 |  | 4.0785 | 0.7663 | 4.0091 | 3.3657 | 3.3382 | 1.0928 | 10.7995 | 14.2673 | 14.8648 | 11.0771 | -0.0001 | -0.0026 | 0.0004 | 0.0033 | 0.0006 | -0.0001 | 0.0141 | -0.0052 | -0.0151 | -360.1342 | 17.4048 | -360.4635 | 17.6677 | -360.8204 | 18.1153 | -360.7773 | 17.5568 | -352.586 | 18.7004 | -352.6844 | 16.8217
12:50 | 5444 | 44.9508 | 202.6758 | 450.1093 | 456.9801 | -16.6081 | -39.5759 | 11.731 | 8.0094 | 2.5394 | 0.6101 | 3.1517 | -0.884 | 12.2208 | 4.9809 | 0.6232 | 0.6672 | 0.9667 | 0.7487 | -129.1813 | 1.484 | 5.7255 | 2.0837 | -2.2507 | -0.9192 | 5.0256 |  | 3.9804 | 0.7375 | 4.0102 | 3.3653 | 3.3409 | 1.0929 | 10.7741 | 14.2766 | 14.8863 | 11.0861 | 0.0004 | -0.003 | 0.0008 | 0.0039 | 0.0012 | -0.0008 | 0.0154 | -0.0062 | 0.0035 | -360.125 | 17.3699 | -360.3712 | 17.6266 | -360.802 | 18.144 | -360.8389 | 17.5876 | -352.6044 | 18.6635 | -352.6013 | 16.793
12:50 | 5445 | 44.9323 | 202.6569 | 450.1196 | 456.9684 | -16.5959 | -39.5939 | 11.7835 | 7.9869 | 2.5311 | 0.6684 | 3.0636 | -0.9726 | 12.1936 | 4.947 | 0.6225 | 0.6611 | 0.9613 | 0.7475 | -129.1683 | 1.4064 | 5.7385 | 2.0526 | -2.2706 | -0.7976 | 4.9912 |  | 4.0467 | 0.6947 | 4.0097 | 3.3691 | 3.3372 | 1.0916 | 10.7649 | 14.2729 | 14.8348 | 11.0775 | 0 | -0.0031 | 0.0011 | 0.0039 | 0.0001 | -0.0004 | -0.005 | -0.0069 | -0.0044 | -360.1742 | 17.4172 | -360.4481 | 17.6307 | -360.7527 | 18.1029 | -360.7897 | 17.5876 | -352.6352 | 18.7087 | -352.6413 | 16.7909
12:50 | 5446 | 44.9669 | 202.701 | 450.0595 | 457.0031 | -16.5857 | -39.6885 | 11.6743 | 7.9753 | 2.505 | 0.7401 | 3.0761 | -1.0406 | 12.1175 | 4.953 | 0.6216 | 0.6623 | 0.961 | 0.7493 | -129.2439 | 1.4009 | 5.7638 | 2.029 | -2.3375 | -0.8991 | 4.9772 |  | 3.9886 | 0.6973 | 4.0099 | 3.3698 | 3.342 | 1.0927 | 10.7765 | 14.2787 | 14.8638 | 11.089 | -0.0002 | -0.0021 | 0.0007 | 0.004 | 0.0012 | -0.0004 | 0.0033 | 0.0037 | 0.0028 | -360.1158 | 17.3658 | -360.4327 | 17.6553 | -360.8112 | 18.1379 | -360.7866 | 17.5547 | -352.5613 | 18.6779 | -352.6136 | 16.8156
12:50 | 5447 | 45.0146 | 202.767 | 450.1818 | 457.0677 | -16.5148 | -39.6457 | 11.7273 | 8.0695 | 2.4971 | 0.7039 | 3.0231 | -1.0127 | 12.1852 | 4.9151 | 0.6211 | 0.6618 | 0.9622 | 0.7481 | -129.23 | 1.3826 | 5.8095 | 2.0631 | -2.3439 | -0.9649 | 4.8749 |  | 3.9984 | 0.5756 | 4.0097 | 3.3691 | 3.3367 | 1.0911 | 10.7788 | 14.2231 | 14.8481 | 11.0742 | -0.0003 | -0.0029 | 0.001 | 0.0044 | 0.0008 | 0 | 0.0171 | -0.0139 | -0.021 | -360.1958 | 17.3843 | -360.3742 | 17.6081 | -360.7558 | 18.1235 | -360.8297 | 17.6143 | -352.626 | 18.6758 | -352.5706 | 16.7766
12:51 | 5448 | 44.9832 | 202.752 | 450.1358 | 457.0487 | -16.6606 | -39.7453 | 11.6367 | 8.0864 | 2.5528 | 0.8992 | 3.0019 | -1.0418 | 12.1888 | 4.866 | 0.6222 | 0.6623 | 0.9644 | 0.7489 | -129.2553 | 1.4077 | 5.8385 | 2.0329 | -2.3117 | -0.9233 | 4.9401 |  | 3.926 | 0.6246 | 4.0092 | 3.3689 | 3.3365 | 1.0919 | 10.7937 | 14.2905 | 14.8948 | 11.0767 | 0.0001 | -0.003 | 0.0008 | 0.0042 | 0.001 | -0.0002 | 0.0085 | -0.0109 | -0.0046 | -360.1588 | 17.4131 | -360.4666 | 17.6492 | -360.7712 | 18.1009 | -360.7435 | 17.5671 | -352.589 | 18.7087 | -352.6598 | 16.8176
12:51 | 5449 | 45.0182 | 202.7092 | 450.1792 | 457.0007 | -16.6393 | -39.7993 | 11.5288 | 7.9782 | 2.5859 | 0.8141 | 2.9945 | -0.9477 | 12.2097 | 4.9618 | 0.621 | 0.657 | 0.9637 | 0.7502 | -129.2407 | 1.4148 | 5.7996 | 2.0724 | -2.3598 | -0.8815 | 4.9937 |  | 3.986 | 0.5711 | 4.0096 | 3.3693 | 3.3426 | 1.0918 | 10.8123 | 14.2684 | 14.8836 | 11.1071 | 0.0007 | -0.0026 | 0.0006 | 0.0035 | 0.0007 | -0.0004 | 0.0067 | -0.0251 | -0.0058 | -360.1034 | 17.3782 | -360.3773 | 17.6553 | -360.8327 | 18.142 | -360.8266 | 17.5814 | -352.5583 | 18.6676 | -352.5983 | 16.8094
12:51 | 5450 | 44.9175 | 202.7734 | 450.1001 | 456.9196 | -16.5143 | -39.829 | 11.5261 | 7.9977 | 2.5615 | 0.7967 | 2.9622 | -0.9048 | 12.1825 | 5.0176 | 0.6215 | 0.6628 | 0.9625 | 0.7489 | -129.1578 | 1.4558 | 5.8815 | 2.0163 | -2.3878 | -0.9188 | 4.9355 |  | 4.0124 | 0.57 | 4.0098 | 3.3697 | 3.3395 | 1.0925 | 10.7499 | 14.2578 | 14.8307 | 11.08 | -0.0004 | -0.0027 | 0.0004 | 0.0033 | 0.0013 | -0.0004 | 0.0195 | -0.0126 | 0.0069 | -360.2142 | 17.4028 | -360.405 | 17.6184 | -360.7281 | 18.1194 | -360.8512 | 17.602 | -352.5767 | 18.6943 | -352.6013 | 16.7745
12:51 | 5451 | 44.9589 | 202.7606 | 450.1449 | 457.0441 | -16.5122 | -39.746 | 11.4877 | 8.0157 | 2.5506 | 0.8466 | 3.0305 | -0.9121 | 12.1325 | 4.9808 | 0.6209 | 0.6619 | 0.9623 | 0.7484 | -129.1988 | 1.3194 | 5.8291 | 2.0549 | -2.3401 | -0.8969 | 4.949 |  | 4.046 | 0.6907 | 4.0104 | 3.3683 | 3.3421 | 1.0927 | 10.7915 | 14.2707 | 14.8447 | 11.1038 | -0.0001 | -0.0025 | 0.0004 | 0.0032 | 0.0008 | -0.0007 | 0.0095 | -0.0224 | -0.0079 | -360.1711 | 17.3966 | -360.4635 | 17.6533 | -360.8174 | 18.1255 | -360.7927 | 17.5814 | -352.589 | 18.6881 | -352.6383 | 16.8176
12:51 | 5452 | 44.9393 | 202.7245 | 450.1663 | 456.9959 | -16.5346 | -39.7416 | 11.5625 | 8.0364 | 2.5194 | 0.7306 | 3.05 | -0.9408 | 12.1622 | 5.0034 | 0.6205 | 0.6637 | 0.9644 | 0.7469 | -129.2196 | 1.4008 | 5.6733 | 2.0674 | -2.3225 | -0.8233 | 4.9895 |  | 3.9375 | 0.6638 | 4.0097 | 3.3662 | 3.3355 | 1.0926 | 10.7788 | 14.2462 | 14.8596 | 11.08 | 0.0002 | -0.0029 | 0.0009 | 0.0041 | 0.0006 | -0.0008 | 0.0154 | -0.0135 | 0.0021 | -360.1527 | 17.3884 | -360.4081 | 17.6225 | -360.7743 | 18.1461 | -360.842 | 17.6061 | -352.5952 | 18.6717 | -352.5706 | 16.7909
12:51 | 5453 | 44.9205 | 202.729 | 450.0804 | 456.9614 | -16.4998 | -39.7796 | 11.4679 | 8.0068 | 2.4733 | 0.6701 | 2.9559 | -0.97 | 12.1192 | 5.0345 | 0.6215 | 0.6656 | 0.966 | 0.7482 | -129.2403 | 1.4225 | 5.7925 | 1.9941 | -2.4041 | -0.8068 | 4.8981 |  | 3.9812 | 0.7426 | 4.0101 | 3.367 | 3.3395 | 1.0901 | 10.7961 | 14.281 | 14.8665 | 11.097 | -0.0002 | -0.003 | 0.0011 | 0.0043 | 0.001 | -0.0005 | 0.0079 | -0.0126 | -0.0079 | -360.1958 | 17.411 | -360.4481 | 17.6594 | -360.7897 | 18.1379 | -360.8143 | 17.5978 | -352.6013 | 18.6861 | -352.6136 | 16.8032
12:51 | 5454 | 44.9613 | 202.7809 | 450.1415 | 457.0338 | -16.5486 | -39.7069 | 11.5259 | 8.0725 | 2.5465 | 0.8042 | 3.0849 | -0.9977 | 12.1225 | 4.9482 | 0.6235 | 0.6643 | 0.9676 | 0.7477 | -129.1853 | 1.3855 | 5.7407 | 2.0456 | -2.4164 | -0.8118 | 4.9534 |  | 3.9463 | 0.6874 | 4.0117 | 3.3673 | 3.3363 | 1.0906 | 10.8179 | 14.3037 | 14.8878 | 11.1229 | 0.0003 | -0.0024 | 0.0006 | 0.0037 | 0.0008 | 0.0002 | -0.0042 | -0.0142 | -0.0183 | -360.1711 | 17.4028 | -360.4512 | 17.6677 | -360.8112 | 18.144 | -360.802 | 17.6102 | -352.5952 | 18.6779 | -352.629 | 16.8115
12:51 | 5455 | 44.9239 | 202.7436 | 450.1252 | 457.0798 | -16.6102 | -39.7492 | 11.476 | 7.9436 | 2.5465 | 0.7533 | 3.0859 | -0.9649 | 12.0431 | 4.9863 | 0.6224 | 0.6631 | 0.9616 | 0.7492 | -129.1259 | 1.3365 | 5.7185 | 2.1118 | -2.3847 | -0.7064 | 4.9379 |  | 4.0208 | 0.5239 | 4.0098 | 3.3671 | 3.3396 | 1.0927 | 10.7961 | 14.3217 | 14.8444 | 11.085 | -0.0003 | -0.0026 | 0.0011 | 0.0039 | 0.001 | -0.0005 | -0.003 | 0.0014 | -0.0183 | -360.2111 | 17.4274 | -360.4512 | 17.6677 | -360.8081 | 18.1461 | -360.8358 | 17.6102 | -352.6229 | 18.7025 | -352.6383 | 16.8053
12:51 | 5456 | 45.0119 | 202.7609 | 450.2657 | 457.0558 | -16.5992 | -39.7253 | 11.5847 | 7.9837 | 2.5276 | 0.6785 | 3.004 | -0.9451 | 12.1678 | 4.9694 | 0.6214 | 0.662 | 0.9633 | 0.7483 | -129.1806 | 1.2898 | 5.677 | 2.0615 | -2.431 | -0.8412 | 4.8757 |  | 4.0152 | 0.5687 | 4.0101 | 3.3659 | 3.3405 | 1.0909 | 10.8111 | 14.2788 | 14.859 | 11.1175 | 0.0003 | -0.003 | 0.0009 | 0.0039 | 0.0005 | -0.0004 | -0.0046 | -0.002 | -0.016 | -360.1804 | 17.4397 | -360.4973 | 17.6882 | -360.845 | 18.144 | -360.7958 | 17.6102 | -352.6198 | 18.7107 | -352.6998 | 16.8381
12:51 | 5457 | 45.0241 | 202.7568 | 450.2367 | 457.0679 | -16.603 | -39.7379 | 11.5871 | 8.022 | 2.5348 | 0.7022 | 3.0009 | -1.0164 | 12.0894 | 4.9773 | 0.6209 | 0.6615 | 0.9664 | 0.7501 | -129.1679 | 1.4546 | 5.7056 | 1.991 | -2.5142 | -0.8601 | 4.8951 |  | 3.9186 | 0.4975 | 4.0103 | 3.3678 | 3.3404 | 1.0908 | 10.7754 | 14.2831 | 14.8671 | 11.0883 | 0.0001 | -0.0033 | 0 | 0.0032 | 0.0008 | -0.0007 | 0.0066 | -0.0185 | -0.0055 | -360.1527 | 17.411 | -360.4819 | 17.6882 | -360.8666 | 18.1666 | -360.8604 | 17.5978 | -352.589 | 18.684 | -352.6537 | 16.8464
12:51 | 5458 | 45.081 | 202.8554 | 450.2557 | 457.0738 | -16.5901 | -39.759 | 11.51 | 8.0561 | 2.6069 | 0.8921 | 3.0242 | -0.9391 | 12.1502 | 5.132 | 0.6211 | 0.6624 | 0.9642 | 0.7478 | -129.1846 | 1.4074 | 5.811 | 1.9861 | -2.5039 | -0.9196 | 4.9325 |  | 3.9377 | 0.5996 | 4.011 | 3.3675 | 3.3387 | 1.0915 | 10.7719 | 14.2797 | 14.8641 | 11.0905 | -0.0003 | -0.0027 | 0.0008 | 0.004 | 0.0006 | 0 | 0.0091 | -0.0118 | -0.007 | -360.2235 | 17.4192 | -360.4512 | 17.641 | -360.7897 | 18.1543 | -360.8943 | 17.643 | -352.6844 | 18.6943 | -352.6413 | 16.8156
12:51 | 5459 | 45.0322 | 202.7772 | 450.2475 | 457.0553 | -16.5449 | -39.814 | 11.6137 | 8.0501 | 2.5172 | 0.8403 | 3.0397 | -0.9809 | 12.1553 | 5.1178 | 0.6225 | 0.6647 | 0.9666 | 0.7492 | -129.1068 | 1.3873 | 5.8739 | 1.9713 | -2.4636 | -0.7564 | 4.9301 |  | 3.9855 | 0.7059 | 4.0096 | 3.3671 | 3.3375 | 1.0909 | 10.7892 | 14.2509 | 14.8188 | 11.0901 | -0.0005 | -0.0029 | 0.0008 | 0.0037 | 0.001 | -0.0011 | 0.0159 | -0.003 | 0.0124 | -360.1742 | 17.4336 | -360.5035 | 17.6923 | -360.8327 | 18.1358 | -360.7866 | 17.5876 | -352.6598 | 18.7128 | -352.6967 | 16.8628
12:51 | 5460 | 45.0088 | 202.7067 | 450.1734 | 457.0352 | -16.5592 | -39.6586 | 11.7175 | 8.0721 | 2.3958 | 0.8509 | 3.0555 | -0.8565 | 12.1977 | 5.1638 | 0.6224 | 0.6645 | 0.9635 | 0.7498 | -129.1267 | 1.3753 | 5.8735 | 1.9259 | -2.4807 | -0.778 | 4.8814 |  | 3.9606 | 0.6712 | 4.0085 | 3.3676 | 3.3404 | 1.0901 | 10.7673 | 14.2632 | 14.8112 | 11.0981 | -0.0002 | -0.0032 | 0.0004 | 0.0035 | 0.0003 | -0.0006 | 0.0102 | -0.0037 | 0.0056 | -360.1465 | 17.3782 | -360.4142 | 17.6656 | -360.8327 | 18.1728 | -360.885 | 17.6143 | -352.6044 | 18.6717 | -352.6044 | 16.8361
12:51 | 5461 | 45.0722 | 202.7193 | 450.2969 | 457.0726 | -16.5037 | -39.6754 | 11.6421 | 8.0585 | 2.364 | 0.8863 | 2.9506 | -0.8811 | 12.2248 | 5.1259 | 0.6203 | 0.6651 | 0.9645 | 0.749 | -129.1164 | 1.3964 | 5.8414 | 1.975 | -2.4967 | -0.8949 | 4.8678 |  | 4.0123 | 0.715 | 4.0091 | 3.3672 | 3.3387 | 1.091 | 10.8029 | 14.2883 | 14.8584 | 11.0973 | 0.0001 | -0.0029 | 0.0008 | 0.0043 | 0.0008 | -0.0006 | 0.0081 | 0.0033 | -0.0265 | -360.2142 | 17.4254 | -360.4296 | 17.6348 | -360.7712 | 18.1153 | -360.7927 | 17.6143 | -352.6752 | 18.7107 | -352.6537 | 16.8135
12:51 | 5462 | 45.0811 | 202.7334 | 450.2294 | 457.108 | -16.5063 | -39.7061 | 11.6656 | 8.0984 | 2.3016 | 0.8267 | 2.9417 | -0.9058 | 12.203 | 5.1283 | 0.6219 | 0.6671 | 0.9677 | 0.7484 | -129.1584 | 1.3986 | 5.8992 | 1.9724 | -2.4671 | -0.7802 | 4.9617 |  | 4.0306 | 0.6254 | 4.0093 | 3.3648 | 3.3392 | 1.091 | 10.8076 | 14.2928 | 14.8734 | 11.1313 | 0 | -0.0028 | 0.0007 | 0.0038 | 0.0008 | -0.0002 | 0.0087 | -0.0038 | -0.021 | -360.0788 | 17.4048 | -360.4696 | 17.6759 | -360.8604 | 18.1358 | -360.762 | 17.5773 | -352.5521 | 18.6799 | -352.666 | 16.8525
12:51 | 5463 | 45.0185 | 202.6847 | 450.3185 | 457.116 | -16.4724 | -39.6369 | 11.7095 | 8.1063 | 2.3349 | 0.7947 | 3.006 | -1.0186 | 12.1315 | 5.0474 | 0.6209 | 0.6623 | 0.9673 | 0.748 | -129.1686 | 1.3176 | 5.8404 | 2.0778 | -2.2808 | -0.7361 | 4.9425 |  | 4.0539 | 0.775 | 4.0086 | 3.3683 | 3.3395 | 1.0918 | 10.8145 | 14.2827 | 14.8595 | 11.1316 | -0.0004 | -0.0025 | 0.0011 | 0.0044 | 0.0008 | -0.0001 | 0.0085 | 0.0087 | 0.0013 | -360.1404 | 17.3638 | -360.3558 | 17.6163 | -360.7435 | 18.1358 | -360.845 | 17.6081 | -352.6106 | 18.6614 | -352.5675 | 16.795
12:51 | 5464 | 44.9943 | 202.7222 | 450.219 | 457.1264 | -16.4559 | -39.6925 | 11.8012 | 8.0209 | 2.382 | 0.8572 | 2.997 | -0.9606 | 12.1393 | 5.1233 | 0.6218 | 0.6627 | 0.9666 | 0.7488 | -129.1093 | 1.3859 | 5.767 | 2.0028 | -2.3691 | -0.8377 | 4.9049 |  | 4.0736 | 0.6176 | 4.0091 | 3.3676 | 3.3394 | 1.0911 | 10.8028 | 14.3005 | 14.9032 | 11.1536 | 0.0005 | -0.0025 | 0.0013 | 0.0043 | 0.0011 | 0.0001 | 0.0259 | -0.0001 | 0.0051 | -360.1681 | 17.4233 | -360.4635 | 17.6307 | -360.7743 | 18.0988 | -360.7743 | 17.5937 | -352.6229 | 18.7004 | -352.626 | 16.8176
12:51 | 5465 | 45.0975 | 202.7404 | 450.3105 | 457.1215 | -16.5283 | -39.6482 | 11.8445 | 8.1176 | 2.4927 | 0.8197 | 3.0637 | -0.9766 | 12.1622 | 5.0741 | 0.6206 | 0.6637 | 0.9641 | 0.7498 | -129.1342 | 1.3195 | 5.6815 | 1.9539 | -2.3155 | -0.8461 | 4.8854 |  | 3.9813 | 0.6196 | 4.0084 | 3.3704 | 3.341 | 1.0913 | 10.803 | 14.3054 | 14.891 | 11.0981 | 0.0001 | -0.0029 | 0.0004 | 0.0037 | 0.0005 | -0.0004 | 0.0153 | -0.0042 | 0.003 | -360.1281 | 17.3679 | -360.4112 | 17.6636 | -360.8081 | 18.144 | -360.7927 | 17.5629 | -352.546 | 18.6635 | -352.626 | 16.8258
12:51 | 5466 | 45.0725 | 202.7315 | 450.352 | 457.1928 | -16.5397 | -39.7381 | 11.8107 | 8.1085 | 2.4834 | 0.7675 | 3.0767 | -0.9979 | 12.0758 | 5.0171 | 0.6208 | 0.6619 | 0.9658 | 0.7492 | -129.1925 | 1.2976 | 5.8456 | 1.9069 | -2.3874 | -0.8378 | 4.875 |  | 4.0006 | 0.6091 | 4.0097 | 3.3686 | 3.3385 | 1.0909 | 10.7845 | 14.2463 | 14.826 | 11.0739 | 0.0002 | -0.0027 | 0.001 | 0.0039 | 0.0009 | -0.0006 | 0.0179 | -0.018 | -0.0101 | -360.2173 | 17.3905 | -360.405 | 17.6266 | -360.7804 | 18.1399 | -360.8389 | 17.6184 | -352.626 | 18.6676 | -352.586 | 16.7991
12:51 | 5467 | 45.001 | 202.639 | 450.1765 | 457.1099 | -16.4907 | -39.7461 | 11.7596 | 8.1558 | 2.5112 | 0.7614 | 3.0586 | -1.0501 | 12.0796 | 5.0527 | 0.6213 | 0.6629 | 0.9624 | 0.7486 | -129.136 | 1.3831 | 5.7681 | 1.9587 | -2.3805 | -0.8211 | 4.8756 |  | 3.915 | 0.6526 | 4.0086 | 3.3693 | 3.3393 | 1.0909 | 10.7855 | 14.2538 | 14.8537 | 11.0854 | 0 | -0.0023 | 0.0007 | 0.004 | 0.0007 | -0.0001 | 0.0229 | 0 | -0.0191 | -360.1773 | 17.4131 | -360.4542 | 17.6636 | -360.8204 | 18.1214 | -360.765 | 17.5876 | -352.6075 | 18.682 | -352.6198 | 16.8197
12:51 | 5468 | 45.0077 | 202.7181 | 450.1624 | 457.0877 | -16.5202 | -39.6811 | 11.7685 | 8.0391 | 2.4546 | 0.734 | 2.9567 | -1.0388 | 12.0837 | 5.0977 | 0.6211 | 0.6607 | 0.9632 | 0.7485 | -129.1768 | 1.3369 | 5.8335 | 2.066 | -2.4558 | -0.7992 | 4.8703 |  | 4.013 | 0.5779 | 4.0086 | 3.3696 | 3.3354 | 1.0897 | 10.7591 | 14.2612 | 14.828 | 11.0952 | 0.0001 | -0.0029 | 0.0006 | 0.004 | 0.0009 | -0.0004 | 0.0097 | -0.0035 | -0.0027 | -360.1896 | 17.409 | -360.445 | 17.6718 | -360.8358 | 18.1625 | -360.8389 | 17.6102 | -352.5921 | 18.6799 | -352.6321 | 16.8279
12:51 | 5469 | 44.9975 | 202.7716 | 450.2811 | 457.1418 | -16.6252 | -39.6531 | 11.735 | 7.9901 | 2.4616 | 0.8224 | 2.9588 | -0.9446 | 12.1586 | 5.034 | 0.6225 | 0.6613 | 0.9635 | 0.7493 | -129.1056 | 1.3421 | 5.779 | 1.8929 | -2.4724 | -0.78 | 4.8749 |  | 3.9654 | 0.5312 | 4.0099 | 3.3696 | 3.3382 | 1.0919 | 10.7844 | 14.2929 | 14.8513 | 11.1078 | 0.0003 | -0.0033 | 0.0016 | 0.0047 | 0.0008 | -0.0003 | 0.03 | 0.0054 | -0.0071 | -360.1773 | 17.4172 | -360.4635 | 17.6677 | -360.8081 | 18.1502 | -360.8574 | 17.6266 | -352.6044 | 18.6963 | -352.6352 | 16.832
12:51 | 5470 | 45.002 | 202.6456 | 450.2274 | 457.0653 | -16.6228 | -39.6704 | 11.6723 | 7.9308 | 2.4125 | 0.8195 | 3.1203 | -1.0284 | 12.1485 | 5.0367 | 0.6229 | 0.6607 | 0.9626 | 0.7492 | -129.0365 | 1.3243 | 5.8884 | 1.7751 | -2.4389 | -0.9021 | 4.808 |  | 4.0036 | 0.5568 | 4.011 | 3.3724 | 3.3417 | 1.0914 | 10.817 | 14.2671 | 14.8522 | 11.0948 | 0.0002 | -0.0025 | 0.0003 | 0.0035 | 0.0008 | -0.0008 | 0.0111 | -0.0077 | -0.0017 | -360.1835 | 17.4254 | -360.4758 | 17.6738 | -360.8481 | 18.1584 | -360.8143 | 17.6122 | -352.6475 | 18.7004 | -352.6567 | 16.8464
12:51 | 5471 | 44.9899 | 202.7604 | 450.1954 | 457.0533 | -16.5347 | -39.6694 | 11.754 | 7.9758 | 2.4484 | 0.8856 | 3.0558 | -1.0912 | 12.1287 | 5.0031 | 0.6203 | 0.6587 | 0.9611 | 0.7492 | -129.1152 | 1.365 | 5.8241 | 1.756 | -2.4182 | -0.8449 | 4.8337 |  | 4.0069 | 0.5931 | 4.0099 | 3.3696 | 3.3404 | 1.0913 | 10.803 | 14.2764 | 14.8621 | 11.0865 | -0.0004 | -0.0025 | 0.0009 | 0.004 | 0.0009 | 0.0003 | 0.0174 | -0.0158 | 0.0111 | -360.2235 | 17.411 | -360.4542 | 17.6615 | -360.8112 | 18.1645 | -360.8727 | 17.6307 | -352.6167 | 18.6963 | -352.6629 | 16.8217
12:51 | 5472 | 45.019 | 202.662 | 450.3584 | 457.074 | -16.6172 | -39.7253 | 11.7332 | 7.9509 | 2.4065 | 0.9037 | 3.1585 | -1.23 | 12.0312 | 5.0216 | 0.6207 | 0.6608 | 0.9661 | 0.7484 | -129.1482 | 1.1656 | 5.7468 | 1.7292 | -2.4524 | -0.9258 | 4.7896 |  | 4.0298 | 0.5849 | 4.0089 | 3.3668 | 3.3394 | 1.0918 | 10.7972 | 14.2766 | 14.8342 | 11.1092 | 0.0007 | -0.002 | 0.0007 | 0.004 | 0.0008 | -0.0007 | 0.017 | -0.0141 | -0.024 | -360.2142 | 17.4172 | -360.4512 | 17.6553 | -360.7989 | 18.1379 | -360.8389 | 17.6061 | -352.6475 | 18.7087 | -352.6598 | 16.8217
12:51 | 5473 | 45.1003 | 202.7314 | 450.2469 | 457.1463 | -16.6029 | -39.6508 | 11.7782 | 7.9996 | 2.5 | 0.9522 | 3.0991 | -1.0358 | 12.1487 | 5.1142 | 0.6224 | 0.6637 | 0.9693 | 0.7518 | -129.1511 | 1.3987 | 5.8463 | 1.7849 | -2.4206 | -0.8938 | 4.865 |  | 4.0469 | 0.5833 | 4.0097 | 3.3678 | 3.3387 | 1.0908 | 10.7938 | 14.2902 | 14.8753 | 11.0948 | 0.0002 | -0.003 | 0.0006 | 0.0038 | 0.0007 | -0.0003 | 0.0027 | -0.013 | -0.0144 | -360.1311 | 17.4048 | -360.5066 | 17.6841 | -360.8266 | 18.142 | -360.802 | 17.5732 | -352.5736 | 18.7025 | -352.7029 | 16.8628
12:51 | 5474 | 45.0812 | 202.6763 | 450.198 | 457.0565 | -16.539 | -39.5929 | 11.7881 | 7.9639 | 2.4821 | 0.7777 | 3.1629 | -1.0858 | 12.1865 | 5.0952 | 0.6207 | 0.6625 | 0.9648 | 0.7488 | -129.0636 | 1.3886 | 5.8361 | 1.8248 | -2.4337 | -0.7394 | 4.8547 |  | 4.0444 | 0.5169 | 4.0105 | 3.3663 | 3.3408 | 1.09 | 10.7846 | 14.2518 | 14.8354 | 11.0862 | -0.0001 | -0.003 | 0.0008 | 0.0039 | 0.0008 | -0.0006 | 0.0252 | -0.0013 | -0.0106 | -360.1311 | 17.3761 | -360.3742 | 17.6245 | -360.7897 | 18.1481 | -360.8297 | 17.602 | -352.6136 | 18.6614 | -352.586 | 16.8135
12:51 | 5475 | 45.1071 | 202.736 | 450.2552 | 457.15 | -16.5998 | -39.5653 | 11.7487 | 7.9473 | 2.4911 | 0.8097 | 3.0733 | -1.008 | 12.2401 | 5.105 | 0.622 | 0.6597 | 0.9635 | 0.7513 | -129.0695 | 1.4425 | 5.802 | 1.7852 | -2.4824 | -0.816 | 4.8752 |  | 4.0056 | 0.5526 | 4.0094 | 3.3667 | 3.3368 | 1.0914 | 10.7787 | 14.2695 | 14.8665 | 11.1028 | -0.0003 | -0.0024 | 0.0008 | 0.0038 | 0.0006 | -0.0008 | 0.031 | -0.011 | -0.0234 | -360.1896 | 17.4172 | -360.4666 | 17.6389 | -360.7589 | 18.1071 | -360.7497 | 17.5896 | -352.6413 | 18.7025 | -352.6352 | 16.8135
12:51 | 5476 | 45.1451 | 202.7444 | 450.3084 | 457.2489 | -16.5425 | -39.6495 | 11.7679 | 7.9478 | 2.4803 | 0.8955 | 3.1349 | -0.9982 | 12.1693 | 5.0379 | 0.6205 | 0.6614 | 0.9659 | 0.7486 | -129.119 | 1.4619 | 5.7584 | 1.8837 | -2.4191 | -0.7972 | 4.936 |  | 3.9852 | 0.5092 | 4.0087 | 3.3658 | 3.337 | 1.0917 | 10.7673 | 14.275 | 14.847 | 11.0919 | -0.0005 | -0.0032 | 0.0007 | 0.0039 | 0.0002 | -0.0004 | 0.0021 | -0.0122 | -0.011 | -360.0819 | 17.3597 | -360.4019 | 17.6574 | -360.7866 | 18.142 | -360.7804 | 17.5547 | -352.5429 | 18.6491 | -352.6075 | 16.8258
12:51 | 5477 | 45.1808 | 202.781 | 450.3774 | 457.2055 | -16.5414 | -39.5429 | 11.7632 | 7.9225 | 2.5002 | 0.8707 | 3.0401 | -1.0416 | 12.1348 | 5.0811 | 0.6222 | 0.6629 | 0.9647 | 0.7491 | -129.1673 | 1.4702 | 5.7844 | 1.8544 | -2.3678 | -0.8526 | 4.9418 |  | 3.9958 | 0.5441 | 4.0099 | 3.3699 | 3.338 | 1.0919 | 10.7706 | 14.2441 | 14.8648 | 11.1291 | 0.0003 | -0.0029 | 0.0006 | 0.004 | 0.001 | -0.0011 | 0.024 | -0.0206 | -0.0101 | -360.1988 | 17.3864 | -360.3773 | 17.6061 | -360.7343 | 18.1255 | -360.8266 | 17.6143 | -352.6321 | 18.6881 | -352.5644 | 16.7909
12:51 | 5478 | 45.1496 | 202.7744 | 450.3285 | 457.1732 | -16.5591 | -39.6783 | 11.7027 | 7.9341 | 2.5468 | 0.699 | 3.073 | -1.0168 | 12.0962 | 5.0474 | 0.621 | 0.6606 | 0.9688 | 0.7509 | -129.1126 | 1.3909 | 5.8886 | 1.8149 | -2.3121 | -0.7719 | 4.8787 |  | 3.9576 | 0.552 | 4.01 | 3.3696 | 3.339 | 1.0923 | 10.7834 | 14.2799 | 14.8478 | 11.0901 | -0.0001 | -0.0031 | 0.0007 | 0.0036 | 0.0007 | -0.0002 | -0.0007 | -0.022 | -0.0009 | -360.1188 | 17.409 | -360.4758 | 17.6615 | -360.7958 | 18.1071 | -360.7404 | 17.565 | -352.5675 | 18.6963 | -352.6321 | 16.8299
12:51 | 5479 | 45.1485 | 202.8219 | 450.3374 | 457.1537 | -16.5271 | -39.5461 | 11.75 | 7.9212 | 2.5313 | 0.8346 | 2.9893 | -0.8875 | 12.2057 | 5.113 | 0.6219 | 0.6636 | 0.9641 | 0.7497 | -129.0822 | 1.4497 | 5.8185 | 1.9767 | -2.3956 | -0.7887 | 4.8279 |  | 3.9899 | 0.5206 | 4.0087 | 3.3683 | 3.3345 | 1.092 | 10.8122 | 14.3206 | 14.8788 | 11.1529 | -0.0007 | -0.0027 | 0.0007 | 0.0038 | 0.001 | -0.0003 | 0.0074 | 0.0092 | -0.0097 | -360.1342 | 17.372 | -360.3835 | 17.6328 | -360.7989 | 18.1625 | -360.845 | 17.5937 | -352.5675 | 18.6491 | -352.5767 | 16.8156
12:51 | 5480 | 45.1777 | 202.7465 | 450.3375 | 457.1956 | -16.5988 | -39.5658 | 11.7916 | 7.9652 | 2.5511 | 0.7362 | 3.0025 | -1.0697 | 12.1123 | 4.9835 | 0.6213 | 0.6606 | 0.9663 | 0.7511 | -129.0962 | 1.3985 | 5.7487 | 1.9555 | -2.4368 | -0.8007 | 4.8473 |  | 4.0144 | 0.5857 | 4.01 | 3.3676 | 3.3405 | 1.0909 | 10.7937 | 14.2732 | 14.8311 | 11.1172 | -0.0002 | -0.0026 | 0.0012 | 0.0039 | 0.0007 | -0.0001 | -0.0082 | -0.0023 | -0.0184 | -360.2081 | 17.411 | -360.4327 | 17.6225 | -360.7404 | 18.1153 | -360.8081 | 17.6081 | -352.5983 | 18.6922 | -352.6013 | 16.7889
12:51 | 5481 | 45.2201 | 202.6805 | 450.2889 | 457.1619 | -16.5627 | -39.4999 | 11.7458 | 8.0737 | 2.5348 | 0.8728 | 2.9615 | -1.0261 | 12.0637 | 5.1115 | 0.6204 | 0.6627 | 0.9629 | 0.75 | -129.0813 | 1.4212 | 5.7672 | 2.0407 | -2.4398 | -0.7832 | 4.8943 |  | 3.9923 | 0.5008 | 4.01 | 3.3707 | 3.3383 | 1.091 | 10.8204 | 14.3055 | 14.8747 | 11.1208 | -0.0001 | -0.0032 | 0.0008 | 0.0037 | 0.0011 | -0.0006 | 0.0162 | -0.0157 | -0.0183 | -360.1373 | 17.4131 | -360.4727 | 17.6759 | -360.8389 | 18.1255 | -360.7897 | 17.5753 | -352.5644 | 18.6922 | -352.6752 | 16.8443
12:51 | 5482 | 45.1711 | 202.7285 | 450.285 | 457.1307 | -16.4834 | -39.508 | 11.8051 | 8.1385 | 2.661 | 0.8347 | 3.0483 | -1.0153 | 12.169 | 5.0981 | 0.6194 | 0.6608 | 0.9623 | 0.75 | -129.0468 | 1.4748 | 5.688 | 2.0624 | -2.4347 | -0.7243 | 5.0137 |  | 3.9433 | 0.5777 | 4.0103 | 3.3677 | 3.3373 | 1.0914 | 10.7834 | 14.2972 | 14.8304 | 11.1017 | -0.0001 | -0.0031 | 0.001 | 0.0039 | 0.0007 | 0 | 0.007 | -0.0106 | -0.0185 | -360.1404 | 17.3823 | -360.4296 | 17.6471 | -360.8174 | 18.1687 | -360.8481 | 17.5999 | -352.5736 | 18.6614 | -352.5706 | 16.8156
12:51 | 5483 | 45.2048 | 202.8333 | 450.3426 | 457.255 | -16.3736 | -39.5219 | 11.9223 | 8.1489 | 2.5577 | 0.8085 | 2.9167 | -1.0189 | 12.1692 | 5.1264 | 0.6219 | 0.6621 | 0.9598 | 0.7498 | -129.1508 | 1.4216 | 5.7491 | 1.9851 | -2.4535 | -0.8073 | 4.9941 |  | 3.9777 | 0.6252 | 4.0089 | 3.3683 | 3.3396 | 1.0918 | 10.7776 | 14.3144 | 14.8467 | 11.0847 | -0.0006 | -0.0032 | 0.0009 | 0.0041 | 0.0012 | -0.0004 | 0.026 | -0.0118 | 0.0008 | -360.2142 | 17.4295 | -360.4512 | 17.6369 | -360.802 | 18.1358 | -360.7989 | 17.604 | -352.626 | 18.6984 | -352.6383 | 16.8115
12:51 | 5484 | 45.1959 | 202.7408 | 450.3096 | 457.2173 | -16.3394 | -39.4298 | 11.9885 | 8.1179 | 2.5667 | 0.8046 | 2.9258 | -0.8597 | 12.2237 | 5.0905 | 0.6219 | 0.6617 | 0.9639 | 0.7504 | -129.1177 | 1.433 | 5.7512 | 2.0921 | -2.449 | -0.8509 | 5.0261 |  | 4.0139 | 0.6082 | 4.0098 | 3.3669 | 3.3386 | 1.0934 | 10.8019 | 14.2809 | 14.8423 | 11.0916 | -0.0004 | -0.0026 | 0.0007 | 0.0038 | 0.001 | -0.0001 | 0.0036 | -0.0008 | -0.0168 | -360.205 | 17.4069 | -360.4542 | 17.6656 | -360.8481 | 18.1461 | -360.8327 | 17.5978 | -352.5829 | 18.684 | -352.6352 | 16.832
12:51 | 5485 | 45.1716 | 202.8601 | 450.3195 | 457.1473 | -16.355 | -39.4811 | 11.9154 | 8.1221 | 2.4858 | 0.7431 | 2.9765 | -0.9382 | 12.1839 | 5.1077 | 0.6224 | 0.662 | 0.967 | 0.7513 | -129.177 | 1.2735 | 5.807 | 2.0523 | -2.399 | -0.7676 | 4.9996 |  | 4.0028 | 0.6755 | 4.009 | 3.3687 | 3.3396 | 1.0926 | 10.7787 | 14.2871 | 14.8686 | 11.0847 | 0.0008 | -0.0027 | 0.001 | 0.0044 | 0.001 | -0.0006 | 0.021 | -0.0073 | 0.0147 | -360.1896 | 17.4048 | -360.4266 | 17.6348 | -360.8143 | 18.1358 | -360.8266 | 17.6122 | -352.5921 | 18.6881 | -352.629 | 16.8197
12:51 | 5486 | 45.1894 | 202.8348 | 450.3994 | 457.1339 | -16.5055 | -39.5919 | 11.8488 | 8.2186 | 2.6057 | 0.7928 | 3.0551 | -1.0063 | 12.1763 | 5.1227 | 0.6224 | 0.6593 | 0.9644 | 0.7516 | -129.2046 | 1.2839 | 5.822 | 2.0405 | -2.3401 | -0.8211 | 4.9564 |  | 3.9008 | 0.685 | 4.0082 | 3.3705 | 3.3359 | 1.0908 | 10.795 | 14.2799 | 14.842 | 11.1074 | 0.0001 | -0.0031 | 0.0005 | 0.0032 | 0.0008 | -0.0004 | 0.0138 | -0.0128 | -0.0203 | -360.1927 | 17.4192 | -360.445 | 17.6451 | -360.7989 | 18.144 | -360.8358 | 17.5978 | -352.6136 | 18.7045 | -352.6413 | 16.8156
12:51 | 5487 | 45.152 | 202.795 | 450.3354 | 457.1456 | -16.4844 | -39.5954 | 11.9422 | 8.0905 | 2.5346 | 0.7215 | 3.0632 | -1.0754 | 12.028 | 4.9698 | 0.6219 | 0.6615 | 0.9653 | 0.75 | -129.1473 | 1.3985 | 5.8446 | 2.0547 | -2.4396 | -0.8835 | 4.8509 |  | 4.0055 | 0.6379 | 4.0089 | 3.3667 | 3.337 | 1.0929 | 10.8086 | 14.306 | 14.8548 | 11.1081 | -0.0001 | -0.0023 | 0.0013 | 0.004 | 0.0011 | -0.0001 | -0.0006 | 0.0059 | -0.0055 | -360.1927 | 17.409 | -360.4512 | 17.6307 | -360.8358 | 18.1502 | -360.8789 | 17.6143 | -352.6136 | 18.6902 | -352.6352 | 16.8217
12:51 | 5488 | 45.2032 | 202.8225 | 450.2744 | 457.1595 | -16.5205 | -39.6121 | 11.8882 | 8.1709 | 2.5911 | 0.7273 | 3.1134 | -0.9993 | 12.073 | 5.0339 | 0.623 | 0.6603 | 0.9627 | 0.7496 | -129.1568 | 1.2874 | 5.8178 | 2.0302 | -2.3992 | -0.8597 | 4.8591 |  | 3.9972 | 0.6522 | 4.0096 | 3.3694 | 3.3367 | 1.0908 | 10.7649 | 14.2844 | 14.8522 | 11.1121 | -0.0002 | -0.0025 | 0.0013 | 0.0041 | 0.0007 | -0.001 | 0.0113 | -0.0048 | -0.0152 | -360.2204 | 17.4213 | -360.4604 | 17.6389 | -360.8297 | 18.144 | -360.8297 | 17.6245 | -352.6229 | 18.7107 | -352.6413 | 16.8176
12:51 | 5489 | 45.1458 | 202.8328 | 450.3083 | 457.112 | -16.4524 | -39.753 | 11.8737 | 8.0603 | 2.4641 | 0.6002 | 3.0139 | -0.9487 | 12.1213 | 5.119 | 0.6223 | 0.6617 | 0.9626 | 0.7503 | -129.1751 | 1.3299 | 5.7532 | 1.9315 | -2.4288 | -0.9236 | 4.8116 |  | 4.0234 | 0.7302 | 4.0086 | 3.3706 | 3.3373 | 1.0929 | 10.8051 | 14.3201 | 14.8933 | 11.1041 | 0.0005 | -0.0025 | 0.0008 | 0.0036 | 0.001 | 0 | 0.0026 | 0.0052 | -0.0062 | -360.1835 | 17.4172 | -360.4727 | 17.6574 | -360.8358 | 18.1625 | -360.8389 | 17.602 | -352.6167 | 18.7148 | -352.6506 | 16.8423
12:51 | 5490 | 45.1769 | 202.8427 | 450.3268 | 457.1068 | -16.4738 | -39.6288 | 11.8921 | 8.0994 | 2.5662 | 0.7084 | 3.0054 | -0.9351 | 12.0937 | 5.0488 | 0.6213 | 0.6624 | 0.9632 | 0.7497 | -129.1732 | 1.3154 | 5.6917 | 1.9243 | -2.3621 | -0.9177 | 4.8671 |  | 3.9944 | 0.7108 | 4.0096 | 3.3669 | 3.3368 | 1.0919 | 10.7718 | 14.2741 | 14.8304 | 11.0786 | 0.0004 | -0.0029 | 0.0009 | 0.0046 | 0.0012 | -0.0006 | -0.0064 | -0.0029 | 0.0045 | -360.2081 | 17.3966 | -360.4358 | 17.6512 | -360.8358 | 18.1769 | -360.8789 | 17.6245 | -352.626 | 18.682 | -352.6167 | 16.832
12:51 | 5491 | 45.1632 | 202.8189 | 450.3566 | 457.1386 | -16.5152 | -39.6642 | 11.8263 | 8.1635 | 2.5332 | 0.7364 | 3.0209 | -1.0261 | 12.0716 | 5.0389 | 0.621 | 0.6627 | 0.9638 | 0.7491 | -129.2149 | 1.3571 | 5.8011 | 1.8983 | -2.4172 | -0.9268 | 4.8246 |  | 3.969 | 0.7268 | 4.0098 | 3.3676 | 3.3379 | 1.0907 | 10.7523 | 14.2598 | 14.8313 | 11.0887 | -0.0003 | -0.0027 | 0.0006 | 0.0042 | 0.0005 | -0.0004 | 0.0181 | -0.0074 | 0.0009 | -360.2481 | 17.4418 | -360.4727 | 17.6389 | -360.7958 | 18.1399 | -360.842 | 17.6266 | -352.7029 | 18.7251 | -352.6598 | 16.8238
12:51 | 5492 | 45.1178 | 202.7599 | 450.3337 | 457.1329 | -16.4495 | -39.6411 | 11.8202 | 8.1749 | 2.5157 | 0.6548 | 2.9501 | -1.0589 | 12.0703 | 5.0289 | 0.6213 | 0.6643 | 0.9656 | 0.7511 | -129.2183 | 1.3473 | 5.7782 | 1.9266 | -2.4223 | -0.8248 | 4.8554 |  | 3.9267 | 0.8254 | 4.0112 | 3.3676 | 3.3396 | 1.0919 | 10.7579 | 14.2545 | 14.8519 | 11.0876 | -0.0001 | -0.0024 | 0.0007 | 0.0036 | 0.0012 | -0.001 | 0.0117 | -0.0138 | 0.0209 | -360.1773 | 17.3966 | -360.4666 | 17.6697 | -360.882 | 18.1728 | -360.8266 | 17.5855 | -352.586 | 18.6902 | -352.6906 | 16.8607
12:51 | 5493 | 45.1386 | 202.7384 | 450.1305 | 457.1367 | -16.57 | -39.6891 | 11.7274 | 8.0571 | 2.4551 | 0.6754 | 2.9549 | -1.0107 | 12.1613 | 5.1015 | 0.6226 | 0.6624 | 0.9633 | 0.7504 | -129.203 | 1.343 | 5.7818 | 1.9894 | -2.3796 | -0.808 | 4.8747 |  | 3.956 | 0.7481 | 4.0095 | 3.3667 | 3.3384 | 1.0924 | 10.7686 | 14.2468 | 14.8162 | 11.0537 | -0.0003 | -0.0031 | 0.0004 | 0.0037 | 0.0005 | -0.0004 | -0.0002 | -0.0175 | 0.0033 | -360.1896 | 17.3987 | -360.4327 | 17.6266 | -360.802 | 18.1625 | -360.9066 | 17.6389 | -352.6875 | 18.6963 | -352.6013 | 16.8094
12:51 | 5494 | 45.1226 | 202.807 | 450.261 | 457.0801 | -16.3548 | -39.4963 | 11.945 | 8.0868 | 2.5135 | 0.707 | 3.0403 | -0.9913 | 12.1249 | 5.0673 | 0.6221 | 0.6643 | 0.9656 | 0.7495 | -129.182 | 1.315 | 5.6896 | 2.0368 | -2.365 | -0.8506 | 4.8807 |  | 3.9776 | 0.5464 | 4.0103 | 3.3676 | 3.3354 | 1.0913 | 10.7672 | 14.2406 | 14.8318 | 11.0912 | 0.0006 | -0.0029 | 0.0013 | 0.0039 | 0.0011 | -0.0006 | -0.0019 | -0.005 | -0.0083 | -360.1804 | 17.4172 | -360.5066 | 17.6656 | -360.8112 | 18.1214 | -360.7743 | 17.5876 | -352.6198 | 18.7128 | -352.7121 | 16.8484
12:51 | 5495 | 45.144 | 202.783 | 450.2078 | 457.1596 | -16.3204 | -39.4333 | 11.9669 | 8.065 | 2.52 | 0.7097 | 2.9673 | -0.9842 | 12.1378 | 5.1245 | 0.622 | 0.6615 | 0.9655 | 0.7514 | -129.136 | 1.4321 | 5.7655 | 2.1122 | -2.361 | -0.7902 | 4.8839 |  | 3.9738 | 0.6155 | 4.0085 | 3.3694 | 3.3397 | 1.0915 | 10.7891 | 14.3031 | 14.843 | 11.1129 | -0.0003 | -0.0026 | 0.0007 | 0.0037 | 0.0004 | -0.0004 | 0.0161 | 0.0045 | -0.0159 | -360.1435 | 17.3658 | -360.3896 | 17.6266 | -360.7958 | 18.183 | -360.8758 | 17.602 | -352.6106 | 18.6512 | -352.6013 | 16.8217
12:51 | 5496 | 45.1122 | 202.7836 | 450.2191 | 457.1287 | -16.3763 | -39.5103 | 11.954 | 8.0342 | 2.5843 | 0.7468 | 3.0157 | -1.0247 | 12.0786 | 5.0053 | 0.6209 | 0.6612 | 0.9637 | 0.7511 | -129.1486 | 1.4264 | 5.8158 | 2.0436 | -2.3471 | -0.8813 | 4.9076 |  | 3.9182 | 0.4588 | 4.0097 | 3.3694 | 3.337 | 1.0926 | 10.8088 | 14.3055 | 14.8747 | 11.1323 | -0.0007 | -0.0028 | 0.0013 | 0.0043 | 0.0008 | -0.0009 | 0.0038 | -0.0105 | 0.0031 | -360.1988 | 17.4213 | -360.4419 | 17.6061 | -360.7466 | 18.1132 | -360.7866 | 17.5958 | -352.6352 | 18.7025 | -352.6383 | 16.8135
12:51 | 5497 | 45.1478 | 202.7518 | 450.3067 | 457.1074 | -16.4298 | -39.5326 | 11.8519 | 7.9719 | 2.6335 | 0.6525 | 2.9796 | -1.0417 | 12.1291 | 5.0993 | 0.6222 | 0.6614 | 0.9639 | 0.7518 | -129.107 | 1.3585 | 5.779 | 2.0791 | -2.2571 | -0.8375 | 4.9773 |  | 3.9017 | 0.5156 | 4.0097 | 3.3666 | 3.3374 | 1.0906 | 10.8017 | 14.3106 | 14.8418 | 11.1359 | 0.0001 | -0.0027 | 0.0011 | 0.0039 | 0.0009 | -0.0002 | 0.0223 | -0.0036 | -0.0268 | -360.0727 | 17.3679 | -360.4173 | 17.6471 | -360.8358 | 18.1502 | -360.7773 | 17.5547 | -352.5644 | 18.6594 | -352.6229 | 16.8381
12:51 | 5498 | 45.268 | 202.7063 | 450.2176 | 457.1298 | -16.4259 | -39.4426 | 11.8657 | 7.957 | 2.5575 | 0.6981 | 2.9906 | -1.0581 | 12.1089 | 5.0244 | 0.6236 | 0.6615 | 0.9669 | 0.7496 | -129.2462 | 1.2913 | 5.7527 | 2.1994 | -2.266 | -0.771 | 4.8973 |  | 3.9479 | 0.6374 | 4.0103 | 3.3689 | 3.3393 | 1.0934 | 10.8123 | 14.3263 | 14.8893 | 11.1186 | -0.0002 | -0.0031 | 0.0007 | 0.0039 | 0.0009 | -0.0004 | 0.02 | -0.0056 | 0.0055 | -360.1558 | 17.3802 | -360.3773 | 17.5937 | -360.7281 | 18.1337 | -360.842 | 17.6184 | -352.6198 | 18.6758 | -352.5921 | 16.7868
12:51 | 5499 | 45.2505 | 202.7698 | 450.3478 | 457.2109 | -16.3448 | -39.4686 | 11.8599 | 8.1391 | 2.5986 | 0.8295 | 3.0149 | -1.1089 | 12.1225 | 5.1239 | 0.6239 | 0.6657 | 0.9647 | 0.7495 | -129.2455 | 1.3773 | 5.5968 | 2.2357 | -2.2311 | -0.7981 | 4.9466 |  | 3.9404 | 0.6312 | 4.0108 | 3.3673 | 3.3358 | 1.0924 | 10.7741 | 14.2707 | 14.8563 | 11.1038 | 0.0001 | -0.0028 | 0.0009 | 0.0042 | 0.0004 | -0.0007 | 0.0128 | -0.0157 | 0.0021 | -360.1404 | 17.3966 | -360.4481 | 17.6553 | -360.802 | 18.0947 | -360.7497 | 17.5671 | -352.5552 | 18.684 | -352.6598 | 16.8381
12:51 | 5500 | 45.2258 | 202.7556 | 450.3136 | 457.2468 | -16.4347 | -39.512 | 11.8128 | 7.9785 | 2.6336 | 0.7133 | 2.9637 | -1.1103 | 12.0549 | 5.147 | 0.6221 | 0.6642 | 0.9628 | 0.7503 | -129.2773 | 1.3242 | 5.6966 | 2.0971 | -2.3095 | -0.854 | 4.9522 |  | 3.9638 | 0.5682 | 4.0089 | 3.3668 | 3.3368 | 1.0923 | 10.8031 | 14.2819 | 14.8368 | 11.0873 | -0.0005 | -0.0027 | 0.0002 | 0.0037 | 0.0001 | -0.0014 | 0.0116 | -0.0163 | -0.0057 | -360.1342 | 17.3699 | -360.3742 | 17.6225 | -360.7989 | 18.1584 | -360.8666 | 17.5855 | -352.5675 | 18.6594 | -352.5675 | 16.8074
12:51 | 5501 | 45.1268 | 202.7225 | 450.3089 | 457.2202 | -16.4361 | -39.4824 | 11.7602 | 8.0596 | 2.6339 | 0.8053 | 3.0237 | -1.0191 | 12.1439 | 5.0085 | 0.6206 | 0.6645 | 0.9613 | 0.7491 | -129.2785 | 1.336 | 5.8982 | 1.9726 | -2.3342 | -0.7723 | 4.9377 |  | 3.9676 | 0.5353 | 4.0078 | 3.3662 | 3.3341 | 1.0917 | 10.7812 | 14.2598 | 14.8429 | 11.0945 | -0.0001 | -0.003 | 0.0005 | 0.0039 | 0.0009 | -0.0007 | 0.0116 | -0.0231 | -0.0191 | -360.2235 | 17.4336 | -360.4604 | 17.6143 | -360.7589 | 18.1091 | -360.7866 | 17.604 | -352.6383 | 18.6984 | -352.6321 | 16.8053
12:51 | 5502 | 45.1051 | 202.7047 | 450.2025 | 457.1021 | -16.4136 | -39.5395 | 11.6974 | 8.0267 | 2.6154 | 0.7814 | 2.9538 | -1.023 | 12.125 | 5.1277 | 0.6229 | 0.6644 | 0.9664 | 0.7502 | -129.2911 | 1.2778 | 5.9657 | 2.0082 | -2.4241 | -0.8153 | 4.8901 |  | 3.9983 | 0.4601 | 4.0094 | 3.3682 | 3.3372 | 1.0932 | 10.7649 | 14.2208 | 14.8174 | 11.0659 | -0.0002 | -0.0036 | 0.0015 | 0.0038 | 0.0009 | -0.0001 | 0.0108 | -0.0092 | -0.0104 | -360.1558 | 17.3905 | -360.4696 | 17.6656 | -360.8697 | 18.1502 | -360.8112 | 17.5568 | -352.5613 | 18.6779 | -352.626 | 16.8423
12:51 | 5503 | 45.2155 | 202.7642 | 450.2619 | 457.1781 | -16.4613 | -39.54 | 11.7819 | 8.0706 | 2.6098 | 0.7989 | 2.9721 | -0.9797 | 12.1356 | 5.0991 | 0.6219 | 0.6616 | 0.9601 | 0.7497 | -129.3016 | 1.2848 | 5.9309 | 1.9637 | -2.4056 | -0.774 | 4.9622 |  | 4.0384 | 0.5591 | 4.0084 | 3.364 | 3.335 | 1.0914 | 10.8064 | 14.3206 | 14.8962 | 11.1183 | -0.0001 | -0.003 | 0.0012 | 0.0038 | 0.0008 | -0.0008 | 0.0058 | -0.0146 | -0.0148 | -360.2512 | 17.4028 | -360.4327 | 17.6204 | -360.7743 | 18.1522 | -360.8697 | 17.6122 | -352.626 | 18.6922 | -352.6106 | 16.8032
12:51 | 5504 | 45.1688 | 202.797 | 450.1852 | 457.0793 | -16.4335 | -39.5142 | 11.6898 | 8.138 | 2.666 | 0.787 | 3.0693 | -0.9641 | 12.0924 | 5.0367 | 0.6215 | 0.6641 | 0.962 | 0.75 | -129.2894 | 1.3589 | 6.011 | 1.939 | -2.4833 | -0.8747 | 4.9163 |  | 4.1344 | 0.6637 | 4.0101 | 3.3669 | 3.3373 | 1.0915 | 10.8284 | 14.2907 | 14.8959 | 11.1052 | 0 | -0.0022 | 0.0012 | 0.0045 | 0.0008 | 0.0001 | 0.0124 | -0.0148 | -0.0053 | -360.205 | 17.4213 | -360.5189 | 17.6677 | -360.8358 | 18.144 | -360.8204 | 17.5958 | -352.6229 | 18.7107 | -352.6783 | 16.8402
12:51 | 5505 | 45.1265 | 202.786 | 450.1316 | 457.1379 | -16.3872 | -39.5373 | 11.835 | 8.1451 | 2.6021 | 0.8167 | 3.0847 | -1.0674 | 12.0564 | 5.0756 | 0.6211 | 0.6626 | 0.9619 | 0.751 | -129.2765 | 1.212 | 5.9289 | 2.0138 | -2.4629 | -0.8099 | 4.9979 |  | 4.0914 | 0.7751 | 4.0085 | 3.3653 | 3.3366 | 1.0911 | 10.8319 | 14.2941 | 14.8932 | 11.1204 | -0.0003 | -0.003 | 0.0012 | 0.0039 | 0.0009 | -0.0008 | 0.0172 | -0.013 | -0.0035 | -360.1681 | 17.4069 | -360.4419 | 17.641 | -360.8481 | 18.1769 | -360.8666 | 17.6122 | -352.6537 | 18.7004 | -352.626 | 16.832
12:51 | 5506 | 45.1519 | 202.8791 | 450.2707 | 457.2515 | -16.4069 | -39.5494 | 11.8183 | 8.2122 | 2.7469 | 0.8689 | 3.157 | -1.068 | 12.1377 | 5.1358 | 0.6203 | 0.662 | 0.9651 | 0.7494 | -129.2509 | 1.2361 | 5.8658 | 1.9927 | -2.4276 | -0.8876 | 4.9225 |  | 3.976 | 0.6212 | 4.0099 | 3.3672 | 3.3359 | 1.094 | 10.8169 | 14.2963 | 14.9064 | 11.1345 | 0.0004 | -0.0027 | 0.0009 | 0.0039 | 0.0007 | 0.0003 | 0.0102 | -0.0128 | -0.0127 | -360.2142 | 17.4336 | -360.4727 | 17.6492 | -360.8112 | 18.1543 | -360.8604 | 17.6163 | -352.626 | 18.721 | -352.6506 | 16.8279
12:51 | 5507 | 45.1345 | 202.7462 | 450.2514 | 457.1923 | -16.4151 | -39.4374 | 11.8243 | 8.1173 | 2.7061 | 0.908 | 3.0521 | -0.9463 | 12.0487 | 5.0271 | 0.62 | 0.6617 | 0.9628 | 0.7485 | -129.2942 | 1.3828 | 5.8752 | 1.9226 | -2.3846 | -0.808 | 4.9698 |  | 3.9769 | 0.6893 | 4.0094 | 3.3656 | 3.3389 | 1.0913 | 10.796 | 14.2931 | 14.8813 | 11.0958 | 0.0002 | -0.0027 | 0.0007 | 0.0042 | 0.0012 | -0.0004 | 0.0054 | -0.0094 | -0.0306 | -360.2019 | 17.4151 | -360.4666 | 17.6492 | -360.8389 | 18.1563 | -360.8604 | 17.6102 | -352.6198 | 18.7087 | -352.6598 | 16.8361
12:52 | 5508 | 45.1597 | 202.7184 | 450.2649 | 457.1874 | -16.3556 | -39.5477 | 11.7578 | 8.139 | 2.6403 | 0.8161 | 3.0434 | -0.9283 | 12.1095 | 5.0685 | 0.6214 | 0.6633 | 0.9669 | 0.7508 | -129.2812 | 1.3441 | 5.9313 | 1.822 | -2.4061 | -0.8402 | 4.9089 |  | 3.9982 | 0.487 | 4.0098 | 3.3667 | 3.3388 | 1.0917 | 10.7602 | 14.2858 | 14.8315 | 11.136 | -0.0003 | -0.0026 | 0.0004 | 0.0036 | 0.0004 | -0.0006 | 0.0162 | -0.0012 | -0.0071 | -360.2419 | 17.4172 | -360.4666 | 17.6471 | -360.8204 | 18.1666 | -360.882 | 17.6122 | -352.6506 | 18.7087 | -352.6506 | 16.8381
12:52 | 5509 | 45.1244 | 202.7326 | 450.3028 | 457.1562 | -16.3677 | -39.5917 | 11.7198 | 8.1406 | 2.6217 | 0.7613 | 2.9968 | -0.9699 | 12.0949 | 5.1005 | 0.6226 | 0.6629 | 0.9651 | 0.7487 | -129.3716 | 1.3942 | 6.0008 | 1.952 | -2.3824 | -0.7957 | 4.9072 |  | 3.9486 | 0.4766 | 4.0104 | 3.369 | 3.3377 | 1.0913 | 10.7754 | 14.26 | 14.8208 | 11.0768 | 0 | -0.003 | 0.0005 | 0.0036 | 0.001 | -0.0006 | 0.0057 | 0.0063 | -0.0036 | -360.1835 | 17.4151 | -360.5004 | 17.6574 | -360.8297 | 18.1666 | -360.8666 | 17.5937 | -352.6229 | 18.7025 | -352.6752 | 16.8566
12:52 | 5510 | 45.1817 | 202.7667 | 450.2238 | 457.2028 | -16.3022 | -39.5526 | 11.7444 | 8.1003 | 2.6061 | 0.6904 | 3.0826 | -0.9441 | 12.1721 | 5.0261 | 0.6219 | 0.6591 | 0.9632 | 0.7488 | -129.278 | 1.431 | 5.9816 | 1.9341 | -2.4378 | -0.7832 | 4.9267 |  | 4.0666 | 0.5842 | 4.0104 | 3.3702 | 3.3397 | 1.0922 | 10.7799 | 14.2475 | 14.8389 | 11.0634 | 0.0004 | -0.003 | 0.0011 | 0.004 | 0.001 | -0.0004 | 0.0062 | -0.0069 | -0.0036 | -360.1896 | 17.4069 | -360.4635 | 17.6389 | -360.845 | 18.1666 | -360.8697 | 17.6143 | -352.626 | 18.6922 | -352.6506 | 16.8525
12:52 | 5511 | 45.3021 | 202.7672 | 450.3592 | 457.22 | -16.3512 | -39.5783 | 11.7624 | 8.2368 | 2.6651 | 0.7977 | 3.1054 | -0.9727 | 12.1087 | 5.0709 | 0.6231 | 0.6621 | 0.9598 | 0.7513 | -129.2371 | 1.3673 | 5.9882 | 1.9561 | -2.4373 | -0.813 | 4.9086 |  | 4.0721 | 0.5916 | 4.0094 | 3.3677 | 3.3374 | 1.0919 | 10.7879 | 14.2676 | 14.8496 | 11.1168 | 0.0004 | -0.0025 | 0.0004 | 0.0035 | 0.0011 | -0.0005 | 0.0067 | -0.0002 | -0.0103 | -360.2204 | 17.4172 | -360.4358 | 17.641 | -360.7927 | 18.1502 | -360.8297 | 17.604 | -352.6444 | 18.7066 | -352.626 | 16.8381
12:52 | 5512 | 45.3251 | 202.7829 | 450.3638 | 457.2031 | -16.3022 | -39.4119 | 11.8073 | 8.1637 | 2.5441 | 0.6727 | 2.9943 | -1.1927 | 11.9562 | 5.0339 | 0.6224 | 0.664 | 0.9645 | 0.7506 | -129.1831 | 1.3953 | 5.9704 | 2.0059 | -2.4476 | -0.8127 | 4.8643 |  | 4.0647 | 0.5091 | 4.0104 | 3.3687 | 3.3377 | 1.0918 | 10.781 | 14.2604 | 14.8414 | 11.0814 | -0.0004 | -0.0026 | 0.0015 | 0.0048 | 0.001 | -0.0001 | 0.0036 | 0.005 | -0.0155 | -360.1373 | 17.3966 | -360.4758 | 17.6656 | -360.8389 | 18.1461 | -360.8358 | 17.5773 | -352.6136 | 18.6922 | -352.6937 | 16.8813
12:52 | 5513 | 45.2244 | 202.7826 | 450.3227 | 457.1291 | -16.294 | -39.4457 | 11.8472 | 8.1629 | 2.6324 | 0.9057 | 3.0294 | -1.0899 | 12.0508 | 5.0562 | 0.6218 | 0.6622 | 0.9619 | 0.7508 | -129.1807 | 1.3244 | 5.9591 | 1.9552 | -2.4309 | -0.7625 | 4.8518 |  | 3.9814 | 0.5892 | 4.0115 | 3.3666 | 3.3405 | 1.0945 | 10.7868 | 14.2778 | 14.8529 | 11.0988 | -0.0001 | -0.0027 | 0.0005 | 0.0037 | 0.0007 | -0.0002 | 0.0159 | 0.0074 | 0.006 | -360.1804 | 17.3802 | -360.3896 | 17.6184 | -360.802 | 18.1604 | -360.8727 | 17.6245 | -352.6629 | 18.6758 | -352.5798 | 16.8299
12:52 | 5514 | 45.2159 | 202.6926 | 450.3348 | 457.1547 | -16.2103 | -39.3814 | 11.8868 | 8.1911 | 2.6553 | 0.9148 | 3.0924 | -1.0616 | 12.0062 | 5.1075 | 0.6222 | 0.6656 | 0.9644 | 0.7499 | -129.1759 | 1.3126 | 5.8986 | 1.8819 | -2.4545 | -0.8433 | 4.762 |  | 3.9514 | 0.5852 | 4.0096 | 3.3705 | 3.3406 | 1.0924 | 10.8134 | 14.3043 | 14.8444 | 11.1313 | 0.0003 | -0.003 | 0.0002 | 0.0038 | 0.0009 | -0.0004 | 0.0108 | -0.0125 | -0.0221 | -360.1773 | 17.4254 | -360.485 | 17.6471 | -360.7989 | 18.1194 | -360.7589 | 17.5814 | -352.6506 | 18.7107 | -352.6813 | 16.8484
12:52 | 5515 | 45.1477 | 202.7534 | 450.2837 | 457.0206 | -16.2827 | -39.4792 | 11.8079 | 8.1033 | 2.5758 | 0.8522 | 2.9942 | -1.0174 | 12.076 | 5.1343 | 0.6219 | 0.6626 | 0.9628 | 0.7498 | -129.2093 | 1.4815 | 5.9855 | 1.8704 | -2.5154 | -0.8246 | 4.7942 |  | 3.9996 | 0.5362 | 4.0089 | 3.3696 | 3.3396 | 1.0942 | 10.7857 | 14.2936 | 14.89 | 11.1042 | 0.0003 | -0.0027 | 0.0005 | 0.0042 | 0.0009 | 0 | 0.0217 | -0.0055 | -0.0167 | -360.1127 | 17.3597 | -360.4419 | 17.6451 | -360.8235 | 18.1769 | -360.845 | 17.5835 | -352.5952 | 18.6737 | -352.626 | 16.8525
12:52 | 5516 | 45.223 | 202.7296 | 450.2555 | 457.0887 | -16.2959 | -39.424 | 11.8772 | 8.0619 | 2.519 | 0.8199 | 2.9987 | -1.0109 | 12.0611 | 5.069 | 0.6218 | 0.662 | 0.9626 | 0.7493 | -129.1959 | 1.4271 | 5.9963 | 1.775 | -2.5283 | -0.9021 | 4.718 |  | 3.9683 | 0.5707 | 4.0071 | 3.3668 | 3.3375 | 1.0922 | 10.7881 | 14.2843 | 14.8627 | 11.1241 | -0.0004 | -0.0027 | 0.0012 | 0.0043 | 0.0009 | -0.0008 | 0.0233 | -0.0045 | -0.0035 | -360.1988 | 17.4192 | -360.4296 | 17.6184 | -360.762 | 18.1235 | -360.8204 | 17.6266 | -352.6721 | 18.7148 | -352.6198 | 16.8217
12:52 | 5517 | 45.3549 | 202.781 | 450.4094 | 457.1135 | -16.218 | -39.3839 | 11.9154 | 8.0537 | 2.5456 | 0.7862 | 3.0121 | -1.0285 | 11.9888 | 5.1083 | 0.6203 | 0.6619 | 0.9631 | 0.7484 | -129.2954 | 1.3837 | 5.9609 | 1.8156 | -2.4861 | -0.8825 | 4.7784 |  | 4.0404 | 0.4772 | 4.0087 | 3.3689 | 3.3362 | 1.0919 | 10.7662 | 14.2621 | 14.7983 | 11.045 | -0.0003 | -0.0027 | 0.0007 | 0.0037 | 0.0006 | -0.0001 | 0.0236 | -0.0069 | -0.0312 | -360.1373 | 17.4172 | -360.4727 | 17.6759 | -360.8604 | 18.1563 | -360.7958 | 17.5794 | -352.6106 | 18.6984 | -352.6783 | 16.8772
12:52 | 5518 | 45.3506 | 202.7989 | 450.28 | 457.0954 | -16.3489 | -39.4301 | 11.9337 | 8.0489 | 2.6021 | 0.8398 | 3.0573 | -1.0514 | 12.017 | 5.1793 | 0.6211 | 0.6623 | 0.9618 | 0.75 | -129.3501 | 1.4646 | 5.9833 | 1.8763 | -2.4386 | -0.8603 | 4.7871 |  | 4.0051 | 0.5506 | 4.0099 | 3.3668 | 3.3386 | 1.0934 | 10.7395 | 14.2472 | 14.8079 | 11.041 | 0.0001 | -0.0032 | 0.0015 | 0.004 | 0.0009 | -0.0009 | 0.0071 | -0.0052 | -0.005 | -360.1588 | 17.3925 | -360.4142 | 17.6204 | -360.7927 | 18.1687 | -360.8666 | 17.6204 | -352.6506 | 18.6922 | -352.6106 | 16.8361
12:52 | 5519 | 45.3267 | 202.8842 | 450.4247 | 457.1379 | -16.3799 | -39.5279 | 11.8679 | 8.1256 | 2.6533 | 0.8214 | 3.0978 | -0.8924 | 12.0725 | 5.1521 | 0.623 | 0.6622 | 0.9609 | 0.7484 | -129.3655 | 1.399 | 6.0529 | 1.9906 | -2.4061 | -0.7888 | 4.8291 |  | 4.0503 | 0.5392 | 4.0108 | 3.3671 | 3.3372 | 1.0922 | 10.7718 | 14.2741 | 14.8593 | 11.0959 | -0.0002 | -0.0032 | 0.0007 | 0.0039 | 0.001 | 0.0001 | 0.0202 | -0.0064 | -0.0171 | -360.2512 | 17.4418 | -360.4912 | 17.6574 | -360.842 | 18.1337 | -360.8081 | 17.5958 | -352.6783 | 18.7312 | -352.706 | 16.8607
12:52 | 5520 | 45.3987 | 202.8482 | 450.325 | 457.1135 | -16.4207 | -39.5971 | 11.7973 | 8.0212 | 2.4927 | 0.7436 | 3.0363 | -0.9879 | 12.1334 | 5.1448 | 0.6216 | 0.6601 | 0.9629 | 0.7495 | -129.2675 | 1.504 | 5.9786 | 2.0365 | -2.3722 | -0.7924 | 4.8906 |  | 4.0031 | 0.4893 | 4.0096 | 3.3663 | 3.3343 | 1.0929 | 10.8411 | 14.3094 | 14.9157 | 11.1291 | 0 | -0.0025 | 0.0007 | 0.004 | 0.0014 | -0.0006 | 0.0059 | -0.0071 | -0.0055 | -360.1096 | 17.3823 | -360.4389 | 17.6656 | -360.8666 | 18.183 | -360.8604 | 17.5855 | -352.6167 | 18.6737 | -352.6321 | 16.8648
12:52 | 5521 | 45.3088 | 202.8388 | 450.4128 | 457.1579 | -16.3801 | -39.5318 | 11.8408 | 8.0044 | 2.6147 | 0.7423 | 3.0192 | -0.9195 | 12.1021 | 5.2184 | 0.623 | 0.6638 | 0.9609 | 0.7491 | -129.333 | 1.4536 | 5.976 | 2.0326 | -2.427 | -0.8197 | 4.8481 |  | 4.1091 | 0.5513 | 4.0086 | 3.3648 | 3.3374 | 1.0925 | 10.8377 | 14.2999 | 14.9047 | 11.1262 | -0.0001 | -0.0023 | 0.0009 | 0.0042 | 0.0006 | -0.0002 | 0.0086 | -0.0225 | -0.0178 | -360.2265 | 17.4233 | -360.4296 | 17.6143 | -360.7927 | 18.1481 | -360.885 | 17.6328 | -352.6813 | 18.7107 | -352.6383 | 16.8258
12:52 | 5522 | 45.3004 | 202.8744 | 450.4131 | 457.1207 | -16.489 | -39.4319 | 11.7658 | 8.0483 | 2.5917 | 0.865 | 3.0261 | -0.8906 | 12.0235 | 5.1861 | 0.6216 | 0.664 | 0.9615 | 0.751 | -129.3275 | 1.4363 | 5.9683 | 2.0233 | -2.3416 | -0.8021 | 4.8708 |  | 4.069 | 0.5529 | 4.0099 | 3.3721 | 3.341 | 1.0927 | 10.8041 | 14.3009 | 14.8645 | 11.1161 | 0.0002 | -0.0029 | 0.0002 | 0.0035 | 0.0007 | -0.0009 | 0.0018 | -0.0109 | -0.0013 | -360.1527 | 17.4172 | -360.4973 | 17.6718 | -360.8574 | 18.1276 | -360.7527 | 17.5773 | -352.5983 | 18.7087 | -352.6813 | 16.8648
12:52 | 5523 | 45.3708 | 202.9606 | 450.4445 | 457.0996 | -16.452 | -39.4052 | 11.7862 | 8.0162 | 2.5704 | 0.9091 | 3.0807 | -0.9491 | 12.1328 | 5.1967 | 0.6209 | 0.664 | 0.9626 | 0.7504 | -129.3792 | 1.4734 | 5.8693 | 2.0935 | -2.3752 | -0.6766 | 4.9429 |  | 4.1489 | 0.5344 | 4.0102 | 3.3702 | 3.3362 | 1.092 | 10.8158 | 14.295 | 14.875 | 11.1338 | 0.0003 | -0.0031 | 0.0007 | 0.004 | 0.0006 | -0.0008 | 0.0061 | -0.0107 | -0.0096 | -360.1588 | 17.374 | -360.4081 | 17.6328 | -360.8112 | 18.1769 | -360.8543 | 17.5999 | -352.5798 | 18.6717 | -352.6044 | 16.8423
12:52 | 5524 | 45.4801 | 203.0139 | 450.4088 | 457.205 | -16.4315 | -39.4036 | 11.731 | 8.0446 | 2.5883 | 0.74 | 3.0861 | -1.0163 | 11.9906 | 5.1134 | 0.6206 | 0.6638 | 0.963 | 0.7504 | -129.3764 | 1.4447 | 5.8762 | 2.1336 | -2.3608 | -0.7617 | 4.95 |  | 4.1618 | 0.6023 | 4.0084 | 3.3705 | 3.3359 | 1.0919 | 10.7948 | 14.2689 | 14.8462 | 11.0771 | -0.0003 | -0.0026 | 0.0011 | 0.0041 | 0.0007 | -0.0003 | 0.0087 | -0.0177 | 0.0041 | -360.1896 | 17.4131 | -360.4296 | 17.604 | -360.762 | 18.1173 | -360.802 | 17.5917 | -352.666 | 18.721 | -352.6352 | 16.8238
12:52 | 5525 | 45.3652 | 202.9106 | 450.3798 | 457.2463 | -16.3611 | -39.4162 | 11.7906 | 8.0897 | 2.54 | 0.8569 | 3.0715 | -0.9588 | 12.0016 | 5.1362 | 0.621 | 0.6608 | 0.9641 | 0.7501 | -129.3756 | 1.3467 | 5.9262 | 2.0914 | -2.3731 | -0.7487 | 4.8863 |  | 4.1456 | 0.5587 | 4.0095 | 3.3722 | 3.338 | 1.0926 | 10.7822 | 14.2671 | 14.8232 | 11.0659 | -0.0003 | -0.0025 | 0.0007 | 0.0037 | 0.0014 | -0.0005 | 0.0019 | -0.0077 | -0.0191 | -360.0973 | 17.3884 | -360.4296 | 17.6533 | -360.802 | 18.1235 | -360.802 | 17.5691 | -352.5706 | 18.6902 | -352.6321 | 16.8505
12:52 | 5526 | 45.2999 | 202.9078 | 450.4093 | 457.2367 | -16.3052 | -39.4475 | 11.8074 | 7.9788 | 2.5396 | 0.7118 | 2.9942 | -0.8616 | 12.0717 | 5.1537 | 0.6213 | 0.6602 | 0.9617 | 0.7502 | -129.338 | 1.2697 | 5.9509 | 1.9777 | -2.4185 | -0.8359 | 4.8156 |  | 4.0592 | 0.4783 | 4.0092 | 3.3727 | 3.3386 | 1.0928 | 10.7776 | 14.2683 | 14.842 | 11.0786 | -0.0005 | -0.0034 | 0.0014 | 0.0043 | 0.0004 | -0.0004 | 0.0261 | -0.0084 | 0.004 | -360.1588 | 17.3802 | -360.3989 | 17.6143 | -360.7804 | 18.1502 | -360.8297 | 17.5978 | -352.6136 | 18.6779 | -352.5736 | 16.8197
12:52 | 5527 | 45.3212 | 202.8499 | 450.3775 | 457.2167 | -16.3525 | -39.3492 | 11.815 | 8.0408 | 2.5694 | 0.7137 | 2.9582 | -0.8571 | 12.06 | 5.1402 | 0.6211 | 0.659 | 0.9623 | 0.7513 | -129.3687 | 1.2431 | 5.8861 | 1.9208 | -2.5539 | -0.7887 | 4.8258 |  | 4.1093 | 0.5173 | 4.0096 | 3.3671 | 3.3365 | 1.0916 | 10.7671 | 14.2812 | 14.8618 | 11.085 | 0.0002 | -0.0032 | 0.0008 | 0.0037 | 0.0012 | -0.0004 | -0.0014 | -0.0104 | -0.0278 | -360.1742 | 17.4007 | -360.4235 | 17.6225 | -360.762 | 18.1173 | -360.7866 | 17.5691 | -352.589 | 18.6963 | -352.6352 | 16.8279
12:52 | 5528 | 45.3479 | 202.8322 | 450.4012 | 457.1964 | -16.368 | -39.3437 | 11.821 | 8.0727 | 2.4614 | 0.8787 | 2.9878 | -0.9287 | 12.0431 | 5.1385 | 0.6216 | 0.6594 | 0.9632 | 0.7506 | -129.353 | 1.2567 | 5.8825 | 1.9733 | -2.4686 | -0.805 | 4.8335 |  | 4.0606 | 0.5643 | 4.0091 | 3.3662 | 3.3346 | 1.0925 | 10.7752 | 14.3009 | 14.8703 | 11.1161 | -0.0002 | -0.0027 | 0.0003 | 0.0036 | 0.0006 | 0 | 0.0147 | -0.0083 | -0.0113 | -360.1558 | 17.3802 | -360.3896 | 17.6328 | -360.7989 | 18.1543 | -360.805 | 17.5794 | -352.5798 | 18.6717 | -352.589 | 16.8423
12:52 | 5529 | 45.333 | 202.9119 | 450.3383 | 457.1451 | -16.4014 | -39.2793 | 11.7548 | 8.0591 | 2.3218 | 0.6686 | 3.0312 | -0.9732 | 12.0478 | 5.1132 | 0.621 | 0.6644 | 0.964 | 0.7493 | -129.1928 | 1.2632 | 5.8601 | 1.9424 | -2.5315 | -0.7425 | 4.8531 |  | 4.0208 | 0.5038 | 4.0102 | 3.3699 | 3.3377 | 1.0931 | 10.7798 | 14.2882 | 14.8747 | 11.0861 | -0.0003 | -0.0027 | 0.0012 | 0.0041 | 0.0015 | -0.0001 | 0.0135 | -0.0229 | -0.013 | -360.1558 | 17.3843 | -360.3989 | 17.6061 | -360.7589 | 18.1235 | -360.802 | 17.5917 | -352.5952 | 18.6737 | -352.6013 | 16.8197
12:52 | 5530 | 45.2696 | 202.8169 | 450.2998 | 457.2678 | -16.3895 | -39.3666 | 11.8086 | 8.1284 | 2.4243 | 0.8115 | 3.0629 | -1.0206 | 12.0631 | 5.1186 | 0.6217 | 0.6617 | 0.9619 | 0.7482 | -129.2735 | 1.2297 | 5.7851 | 1.9351 | -2.473 | -0.7597 | 4.8374 |  | 3.9862 | 0.4614 | 4.01 | 3.3687 | 3.3377 | 1.0928 | 10.7902 | 14.2988 | 14.8639 | 11.1074 | 0 | -0.003 | 0.0003 | 0.0033 | 0.001 | -0.0001 | 0.0001 | -0.0137 | -0.01 | -360.1865 | 17.3843 | -360.4358 | 17.6328 | -360.7866 | 18.1337 | -360.7743 | 17.5794 | -352.5367 | 18.6737 | -352.5921 | 16.8423
12:52 | 5531 | 45.2653 | 202.8165 | 450.3127 | 457.235 | -16.3756 | -39.3614 | 11.8054 | 8.1187 | 2.3673 | 0.7288 | 3.0247 | -0.9475 | 12.0175 | 5.1176 | 0.622 | 0.662 | 0.9653 | 0.7514 | -129.2275 | 1.1649 | 5.7665 | 1.9429 | -2.4838 | -0.7814 | 4.7471 |  | 4.0043 | 0.4401 | 4.0102 | 3.3667 | 3.3357 | 1.0933 | 10.7869 | 14.2833 | 14.8566 | 11.0937 | 0.0002 | -0.0029 | 0.0005 | 0.0042 | 0.0013 | -0.0004 | 0.0171 | -0.0054 | -0.0168 | -360.1096 | 17.3843 | -360.3773 | 17.6102 | -360.7589 | 18.1358 | -360.7866 | 17.5794 | -352.5983 | 18.6655 | -352.5921 | 16.8238
12:52 | 5532 | 45.31 | 202.8274 | 450.3835 | 457.1594 | -16.4916 | -39.3261 | 11.8126 | 8.1654 | 2.4054 | 0.7926 | 3.013 | -0.9216 | 12.1209 | 5.1787 | 0.621 | 0.6653 | 0.9652 | 0.7497 | -129.2251 | 1.3715 | 5.8025 | 1.9467 | -2.4689 | -0.7904 | 4.7593 |  | 3.979 | 0.4293 | 4.0089 | 3.3662 | 3.3351 | 1.0922 | 10.7891 | 14.257 | 14.8673 | 11.1183 | 0 | -0.0025 | 0.001 | 0.0037 | 0.0011 | -0.0001 | 0.0153 | -0.0025 | -0.0114 | -360.1342 | 17.3905 | -360.4204 | 17.6204 | -360.7835 | 18.1337 | -360.802 | 17.5814 | -352.5583 | 18.684 | -352.6106 | 16.8299
12:52 | 5533 | 45.2664 | 202.8898 | 450.2987 | 457.1447 | -16.4558 | -39.2903 | 11.8161 | 8.1535 | 2.38 | 0.7258 | 2.962 | -0.9615 | 12.0976 | 5.0819 | 0.6202 | 0.6623 | 0.9661 | 0.7485 | -129.3009 | 1.3645 | 5.8997 | 1.8156 | -2.4434 | -0.7459 | 4.7813 |  | 4.0568 | 0.5051 | 4.0093 | 3.3684 | 3.3372 | 1.0921 | 10.7984 | 14.2892 | 14.8519 | 11.076 | -0.0003 | -0.0025 | 0.0007 | 0.0034 | 0.0011 | -0.0006 | 0.0155 | -0.0074 | -0.0157 | -360.1527 | 17.3802 | -360.4142 | 17.6184 | -360.7743 | 18.1358 | -360.8174 | 17.5794 | -352.546 | 18.6758 | -352.5952 | 16.8279
12:52 | 5534 | 45.2208 | 202.8456 | 450.3426 | 457.2078 | -16.4826 | -39.304 | 11.7574 | 8.1176 | 2.3168 | 0.7421 | 2.9889 | -1.0262 | 11.9829 | 5.1227 | 0.6206 | 0.6647 | 0.9649 | 0.7514 | -129.2829 | 1.3801 | 5.8596 | 1.7153 | -2.5099 | -0.9228 | 4.7409 |  | 4.0559 | 0.5619 | 4.0104 | 3.3676 | 3.3384 | 1.0928 | 10.7939 | 14.2726 | 14.8616 | 11.1187 | 0 | -0.003 | 0.001 | 0.0039 | 0.0003 | -0.0008 | 0.0014 | 0.0028 | -0.0123 | -360.1373 | 17.3966 | -360.4081 | 17.6122 | -360.7681 | 18.1337 | -360.805 | 17.5835 | -352.5767 | 18.6861 | -352.626 | 16.8279
12:52 | 5535 | 45.3095 | 202.8259 | 450.3859 | 457.3029 | -16.5095 | -39.4098 | 11.7123 | 8.169 | 2.3319 | 0.6726 | 3.0206 | -0.9877 | 12.0773 | 5.174 | 0.623 | 0.665 | 0.9689 | 0.7513 | -129.2674 | 1.3791 | 5.8252 | 1.8668 | -2.5148 | -0.8419 | 4.7941 |  | 3.9742 | 0.4782 | 4.0102 | 3.3673 | 3.3392 | 1.0925 | 10.8029 | 14.2825 | 14.8353 | 11.1031 | 0.0007 | -0.0026 | 0.0011 | 0.0037 | 0.001 | -0.0006 | 0.0155 | -0.0207 | -0.0283 | -360.1435 | 17.3843 | -360.4235 | 17.6245 | -360.7897 | 18.1379 | -360.7897 | 17.565 | -352.5829 | 18.684 | -352.5983 | 16.832
12:52 | 5536 | 45.3138 | 202.9183 | 450.4137 | 457.2288 | -16.4889 | -39.4446 | 11.8595 | 8.1355 | 2.3684 | 0.722 | 3.063 | -0.929 | 12.1222 | 5.2296 | 0.6229 | 0.6622 | 0.9631 | 0.7513 | -129.2564 | 1.4331 | 5.7436 | 2.0491 | -2.5217 | -0.7363 | 4.7876 |  | 4.0604 | 0.524 | 4.0089 | 3.3707 | 3.3337 | 1.0918 | 10.7742 | 14.2646 | 14.8599 | 11.093 | -0.0003 | -0.0031 | 0.0005 | 0.0038 | 0.0007 | -0.0005 | 0.0247 | -0.0133 | 0.0051 | -360.1527 | 17.3905 | -360.4266 | 17.6163 | -360.7497 | 18.1461 | -360.8481 | 17.5917 | -352.6044 | 18.684 | -352.6167 | 16.8135
12:52 | 5537 | 45.319 | 202.9156 | 450.4586 | 457.1859 | -16.4691 | -39.2808 | 11.7415 | 8.0927 | 2.4 | 0.8152 | 3.0156 | -1.0218 | 12.0109 | 5.1605 | 0.6213 | 0.6638 | 0.9634 | 0.7511 | -129.3189 | 1.3299 | 5.7806 | 2.0613 | -2.5633 | -0.7977 | 4.7569 |  | 4.1075 | 0.6617 | 4.0097 | 3.3701 | 3.3331 | 1.0931 | 10.7833 | 14.2337 | 14.8199 | 11.0782 | 0.0004 | -0.0021 | 0.0007 | 0.0042 | 0.0006 | -0.0003 | -0.0002 | -0.0167 | -0.0114 | -360.1988 | 17.409 | -360.4604 | 17.6204 | -360.7989 | 18.1173 | -360.7773 | 17.5876 | -352.5921 | 18.7107 | -352.6229 | 16.8258
12:52 | 5538 | 45.2937 | 202.8298 | 450.3685 | 457.2373 | -16.4157 | -39.3009 | 11.7302 | 8.0971 | 2.4517 | 0.6636 | 2.9603 | -1.0869 | 12.0455 | 5.0606 | 0.6216 | 0.6646 | 0.9647 | 0.7504 | -129.1741 | 1.3422 | 5.8782 | 2.0707 | -2.5143 | -0.771 | 4.8242 |  | 4.0823 | 0.578 | 4.0088 | 3.367 | 3.3331 | 1.0934 | 10.7799 | 14.2822 | 14.8679 | 11.0749 | -0.0001 | -0.0029 | 0.001 | 0.0038 | 0.001 | -0.0006 | 0.0084 | -0.005 | -0.0123 | -360.1896 | 17.3946 | -360.4327 | 17.6266 | -360.8235 | 18.1481 | -360.8327 | 17.5773 | -352.5798 | 18.6922 | -352.6321 | 16.834
12:52 | 5539 | 45.4324 | 202.8835 | 450.3988 | 457.2296 | -16.4296 | -39.333 | 11.796 | 8.1095 | 2.4844 | 0.7644 | 2.9172 | -1.0278 | 11.968 | 5.1665 | 0.6219 | 0.6624 | 0.967 | 0.7513 | -129.3591 | 1.3558 | 5.837 | 1.9797 | -2.405 | -0.7874 | 4.8162 |  | 4.1174 | 0.6318 | 4.0092 | 3.3661 | 3.3375 | 1.0929 | 10.787 | 14.2772 | 14.8603 | 11.1176 | -0.0002 | -0.0033 | 0.0007 | 0.0036 | 0.0002 | -0.0003 | 0.0037 | -0.0107 | -0.0232 | -360.1988 | 17.3925 | -360.4481 | 17.6061 | -360.7958 | 18.1522 | -360.8727 | 17.6081 | -352.5952 | 18.6902 | -352.5829 | 16.8156
12:52 | 5540 | 45.3895 | 202.8133 | 450.4717 | 457.1782 | -16.5798 | -39.404 | 11.7744 | 8.1125 | 2.4405 | 0.8854 | 2.9123 | -0.9415 | 12.055 | 5.1497 | 0.6216 | 0.6623 | 0.9647 | 0.7517 | -129.2667 | 1.4448 | 5.9154 | 1.9163 | -2.405 | -0.7638 | 4.7493 |  | 4.0793 | 0.5509 | 4.0084 | 3.3683 | 3.3346 | 1.094 | 10.7718 | 14.2625 | 14.8593 | 11.0439 | 0 | -0.0027 | 0.0011 | 0.004 | 0.0013 | -0.0006 | 0.0167 | -0.0009 | -0.017 | -360.2235 | 17.4418 | -360.4912 | 17.6225 | -360.8235 | 18.1379 | -360.8081 | 17.5999 | -352.6537 | 18.721 | -352.6875 | 16.8402
12:52 | 5541 | 45.297 | 202.7863 | 450.4274 | 457.1263 | -16.5712 | -39.3732 | 11.6985 | 8.1018 | 2.5615 | 0.8783 | 2.9198 | -0.953 | 12.0272 | 5.1784 | 0.6209 | 0.6605 | 0.9643 | 0.7502 | -129.3085 | 1.4122 | 5.9675 | 1.9462 | -2.4411 | -0.8685 | 4.6916 |  | 4.0973 | 0.5646 | 4.0082 | 3.3666 | 3.3372 | 1.092 | 10.7892 | 14.2683 | 14.8651 | 11.1132 | -0.0005 | -0.0026 | 0.0012 | 0.0037 | 0.0008 | -0.0003 | 0.0039 | -0.0094 | -0.0101 | -360.1496 | 17.409 | -360.4573 | 17.643 | -360.842 | 18.1912 | -360.8266 | 17.5814 | -352.6013 | 18.6943 | -352.6106 | 16.8484
12:52 | 5542 | 45.4831 | 202.8388 | 450.5511 | 457.2366 | -16.5334 | -39.3392 | 11.7825 | 8.0963 | 2.5033 | 0.861 | 2.9158 | -0.9532 | 12.0464 | 5.1957 | 0.621 | 0.6587 | 0.9675 | 0.7508 | -129.2489 | 1.5182 | 5.9267 | 2.0028 | -2.4276 | -0.8008 | 4.78 |  | 4.0018 | 0.6079 | 4.0087 | 3.3722 | 3.3369 | 1.0919 | 10.7857 | 14.2821 | 14.8436 | 11.0984 | -0.0001 | -0.0027 | 0.0006 | 0.0038 | 0.0007 | -0.0008 | 0.02 | -0.009 | -0.024 | -360.1988 | 17.4295 | -360.4542 | 17.6122 | -360.7835 | 18.1728 | -360.8758 | 17.6307 | -352.6383 | 18.7148 | -352.6383 | 16.8197
12:52 | 5543 | 45.3892 | 202.903 | 450.5597 | 457.218 | -16.5389 | -39.3641 | 11.7369 | 8.1116 | 2.4317 | 0.8079 | 2.9507 | -0.9831 | 12.0493 | 5.1283 | 0.6209 | 0.6581 | 0.9647 | 0.7508 | -129.2784 | 1.3616 | 5.828 | 1.9305 | -2.4461 | -0.8244 | 4.7644 |  | 4.0756 | 0.6883 | 4.0086 | 3.3673 | 3.3358 | 1.0911 | 10.7637 | 14.2833 | 14.8334 | 11.1053 | 0.0001 | -0.0033 | 0.0009 | 0.0038 | 0.0005 | -0.0003 | 0.0073 | -0.0141 | -0.0175 | -360.1896 | 17.4254 | -360.5189 | 17.6594 | -360.8635 | 18.1666 | -360.7989 | 17.5855 | -352.6167 | 18.721 | -352.7244 | 16.8648
12:52 | 5544 | 45.4669 | 202.9095 | 450.4607 | 457.1611 | -16.4926 | -39.343 | 11.7535 | 8.1644 | 2.4461 | 0.835 | 2.9551 | -0.9189 | 12.0271 | 5.1904 | 0.622 | 0.6567 | 0.9624 | 0.7508 | -129.2318 | 1.467 | 5.7749 | 1.8891 | -2.4447 | -0.7411 | 4.776 |  | 4.0947 | 0.6822 | 4.0081 | 3.3661 | 3.3324 | 1.0915 | 10.8169 | 14.2904 | 14.888 | 11.1118 | -0.0002 | -0.003 | 0.0002 | 0.0036 | 0.0011 | -0.0006 | 0.0036 | -0.0025 | -0.0011 | -360.1435 | 17.3905 | -360.4142 | 17.6307 | -360.8481 | 18.2179 | -360.8974 | 17.6204 | -352.6475 | 18.6881 | -352.5921 | 16.8423
12:52 | 5545 | 45.3788 | 202.7938 | 450.4465 | 457.2594 | -16.5415 | -39.3712 | 11.746 | 8.0902 | 2.4918 | 0.7923 | 2.9102 | -1.0448 | 12.1157 | 5.1145 | 0.623 | 0.6618 | 0.9641 | 0.7498 | -129.1692 | 1.3913 | 5.8055 | 1.9238 | -2.4764 | -0.8914 | 4.8547 |  | 4.0623 | 0.6819 | 4.0077 | 3.3647 | 3.3331 | 1.0927 | 10.8007 | 14.2802 | 14.8615 | 11.124 | 0.0001 | -0.0027 | 0.0008 | 0.0043 | 0.0006 | -0.0003 | 0.0014 | -0.003 | 0.0039 | -360.2327 | 17.4521 | -360.4696 | 17.6328 | -360.7927 | 18.1625 | -360.8174 | 17.6286 | -352.6875 | 18.7436 | -352.6937 | 16.832
12:52 | 5546 | 45.3908 | 202.8585 | 450.3164 | 457.2542 | -16.4855 | -39.4354 | 11.7638 | 8.0874 | 2.543 | 0.7612 | 2.9162 | -0.9748 | 12.066 | 5.2322 | 0.6221 | 0.6644 | 0.9639 | 0.7522 | -129.2399 | 1.4156 | 5.6953 | 2.0374 | -2.3808 | -0.8558 | 4.8415 |  | 4.0568 | 0.6185 | 4.0085 | 3.3662 | 3.3356 | 1.0928 | 10.788 | 14.296 | 14.8638 | 11.1353 | 0 | -0.0025 | 0.0008 | 0.0039 | 0.0005 | -0.0007 | 0.0044 | -0.0132 | -0.0132 | -360.1742 | 17.4131 | -360.5004 | 17.6779 | -360.9004 | 18.1933 | -360.8389 | 17.5835 | -352.6013 | 18.7128 | -352.6844 | 16.8689
12:52 | 5547 | 45.4256 | 202.8155 | 450.4086 | 457.1697 | -16.402 | -39.2602 | 11.8446 | 8.1402 | 2.5283 | 0.783 | 2.9634 | -0.9144 | 12.0804 | 5.2148 | 0.6213 | 0.6617 | 0.9638 | 0.7515 | -129.3209 | 1.3561 | 5.7805 | 2.0686 | -2.4396 | -0.784 | 4.8269 |  | 4.0715 | 0.5689 | 4.0077 | 3.3674 | 3.3347 | 1.0927 | 10.8018 | 14.2929 | 14.886 | 11.1193 | 0.0003 | -0.0028 | 0.0009 | 0.0041 | 0.001 | -0.0001 | 0.0135 | -0.0046 | -0.0116 | -360.1896 | 17.3946 | -360.4204 | 17.604 | -360.7773 | 18.1974 | -360.8943 | 17.6245 | -352.6444 | 18.7025 | -352.5921 | 16.8176
12:52 | 5548 | 45.4297 | 202.7798 | 450.3936 | 457.2236 | -16.4618 | -39.1455 | 11.7677 | 8.1024 | 2.4872 | 0.813 | 2.9363 | -0.9258 | 12.0997 | 5.2745 | 0.6228 | 0.6575 | 0.9624 | 0.7512 | -129.2038 | 1.4536 | 5.8352 | 2.0528 | -2.5025 | -0.7732 | 4.8645 |  | 3.9861 | 0.587 | 4.0089 | 3.3663 | 3.3356 | 1.0921 | 10.7719 | 14.2681 | 14.8467 | 11.0905 | -0.0005 | -0.0035 | 0.0015 | 0.0042 | 0.001 | -0.0006 | 0.0159 | -0.0074 | 0.0092 | -360.1896 | 17.4439 | -360.5189 | 17.6369 | -360.842 | 18.1563 | -360.7897 | 17.5835 | -352.6937 | 18.7374 | -352.6937 | 16.8628
12:52 | 5549 | 45.4589 | 202.8081 | 450.3222 | 457.2322 | -16.4889 | -39.188 | 11.8358 | 8.0627 | 2.478 | 0.824 | 2.9109 | -0.9263 | 12.0811 | 5.2195 | 0.6226 | 0.6619 | 0.9617 | 0.7521 | -129.1896 | 1.4132 | 5.8169 | 2.0282 | -2.5207 | -0.8349 | 4.8497 |  | 4.0677 | 0.539 | 4.0089 | 3.3689 | 3.338 | 1.0926 | 10.788 | 14.3018 | 14.8522 | 11.0833 | -0.0005 | -0.0026 | 0.0009 | 0.0039 | 0.0007 | -0.0006 | 0.0058 | -0.0003 | 0.0051 | -360.1311 | 17.3884 | -360.4389 | 17.6348 | -360.8327 | 18.2015 | -360.8697 | 17.5712 | -352.589 | 18.684 | -352.6413 | 16.8607
12:52 | 5550 | 45.4402 | 202.8092 | 450.3356 | 457.279 | -16.4512 | -39.2467 | 11.9581 | 8.1524 | 2.4975 | 0.8507 | 2.9528 | -0.9834 | 12.0423 | 5.2697 | 0.6214 | 0.6622 | 0.9608 | 0.7522 | -129.1573 | 1.4011 | 5.8319 | 2.0531 | -2.3459 | -0.7318 | 4.919 |  | 4.0786 | 0.558 | 4.008 | 3.3665 | 3.3321 | 1.0923 | 10.7822 | 14.2788 | 14.8532 | 11.0655 | -0.0002 | -0.0027 | 0.0009 | 0.0039 | 0.0008 | -0.0003 | 0.0274 | -0.0074 | -0.0089 | -360.2388 | 17.4213 | -360.4419 | 17.5958 | -360.7681 | 18.1604 | -360.8389 | 17.6102 | -352.6721 | 18.7128 | -352.626 | 16.8258
12:52 | 5551 | 45.4329 | 202.8401 | 450.3851 | 457.294 | -16.5039 | -39.2108 | 11.8651 | 8.0754 | 2.5366 | 0.8446 | 2.883 | -0.9594 | 12.0988 | 5.2876 | 0.6221 | 0.6622 | 0.9642 | 0.7525 | -129.1872 | 1.4134 | 5.9013 | 2.0184 | -2.4331 | -0.7915 | 4.9316 |  | 4.1426 | 0.5803 | 4.0079 | 3.3704 | 3.3338 | 1.0917 | 10.78 | 14.2704 | 14.8599 | 11.1104 | 0.0001 | -0.003 | 0.0008 | 0.0041 | 0.0009 | -0.0006 | 0.0204 | -0.0028 | -0.0076 | -360.1527 | 17.4131 | -360.4789 | 17.6328 | -360.845 | 18.1522 | -360.7804 | 17.5568 | -352.589 | 18.7148 | -352.6629 | 16.8525
12:52 | 5552 | 45.4564 | 202.8959 | 450.3126 | 457.2113 | -16.5017 | -39.3326 | 11.7832 | 7.9777 | 2.4975 | 0.8904 | 2.9386 | -1.0393 | 12.0406 | 5.2502 | 0.6226 | 0.6613 | 0.9625 | 0.7515 | -129.2594 | 1.3718 | 5.7458 | 2.0443 | -2.4716 | -0.7933 | 4.8434 |  | 4.0054 | 0.509 | 4.0082 | 3.3652 | 3.3341 | 1.092 | 10.7706 | 14.2848 | 14.8427 | 11.0825 | 0.0003 | -0.0027 | 0 | 0.0037 | 0.0012 | 0.0001 | 0.0148 | -0.0248 | -0.0015 | -360.1373 | 17.3658 | -360.3896 | 17.5855 | -360.7897 | 18.1892 | -360.842 | 17.5814 | -352.6044 | 18.6614 | -352.5798 | 16.8197
12:52 | 5553 | 45.4342 | 202.8319 | 450.3916 | 457.1336 | -16.3333 | -39.2298 | 11.8926 | 8.0435 | 2.5085 | 0.8111 | 2.989 | -0.8905 | 11.9714 | 5.1207 | 0.6215 | 0.661 | 0.9615 | 0.753 | -129.2058 | 1.4014 | 5.7635 | 2.0395 | -2.4594 | -0.8348 | 4.8294 |  | 4.0568 | 0.4948 | 4.0082 | 3.3652 | 3.335 | 1.0921 | 10.8076 | 14.264 | 14.857 | 11.0847 | -0.0002 | -0.0025 | 0.0009 | 0.0041 | 0.0012 | -0.0005 | 0 | 0.0011 | -0.017 | -360.1927 | 17.4172 | -360.4389 | 17.5794 | -360.7466 | 18.1337 | -360.7866 | 17.5691 | -352.6321 | 18.723 | -352.6013 | 16.8012
12:52 | 5554 | 45.4127 | 202.8337 | 450.3064 | 457.1588 | -16.383 | -39.2511 | 11.8737 | 8.0935 | 2.5568 | 0.8325 | 2.9955 | -0.8837 | 12.0805 | 5.263 | 0.6227 | 0.6634 | 0.9605 | 0.7519 | -129.2416 | 1.4 | 5.7925 | 1.9365 | -2.5757 | -0.8767 | 4.774 |  | 4.0208 | 0.5452 | 4.0085 | 3.368 | 3.3354 | 1.0925 | 10.8041 | 14.2662 | 14.8819 | 11.1045 | 0.0002 | -0.0026 | 0.0008 | 0.0039 | 0.0006 | 0.0002 | 0.015 | -0.0167 | -0.0137 | -360.0942 | 17.3905 | -360.4573 | 17.6225 | -360.802 | 18.1604 | -360.7958 | 17.5404 | -352.549 | 18.7025 | -352.6444 | 16.8423
12:52 | 5555 | 45.4435 | 202.769 | 450.3043 | 457.2186 | -16.3849 | -39.2348 | 11.8602 | 8.0195 | 2.541 | 0.9188 | 2.9953 | -0.9043 | 12.0717 | 5.2795 | 0.6218 | 0.6629 | 0.9602 | 0.7526 | -129.2058 | 1.3805 | 5.851 | 1.9503 | -2.4947 | -0.9222 | 4.8252 |  | 4.0988 | 0.6057 | 4.0082 | 3.3678 | 3.3372 | 1.0923 | 10.8052 | 14.2849 | 14.867 | 11.0937 | 0.0003 | -0.003 | 0.0003 | 0.0036 | 0.0009 | -0.0007 | 0.0179 | -0.0054 | 0.0053 | -360.1619 | 17.3699 | -360.3712 | 17.5773 | -360.7497 | 18.1748 | -360.8481 | 17.5876 | -352.5983 | 18.6881 | -352.5552 | 16.8012
12:52 | 5556 | 45.4575 | 202.716 | 450.3007 | 457.2022 | -16.4577 | -39.2373 | 11.7978 | 7.9966 | 2.5054 | 0.8143 | 2.9998 | -0.917 | 12.0809 | 5.2754 | 0.6206 | 0.6649 | 0.9646 | 0.7516 | -129.1869 | 1.4056 | 5.8476 | 1.9645 | -2.408 | -0.7762 | 4.8876 |  | 4.0276 | 0.7374 | 4.0085 | 3.3685 | 3.3376 | 1.0944 | 10.7973 | 14.2707 | 14.8389 | 11.1327 | 0.0006 | -0.0027 | 0.0016 | 0.0041 | 0.0004 | -0.0003 | 0.0105 | 0.0024 | -0.0005 | -360.1988 | 17.4233 | -360.4635 | 17.602 | -360.7897 | 18.1399 | -360.802 | 17.5691 | -352.6044 | 18.7292 | -352.6383 | 16.8074
12:52 | 5557 | 45.4769 | 202.7829 | 450.3119 | 457.1801 | -16.4593 | -39.2324 | 11.8156 | 8.0737 | 2.5434 | 0.8188 | 2.9632 | -0.9855 | 12.0311 | 5.1803 | 0.6232 | 0.6636 | 0.9632 | 0.7511 | -129.2317 | 1.3742 | 5.8509 | 1.9487 | -2.4078 | -0.7892 | 4.8729 |  | 4.0184 | 0.6989 | 4.0078 | 3.3641 | 3.334 | 1.0926 | 10.7694 | 14.2836 | 14.8471 | 11.1103 | -0.0004 | -0.0027 | 0.0011 | 0.0039 | 0.0009 | -0.0009 | 0.0246 | -0.0113 | 0.0046 | -360.1342 | 17.3802 | -360.445 | 17.6328 | -360.8481 | 18.181 | -360.8174 | 17.5445 | -352.5429 | 18.6984 | -352.6321 | 16.8299
12:52 | 5558 | 45.5021 | 202.8263 | 450.4462 | 457.2962 | -16.4644 | -39.1942 | 11.8051 | 7.9775 | 2.5073 | 0.9421 | 2.9997 | -0.9661 | 12.0248 | 5.2702 | 0.6227 | 0.6624 | 0.9628 | 0.7518 | -129.2679 | 1.333 | 5.8147 | 1.9751 | -2.3721 | -0.7787 | 4.9173 |  | 4.0867 | 0.6823 | 4.0094 | 3.3679 | 3.3354 | 1.0932 | 10.7567 | 14.265 | 14.811 | 11.0803 | 0.0001 | -0.002 | 0.0008 | 0.0041 | 0.0007 | -0.0007 | 0.0193 | -0.0184 | 0.0016 | -360.2358 | 17.4069 | -360.4358 | 17.6102 | -360.8143 | 18.1728 | -360.8666 | 17.604 | -352.6598 | 18.723 | -352.626 | 16.8135
12:52 | 5559 | 45.4469 | 202.748 | 450.4109 | 457.2183 | -16.3707 | -39.2127 | 11.8308 | 7.9756 | 2.4789 | 0.8595 | 2.9403 | -0.9911 | 11.9843 | 5.163 | 0.6225 | 0.6655 | 0.9652 | 0.7526 | -129.3002 | 1.391 | 5.8405 | 1.8981 | -2.4016 | -0.8129 | 4.9218 |  | 4.1415 | 0.7016 | 4.0073 | 3.3678 | 3.3338 | 1.0929 | 10.8019 | 14.2521 | 14.8376 | 11.1085 | 0.0001 | -0.0031 | 0.0007 | 0.0039 | 0.0009 | -0.0004 | 0.0047 | 0.0036 | -0.0088 | -360.2204 | 17.4192 | -360.4819 | 17.6286 | -360.8297 | 18.1666 | -360.7927 | 17.5753 | -352.6106 | 18.7353 | -352.6383 | 16.834
12:52 | 5560 | 45.5308 | 202.803 | 450.432 | 457.1401 | -16.3823 | -39.329 | 11.8389 | 7.9966 | 2.4512 | 0.8233 | 2.9455 | -1.0217 | 12.0078 | 5.1054 | 0.6215 | 0.6611 | 0.9642 | 0.7534 | -129.3013 | 1.3115 | 5.8515 | 1.9506 | -2.4323 | -0.824 | 4.9495 |  | 4.1438 | 0.7399 | 4.0063 | 3.3684 | 3.3325 | 1.0936 | 10.7592 | 14.2726 | 14.8269 | 11.0898 | 0 | -0.0033 | 0.0004 | 0.0038 | 0.0008 | -0.0008 | 0.0102 | -0.0203 | -0.002 | -360.1835 | 17.4069 | -360.4604 | 17.643 | -360.8297 | 18.1892 | -360.8697 | 17.5753 | -352.6136 | 18.7128 | -352.6383 | 16.8361
12:52 | 5561 | 45.5127 | 202.8403 | 450.4489 | 457.2585 | -16.4928 | -39.2596 | 11.8793 | 7.9673 | 2.5029 | 0.7633 | 2.9748 | -0.916 | 12.0384 | 5.1565 | 0.6207 | 0.6613 | 0.9602 | 0.7545 | -129.235 | 1.3857 | 5.9355 | 1.9726 | -2.373 | -0.7258 | 4.9467 |  | 4.141 | 0.7615 | 4.0085 | 3.3685 | 3.3312 | 1.0932 | 10.7834 | 14.2625 | 14.813 | 11.1017 | -0.0002 | -0.0028 | 0.0011 | 0.0041 | 0.0008 | -0.0007 | 0.0112 | -0.0129 | -0.0067 | -360.2419 | 17.4131 | -360.4419 | 17.6204 | -360.802 | 18.1666 | -360.8481 | 17.5978 | -352.6075 | 18.7251 | -352.629 | 16.8217
12:52 | 5562 | 45.4872 | 202.7932 | 450.4097 | 457.241 | -16.4467 | -39.3851 | 11.7511 | 8.027 | 2.5384 | 0.7594 | 3.0303 | -1.0355 | 12.0412 | 5.1364 | 0.6211 | 0.6653 | 0.958 | 0.752 | -129.1862 | 1.315 | 5.8351 | 2.0222 | -2.3087 | -0.8195 | 4.8757 |  | 4.1211 | 0.7406 | 4.0089 | 3.3676 | 3.335 | 1.0934 | 10.7672 | 14.2693 | 14.8423 | 11.0973 | -0.0003 | -0.0026 | 0.0006 | 0.0038 | 0.0008 | -0.0006 | 0.0113 | -0.0044 | -0.0111 | -360.1742 | 17.409 | -360.4819 | 17.641 | -360.8174 | 18.1769 | -360.8266 | 17.5876 | -352.5983 | 18.7128 | -352.6506 | 16.8381
12:52 | 5563 | 45.5104 | 202.8142 | 450.4556 | 457.2681 | -16.4527 | -39.4185 | 11.7233 | 8.022 | 2.3965 | 0.8996 | 2.9919 | -1.0083 | 12.0158 | 5.1228 | 0.6218 | 0.6651 | 0.9634 | 0.7523 | -129.1512 | 1.4749 | 5.9205 | 2.012 | -2.3594 | -0.7278 | 4.8579 |  | 4.1372 | 0.7109 | 4.0077 | 3.364 | 3.3376 | 1.0951 | 10.7937 | 14.2732 | 14.8485 | 11.1172 | -0.0001 | -0.0029 | 0.0008 | 0.0038 | 0.0009 | 0 | 0.0026 | -0.0133 | -0.0239 | -360.2019 | 17.4131 | -360.4512 | 17.6163 | -360.8081 | 18.1769 | -360.8389 | 17.5794 | -352.629 | 18.723 | -352.629 | 16.8381
12:52 | 5564 | 45.5744 | 202.8097 | 450.5856 | 457.352 | -16.4535 | -39.3969 | 11.7813 | 7.976 | 2.3669 | 0.7975 | 2.99 | -0.9478 | 12.028 | 5.1271 | 0.6216 | 0.6618 | 0.9636 | 0.7512 | -129.2373 | 1.2875 | 5.7872 | 2.054 | -2.3684 | -0.7927 | 4.9352 |  | 4.0743 | 0.613 | 4.0081 | 3.3686 | 3.3339 | 1.0939 | 10.81 | 14.2718 | 14.8403 | 11.1107 | 0.0003 | -0.0031 | 0.001 | 0.0039 | 0.0011 | -0.0006 | -0.0054 | -0.0147 | -0.013 | -360.1558 | 17.4233 | -360.4789 | 17.6328 | -360.805 | 18.1707 | -360.8204 | 17.5835 | -352.6167 | 18.7271 | -352.6321 | 16.8423
12:52 | 5565 | 45.52 | 202.7505 | 450.4883 | 457.2968 | -16.4823 | -39.3211 | 11.8463 | 7.9799 | 2.3789 | 0.8761 | 2.967 | -1.0044 | 12.0348 | 5.112 | 0.6224 | 0.6638 | 0.9623 | 0.754 | -129.2637 | 1.2692 | 5.8832 | 1.9504 | -2.4439 | -0.7592 | 4.8884 |  | 4.0756 | 0.7259 | 4.0063 | 3.3693 | 3.3356 | 1.0927 | 10.7869 | 14.2948 | 14.8277 | 11.0822 | -0.0006 | -0.003 | 0.0012 | 0.0035 | 0.0008 | -0.0002 | 0.0056 | -0.0134 | -0.0156 | -360.1835 | 17.411 | -360.4573 | 17.6328 | -360.8512 | 18.1769 | -360.8389 | 17.5937 | -352.6044 | 18.7066 | -352.626 | 16.8484
12:52 | 5566 | 45.5234 | 202.7917 | 450.4019 | 457.2578 | -16.4673 | -39.2839 | 11.8612 | 8.0042 | 2.3874 | 0.8587 | 3.0099 | -0.9139 | 12.0697 | 5.1054 | 0.621 | 0.6649 | 0.9629 | 0.7519 | -129.2256 | 1.2758 | 5.8303 | 1.9609 | -2.4687 | -0.7514 | 4.8327 |  | 4.1046 | 0.7125 | 4.0074 | 3.3671 | 3.3331 | 1.0941 | 10.8227 | 14.2905 | 14.8659 | 11.0941 | -0.0003 | -0.0026 | 0.0006 | 0.0037 | 0.0011 | -0.0008 | 0.0197 | -0.0143 | -0.006 | -360.1865 | 17.4192 | -360.4481 | 17.6204 | -360.8112 | 18.1769 | -360.8574 | 17.5999 | -352.6383 | 18.7353 | -352.6229 | 16.8258
12:52 | 5567 | 45.5036 | 202.8197 | 450.5597 | 457.2905 | -16.3562 | -39.209 | 11.8813 | 8.0491 | 2.3381 | 0.8438 | 2.9091 | -1.0727 | 11.9444 | 5.0476 | 0.6224 | 0.6631 | 0.9597 | 0.7512 | -129.1977 | 1.389 | 5.9098 | 2.0127 | -2.4003 | -0.7334 | 4.8656 |  | 4.0891 | 0.6963 | 4.0081 | 3.3697 | 3.3348 | 1.0931 | 10.7857 | 14.2936 | 14.8842 | 11.1273 | -0.0001 | -0.003 | 0.0005 | 0.0039 | 0.0005 | -0.0004 | 0.0075 | -0.0066 | -0.0286 | -360.1835 | 17.4274 | -360.5127 | 17.643 | -360.8112 | 18.1707 | -360.8327 | 17.5814 | -352.6475 | 18.7374 | -352.669 | 16.8464
12:53 | 5568 | 45.5389 | 202.8584 | 450.5964 | 457.3288 | -16.3101 | -39.2584 | 11.7738 | 8.031 | 2.3878 | 0.8491 | 2.9866 | -1.0276 | 12.0184 | 5.1345 | 0.6224 | 0.6621 | 0.964 | 0.7519 | -129.1436 | 1.3874 | 5.9235 | 2.0698 | -2.388 | -0.743 | 4.9938 |  | 4.0363 | 0.6106 | 4.0082 | 3.37 | 3.3341 | 1.0927 | 10.7961 | 14.2754 | 14.8676 | 11.1255 | 0 | -0.0031 | 0.0005 | 0.0038 | 0.001 | -0.0011 | 0.002 | -0.0136 | -0.0153 | -360.1619 | 17.4131 | -360.4727 | 17.643 | -360.8235 | 18.2015 | -360.8604 | 17.565 | -352.6075 | 18.721 | -352.6537 | 16.8607
12:53 | 5569 | 45.456 | 202.8386 | 450.5302 | 457.2661 | -16.4088 | -39.2371 | 11.8202 | 7.9343 | 2.3731 | 0.8429 | 2.8804 | -1.0036 | 12.0274 | 5.1558 | 0.6238 | 0.6671 | 0.964 | 0.7527 | -129.1624 | 1.436 | 5.9072 | 2.0268 | -2.3266 | -0.7604 | 4.9835 |  | 4.0816 | 0.6392 | 4.0085 | 3.37 | 3.3365 | 1.0933 | 10.7776 | 14.2681 | 14.8409 | 11.0732 | -0.0003 | -0.003 | 0.0006 | 0.0041 | 0.0003 | -0.0005 | -0.0051 | -0.0044 | -0.0215 | -360.2265 | 17.4151 | -360.4666 | 17.6204 | -360.802 | 18.1871 | -360.8666 | 17.6163 | -352.6967 | 18.7312 | -352.626 | 16.8176
12:53 | 5570 | 45.5244 | 202.8392 | 450.5817 | 457.257 | -16.3758 | -39.3012 | 11.8739 | 7.9952 | 2.4596 | 0.8086 | 2.9868 | -0.9676 | 12.0741 | 5.1836 | 0.6239 | 0.6642 | 0.9657 | 0.7518 | -129.1948 | 1.2981 | 5.8121 | 2.0124 | -2.3493 | -0.7845 | 5.0157 |  | 4.0657 | 0.5833 | 4.0089 | 3.37 | 3.3345 | 1.0945 | 10.7891 | 14.2802 | 14.8673 | 11.1125 | -0.0003 | -0.0025 | 0.0009 | 0.0036 | 0.001 | -0.0004 | 0.007 | 0.0033 | -0.0071 | -360.1927 | 17.448 | -360.5035 | 17.6615 | -360.8481 | 18.1666 | -360.8081 | 17.5753 | -352.6106 | 18.7477 | -352.6937 | 16.8648
12:53 | 5571 | 45.5347 | 202.7413 | 450.5413 | 457.223 | -16.3932 | -39.4322 | 11.8798 | 8.0407 | 2.4919 | 0.8744 | 3.0848 | -1.0049 | 12.0364 | 5.1551 | 0.6238 | 0.6632 | 0.9657 | 0.7518 | -129.2364 | 1.4607 | 5.9048 | 2.0512 | -2.3695 | -0.8046 | 4.9408 |  | 3.9367 | 0.6195 | 4.0081 | 3.3714 | 3.3352 | 1.0931 | 10.759 | 14.2788 | 14.859 | 11.1002 | 0.0001 | -0.0028 | 0.0006 | 0.0034 | 0.0009 | -0.0003 | 0.0112 | -0.0071 | -0.0112 | -360.1527 | 17.4048 | -360.4419 | 17.6389 | -360.8635 | 18.2241 | -360.8912 | 17.5978 | -352.626 | 18.7066 | -352.6044 | 16.8546
12:53 | 5572 | 45.4603 | 202.8305 | 450.4832 | 457.2051 | -16.3989 | -39.4496 | 11.9052 | 8.0213 | 2.4371 | 0.9207 | 3.0755 | -1.0581 | 11.9842 | 5.1953 | 0.6233 | 0.6638 | 0.9627 | 0.7516 | -129.1406 | 1.398 | 5.9093 | 1.8784 | -2.4178 | -0.831 | 4.999 |  | 4.0384 | 0.7908 | 4.0093 | 3.3679 | 3.3349 | 1.093 | 10.7764 | 14.273 | 14.8359 | 11.0887 | 0.0002 | -0.003 | 0.0011 | 0.0037 | 0.0007 | -0.0001 | 0.0112 | -0.0031 | 0.003 | -360.2758 | 17.4439 | -360.4758 | 17.6286 | -360.7989 | 18.1666 | -360.8481 | 17.5978 | -352.6752 | 18.7518 | -352.6875 | 16.8402
12:53 | 5573 | 45.5426 | 202.83 | 450.534 | 457.2261 | -16.3618 | -39.3396 | 11.7411 | 8.0001 | 2.5322 | 0.8604 | 3.117 | -1.0385 | 11.9915 | 5.2263 | 0.6222 | 0.6617 | 0.9617 | 0.7521 | -129.2744 | 1.419 | 5.7925 | 2.03 | -2.3278 | -0.8346 | 4.9293 |  | 4.0889 | 0.7244 | 4.0071 | 3.3713 | 3.3321 | 1.0933 | 10.7717 | 14.2975 | 14.8325 | 11.1125 | 0.0004 | -0.0027 | 0.001 | 0.0036 | 0.0012 | -0.0005 | -0.0002 | -0.0002 | -0.0039 | -360.1711 | 17.4172 | -360.5127 | 17.6697 | -360.8974 | 18.1851 | -360.8327 | 17.5691 | -352.589 | 18.7251 | -352.6813 | 16.8854
12:53 | 5574 | 45.4935 | 202.7695 | 450.4263 | 457.2302 | -16.3681 | -39.3919 | 11.7752 | 8.0649 | 2.4485 | 0.8851 | 3.1473 | -0.9651 | 12.0229 | 5.2142 | 0.6243 | 0.6627 | 0.9633 | 0.7527 | -129.2111 | 1.266 | 5.8002 | 2.0187 | -2.4016 | -0.8115 | 4.8474 |  | 4.1124 | 0.6777 | 4.008 | 3.3696 | 3.3355 | 1.0938 | 10.7892 | 14.2681 | 14.8698 | 11.102 | -0.0004 | -0.0027 | 0.0003 | 0.0036 | 0.0003 | -0.0004 | 0.0097 | -0.0067 | -0.0087 | -360.2296 | 17.4048 | -360.4235 | 17.6081 | -360.7958 | 18.1953 | -360.8881 | 17.5999 | -352.6598 | 18.7107 | -352.626 | 16.8299
12:53 | 5575 | 45.5337 | 202.8306 | 450.4297 | 457.2396 | -16.3719 | -39.2941 | 11.8887 | 8.135 | 2.4562 | 0.9724 | 3.0579 | -1.0223 | 12.0461 | 5.2092 | 0.6233 | 0.6654 | 0.9635 | 0.7515 | -129.1963 | 1.3633 | 5.8075 | 2.0774 | -2.3571 | -0.7226 | 4.9039 |  | 4.1884 | 0.6937 | 4.0077 | 3.3679 | 3.3367 | 1.0928 | 10.7556 | 14.2928 | 14.8386 | 11.0908 | 0.0002 | -0.0027 | 0.001 | 0.0042 | 0.0014 | -0.0005 | -0.0072 | -0.0178 | -0.0226 | -360.2296 | 17.448 | -360.5127 | 17.6307 | -360.7927 | 18.1728 | -360.8297 | 17.5999 | -352.6998 | 18.7518 | -352.6844 | 16.8464
12:53 | 5576 | 45.5127 | 202.8392 | 450.4959 | 457.325 | -16.3905 | -39.5475 | 11.7519 | 8.1712 | 2.5071 | 0.8867 | 3.0327 | -1.0491 | 11.9854 | 5.1252 | 0.622 | 0.6629 | 0.9643 | 0.7533 | -129.2509 | 1.332 | 5.8161 | 2.0843 | -2.3026 | -0.7724 | 5.001 |  | 4.0868 | 0.6303 | 4.01 | 3.3708 | 3.3375 | 1.0933 | 10.7798 | 14.2766 | 14.8863 | 11.1208 | 0.0003 | -0.0031 | 0.0003 | 0.004 | 0.0004 | -0.0006 | -0.0002 | -0.0191 | -0.0074 | -360.1465 | 17.3905 | -360.4727 | 17.6594 | -360.8697 | 18.2036 | -360.8389 | 17.565 | -352.6075 | 18.7107 | -352.6506 | 16.8772
12:53 | 5577 | 45.5051 | 202.9029 | 450.4461 | 457.2566 | -16.4372 | -39.4244 | 11.7813 | 8.0728 | 2.5219 | 0.94 | 3.0782 | -0.9782 | 12.115 | 5.1224 | 0.6232 | 0.6655 | 0.9637 | 0.7526 | -129.2668 | 1.2954 | 5.7457 | 2.0769 | -2.3435 | -0.8843 | 4.9698 |  | 4.1396 | 0.5531 | 4.008 | 3.3703 | 3.3346 | 1.0944 | 10.7973 | 14.2647 | 14.8552 | 11.11 | -0.0001 | -0.0029 | 0.0004 | 0.004 | 0.0013 | -0.0006 | 0.0065 | -0.0049 | -0.0096 | -360.1958 | 17.3987 | -360.4081 | 17.5978 | -360.7835 | 18.1912 | -360.8727 | 17.6122 | -352.6598 | 18.7128 | -352.6106 | 16.8238
12:53 | 5578 | 45.5746 | 202.9005 | 450.4757 | 457.306 | -16.3896 | -39.4594 | 11.7056 | 8.1923 | 2.5251 | 1.0185 | 3.1086 | -0.9525 | 11.992 | 5.1752 | 0.6225 | 0.6645 | 0.9653 | 0.7523 | -129.2592 | 1.2786 | 5.7197 | 2.0162 | -2.3467 | -0.8267 | 4.941 |  | 4.0935 | 0.5114 | 4.0082 | 3.3684 | 3.3339 | 1.0933 | 10.7949 | 14.2858 | 14.843 | 11.1071 | 0.0001 | -0.0022 | 0.0007 | 0.0039 | 0.0006 | -0.0001 | 0.0188 | -0.0056 | -0.0038 | -360.1896 | 17.4315 | -360.4881 | 17.6328 | -360.8081 | 18.1543 | -360.7958 | 17.5753 | -352.629 | 18.7436 | -352.669 | 16.8628
12:53 | 5579 | 45.576 | 203.0023 | 450.5198 | 457.3432 | -16.3878 | -39.504 | 11.6487 | 8.108 | 2.5118 | 0.8704 | 3.1803 | -1.0417 | 11.9658 | 5.0432 | 0.6237 | 0.6679 | 0.9622 | 0.7516 | -129.2244 | 1.3571 | 5.7977 | 1.9553 | -2.3306 | -0.7504 | 4.9189 |  | 4.0809 | 0.5813 | 4.0089 | 3.3679 | 3.3356 | 1.0933 | 10.8134 | 14.287 | 14.8734 | 11.0908 | 0 | -0.0028 | 0.0007 | 0.0036 | 0.001 | -0.0005 | 0.0301 | -0.022 | -0.0046 | -360.1096 | 17.374 | -360.4481 | 17.6348 | -360.8358 | 18.1933 | -360.8789 | 17.5609 | -352.5921 | 18.7107 | -352.629 | 16.8566
12:53 | 5580 | 45.5056 | 203.0492 | 450.4146 | 457.3097 | -16.5137 | -39.7728 | 11.6194 | 8.0703 | 2.57 | 0.9556 | 3.1634 | -1.022 | 12.041 | 5.1179 | 0.622 | 0.6659 | 0.9629 | 0.7523 | -129.2088 | 1.3247 | 5.7172 | 1.9603 | -2.2832 | -0.7016 | 4.9317 |  | 4.075 | 0.6228 | 4.0084 | 3.3691 | 3.333 | 1.0939 | 10.7798 | 14.2939 | 14.8574 | 11.0977 | 0.0006 | -0.0028 | 0.001 | 0.0036 | 0.0004 | -0.0002 | 0.0081 | 0.0056 | -0.0176 | -360.1896 | 17.4069 | -360.4327 | 17.5896 | -360.7897 | 18.1748 | -360.8604 | 17.5958 | -352.6598 | 18.7333 | -352.629 | 16.8238
12:53 | 5581 | 45.4834 | 202.9092 | 450.4327 | 457.2801 | -16.437 | -39.5917 | 11.6673 | 8.0285 | 2.5479 | 0.9342 | 3.1421 | -0.9441 | 12.0287 | 5.0915 | 0.6221 | 0.6657 | 0.9639 | 0.7515 | -129.3654 | 1.348 | 5.7128 | 1.9837 | -2.2543 | -0.6892 | 4.9738 |  | 3.9877 | 0.5575 | 4.0089 | 3.3672 | 3.3331 | 1.094 | 10.8134 | 14.2929 | 14.886 | 11.1136 | 0.0001 | -0.0025 | 0.0013 | 0.0043 | 0.0008 | -0.0006 | 0.0188 | -0.0042 | -0.0173 | -360.1619 | 17.4069 | -360.4881 | 17.643 | -360.8174 | 18.1645 | -360.7804 | 17.5629 | -352.5921 | 18.7333 | -352.6844 | 16.871
12:53 | 5582 | 45.3933 | 202.9288 | 450.3973 | 457.2263 | -16.3959 | -39.3799 | 11.5964 | 7.9985 | 2.4642 | 0.9766 | 3.1574 | -1.0379 | 11.9946 | 5.085 | 0.622 | 0.6638 | 0.9592 | 0.7512 | -129.2625 | 1.4357 | 5.7128 | 2.0196 | -2.2319 | -0.8475 | 4.9265 |  | 4.0702 | 0.5571 | 4.0098 | 3.3703 | 3.338 | 1.0942 | 10.7626 | 14.2704 | 14.8252 | 11.1161 | -0.0002 | -0.0024 | 0.0005 | 0.0037 | 0.0005 | -0.0005 | 0.0076 | -0.022 | -0.0103 | -360.165 | 17.3843 | -360.4204 | 17.604 | -360.8204 | 18.1953 | -360.8635 | 17.5896 | -352.6444 | 18.7066 | -352.5983 | 16.8505
12:53 | 5583 | 45.4551 | 202.9023 | 450.462 | 457.3033 | -16.4258 | -39.2964 | 11.7118 | 7.9962 | 2.4 | 0.9582 | 3.1718 | -1.0328 | 12.0693 | 5.1777 | 0.622 | 0.6658 | 0.9643 | 0.7524 | -129.2426 | 1.4217 | 5.7175 | 2.0925 | -2.2668 | -0.7123 | 5.0211 |  | 4.0751 | 0.5729 | 4.0079 | 3.3652 | 3.3336 | 1.0925 | 10.7683 | 14.2591 | 14.8273 | 11.0692 | -0.0001 | -0.0028 | 0.0011 | 0.0041 | 0.0011 | -0.0005 | 0.0152 | -0.0109 | -0.0103 | -360.2388 | 17.4172 | -360.4696 | 17.6102 | -360.7804 | 18.181 | -360.842 | 17.5896 | -352.6506 | 18.7415 | -352.6506 | 16.8464
12:53 | 5584 | 45.4847 | 202.8904 | 450.496 | 457.2687 | -16.4945 | -39.3007 | 11.7347 | 7.9621 | 2.3851 | 0.8169 | 3.0811 | -1.0982 | 11.9692 | 5.1746 | 0.6242 | 0.6639 | 0.9624 | 0.7513 | -129.2271 | 1.4324 | 5.7073 | 2.0647 | -2.3549 | -0.8461 | 4.9149 |  | 4.0306 | 0.4902 | 4.0082 | 3.3663 | 3.3355 | 1.0919 | 10.7788 | 14.2751 | 14.8423 | 11.0973 | 0.0002 | -0.0032 | 0.0008 | 0.0041 | 0.0011 | -0.0005 | 0.0108 | -0.0157 | -0.0032 | -360.165 | 17.4007 | -360.4666 | 17.6266 | -360.8235 | 18.1892 | -360.8512 | 17.5732 | -352.6013 | 18.7148 | -352.6413 | 16.8731
12:53 | 5585 | 45.539 | 202.9032 | 450.5367 | 457.2533 | -16.4299 | -39.4006 | 11.7029 | 8.0212 | 2.4412 | 0.8474 | 3.1352 | -1.0688 | 11.9579 | 5.1481 | 0.622 | 0.6613 | 0.9644 | 0.7512 | -129.2183 | 1.5112 | 5.7535 | 2.004 | -2.3817 | -0.8593 | 4.8807 |  | 4.0138 | 0.5084 | 4.008 | 3.3685 | 3.3359 | 1.0941 | 10.7822 | 14.2555 | 14.8348 | 11.1064 | 0.0001 | -0.0028 | 0.0002 | 0.0034 | 0.0009 | -0.0005 | 0.0165 | 0.0049 | -0.0185 | -360.1804 | 17.4007 | -360.4296 | 17.6225 | -360.8174 | 18.1851 | -360.8358 | 17.5978 | -352.6629 | 18.7189 | -352.6475 | 16.8484
12:53 | 5586 | 45.5381 | 202.8958 | 450.462 | 457.2921 | -16.4558 | -39.3596 | 11.5847 | 8.0375 | 2.4287 | 0.864 | 3.0114 | -1.038 | 12.0452 | 5.1884 | 0.6215 | 0.661 | 0.9609 | 0.7508 | -129.2158 | 1.3907 | 5.6708 | 2.0649 | -2.4529 | -0.9168 | 4.8722 |  | 4.0598 | 0.5986 | 4.0081 | 3.3705 | 3.3395 | 1.0945 | 10.7776 | 14.2799 | 14.8593 | 11.1248 | -0.0005 | -0.0027 | 0.0005 | 0.0037 | 0.0011 | -0.0006 | 0.013 | -0.0038 | 0.0039 | -360.1373 | 17.4172 | -360.4573 | 17.6122 | -360.8235 | 18.181 | -360.8512 | 17.5835 | -352.6167 | 18.7189 | -352.6383 | 16.8525
12:53 | 5587 | 45.547 | 202.933 | 450.4615 | 457.2837 | -16.515 | -39.4437 | 11.654 | 8.1416 | 2.424 | 0.8191 | 2.9988 | -1.1775 | 11.9392 | 5.1116 | 0.6226 | 0.6653 | 0.9659 | 0.7511 | -129.2063 | 1.4377 | 5.7269 | 2.0314 | -2.3479 | -0.8462 | 4.8965 |  | 4.0822 | 0.482 | 4.0081 | 3.3683 | 3.3374 | 1.0925 | 10.8007 | 14.2799 | 14.8535 | 11.0959 | -0.0004 | -0.003 | 0.0006 | 0.0031 | 0.0003 | -0.0001 | 0.0026 | -0.0102 | -0.0302 | -360.1896 | 17.3987 | -360.445 | 17.6204 | -360.7958 | 18.1666 | -360.8174 | 17.5773 | -352.6167 | 18.7169 | -352.6567 | 16.8587
12:53 | 5588 | 45.4841 | 202.8227 | 450.4214 | 457.2702 | -16.4768 | -39.4052 | 11.7126 | 8.0919 | 2.5308 | 0.7412 | 3.0859 | -1.0545 | 11.9248 | 5.1898 | 0.6218 | 0.6672 | 0.9635 | 0.7522 | -129.3116 | 1.2466 | 5.7265 | 2.0167 | -2.4316 | -0.7693 | 4.9184 |  | 4.1016 | 0.5405 | 4.0084 | 3.3697 | 3.3364 | 1.0921 | 10.7661 | 14.2797 | 14.8351 | 11.1136 | 0.0001 | -0.0033 | 0.0008 | 0.0036 | 0.0007 | -0.0008 | 0.0175 | 0.0004 | 0.0105 | -360.2081 | 17.411 | -360.4789 | 17.6061 | -360.802 | 18.1707 | -360.8389 | 17.5876 | -352.6444 | 18.723 | -352.626 | 16.8423
12:53 | 5589 | 45.5793 | 202.9081 | 450.438 | 457.279 | -16.4925 | -39.4053 | 11.699 | 8.1066 | 2.462 | 0.716 | 3.0735 | -1.0632 | 11.9285 | 5.2403 | 0.6215 | 0.6642 | 0.9654 | 0.753 | -129.21 | 1.4075 | 5.7581 | 2.1016 | -2.4444 | -0.8319 | 4.9332 |  | 4.1606 | 0.5091 | 4.0093 | 3.368 | 3.335 | 1.0938 | 10.7799 | 14.2822 | 14.891 | 11.1096 | -0.0001 | -0.0032 | 0.0007 | 0.0037 | 0.0003 | 0 | 0.0203 | -0.0062 | 0.0098 | -360.1588 | 17.3987 | -360.4542 | 17.6102 | -360.805 | 18.1543 | -360.7897 | 17.5609 | -352.5921 | 18.7189 | -352.6198 | 16.8484
12:53 | 5590 | 45.5897 | 202.9462 | 450.4688 | 457.262 | -16.5809 | -39.5027 | 11.6827 | 8.1123 | 2.4931 | 0.7269 | 3.0379 | -1.0862 | 12.0268 | 5.2389 | 0.6217 | 0.6657 | 0.9646 | 0.7524 | -129.195 | 1.362 | 5.9268 | 2.0576 | -2.3924 | -0.8269 | 4.9904 |  | 4.101 | 0.5313 | 4.0097 | 3.3695 | 3.3343 | 1.0929 | 10.774 | 14.271 | 14.8584 | 11.0915 | -0.0003 | -0.0027 | 0.0009 | 0.0044 | 0.0011 | -0.0005 | 0.0043 | -0.0023 | -0.0208 | -360.1558 | 17.3782 | -360.4019 | 17.6081 | -360.7835 | 18.1748 | -360.8543 | 17.5773 | -352.6013 | 18.6902 | -352.6075 | 16.8505
12:53 | 5591 | 45.5601 | 202.8409 | 450.4309 | 457.2239 | -16.5271 | -39.5213 | 11.6845 | 8.1424 | 2.5094 | 0.7972 | 3.015 | -1.0801 | 12.0186 | 5.1601 | 0.6217 | 0.6651 | 0.9678 | 0.7523 | -129.261 | 1.3826 | 5.727 | 2.0703 | -2.4737 | -0.7762 | 4.9463 |  | 4.2186 | 0.5225 | 4.0071 | 3.3651 | 3.3339 | 1.0928 | 10.8065 | 14.2858 | 14.8836 | 11.1071 | -0.0006 | -0.0029 | 0.001 | 0.0043 | 0.0006 | -0.0007 | 0.0079 | 0.0031 | -0.0016 | -360.205 | 17.4028 | -360.4296 | 17.5855 | -360.7527 | 18.1728 | -360.845 | 17.5814 | -352.6167 | 18.7107 | -352.6198 | 16.8299
12:53 | 5592 | 45.6488 | 202.8396 | 450.396 | 457.2577 | -16.5111 | -39.4181 | 11.7208 | 8.0671 | 2.4529 | 0.7238 | 3.037 | -1.1256 | 11.8904 | 5.0723 | 0.622 | 0.6633 | 0.9631 | 0.7512 | -129.2808 | 1.3383 | 5.7665 | 1.9883 | -2.4965 | -0.9073 | 4.922 |  | 4.2245 | 0.7437 | 4.0087 | 3.3689 | 3.3368 | 1.093 | 10.8295 | 14.2745 | 14.8741 | 11.1237 | 0.0005 | -0.0027 | 0.001 | 0.004 | 0.001 | -0.0003 | 0.0116 | -0.0019 | -0.0067 | -360.1804 | 17.411 | -360.4696 | 17.6163 | -360.7989 | 18.1584 | -360.7681 | 17.5609 | -352.6106 | 18.7169 | -352.6506 | 16.8628
12:53 | 5593 | 45.6383 | 202.8557 | 450.4224 | 457.2478 | -16.5304 | -39.4382 | 11.6462 | 8.0888 | 2.5452 | 0.7041 | 3.0065 | -1.1269 | 11.9709 | 5.1495 | 0.6235 | 0.6634 | 0.9643 | 0.7517 | -129.2082 | 1.4254 | 5.7791 | 2.0364 | -2.5049 | -0.9221 | 4.9645 |  | 4.1479 | 0.5219 | 4.0075 | 3.3661 | 3.3378 | 1.0929 | 10.7776 | 14.2914 | 14.842 | 11.0843 | -0.0001 | -0.0036 | 0.0007 | 0.0037 | 0.0007 | -0.0003 | -0.0021 | -0.0057 | -0.0165 | -360.1096 | 17.374 | -360.3804 | 17.5999 | -360.7927 | 18.2036 | -360.8297 | 17.5629 | -352.5952 | 18.684 | -352.5798 | 16.8464
12:53 | 5594 | 45.6162 | 202.7722 | 450.4437 | 457.248 | -16.5412 | -39.4586 | 11.6863 | 8.0559 | 2.5552 | 0.6691 | 3.0411 | -1.101 | 11.9793 | 5.162 | 0.6225 | 0.6612 | 0.9628 | 0.7522 | -129.1495 | 1.4399 | 5.8717 | 1.8202 | -2.4793 | -0.9462 | 4.8533 |  | 4.0839 | 0.4965 | 4.0093 | 3.3659 | 3.3372 | 1.095 | 10.781 | 14.2834 | 14.8403 | 11.1107 | -0.0002 | -0.0025 | 0.0007 | 0.0038 | 0.0008 | -0.0007 | 0.0224 | -0.0186 | -0.0174 | -360.2019 | 17.4048 | -360.3958 | 17.5814 | -360.7189 | 18.1645 | -360.7989 | 17.5835 | -352.5983 | 18.7107 | -352.6075 | 16.8238
12:53 | 5595 | 45.6926 | 202.9268 | 450.5082 | 457.2361 | -16.4743 | -39.3886 | 11.5978 | 8.0532 | 2.6079 | 0.7276 | 3.0521 | -1.0133 | 12.0566 | 5.2091 | 0.6225 | 0.6637 | 0.9647 | 0.7528 | -129.1564 | 1.475 | 5.835 | 1.8671 | -2.4374 | -0.9068 | 4.8703 |  | 4.1647 | 0.5469 | 4.0084 | 3.3671 | 3.3367 | 1.0933 | 10.7776 | 14.2627 | 14.8372 | 11.0955 | 0 | -0.0024 | 0.0009 | 0.0036 | 0.0012 | 0.0002 | 0.0181 | -0.009 | -0.0153 | -360.1619 | 17.3905 | -360.4542 | 17.6286 | -360.8327 | 18.183 | -360.765 | 17.5383 | -352.5613 | 18.7004 | -352.6444 | 16.8751
12:53 | 5596 | 45.6192 | 202.891 | 450.4978 | 457.2508 | -16.5521 | -39.3459 | 11.6757 | 8.025 | 2.617 | 0.7278 | 3.0911 | -1.1075 | 12.0429 | 5.3083 | 0.6226 | 0.6628 | 0.9655 | 0.7524 | -129.3279 | 1.5007 | 5.7873 | 1.9577 | -2.3578 | -0.7947 | 4.8958 |  | 4.122 | 0.5041 | 4.0082 | 3.3665 | 3.3337 | 1.0933 | 10.7823 | 14.2727 | 14.8627 | 11.0779 | 0.0001 | -0.0031 | 0.0007 | 0.0037 | 0.0008 | -0.0005 | 0.008 | -0.0124 | -0.0073 | -360.165 | 17.3617 | -360.3681 | 17.5712 | -360.7527 | 18.1933 | -360.8727 | 17.5794 | -352.586 | 18.6779 | -352.5675 | 16.8135
12:53 | 5597 | 45.6158 | 202.973 | 450.5279 | 457.1909 | -16.5886 | -39.2852 | 11.6857 | 8.0075 | 2.5132 | 0.7476 | 3.0672 | -0.9848 | 12.0747 | 5.2821 | 0.6219 | 0.6601 | 0.965 | 0.7539 | -129.2662 | 1.5255 | 5.9179 | 1.9468 | -2.4425 | -0.9102 | 4.9477 |  | 4.1138 | 0.5665 | 4.0091 | 3.3675 | 3.3376 | 1.0929 | 10.7845 | 14.2523 | 14.8676 | 11.1082 | 0.0004 | -0.0028 | 0.001 | 0.0041 | 0.0012 | -0.0001 | 0.0127 | -0.0108 | -0.0082 | -360.2019 | 17.4213 | -360.4512 | 17.6081 | -360.7773 | 18.1604 | -360.7681 | 17.5609 | -352.6106 | 18.7271 | -352.6383 | 16.8402
12:53 | 5598 | 45.5349 | 202.9189 | 450.4457 | 457.2193 | -16.528 | -39.1563 | 11.7335 | 8.0173 | 2.5397 | 0.7379 | 2.9788 | -1.0286 | 12.1383 | 5.3443 | 0.6227 | 0.6585 | 0.966 | 0.7519 | -129.226 | 1.4388 | 5.8149 | 1.919 | -2.4527 | -0.9153 | 4.9057 |  | 4.1312 | 0.5996 | 4.0086 | 3.3684 | 3.3358 | 1.0925 | 10.8053 | 14.2788 | 14.859 | 11.0944 | 0 | -0.0026 | 0.0003 | 0.0034 | 0.0006 | -0.0006 | 0.0023 | -0.0174 | -0.0251 | -360.1065 | 17.3617 | -360.4389 | 17.6143 | -360.8235 | 18.2159 | -360.8112 | 17.5301 | -352.5675 | 18.682 | -352.5798 | 16.8566
12:53 | 5599 | 45.5562 | 202.8693 | 450.3724 | 457.2202 | -16.4707 | -39.2088 | 11.7749 | 7.9803 | 2.4511 | 0.8262 | 2.9844 | -0.9676 | 12.0585 | 5.3357 | 0.6212 | 0.6652 | 0.9671 | 0.7531 | -129.1708 | 1.5189 | 5.7698 | 2.0004 | -2.3579 | -0.9033 | 4.9031 |  | 4.0372 | 0.6127 | 4.0088 | 3.3667 | 3.336 | 1.0946 | 10.7891 | 14.2975 | 14.8499 | 11.0836 | -0.0002 | -0.0021 | 0.0003 | 0.0042 | 0.0011 | -0.0005 | 0.0035 | -0.0174 | -0.0075 | -360.1896 | 17.4007 | -360.4327 | 17.5978 | -360.7681 | 18.2015 | -360.885 | 17.5876 | -352.6444 | 18.7189 | -352.5952 | 16.8135
12:53 | 5600 | 45.6333 | 202.827 | 450.3719 | 457.1875 | -16.5202 | -39.3129 | 11.7385 | 8.0112 | 2.4183 | 0.7416 | 3.0215 | -0.93 | 12.0771 | 5.2607 | 0.6218 | 0.6635 | 0.9633 | 0.7533 | -129.2065 | 1.5159 | 5.8937 | 1.9807 | -2.447 | -0.9309 | 4.9256 |  | 4.1241 | 0.5233 | 4.0085 | 3.3645 | 3.3334 | 1.0927 | 10.7995 | 14.2907 | 14.8496 | 11.111 | 0.0004 | -0.0027 | 0.0007 | 0.0038 | 0.0006 | -0.0001 | 0.0054 | -0.0051 | -0.0219 | -360.1558 | 17.4315 | -360.5096 | 17.6348 | -360.8543 | 18.1851 | -360.7743 | 17.5404 | -352.6013 | 18.7353 | -352.6813 | 16.8607
12:53 | 5601 | 45.5583 | 202.8797 | 450.4534 | 457.2365 | -16.5487 | -39.2741 | 11.7596 | 7.99 | 2.4192 | 0.737 | 3.0849 | -0.9789 | 12.0934 | 5.3242 | 0.621 | 0.6625 | 0.9643 | 0.7529 | -129.2895 | 1.4994 | 5.7881 | 2.0484 | -2.3915 | -0.9835 | 4.9406 |  | 4.1112 | 0.5096 | 4.0079 | 3.368 | 3.3355 | 1.0955 | 10.8077 | 14.2751 | 14.8596 | 11.0973 | 0.0003 | -0.0028 | 0.0004 | 0.0034 | 0.0007 | -0.0011 | 0.0074 | -0.0117 | -0.0102 | -360.1588 | 17.3905 | -360.4481 | 17.6286 | -360.845 | 18.2426 | -360.8974 | 17.5671 | -352.6106 | 18.6861 | -352.6136 | 16.8546
12:53 | 5602 | 45.6712 | 202.9375 | 450.446 | 457.3429 | -16.5765 | -39.2804 | 11.8095 | 7.9431 | 2.4576 | 0.8346 | 3.0049 | -0.9816 | 12.0524 | 5.2816 | 0.6213 | 0.6625 | 0.9651 | 0.7541 | -129.272 | 1.472 | 5.7694 | 2.1527 | -2.4078 | -0.9478 | 4.8909 |  | 4.1088 | 0.6045 | 4.0097 | 3.3695 | 3.3355 | 1.0935 | 10.7869 | 14.2833 | 14.8566 | 11.0648 | -0.0005 | -0.0028 | 0.0009 | 0.0038 | 0.0008 | 0 | 0.0132 | -0.003 | -0.0061 | -360.2296 | 17.4274 | -360.4481 | 17.6102 | -360.7927 | 18.2118 | -360.8666 | 17.602 | -352.6937 | 18.7312 | -352.6013 | 16.8361
12:53 | 5603 | 45.7035 | 202.9454 | 450.4359 | 457.3117 | -16.543 | -39.24 | 11.8499 | 7.9392 | 2.5003 | 0.76 | 2.916 | -0.9936 | 12.0791 | 5.1972 | 0.6216 | 0.6631 | 0.9651 | 0.7523 | -129.2505 | 1.5457 | 5.7791 | 2.0435 | -2.3848 | -0.947 | 4.8637 |  | 4.1131 | 0.6119 | 4.0074 | 3.3692 | 3.3368 | 1.0934 | 10.7741 | 14.2535 | 14.8226 | 11.115 | -0.0001 | -0.0024 | 0.0013 | 0.0043 | 0.0008 | -0.0008 | 0.0359 | 0.0081 | 0.0113 | -360.1742 | 17.4315 | -360.5158 | 17.6492 | -360.8666 | 18.2015 | -360.7927 | 17.5629 | -352.626 | 18.7395 | -352.706 | 16.8813
12:53 | 5604 | 45.68 | 202.9181 | 450.4932 | 457.2537 | -16.5199 | -39.3134 | 11.7148 | 7.9974 | 2.5814 | 0.8206 | 3.0373 | -1.0143 | 12.0587 | 5.2265 | 0.6221 | 0.6664 | 0.9658 | 0.7549 | -129.3117 | 1.436 | 5.7057 | 1.9246 | -2.445 | -0.8866 | 4.9621 |  | 4.1009 | 0.6246 | 4.0087 | 3.3665 | 3.3355 | 1.0935 | 10.7579 | 14.2833 | 14.8161 | 11.0822 | 0.0006 | -0.0021 | 0.0007 | 0.0042 | 0.0002 | -0.0006 | 0.0126 | -0.006 | 0.0163 | -360.1373 | 17.3864 | -360.4296 | 17.6266 | -360.8697 | 18.2405 | -360.8697 | 17.5691 | -352.5983 | 18.7045 | -352.629 | 16.8607
12:53 | 5605 | 45.688 | 202.954 | 450.4772 | 457.2378 | -16.4707 | -39.2688 | 11.7491 | 7.9146 | 2.5574 | 0.7973 | 2.9591 | -0.9718 | 12.1045 | 5.2355 | 0.6209 | 0.6639 | 0.9664 | 0.7524 | -129.3108 | 1.4847 | 5.8034 | 1.9799 | -2.3428 | -0.8586 | 5.0288 |  | 4.0737 | 0.5596 | 4.0099 | 3.3683 | 3.3353 | 1.0931 | 10.7684 | 14.2532 | 14.8379 | 11.0638 | 0.0001 | -0.0033 | 0.0011 | 0.0042 | 0.0005 | -0.0009 | 0.0067 | -0.0012 | -0.007 | -360.2142 | 17.411 | -360.405 | 17.602 | -360.7927 | 18.2015 | -360.8512 | 17.5814 | -352.6475 | 18.7333 | -352.6444 | 16.8299
12:53 | 5606 | 45.7223 | 203.0176 | 450.6064 | 457.2655 | -16.502 | -39.2727 | 11.7951 | 7.7973 | 2.501 | 0.658 | 2.9877 | -0.9291 | 12.1031 | 5.3304 | 0.6217 | 0.6645 | 0.9641 | 0.7519 | -129.2543 | 1.5235 | 5.8814 | 2.0605 | -2.3423 | -0.7854 | 5.0124 |  | 4.1243 | 0.6242 | 4.0081 | 3.3667 | 3.335 | 1.0914 | 10.7844 | 14.2756 | 14.8744 | 11.1078 | -0.0001 | -0.0026 | 0.0004 | 0.0038 | 0.0005 | -0.0003 | 0.0157 | -0.005 | 0.0154 | -360.1773 | 17.4048 | -360.4819 | 17.6266 | -360.8266 | 18.1728 | -360.762 | 17.5404 | -352.5921 | 18.7333 | -352.6844 | 16.8689
12:53 | 5607 | 45.7365 | 202.9335 | 450.555 | 457.3228 | -16.4181 | -39.2324 | 11.8855 | 7.895 | 2.4581 | 0.7155 | 2.9778 | -0.9704 | 12.0252 | 5.2365 | 0.6222 | 0.6625 | 0.9636 | 0.7529 | -129.1913 | 1.5792 | 5.8488 | 2.0356 | -2.3698 | -0.8226 | 4.9844 |  | 4.1143 | 0.6515 | 4.0086 | 3.3702 | 3.337 | 1.0923 | 10.7834 | 14.2739 | 14.8467 | 11.102 | 0 | -0.0024 | 0.0001 | 0.0036 | 0.0005 | -0.0007 | 0.013 | 0.0075 | 0.0096 | -360.1311 | 17.3679 | -360.3742 | 17.6081 | -360.8266 | 18.222 | -360.8389 | 17.5547 | -352.6013 | 18.7025 | -352.589 | 16.8505
12:53 | 5608 | 45.6558 | 202.9994 | 450.4954 | 457.3419 | -16.447 | -39.2072 | 11.9051 | 7.9436 | 2.5125 | 0.772 | 2.951 | -1.0545 | 12.0295 | 5.2542 | 0.6221 | 0.6623 | 0.9625 | 0.7523 | -129.2072 | 1.6078 | 5.7781 | 1.988 | -2.4499 | -0.8978 | 4.9057 |  | 4.0382 | 0.5028 | 4.0075 | 3.3693 | 3.3348 | 1.0931 | 10.7845 | 14.281 | 14.8839 | 11.0681 | -0.0002 | -0.0031 | 0.0009 | 0.0036 | 0.0008 | -0.0006 | -0.0092 | 0.0058 | -0.0167 | -360.1681 | 17.3925 | -360.405 | 17.5773 | -360.7281 | 18.1604 | -360.8143 | 17.5794 | -352.6167 | 18.721 | -352.5983 | 16.8115
12:53 | 5609 | 45.6422 | 202.9231 | 450.5525 | 457.3257 | -16.4352 | -39.3074 | 11.8379 | 7.9816 | 2.432 | 0.8743 | 2.9607 | -1.0162 | 11.9708 | 5.2789 | 0.6216 | 0.6633 | 0.9628 | 0.7527 | -129.2418 | 1.575 | 5.8578 | 2.1237 | -2.3595 | -0.914 | 4.9941 |  | 4.0661 | 0.6004 | 4.0071 | 3.3655 | 3.3333 | 1.0924 | 10.817 | 14.2668 | 14.8616 | 11.084 | 0.0002 | -0.0029 | 0.0001 | 0.003 | 0.0005 | -0.0006 | 0.0252 | -0.0097 | -0.0186 | -360.1188 | 17.4007 | -360.4512 | 17.6163 | -360.8112 | 18.1789 | -360.7189 | 17.5342 | -352.5736 | 18.7189 | -352.6413 | 16.8587
12:53 | 5610 | 45.6432 | 203.0095 | 450.5251 | 457.2899 | -16.4892 | -39.2782 | 11.9034 | 8.0287 | 2.4707 | 0.9155 | 2.9569 | -0.9304 | 12.0287 | 5.3365 | 0.6222 | 0.6656 | 0.9632 | 0.7535 | -129.2141 | 1.6434 | 5.8411 | 2.1399 | -2.2913 | -0.8116 | 5.004 |  | 4.0992 | 0.6025 | 4.0071 | 3.3665 | 3.3367 | 1.0934 | 10.817 | 14.2843 | 14.8858 | 11.0952 | -0.0003 | -0.0031 | 0.0009 | 0.0036 | 0.0011 | -0.0007 | 0.0159 | 0.0023 | -0.0024 | -360.1373 | 17.3617 | -360.3989 | 17.5937 | -360.8266 | 18.2138 | -360.8481 | 17.5506 | -352.5552 | 18.6902 | -352.5829 | 16.8423
12:53 | 5611 | 45.5975 | 202.9568 | 450.5801 | 457.3598 | -16.4846 | -39.2886 | 11.919 | 8.006 | 2.4194 | 0.7733 | 2.8695 | -0.96 | 11.9914 | 5.1909 | 0.6211 | 0.6675 | 0.9647 | 0.7531 | -129.22 | 1.6161 | 5.8637 | 2.0853 | -2.3209 | -0.823 | 5.0251 |  | 4.094 | 0.539 | 4.0068 | 3.3662 | 3.3359 | 1.0935 | 10.7821 | 14.2848 | 14.8369 | 11.0998 | -0.0001 | -0.0024 | 0.0014 | 0.0042 | 0.0007 | -0.0003 | 0.0162 | -0.0097 | 0.0059 | -360.2265 | 17.4233 | -360.4512 | 17.5814 | -360.7527 | 18.183 | -360.8266 | 17.5814 | -352.6413 | 18.7374 | -352.629 | 16.8176
12:53 | 5612 | 45.6892 | 202.8768 | 450.6105 | 457.3339 | -16.5312 | -39.2828 | 11.8734 | 8.0006 | 2.4277 | 0.745 | 2.9012 | -0.9906 | 11.9672 | 5.1965 | 0.6232 | 0.6635 | 0.963 | 0.7526 | -129.1511 | 1.5696 | 5.8715 | 2.1224 | -2.3934 | -0.8867 | 5.0086 |  | 4.1292 | 0.6005 | 4.0078 | 3.3647 | 3.338 | 1.0945 | 10.7765 | 14.2901 | 14.8511 | 11.0952 | -0.0006 | -0.0032 | 0.0005 | 0.0039 | 0.0008 | -0.0008 | 0.0108 | 0.0052 | 0.0027 | -360.2019 | 17.4233 | -360.4973 | 17.6533 | -360.9097 | 18.2056 | -360.8204 | 17.5547 | -352.589 | 18.7353 | -352.6721 | 16.871
12:53 | 5613 | 45.6591 | 202.9034 | 450.4794 | 457.262 | -16.5459 | -39.3297 | 11.8324 | 7.9168 | 2.4209 | 0.7215 | 2.8991 | -0.9942 | 11.9193 | 5.2624 | 0.6218 | 0.6623 | 0.9631 | 0.752 | -129.154 | 1.6566 | 5.886 | 2.1012 | -2.4062 | -0.859 | 5.0064 |  | 4.07 | 0.5733 | 4.0069 | 3.3664 | 3.3337 | 1.0937 | 10.8052 | 14.2735 | 14.8738 | 11.128 | 0.0003 | -0.0028 | 0.0013 | 0.0045 | 0.0009 | 0 | 0.0122 | -0.0071 | -0.0056 | -360.1681 | 17.3966 | -360.4389 | 17.6122 | -360.8327 | 18.2364 | -360.8789 | 17.5917 | -352.6352 | 18.7087 | -352.6229 | 16.8546
12:53 | 5614 | 45.6822 | 202.9342 | 450.5793 | 457.3635 | -16.5571 | -39.3629 | 11.7332 | 7.8417 | 2.4399 | 0.6795 | 2.8042 | -0.9366 | 12.0866 | 5.3005 | 0.6232 | 0.6629 | 0.9621 | 0.7524 | -129.1892 | 1.5906 | 5.9417 | 2.1276 | -2.4196 | -0.873 | 5.0217 |  | 4.2056 | 0.6172 | 4.0072 | 3.3682 | 3.3351 | 1.0925 | 10.8041 | 14.2951 | 14.8877 | 11.1392 | -0.0001 | -0.0033 | 0.0008 | 0.0039 | 0.0009 | -0.0007 | 0.0064 | -0.01 | -0.0284 | -360.2481 | 17.4377 | -360.4789 | 17.6122 | -360.802 | 18.1994 | -360.8481 | 17.5835 | -352.6813 | 18.7518 | -352.6937 | 16.8484
12:53 | 5615 | 45.7196 | 202.9581 | 450.512 | 457.3175 | -16.5313 | -39.3766 | 11.5796 | 7.995 | 2.5007 | 0.7709 | 2.9028 | -0.9714 | 12.0974 | 5.3688 | 0.622 | 0.6634 | 0.9638 | 0.7509 | -129.2117 | 1.5936 | 5.8752 | 2.1243 | -2.4878 | -0.8569 | 4.9548 |  | 4.1561 | 0.6292 | 4.0072 | 3.3674 | 3.3415 | 1.093 | 10.8088 | 14.3054 | 14.8621 | 11.1501 | -0.0004 | -0.0025 | 0.0002 | 0.0035 | 0.0002 | -0.0002 | 0.0103 | -0.0084 | -0.008 | -360.165 | 17.4048 | -360.4942 | 17.6492 | -360.8727 | 18.2118 | -360.8512 | 17.5404 | -352.6075 | 18.723 | -352.6937 | 16.8874
12:53 | 5616 | 45.7817 | 202.9312 | 450.5843 | 457.3817 | -16.6396 | -39.4622 | 11.5966 | 7.9321 | 2.5903 | 0.626 | 2.9784 | -1.0043 | 12.0481 | 5.3656 | 0.6226 | 0.6655 | 0.962 | 0.7516 | -129.193 | 1.6624 | 5.925 | 2.2088 | -2.3996 | -0.7797 | 5.0254 |  | 4.0861 | 0.5477 | 4.0081 | 3.3657 | 3.3359 | 1.0934 | 10.7948 | 14.2572 | 14.8857 | 11.1005 | 0 | -0.0028 | 0.0006 | 0.0036 | 0.001 | -0.0006 | 0.0089 | -0.0234 | -0.0182 | -360.1804 | 17.3905 | -360.4173 | 17.5978 | -360.805 | 18.2138 | -360.8666 | 17.5814 | -352.6413 | 18.7045 | -352.6044 | 16.8443
12:53 | 5617 | 45.6697 | 202.8757 | 450.476 | 457.2711 | -16.6376 | -39.3571 | 11.6642 | 7.9611 | 2.6531 | 0.6095 | 3.0055 | -0.9767 | 12.0403 | 5.3338 | 0.6228 | 0.6683 | 0.9625 | 0.7523 | -129.3186 | 1.5506 | 5.7952 | 2.0362 | -2.4257 | -0.8314 | 5.0323 |  | 4.1637 | 0.6165 | 4.0082 | 3.3657 | 3.3356 | 1.0929 | 10.7626 | 14.2588 | 14.8252 | 11.0988 | 0.0001 | -0.0032 | 0.0003 | 0.0034 | 0.001 | 0 | 0.0247 | -0.0063 | 0.0074 | -360.2081 | 17.4233 | -360.4727 | 17.5999 | -360.7897 | 18.1728 | -360.805 | 17.5547 | -352.6444 | 18.7395 | -352.6352 | 16.8484
12:53 | 5618 | 45.6804 | 202.834 | 450.4349 | 457.2645 | -16.5943 | -39.3413 | 11.627 | 7.8774 | 2.5519 | 0.7899 | 2.9682 | -0.9395 | 12.0577 | 5.2498 | 0.623 | 0.6661 | 0.9635 | 0.7513 | -129.2087 | 1.5778 | 5.8561 | 2.0566 | -2.4452 | -0.9781 | 5.0326 |  | 4.0817 | 0.5394 | 4.008 | 3.3666 | 3.3405 | 1.0927 | 10.7845 | 14.2695 | 14.8491 | 11.097 | 0.0001 | -0.0028 | 0.0009 | 0.0038 | 0.0014 | -0.0009 | 0.0218 | -0.0119 | -0.0096 | -360.125 | 17.3864 | -360.4512 | 17.6204 | -360.7958 | 18.1912 | -360.7743 | 17.5321 | -352.5644 | 18.7066 | -352.6352 | 16.8628
12:53 | 5619 | 45.7279 | 202.8642 | 450.53 | 457.2635 | -16.5991 | -39.3128 | 11.716 | 7.9083 | 2.5063 | 0.6165 | 2.947 | -1.0002 | 12.0502 | 5.2218 | 0.6228 | 0.6645 | 0.9637 | 0.7528 | -129.1488 | 1.5411 | 5.8685 | 1.9365 | -2.3718 | -0.8113 | 4.9637 |  | 4.0276 | 0.6278 | 4.0098 | 3.3664 | 3.3354 | 1.0932 | 10.7983 | 14.2606 | 14.8482 | 11.0868 | -0.0005 | -0.0024 | 0.0012 | 0.0042 | 0.0007 | 0 | 0.0195 | 0.0008 | -0.0013 | -360.1773 | 17.372 | -360.3712 | 17.5732 | -360.7712 | 18.1994 | -360.8358 | 17.5732 | -352.629 | 18.6881 | -352.6106 | 16.8258
12:53 | 5620 | 45.6561 | 202.8091 | 450.4786 | 457.341 | -16.6028 | -39.3683 | 11.7184 | 8.0014 | 2.622 | 0.6645 | 2.9229 | -1.0068 | 12.1008 | 5.1799 | 0.6214 | 0.6638 | 0.9643 | 0.7508 | -129.1789 | 1.5911 | 5.9322 | 1.8918 | -2.3994 | -0.8175 | 4.89 |  | 4.1222 | 0.5756 | 4.0088 | 3.3635 | 3.3386 | 1.0946 | 10.803 | 14.2939 | 14.8689 | 11.1208 | 0 | -0.0029 | 0.0005 | 0.0038 | 0.0006 | -0.0003 | -0.0081 | -0.0055 | -0.0159 | -360.1373 | 17.409 | -360.4327 | 17.5917 | -360.7589 | 18.1687 | -360.7558 | 17.5383 | -352.6075 | 18.7271 | -352.6567 | 16.8443
12:53 | 5621 | 45.6413 | 202.8272 | 450.4392 | 457.3525 | -16.5847 | -39.5577 | 11.5727 | 7.9658 | 2.5512 | 0.7052 | 2.948 | -1.1413 | 12.0258 | 5.187 | 0.6222 | 0.6603 | 0.9662 | 0.7527 | -129.1387 | 1.586 | 5.9756 | 1.9255 | -2.3624 | -0.8094 | 4.9404 |  | 4.1338 | 0.6057 | 4.0087 | 3.3683 | 3.3374 | 1.0942 | 10.7879 | 14.2848 | 14.8369 | 11.0767 | 0.0003 | -0.0029 | 0.0006 | 0.0039 | 0.0007 | -0.0006 | 0.0218 | -0.0048 | -0.0235 | -360.0942 | 17.3802 | -360.4173 | 17.5978 | -360.805 | 18.1892 | -360.7773 | 17.5219 | -352.5521 | 18.6922 | -352.626 | 16.8566
12:53 | 5622 | 45.811 | 202.8596 | 450.5154 | 457.2818 | -16.4759 | -39.6114 | 11.5053 | 7.924 | 2.5534 | 0.6656 | 2.9447 | -1.0884 | 12.0745 | 5.2172 | 0.6219 | 0.6626 | 0.9631 | 0.7506 | -129.3094 | 1.5949 | 5.9378 | 1.9512 | -2.3541 | -0.7811 | 4.923 |  | 4.1495 | 0.6355 | 4.008 | 3.3692 | 3.3346 | 1.0941 | 10.8122 | 14.3149 | 14.8846 | 11.1183 | 0.001 | -0.0026 | 0.0011 | 0.0042 | 0.0008 | 0 | 0.0115 | -0.0083 | 0.001 | -360.165 | 17.3864 | -360.4266 | 17.5753 | -360.7497 | 18.1912 | -360.8112 | 17.5671 | -352.5952 | 18.7045 | -352.5983 | 16.8279
12:53 | 5623 | 45.7977 | 202.8991 | 450.5564 | 457.29 | -16.5051 | -39.533 | 11.5545 | 7.9431 | 2.5391 | 0.648 | 2.9357 | -1.0932 | 12.0187 | 5.3083 | 0.6223 | 0.6611 | 0.9634 | 0.7502 | -129.2093 | 1.5956 | 5.9212 | 1.8273 | -2.3498 | -0.8337 | 4.9677 |  | 4.1711 | 0.7584 | 4.0074 | 3.3687 | 3.3359 | 1.0941 | 10.8053 | 14.2904 | 14.8764 | 11.0944 | -0.0001 | -0.0021 | 0.0003 | 0.0035 | 0.0007 | -0.0008 | 0.0064 | -0.0106 | -0.0025 | -360.1681 | 17.4192 | -360.4666 | 17.6081 | -360.805 | 18.1687 | -360.7589 | 17.5404 | -352.629 | 18.723 | -352.6567 | 16.8505
12:53 | 5624 | 45.7674 | 202.9076 | 450.492 | 457.3169 | -16.4757 | -39.4927 | 11.5233 | 7.9802 | 2.4521 | 0.7189 | 2.9466 | -1.0724 | 12.0304 | 5.1889 | 0.6224 | 0.6657 | 0.9668 | 0.7517 | -129.1118 | 1.6745 | 5.9584 | 1.9243 | -2.4054 | -0.9595 | 4.9183 |  | 4.1838 | 0.7682 | 4.0073 | 3.3693 | 3.3393 | 1.0937 | 10.7753 | 14.289 | 14.845 | 11.0822 | -0.0003 | -0.0027 | 0.001 | 0.0039 | 0.0007 | -0.0006 | 0.017 | 0.0047 | -0.0103 | -360.1527 | 17.3823 | -360.4389 | 17.604 | -360.8266 | 18.222 | -360.8235 | 17.5424 | -352.5952 | 18.7004 | -352.5952 | 16.8423
12:53 | 5625 | 45.8073 | 203.0125 | 450.5905 | 457.3757 | -16.5039 | -39.5138 | 11.5094 | 7.9873 | 2.4064 | 0.6427 | 2.9297 | -1.0984 | 11.976 | 5.1272 | 0.623 | 0.6658 | 0.9636 | 0.7513 | -129.1465 | 1.5463 | 5.9856 | 1.9107 | -2.4391 | -0.8611 | 4.9144 |  | 4.1893 | 0.7588 | 4.0076 | 3.3683 | 3.3402 | 1.0936 | 10.7776 | 14.2972 | 14.8246 | 11.0786 | 0.0004 | -0.0026 | 0.0009 | 0.004 | 0.0011 | -0.0003 | 0.0221 | -0.005 | -0.0133 | -360.2019 | 17.4048 | -360.4266 | 17.5876 | -360.7681 | 18.1953 | -360.8574 | 17.5794 | -352.5983 | 18.7148 | -352.6106 | 16.8156
12:53 | 5626 | 45.8451 | 202.9802 | 450.5133 | 457.3979 | -16.4747 | -39.5326 | 11.4432 | 8.0397 | 2.4902 | 0.5502 | 2.9498 | -1.0348 | 12.0784 | 5.2232 | 0.6224 | 0.6649 | 0.966 | 0.7518 | -129.1824 | 1.56 | 5.8619 | 1.9726 | -2.4165 | -0.8883 | 4.9672 |  | 4.1032 | 0.671 | 4.0076 | 3.3673 | 3.3383 | 1.0927 | 10.7824 | 14.2435 | 14.849 | 11.1017 | 0 | -0.0029 | 0.0003 | 0.0036 | 0.0003 | -0.0008 | 0.0219 | -0.0035 | 0.0071 | -360.1681 | 17.4233 | -360.4881 | 17.6266 | -360.8389 | 18.1871 | -360.7989 | 17.5568 | -352.6167 | 18.723 | -352.6352 | 16.871
12:53 | 5627 | 45.9464 | 202.9381 | 450.4954 | 457.3533 | -16.4964 | -39.5601 | 11.5746 | 8.0042 | 2.4649 | 0.607 | 2.9473 | -1.0419 | 12.0414 | 5.1334 | 0.6227 | 0.6651 | 0.9646 | 0.7524 | -129.1006 | 1.6024 | 5.9075 | 1.9636 | -2.4482 | -0.8547 | 5.0098 |  | 4.1239 | 0.6704 | 4.0067 | 3.3688 | 3.3363 | 1.0936 | 10.7811 | 14.289 | 14.8334 | 11.0937 | -0.0004 | -0.0026 | 0.0012 | 0.0046 | 0.0011 | -0.0008 | -0.0004 | -0.0168 | -0.0207 | -360.1896 | 17.3966 | -360.4358 | 17.6204 | -360.8727 | 18.2364 | -360.8604 | 17.5671 | -352.6044 | 18.6963 | -352.6013 | 16.8484
12:54 | 5628 | 45.898 | 202.9807 | 450.4213 | 457.3956 | -16.5962 | -39.5183 | 11.5106 | 7.9873 | 2.4737 | 0.6082 | 2.95 | -1.0549 | 12.1317 | 5.1867 | 0.6233 | 0.6641 | 0.9617 | 0.7514 | -129.0821 | 1.6584 | 5.8607 | 2.0528 | -2.4253 | -0.8443 | 4.9293 |  | 4.2003 | 0.6261 | 4.008 | 3.3679 | 3.3323 | 1.0944 | 10.7913 | 14.3058 | 14.8653 | 11.0854 | 0 | -0.0026 | 0.0005 | 0.0037 | 0.0007 | 0.0001 | 0.0104 | 0.0022 | -0.0342 | -360.2481 | 17.4356 | -360.4666 | 17.5937 | -360.7681 | 18.1974 | -360.8543 | 17.5732 | -352.6413 | 18.7395 | -352.6321 | 16.8443
12:54 | 5629 | 45.7633 | 202.9315 | 450.4559 | 457.3381 | -16.5465 | -39.4604 | 11.5105 | 8.0085 | 2.4484 | 0.5164 | 2.8822 | -1.0165 | 12.1921 | 5.2156 | 0.6239 | 0.6645 | 0.9652 | 0.7516 | -129.0419 | 1.6092 | 5.9097 | 2.0986 | -2.3689 | -0.8106 | 4.9966 |  | 4.1223 | 0.7693 | 4.0096 | 3.3713 | 3.3382 | 1.0937 | 10.7603 | 14.2681 | 14.8467 | 11.0847 | 0.0001 | -0.0033 | 0.0006 | 0.004 | 0.0008 | -0.0008 | -0.0095 | -0.0111 | -0.0014 | -360.1896 | 17.4192 | -360.5158 | 17.6574 | -360.845 | 18.2138 | -360.8143 | 17.5629 | -352.6383 | 18.7374 | -352.6967 | 16.8854
12:54 | 5630 | 45.8406 | 202.8746 | 450.4845 | 457.304 | -16.5434 | -39.4477 | 11.5619 | 8.0202 | 2.4386 | 0.697 | 2.915 | -1.0105 | 12.2005 | 5.2314 | 0.6221 | 0.6636 | 0.9626 | 0.751 | -129.142 | 1.5408 | 5.9133 | 2.0265 | -2.3839 | -0.8818 | 4.9534 |  | 4.2526 | 0.8057 | 4.0079 | 3.3675 | 3.3363 | 1.0936 | 10.8121 | 14.3036 | 14.8694 | 11.0886 | 0.0003 | -0.0029 | 0.0007 | 0.004 | 0.0009 | -0.0002 | 0.0104 | 0.0025 | -0.0002 | -360.1988 | 17.3946 | -360.4296 | 17.6184 | -360.8543 | 18.2405 | -360.8635 | 17.5814 | -352.6537 | 18.7066 | -352.6044 | 16.8607
12:54 | 5631 | 45.8249 | 202.8867 | 450.4375 | 457.2972 | -16.4968 | -39.4744 | 11.5161 | 8.0254 | 2.5002 | 0.7098 | 2.909 | -1.0879 | 12.1586 | 5.167 | 0.6223 | 0.6648 | 0.9649 | 0.7517 | -129.1368 | 1.463 | 5.7938 | 2.0704 | -2.3958 | -0.8994 | 4.9556 |  | 4.1609 | 0.7281 | 4.0088 | 3.368 | 3.3365 | 1.0946 | 10.7858 | 14.2761 | 14.8889 | 11.1219 | -0.0005 | -0.0032 | 0.0002 | 0.003 | 0.0005 | -0.0008 | 0.0091 | -0.0045 | -0.0035 | -360.2358 | 17.45 | -360.4881 | 17.6163 | -360.7958 | 18.1933 | -360.845 | 17.5876 | -352.6721 | 18.7538 | -352.6813 | 16.8546
12:54 | 5632 | 45.8296 | 202.8944 | 450.5004 | 457.269 | -16.5692 | -39.4623 | 11.4562 | 8.0741 | 2.4894 | 0.6342 | 2.8791 | -1.0934 | 12.1049 | 5.1966 | 0.623 | 0.6644 | 0.9644 | 0.7523 | -129.1532 | 1.6061 | 5.8471 | 2.032 | -2.3771 | -1.0603 | 4.9422 |  | 4.0845 | 0.7387 | 4.0082 | 3.369 | 3.3347 | 1.0938 | 10.7915 | 14.2879 | 14.8726 | 11.0869 | -0.0001 | -0.0027 | 0.0005 | 0.0035 | 0.0007 | -0.0005 | 0.0101 | 0.0052 | 0.0062 | -360.1804 | 17.4192 | -360.5004 | 17.643 | -360.8635 | 18.2056 | -360.842 | 17.5506 | -352.6044 | 18.7353 | -352.6875 | 16.8895
12:54 | 5633 | 45.7942 | 202.8293 | 450.3641 | 457.171 | -16.5136 | -39.3698 | 11.454 | 8.0171 | 2.4341 | 0.5775 | 2.9427 | -1.2003 | 12.0558 | 5.066 | 0.6219 | 0.6649 | 0.9598 | 0.7518 | -129.0909 | 1.5524 | 5.8519 | 2.044 | -2.5068 | -0.8578 | 4.9235 |  | 4.1703 | 0.7528 | 4.0074 | 3.3684 | 3.3354 | 1.0936 | 10.7752 | 14.272 | 14.8587 | 11.0583 | 0.0002 | -0.0029 | 0.0006 | 0.0038 | 0.0014 | 0 | 0.0172 | -0.0168 | 0.0051 | -360.1865 | 17.3843 | -360.4266 | 17.5999 | -360.802 | 18.222 | -360.885 | 17.5855 | -352.6352 | 18.7025 | -352.6044 | 16.8607
12:54 | 5634 | 45.8113 | 202.8679 | 450.4155 | 457.3003 | -16.4528 | -39.469 | 11.5365 | 7.9367 | 2.4137 | 0.6181 | 2.9898 | -1.2465 | 12.0445 | 5.0676 | 0.6203 | 0.6658 | 0.9625 | 0.7513 | -129.1439 | 1.5577 | 5.8883 | 2.0257 | -2.4541 | -0.9345 | 4.8982 |  | 4.0817 | 0.6517 | 4.009 | 3.3696 | 3.3363 | 1.0947 | 10.7846 | 14.2693 | 14.8944 | 11.0858 | -0.0003 | -0.0033 | 0.0004 | 0.0039 | 0.0007 | -0.0007 | -0.0049 | -0.0098 | -0.0271 | -360.205 | 17.4336 | -360.4727 | 17.604 | -360.8081 | 18.183 | -360.8358 | 17.5712 | -352.6967 | 18.7497 | -352.6906 | 16.8607
12:54 | 5635 | 45.7895 | 202.7886 | 450.4325 | 457.2421 | -16.5547 | -39.5675 | 11.4964 | 7.9618 | 2.3922 | 0.6913 | 2.8874 | -1.1043 | 12.1613 | 5.0911 | 0.6211 | 0.6663 | 0.9633 | 0.7511 | -129.104 | 1.5413 | 5.9153 | 2.1133 | -2.4575 | -0.8934 | 4.9738 |  | 4.1743 | 0.7447 | 4.0079 | 3.366 | 3.3316 | 1.0929 | 10.7798 | 14.2941 | 14.8526 | 11.0915 | -0.0001 | -0.0026 | 0.001 | 0.0042 | 0.0008 | -0.0002 | 0.0193 | -0.0094 | -0.0151 | -360.1742 | 17.3946 | -360.4696 | 17.6369 | -360.8481 | 18.2056 | -360.8204 | 17.5486 | -352.5736 | 18.7148 | -352.6537 | 16.8833
12:54 | 5636 | 45.7646 | 202.8051 | 450.4336 | 457.146 | -16.5086 | -39.4195 | 11.5243 | 7.9542 | 2.3567 | 0.5393 | 2.9473 | -1.0687 | 12.124 | 5.1663 | 0.6217 | 0.6656 | 0.9619 | 0.7535 | -129.1774 | 1.6005 | 5.8886 | 2.0809 | -2.4182 | -0.9374 | 4.9718 |  | 4.2387 | 0.7788 | 4.0087 | 3.3717 | 3.3377 | 1.0925 | 10.8272 | 14.2779 | 14.9003 | 11.1099 | -0.0004 | -0.003 | 0.0008 | 0.0039 | 0.001 | -0.0006 | 0.0159 | -0.0223 | -0.0056 | -360.1435 | 17.3679 | -360.3896 | 17.5876 | -360.7497 | 18.2077 | -360.8604 | 17.5732 | -352.6198 | 18.6922 | -352.5798 | 16.8423
12:54 | 5637 | 45.8103 | 202.8655 | 450.5006 | 457.1448 | -16.5325 | -39.5103 | 11.5193 | 7.9866 | 2.4344 | 0.5195 | 2.9932 | -1.1193 | 12.1264 | 5.0556 | 0.6214 | 0.6628 | 0.9643 | 0.7529 | -129.209 | 1.5682 | 5.9252 | 2.0528 | -2.457 | -0.8853 | 4.8919 |  | 4.1253 | 0.7339 | 4.0076 | 3.3671 | 3.3356 | 1.0927 | 10.8238 | 14.3149 | 14.8962 | 11.1298 | 0.0003 | -0.0029 | 0.0006 | 0.0038 | 0.0005 | -0.0004 | 0.0027 | -0.0042 | 0.0027 | -360.1958 | 17.4233 | -360.4481 | 17.6122 | -360.7927 | 18.1563 | -360.7712 | 17.5506 | -352.6783 | 18.7436 | -352.6598 | 16.8525
12:54 | 5638 | 45.8375 | 202.9387 | 450.5756 | 457.2578 | -16.5843 | -39.5557 | 11.524 | 7.9596 | 2.4735 | 0.4867 | 3.0163 | -1.0606 | 12.1493 | 5.092 | 0.6207 | 0.668 | 0.9616 | 0.7531 | -129.2434 | 1.6131 | 6.0077 | 1.993 | -2.5704 | -0.9358 | 4.9695 |  | 4.1758 | 0.6731 | 4.0074 | 3.3693 | 3.3357 | 1.0942 | 10.7866 | 14.2724 | 14.8677 | 11.063 | 0.0003 | -0.003 | 0.0009 | 0.004 | 0.0011 | -0.0005 | 0.0146 | -0.0052 | -0.0127 | -360.0665 | 17.3658 | -360.4235 | 17.6143 | -360.8174 | 18.2056 | -360.8143 | 17.5219 | -352.5429 | 18.6922 | -352.6136 | 16.8628
12:54 | 5639 | 45.9001 | 202.9691 | 450.561 | 457.2597 | -16.6303 | -39.6159 | 11.4691 | 7.9979 | 2.4611 | 0.48 | 2.999 | -1.0321 | 12.1892 | 5.1127 | 0.6222 | 0.6668 | 0.965 | 0.7521 | -129.1769 | 1.6317 | 5.877 | 2.0231 | -2.5768 | -0.9096 | 4.9075 |  | 4.1511 | 0.6242 | 4.0083 | 3.3665 | 3.3403 | 1.0932 | 10.8147 | 14.2879 | 14.8726 | 11.11 | -0.0002 | -0.0027 | 0.0002 | 0.0035 | 0.0005 | -0.0002 | 0.0095 | -0.0024 | -0.0034 | -360.1435 | 17.372 | -360.3742 | 17.5732 | -360.722 | 18.1974 | -360.842 | 17.5712 | -352.6444 | 18.7066 | -352.5706 | 16.8258
12:54 | 5640 | 45.953 | 203.0069 | 450.4541 | 457.2248 | -16.5787 | -39.626 | 11.4712 | 7.9385 | 2.4457 | 0.4838 | 2.9638 | -1.0176 | 12.1851 | 5.0358 | 0.6233 | 0.6646 | 0.9666 | 0.7531 | -129.0944 | 1.6066 | 5.9629 | 1.9538 | -2.4871 | -0.8878 | 4.9243 |  | 4.202 | 0.6262 | 4.0079 | 3.3665 | 3.3381 | 1.094 | 10.7857 | 14.2416 | 14.78 | 11.0638 | -0.0001 | -0.0024 | 0.0013 | 0.0037 | 0.001 | -0.0009 | 0.0215 | 0.0038 | -0.0215 | -360.1711 | 17.409 | -360.4573 | 17.6245 | -360.7743 | 18.1563 | -360.7589 | 17.526 | -352.5983 | 18.7333 | -352.6444 | 16.8566
12:54 | 5641 | 45.9207 | 202.9503 | 450.4709 | 457.2091 | -16.4947 | -39.5062 | 11.6427 | 7.9785 | 2.4845 | 0.4825 | 2.977 | -0.9755 | 12.2754 | 5.2284 | 0.6231 | 0.6632 | 0.9697 | 0.7523 | -129.1792 | 1.5841 | 5.9106 | 1.9658 | -2.5037 | -0.8375 | 4.9844 |  | 4.1477 | 0.6054 | 4.0069 | 3.3668 | 3.3341 | 1.0929 | 10.7823 | 14.2554 | 14.8395 | 11.0779 | 0.0003 | -0.0029 | 0.0006 | 0.0036 | 0.0005 | -0.0003 | 0.0112 | -0.0196 | -0.0142 | -360.0604 | 17.3515 | -360.3927 | 17.6163 | -360.802 | 18.2138 | -360.8143 | 17.5383 | -352.5613 | 18.6737 | -352.5829 | 16.8628
12:54 | 5642 | 45.911 | 202.9315 | 450.4333 | 457.2798 | -16.3964 | -39.4721 | 11.6455 | 7.8922 | 2.4885 | 0.4657 | 3.0241 | -1.0307 | 12.2476 | 5.1973 | 0.6224 | 0.6639 | 0.9664 | 0.751 | -129.2297 | 1.5343 | 5.8956 | 2.0049 | -2.5651 | -0.9309 | 4.8428 |  | 4.1718 | 0.6458 | 4.0061 | 3.3676 | 3.3385 | 1.0952 | 10.7926 | 14.2834 | 14.8808 | 11.1165 | 0.0004 | -0.0029 | 0.0009 | 0.0039 | 0.0008 | -0.0008 | 0.0013 | -0.0058 | -0.014 | -360.1958 | 17.3946 | -360.4112 | 17.5794 | -360.7404 | 18.1687 | -360.8112 | 17.5691 | -352.6475 | 18.723 | -352.6013 | 16.8176
12:54 | 5643 | 45.9215 | 202.9295 | 450.3734 | 457.3014 | -16.4045 | -39.3892 | 11.6023 | 7.8838 | 2.5019 | 0.5077 | 2.9203 | -0.9769 | 12.2231 | 5.1859 | 0.6245 | 0.6662 | 0.967 | 0.7525 | -129.2404 | 1.4908 | 5.8802 | 1.8307 | -2.583 | -0.8103 | 4.9207 |  | 4.146 | 0.6167 | 4.0073 | 3.3655 | 3.3362 | 1.0948 | 10.7787 | 14.2696 | 14.827 | 11.085 | -0.0002 | -0.0028 | 0.0009 | 0.0047 | 0.0009 | -0.0001 | 0.0112 | -0.0089 | -0.0103 | -360.1527 | 17.3946 | -360.4389 | 17.6143 | -360.805 | 18.1728 | -360.7681 | 17.5157 | -352.586 | 18.7292 | -352.6136 | 16.8628
12:54 | 5644 | 45.8929 | 202.8772 | 450.5431 | 457.2849 | -16.3932 | -39.3254 | 11.6201 | 8.01 | 2.4958 | 0.4656 | 3.0157 | -1.1143 | 12.1282 | 5.0523 | 0.6214 | 0.6646 | 0.9666 | 0.7522 | -129.2156 | 1.573 | 5.8784 | 1.8012 | -2.5672 | -0.8824 | 4.9008 |  | 4.1604 | 0.6255 | 4.0074 | 3.3652 | 3.3297 | 1.093 | 10.7846 | 14.2982 | 14.8481 | 11.0685 | -0.0003 | -0.0022 | 0.0004 | 0.0039 | 0.0009 | -0.0004 | 0.026 | -0.0038 | -0.014 | -360.1219 | 17.3617 | -360.3681 | 17.5937 | -360.7897 | 18.2302 | -360.8512 | 17.5527 | -352.5583 | 18.6737 | -352.5613 | 16.8464
12:54 | 5645 | 45.8903 | 202.8729 | 450.5296 | 457.3399 | -16.3548 | -39.2242 | 11.6619 | 7.8804 | 2.5323 | 0.5685 | 3.0628 | -0.8789 | 12.2618 | 5.1692 | 0.6221 | 0.6678 | 0.9643 | 0.7513 | -129.1617 | 1.5784 | 5.8567 | 1.8097 | -2.5894 | -0.8453 | 4.9771 |  | 4.2009 | 0.6413 | 4.0075 | 3.3664 | 3.3375 | 1.095 | 10.8066 | 14.297 | 14.8467 | 11.1252 | -0.0001 | -0.0028 | 0.0009 | 0.004 | 0.0006 | -0.0002 | 0.0327 | -0.0115 | 0.0041 | -360.1988 | 17.4007 | -360.4204 | 17.5814 | -360.7404 | 18.1748 | -360.7897 | 17.565 | -352.626 | 18.7292 | -352.6013 | 16.8197
12:54 | 5646 | 45.8839 | 202.8585 | 450.5837 | 457.3499 | -16.3669 | -39.3357 | 11.6697 | 7.9783 | 2.5746 | 0.6713 | 3.083 | -0.9597 | 12.2299 | 5.1708 | 0.6215 | 0.6645 | 0.9628 | 0.7528 | -129.1413 | 1.5858 | 5.912 | 1.9029 | -2.5595 | -0.8879 | 4.9372 |  | 4.1833 | 0.6028 | 4.0072 | 3.3664 | 3.3356 | 1.0928 | 10.7845 | 14.287 | 14.8502 | 11.1313 | 0.0003 | -0.0028 | 0.001 | 0.0036 | 0.0007 | -0.0002 | 0.028 | -0.0145 | -0.0179 | -360.1127 | 17.3843 | -360.4542 | 17.6369 | -360.8358 | 18.2015 | -360.805 | 17.5239 | -352.5613 | 18.7128 | -352.6383 | 16.8751
12:54 | 5647 | 45.843 | 202.8974 | 450.3883 | 457.2235 | -16.3575 | -39.2377 | 11.783 | 7.9748 | 2.6057 | 0.621 | 3.0372 | -0.9473 | 12.295 | 5.2339 | 0.6222 | 0.6668 | 0.9641 | 0.7521 | -129.1835 | 1.5462 | 5.9321 | 1.8576 | -2.547 | -0.9018 | 4.9371 |  | 4.0831 | 0.5633 | 4.0072 | 3.3686 | 3.3344 | 1.0922 | 10.7926 | 14.295 | 14.8287 | 11.0818 | 0.0004 | -0.0025 | 0.0006 | 0.0033 | 0.0009 | -0.0004 | 0.0098 | -0.0085 | -0.0048 | -360.1219 | 17.3597 | -360.365 | 17.5855 | -360.7527 | 18.22 | -360.8789 | 17.5568 | -352.629 | 18.684 | -352.549 | 16.832
12:54 | 5648 | 45.8299 | 202.9171 | 450.5922 | 457.3807 | -16.4056 | -39.2769 | 11.6223 | 8.0725 | 2.5449 | 0.7719 | 3.0724 | -0.8112 | 12.2788 | 5.1557 | 0.6223 | 0.6659 | 0.9651 | 0.7522 | -129.14 | 1.5343 | 5.8973 | 1.818 | -2.5541 | -0.9506 | 4.9269 |  | 4.0918 | 0.4861 | 4.0067 | 3.366 | 3.3362 | 1.0937 | 10.7615 | 14.2575 | 14.8402 | 11.1039 | -0.0005 | -0.0029 | 0.001 | 0.004 | 0.0009 | -0.0003 | 0.0064 | -0.004 | -0.0119 | -360.245 | 17.4315 | -360.4573 | 17.6081 | -360.7835 | 18.1748 | -360.7743 | 17.5547 | -352.6567 | 18.7395 | -352.6783 | 16.8587
12:54 | 5649 | 45.8278 | 202.8877 | 450.6126 | 457.4259 | -16.4661 | -39.2516 | 11.5944 | 7.9823 | 2.4501 | 0.8119 | 2.9963 | -0.8533 | 12.2033 | 5.1491 | 0.6222 | 0.6632 | 0.962 | 0.7508 | -129.1934 | 1.5914 | 5.795 | 1.8268 | -2.6117 | -0.9834 | 4.9336 |  | 4.0574 | 0.4908 | 4.0054 | 3.3664 | 3.3355 | 1.094 | 10.7753 | 14.2544 | 14.8624 | 11.088 | 0 | -0.003 | 0.001 | 0.004 | 0.0009 | -0.0008 | 0.0359 | -0.0026 | -0.0094 | -360.0604 | 17.3658 | -360.4112 | 17.6204 | -360.8174 | 18.2241 | -360.8112 | 17.528 | -352.5306 | 18.6881 | -352.6136 | 16.8669
12:54 | 5650 | 45.9725 | 202.9471 | 450.6743 | 457.5653 | -16.5297 | -39.2416 | 11.6859 | 7.8846 | 2.3722 | 0.8109 | 3.0321 | -0.8361 | 12.3257 | 5.2298 | 0.6231 | 0.6626 | 0.9634 | 0.7519 | -129.2261 | 1.5606 | 5.7935 | 1.8166 | -2.5151 | -0.8113 | 4.8975 |  | 4.1191 | 0.5324 | 4.0065 | 3.3713 | 3.3378 | 1.0943 | 10.7914 | 14.2708 | 14.8805 | 11.1092 | 0.0004 | -0.003 | 0.001 | 0.0039 | 0.0006 | -0.0002 | 0.0131 | -0.0103 | -0.0102 | -360.2204 | 17.4028 | -360.4081 | 17.5855 | -360.7466 | 18.1953 | -360.8543 | 17.5794 | -352.6629 | 18.7148 | -352.6106 | 16.834
12:54 | 5651 | 45.8989 | 202.9018 | 450.6882 | 457.4942 | -16.4973 | -39.2742 | 11.7543 | 7.8857 | 2.3412 | 0.8205 | 3.0891 | -0.9065 | 12.2763 | 5.0338 | 0.6224 | 0.6643 | 0.9625 | 0.7524 | -129.2137 | 1.7533 | 5.9454 | 1.8999 | -2.5839 | -0.8399 | 4.9619 |  | 4.1378 | 0.5391 | 4.0073 | 3.368 | 3.3358 | 1.0939 | 10.8053 | 14.2788 | 14.8938 | 11.1118 | -0.0002 | -0.003 | 0.0006 | 0.0042 | 0.0014 | -0.0005 | 0.0132 | -0.0043 | -0.015 | -360.165 | 17.409 | -360.4604 | 17.6266 | -360.845 | 18.1851 | -360.7743 | 17.526 | -352.6136 | 18.7189 | -352.6567 | 16.8772
12:54 | 5652 | 45.8934 | 202.917 | 450.5558 | 457.4403 | -16.5521 | -39.2281 | 11.6942 | 7.9704 | 2.3642 | 0.7285 | 3.0908 | -0.9097 | 12.2567 | 5.0471 | 0.6231 | 0.6646 | 0.9607 | 0.7517 | -129.2637 | 1.7065 | 5.8761 | 1.9104 | -2.5186 | -0.7952 | 4.9021 |  | 4.0918 | 0.5972 | 4.0082 | 3.3706 | 3.3374 | 1.0923 | 10.7856 | 14.2882 | 14.8226 | 11.0688 | -0.0003 | -0.0026 | 0.0009 | 0.0039 | 0.0007 | -0.0001 | 0.0009 | -0.0071 | 0.0044 | -360.165 | 17.3658 | -360.3804 | 17.602 | -360.8204 | 18.2385 | -360.842 | 17.5609 | -352.5921 | 18.682 | -352.586 | 16.8484
12:54 | 5653 | 45.9141 | 202.9472 | 450.5987 | 457.4712 | -16.4337 | -39.1087 | 11.8285 | 7.9709 | 2.444 | 0.682 | 3.1292 | -0.9363 | 12.227 | 5.0758 | 0.6216 | 0.6616 | 0.9666 | 0.7519 | -129.2843 | 1.6529 | 5.8114 | 1.7844 | -2.5376 | -0.8954 | 4.8285 |  | 4.1187 | 0.6419 | 4.0079 | 3.3687 | 3.3338 | 1.0935 | 10.8065 | 14.2799 | 14.8825 | 11.0843 | -0.0001 | -0.0029 | 0.0009 | 0.0039 | 0.0009 | -0.0006 | 0.0083 | -0.0034 | -0.0157 | -360.1804 | 17.4172 | -360.4573 | 17.5896 | -360.7497 | 18.1953 | -360.8143 | 17.5588 | -352.6998 | 18.7395 | -352.6383 | 16.8484
12:54 | 5654 | 45.8935 | 202.952 | 450.5851 | 457.4244 | -16.4108 | -39.1068 | 11.8294 | 8.0335 | 2.4856 | 0.6685 | 3.1659 | -0.9892 | 12.2409 | 5.0562 | 0.6224 | 0.6635 | 0.9635 | 0.752 | -129.1889 | 1.6205 | 5.7876 | 1.7266 | -2.5272 | -0.8647 | 4.8709 |  | 4.1324 | 0.6039 | 4.0069 | 3.3687 | 3.3358 | 1.0925 | 10.8192 | 14.2985 | 14.8676 | 11.0966 | 0.0002 | -0.0031 | 0.0006 | 0.0039 | 0.0004 | -0.0002 | 0.0143 | -0.0172 | -0.0079 | -360.1311 | 17.3925 | -360.4481 | 17.6307 | -360.8481 | 18.222 | -360.802 | 17.528 | -352.5613 | 18.7066 | -352.6506 | 16.8813
12:54 | 5655 | 45.9888 | 202.9054 | 450.6144 | 457.4684 | -16.4361 | -39.2994 | 11.6706 | 8.0399 | 2.4843 | 0.6672 | 3.1145 | -1.0569 | 12.2354 | 5.0793 | 0.6223 | 0.6637 | 0.9685 | 0.7521 | -129.2239 | 1.615 | 5.7893 | 1.8327 | -2.6206 | -0.9224 | 4.8844 |  | 4.1323 | 0.6966 | 4.0068 | 3.3698 | 3.3344 | 1.0936 | 10.7857 | 14.2707 | 14.8273 | 11.0981 | 0 | -0.0031 | 0.0005 | 0.0035 | 0.001 | -0.0002 | 0.0058 | -0.0107 | -0.0095 | -360.205 | 17.3864 | -360.3989 | 17.5937 | -360.7589 | 18.22 | -360.885 | 17.5753 | -352.6537 | 18.7148 | -352.6013 | 16.8381
12:54 | 5656 | 46.0083 | 202.9511 | 450.7054 | 457.4823 | -16.4665 | -39.2545 | 11.8332 | 8.1308 | 2.5402 | 0.7361 | 3.1453 | -0.9723 | 12.237 | 5.1064 | 0.622 | 0.6628 | 0.9678 | 0.7528 | -129.2835 | 1.5387 | 5.7065 | 2.0127 | -2.6394 | -0.879 | 4.905 |  | 4.0914 | 0.6322 | 4.0074 | 3.3654 | 3.3337 | 1.0932 | 10.7764 | 14.3019 | 14.8359 | 11.0829 | -0.0005 | -0.0025 | 0.001 | 0.004 | 0.0006 | -0.0002 | 0.0254 | -0.0124 | 0.0026 | -360.1588 | 17.4213 | -360.4727 | 17.6266 | -360.7743 | 18.1871 | -360.7681 | 17.5424 | -352.626 | 18.7353 | -352.6598 | 16.8669
12:54 | 5657 | 45.9157 | 202.9127 | 450.6086 | 457.3444 | -16.424 | -39.2918 | 11.7994 | 8.0886 | 2.597 | 0.6138 | 3.0918 | -0.9834 | 12.1796 | 5.1459 | 0.6235 | 0.6607 | 0.9617 | 0.7528 | -129.2465 | 1.5546 | 5.8179 | 2.0633 | -2.5182 | -0.7902 | 4.8503 |  | 4.123 | 0.7257 | 4.0066 | 3.3689 | 3.3358 | 1.0924 | 10.7648 | 14.273 | 14.8648 | 11.1233 | -0.0004 | -0.0031 | 0.0008 | 0.0042 | 0.0008 | -0.0006 | 0.0071 | -0.0079 | -0.0052 | -360.1311 | 17.3699 | -360.405 | 17.6122 | -360.8081 | 18.2467 | -360.8174 | 17.5445 | -352.586 | 18.684 | -352.5952 | 16.8669
12:54 | 5658 | 46.0141 | 202.9455 | 450.6902 | 457.4673 | -16.4277 | -39.3249 | 11.7506 | 8.0621 | 2.4939 | 0.6459 | 3.0389 | -0.9663 | 12.2219 | 5.1348 | 0.6225 | 0.6615 | 0.9631 | 0.7532 | -129.2023 | 1.6088 | 5.8378 | 1.9723 | -2.5978 | -0.7718 | 4.9216 |  | 4.0947 | 0.6836 | 4.0081 | 3.3674 | 3.335 | 1.0922 | 10.8018 | 14.3103 | 14.8513 | 11.102 | 0.0004 | -0.0027 | 0.0007 | 0.004 | 0.0009 | -0.0004 | -0.0006 | -0.009 | -0.014 | -360.1527 | 17.4028 | -360.405 | 17.5732 | -360.7373 | 18.1933 | -360.8327 | 17.5671 | -352.6229 | 18.7128 | -352.5952 | 16.8217
12:54 | 5659 | 45.9527 | 202.8191 | 450.5208 | 457.3291 | -16.3739 | -39.2261 | 11.7552 | 8.117 | 2.5341 | 0.5832 | 3.0446 | -0.992 | 12.2636 | 5.0315 | 0.6239 | 0.6617 | 0.9653 | 0.7524 | -129.2065 | 1.5752 | 5.7989 | 1.9266 | -2.6245 | -0.7728 | 4.8365 |  | 4.0492 | 0.5942 | 4.0067 | 3.3662 | 3.3308 | 1.0931 | 10.774 | 14.271 | 14.8526 | 11.0915 | 0.0001 | -0.0028 | 0.0005 | 0.0043 | 0.001 | -0.0004 | 0.0068 | -0.0061 | -0.006 | -360.1281 | 17.3946 | -360.4635 | 17.6286 | -360.8512 | 18.1851 | -360.7558 | 17.5219 | -352.5583 | 18.721 | -352.6383 | 16.8587
12:54 | 5660 | 46.0692 | 202.883 | 450.5574 | 457.4657 | -16.3876 | -39.2069 | 11.7389 | 8.04 | 2.4648 | 0.6016 | 3.1457 | -0.9908 | 12.1907 | 5.0986 | 0.6217 | 0.6624 | 0.9687 | 0.7518 | -129.1885 | 1.5671 | 5.8231 | 1.9761 | -2.6347 | -0.9266 | 4.8424 |  | 4.1261 | 0.6113 | 4.0072 | 3.3673 | 3.3347 | 1.0945 | 10.7822 | 14.2555 | 14.8869 | 11.1064 | -0.0002 | -0.0026 | 0.0006 | 0.0037 | 0.0012 | -0.0004 | 0.0157 | -0.0113 | -0.012 | -360.1281 | 17.3515 | -360.3742 | 17.5917 | -360.7866 | 18.2282 | -360.842 | 17.5424 | -352.5736 | 18.684 | -352.5675 | 16.8258
12:54 | 5661 | 46.1319 | 202.9137 | 450.6454 | 457.5552 | -16.3778 | -39.2503 | 11.7974 | 8.1173 | 2.4901 | 0.6842 | 3.1921 | -0.9993 | 12.2368 | 5.1256 | 0.6213 | 0.6635 | 0.965 | 0.753 | -129.2306 | 1.4744 | 5.7195 | 1.9681 | -2.5196 | -0.9235 | 4.8306 |  | 4.0721 | 0.6191 | 4.008 | 3.3674 | 3.3351 | 1.0937 | 10.8052 | 14.2966 | 14.8564 | 11.1164 | -0.0002 | -0.0024 | 0.0008 | 0.0041 | 0.0007 | 0.0003 | 0.0119 | -0.0043 | -0.0049 | -360.1804 | 17.4151 | -360.4296 | 17.5958 | -360.7373 | 18.1687 | -360.7712 | 17.5588 | -352.5921 | 18.7395 | -352.626 | 16.8217
12:54 | 5662 | 46.0982 | 203.0129 | 450.7059 | 457.4933 | -16.4072 | -39.2085 | 11.8191 | 8.0974 | 2.5975 | 0.8622 | 3.1512 | -0.918 | 12.2497 | 5.1896 | 0.622 | 0.6628 | 0.964 | 0.7532 | -129.1884 | 1.4914 | 5.6758 | 1.9175 | -2.4551 | -0.8829 | 4.8965 |  | 4.0676 | 0.599 | 4.0073 | 3.3678 | 3.3376 | 1.0943 | 10.7972 | 14.3113 | 14.8863 | 11.1266 | 0.0002 | -0.003 | 0.0012 | 0.0044 | 0.0011 | -0.0004 | 0.0074 | -0.0084 | -0.0088 | -360.0973 | 17.372 | -360.4327 | 17.6307 | -360.8174 | 18.2159 | -360.7773 | 17.5178 | -352.5306 | 18.7087 | -352.6044 | 16.8566
12:54 | 5663 | 46.0183 | 203.0112 | 450.6264 | 457.4355 | -16.362 | -39.2282 | 11.9006 | 7.9889 | 2.5639 | 0.7766 | 3.1396 | -0.944 | 12.244 | 5.1899 | 0.6229 | 0.6614 | 0.9624 | 0.7522 | -129.2138 | 1.6525 | 5.7052 | 1.9284 | -2.5463 | -0.8559 | 4.9109 |  | 4.0529 | 0.6056 | 4.0085 | 3.3667 | 3.3383 | 1.0942 | 10.781 | 14.2893 | 14.8645 | 11.1219 | 0.0001 | -0.0029 | 0.001 | 0.0039 | 0.0008 | -0.0002 | -0.0054 | -0.0123 | -0.0127 | -360.1311 | 17.3802 | -360.3865 | 17.5876 | -360.7466 | 18.2138 | -360.8481 | 17.5712 | -352.6229 | 18.7004 | -352.5367 | 16.8135
12:54 | 5664 | 48.4024 | 202.951 | 450.7108 | 445.8696 | -16.3096 | -39.2723 | 11.7956 | 8.0183 | 2.6213 | 0.7304 | 3.1604 | -0.9761 | 12.2313 | 5.1617 | 0.6225 | 0.6619 | 0.9647 | 0.752 | -129.2219 | 1.6896 | 5.716 | 2.0248 | -2.5956 | -0.7298 | 4.9514 |  | 4.0828 | 0.6641 | 4.0062 | 3.3648 | 3.3347 | 1.0919 | 10.7636 | 14.2893 | 14.8761 | 11.0988 | -0.0001 | -0.0025 | 0.0009 | 0.0042 | 0.0011 | -0.0006 | 0.0014 | -0.0107 | -0.0039 | -360.1865 | 17.4172 | -360.4481 | 17.6143 | -360.802 | 18.181 | -360.7435 | 17.5342 | -352.6013 | 18.7333 | -352.629 | 16.8381
12:54 | 5665 | 51.7364 | 202.7342 | 448.3988 | 438.2305 | -16.824 | -39.2382 | 11.9339 | 8.0413 | 2.681 | 0.7905 | 3.1797 | -1.0049 | 12.1678 | 5.1909 | 0.6231 | 0.6638 | 0.9657 | 0.7518 | -129.1449 | 1.6517 | 5.777 | 2.0298 | -2.5953 | -0.8325 | 4.9326 |  | 4.1061 | 0.6389 | 4.0069 | 3.3683 | 3.3326 | 1.0924 | 10.7524 | 14.2364 | 14.8176 | 11.0721 | -0.0002 | -0.0028 | 0.0007 | 0.004 | 0.0007 | -0.0002 | 0.0171 | -0.0021 | -0.0128 | -360.0758 | 17.3515 | -360.3804 | 17.6184 | -360.7989 | 18.2385 | -360.842 | 17.5198 | -352.5275 | 18.6861 | -352.549 | 16.8381
12:54 | 5666 | 51.1731 | 202.6867 | 448.667 | 442.8049 | -17.0136 | -39.2249 | 11.8607 | 8.0949 | 2.7497 | 0.7862 | 3.2231 | -1.1025 | 12.2376 | 5.1715 | 0.6233 | 0.662 | 0.9671 | 0.7515 | -129.2981 | 1.5369 | 5.7437 | 2.0392 | -2.6153 | -0.8062 | 4.899 |  | 4.0756 | 0.6147 | 4.0074 | 3.372 | 3.3381 | 1.0931 | 10.7753 | 14.2486 | 14.7929 | 11.088 | 0.0005 | -0.0029 | 0.0003 | 0.0034 | 0.0012 | -0.0004 | -0.0024 | -0.0233 | -0.0264 | -360.1958 | 17.3966 | -360.4235 | 17.5773 | -360.7373 | 18.1974 | -360.805 | 17.5629 | -352.6444 | 18.7271 | -352.589 | 16.8115
12:54 | 5667 | 50.9065 | 202.7448 | 448.6921 | 442.8657 | -16.8809 | -39.1003 | 11.8345 | 8.0469 | 2.7246 | 0.8015 | 3.1598 | -1.0564 | 12.2044 | 5.0946 | 0.6242 | 0.6629 | 0.9632 | 0.7531 | -129.2962 | 1.5051 | 5.8098 | 1.9852 | -2.6628 | -0.8992 | 4.8336 |  | 4.0409 | 0.6605 | 4.0073 | 3.3688 | 3.3351 | 1.0941 | 10.7743 | 14.2644 | 14.8242 | 11.0876 | 0.0001 | -0.0032 | 0.0006 | 0.0041 | 0.0003 | -0.0005 | 0.0116 | 0.0041 | -0.0141 | -360.1219 | 17.3966 | -360.4573 | 17.6225 | -360.8235 | 18.1769 | -360.7589 | 17.5034 | -352.5736 | 18.7189 | -352.6352 | 16.8464
12:54 | 5668 | 50.6685 | 202.6616 | 448.6403 | 442.9866 | -16.979 | -39.21 | 11.8091 | 8.0121 | 2.733 | 0.7156 | 3.0632 | -1.1208 | 12.1773 | 5.019 | 0.6217 | 0.6624 | 0.9616 | 0.7533 | -129.2196 | 1.5442 | 5.8081 | 1.9599 | -2.6408 | -0.808 | 4.9104 |  | 4.1133 | 0.7356 | 4.0069 | 3.3687 | 3.3319 | 1.0951 | 10.7798 | 14.265 | 14.8631 | 11.0919 | -0.0001 | -0.0024 | 0.001 | 0.0038 | 0.001 | -0.0006 | 0.0083 | -0.0092 | -0.0139 | -360.1219 | 17.3617 | -360.3835 | 17.6102 | -360.7835 | 18.2344 | -360.8543 | 17.5363 | -352.549 | 18.6861 | -352.5613 | 16.834
12:54 | 5669 | 50.5432 | 202.7392 | 448.7441 | 443.25 | -16.9118 | -39.2224 | 11.7776 | 8.0543 | 2.7045 | 0.766 | 3.1254 | -1.0229 | 12.2774 | 5.0449 | 0.6231 | 0.6598 | 0.9642 | 0.7538 | -129.205 | 1.661 | 5.8454 | 1.9504 | -2.5668 | -0.7417 | 4.9636 |  | 4.1405 | 0.7508 | 4.0049 | 3.3671 | 3.3325 | 1.0941 | 10.8006 | 14.2977 | 14.8799 | 11.1237 | 0.0001 | -0.0026 | 0.001 | 0.004 | 0.0009 | -0.0004 | 0.009 | -0.0141 | -0.0253 | -360.1373 | 17.409 | -360.4112 | 17.5835 | -360.7373 | 18.1851 | -360.8112 | 17.5527 | -352.6506 | 18.7251 | -352.6013 | 16.8074
12:54 | 5670 | 50.4251 | 202.8126 | 448.8122 | 443.662 | -16.8875 | -39.1389 | 11.8333 | 8.0831 | 2.744 | 0.8822 | 3.1962 | -1.0612 | 12.2181 | 5.0993 | 0.6238 | 0.6639 | 0.9671 | 0.7542 | -129.1728 | 1.5755 | 5.8817 | 1.9439 | -2.5336 | -0.7543 | 4.9054 |  | 4.0969 | 0.696 | 4.0049 | 3.3667 | 3.3356 | 1.0946 | 10.8147 | 14.2879 | 14.8668 | 11.0984 | 0.0002 | -0.003 | 0.001 | 0.0037 | 0.0004 | -0.0007 | 0.0014 | -0.0046 | -0.0051 | -360.1188 | 17.4007 | -360.4666 | 17.6307 | -360.8112 | 18.1933 | -360.762 | 17.5137 | -352.5367 | 18.721 | -352.6506 | 16.8607
12:54 | 5671 | 50.1201 | 202.6616 | 448.6741 | 443.8062 | -16.9308 | -39.1252 | 11.8618 | 8.1191 | 2.765 | 0.7955 | 3.1462 | -1.109 | 12.2464 | 5.1138 | 0.6236 | 0.6634 | 0.9621 | 0.7561 | -129.32 | 1.5902 | 5.8772 | 2.032 | -2.5346 | -0.8286 | 4.9292 |  | 4.068 | 0.649 | 4.0066 | 3.3678 | 3.3353 | 1.0936 | 10.7902 | 14.2931 | 14.8581 | 11.0785 | 0.0002 | -0.0028 | 0.0009 | 0.0041 | 0.0011 | -0.0004 | 0.0205 | -0.0098 | -0.0025 | -360.1158 | 17.3576 | -360.365 | 17.5999 | -360.805 | 18.2385 | -360.8758 | 17.5486 | -352.5983 | 18.6881 | -352.5706 | 16.834
12:54 | 5672 | 50.1602 | 202.7499 | 448.7756 | 444.0831 | -16.9586 | -39.1526 | 11.7743 | 8.1757 | 2.7469 | 0.9344 | 3.1779 | -0.955 | 12.3371 | 5.1188 | 0.6242 | 0.662 | 0.9597 | 0.7529 | -129.2387 | 1.6388 | 5.8646 | 2.0091 | -2.584 | -0.8677 | 4.9047 |  | 4.098 | 0.7583 | 4.0062 | 3.3692 | 3.3338 | 1.094 | 10.7777 | 14.2796 | 14.8514 | 11.0909 | 0 | -0.0027 | 0.0003 | 0.0035 | 0.0004 | -0.0006 | 0.0032 | -0.0054 | -0.0288 | -360.1835 | 17.4069 | -360.4296 | 17.5876 | -360.7404 | 18.183 | -360.7897 | 17.5445 | -352.6444 | 18.7353 | -352.626 | 16.8238
12:54 | 5673 | 50.2 | 202.6965 | 448.8136 | 443.8313 | -17.0093 | -39.0985 | 11.7558 | 8.1488 | 2.7212 | 0.8484 | 3.1274 | -0.9265 | 12.3031 | 5.2478 | 0.6231 | 0.662 | 0.9643 | 0.7534 | -129.1908 | 1.6835 | 5.8182 | 1.8618 | -2.6 | -0.8395 | 4.907 |  | 4.0099 | 0.6701 | 4.0057 | 3.3662 | 3.3347 | 1.0943 | 10.7857 | 14.2763 | 14.8668 | 11.11 | -0.0003 | -0.0027 | 0.0006 | 0.004 | 0.0008 | -0.0008 | 0.0068 | -0.0199 | 0.0125 | -360.1373 | 17.3884 | -360.4419 | 17.641 | -360.8512 | 18.1953 | -360.7989 | 17.5116 | -352.5583 | 18.7148 | -352.6506 | 16.8607
12:54 | 5674 | 50.1144 | 202.7644 | 448.8162 | 443.8567 | -16.9704 | -39.1764 | 11.7099 | 8.1639 | 2.7449 | 0.7753 | 3.2041 | -0.9365 | 12.3298 | 5.2167 | 0.624 | 0.6614 | 0.9644 | 0.7525 | -129.2274 | 1.644 | 5.7994 | 1.9638 | -2.5606 | -0.8429 | 4.8816 |  | 4.0116 | 0.5953 | 4.0073 | 3.364 | 3.334 | 1.0921 | 10.7614 | 14.2579 | 14.8086 | 11.0681 | 0.0003 | -0.0031 | 0.0003 | 0.0039 | 0.0006 | -0.0001 | 0.0112 | -0.0146 | -0.0175 | -360.1465 | 17.3556 | -360.3804 | 17.5978 | -360.7743 | 18.2282 | -360.8481 | 17.5445 | -352.5644 | 18.684 | -352.5583 | 16.8238
12:54 | 5675 | 49.8935 | 202.6833 | 448.7656 | 443.6532 | -16.9164 | -39.0021 | 11.8373 | 8.0722 | 2.681 | 0.8551 | 3.2129 | -0.9268 | 12.2696 | 5.2127 | 0.623 | 0.6616 | 0.967 | 0.7539 | -129.327 | 1.6551 | 5.8086 | 1.8389 | -2.5204 | -0.8762 | 4.9455 |  | 4.0934 | 0.6343 | 4.0076 | 3.3658 | 3.3328 | 1.0918 | 10.772 | 14.2447 | 14.8156 | 11.0739 | 0.0001 | -0.0031 | 0.0002 | 0.0036 | 0.0009 | -0.0004 | 0.0001 | 0.0005 | -0.011 | -360.2142 | 17.4151 | -360.4296 | 17.5937 | -360.7435 | 18.181 | -360.7835 | 17.5445 | -352.6475 | 18.7353 | -352.626 | 16.8238
12:54 | 5676 | 49.8559 | 202.7528 | 448.659 | 443.9474 | -16.9633 | -39 | 11.7098 | 8.086 | 2.6373 | 0.7827 | 3.1633 | -0.9735 | 12.2642 | 5.191 | 0.6241 | 0.6616 | 0.9666 | 0.7544 | -129.3147 | 1.6713 | 5.7976 | 1.8542 | -2.3987 | -0.7347 | 4.9611 |  | 4.1975 | 0.697 | 4.0081 | 3.3668 | 3.3386 | 1.0924 | 10.7844 | 14.2756 | 14.8686 | 11.1136 | -0.0001 | -0.0025 | 0.0013 | 0.0042 | 0.001 | -0.0003 | 0.0025 | -0.0033 | 0.0151 | -360.1219 | 17.3864 | -360.4512 | 17.6369 | -360.8081 | 18.2077 | -360.7927 | 17.5239 | -352.5675 | 18.7107 | -352.6413 | 16.8628
12:54 | 5677 | 49.8416 | 202.8185 | 448.8007 | 444.1181 | -16.9046 | -39.0115 | 11.7706 | 8.1119 | 2.6166 | 0.7732 | 3.1 | -1.0101 | 12.2646 | 5.1744 | 0.6233 | 0.6629 | 0.9635 | 0.7533 | -129.2472 | 1.5536 | 5.7924 | 1.8053 | -2.4861 | -0.8507 | 4.8901 |  | 4.1341 | 0.6959 | 4.0079 | 3.3668 | 3.3351 | 1.0917 | 10.7996 | 14.2787 | 14.8522 | 11.089 | -0.0005 | -0.0026 | 0.0009 | 0.004 | 0.0007 | -0.0005 | 0.0089 | -0.0014 | -0.0102 | -360.1465 | 17.3515 | -360.365 | 17.5937 | -360.765 | 18.2261 | -360.845 | 17.5465 | -352.5921 | 18.6799 | -352.5675 | 16.8238
12:54 | 5678 | 49.9725 | 202.8661 | 448.7587 | 443.2881 | -17.0071 | -39.1182 | 11.7515 | 8.038 | 2.5737 | 0.7599 | 3.0806 | -1.0097 | 12.2615 | 5.2046 | 0.6217 | 0.6575 | 0.9635 | 0.751 | -129.3337 | 1.5867 | 5.7618 | 1.77 | -2.4274 | -0.8625 | 4.9058 |  | 4.1811 | 0.6523 | 4.0076 | 3.3667 | 3.3337 | 1.0933 | 10.8076 | 14.2812 | 14.8386 | 11.1024 | 0.0003 | -0.0026 | 0.001 | 0.004 | 0.0008 | 0.0005 | 0.0094 | -0.0042 | -0.0324 | -360.1804 | 17.4233 | -360.4419 | 17.5917 | -360.7466 | 18.183 | -360.7712 | 17.5445 | -352.6352 | 18.7353 | -352.6229 | 16.8238
12:54 | 5679 | 49.9844 | 202.8152 | 448.8334 | 442.472 | -16.9482 | -39.1124 | 11.6544 | 8.0611 | 2.5653 | 0.6688 | 3.0779 | -0.9007 | 12.2361 | 5.2108 | 0.6227 | 0.6618 | 0.9624 | 0.7521 | -129.2951 | 1.5916 | 5.7918 | 1.8922 | -2.4585 | -0.7855 | 4.9351 |  | 4.2044 | 0.6523 | 4.007 | 3.3684 | 3.337 | 1.0932 | 10.8109 | 14.3199 | 14.898 | 11.1218 | 0.0003 | -0.0033 | 0.001 | 0.0043 | 0.0013 | -0.0003 | 0.0113 | -0.0062 | -0.0048 | -360.1404 | 17.3823 | -360.4235 | 17.6286 | -360.8112 | 18.2118 | -360.7897 | 17.5178 | -352.5952 | 18.7045 | -352.6229 | 16.8505
12:54 | 5680 | 49.934 | 202.8331 | 448.8585 | 442.7899 | -16.9384 | -39.1172 | 11.7428 | 8.1124 | 2.523 | 0.8057 | 3.0079 | -0.8151 | 12.2714 | 5.2403 | 0.625 | 0.6634 | 0.962 | 0.7542 | -129.1554 | 1.5808 | 5.8481 | 2.0317 | -2.4488 | -0.8103 | 4.9532 |  | 4.234 | 0.6173 | 4.0086 | 3.3654 | 3.3392 | 1.0939 | 10.8145 | 14.3057 | 14.8874 | 11.1146 | 0 | -0.0027 | 0.0001 | 0.0036 | 0.0009 | 0.0001 | -0.0045 | 0.0017 | 0.0016 | -360.1465 | 17.3658 | -360.3496 | 17.5896 | -360.762 | 18.2159 | -360.8389 | 17.5588 | -352.5798 | 18.6881 | -352.5798 | 16.8176
12:54 | 5681 | 49.7372 | 202.7784 | 448.9791 | 442.6984 | -16.9337 | -39.1491 | 11.7757 | 8.1806 | 2.5532 | 0.6758 | 3.0805 | -0.9525 | 12.2504 | 5.2027 | 0.6225 | 0.6615 | 0.9646 | 0.7524 | -129.1877 | 1.6163 | 5.8508 | 2.0944 | -2.3443 | -0.8042 | 4.9616 |  | 4.1919 | 0.5839 | 4.0087 | 3.3674 | 3.339 | 1.0926 | 10.7961 | 14.2754 | 14.8791 | 11.085 | -0.0003 | -0.0027 | 0.0007 | 0.0039 | 0.0009 | -0.0007 | 0.0121 | -0.0191 | -0.0129 | -360.1896 | 17.4131 | -360.4235 | 17.6061 | -360.765 | 18.183 | -360.7558 | 17.5342 | -352.6198 | 18.7271 | -352.6413 | 16.8217
12:54 | 5682 | 49.587 | 202.7367 | 448.8865 | 444.2153 | -16.8467 | -39.0745 | 11.861 | 8.1087 | 2.5432 | 0.6857 | 3.103 | -0.967 | 12.2395 | 5.188 | 0.6238 | 0.6621 | 0.9641 | 0.7529 | -129.2436 | 1.5223 | 5.7647 | 2.0503 | -2.3423 | -0.7511 | 4.9347 |  | 4.1778 | 0.6682 | 4.0068 | 3.3646 | 3.3357 | 1.0934 | 10.8111 | 14.273 | 14.888 | 11.1233 | 0.0003 | -0.0027 | 0.0006 | 0.0039 | 0.0008 | -0.0007 | -0.0005 | 0.0071 | -0.0092 | -360.1219 | 17.3802 | -360.4081 | 17.6102 | -360.7897 | 18.2097 | -360.7835 | 17.5178 | -352.5244 | 18.6902 | -352.6198 | 16.8464
12:54 | 5683 | 49.5801 | 202.7756 | 448.8471 | 444.6657 | -16.8619 | -39.0347 | 11.87 | 8.1389 | 2.6023 | 0.7099 | 3.1347 | -0.9907 | 12.2464 | 5.2236 | 0.6233 | 0.6632 | 0.9656 | 0.7526 | -129.2215 | 1.4886 | 5.6989 | 2.0433 | -2.394 | -0.696 | 4.9686 |  | 4.1155 | 0.6466 | 4.0071 | 3.3643 | 3.3338 | 1.0928 | 10.7707 | 14.2554 | 14.8511 | 11.1067 | 0.0004 | -0.0031 | 0.0008 | 0.0037 | 0.0008 | -0.0004 | 0.0061 | -0.0184 | 0.0085 | -360.165 | 17.372 | -360.3712 | 17.5917 | -360.7681 | 18.1974 | -360.8143 | 17.5609 | -352.586 | 18.7045 | -352.5798 | 16.8238
12:54 | 5684 | 49.5606 | 202.7833 | 448.9511 | 445.1036 | -16.9259 | -39.1397 | 11.8697 | 8.0608 | 2.5556 | 0.7712 | 3.0849 | -0.9285 | 12.2577 | 5.1436 | 0.6233 | 0.6631 | 0.9695 | 0.7521 | -129.2365 | 1.4755 | 5.7121 | 2.082 | -2.3802 | -0.8221 | 4.8682 |  | 4.1611 | 0.6493 | 4.0086 | 3.3663 | 3.3361 | 1.095 | 10.7648 | 14.2615 | 14.8185 | 11.0887 | -0.0002 | -0.0027 | 0.0017 | 0.0043 | 0.0013 | -0.0011 | 0.0149 | -0.0089 | -0.0073 | -360.1619 | 17.4048 | -360.4204 | 17.5958 | -360.7497 | 18.1871 | -360.7527 | 17.5383 | -352.6106 | 18.7066 | -352.5829 | 16.8279
12:54 | 5685 | 49.3685 | 202.6056 | 448.8439 | 445.2329 | -16.8798 | -39.2293 | 11.8148 | 8.0137 | 2.6233 | 0.8271 | 3.0813 | -0.9627 | 12.3027 | 5.1989 | 0.6239 | 0.6627 | 0.965 | 0.7512 | -129.2794 | 1.5398 | 5.6254 | 2.1091 | -2.3751 | -0.8365 | 4.9317 |  | 4.128 | 0.5172 | 4.0074 | 3.3632 | 3.3316 | 1.0951 | 10.8306 | 14.3048 | 14.9113 | 11.107 | -0.0002 | -0.0025 | 0.001 | 0.0038 | 0.0008 | -0.0002 | 0.0089 | 0.0062 | 0.0024 | -360.0973 | 17.3761 | -360.3989 | 17.6143 | -360.7958 | 18.2077 | -360.8204 | 17.5219 | -352.5706 | 18.7025 | -352.5767 | 16.8402
12:54 | 5686 | 49.4439 | 202.6703 | 449.024 | 445.3942 | -16.9468 | -39.1913 | 11.8856 | 8.0423 | 2.5482 | 0.7117 | 3.0509 | -0.9512 | 12.2532 | 5.2615 | 0.6224 | 0.6651 | 0.966 | 0.7528 | -129.2543 | 1.6008 | 5.7449 | 2.119 | -2.3819 | -0.9198 | 4.9779 |  | 4.1474 | 0.5812 | 4.0099 | 3.3681 | 3.3355 | 1.0949 | 10.7718 | 14.2742 | 14.8488 | 11.1071 | 0.0001 | -0.0028 | 0.0012 | 0.0042 | 0.0014 | -0.0003 | 0.0086 | -0.0093 | -0.0042 | -360.1773 | 17.3905 | -360.405 | 17.5917 | -360.7804 | 18.1933 | -360.7989 | 17.5547 | -352.5736 | 18.7107 | -352.5952 | 16.8156
12:54 | 5687 | 49.5242 | 202.7484 | 448.9641 | 445.692 | -16.9292 | -39.1529 | 11.9501 | 8.0414 | 2.5491 | 0.6523 | 3.1144 | -0.9416 | 12.2148 | 5.1343 | 0.6218 | 0.6638 | 0.9638 | 0.7519 | -129.2593 | 1.675 | 5.8464 | 2.085 | -2.3525 | -0.7952 | 4.9742 |  | 4.1646 | 0.6206 | 4.0083 | 3.3693 | 3.3368 | 1.0933 | 10.7787 | 14.2696 | 14.8676 | 11.1197 | 0.0004 | -0.0028 | 0.0008 | 0.0038 | 0.0007 | -0.0001 | 0.0221 | -0.0136 | -0.0123 | -360.1588 | 17.3864 | -360.4173 | 17.6102 | -360.7558 | 18.1974 | -360.7743 | 17.528 | -352.5429 | 18.7045 | -352.5706 | 16.8299
12:55 | 5688 | 49.546 | 202.774 | 448.9724 | 445.805 | -16.9703 | -39.1813 | 11.9251 | 8.0481 | 2.5346 | 0.6216 | 3.1086 | -1.1079 | 12.2576 | 5.1438 | 0.6231 | 0.6633 | 0.9609 | 0.7526 | -129.3725 | 1.5157 | 5.7347 | 2.1163 | -2.4031 | -0.8854 | 4.8925 |  | 4.1407 | 0.5723 | 4.0068 | 3.3674 | 3.3341 | 1.0929 | 10.7891 | 14.2569 | 14.8604 | 11.084 | 0 | -0.0028 | 0.0005 | 0.0041 | 0.0013 | -0.0002 | 0.0109 | -0.006 | -0.0123 | -360.1619 | 17.3905 | -360.4173 | 17.6184 | -360.762 | 18.2077 | -360.8235 | 17.5404 | -352.5736 | 18.7087 | -352.589 | 16.832
12:55 | 5689 | 49.4777 | 202.6404 | 448.9532 | 445.7806 | -16.9484 | -39.1836 | 11.8389 | 8.0457 | 2.5333 | 0.6801 | 3.0916 | -0.9967 | 12.2777 | 5.175 | 0.6219 | 0.662 | 0.9644 | 0.7539 | -129.2457 | 1.6287 | 5.7764 | 1.9686 | -2.4457 | -0.8139 | 4.9494 |  | 4.2106 | 0.5483 | 4.0078 | 3.3677 | 3.3327 | 1.0924 | 10.7684 | 14.2877 | 14.8368 | 11.0699 | -0.0005 | -0.0024 | 0.0008 | 0.0043 | 0.0009 | -0.0001 | -0.0039 | -0.0037 | 0.0052 | -360.1281 | 17.3864 | -360.4112 | 17.6225 | -360.7743 | 18.1974 | -360.802 | 17.5383 | -352.5675 | 18.7004 | -352.6013 | 16.8176
12:55 | 5690 | 49.4449 | 202.7224 | 448.9424 | 445.7739 | -16.9207 | -39.1578 | 11.9037 | 8.0754 | 2.5072 | 0.6465 | 3.0977 | -0.9764 | 12.2691 | 5.2142 | 0.6226 | 0.6634 | 0.9634 | 0.7533 | -129.2442 | 1.6362 | 5.8248 | 1.9063 | -2.3285 | -0.6705 | 4.9545 |  | 4.1613 | 0.5797 | 4.0069 | 3.3649 | 3.3335 | 1.0925 | 10.751 | 14.2532 | 14.8031 | 11.0753 | 0.0002 | -0.0027 | 0.0009 | 0.004 | 0.0009 | -0.0008 | 0.0115 | -0.0204 | -0.0146 | -360.1835 | 17.3946 | -360.4389 | 17.6451 | -360.7897 | 18.2056 | -360.7958 | 17.5404 | -352.5613 | 18.7107 | -352.589 | 16.8381
12:55 | 5691 | 49.3844 | 202.7338 | 448.9528 | 446.0337 | -16.9589 | -39.098 | 11.7306 | 8.0941 | 2.3893 | 0.5671 | 3.109 | -1.0146 | 12.1759 | 5.1258 | 0.6215 | 0.6634 | 0.9613 | 0.7538 | -129.2657 | 1.5651 | 5.8837 | 1.8609 | -2.3231 | -0.7344 | 4.9153 |  | 4.2288 | 0.5203 | 4.0065 | 3.3644 | 3.3368 | 1.0935 | 10.7777 | 14.2564 | 14.8167 | 11.0851 | 0 | -0.0032 | 0.0009 | 0.0037 | 0.0005 | -0.0004 | 0.0034 | -0.0147 | -0.0151 | -360.1527 | 17.3843 | -360.4235 | 17.6389 | -360.7773 | 18.1994 | -360.805 | 17.5404 | -352.5767 | 18.7087 | -352.589 | 16.8217
12:55 | 5692 | 49.3773 | 202.7255 | 449.0622 | 446.2961 | -16.9272 | -39.1584 | 11.7472 | 8.0718 | 2.5343 | 0.7285 | 3.1414 | -0.9813 | 12.1164 | 5.1475 | 0.6224 | 0.6624 | 0.9666 | 0.753 | -129.2074 | 1.5872 | 5.8314 | 1.8725 | -2.3307 | -0.8391 | 4.8957 |  | 4.1244 | 0.4925 | 4.0064 | 3.3659 | 3.3338 | 1.0913 | 10.7961 | 14.2812 | 14.827 | 11.085 | 0 | -0.0029 | 0.0011 | 0.0041 | 0.0009 | -0.0007 | 0.0267 | -0.0132 | -0.0076 | -360.1404 | 17.4007 | -360.4204 | 17.6389 | -360.7589 | 18.181 | -360.7681 | 17.5301 | -352.5798 | 18.7045 | -352.6167 | 16.8402
12:55 | 5693 | 49.3926 | 202.6815 | 449.0505 | 446.5443 | -16.8918 | -39.1046 | 11.7657 | 8.0046 | 2.5657 | 0.745 | 3.15 | -1.0295 | 12.1717 | 5.1421 | 0.6218 | 0.6615 | 0.9652 | 0.7541 | -129.1932 | 1.7111 | 5.9015 | 1.9594 | -2.375 | -0.7439 | 4.8618 |  | 4.1508 | 0.6317 | 4.0075 | 3.3668 | 3.3378 | 1.0929 | 10.7787 | 14.2871 | 14.8281 | 11.0962 | -0.0004 | -0.0026 | 0.001 | 0.0039 | 0.001 | -0.0003 | 0.0138 | 0.0004 | -0.0161 | -360.1311 | 17.3864 | -360.4112 | 17.643 | -360.7804 | 18.1974 | -360.7927 | 17.5404 | -352.5644 | 18.7025 | -352.6013 | 16.8381
12:55 | 5694 | 49.394 | 202.7293 | 448.8791 | 446.6634 | -16.8586 | -39.1573 | 11.8318 | 8.0139 | 2.6048 | 0.6972 | 3.1034 | -0.9086 | 12.1697 | 5.1168 | 0.6233 | 0.6643 | 0.9627 | 0.7539 | -129.2268 | 1.733 | 5.9111 | 2.0645 | -2.3516 | -0.8283 | 4.8775 |  | 4.0707 | 0.5469 | 4.0068 | 3.3662 | 3.3371 | 1.0934 | 10.8145 | 14.323 | 14.8758 | 11.1204 | -0.0003 | -0.0027 | 0.0004 | 0.0037 | 0.0009 | -0.0003 | 0.0114 | -0.0049 | -0.024 | -360.1588 | 17.3905 | -360.4235 | 17.6102 | -360.7404 | 18.1974 | -360.8081 | 17.5506 | -352.5829 | 18.7148 | -352.5736 | 16.8156
12:55 | 5695 | 49.4425 | 202.7451 | 449.0702 | 446.9105 | -16.7741 | -39.125 | 11.8924 | 8.0382 | 2.5624 | 0.7251 | 3.1265 | -0.9555 | 12.2619 | 5.1586 | 0.6222 | 0.6658 | 0.9669 | 0.7536 | -129.1784 | 1.7088 | 5.9352 | 1.9869 | -2.3962 | -0.7734 | 4.8191 |  | 4.1459 | 0.644 | 4.0072 | 3.3703 | 3.3336 | 1.0945 | 10.7972 | 14.3055 | 14.8805 | 11.0861 | 0.0003 | -0.003 | 0.0003 | 0.0037 | 0.0007 | -0.0004 | 0.024 | -0.0035 | -0.0187 | -360.1588 | 17.4069 | -360.4542 | 17.641 | -360.7681 | 18.1789 | -360.7989 | 17.5404 | -352.6013 | 18.721 | -352.6167 | 16.8381
12:55 | 5696 | 49.429 | 202.7028 | 448.92 | 447.0519 | -16.7966 | -38.9783 | 11.89 | 7.9541 | 2.5203 | 0.7708 | 3.1114 | -1.0408 | 12.1864 | 5.0849 | 0.6245 | 0.6581 | 0.9648 | 0.7533 | -129.1906 | 1.6362 | 5.8828 | 1.9778 | -2.3934 | -0.8737 | 4.848 |  | 4.1804 | 0.61 | 4.0084 | 3.369 | 3.3365 | 1.093 | 10.8261 | 14.3 | 14.9174 | 11.1374 | -0.0001 | -0.003 | 0.0005 | 0.0038 | 0.0009 | 0.0002 | 0.011 | -0.0028 | 0.0012 | -360.1342 | 17.3802 | -360.4204 | 17.6615 | -360.8266 | 18.2056 | -360.805 | 17.5321 | -352.5552 | 18.7066 | -352.5798 | 16.834
12:55 | 5697 | 49.4245 | 202.6786 | 448.9906 | 447.0125 | -16.8601 | -39.1179 | 11.8163 | 7.9747 | 2.5222 | 0.6567 | 3.0264 | -1.0417 | 12.1679 | 5.1651 | 0.623 | 0.661 | 0.966 | 0.7533 | -129.2793 | 1.6038 | 5.7909 | 1.8845 | -2.4692 | -0.8662 | 4.7639 |  | 4.2839 | 0.711 | 4.0074 | 3.366 | 3.3343 | 1.0933 | 10.7788 | 14.2923 | 14.8644 | 11.0862 | -0.0001 | -0.0025 | 0.0007 | 0.004 | 0.0005 | -0.001 | 0.0248 | -0.0025 | -0.0121 | -360.1804 | 17.4007 | -360.4204 | 17.6369 | -360.7804 | 18.1994 | -360.8266 | 17.5753 | -352.6136 | 18.7148 | -352.5829 | 16.8074
12:55 | 5698 | 49.4453 | 202.8076 | 449.0941 | 447.0631 | -16.89 | -39.0343 | 11.7322 | 7.9199 | 2.5243 | 0.5927 | 3.0699 | -1.0183 | 12.1268 | 5.1311 | 0.6231 | 0.6612 | 0.9631 | 0.7508 | -129.2024 | 1.6572 | 5.8699 | 1.9066 | -2.4734 | -0.8999 | 4.8188 |  | 4.2974 | 0.6684 | 4.0062 | 3.3649 | 3.3343 | 1.0947 | 10.7834 | 14.2508 | 14.8293 | 11.0558 | -0.0004 | -0.0029 | 0.001 | 0.0043 | 0.0005 | -0.0001 | 0.0046 | -0.0053 | -0.0281 | -360.1804 | 17.4172 | -360.4358 | 17.6389 | -360.802 | 18.1851 | -360.765 | 17.5465 | -352.5798 | 18.7333 | -352.6444 | 16.8197
12:55 | 5699 | 49.4412 | 202.7613 | 449.0924 | 447.1785 | -16.9178 | -38.9765 | 11.8427 | 7.9121 | 2.4494 | 0.6357 | 3.0955 | -1.0772 | 12.1555 | 5.1229 | 0.6227 | 0.6606 | 0.9697 | 0.7511 | -129.2259 | 1.6631 | 5.8714 | 2.0018 | -2.4017 | -0.8391 | 4.8252 |  | 4.2587 | 0.5536 | 4.0064 | 3.3665 | 3.331 | 1.0946 | 10.7534 | 14.2552 | 14.8443 | 11.0956 | 0.0001 | -0.0033 | 0.0006 | 0.0036 | 0.001 | -0.0007 | 0.0054 | -0.016 | 0.0063 | -360.1404 | 17.3761 | -360.4112 | 17.6553 | -360.8235 | 18.2241 | -360.8235 | 17.5301 | -352.5398 | 18.7025 | -352.589 | 16.8361
12:55 | 5700 | 49.5363 | 202.7885 | 449.1676 | 447.2297 | -16.8857 | -39.041 | 11.8857 | 7.8721 | 2.3904 | 0.7835 | 3.0462 | -1.0474 | 12.149 | 5.1616 | 0.622 | 0.6634 | 0.9691 | 0.7529 | -129.2444 | 1.6398 | 5.8838 | 1.9992 | -2.3664 | -0.8238 | 4.846 |  | 4.2464 | 0.6297 | 4.0073 | 3.3673 | 3.3325 | 1.0955 | 10.7534 | 14.2437 | 14.8095 | 11.0494 | -0.0001 | -0.0031 | 0.0014 | 0.0041 | 0.0004 | -0.0005 | -0.0026 | 0.0025 | -0.0356 | -360.205 | 17.3966 | -360.4142 | 17.6163 | -360.7681 | 18.1953 | -360.8174 | 17.5609 | -352.6229 | 18.721 | -352.589 | 16.8115
12:55 | 5701 | 49.423 | 202.7228 | 449.0669 | 447.2288 | -17.0138 | -39.2089 | 11.7639 | 7.8342 | 2.42 | 0.7532 | 3.01 | -1.0583 | 12.1555 | 5.1425 | 0.6226 | 0.6635 | 0.9657 | 0.7521 | -129.2799 | 1.5724 | 5.7908 | 2.049 | -2.3632 | -0.7383 | 4.9727 |  | 4.3092 | 0.7709 | 4.0076 | 3.3656 | 3.3344 | 1.0931 | 10.7706 | 14.2905 | 14.8369 | 11.1056 | -0.0004 | -0.0025 | 0.001 | 0.0041 | 0.0013 | -0.0006 | 0.0209 | -0.0065 | 0.0069 | -360.165 | 17.4048 | -360.4419 | 17.6451 | -360.8143 | 18.1769 | -360.7404 | 17.5301 | -352.6013 | 18.7251 | -352.6321 | 16.8381
12:55 | 5702 | 49.4191 | 202.6358 | 449.0811 | 447.2501 | -17.1255 | -39.2306 | 11.7268 | 7.8925 | 2.4284 | 0.6571 | 3.0461 | -1.0265 | 12.1799 | 5.1568 | 0.6227 | 0.6694 | 0.9682 | 0.7544 | -129.2628 | 1.616 | 5.7672 | 1.9318 | -2.4129 | -0.841 | 4.8864 |  | 4.2917 | 0.7115 | 4.0068 | 3.3641 | 3.3359 | 1.0924 | 10.8098 | 14.3301 | 14.8956 | 11.1269 | 0 | -0.0025 | 0.0009 | 0.0042 | 0.0008 | -0.0002 | 0.0021 | -0.0103 | 0.0006 | -360.1188 | 17.3679 | -360.3896 | 17.6266 | -360.7897 | 18.2282 | -360.802 | 17.5445 | -352.5706 | 18.684 | -352.5767 | 16.834
12:55 | 5703 | 49.3661 | 202.6101 | 448.9539 | 447.1891 | -17.121 | -39.1539 | 11.7736 | 8.0405 | 2.4497 | 0.7073 | 3.1046 | -0.9255 | 12.1643 | 5.2327 | 0.6225 | 0.666 | 0.9671 | 0.7514 | -129.2271 | 1.6946 | 5.8815 | 1.9692 | -2.4648 | -0.8134 | 4.871 |  | 4.2767 | 0.7019 | 4.0053 | 3.3678 | 3.3348 | 1.093 | 10.7765 | 14.2785 | 14.8453 | 11.0836 | 0.0002 | -0.0031 | 0.0006 | 0.004 | 0.0009 | -0.0003 | 0.0122 | -0.001 | -0.0166 | -360.1496 | 17.4048 | -360.4081 | 17.602 | -360.7466 | 18.1789 | -360.8204 | 17.5629 | -352.6567 | 18.721 | -352.549 | 16.8053
12:55 | 5704 | 49.5142 | 202.7516 | 449.0929 | 447.3379 | -17.0216 | -39.1891 | 11.8128 | 8.0057 | 2.3989 | 0.6873 | 3.0898 | -0.9675 | 12.2084 | 5.2585 | 0.6227 | 0.6664 | 0.9661 | 0.7505 | -129.2124 | 1.7096 | 5.7841 | 1.9164 | -2.3629 | -0.6922 | 4.8997 |  | 4.2704 | 0.7021 | 4.0056 | 3.3652 | 3.3366 | 1.0938 | 10.8306 | 14.2816 | 14.8997 | 11.1301 | 0.0002 | -0.0029 | 0.0005 | 0.0038 | 0.0011 | 0.0001 | 0.008 | -0.0034 | 0.0132 | -360.1219 | 17.4007 | -360.4573 | 17.6512 | -360.842 | 18.183 | -360.765 | 17.5219 | -352.5829 | 18.7189 | -352.6567 | 16.8546
12:55 | 5705 | 49.4789 | 202.6956 | 449.0192 | 447.3802 | -16.81 | -38.9502 | 11.965 | 7.9864 | 2.5026 | 0.6642 | 3.0789 | -1.0135 | 12.2315 | 5.356 | 0.6226 | 0.6649 | 0.966 | 0.752 | -129.2822 | 1.6562 | 5.6722 | 2.0278 | -2.3997 | -0.8967 | 4.878 |  | 4.2944 | 0.7184 | 4.0069 | 3.3671 | 3.3323 | 1.095 | 10.795 | 14.2913 | 14.8467 | 11.0905 | -0.0003 | -0.0027 | 0.0006 | 0.0039 | 0.0002 | -0.0009 | 0.0181 | -0.0062 | -0.0131 | -360.1188 | 17.3597 | -360.3342 | 17.6204 | -360.7897 | 18.2179 | -360.8666 | 17.5629 | -352.5798 | 18.6902 | -352.546 | 16.8156
12:55 | 5706 | 49.3652 | 202.7475 | 449.0756 | 447.6446 | -16.9335 | -39.0204 | 11.9197 | 7.9917 | 2.5705 | 0.7374 | 3.0846 | -1.0202 | 12.2414 | 5.2555 | 0.6221 | 0.6701 | 0.9678 | 0.7523 | -129.2763 | 1.6582 | 5.796 | 2.1058 | -2.4319 | -0.7919 | 4.8704 |  | 4.1689 | 0.7452 | 4.0075 | 3.3679 | 3.3358 | 1.0951 | 10.7776 | 14.2625 | 14.8593 | 11.0843 | -0.0003 | -0.0027 | 0.001 | 0.0038 | 0.001 | -0.0003 | 0.026 | -0.0205 | 0.0075 | -360.1742 | 17.4233 | -360.4696 | 17.6328 | -360.7835 | 18.183 | -360.805 | 17.5568 | -352.6813 | 18.7333 | -352.6844 | 16.834
12:55 | 5707 | 49.4534 | 202.6809 | 449.0264 | 447.8536 | -16.9032 | -38.9317 | 11.8995 | 7.9111 | 2.5993 | 0.6936 | 3.0165 | -0.9125 | 12.2646 | 5.328 | 0.623 | 0.6649 | 0.9635 | 0.7519 | -129.1924 | 1.6132 | 5.8119 | 2.0161 | -2.4353 | -0.8494 | 4.8539 |  | 4.1973 | 0.7913 | 4.0068 | 3.3695 | 3.3349 | 1.0952 | 10.7429 | 14.2452 | 14.813 | 11.0786 | 0.0007 | -0.0028 | 0.0009 | 0.0037 | 0.0008 | -0.0007 | 0.012 | -0.0142 | -0.0074 | -360.1281 | 17.3843 | -360.4389 | 17.6512 | -360.8327 | 18.2261 | -360.8297 | 17.5342 | -352.5829 | 18.7045 | -352.6167 | 16.8669
12:55 | 5708 | 49.4183 | 202.6668 | 449.0097 | 447.9376 | -16.9495 | -38.9188 | 11.8242 | 7.8407 | 2.5919 | 0.6806 | 2.9907 | -0.9659 | 12.2334 | 5.3445 | 0.6222 | 0.6684 | 0.9679 | 0.7526 | -129.2767 | 1.6091 | 5.8335 | 2.0124 | -2.4389 | -0.84 | 4.8587 |  | 4.2263 | 0.7693 | 4.0066 | 3.3658 | 3.3364 | 1.0954 | 10.7731 | 14.2517 | 14.8228 | 11.075 | 0.0002 | -0.003 | 0.0007 | 0.0036 | 0.0007 | -0.0008 | 0.0091 | 0.0028 | -0.0014 | -360.2204 | 17.3966 | -360.405 | 17.6204 | -360.7712 | 18.22 | -360.8789 | 17.5937 | -352.6537 | 18.721 | -352.586 | 16.8238
12:55 | 5709 | 49.4511 | 202.6817 | 449.0561 | 448.1834 | -16.8911 | -38.8317 | 11.8728 | 7.8931 | 2.5748 | 0.7148 | 2.9843 | -0.9972 | 12.1512 | 5.3596 | 0.6237 | 0.6649 | 0.9688 | 0.7525 | -129.2083 | 1.5744 | 5.7526 | 2.028 | -2.3007 | -0.8441 | 4.8731 |  | 4.2758 | 0.7636 | 4.0064 | 3.3639 | 3.3337 | 1.0943 | 10.7845 | 14.2754 | 14.8444 | 11.085 | 0.0002 | -0.0025 | 0.0006 | 0.0038 | 0.0007 | -0.0002 | 0.0138 | -0.0109 | 0.0012 | -360.1927 | 17.4377 | -360.5158 | 17.6677 | -360.8389 | 18.1912 | -360.7866 | 17.5506 | -352.6506 | 18.7477 | -352.6937 | 16.8648
12:55 | 5710 | 49.4863 | 202.7181 | 449.1372 | 448.5843 | -16.8591 | -38.8171 | 11.9119 | 7.9483 | 2.5326 | 0.672 | 3.0182 | -0.9323 | 12.2237 | 5.351 | 0.624 | 0.664 | 0.964 | 0.7533 | -129.2002 | 1.6436 | 5.8373 | 2.0023 | -2.3587 | -0.8517 | 4.8666 |  | 4.3375 | 0.8418 | 4.0069 | 3.3698 | 3.333 | 1.096 | 10.7915 | 14.2938 | 14.9084 | 11.1269 | -0.0004 | -0.0027 | 0.0004 | 0.0036 | 0.001 | -0.0006 | 0.0047 | -0.0123 | 0.0065 | -360.1373 | 17.3884 | -360.4512 | 17.6553 | -360.8481 | 18.2652 | -360.8943 | 17.5671 | -352.6229 | 18.7107 | -352.6321 | 16.8505
12:55 | 5711 | 49.4515 | 202.604 | 449.0968 | 449.3246 | -16.7931 | -38.831 | 11.9152 | 7.9302 | 2.5887 | 0.6638 | 2.9626 | -0.9108 | 12.1276 | 5.3205 | 0.622 | 0.6629 | 0.9614 | 0.7532 | -129.2401 | 1.6974 | 5.7907 | 2.0126 | -2.3842 | -0.8446 | 4.9003 |  | 4.2265 | 0.8384 | 4.0071 | 3.3687 | 3.334 | 1.0954 | 10.7603 | 14.2506 | 14.8109 | 11.0909 | 0.0002 | -0.0029 | 0.0007 | 0.0039 | 0.0008 | 0.0003 | 0.0127 | -0.0219 | -0.0091 | -360.2512 | 17.4356 | -360.445 | 17.6348 | -360.7958 | 18.2097 | -360.8635 | 17.5896 | -352.6967 | 18.7477 | -352.6352 | 16.8135
12:55 | 5712 | 49.5158 | 202.6432 | 449.1119 | 449.9527 | -16.8472 | -38.9235 | 11.8484 | 7.9982 | 2.4774 | 0.5605 | 2.9639 | -0.9042 | 12.2154 | 5.383 | 0.6234 | 0.667 | 0.9626 | 0.7519 | -129.2733 | 1.6531 | 5.8035 | 1.994 | -2.5239 | -0.8845 | 4.7648 |  | 4.2092 | 0.7654 | 4.008 | 3.364 | 3.3334 | 1.096 | 10.7972 | 14.2766 | 14.8574 | 11.0803 | 0.0001 | -0.003 | 0.0006 | 0.0043 | 0.0012 | -0.0004 | 0.0106 | -0.02 | -0.0304 | -360.165 | 17.4418 | -360.485 | 17.6779 | -360.8912 | 18.2138 | -360.8143 | 17.5404 | -352.6106 | 18.7374 | -352.6752 | 16.8628
12:55 | 5713 | 49.6148 | 202.7135 | 449.1373 | 450.2102 | -16.8693 | -38.9484 | 11.8449 | 7.9612 | 2.4259 | 0.6524 | 2.9797 | -0.8459 | 12.1997 | 5.3489 | 0.6234 | 0.6655 | 0.9633 | 0.7535 | -129.1859 | 1.6637 | 5.8815 | 2.0002 | -2.4244 | -0.9263 | 4.8659 |  | 4.2662 | 0.7216 | 4.0073 | 3.3679 | 3.3333 | 1.0943 | 10.7857 | 14.3169 | 14.8679 | 11.1269 | 0 | -0.0027 | 0.0006 | 0.0041 | 0.0006 | 0.0001 | -0.0028 | -0.0151 | -0.0003 | -360.1988 | 17.3802 | -360.3989 | 17.6328 | -360.8266 | 18.2426 | -360.9035 | 17.5814 | -352.629 | 18.7045 | -352.5921 | 16.8053
12:55 | 5714 | 49.6327 | 202.7322 | 449.0709 | 450.4784 | -16.8261 | -38.9719 | 11.7695 | 7.9852 | 2.464 | 0.7681 | 2.9393 | -0.9935 | 12.2794 | 5.3495 | 0.6211 | 0.6619 | 0.9627 | 0.7514 | -129.2308 | 1.6299 | 5.8738 | 2.0491 | -2.3561 | -1.0317 | 4.8203 |  | 4.3182 | 0.8155 | 4.0079 | 3.3687 | 3.3366 | 1.0935 | 10.7476 | 14.2612 | 14.828 | 11.0836 | -0.0003 | -0.0027 | 0.0013 | 0.0042 | 0.0009 | -0.0006 | 0.0216 | -0.0203 | 0.0065 | -360.205 | 17.4336 | -360.4604 | 17.6328 | -360.7958 | 18.183 | -360.7835 | 17.5629 | -352.6321 | 18.7477 | -352.6475 | 16.8156
12:55 | 5715 | 49.6807 | 202.7539 | 449.0808 | 450.4331 | -16.8302 | -38.9548 | 11.864 | 7.9956 | 2.5514 | 0.8301 | 3.0937 | -0.9036 | 12.2613 | 5.366 | 0.6226 | 0.6664 | 0.9652 | 0.7527 | -129.1457 | 1.7064 | 5.9414 | 2.1017 | -2.3932 | -0.9266 | 4.8169 |  | 4.3215 | 0.7574 | 4.007 | 3.367 | 3.335 | 1.0946 | 10.7811 | 14.2833 | 14.8797 | 11.1111 | 0 | -0.0029 | 0.0007 | 0.0037 | 0.0004 | -0.0004 | 0.0049 | -0.0013 | -0.0211 | -360.125 | 17.3843 | -360.4512 | 17.6553 | -360.8481 | 18.2138 | -360.7835 | 17.5239 | -352.546 | 18.6943 | -352.629 | 16.832
12:55 | 5716 | 49.579 | 202.7259 | 449.1881 | 450.689 | -16.7843 | -38.981 | 11.8588 | 8.0493 | 2.6248 | 0.8231 | 3.0713 | -0.9416 | 12.2873 | 5.3375 | 0.6225 | 0.6661 | 0.9626 | 0.7527 | -129.2746 | 1.6384 | 5.8205 | 2.0769 | -2.3814 | -0.8616 | 4.8631 |  | 4.3277 | 0.8025 | 4.0069 | 3.3712 | 3.333 | 1.0951 | 10.8018 | 14.2581 | 14.8676 | 11.0908 | 0.0002 | -0.0028 | 0.0012 | 0.0038 | 0.0009 | -0.0008 | 0.017 | 0.0027 | -0.0086 | -360.2081 | 17.374 | -360.3927 | 17.604 | -360.7373 | 18.2036 | -360.8697 | 17.5712 | -352.6136 | 18.7087 | -352.5613 | 16.7807
12:55 | 5717 | 49.5187 | 202.6908 | 449.125 | 450.841 | -16.8077 | -39.0553 | 11.8444 | 7.9742 | 2.6463 | 0.7701 | 3.0537 | -0.9461 | 12.2706 | 5.2837 | 0.6251 | 0.665 | 0.9651 | 0.7538 | -129.2613 | 1.6531 | 5.7017 | 2.1952 | -2.3345 | -0.8562 | 4.9158 |  | 4.1998 | 0.8176 | 4.0067 | 3.3658 | 3.3326 | 1.0944 | 10.7868 | 14.2776 | 14.8519 | 11.1107 | -0.0004 | -0.003 | 0.001 | 0.0037 | 0.0009 | -0.0007 | 0.011 | -0.004 | -0.0097 | -360.1835 | 17.409 | -360.4481 | 17.6471 | -360.7989 | 18.1728 | -360.7435 | 17.526 | -352.5921 | 18.7189 | -352.6321 | 16.8176
12:55 | 5718 | 49.4699 | 202.7091 | 449.1318 | 450.9205 | -16.8048 | -38.893 | 11.8911 | 7.9446 | 2.556 | 0.7377 | 3.0229 | -0.9447 | 12.3244 | 5.2757 | 0.6212 | 0.6677 | 0.9642 | 0.752 | -129.212 | 1.6794 | 5.7804 | 2.0782 | -2.4616 | -0.8945 | 4.851 |  | 4.3016 | 0.8598 | 4.0065 | 3.3722 | 3.3361 | 1.0942 | 10.7995 | 14.2673 | 14.859 | 11.0829 | -0.0003 | -0.0028 | 0.0001 | 0.0033 | 0.001 | -0.0003 | 0.0096 | -0.0092 | -0.0148 | -360.1004 | 17.3617 | -360.3712 | 17.6328 | -360.7866 | 18.2241 | -360.8389 | 17.5342 | -352.5367 | 18.6799 | -352.5798 | 16.8115
12:55 | 5719 | 49.4738 | 202.7549 | 448.9776 | 450.934 | -16.7803 | -38.8633 | 11.9018 | 8.0154 | 2.5499 | 0.829 | 3.074 | -0.9114 | 12.3057 | 5.275 | 0.6231 | 0.6629 | 0.9605 | 0.7522 | -129.302 | 1.6633 | 5.7181 | 2.104 | -2.3896 | -0.7952 | 4.9083 |  | 4.3068 | 0.8497 | 4.0064 | 3.366 | 3.3339 | 1.0931 | 10.8064 | 14.2919 | 14.8567 | 11.1237 | 0 | -0.0026 | 0.0008 | 0.0041 | 0.001 | -0.0002 | 0.0053 | -0.0163 | -0.0051 | -360.1804 | 17.4131 | -360.3958 | 17.5917 | -360.7404 | 18.181 | -360.7897 | 17.5609 | -352.626 | 18.723 | -352.586 | 16.7868
12:55 | 5720 | 49.5673 | 202.6797 | 449.1197 | 450.9984 | -16.7659 | -39.0462 | 11.883 | 7.9827 | 2.5786 | 0.7156 | 3.0129 | -0.9291 | 12.2855 | 5.304 | 0.6224 | 0.6625 | 0.9689 | 0.7524 | -129.2365 | 1.7557 | 5.6657 | 2.1894 | -2.4069 | -0.8079 | 4.9503 |  | 4.2782 | 0.8774 | 4.0063 | 3.3703 | 3.3355 | 1.0931 | 10.7949 | 14.3149 | 14.8788 | 11.0951 | 0.0002 | -0.0032 | 0.0008 | 0.0043 | 0.0006 | -0.0004 | 0.0103 | -0.007 | -0.0184 | -360.1496 | 17.3843 | -360.4666 | 17.6512 | -360.8297 | 18.2015 | -360.7804 | 17.5116 | -352.5429 | 18.7148 | -352.6383 | 16.8484
12:55 | 5721 | 49.6395 | 202.8128 | 449.184 | 451.0511 | -16.7803 | -39.0043 | 11.8981 | 8.0594 | 2.602 | 0.7543 | 3.0689 | -0.9527 | 12.1749 | 5.2079 | 0.6236 | 0.6639 | 0.9661 | 0.7537 | -129.2209 | 1.6775 | 5.5836 | 2.1625 | -2.4075 | -0.7923 | 4.9992 |  | 4.3561 | 0.8724 | 4.0065 | 3.3684 | 3.3375 | 1.0949 | 10.7857 | 14.2821 | 14.8494 | 11.11 | -0.0001 | -0.003 | 0.0011 | 0.0038 | 0.0011 | -0.0003 | 0.0147 | 0.0035 | -0.0223 | -360.1311 | 17.3638 | -360.3558 | 17.602 | -360.7712 | 18.2015 | -360.8604 | 17.5588 | -352.5952 | 18.6922 | -352.5644 | 16.795
12:55 | 5722 | 49.6811 | 202.8587 | 449.2241 | 451.1234 | -16.7726 | -38.962 | 11.8354 | 8.0158 | 2.5514 | 0.7292 | 2.987 | -0.874 | 12.2065 | 5.2309 | 0.6235 | 0.6626 | 0.9675 | 0.753 | -129.171 | 1.7544 | 5.7725 | 2.1815 | -2.4025 | -0.8374 | 4.9836 |  | 4.2962 | 0.9547 | 4.0063 | 3.3689 | 3.335 | 1.0945 | 10.8111 | 14.2848 | 14.8948 | 11.0998 | -0.0006 | -0.0027 | 0.0013 | 0.0043 | 0.0007 | -0.0001 | 0.0027 | -0.0113 | -0.0161 | -360.1804 | 17.4192 | -360.4696 | 17.6369 | -360.7835 | 18.1789 | -360.765 | 17.5424 | -352.626 | 18.7395 | -352.6413 | 16.8135
12:55 | 5723 | 49.5224 | 202.7441 | 449.1978 | 451.1084 | -16.8093 | -38.9675 | 11.9381 | 8.0525 | 2.6051 | 0.7734 | 3.0249 | -0.9434 | 12.2313 | 5.2214 | 0.6237 | 0.662 | 0.9664 | 0.754 | -129.2416 | 1.6516 | 5.7773 | 2.0361 | -2.3826 | -0.7696 | 4.9605 |  | 4.3515 | 0.8605 | 4.0061 | 3.3684 | 3.3384 | 1.0933 | 10.7915 | 14.2822 | 14.8852 | 11.0807 | -0.0002 | -0.0031 | 0.0007 | 0.0035 | 0.0007 | -0.0007 | 0.0033 | 0.0088 | 0.0029 | -360.1004 | 17.374 | -360.3989 | 17.6471 | -360.8327 | 18.2179 | -360.805 | 17.5178 | -352.5583 | 18.6922 | -352.6229 | 16.8381
12:55 | 5724 | 49.5643 | 202.7626 | 449.1534 | 451.2342 | -16.89 | -38.9282 | 11.9018 | 8.0039 | 2.6157 | 0.7364 | 3.1014 | -0.8837 | 12.2873 | 5.2403 | 0.6236 | 0.6663 | 0.9637 | 0.754 | -129.2071 | 1.6101 | 5.6996 | 1.9987 | -2.3342 | -0.8488 | 4.9014 |  | 4.31 | 0.8148 | 4.0058 | 3.3676 | 3.3378 | 1.0949 | 10.7926 | 14.2662 | 14.8471 | 11.1161 | 0.0001 | -0.0035 | 0.0012 | 0.004 | 0.0011 | 0.0002 | 0.0286 | -0.0168 | -0.0279 | -360.1711 | 17.3905 | -360.4019 | 17.5958 | -360.7497 | 18.2056 | -360.8512 | 17.5835 | -352.6506 | 18.7107 | -352.5952 | 16.7909
12:55 | 5725 | 49.6324 | 202.7515 | 449.1768 | 451.2997 | -16.9313 | -38.9136 | 11.8961 | 8.0779 | 2.5598 | 0.8057 | 3.0491 | -0.8474 | 12.2787 | 5.249 | 0.6231 | 0.6666 | 0.9648 | 0.7544 | -129.2357 | 1.7443 | 5.6915 | 1.9818 | -2.3472 | -0.9007 | 4.9806 |  | 4.3386 | 0.9029 | 4.0061 | 3.369 | 3.3335 | 1.0928 | 10.78 | 14.2646 | 14.8773 | 11.0815 | -0.0001 | -0.003 | 0.0009 | 0.0038 | 0.001 | -0.0008 | -0.0022 | -0.0137 | -0.0274 | -360.1188 | 17.4048 | -360.4389 | 17.6492 | -360.7773 | 18.1707 | -360.7743 | 17.5157 | -352.5767 | 18.7169 | -352.666 | 16.834
12:55 | 5726 | 49.5943 | 202.8169 | 449.1223 | 451.317 | -16.9349 | -39.1321 | 11.8241 | 8.0873 | 2.5229 | 0.7825 | 3.118 | -0.8929 | 12.2844 | 5.3281 | 0.6242 | 0.6677 | 0.9667 | 0.7547 | -129.2584 | 1.7318 | 5.7373 | 1.97 | -2.352 | -0.7521 | 4.9551 |  | 4.3766 | 0.9079 | 4.0064 | 3.3697 | 3.3342 | 1.0932 | 10.7626 | 14.2589 | 14.8494 | 11.0811 | -0.0004 | -0.0027 | -0.0004 | 0.0032 | 0.0005 | -0.0001 | 0.001 | -0.0018 | -0.0158 | -360.1404 | 17.3679 | -360.3742 | 17.6225 | -360.802 | 18.22 | -360.8574 | 17.5445 | -352.5736 | 18.682 | -352.549 | 16.8238
12:55 | 5727 | 49.5599 | 202.8014 | 449.2488 | 451.4257 | -16.9516 | -39.1096 | 11.6932 | 8.137 | 2.5481 | 0.7406 | 3.1479 | -0.8995 | 12.3298 | 5.4213 | 0.6235 | 0.666 | 0.967 | 0.7557 | -129.2303 | 1.6525 | 5.7188 | 2.1899 | -2.3212 | -0.8556 | 5.0188 |  | 4.3523 | 0.8233 | 4.0066 | 3.3723 | 3.3343 | 1.0929 | 10.7844 | 14.2756 | 14.886 | 11.1078 | 0.0002 | -0.0029 | 0.001 | 0.0046 | 0.0013 | -0.0004 | 0.001 | -0.0081 | -0.0002 | -360.1865 | 17.4007 | -360.4112 | 17.5978 | -360.7312 | 18.1789 | -360.7835 | 17.5588 | -352.626 | 18.7148 | -352.5767 | 16.795
12:55 | 5728 | 49.5558 | 202.7546 | 449.165 | 451.5192 | -16.9668 | -39.1123 | 11.7699 | 8.1367 | 2.5445 | 0.7033 | 3.1794 | -0.9433 | 12.2365 | 5.3377 | 0.6245 | 0.6657 | 0.9669 | 0.7535 | -129.2615 | 1.6418 | 5.7009 | 2.2228 | -2.3196 | -0.7524 | 5.0303 |  | 4.3124 | 0.8643 | 4.0056 | 3.3674 | 3.3331 | 1.0937 | 10.8041 | 14.2778 | 14.8587 | 11.1219 | 0.0002 | -0.0028 | 0.0008 | 0.0041 | 0.0008 | -0.0002 | -0.002 | -0.0069 | -0.0087 | -360.1342 | 17.374 | -360.4389 | 17.6533 | -360.8174 | 18.1953 | -360.802 | 17.5075 | -352.549 | 18.6984 | -352.6352 | 16.8525
12:55 | 5729 | 49.6248 | 202.7389 | 449.2463 | 451.5534 | -16.8806 | -39.0747 | 11.7959 | 8.0644 | 2.5193 | 0.7811 | 3.1147 | -0.8907 | 12.2327 | 5.3676 | 0.6241 | 0.6647 | 0.9664 | 0.7523 | -129.2886 | 1.6729 | 5.7172 | 2.2267 | -2.3051 | -0.6994 | 5.0321 |  | 4.3455 | 0.923 | 4.0067 | 3.372 | 3.3345 | 1.0952 | 10.7925 | 14.2953 | 14.8887 | 11.1215 | 0 | -0.0031 | 0.001 | 0.0037 | 0.0009 | -0.0006 | 0.0124 | -0.0227 | -0.0139 | -360.1219 | 17.3597 | -360.3496 | 17.5999 | -360.7497 | 18.2097 | -360.845 | 17.5609 | -352.5921 | 18.6717 | -352.5552 | 16.7991
12:55 | 5730 | 49.6732 | 202.8777 | 449.1771 | 451.5681 | -16.9544 | -38.998 | 11.777 | 8.0628 | 2.5032 | 0.7107 | 2.9993 | -0.8513 | 12.3343 | 5.3578 | 0.6227 | 0.6654 | 0.9631 | 0.7519 | -129.3651 | 1.6724 | 5.6932 | 2.0863 | -2.32 | -0.7736 | 4.9881 |  | 4.3556 | 0.9151 | 4.0063 | 3.3696 | 3.3314 | 1.0944 | 10.8214 | 14.2896 | 14.9245 | 11.1327 | 0 | -0.0019 | 0.0014 | 0.0043 | 0.0006 | -0.0008 | 0.0143 | 0.0129 | -0.0116 | -360.1711 | 17.411 | -360.4389 | 17.6245 | -360.7681 | 18.1687 | -360.762 | 17.5404 | -352.6136 | 18.7169 | -352.6198 | 16.8197
12:55 | 5731 | 49.7047 | 202.8852 | 449.2152 | 451.633 | -16.9591 | -39.0977 | 11.7198 | 8.0795 | 2.5006 | 0.5989 | 2.9945 | -0.9355 | 12.2849 | 5.2532 | 0.6241 | 0.6666 | 0.9616 | 0.7525 | -129.2676 | 1.6455 | 5.7278 | 2.1112 | -2.3202 | -0.7266 | 4.9482 |  | 4.4234 | 0.938 | 4.0061 | 3.369 | 3.3323 | 1.0948 | 10.7788 | 14.2751 | 14.8481 | 11.0973 | -0.0001 | -0.0027 | 0.0007 | 0.0033 | 0.0009 | -0.0004 | 0.0046 | -0.012 | -0.0135 | -360.1127 | 17.3679 | -360.4173 | 17.6307 | -360.8204 | 18.2138 | -360.7804 | 17.526 | -352.5152 | 18.6799 | -352.5952 | 16.8279
12:55 | 5732 | 49.6534 | 202.8891 | 449.2059 | 451.6867 | -16.9252 | -39.1627 | 11.9159 | 8.0903 | 2.5614 | 0.8251 | 3.0371 | -0.985 | 12.2182 | 5.202 | 0.6228 | 0.6659 | 0.9668 | 0.7538 | -129.2777 | 1.6857 | 5.6548 | 2.1779 | -2.3502 | -0.7092 | 4.9631 |  | 4.3705 | 0.8597 | 4.0072 | 3.3692 | 3.3333 | 1.0939 | 10.7591 | 14.2729 | 14.8059 | 11.0601 | 0.0002 | -0.0032 | 0.0006 | 0.0034 | 0.0008 | -0.0006 | 0.0102 | -0.0155 | -0.0103 | -360.1711 | 17.3761 | -360.3527 | 17.5896 | -360.7312 | 18.2036 | -360.8297 | 17.5671 | -352.6013 | 18.7025 | -352.5644 | 16.7868
12:55 | 5733 | 49.5789 | 202.9022 | 449.1275 | 451.635 | -16.8673 | -38.9811 | 11.9507 | 8.0856 | 2.4768 | 0.6661 | 3.0109 | -0.9844 | 12.1722 | 5.2356 | 0.6227 | 0.6657 | 0.9637 | 0.7517 | -129.2639 | 1.7113 | 5.7634 | 2.1224 | -2.3978 | -0.7039 | 4.997 |  | 4.3642 | 0.9258 | 4.0057 | 3.3681 | 3.3312 | 1.0937 | 10.7904 | 14.2693 | 14.8596 | 11.1147 | 0.0002 | -0.0027 | 0.0009 | 0.0041 | 0.0007 | -0.0003 | 0.0036 | 0.005 | 0.006 | -360.125 | 17.409 | -360.4666 | 17.6307 | -360.7866 | 18.1769 | -360.7497 | 17.5239 | -352.589 | 18.723 | -352.6413 | 16.8299
12:55 | 5734 | 49.6547 | 202.8256 | 449.1009 | 451.6746 | -16.8579 | -39.013 | 11.9347 | 8.0709 | 2.4077 | 0.6113 | 3.0082 | -1.0922 | 12.2536 | 5.2757 | 0.6239 | 0.663 | 0.9644 | 0.7531 | -129.2879 | 1.7199 | 5.7143 | 2.1561 | -2.3595 | -0.7171 | 4.9821 |  | 4.3358 | 0.9354 | 4.0066 | 3.369 | 3.334 | 1.0949 | 10.7638 | 14.2658 | 14.8497 | 11.0883 | -0.0003 | -0.0026 | 0.0007 | 0.004 | 0.0009 | -0.0008 | 0.0143 | -0.0004 | -0.0146 | -360.1188 | 17.3658 | -360.3896 | 17.6143 | -360.8112 | 18.2282 | -360.805 | 17.5301 | -352.5275 | 18.6799 | -352.5583 | 16.8258
12:55 | 5735 | 49.6484 | 202.7529 | 449.2047 | 451.7448 | -16.8347 | -38.9648 | 11.9115 | 8.0321 | 2.556 | 0.6895 | 3.0275 | -1.0823 | 12.1785 | 5.2361 | 0.6228 | 0.6653 | 0.9676 | 0.7532 | -129.2598 | 1.7237 | 5.719 | 2.1304 | -2.3219 | -0.6956 | 4.996 |  | 4.3258 | 0.9243 | 4.0072 | 3.369 | 3.3365 | 1.0934 | 10.7486 | 14.2569 | 14.8025 | 11.0666 | 0.0005 | -0.0018 | 0.001 | 0.0046 | 0.0006 | -0.0001 | 0.0161 | -0.019 | 0.0018 | -360.2235 | 17.3987 | -360.4081 | 17.5917 | -360.7497 | 18.181 | -360.8204 | 17.5712 | -352.6229 | 18.7148 | -352.5983 | 16.793
12:55 | 5736 | 49.7227 | 202.8133 | 449.2324 | 451.7747 | -16.8211 | -38.8329 | 11.914 | 8.0399 | 2.6081 | 0.8212 | 3.0992 | -1.0298 | 12.3074 | 5.2343 | 0.6225 | 0.6679 | 0.963 | 0.7537 | -129.3194 | 1.6658 | 5.6339 | 2.1123 | -2.4126 | -0.8636 | 4.9529 |  | 4.3472 | 0.8812 | 4.0075 | 3.3711 | 3.3352 | 1.0942 | 10.8146 | 14.3054 | 14.8679 | 11.1443 | 0.0003 | -0.003 | 0.001 | 0.004 | 0.0012 | -0.0003 | 0.0042 | -0.0029 | -0.0116 | -360.1158 | 17.3843 | -360.4635 | 17.6471 | -360.8143 | 18.1892 | -360.7558 | 17.5096 | -352.5798 | 18.7066 | -352.6475 | 16.8464
12:55 | 5737 | 49.655 | 202.8071 | 449.2403 | 451.84 | -16.8549 | -38.8406 | 11.9233 | 8.1086 | 2.6263 | 0.8083 | 3.1153 | -1.053 | 12.2806 | 5.3253 | 0.6219 | 0.6672 | 0.9639 | 0.7532 | -129.2569 | 1.7698 | 5.8282 | 2.1474 | -2.3959 | -0.7327 | 5.0031 |  | 4.2941 | 0.8734 | 4.0068 | 3.3696 | 3.3332 | 1.0937 | 10.818 | 14.3264 | 14.8846 | 11.124 | -0.0002 | -0.003 | 0.0008 | 0.0037 | 0.0008 | -0.0002 | 0.0047 | -0.0115 | -0.0023 | -360.1311 | 17.3658 | -360.365 | 17.6122 | -360.7989 | 18.2118 | -360.8297 | 17.5486 | -352.5706 | 18.6861 | -352.5736 | 16.7971
12:55 | 5738 | 49.6217 | 202.82 | 449.2147 | 451.7247 | -16.7976 | -38.849 | 12.0446 | 8.0099 | 2.6538 | 0.746 | 3.0018 | -0.9969 | 12.3232 | 5.3571 | 0.6236 | 0.6662 | 0.9676 | 0.753 | -129.2382 | 1.7167 | 5.7301 | 2.1168 | -2.4364 | -0.7755 | 4.9954 |  | 4.2984 | 0.7447 | 4.0058 | 3.3692 | 3.3342 | 1.0934 | 10.7903 | 14.3042 | 14.8723 | 11.1374 | -0.0004 | -0.0026 | 0.0014 | 0.0044 | 0.0005 | -0.0008 | 0.011 | -0.0121 | 0.0029 | -360.205 | 17.4172 | -360.4389 | 17.6081 | -360.7681 | 18.1707 | -360.7804 | 17.5486 | -352.6413 | 18.7271 | -352.6383 | 16.793
12:55 | 5739 | 49.5167 | 202.7538 | 449.1858 | 451.6887 | -16.8447 | -38.909 | 12.0806 | 7.9578 | 2.6557 | 0.8392 | 3.0006 | -0.957 | 12.2752 | 5.3754 | 0.622 | 0.6654 | 0.9641 | 0.7521 | -129.2615 | 1.7754 | 5.7046 | 2.0834 | -2.4696 | -0.8015 | 4.9967 |  | 4.3531 | 0.8793 | 4.0072 | 3.3695 | 3.3358 | 1.094 | 10.8019 | 14.3042 | 14.8723 | 11.1143 | -0.0003 | -0.0027 | 0.0012 | 0.0037 | 0.0007 | -0.0003 | 0.0053 | -0.0066 | -0.0083 | -360.1188 | 17.3884 | -360.4419 | 17.6574 | -360.8297 | 18.2097 | -360.805 | 17.5178 | -352.5429 | 18.6963 | -352.6136 | 16.832
12:55 | 5740 | 49.5612 | 202.8521 | 449.2149 | 451.6549 | -16.8582 | -38.7897 | 12.1018 | 8.032 | 2.5972 | 0.6225 | 3.0256 | -1.0154 | 12.1862 | 5.3576 | 0.6224 | 0.6661 | 0.9658 | 0.7532 | -129.2846 | 1.7922 | 5.7596 | 2.0705 | -2.462 | -0.7953 | 4.9013 |  | 4.2994 | 0.9427 | 4.0047 | 3.3666 | 3.3349 | 1.0946 | 10.7927 | 14.2775 | 14.8277 | 11.0937 | 0.0003 | -0.0031 | 0.0007 | 0.0037 | 0.0008 | -0.001 | 0.0047 | 0.0048 | -0.0288 | -360.1219 | 17.3617 | -360.3527 | 17.6061 | -360.7497 | 18.22 | -360.842 | 17.5547 | -352.5829 | 18.6902 | -352.549 | 16.7889
12:55 | 5741 | 49.5828 | 202.7498 | 449.1354 | 451.7123 | -16.8806 | -38.7614 | 12.1039 | 8.0616 | 2.5965 | 0.762 | 3.0036 | -1.0101 | 12.1892 | 5.3237 | 0.6228 | 0.6684 | 0.9689 | 0.753 | -129.3741 | 1.7108 | 5.731 | 2.0125 | -2.4393 | -0.7598 | 4.9181 |  | 4.3582 | 0.9285 | 4.0052 | 3.3685 | 3.3339 | 1.0942 | 10.795 | 14.2738 | 14.8688 | 11.1024 | -0.0001 | -0.0033 | 0.0007 | 0.004 | 0.0005 | -0.0005 | 0.0054 | -0.0142 | -0.0163 | -360.1527 | 17.409 | -360.4573 | 17.6369 | -360.7712 | 18.1789 | -360.765 | 17.5301 | -352.6167 | 18.7312 | -352.6444 | 16.8135
12:55 | 5742 | 49.5908 | 202.7614 | 449.1962 | 451.7249 | -16.797 | -38.7858 | 12.0804 | 8.0505 | 2.6518 | 0.7489 | 3.0428 | -1.0472 | 12.2267 | 5.2781 | 0.6238 | 0.6662 | 0.9621 | 0.7522 | -129.3092 | 1.7134 | 5.6427 | 1.9942 | -2.4331 | -0.8178 | 4.9924 |  | 4.3108 | 0.9006 | 4.0057 | 3.3672 | 3.3341 | 1.0949 | 10.7695 | 14.2834 | 14.8403 | 11.0645 | 0 | -0.0026 | 0.0008 | 0.0044 | 0.001 | -0.0002 | 0.0154 | -0.0034 | -0.0097 | -360.0973 | 17.372 | -360.4142 | 17.6553 | -360.805 | 18.2097 | -360.7989 | 17.5137 | -352.509 | 18.6943 | -352.6044 | 16.8238
12:55 | 5743 | 49.5471 | 202.7821 | 449.2344 | 451.7325 | -16.7958 | -38.8072 | 12.0237 | 8.0243 | 2.6429 | 0.7294 | 2.9727 | -0.9807 | 12.2842 | 5.3189 | 0.6241 | 0.6604 | 0.9645 | 0.7523 | -129.2343 | 1.6407 | 5.6071 | 2.0643 | -2.4346 | -0.8261 | 4.9904 |  | 4.3878 | 0.8796 | 4.0061 | 3.3673 | 3.3343 | 1.0942 | 10.7684 | 14.2761 | 14.8136 | 11.093 | -0.0003 | -0.0031 | 0.0009 | 0.0041 | 0.0008 | -0.0003 | 0.0139 | -0.0061 | -0.0257 | -360.1896 | 17.3802 | -360.365 | 17.6061 | -360.7404 | 18.2015 | -360.8635 | 17.565 | -352.6229 | 18.7004 | -352.5613 | 16.7889
12:55 | 5744 | 49.5652 | 202.7254 | 449.2389 | 451.6985 | -16.8836 | -38.8866 | 11.8543 | 7.9797 | 2.6136 | 0.6596 | 3.0439 | -1.0169 | 12.2535 | 5.2301 | 0.6221 | 0.6633 | 0.9635 | 0.7523 | -129.2239 | 1.6502 | 5.6296 | 2.0944 | -2.3815 | -0.7233 | 4.9995 |  | 4.282 | 0.8247 | 4.0068 | 3.3692 | 3.3298 | 1.0953 | 10.7984 | 14.2836 | 14.8761 | 11.093 | 0 | -0.0028 | 0.0008 | 0.004 | 0.0012 | 0.0001 | -0.0059 | 0.0056 | -0.002 | -360.1527 | 17.411 | -360.4327 | 17.6512 | -360.7743 | 18.1645 | -360.7497 | 17.5321 | -352.5767 | 18.7292 | -352.629 | 16.8156
12:55 | 5745 | 49.5975 | 202.7922 | 449.1736 | 451.8139 | -16.9011 | -38.8955 | 11.8862 | 7.9863 | 2.6066 | 0.8303 | 3.0122 | -1.062 | 12.1847 | 5.2018 | 0.6234 | 0.6645 | 0.9648 | 0.7534 | -129.2634 | 1.6954 | 5.6046 | 2.1418 | -2.3703 | -0.7458 | 4.9682 |  | 4.3299 | 0.8684 | 4.006 | 3.3682 | 3.3324 | 1.0935 | 10.8052 | 14.2965 | 14.8612 | 11.1052 | 0.0004 | -0.0027 | 0.0008 | 0.0037 | 0.001 | -0.0003 | 0.0137 | -0.0102 | -0.0147 | -360.0819 | 17.3699 | -360.4081 | 17.6451 | -360.8081 | 18.1871 | -360.8204 | 17.5301 | -352.5552 | 18.6881 | -352.5829 | 16.8217
12:55 | 5746 | 49.5832 | 202.7991 | 449.2329 | 451.8635 | -16.998 | -38.877 | 11.8116 | 7.9937 | 2.5568 | 0.7028 | 3.0155 | -0.9742 | 12.1992 | 5.3105 | 0.6239 | 0.6676 | 0.9672 | 0.7521 | -129.2211 | 1.6393 | 5.652 | 2.1205 | -2.3338 | -0.6758 | 5.011 |  | 4.3724 | 0.8428 | 4.0057 | 3.3706 | 3.3331 | 1.0947 | 10.7983 | 14.3011 | 14.8714 | 11.0984 | -0.0004 | -0.0028 | 0.0012 | 0.0039 | 0.0007 | 0.0001 | 0.0068 | -0.0061 | -0.0154 | -360.2142 | 17.3884 | -360.3958 | 17.6225 | -360.7404 | 18.1769 | -360.845 | 17.5568 | -352.6321 | 18.7045 | -352.589 | 16.7848
12:55 | 5747 | 49.5884 | 202.8419 | 449.2898 | 451.8364 | -16.8824 | -38.9305 | 11.7168 | 7.9874 | 2.4769 | 0.5806 | 3.0738 | -0.9644 | 12.2739 | 5.284 | 0.6237 | 0.6656 | 0.9647 | 0.7542 | -129.2009 | 1.6181 | 5.7325 | 2.045 | -2.422 | -0.784 | 5.0064 |  | 4.3772 | 0.8534 | 4.0055 | 3.3686 | 3.3323 | 1.094 | 10.8134 | 14.2987 | 14.8628 | 11.0731 | -0.0004 | -0.0023 | 0.0008 | 0.0035 | 0.001 | -0.0006 | 0.0053 | -0.0104 | -0.0245 | -360.1311 | 17.4069 | -360.4758 | 17.6594 | -360.7804 | 18.1481 | -360.7589 | 17.5178 | -352.586 | 18.7189 | -352.626 | 16.832
12:56 | 5748 | 49.6204 | 202.7367 | 449.2269 | 451.9777 | -16.8986 | -38.8677 | 11.7715 | 7.9491 | 2.5372 | 0.5735 | 3.12 | -0.9856 | 12.2304 | 5.3242 | 0.6237 | 0.6658 | 0.9693 | 0.7534 | -129.2282 | 1.5475 | 5.6392 | 2.0117 | -2.4376 | -0.7948 | 5.0314 |  | 4.4152 | 0.898 | 4.0059 | 3.3665 | 3.3331 | 1.0937 | 10.7788 | 14.2807 | 14.8354 | 11.0977 | 0 | -0.0031 | 0.0005 | 0.0039 | 0.0002 | -0.0005 | 0.0137 | -0.0046 | -0.0177 | -360.1435 | 17.3782 | -360.3927 | 17.6471 | -360.845 | 18.1974 | -360.8358 | 17.5383 | -352.5613 | 18.6922 | -352.5798 | 16.8156
12:56 | 5749 | 49.6447 | 202.7875 | 449.2063 | 451.9666 | -16.7987 | -38.9953 | 11.8717 | 7.9495 | 2.5556 | 0.4831 | 3.0921 | -1.0356 | 12.229 | 5.2458 | 0.6239 | 0.665 | 0.9671 | 0.7546 | -129.273 | 1.5288 | 5.6261 | 1.9597 | -2.4594 | -0.8283 | 4.9539 |  | 4.42 | 0.9384 | 4.0071 | 3.3712 | 3.3354 | 1.094 | 10.7995 | 14.2673 | 14.8764 | 11.1118 | 0.0001 | -0.0031 | 0.0004 | 0.004 | 0.0014 | -0.0006 | 0.0041 | 0.0041 | -0.0022 | -360.2111 | 17.4048 | -360.4235 | 17.6266 | -360.7281 | 18.1728 | -360.8327 | 17.5568 | -352.626 | 18.7148 | -352.5921 | 16.7848
12:56 | 5750 | 49.6895 | 202.7854 | 449.2884 | 452.0782 | -16.9168 | -38.8689 | 11.8871 | 7.9884 | 2.6156 | 0.6049 | 3.0875 | -1.0835 | 12.2591 | 5.22 | 0.6231 | 0.6675 | 0.9631 | 0.7536 | -129.2494 | 1.5144 | 5.7501 | 2.0257 | -2.4025 | -0.8224 | 4.9405 |  | 4.2921 | 0.8305 | 4.006 | 3.3725 | 3.3311 | 1.0936 | 10.796 | 14.2756 | 14.8802 | 11.1193 | 0.0002 | -0.0024 | 0.001 | 0.0043 | 0.0006 | -0.0007 | 0.0102 | -0.0077 | -0.0017 | -360.1465 | 17.4172 | -360.4635 | 17.6759 | -360.805 | 18.1584 | -360.7989 | 17.5363 | -352.6075 | 18.723 | -352.6567 | 16.832
12:56 | 5751 | 49.6352 | 202.7801 | 449.3022 | 452.0241 | -16.897 | -38.9665 | 11.8651 | 8.0726 | 2.6848 | 0.5839 | 3.0654 | -1.0691 | 12.3407 | 5.2619 | 0.6224 | 0.663 | 0.9636 | 0.7526 | -129.2666 | 1.4706 | 5.6428 | 1.9899 | -2.4474 | -0.8456 | 4.9065 |  | 4.3141 | 0.8655 | 4.0061 | 3.3658 | 3.3319 | 1.0946 | 10.7833 | 14.2742 | 14.872 | 11.1186 | -0.0001 | -0.0022 | 0.0012 | 0.0051 | 0.0009 | -0.0011 | 0.0179 | -0.0099 | -0.0144 | -360.1588 | 17.3864 | -360.3927 | 17.6512 | -360.8297 | 18.2015 | -360.8358 | 17.5671 | -352.5675 | 18.6984 | -352.5829 | 16.8094
12:56 | 5752 | 49.6406 | 202.7654 | 449.2478 | 452.0881 | -16.9219 | -39.004 | 11.862 | 7.9871 | 2.664 | 0.6188 | 3.0532 | -0.9826 | 12.3072 | 5.319 | 0.6245 | 0.6642 | 0.9651 | 0.7531 | -129.2444 | 1.7095 | 5.6439 | 1.966 | -2.396 | -0.8053 | 4.8737 |  | 4.3061 | 0.8299 | 4.0062 | 3.3663 | 3.332 | 1.0937 | 10.7764 | 14.2441 | 14.8301 | 11.054 | 0.0003 | -0.0028 | 0.0011 | 0.004 | 0.0006 | 0 | 0.0045 | -0.0104 | -0.0192 | -360.2204 | 17.4274 | -360.4727 | 17.6656 | -360.7835 | 18.1645 | -360.8235 | 17.5691 | -352.6321 | 18.7395 | -352.6506 | 16.8197
12:56 | 5753 | 49.7186 | 202.7372 | 449.2774 | 452.1357 | -16.9038 | -38.9889 | 11.7686 | 7.946 | 2.6681 | 0.6798 | 3.0857 | -1.1313 | 12.2512 | 5.2678 | 0.6242 | 0.6597 | 0.9622 | 0.753 | -129.2853 | 1.5522 | 5.6555 | 2.026 | -2.4664 | -0.8168 | 4.9006 |  | 4.2989 | 0.8777 | 4.0059 | 3.3676 | 3.3348 | 1.0946 | 10.7973 | 14.3054 | 14.8505 | 11.0981 | 0.0001 | -0.0032 | 0.0008 | 0.0037 | 0.0005 | -0.0006 | 0.014 | -0.0136 | -0.0132 | -360.1804 | 17.409 | -360.4573 | 17.6779 | -360.8481 | 18.1994 | -360.8235 | 17.5671 | -352.6013 | 18.7087 | -352.6321 | 16.8381
12:56 | 5754 | 49.6735 | 202.7596 | 449.118 | 452.0888 | -16.9978 | -39.0107 | 11.6307 | 7.91 | 2.6575 | 0.6944 | 3.0092 | -0.9882 | 12.2729 | 5.3411 | 0.623 | 0.6646 | 0.9637 | 0.753 | -129.4071 | 1.5936 | 5.5786 | 1.9699 | -2.4709 | -0.7681 | 4.8837 |  | 4.3675 | 0.9634 | 4.0065 | 3.368 | 3.3342 | 1.0933 | 10.7522 | 14.2542 | 14.8324 | 11.071 | -0.0001 | -0.0026 | 0.0011 | 0.0038 | 0.0007 | -0.0001 | 0.0194 | -0.0031 | -0.0118 | -360.1804 | 17.4151 | -360.4296 | 17.6594 | -360.8081 | 18.1933 | -360.8758 | 17.5835 | -352.6044 | 18.723 | -352.6075 | 16.8094
12:56 | 5755 | 49.6534 | 202.8421 | 449.0423 | 452.0585 | -16.996 | -38.9377 | 11.6621 | 7.9563 | 2.6658 | 0.6703 | 3.0002 | -0.9341 | 12.2565 | 5.3811 | 0.6228 | 0.6643 | 0.9677 | 0.7536 | -129.2423 | 1.5804 | 5.601 | 2.0175 | -2.4017 | -0.8332 | 4.9091 |  | 4.4425 | 1.0528 | 4.0077 | 3.3685 | 3.3322 | 1.0945 | 10.7753 | 14.2718 | 14.8577 | 11.0645 | -0.0004 | -0.0027 | 0.0011 | 0.0043 | 0.0008 | -0.0003 | 0.0077 | -0.0169 | -0.0082 | -360.2358 | 17.411 | -360.4727 | 17.6738 | -360.7989 | 18.1953 | -360.842 | 17.5773 | -352.6106 | 18.7312 | -352.6598 | 16.8299
12:56 | 5756 | 49.662 | 202.7899 | 449.2277 | 452.1568 | -17.0161 | -38.933 | 11.7912 | 7.9494 | 2.6318 | 0.6514 | 3.0187 | -0.9596 | 12.2418 | 5.3893 | 0.6239 | 0.6683 | 0.9646 | 0.7539 | -129.3077 | 1.6303 | 5.6691 | 2.0226 | -2.3603 | -0.9051 | 4.9077 |  | 4.4205 | 0.9616 | 4.0062 | 3.3708 | 3.3318 | 1.0936 | 10.7869 | 14.2889 | 14.8729 | 11.1057 | 0.0001 | -0.0028 | 0.0009 | 0.0041 | 0.0005 | -0.0006 | 0.0102 | -0.0112 | -0.0357 | -360.1804 | 17.4131 | -360.4542 | 17.6656 | -360.8174 | 18.1994 | -360.842 | 17.5814 | -352.6198 | 18.7128 | -352.6321 | 16.832
12:56 | 5757 | 49.6447 | 202.7568 | 449.1807 | 452.0967 | -16.9688 | -38.9458 | 11.8385 | 8.0657 | 2.6382 | 0.6967 | 2.8025 | -0.9833 | 12.2579 | 5.2766 | 0.6234 | 0.667 | 0.9639 | 0.7538 | -129.3405 | 1.625 | 5.6496 | 2.0281 | -2.3118 | -0.8046 | 4.9527 |  | 4.3977 | 0.9797 | 4.0069 | 3.3693 | 3.3325 | 1.0952 | 10.7995 | 14.2963 | 14.8833 | 11.0941 | 0.0002 | -0.0031 | 0.0007 | 0.0046 | 0.001 | 0 | -0.0069 | -0.0055 | -0.0275 | -360.2081 | 17.4151 | -360.4296 | 17.6718 | -360.8389 | 18.1953 | -360.8727 | 17.5855 | -352.6106 | 18.7066 | -352.6567 | 16.8299
12:56 | 5758 | 49.5914 | 202.8061 | 449.3348 | 452.1512 | -16.9977 | -39.0198 | 11.669 | 7.9925 | 2.5437 | 0.672 | 2.7438 | -0.9747 | 12.3159 | 5.2447 | 0.6236 | 0.666 | 0.9646 | 0.7509 | -129.2279 | 1.6244 | 5.7114 | 1.9376 | -2.3147 | -0.8212 | 4.8831 |  | 4.3804 | 0.8791 | 4.0068 | 3.3701 | 3.3354 | 1.0931 | 10.7731 | 14.2461 | 14.8123 | 11.1035 | -0.0003 | -0.003 | 0.0006 | 0.0035 | 0.0009 | -0.0009 | 0.0183 | -0.0022 | -0.009 | -360.2327 | 17.4356 | -360.4758 | 17.6553 | -360.8235 | 18.1892 | -360.8358 | 17.5896 | -352.626 | 18.7312 | -352.6383 | 16.8381
12:56 | 5759 | 49.6328 | 202.7831 | 449.2467 | 452.1489 | -16.9825 | -39.0543 | 11.7034 | 7.9536 | 2.4684 | 0.6888 | 2.7161 | -0.937 | 12.2714 | 5.3019 | 0.6234 | 0.6653 | 0.9641 | 0.7523 | -129.2494 | 1.5339 | 5.6544 | 1.9122 | -2.319 | -0.7741 | 4.8901 |  | 4.4577 | 0.909 | 4.0056 | 3.3713 | 3.3298 | 1.0932 | 10.8042 | 14.295 | 14.8692 | 11.1222 | -0.0003 | -0.0026 | 0.0003 | 0.0035 | 0.0006 | -0.0003 | -0.008 | -0.0227 | -0.0199 | -360.1619 | 17.4131 | -360.4635 | 17.6779 | -360.8543 | 18.2118 | -360.8635 | 17.5629 | -352.5921 | 18.7169 | -352.6752 | 16.8484
12:56 | 5760 | 49.5743 | 202.7658 | 449.0871 | 452.2075 | -16.8747 | -38.9002 | 11.8533 | 7.958 | 2.4562 | 0.5911 | 2.7564 | -1.0281 | 12.2968 | 5.3017 | 0.6238 | 0.6685 | 0.9658 | 0.7522 | -129.2996 | 1.4519 | 5.5908 | 2.0387 | -2.3094 | -0.7751 | 4.9509 |  | 4.4146 | 0.9044 | 4.0055 | 3.3688 | 3.3322 | 1.0945 | 10.8077 | 14.281 | 14.8607 | 11.1028 | 0.0001 | -0.0031 | 0.0009 | 0.0035 | 0.0011 | -0.0007 | 0.0345 | -0.0098 | 0 | -360.2265 | 17.4213 | -360.4419 | 17.6533 | -360.8235 | 18.1953 | -360.8789 | 17.6122 | -352.669 | 18.7169 | -352.6383 | 16.8217
12:56 | 5761 | 49.6474 | 202.8318 | 449.2176 | 452.333 | -16.8264 | -38.7346 | 11.9301 | 8.0088 | 2.5125 | 0.6324 | 2.824 | -0.9508 | 12.189 | 5.3035 | 0.6235 | 0.6616 | 0.9649 | 0.7534 | -129.2759 | 1.5052 | 5.4592 | 2.1035 | -2.3089 | -0.7878 | 4.9533 |  | 4.4231 | 0.7816 | 4.0066 | 3.3689 | 3.3327 | 1.0948 | 10.8101 | 14.2542 | 14.8382 | 11.1172 | 0.0002 | -0.003 | 0.0002 | 0.0031 | 0.0005 | -0.0001 | 0.005 | -0.0198 | -0.0143 | -360.1927 | 17.4192 | -360.4789 | 17.6902 | -360.8635 | 18.181 | -360.8174 | 17.5773 | -352.6413 | 18.7353 | -352.6813 | 16.8546
12:56 | 5762 | 49.6156 | 202.7781 | 449.3386 | 452.2454 | -16.8378 | -38.9887 | 11.9902 | 7.9864 | 2.595 | 0.7357 | 2.87 | -0.9002 | 12.2441 | 5.3387 | 0.624 | 0.6645 | 0.9675 | 0.7518 | -129.3049 | 1.4753 | 5.5036 | 2.084 | -2.3789 | -0.7162 | 4.8737 |  | 4.377 | 0.8908 | 4.0057 | 3.3669 | 3.3342 | 1.0942 | 10.7787 | 14.2581 | 14.8039 | 11.0793 | -0.0001 | -0.0028 | 0.001 | 0.0039 | 0.0013 | -0.0006 | 0.0059 | -0.0097 | -0.0163 | -360.1835 | 17.3823 | -360.3989 | 17.6512 | -360.842 | 18.2344 | -360.8974 | 17.5855 | -352.6352 | 18.6902 | -352.6013 | 16.832
12:56 | 5763 | 49.5897 | 202.838 | 449.3293 | 452.3027 | -16.7161 | -38.9068 | 12.0399 | 8.0384 | 2.516 | 0.7533 | 2.8887 | -0.9136 | 12.1925 | 5.4115 | 0.6231 | 0.6651 | 0.9655 | 0.7514 | -129.2978 | 1.5435 | 5.5119 | 1.9904 | -2.4298 | -0.7886 | 4.8367 |  | 4.4093 | 0.8444 | 4.0063 | 3.3666 | 3.3328 | 1.0942 | 10.7856 | 14.2997 | 14.8863 | 11.0977 | -0.0005 | -0.0026 | 0.0013 | 0.0044 | 0.0006 | -0.0004 | 0.0061 | -0.0068 | -0.0096 | -360.2388 | 17.4397 | -360.4881 | 17.6533 | -360.8112 | 18.1707 | -360.8358 | 17.5937 | -352.666 | 18.7415 | -352.6783 | 16.8258
12:56 | 5764 | 49.6298 | 202.772 | 449.3036 | 452.2763 | -16.7653 | -38.9883 | 11.9772 | 8.0628 | 2.551 | 0.6912 | 2.8666 | -0.9011 | 12.2858 | 5.3646 | 0.6227 | 0.6639 | 0.9656 | 0.7513 | -129.3206 | 1.4805 | 5.5335 | 1.9902 | -2.4358 | -0.8291 | 4.8487 |  | 4.4319 | 0.835 | 4.0052 | 3.3684 | 3.3285 | 1.0946 | 10.8007 | 14.3091 | 14.873 | 11.1183 | 0 | -0.0028 | 0.0006 | 0.0042 | 0.0011 | -0.0006 | 0.0124 | -0.0054 | -0.0195 | -360.1188 | 17.3946 | -360.4512 | 17.6902 | -360.8943 | 18.22 | -360.845 | 17.5629 | -352.5706 | 18.6881 | -352.6475 | 16.8587
12:56 | 5765 | 49.7134 | 202.8849 | 449.3332 | 452.4163 | -16.7451 | -38.9278 | 11.9831 | 8.1193 | 2.5557 | 0.6841 | 2.9256 | -0.9273 | 12.2997 | 5.3921 | 0.6229 | 0.6668 | 0.9663 | 0.7533 | -129.2675 | 1.5107 | 5.5589 | 1.9898 | -2.3894 | -0.7851 | 4.9087 |  | 4.4382 | 0.8425 | 4.0069 | 3.3682 | 3.3364 | 1.0959 | 10.7949 | 14.2627 | 14.8662 | 11.1013 | -0.0003 | -0.0032 | 0.0011 | 0.0045 | 0.0005 | -0.0002 | 0.0127 | -0.0015 | -0.0037 | -360.245 | 17.4048 | -360.405 | 17.6348 | -360.7773 | 18.2036 | -360.9158 | 17.6184 | -352.669 | 18.7066 | -352.6106 | 16.8012
12:56 | 5766 | 49.6228 | 202.8625 | 449.3958 | 452.4208 | -16.779 | -38.8975 | 11.9822 | 8.1553 | 2.6111 | 0.7292 | 2.8939 | -0.8984 | 12.3914 | 5.4174 | 0.623 | 0.661 | 0.9656 | 0.7529 | -129.2099 | 1.51 | 5.549 | 1.841 | -2.3806 | -0.7996 | 4.8692 |  | 4.3504 | 0.8532 | 4.0068 | 3.3635 | 3.3311 | 1.0937 | 10.7776 | 14.2567 | 14.8651 | 11.0901 | 0 | -0.0027 | 0.001 | 0.0041 | 0.001 | -0.0003 | 0.0155 | 0.0013 | 0.0024 | -360.205 | 17.4377 | -360.5404 | 17.6759 | -360.845 | 18.1769 | -360.7927 | 17.5609 | -352.6321 | 18.7415 | -352.6998 | 16.8464
12:56 | 5767 | 49.7284 | 202.9256 | 449.3844 | 452.5277 | -16.7608 | -38.8442 | 12.023 | 8.1929 | 2.5539 | 0.6798 | 2.8756 | -0.9889 | 12.3127 | 5.3831 | 0.6246 | 0.6622 | 0.9657 | 0.7522 | -129.2437 | 1.4777 | 5.4942 | 1.8736 | -2.3571 | -0.7402 | 4.9136 |  | 4.3883 | 0.7945 | 4.0061 | 3.3665 | 3.329 | 1.0933 | 10.7879 | 14.2674 | 14.8601 | 11.1056 | -0.0003 | -0.003 | 0.0007 | 0.004 | 0.0009 | -0.0001 | 0.0079 | -0.018 | -0.0189 | -360.1619 | 17.3925 | -360.4358 | 17.6759 | -360.8666 | 18.2282 | -360.8881 | 17.5814 | -352.6013 | 18.6943 | -352.626 | 16.8381
12:56 | 5768 | 49.7251 | 202.9127 | 449.3506 | 452.4998 | -16.7279 | -38.7401 | 11.9865 | 8.1338 | 2.4707 | 0.6411 | 2.7888 | -0.9945 | 12.2387 | 5.3233 | 0.6243 | 0.6644 | 0.9704 | 0.7531 | -129.2921 | 1.409 | 5.5778 | 1.7538 | -2.4579 | -0.8706 | 4.8318 |  | 4.4331 | 0.853 | 4.0056 | 3.3645 | 3.3312 | 1.092 | 10.7856 | 14.265 | 14.7995 | 11.115 | 0 | -0.0028 | 0.0008 | 0.0035 | 0.0009 | -0.0004 | 0.0307 | -0.0096 | -0.0028 | -360.2265 | 17.4356 | -360.4542 | 17.6348 | -360.7773 | 18.1789 | -360.8758 | 17.6061 | -352.6506 | 18.7292 | -352.6106 | 16.7909
12:56 | 5769 | 49.7912 | 202.9073 | 449.3407 | 452.4765 | -16.7432 | -38.865 | 12.0226 | 8.1061 | 2.5076 | 0.7138 | 2.8712 | -0.966 | 12.2813 | 5.2969 | 0.6229 | 0.6665 | 0.9652 | 0.7523 | -129.2699 | 1.4888 | 5.526 | 1.7583 | -2.4249 | -0.8177 | 4.8665 |  | 4.4265 | 0.9457 | 4.0053 | 3.3664 | 3.3325 | 1.0923 | 10.7707 | 14.2498 | 14.829 | 11.0833 | 0.0003 | -0.003 | 0.0007 | 0.0033 | 0.0013 | 0.0001 | 0.0235 | -0.007 | -0.0078 | -360.1773 | 17.4151 | -360.4881 | 17.6841 | -360.8758 | 18.1871 | -360.8081 | 17.5588 | -352.6075 | 18.7107 | -352.6813 | 16.8484
12:56 | 5770 | 49.6619 | 202.9236 | 449.2498 | 452.3905 | -16.9944 | -38.9878 | 11.9073 | 8.1458 | 2.4954 | 0.6625 | 2.8821 | -0.8822 | 12.2554 | 5.3905 | 0.624 | 0.6681 | 0.9649 | 0.751 | -129.3036 | 1.5176 | 5.6078 | 1.875 | -2.3499 | -0.9135 | 4.8984 |  | 4.3889 | 0.9267 | 4.0073 | 3.3664 | 3.3337 | 1.0928 | 10.7939 | 14.2785 | 14.828 | 11.0952 | 0 | -0.0029 | 0.0008 | 0.0035 | 0.0008 | -0.0005 | 0.0243 | 0.0043 | -0.0155 | -360.1588 | 17.3946 | -360.4142 | 17.6533 | -360.8266 | 18.2077 | -360.885 | 17.5876 | -352.6044 | 18.684 | -352.5952 | 16.8115
12:56 | 5771 | 49.7795 | 202.9222 | 449.3794 | 452.4557 | -16.9629 | -38.9635 | 11.8766 | 8.1203 | 2.494 | 0.6989 | 2.8522 | -0.9121 | 12.2762 | 5.3371 | 0.6231 | 0.6651 | 0.9672 | 0.753 | -129.2099 | 1.7065 | 5.6667 | 1.9261 | -2.4885 | -0.8109 | 4.8477 |  | 4.4302 | 0.8885 | 4.008 | 3.3632 | 3.3297 | 1.0945 | 10.8329 | 14.3014 | 14.9082 | 11.1496 | 0 | -0.0022 | 0.0012 | 0.0045 | 0.0008 | -0.0005 | 0.021 | -0.0063 | -0.0101 | -360.2204 | 17.4315 | -360.4542 | 17.6615 | -360.7773 | 18.1563 | -360.7927 | 17.5835 | -352.6383 | 18.7251 | -352.6383 | 16.7971
12:56 | 5772 | 49.8355 | 202.902 | 449.3045 | 452.413 | -17.0276 | -39.0815 | 11.8187 | 8.1831 | 2.5383 | 0.7314 | 2.8875 | -0.938 | 12.3177 | 5.4519 | 0.6222 | 0.6657 | 0.9706 | 0.7524 | -129.303 | 1.6437 | 5.626 | 1.8595 | -2.4558 | -0.857 | 4.8613 |  | 4.4128 | 0.9086 | 4.0087 | 3.3683 | 3.3331 | 1.094 | 10.8064 | 14.2859 | 14.8615 | 11.1125 | 0.0001 | -0.0026 | 0.0005 | 0.0044 | 0.0008 | -0.0002 | 0.0351 | -0.0081 | 0.0175 | -360.1342 | 17.4069 | -360.4881 | 17.6779 | -360.8574 | 18.1912 | -360.802 | 17.5691 | -352.5952 | 18.6963 | -352.6506 | 16.8361
12:56 | 5773 | 49.8487 | 202.8647 | 449.3732 | 452.3868 | -16.8848 | -38.9583 | 11.902 | 8.2159 | 2.4994 | 0.7111 | 2.856 | -0.9589 | 12.2313 | 5.3698 | 0.6247 | 0.6638 | 0.9669 | 0.7522 | -129.3045 | 1.618 | 5.5492 | 1.7748 | -2.4446 | -0.759 | 4.9173 |  | 4.4335 | 0.8458 | 4.008 | 3.3662 | 3.3313 | 1.095 | 10.7752 | 14.2662 | 14.8298 | 11.0872 | 0.0005 | -0.0027 | 0.0009 | 0.0042 | 0.001 | -0.0009 | 0.0023 | -0.0137 | -0.0123 | -360.2358 | 17.4069 | -360.4266 | 17.641 | -360.7989 | 18.1912 | -360.8604 | 17.5937 | -352.5983 | 18.6963 | -352.5675 | 16.8032
12:56 | 5774 | 49.8189 | 202.9271 | 449.2907 | 452.4595 | -16.871 | -38.9395 | 11.8971 | 8.2472 | 2.5349 | 0.6973 | 2.8385 | -1.0325 | 12.2109 | 5.3813 | 0.6246 | 0.6623 | 0.9707 | 0.7525 | -129.1882 | 1.6227 | 5.6238 | 1.7076 | -2.5213 | -0.9216 | 4.891 |  | 4.3522 | 0.7892 | 4.0076 | 3.3675 | 3.3331 | 1.0935 | 10.8076 | 14.2813 | 14.8513 | 11.102 | 0.0004 | -0.0026 | 0.0008 | 0.0041 | 0.0008 | -0.0001 | 0.0079 | -0.0022 | 0.008 | -360.165 | 17.4069 | -360.445 | 17.6615 | -360.8358 | 18.1769 | -360.8081 | 17.5671 | -352.6044 | 18.7128 | -352.626 | 16.8197
12:56 | 5775 | 49.7853 | 202.8708 | 449.3761 | 452.388 | -16.5082 | -38.9293 | 11.894 | 8.2187 | 2.5383 | 0.6382 | 2.8463 | -1.0043 | 12.1953 | 5.3645 | 0.6238 | 0.663 | 0.9636 | 0.7499 | -129.2605 | 1.4925 | 5.5895 | 1.8322 | -2.4977 | -0.786 | 4.8592 |  | 4.3871 | 0.853 | 4.0075 | 3.3681 | 3.3311 | 1.0954 | 10.7546 | 14.2506 | 14.8283 | 11.0735 | -0.0005 | -0.0025 | 0.0003 | 0.0035 | 0.0007 | -0.0011 | 0.0318 | -0.0188 | 0.0103 | -360.1527 | 17.3843 | -360.405 | 17.6369 | -360.7866 | 18.183 | -360.8635 | 17.5732 | -352.586 | 18.6779 | -352.5921 | 16.7991
12:56 | 5776 | 49.8702 | 203.0369 | 449.4069 | 452.5056 | -16.6431 | -39.0792 | 11.8278 | 8.1966 | 2.5816 | 0.8104 | 2.875 | -0.9926 | 12.1946 | 5.3705 | 0.6246 | 0.6635 | 0.9663 | 0.7521 | -129.2485 | 1.5717 | 5.5907 | 2.0187 | -2.4854 | -0.8601 | 4.9541 |  | 4.4036 | 0.8838 | 4.0079 | 3.3676 | 3.3349 | 1.0935 | 10.788 | 14.244 | 14.829 | 11.089 | 0.0002 | -0.0025 | 0.0009 | 0.0037 | 0.0007 | -0.0002 | 0.0258 | 0.0012 | -0.0125 | -360.1711 | 17.411 | -360.4358 | 17.6451 | -360.7897 | 18.1769 | -360.8358 | 17.5773 | -352.5952 | 18.6984 | -352.6044 | 16.8032
12:56 | 5777 | 49.8542 | 202.9676 | 449.4315 | 452.4578 | -16.6626 | -39.206 | 11.7802 | 8.1463 | 2.5482 | 0.8028 | 2.807 | -0.9593 | 12.1464 | 5.333 | 0.6244 | 0.6648 | 0.9658 | 0.7531 | -129.2796 | 1.6103 | 5.6047 | 1.9817 | -2.5498 | -0.8431 | 4.8981 |  | 4.3692 | 0.8374 | 4.0069 | 3.3681 | 3.3338 | 1.0934 | 10.7937 | 14.2733 | 14.8554 | 11.0764 | 0.0005 | -0.0028 | 0.0017 | 0.0041 | 0.001 | -0.0004 | 0.017 | 0.0097 | -0.0021 | -360.1742 | 17.3946 | -360.4142 | 17.6451 | -360.7958 | 18.1666 | -360.805 | 17.5629 | -352.5736 | 18.7004 | -352.5983 | 16.8135
12:56 | 5778 | 49.8018 | 202.9338 | 449.334 | 452.4892 | -16.6708 | -39.2845 | 11.7246 | 8.1049 | 2.4388 | 0.8495 | 2.8315 | -0.8687 | 12.1231 | 5.3061 | 0.6232 | 0.6632 | 0.9666 | 0.7507 | -129.2163 | 1.6227 | 5.7475 | 2.0677 | -2.5602 | -0.9069 | 4.8939 |  | 4.3618 | 0.8193 | 4.0072 | 3.3703 | 3.3347 | 1.0941 | 10.7731 | 14.2576 | 14.7891 | 11.0631 | 0.0005 | -0.0028 | 0.0008 | 0.0037 | 0.0005 | -0.0003 | 0.0055 | -0.0078 | -0.0164 | -360.1496 | 17.3946 | -360.4296 | 17.6512 | -360.805 | 18.1851 | -360.8235 | 17.565 | -352.586 | 18.6963 | -352.589 | 16.8135
12:56 | 5779 | 49.9197 | 203.0296 | 449.414 | 452.51 | -16.5459 | -39.1886 | 11.7827 | 8.099 | 2.409 | 0.7963 | 2.8215 | -0.9517 | 12.1286 | 5.2235 | 0.6248 | 0.6686 | 0.9664 | 0.7517 | -129.2414 | 1.5297 | 5.684 | 2.0506 | -2.5404 | -0.9538 | 4.8301 |  | 4.3516 | 0.8149 | 4.0075 | 3.3676 | 3.3283 | 1.0944 | 10.796 | 14.2756 | 14.8918 | 11.0962 | -0.0002 | -0.0025 | 0.0012 | 0.0046 | 0.0012 | 0 | 0.0152 | -0.0085 | -0.0148 | -360.1711 | 17.3966 | -360.4512 | 17.6369 | -360.7773 | 18.1687 | -360.8174 | 17.5753 | -352.5921 | 18.6943 | -352.626 | 16.8094
12:56 | 5780 | 49.9248 | 203.061 | 449.5313 | 452.4766 | -16.6931 | -39.3065 | 11.764 | 8.0576 | 2.4183 | 0.8159 | 2.7657 | -0.9585 | 12.1957 | 5.2741 | 0.6239 | 0.6665 | 0.964 | 0.7525 | -129.3577 | 1.6045 | 5.5445 | 2.0392 | -2.5825 | -0.9169 | 4.8299 |  | 4.4479 | 0.8365 | 4.0061 | 3.3711 | 3.3316 | 1.0927 | 10.8226 | 14.3023 | 14.8959 | 11.163 | 0 | -0.0026 | 0.0007 | 0.0041 | 0.0006 | -0.0003 | 0.0061 | -0.0137 | -0.009 | -360.1619 | 17.3946 | -360.4542 | 17.6677 | -360.8174 | 18.1728 | -360.805 | 17.5629 | -352.586 | 18.7066 | -352.6567 | 16.8156
12:56 | 5781 | 49.8976 | 202.9447 | 449.4763 | 452.4802 | -16.6975 | -39.3043 | 11.696 | 8.0542 | 2.4116 | 0.7854 | 2.8414 | -1.0024 | 12.1822 | 5.1982 | 0.6233 | 0.6632 | 0.9681 | 0.7512 | -129.2717 | 1.653 | 5.5524 | 1.955 | -2.5894 | -1.0046 | 4.8263 |  | 4.4748 | 0.9235 | 4.0055 | 3.3693 | 3.3315 | 1.093 | 10.7915 | 14.2764 | 14.8794 | 11.0865 | 0.0002 | -0.0032 | 0.0005 | 0.0039 | 0.0013 | -0.0001 | 0.0051 | -0.0013 | -0.0114 | -360.1711 | 17.3864 | -360.4081 | 17.6574 | -360.8297 | 18.1912 | -360.8358 | 17.5671 | -352.5798 | 18.6779 | -352.6013 | 16.8032
12:56 | 5782 | 49.9126 | 202.9724 | 449.3889 | 452.5339 | -16.5771 | -39.1837 | 11.7691 | 8.0409 | 2.4208 | 0.7519 | 2.8935 | -1.0681 | 12.2658 | 5.2348 | 0.6238 | 0.667 | 0.9666 | 0.7515 | -129.2329 | 1.6981 | 5.6747 | 2.0238 | -2.5039 | -0.9042 | 4.7878 |  | 4.3645 | 0.8721 | 4.0061 | 3.3692 | 3.3326 | 1.0929 | 10.7787 | 14.2637 | 14.8318 | 11.0912 | -0.0001 | -0.0029 | 0.0009 | 0.0041 | 0.0015 | -0.0001 | 0.0052 | -0.0087 | -0.0015 | -360.1865 | 17.4233 | -360.4573 | 17.643 | -360.7897 | 18.1789 | -360.802 | 17.5855 | -352.6136 | 18.7189 | -352.6475 | 16.8074
12:56 | 5783 | 49.8268 | 202.9544 | 449.3477 | 452.5179 | -16.5633 | -39.1821 | 11.752 | 7.9978 | 2.3606 | 0.7578 | 2.9047 | -1.0218 | 12.2072 | 5.1825 | 0.6242 | 0.6646 | 0.9651 | 0.7527 | -129.2645 | 1.6545 | 5.6922 | 1.9909 | -2.5494 | -0.9168 | 4.7594 |  | 4.432 | 0.9817 | 4.0067 | 3.37 | 3.3352 | 1.0942 | 10.7984 | 14.2892 | 14.8692 | 11.1338 | -0.0003 | -0.0028 | 0.0002 | 0.0031 | 0.0005 | -0.0004 | -0.0066 | -0.0096 | -0.0099 | -360.125 | 17.411 | -360.4789 | 17.6779 | -360.8666 | 18.1912 | -360.8358 | 17.5609 | -352.5767 | 18.7128 | -352.6352 | 16.832
12:56 | 5784 | 49.794 | 202.889 | 449.2382 | 452.4268 | -16.5369 | -38.9584 | 11.7205 | 7.9434 | 2.318 | 0.6829 | 2.9264 | -0.9264 | 12.251 | 5.1606 | 0.6239 | 0.6622 | 0.9622 | 0.7519 | -129.2866 | 1.6653 | 5.6402 | 2.02 | -2.4579 | -1.064 | 4.8136 |  | 4.4366 | 0.933 | 4.0053 | 3.3684 | 3.333 | 1.0941 | 10.7535 | 14.2492 | 14.8074 | 11.0732 | -0.0007 | -0.003 | 0.0004 | 0.0033 | 0.0006 | -0.0013 | 0.0217 | -0.0053 | -0.0033 | -360.1835 | 17.3905 | -360.3958 | 17.6574 | -360.8327 | 18.2056 | -360.885 | 17.5896 | -352.6198 | 18.6963 | -352.6044 | 16.8197
12:56 | 5785 | 49.7866 | 202.8049 | 449.3354 | 452.4469 | -16.4238 | -38.8112 | 11.8857 | 7.9118 | 2.2859 | 0.6401 | 2.9277 | -1.0802 | 12.191 | 5.1019 | 0.6245 | 0.6659 | 0.961 | 0.7533 | -129.3095 | 1.695 | 5.5972 | 2.0245 | -2.4738 | -0.8567 | 4.7527 |  | 4.3841 | 1.0001 | 4.0079 | 3.3669 | 3.3304 | 1.0935 | 10.7856 | 14.2766 | 14.8458 | 11.0861 | 0.0003 | -0.0029 | 0.0013 | 0.004 | 0.0004 | -0.0003 | 0.0054 | -0.0029 | 0.0013 | -360.2142 | 17.4459 | -360.4758 | 17.6718 | -360.8297 | 18.181 | -360.8389 | 17.5917 | -352.6598 | 18.7415 | -352.6537 | 16.8156
12:56 | 5786 | 49.8352 | 202.8835 | 449.3166 | 452.4971 | -16.4779 | -38.7623 | 11.8623 | 7.9217 | 2.2818 | 0.742 | 2.939 | -0.9834 | 12.2997 | 5.112 | 0.6248 | 0.6657 | 0.963 | 0.7532 | -129.2916 | 1.7065 | 5.5214 | 1.8643 | -2.5194 | -0.9897 | 4.7181 |  | 4.2654 | 0.8667 | 4.0061 | 3.367 | 3.3348 | 1.0952 | 10.7892 | 14.297 | 14.8698 | 11.0963 | -0.0002 | -0.0034 | 0.0006 | 0.0038 | 0.0009 | -0.0007 | 0.0101 | -0.0119 | -0.022 | -360.1219 | 17.4131 | -360.4881 | 17.6882 | -360.8604 | 18.2097 | -360.8327 | 17.5671 | -352.6013 | 18.723 | -352.6813 | 16.8484
12:56 | 5787 | 49.8325 | 202.9176 | 449.3308 | 452.4593 | -16.5179 | -38.8709 | 11.7984 | 7.8678 | 2.2992 | 0.6851 | 2.9264 | -1.0622 | 12.1848 | 5.0801 | 0.6238 | 0.6629 | 0.961 | 0.7523 | -129.3264 | 1.7279 | 5.6256 | 1.893 | -2.6553 | -0.863 | 4.7413 |  | 4.3315 | 0.8759 | 4.0067 | 3.3687 | 3.3322 | 1.0944 | 10.7937 | 14.2558 | 14.8659 | 11.0767 | -0.0001 | -0.0025 | 0.0011 | 0.0044 | 0.0004 | -0.0002 | 0.0107 | -0.0073 | -0.0085 | -360.1958 | 17.3987 | -360.4235 | 17.6533 | -360.8235 | 18.2118 | -360.9004 | 17.604 | -352.6352 | 18.6963 | -352.6106 | 16.8094
12:56 | 5788 | 49.8221 | 202.8095 | 449.3256 | 452.5099 | -16.5552 | -38.9063 | 11.8054 | 7.9197 | 2.3936 | 0.7267 | 2.8734 | -0.9781 | 12.1072 | 5.0628 | 0.6241 | 0.6658 | 0.9641 | 0.7519 | -129.2737 | 1.6815 | 5.5599 | 1.9273 | -2.4944 | -0.8356 | 4.8053 |  | 4.3673 | 0.8359 | 4.0072 | 3.3681 | 3.3333 | 1.0952 | 10.8156 | 14.3072 | 14.9082 | 11.1381 | 0 | -0.0025 | 0.0013 | 0.0046 | 0.0012 | -0.0005 | 0.0171 | -0.0062 | -0.0134 | -360.2142 | 17.4459 | -360.5189 | 17.6656 | -360.8266 | 18.1707 | -360.8204 | 17.5896 | -352.6783 | 18.7477 | -352.6875 | 16.8238
12:56 | 5789 | 49.8688 | 202.9381 | 449.2551 | 452.5006 | -16.461 | -38.8312 | 11.733 | 7.8403 | 2.2647 | 0.6801 | 2.9075 | -0.9612 | 12.2304 | 5.0789 | 0.6253 | 0.6672 | 0.9631 | 0.7531 | -129.3124 | 1.6413 | 5.5976 | 1.8871 | -2.4983 | -0.8322 | 4.8047 |  | 4.3066 | 0.8322 | 4.0068 | 3.3696 | 3.335 | 1.0946 | 10.8366 | 14.3042 | 14.907 | 11.1316 | -0.0001 | -0.0032 | 0.0008 | 0.004 | 0.0006 | -0.0004 | 0.005 | -0.0063 | -0.0265 | -360.1558 | 17.3884 | -360.4389 | 17.682 | -360.8604 | 18.2077 | -360.8389 | 17.5629 | -352.6075 | 18.7128 | -352.6567 | 16.8423
12:56 | 5790 | 49.9687 | 202.9378 | 449.3134 | 452.504 | -16.3807 | -38.8322 | 11.7738 | 7.9013 | 2.2943 | 0.6413 | 2.8431 | -0.9541 | 12.3065 | 5.1871 | 0.6244 | 0.6643 | 0.9682 | 0.7538 | -129.2092 | 1.7034 | 5.5811 | 1.9875 | -2.4332 | -0.8205 | 4.8531 |  | 4.3662 | 0.8966 | 4.0074 | 3.3678 | 3.3337 | 1.0937 | 10.7914 | 14.2767 | 14.841 | 11.0857 | 0.0005 | -0.0026 | 0.0013 | 0.004 | 0.001 | -0.0005 | 0.0226 | -0.0069 | -0.0039 | -360.2419 | 17.4007 | -360.4173 | 17.6369 | -360.7866 | 18.2138 | -360.8881 | 17.6102 | -352.6629 | 18.7045 | -352.6136 | 16.8032
12:56 | 5791 | 49.8632 | 202.9333 | 449.3962 | 452.518 | -16.3107 | -38.9231 | 11.7761 | 7.9164 | 2.3581 | 0.6645 | 2.776 | -1.0211 | 12.245 | 5.2159 | 0.6239 | 0.6678 | 0.9666 | 0.7524 | -129.2751 | 1.6568 | 5.5855 | 2.1238 | -2.4746 | -0.8991 | 4.8549 |  | 4.4066 | 0.9704 | 4.0063 | 3.3641 | 3.3308 | 1.0948 | 10.7939 | 14.2959 | 14.8569 | 11.1067 | -0.0002 | -0.0027 | -0.0001 | 0.0031 | 0.0004 | -0.0006 | 0.0057 | -0.0132 | -0.0014 | -360.2142 | 17.4397 | -360.5004 | 17.6697 | -360.8143 | 18.1645 | -360.8081 | 17.5671 | -352.6629 | 18.7497 | -352.6937 | 16.834
12:56 | 5792 | 49.8321 | 202.9604 | 449.3682 | 452.584 | -16.4285 | -38.8654 | 11.8697 | 7.9181 | 2.2252 | 0.6548 | 2.7793 | -1.1207 | 12.2074 | 5.23 | 0.6237 | 0.6634 | 0.963 | 0.7517 | -129.2272 | 1.7029 | 5.6514 | 2.1134 | -2.4817 | -0.8884 | 4.8704 |  | 4.3582 | 0.8679 | 4.0053 | 3.3642 | 3.3337 | 1.094 | 10.7556 | 14.281 | 14.8318 | 11.0854 | -0.0002 | -0.0025 | 0.0007 | 0.0036 | 0.0012 | -0.0004 | -0.0009 | -0.018 | -0.0162 | -360.125 | 17.3761 | -360.4235 | 17.6656 | -360.8297 | 18.2118 | -360.8174 | 17.5568 | -352.5952 | 18.6861 | -352.629 | 16.8402
12:56 | 5793 | 49.8296 | 202.9322 | 449.4427 | 452.5969 | -16.5768 | -38.9481 | 11.7786 | 7.9409 | 2.2927 | 0.6054 | 2.84 | -1.0824 | 12.2965 | 5.2357 | 0.6243 | 0.6657 | 0.9655 | 0.7529 | -129.2841 | 1.6482 | 5.6171 | 2.2289 | -2.4089 | -0.875 | 4.8539 |  | 4.4124 | 0.7744 | 4.0063 | 3.3668 | 3.3325 | 1.0949 | 10.7902 | 14.2813 | 14.8455 | 11.0847 | 0.0003 | -0.0027 | 0.0012 | 0.004 | 0.001 | -0.0005 | 0.0129 | -0.0046 | -0.0034 | -360.2173 | 17.4007 | -360.405 | 17.6286 | -360.7527 | 18.1892 | -360.8543 | 17.5999 | -352.6783 | 18.7128 | -352.6013 | 16.7909
12:56 | 5794 | 49.761 | 202.9206 | 449.3154 | 452.572 | -16.5322 | -38.9428 | 11.688 | 7.8963 | 2.3385 | 0.6353 | 2.9477 | -1.0415 | 12.2961 | 5.2725 | 0.6236 | 0.6655 | 0.9661 | 0.7524 | -129.3125 | 1.5209 | 5.5722 | 2.1887 | -2.3722 | -0.8076 | 4.8666 |  | 4.3676 | 0.7423 | 4.0061 | 3.3668 | 3.3313 | 1.0952 | 10.8227 | 14.3021 | 14.8775 | 11.1403 | 0.0003 | -0.003 | 0.0008 | 0.004 | 0.0006 | -0.0001 | 0.007 | -0.009 | -0.0195 | -360.1835 | 17.4172 | -360.4789 | 17.6636 | -360.8204 | 18.1625 | -360.7835 | 17.5547 | -352.589 | 18.721 | -352.6537 | 16.834
12:56 | 5795 | 49.8277 | 202.966 | 449.3873 | 452.5143 | -16.5915 | -39.0341 | 11.6481 | 7.9257 | 2.2899 | 0.6103 | 2.8588 | -1.001 | 12.2429 | 5.2576 | 0.6247 | 0.6626 | 0.9673 | 0.7541 | -129.3153 | 1.5629 | 5.59 | 2.105 | -2.4337 | -0.802 | 4.8298 |  | 4.3038 | 0.7387 | 4.0057 | 3.3656 | 3.3325 | 1.0944 | 10.7845 | 14.2696 | 14.8734 | 11.0966 | 0.0001 | -0.0025 | 0.0006 | 0.0039 | 0.0012 | -0.0003 | 0.029 | -0.0019 | -0.0317 | -360.0911 | 17.3617 | -360.3927 | 17.6553 | -360.802 | 18.2097 | -360.8358 | 17.5629 | -352.5644 | 18.6779 | -352.586 | 16.8156
12:56 | 5796 | 49.8636 | 202.9013 | 449.2847 | 452.5085 | -16.643 | -38.8967 | 11.7088 | 7.8169 | 2.3651 | 0.6377 | 2.8894 | -1.0851 | 12.1495 | 5.2153 | 0.6231 | 0.6641 | 0.9638 | 0.7519 | -129.2912 | 1.6193 | 5.6607 | 2.1895 | -2.4249 | -0.7933 | 4.8733 |  | 4.3212 | 0.8313 | 4.0058 | 3.364 | 3.3295 | 1.0948 | 10.8296 | 14.3033 | 14.8846 | 11.1414 | -0.0004 | -0.0028 | 0.0007 | 0.0038 | 0.0006 | 0.0001 | 0.0035 | -0.0182 | -0.0109 | -360.1742 | 17.4048 | -360.4173 | 17.6225 | -360.7343 | 18.1399 | -360.8081 | 17.5753 | -352.6352 | 18.721 | -352.6198 | 16.7889
12:56 | 5797 | 49.9125 | 202.9101 | 449.4014 | 452.5904 | -16.6345 | -38.9639 | 11.7433 | 7.8641 | 2.2903 | 0.6982 | 2.8452 | -1.03 | 12.212 | 5.2839 | 0.623 | 0.6624 | 0.9644 | 0.7508 | -129.3242 | 1.6496 | 5.5528 | 2.1541 | -2.4449 | -0.8882 | 4.9176 |  | 4.3231 | 0.8172 | 4.0068 | 3.3689 | 3.3332 | 1.096 | 10.7914 | 14.265 | 14.8516 | 11.0977 | 0.0001 | -0.0024 | 0.0006 | 0.0038 | 0.0012 | -0.0005 | 0.0061 | -0.0184 | 0.0017 | -360.1435 | 17.4069 | -360.4635 | 17.6656 | -360.8081 | 18.1358 | -360.7343 | 17.5404 | -352.589 | 18.7045 | -352.6413 | 16.8197
12:56 | 5798 | 49.8541 | 202.9052 | 449.2884 | 452.5582 | -16.6327 | -38.9644 | 11.7813 | 7.8157 | 2.3526 | 0.6844 | 2.847 | -1.0464 | 12.2021 | 5.1962 | 0.6243 | 0.6632 | 0.9666 | 0.7528 | -129.3841 | 1.5292 | 5.4902 | 2.1563 | -2.4818 | -0.9229 | 4.8574 |  | 4.3285 | 0.8169 | 4.0063 | 3.3668 | 3.3344 | 1.0953 | 10.7995 | 14.2788 | 14.8475 | 11.0887 | 0.0001 | -0.0033 | 0.0012 | 0.0041 | 0.0006 | -0.0006 | 0.021 | -0.0147 | -0.0029 | -360.1681 | 17.3556 | -360.3681 | 17.6492 | -360.7989 | 18.1769 | -360.845 | 17.565 | -352.5552 | 18.6758 | -352.5767 | 16.8074
12:56 | 5799 | 49.8958 | 202.9088 | 449.3851 | 452.5792 | -16.5807 | -38.9271 | 11.6863 | 7.8562 | 2.3796 | 0.7325 | 2.9199 | -1.0113 | 12.2266 | 5.2823 | 0.6246 | 0.6619 | 0.9689 | 0.7513 | -129.3834 | 1.6443 | 5.5954 | 2.1709 | -2.5633 | -0.8424 | 4.9046 |  | 4.3576 | 0.8737 | 4.0065 | 3.3652 | 3.3302 | 1.0937 | 10.7845 | 14.2637 | 14.8376 | 11.0854 | 0 | -0.0025 | 0.0012 | 0.0039 | 0.0007 | -0.0009 | 0.013 | -0.0074 | 0.0073 | -360.1988 | 17.409 | -360.4019 | 17.6389 | -360.7435 | 18.1255 | -360.7897 | 17.5691 | -352.6198 | 18.7025 | -352.629 | 16.7786
12:56 | 5800 | 49.8526 | 202.8905 | 449.3233 | 452.6066 | -16.6264 | -38.8146 | 11.7182 | 7.9137 | 2.3944 | 0.8076 | 2.9619 | -0.9367 | 12.235 | 5.2318 | 0.6242 | 0.6628 | 0.9664 | 0.7532 | -129.3145 | 1.7315 | 5.5957 | 2.1612 | -2.5075 | -0.8621 | 4.9043 |  | 4.3659 | 0.8628 | 4.0062 | 3.3642 | 3.3399 | 1.0956 | 10.7707 | 14.2555 | 14.8348 | 11.0659 | -0.0005 | -0.0026 | 0.0007 | 0.0036 | 0.001 | 0 | 0.0258 | -0.0059 | -0.0096 | -360.1219 | 17.3966 | -360.4481 | 17.6697 | -360.8297 | 18.1379 | -360.7835 | 17.5486 | -352.5336 | 18.6963 | -352.6383 | 16.8238
12:56 | 5801 | 49.8455 | 202.8499 | 449.3833 | 452.5545 | -16.5927 | -38.8252 | 11.7613 | 7.8844 | 2.4378 | 0.7632 | 2.928 | -1.068 | 12.1698 | 5.2271 | 0.6242 | 0.6651 | 0.9669 | 0.7538 | -129.2387 | 1.721 | 5.7009 | 1.9382 | -2.5242 | -0.8523 | 4.7819 |  | 4.3054 | 0.9092 | 4.0063 | 3.3679 | 3.3356 | 1.0959 | 10.7579 | 14.2659 | 14.8334 | 11.1053 | 0.0001 | -0.003 | 0.0012 | 0.0047 | 0.0007 | -0.0006 | 0.0074 | -0.0069 | 0.0098 | -360.1127 | 17.3679 | -360.3712 | 17.6348 | -360.7835 | 18.1625 | -360.8512 | 17.5732 | -352.589 | 18.6696 | -352.5336 | 16.7991
12:56 | 5802 | 49.7465 | 202.8471 | 449.392 | 452.4563 | -16.5908 | -38.9345 | 11.7166 | 7.8473 | 2.3871 | 0.7107 | 2.9251 | -1.0533 | 12.1576 | 5.192 | 0.6251 | 0.6637 | 0.9671 | 0.7555 | -129.2495 | 1.743 | 5.758 | 1.9895 | -2.5543 | -0.9433 | 4.8148 |  | 4.3684 | 0.9667 | 4.0066 | 3.3652 | 3.3348 | 1.095 | 10.7962 | 14.2289 | 14.8365 | 11.08 | 0 | -0.003 | 0.0007 | 0.0036 | 0.0008 | 0.0001 | 0.0061 | -0.0127 | -0.0117 | -360.1527 | 17.4213 | -360.4235 | 17.6328 | -360.7343 | 18.1235 | -360.7743 | 17.5753 | -352.6013 | 18.7169 | -352.6321 | 16.7991
12:56 | 5803 | 49.8585 | 202.9121 | 449.3746 | 452.4935 | -16.6724 | -39.0498 | 11.7429 | 7.9192 | 2.4328 | 0.7148 | 2.8863 | -0.9791 | 12.1557 | 5.272 | 0.6236 | 0.6644 | 0.964 | 0.7539 | -129.2665 | 1.7329 | 5.7197 | 2.0345 | -2.4933 | -0.8848 | 4.8284 |  | 4.3264 | 0.8564 | 4.0066 | 3.3661 | 3.3364 | 1.0942 | 10.7742 | 14.2994 | 14.8089 | 11.0984 | -0.0003 | -0.003 | 0.0009 | 0.0042 | 0.0012 | -0.0006 | 0.0007 | -0.0182 | -0.0048 | -360.1373 | 17.3823 | -360.4419 | 17.6677 | -360.8143 | 18.1543 | -360.805 | 17.5609 | -352.5336 | 18.684 | -352.6167 | 16.8279
12:56 | 5804 | 49.884 | 202.9191 | 449.5203 | 452.6137 | -16.6393 | -38.917 | 11.8245 | 7.9254 | 2.3387 | 0.7874 | 2.914 | -0.9008 | 12.2365 | 5.3375 | 0.6247 | 0.6651 | 0.9654 | 0.7531 | -129.2122 | 1.7117 | 5.7917 | 2.1069 | -2.5195 | -0.9421 | 4.8081 |  | 4.3588 | 0.9038 | 4.0067 | 3.3678 | 3.3333 | 1.0935 | 10.8214 | 14.2954 | 14.884 | 11.1038 | -0.0002 | -0.0023 | 0.0011 | 0.0041 | 0.0013 | 0.0001 | 0.004 | -0.0152 | -0.0177 | -360.1558 | 17.372 | -360.3527 | 17.6328 | -360.7558 | 18.1522 | -360.842 | 17.5999 | -352.5952 | 18.6799 | -352.5613 | 16.7889
12:56 | 5805 | 49.9494 | 202.9788 | 449.5468 | 452.5616 | -16.6826 | -38.9675 | 11.7902 | 7.8994 | 2.3445 | 0.8461 | 2.9532 | -1.0421 | 12.1561 | 5.286 | 0.6232 | 0.6675 | 0.9626 | 0.7532 | -129.2557 | 1.678 | 5.7869 | 2.1233 | -2.412 | -0.8211 | 4.8697 |  | 4.3045 | 0.8707 | 4.0073 | 3.3675 | 3.3286 | 1.0932 | 10.7903 | 14.2868 | 14.8376 | 11.1316 | -0.0001 | -0.0028 | 0.0002 | 0.0031 | 0.001 | -0.0004 | 0.0255 | -0.0072 | -0.0193 | -360.1681 | 17.4131 | -360.4081 | 17.6451 | -360.7835 | 18.1194 | -360.7927 | 17.5814 | -352.629 | 18.7025 | -352.6198 | 16.8032
12:56 | 5806 | 49.8598 | 202.9436 | 449.4849 | 452.5776 | -16.7397 | -38.9479 | 11.827 | 7.847 | 2.3941 | 0.8001 | 2.9524 | -1.0838 | 12.1586 | 5.256 | 0.6249 | 0.6645 | 0.9634 | 0.7525 | -129.297 | 1.6359 | 5.6571 | 2.0264 | -2.468 | -0.8942 | 4.8071 |  | 4.2907 | 0.8103 | 4.0071 | 3.3687 | 3.3334 | 1.0925 | 10.7973 | 14.2763 | 14.8552 | 11.0984 | 0 | -0.0032 | 0.0008 | 0.0037 | 0.0009 | -0.0007 | 0.0198 | -0.0026 | -0.0061 | -360.0819 | 17.3679 | -360.3989 | 17.6512 | -360.7958 | 18.1645 | -360.7927 | 17.5568 | -352.5398 | 18.6655 | -352.5767 | 16.8258
12:56 | 5807 | 49.9281 | 202.8908 | 449.4391 | 452.5338 | -16.9668 | -38.8821 | 11.8172 | 7.8418 | 2.4662 | 0.7701 | 2.9244 | -1.0796 | 12.1743 | 5.2966 | 0.6249 | 0.6643 | 0.9621 | 0.7539 | -129.2326 | 1.6544 | 5.6761 | 2.0654 | -2.4535 | -0.8334 | 4.8588 |  | 4.3524 | 0.8313 | 4.0065 | 3.3651 | 3.3335 | 1.0941 | 10.8076 | 14.287 | 14.8907 | 11.1255 | 0.0001 | -0.0029 | 0.0012 | 0.004 | 0.001 | 0 | 0.0157 | 0.004 | -0.0004 | -360.1988 | 17.3987 | -360.405 | 17.641 | -360.7466 | 18.1379 | -360.7989 | 17.5978 | -352.6383 | 18.6902 | -352.5798 | 16.7889
12:57 | 5808 | 50.0055 | 202.8533 | 449.4898 | 452.53 | -16.9505 | -38.8092 | 11.9379 | 7.8392 | 2.5627 | 0.8028 | 2.8989 | -1.1078 | 12.1119 | 5.2994 | 0.624 | 0.6675 | 0.963 | 0.754 | -129.3005 | 1.6744 | 5.7858 | 2.0113 | -2.5419 | -0.9509 | 4.8202 |  | 4.3752 | 0.9689 | 4.0065 | 3.3658 | 3.3325 | 1.0944 | 10.7938 | 14.296 | 14.9043 | 11.1179 | -0.0007 | -0.0032 | 0.0009 | 0.0042 | 0.001 | -0.0008 | 0.0094 | -0.0074 | 0.0084 | -360.1034 | 17.3699 | -360.4081 | 17.6636 | -360.7958 | 18.1502 | -360.7927 | 17.5506 | -352.5429 | 18.6779 | -352.5952 | 16.8156
12:57 | 5809 | 49.9335 | 202.9303 | 449.507 | 452.5606 | -16.8933 | -38.7975 | 11.9946 | 7.8121 | 2.5405 | 0.6708 | 2.8012 | -1.0273 | 12.1901 | 5.3371 | 0.6239 | 0.6652 | 0.9662 | 0.7531 | -129.1935 | 1.7596 | 5.7908 | 1.977 | -2.5638 | -0.835 | 4.8728 |  | 4.3161 | 0.9726 | 4.0071 | 3.3653 | 3.3343 | 1.0947 | 10.7694 | 14.2662 | 14.8124 | 11.0988 | 0 | -0.0027 | 0.0012 | 0.0047 | 0.0006 | -0.0004 | 0.0181 | -0.0099 | -0.0042 | -360.1342 | 17.3802 | -360.4019 | 17.6533 | -360.7897 | 18.1625 | -360.8297 | 17.5896 | -352.589 | 18.6696 | -352.5767 | 16.8074
12:57 | 5810 | 49.9019 | 202.9768 | 449.5043 | 452.4625 | -16.5655 | -38.8536 | 11.8252 | 7.9153 | 2.683 | 0.6853 | 2.8723 | -1.0239 | 12.1512 | 5.3399 | 0.6255 | 0.6678 | 0.9641 | 0.7544 | -129.1904 | 1.7083 | 5.7871 | 1.9344 | -2.6173 | -0.9065 | 4.8633 |  | 4.3415 | 0.8735 | 4.0067 | 3.3615 | 3.3323 | 1.0926 | 10.8145 | 14.2942 | 14.8884 | 11.12 | 0.0004 | -0.0031 | 0.0007 | 0.0038 | 0.001 | -0.0006 | 0.0113 | -0.0028 | 0.0001 | -360.1342 | 17.3905 | -360.4173 | 17.6512 | -360.7897 | 18.142 | -360.7958 | 17.5773 | -352.6198 | 18.684 | -352.6044 | 16.8156
12:57 | 5811 | 50.0037 | 202.997 | 449.6116 | 452.5103 | -16.4749 | -38.8195 | 11.8516 | 7.9103 | 2.6329 | 0.821 | 2.951 | -1.0067 | 12.1292 | 5.3862 | 0.6254 | 0.6705 | 0.9667 | 0.753 | -129.2715 | 1.6778 | 5.7631 | 2.0079 | -2.6322 | -0.958 | 4.7651 |  | 4.3151 | 0.8281 | 4.0063 | 3.3687 | 3.3349 | 1.0933 | 10.7995 | 14.2846 | 14.859 | 11.1349 | 0.0003 | -0.0026 | 0.0005 | 0.0039 | 0.0006 | -0.0003 | 0.0102 | -0.0082 | -0.024 | -360.165 | 17.3843 | -360.4173 | 17.6512 | -360.7712 | 18.1604 | -360.8297 | 17.5773 | -352.5736 | 18.684 | -352.6198 | 16.8156
12:57 | 5812 | 50.01 | 203.0081 | 449.4922 | 452.5117 | -16.4531 | -38.8209 | 11.8912 | 7.9798 | 2.6221 | 0.8935 | 2.9439 | -1.0834 | 12.073 | 5.3241 | 0.6255 | 0.6655 | 0.9638 | 0.7514 | -129.2531 | 1.6707 | 5.8022 | 1.9808 | -2.6465 | -0.8599 | 4.7656 |  | 4.3214 | 0.9573 | 4.0073 | 3.3675 | 3.3333 | 1.0955 | 10.7868 | 14.2603 | 14.8634 | 11.1049 | -0.0002 | -0.0028 | 0.0008 | 0.0038 | 0.0013 | -0.0003 | 0.0055 | -0.0117 | -0.018 | -360.1496 | 17.3864 | -360.4142 | 17.6553 | -360.7712 | 18.1584 | -360.805 | 17.5814 | -352.589 | 18.6943 | -352.6075 | 16.8135
12:57 | 5813 | 49.9962 | 203.0821 | 449.4759 | 452.5101 | -16.519 | -39.0059 | 11.7809 | 7.9731 | 2.6305 | 0.8681 | 2.9062 | -1.1945 | 12.0686 | 5.3105 | 0.6248 | 0.6617 | 0.9651 | 0.7524 | -129.2369 | 1.6882 | 5.7813 | 1.9085 | -2.7211 | -0.844 | 4.7408 |  | 4.4212 | 0.9121 | 4.0063 | 3.3655 | 3.3341 | 1.0942 | 10.8041 | 14.3067 | 14.8529 | 11.1334 | -0.0002 | -0.0029 | 0.0002 | 0.003 | 0.0006 | -0.0004 | 0.0146 | -0.0025 | -0.0267 | -360.1465 | 17.3946 | -360.405 | 17.641 | -360.7835 | 18.1502 | -360.8327 | 17.5794 | -352.6136 | 18.6861 | -352.6198 | 16.8135
12:57 | 5814 | 50.0521 | 203.0619 | 449.4158 | 452.5088 | -16.63 | -39.165 | 11.7873 | 8.0266 | 2.5928 | 0.759 | 2.9221 | -1.0987 | 12.1607 | 5.3365 | 0.6252 | 0.6647 | 0.9626 | 0.7539 | -129.2712 | 1.6589 | 5.7723 | 2.0674 | -2.6511 | -0.8345 | 4.7745 |  | 4.3748 | 0.9445 | 4.0063 | 3.3673 | 3.3307 | 1.094 | 10.773 | 14.2753 | 14.8549 | 11.0681 | 0.0001 | -0.003 | 0.0009 | 0.0037 | 0.001 | -0.0005 | 0.0098 | -0.0068 | -0.0038 | -360.1465 | 17.4007 | -360.4266 | 17.6615 | -360.802 | 18.144 | -360.8081 | 17.5794 | -352.5798 | 18.684 | -352.6352 | 16.8217
12:57 | 5815 | 49.9804 | 203.0772 | 449.3883 | 452.5324 | -16.5732 | -39.1101 | 11.8326 | 8.1043 | 2.6419 | 0.6591 | 2.8719 | -1.0497 | 12.1309 | 5.2982 | 0.6246 | 0.6646 | 0.9619 | 0.7528 | -129.2364 | 1.6048 | 5.663 | 2.0645 | -2.6712 | -0.9049 | 4.7029 |  | 4.3079 | 0.9158 | 4.0073 | 3.3701 | 3.3366 | 1.0936 | 10.7602 | 14.2567 | 14.8593 | 11.0959 | 0.0001 | -0.0028 | 0.0008 | 0.0038 | 0.001 | -0.0005 | 0.0145 | 0.0064 | 0.0052 | -360.1373 | 17.3884 | -360.3865 | 17.6451 | -360.7989 | 18.1543 | -360.8112 | 17.5814 | -352.5644 | 18.6758 | -352.6167 | 16.8094
12:57 | 5816 | 49.9565 | 203.0216 | 449.4605 | 452.4541 | -16.6425 | -39.0507 | 11.8038 | 8.0494 | 2.7005 | 0.7414 | 3.0122 | -0.9979 | 12.2173 | 5.3135 | 0.6235 | 0.666 | 0.9636 | 0.7531 | -129.1942 | 1.6658 | 5.7528 | 1.9941 | -2.6664 | -0.9409 | 4.7159 |  | 4.3358 | 0.9712 | 4.0067 | 3.3656 | 3.3344 | 1.0944 | 10.8134 | 14.2871 | 14.8802 | 11.1078 | -0.0002 | -0.0025 | 0.0009 | 0.0041 | 0.0011 | -0.0004 | 0.0089 | -0.0108 | -0.0218 | -360.1281 | 17.4048 | -360.4112 | 17.6328 | -360.7589 | 18.1522 | -360.7958 | 17.5794 | -352.629 | 18.6984 | -352.6167 | 16.8053
12:57 | 5817 | 49.9203 | 203.0017 | 449.4518 | 452.4204 | -16.7204 | -39.0081 | 11.8383 | 8.0592 | 2.5946 | 0.7969 | 3.0018 | -1.0274 | 12.1392 | 5.2811 | 0.6235 | 0.6661 | 0.9634 | 0.7527 | -129.1086 | 1.7602 | 5.7402 | 2.0669 | -2.6734 | -0.9899 | 4.7939 |  | 4.3844 | 0.9494 | 4.0083 | 3.3668 | 3.3366 | 1.0934 | 10.781 | 14.2661 | 14.8808 | 11.0818 | -0.0002 | -0.0025 | 0.0005 | 0.0042 | 0.0007 | -0.0005 | 0.0111 | -0.0051 | -0.0031 | -360.1742 | 17.3905 | -360.4358 | 17.6656 | -360.7773 | 18.1502 | -360.7897 | 17.5588 | -352.5552 | 18.6799 | -352.6229 | 16.8217
12:57 | 5818 | 49.8916 | 202.9198 | 449.3023 | 452.3613 | -16.6658 | -39.0294 | 11.7405 | 8.0379 | 2.607 | 0.8329 | 2.9166 | -1.001 | 12.1194 | 5.2813 | 0.6238 | 0.6647 | 0.9651 | 0.7521 | -129.2717 | 1.7427 | 5.7429 | 2.0883 | -2.5429 | -0.7752 | 4.7853 |  | 4.3178 | 0.9044 | 4.0065 | 3.3658 | 3.3338 | 1.0953 | 10.7706 | 14.279 | 14.8659 | 11.1056 | 0.0001 | -0.0033 | 0.0008 | 0.0039 | 0.0008 | -0.0006 | 0.0017 | 0.0008 | -0.0052 | -360.1619 | 17.3658 | -360.3742 | 17.6307 | -360.7497 | 18.1563 | -360.8266 | 17.5835 | -352.5644 | 18.6676 | -352.5552 | 16.793
12:57 | 5819 | 49.8324 | 202.944 | 449.4486 | 452.3856 | -16.5108 | -38.9566 | 11.7588 | 8.1114 | 2.5767 | 0.8376 | 2.9983 | -1.0805 | 12.1059 | 5.2512 | 0.6245 | 0.6658 | 0.9666 | 0.7529 | -129.2335 | 1.6346 | 5.7367 | 1.8856 | -2.5882 | -0.9167 | 4.8292 |  | 4.3111 | 0.9797 | 4.0076 | 3.3641 | 3.3321 | 1.0947 | 10.7915 | 14.2707 | 14.8505 | 11.0749 | 0.0004 | -0.0028 | 0.0008 | 0.004 | 0.0007 | -0.0004 | 0.0203 | 0.0012 | -0.0146 | -360.1127 | 17.4131 | -360.4173 | 17.6389 | -360.765 | 18.1296 | -360.7712 | 17.5732 | -352.6229 | 18.7066 | -352.6106 | 16.8053
12:57 | 5820 | 49.9024 | 202.9502 | 449.4771 | 452.3929 | -16.608 | -38.9589 | 11.6627 | 8.1563 | 2.5645 | 0.8411 | 2.9375 | -1.0303 | 12.1682 | 5.2942 | 0.6245 | 0.6648 | 0.9694 | 0.7543 | -129.1189 | 1.7057 | 5.8148 | 1.8781 | -2.5632 | -0.8163 | 4.8474 |  | 4.3289 | 0.9818 | 4.0059 | 3.3677 | 3.3336 | 1.0948 | 10.7984 | 14.2778 | 14.8703 | 11.093 | -0.0002 | -0.0026 | 0.0009 | 0.004 | 0.0005 | -0.0003 | 0.0156 | -0.0043 | -0.0097 | -360.0604 | 17.3638 | -360.3927 | 17.6594 | -360.8112 | 18.1666 | -360.8174 | 17.5568 | -352.5121 | 18.6696 | -352.5921 | 16.8197
12:57 | 5821 | 49.866 | 202.9423 | 449.3086 | 452.2719 | -16.8756 | -38.9854 | 11.7633 | 8.0828 | 2.621 | 0.7792 | 2.9587 | -1.0375 | 12.1486 | 5.2662 | 0.6233 | 0.6606 | 0.9661 | 0.7527 | -129.1102 | 1.6567 | 5.7651 | 1.9218 | -2.5145 | -0.8155 | 4.8873 |  | 4.3448 | 0.9156 | 4.0066 | 3.3645 | 3.3334 | 1.0943 | 10.7868 | 14.2892 | 14.8634 | 11.1222 | 0.0001 | -0.0024 | 0.0007 | 0.0036 | 0.0011 | -0.0006 | -0.0002 | -0.0118 | 0.0041 | -360.1896 | 17.3966 | -360.4112 | 17.6307 | -360.7343 | 18.142 | -360.842 | 17.6061 | -352.6167 | 18.6881 | -352.5829 | 16.7827
12:57 | 5822 | 49.9114 | 203.0423 | 449.5053 | 452.3869 | -16.7513 | -39.1152 | 11.7357 | 8.1498 | 2.5185 | 1.015 | 3.0217 | -1.0457 | 12.123 | 5.2155 | 0.6247 | 0.6642 | 0.9703 | 0.753 | -129.2018 | 1.8023 | 5.7512 | 2.0781 | -2.5187 | -0.8143 | 4.91 |  | 4.3046 | 1.0173 | 4.0064 | 3.3694 | 3.3334 | 1.0949 | 10.7833 | 14.3091 | 14.8615 | 11.1298 | 0.0001 | -0.0029 | 0.001 | 0.0043 | 0.0007 | 0.0001 | 0.0097 | 0.0032 | -0.0154 | -360.1681 | 17.4048 | -360.4635 | 17.6677 | -360.802 | 18.1235 | -360.7589 | 17.5445 | -352.5736 | 18.7045 | -352.6444 | 16.8135
12:57 | 5823 | 49.9534 | 203.0524 | 449.5207 | 452.4417 | -16.5824 | -39.0456 | 11.8029 | 8.0651 | 2.5999 | 0.8466 | 2.9725 | -1.012 | 12.1632 | 5.1432 | 0.6227 | 0.6613 | 0.9647 | 0.7545 | -129.2784 | 1.6546 | 5.8542 | 1.9634 | -2.5694 | -0.844 | 4.8565 |  | 4.3112 | 0.9541 | 4.0068 | 3.3661 | 3.3362 | 1.095 | 10.7903 | 14.2984 | 14.8549 | 11.1143 | -0.0003 | -0.0031 | 0.0006 | 0.0041 | 0.0012 | -0.0008 | -0.0028 | -0.024 | 0.0052 | -360.1219 | 17.3699 | -360.3865 | 17.6574 | -360.8235 | 18.1789 | -360.8666 | 17.5835 | -352.5613 | 18.6655 | -352.5706 | 16.8115
12:57 | 5824 | 49.9587 | 202.9771 | 449.3802 | 452.3868 | -16.62 | -39.024 | 11.7394 | 8.179 | 2.5959 | 0.8604 | 3.0261 | -1.0453 | 12.0998 | 5.1258 | 0.6246 | 0.6645 | 0.9659 | 0.7551 | -129.297 | 1.6465 | 5.834 | 2.0201 | -2.4647 | -0.8373 | 4.9306 |  | 4.3389 | 0.9158 | 4.0067 | 3.3676 | 3.3335 | 1.0939 | 10.7742 | 14.2705 | 14.861 | 11.0984 | -0.0003 | -0.0028 | 0.0003 | 0.0035 | 0.0004 | -0.0003 | 0.0092 | 0.0022 | -0.006 | -360.1835 | 17.4295 | -360.4512 | 17.6471 | -360.7835 | 18.1276 | -360.8112 | 17.604 | -352.6444 | 18.7128 | -352.6383 | 16.7889
12:57 | 5825 | 49.9583 | 202.9693 | 449.4346 | 452.3633 | -16.4423 | -38.9385 | 11.817 | 8.0716 | 2.4505 | 0.8068 | 2.9846 | -1.0812 | 12.1374 | 5.273 | 0.6258 | 0.6636 | 0.9678 | 0.753 | -129.1846 | 1.8419 | 5.8512 | 2.0971 | -2.4642 | -0.7175 | 4.8599 |  | 4.3565 | 0.8261 | 4.0074 | 3.3637 | 3.3319 | 1.0934 | 10.8007 | 14.2858 | 14.8546 | 11.1302 | -0.0003 | -0.0023 | 0.0008 | 0.0041 | 0.0013 | -0.0007 | 0.0158 | -0.0216 | -0.0114 | -360.1281 | 17.411 | -360.485 | 17.6985 | -360.8789 | 18.1687 | -360.8174 | 17.5732 | -352.5706 | 18.684 | -352.6506 | 16.8443
12:57 | 5826 | 49.9515 | 202.9481 | 449.5194 | 452.3296 | -16.5906 | -38.8259 | 11.8131 | 8.0865 | 2.3644 | 0.7543 | 2.9946 | -1.1055 | 12.0975 | 5.2056 | 0.6233 | 0.666 | 0.9684 | 0.7544 | -129.291 | 1.7468 | 5.8132 | 2.1119 | -2.4723 | -0.8145 | 4.9445 |  | 4.2795 | 0.8943 | 4.0085 | 3.3699 | 3.3319 | 1.0949 | 10.7903 | 14.2521 | 14.8376 | 11.1028 | 0.0002 | -0.0029 | 0.0005 | 0.0035 | 0.0006 | -0.0001 | 0.0177 | -0.0059 | -0.019 | -360.2111 | 17.4048 | -360.4019 | 17.643 | -360.7958 | 18.1769 | -360.8758 | 17.6143 | -352.6506 | 18.6881 | -352.586 | 16.8012
12:57 | 5827 | 49.9904 | 203.0659 | 449.5623 | 452.4416 | -16.8758 | -38.9134 | 11.8591 | 8.1021 | 2.3729 | 0.761 | 2.9709 | -1.093 | 12.1005 | 5.2007 | 0.6238 | 0.6672 | 0.9631 | 0.7547 | -129.2577 | 1.7289 | 5.7038 | 2.0834 | -2.3549 | -0.8846 | 4.9096 |  | 4.3645 | 0.8496 | 4.0072 | 3.3721 | 3.3359 | 1.0939 | 10.7996 | 14.2612 | 14.8337 | 11.101 | 0 | -0.0031 | 0.0005 | 0.0038 | 0.0007 | -0.0005 | 0.0002 | -0.0148 | -0.0033 | -360.2204 | 17.4418 | -360.4942 | 17.682 | -360.8297 | 18.1502 | -360.8266 | 17.5917 | -352.6721 | 18.7374 | -352.6537 | 16.8238
12:57 | 5828 | 49.8657 | 202.9583 | 449.4559 | 452.2979 | -16.9351 | -38.8934 | 11.9622 | 8.1749 | 2.3768 | 0.7527 | 2.9746 | -1.1472 | 12.1195 | 5.2023 | 0.6237 | 0.6672 | 0.9638 | 0.7537 | -129.2246 | 1.7291 | 5.6984 | 2.1308 | -2.3346 | -0.8727 | 4.9278 |  | 4.4096 | 0.9105 | 4.0056 | 3.368 | 3.331 | 1.0939 | 10.7799 | 14.2879 | 14.8552 | 11.0927 | 0 | -0.0025 | 0.001 | 0.004 | 0.0002 | -0.0006 | 0.0121 | -0.0039 | -0.0126 | -360.1065 | 17.3864 | -360.4512 | 17.6985 | -360.8635 | 18.1912 | -360.885 | 17.5773 | -352.549 | 18.6779 | -352.626 | 16.8402
12:57 | 5829 | 49.8856 | 202.9825 | 449.5251 | 452.2791 | -16.8461 | -38.9629 | 12.0057 | 8.2216 | 2.4126 | 0.7582 | 3.0031 | -1.104 | 12.152 | 5.3009 | 0.6239 | 0.6627 | 0.9671 | 0.7526 | -129.1947 | 1.6897 | 5.7472 | 2.1425 | -2.3854 | -0.9107 | 4.9224 |  | 4.31 | 0.8506 | 4.0073 | 3.3686 | 3.3327 | 1.0947 | 10.8089 | 14.2819 | 14.9063 | 11.1046 | -0.0005 | -0.0029 | 0.0009 | 0.0039 | 0.0004 | -0.0006 | -0.0054 | -0.0182 | 0.0066 | -360.2573 | 17.4192 | -360.4481 | 17.6492 | -360.8112 | 18.1748 | -360.882 | 17.6307 | -352.6752 | 18.7128 | -352.6013 | 16.7971
12:57 | 5830 | 49.96 | 203.0294 | 449.4817 | 452.3885 | -16.8033 | -39.004 | 11.8544 | 8.1364 | 2.3177 | 0.6747 | 2.9449 | -1.0616 | 12.1279 | 5.3701 | 0.6238 | 0.6643 | 0.9651 | 0.7534 | -129.2698 | 1.6562 | 5.6718 | 2.1464 | -2.3886 | -0.8308 | 4.8912 |  | 4.3736 | 0.897 | 4.006 | 3.3673 | 3.3345 | 1.0949 | 10.7995 | 14.2904 | 14.888 | 11.106 | 0.0002 | -0.0029 | 0.001 | 0.0039 | 0.0013 | -0.0004 | -0.0077 | -0.0042 | 0.0192 | -360.1835 | 17.4254 | -360.4942 | 17.6944 | -360.8512 | 18.1563 | -360.8112 | 17.5794 | -352.6075 | 18.7271 | -352.7213 | 16.8402
12:57 | 5831 | 49.9541 | 202.8971 | 449.4267 | 452.2767 | -16.8828 | -39.0192 | 11.9364 | 8.0587 | 2.3569 | 0.6209 | 2.9513 | -1.0899 | 12.0929 | 5.2162 | 0.6245 | 0.6653 | 0.9629 | 0.7545 | -129.3755 | 1.6624 | 5.7302 | 2.1001 | -2.4953 | -0.8292 | 4.9197 |  | 4.3618 | 0.8937 | 4.0063 | 3.3691 | 3.3332 | 1.0945 | 10.8099 | 14.2778 | 14.8587 | 11.1161 | 0.0004 | -0.0028 | 0.0008 | 0.0039 | 0.0005 | -0.0006 | 0.0203 | -0.0139 | 0.0028 | -360.1527 | 17.3946 | -360.4204 | 17.6759 | -360.8543 | 18.2036 | -360.882 | 17.5999 | -352.6506 | 18.682 | -352.6075 | 16.832
12:57 | 5832 | 49.9165 | 202.9685 | 449.4062 | 452.1554 | -16.8744 | -38.9215 | 11.9765 | 8.1205 | 2.3689 | 0.7466 | 2.9852 | -1.1099 | 12.1331 | 5.3817 | 0.6232 | 0.6641 | 0.9652 | 0.7529 | -129.3594 | 1.6573 | 5.663 | 2.0625 | -2.5134 | -0.7235 | 4.8799 |  | 4.497 | 0.9026 | 4.0072 | 3.3668 | 3.3319 | 1.0942 | 10.8203 | 14.2883 | 14.8816 | 11.1378 | -0.0005 | -0.0031 | 0.0005 | 0.0038 | 0.0009 | -0.0005 | 0.0064 | -0.0128 | -0.0132 | -360.2111 | 17.4172 | -360.4358 | 17.6553 | -360.7958 | 18.1625 | -360.842 | 17.6122 | -352.6783 | 18.7169 | -352.626 | 16.8074
12:57 | 5833 | 49.9216 | 202.9793 | 449.3961 | 452.1816 | -16.8554 | -38.8775 | 11.934 | 8.011 | 2.2854 | 0.6202 | 2.8892 | -1.1267 | 12.1671 | 5.3047 | 0.6233 | 0.6644 | 0.9664 | 0.753 | -129.3673 | 1.6919 | 5.6568 | 2.1159 | -2.4329 | -0.7995 | 4.8995 |  | 4.413 | 0.9466 | 4.0056 | 3.3676 | 3.3369 | 1.0947 | 10.7961 | 14.2812 | 14.856 | 11.1139 | 0 | -0.0024 | 0.0007 | 0.0039 | 0.0003 | -0.0008 | 0.0111 | -0.0137 | -0.0144 | -360.1158 | 17.3905 | -360.4573 | 17.6861 | -360.8235 | 18.1728 | -360.8143 | 17.5732 | -352.5921 | 18.6922 | -352.669 | 16.8566
12:57 | 5834 | 49.9226 | 203.0677 | 449.4747 | 452.2682 | -16.9446 | -38.9573 | 11.9278 | 8.0838 | 2.347 | 0.7915 | 2.9515 | -1.0914 | 12.1788 | 5.1598 | 0.6237 | 0.6655 | 0.9648 | 0.7548 | -129.2454 | 1.6994 | 5.6893 | 2.0431 | -2.3666 | -0.8034 | 4.8924 |  | 4.4141 | 0.8664 | 4.0072 | 3.3689 | 3.3341 | 1.0956 | 10.8041 | 14.3068 | 14.8887 | 11.1215 | 0.0001 | -0.0031 | 0.0008 | 0.0034 | 0.0008 | -0.0008 | 0.0082 | -0.004 | -0.0229 | -360.1681 | 17.3905 | -360.3989 | 17.6286 | -360.762 | 18.1522 | -360.8266 | 17.5978 | -352.626 | 18.682 | -352.586 | 16.7991
12:57 | 5835 | 49.9645 | 203.0216 | 449.5061 | 452.2545 | -16.8514 | -38.9195 | 11.9719 | 8.1059 | 2.3913 | 0.8205 | 2.9299 | -1.0792 | 12.219 | 5.2615 | 0.624 | 0.6637 | 0.9671 | 0.7534 | -129.3306 | 1.6788 | 5.6234 | 2.0628 | -2.4778 | -0.7144 | 4.8933 |  | 4.4334 | 0.8402 | 4.0064 | 3.3642 | 3.333 | 1.0944 | 10.8157 | 14.2721 | 14.8656 | 11.1099 | 0.0003 | -0.003 | 0.001 | 0.0039 | 0.0011 | 0.0001 | 0.0133 | -0.0097 | 0.0085 | -360.1281 | 17.4007 | -360.4358 | 17.6738 | -360.7989 | 18.1358 | -360.7773 | 17.5773 | -352.5675 | 18.6922 | -352.6413 | 16.8238
12:57 | 5836 | 50.0312 | 203.1223 | 449.6222 | 452.2165 | -16.889 | -38.8917 | 11.8387 | 8.0603 | 2.3308 | 0.8593 | 2.9386 | -1.1581 | 12.1638 | 5.2786 | 0.6244 | 0.6646 | 0.9617 | 0.7527 | -129.3134 | 1.5848 | 5.5627 | 2.1557 | -2.4554 | -0.7528 | 4.9614 |  | 4.3933 | 0.8873 | 4.0068 | 3.3678 | 3.3322 | 1.0955 | 10.7776 | 14.2684 | 14.8141 | 11.0897 | 0.0001 | -0.0026 | 0.0011 | 0.004 | 0.0008 | -0.0009 | 0.0074 | -0.0103 | -0.0155 | -360.1496 | 17.3761 | -360.3958 | 17.641 | -360.762 | 18.1461 | -360.8112 | 17.5794 | -352.5767 | 18.6737 | -352.5983 | 16.8115
12:57 | 5837 | 49.9706 | 203.0348 | 449.4425 | 452.1552 | -16.8902 | -38.9037 | 11.9355 | 8.1245 | 2.2751 | 0.7691 | 2.9102 | -1.0647 | 12.246 | 5.2648 | 0.6241 | 0.6652 | 0.9627 | 0.752 | -129.266 | 1.6186 | 5.6447 | 2.1192 | -2.5342 | -0.7453 | 4.9355 |  | 4.3544 | 0.8484 | 4.0069 | 3.3682 | 3.3325 | 1.0964 | 10.7822 | 14.2673 | 14.8243 | 11.0887 | -0.0002 | -0.0028 | 0.0009 | 0.0038 | 0.0011 | 0.0004 | 0.0105 | -0.0072 | -0.0125 | -360.125 | 17.3884 | -360.4081 | 17.6553 | -360.7835 | 18.144 | -360.7835 | 17.5876 | -352.5798 | 18.6779 | -352.6106 | 16.8053
12:57 | 5838 | 49.9563 | 203.0086 | 449.4831 | 452.1733 | -16.9107 | -38.9045 | 11.8745 | 8.0741 | 2.2924 | 0.7446 | 2.8494 | -1.0739 | 12.1379 | 5.2662 | 0.6245 | 0.6644 | 0.9683 | 0.7533 | -129.3017 | 1.6125 | 5.6756 | 2.1318 | -2.472 | -0.8515 | 4.8867 |  | 4.4176 | 0.8144 | 4.0081 | 3.3705 | 3.3315 | 1.0951 | 10.7857 | 14.2707 | 14.8563 | 11.0807 | 0.0002 | -0.0028 | 0.0004 | 0.0037 | 0.0011 | -0.0004 | 0.0113 | -0.01 | -0.0056 | -360.1281 | 17.3946 | -360.4327 | 17.6389 | -360.7527 | 18.142 | -360.7989 | 17.5794 | -352.5644 | 18.682 | -352.6013 | 16.8032
12:57 | 5839 | 50.0672 | 203.0659 | 449.4454 | 452.1572 | -16.9726 | -39.019 | 11.7608 | 7.9511 | 2.2504 | 0.6849 | 2.8238 | -0.9827 | 12.2479 | 5.3699 | 0.626 | 0.6655 | 0.9686 | 0.7535 | -129.2705 | 1.6925 | 5.7202 | 2.0229 | -2.5684 | -0.8898 | 4.8684 |  | 4.3642 | 0.8815 | 4.0072 | 3.37 | 3.3333 | 1.0958 | 10.7707 | 14.2498 | 14.829 | 11.089 | 0.0003 | -0.0031 | 0.0006 | 0.0038 | 0.0003 | -0.0007 | -0.0023 | -0.0185 | -0.0065 | -360.1773 | 17.3946 | -360.405 | 17.6492 | -360.7897 | 18.1584 | -360.8204 | 17.5917 | -352.5675 | 18.6922 | -352.6167 | 16.8032
12:57 | 5840 | 50.1275 | 202.9598 | 449.4209 | 452.1326 | -17.0021 | -38.9821 | 11.8836 | 7.9832 | 2.2933 | 0.7449 | 2.773 | -1.1185 | 12.1768 | 5.2522 | 0.6238 | 0.6651 | 0.9669 | 0.7523 | -129.2928 | 1.6047 | 5.753 | 2.0106 | -2.5458 | -0.7619 | 4.9034 |  | 4.3732 | 0.7686 | 4.0068 | 3.3679 | 3.3363 | 1.0946 | 10.7752 | 14.2836 | 14.8761 | 11.1219 | 0.0001 | -0.0029 | 0.0005 | 0.0036 | 0.0011 | -0.0005 | 0.0159 | -0.0133 | 0.0013 | -360.1465 | 17.3925 | -360.4235 | 17.643 | -360.7589 | 18.1461 | -360.8112 | 17.5855 | -352.586 | 18.6902 | -352.589 | 16.793
12:57 | 5841 | 50.0024 | 203.0281 | 449.3116 | 452.1529 | -17.017 | -38.8704 | 11.7973 | 8.0688 | 2.3471 | 0.7599 | 2.9456 | -1.1183 | 12.1836 | 5.3395 | 0.6242 | 0.6643 | 0.9643 | 0.753 | -129.188 | 1.7245 | 5.8217 | 2.0063 | -2.477 | -0.8348 | 4.8225 |  | 4.3825 | 0.8733 | 4.0062 | 3.3664 | 3.3334 | 1.094 | 10.773 | 14.2868 | 14.826 | 11.097 | -0.0001 | -0.0024 | 0.001 | 0.0039 | 0.0006 | -0.0007 | 0.0184 | -0.014 | 0.0023 | -360.1927 | 17.409 | -360.4789 | 17.6636 | -360.7989 | 18.1522 | -360.8174 | 17.5814 | -352.6075 | 18.7045 | -352.6352 | 16.8176
12:57 | 5842 | 49.9706 | 203.0566 | 449.2815 | 452.1016 | -16.9755 | -38.7545 | 11.8283 | 8.0787 | 2.4448 | 0.7493 | 2.972 | -1.0883 | 12.2159 | 5.2691 | 0.6247 | 0.6657 | 0.9701 | 0.7538 | -129.2638 | 1.8096 | 5.7004 | 1.9891 | -2.4073 | -0.7609 | 4.9566 |  | 4.4135 | 0.9431 | 4.0074 | 3.368 | 3.3296 | 1.0956 | 10.7776 | 14.2627 | 14.8372 | 11.084 | 0.0003 | -0.0024 | 0.0012 | 0.0039 | 0.001 | -0.0001 | 0.0085 | -0.0091 | -0.0065 | -360.1342 | 17.3823 | -360.4142 | 17.641 | -360.8204 | 18.1707 | -360.8512 | 17.5958 | -352.589 | 18.6737 | -352.5952 | 16.7991
12:57 | 5843 | 50.0497 | 202.9065 | 449.4095 | 452.1951 | -16.9269 | -38.6989 | 11.8645 | 8.0558 | 2.294 | 0.6482 | 2.8755 | -0.8475 | 12.2698 | 5.3067 | 0.6237 | 0.6629 | 0.9671 | 0.7531 | -129.2744 | 1.6562 | 5.6474 | 1.9165 | -2.3806 | -0.7446 | 4.9591 |  | 4.3564 | 0.7566 | 4.0073 | 3.3697 | 3.3329 | 1.0943 | 10.7937 | 14.279 | 14.8427 | 11.123 | 0.0001 | -0.0031 | 0.0013 | 0.0042 | 0.001 | -0.0004 | 0.0081 | -0.0074 | -0.016 | -360.2265 | 17.4377 | -360.4696 | 17.6389 | -360.8081 | 18.1481 | -360.7866 | 17.6081 | -352.6629 | 18.721 | -352.6475 | 16.8053
12:57 | 5844 | 50.0089 | 202.9757 | 449.4373 | 452.1141 | -16.8731 | -38.7299 | 11.8223 | 8.0661 | 2.3427 | 0.6771 | 2.9167 | -0.9591 | 12.2429 | 5.221 | 0.6244 | 0.6609 | 0.9696 | 0.7536 | -129.2844 | 1.7172 | 5.6321 | 1.9422 | -2.4203 | -0.7824 | 4.985 |  | 4.4095 | 0.8308 | 4.0079 | 3.3688 | 3.3366 | 1.0958 | 10.78 | 14.253 | 14.8715 | 11.0815 | -0.0002 | -0.0035 | 0.0012 | 0.0041 | 0.0001 | -0.0008 | 0.0085 | -0.0024 | -0.0209 | -360.1404 | 17.4048 | -360.4973 | 17.6759 | -360.8512 | 18.1707 | -360.8204 | 17.5773 | -352.5921 | 18.7004 | -352.6475 | 16.8258
12:57 | 5845 | 49.948 | 202.9422 | 449.3252 | 452.0618 | -16.9594 | -38.8192 | 11.6997 | 7.975 | 2.3055 | 0.5681 | 2.8283 | -0.8677 | 12.2869 | 5.2763 | 0.6234 | 0.6649 | 0.9655 | 0.7526 | -129.2424 | 1.6456 | 5.5779 | 1.8983 | -2.4291 | -0.8756 | 4.9172 |  | 4.3748 | 0.7831 | 4.0065 | 3.3675 | 3.3313 | 1.0966 | 10.8086 | 14.277 | 14.8663 | 11.137 | 0.0004 | -0.0021 | 0.001 | 0.0038 | 0.0008 | -0.0007 | -0.0018 | -0.0041 | 0.0026 | -360.2235 | 17.4172 | -360.4389 | 17.6389 | -360.8112 | 18.1769 | -360.882 | 17.6102 | -352.6198 | 18.7066 | -352.6136 | 16.8094
12:57 | 5846 | 50.0806 | 203.0973 | 449.5092 | 452.1703 | -16.9186 | -38.7747 | 11.7823 | 8.0223 | 2.3185 | 0.5463 | 2.8533 | -0.9528 | 12.263 | 5.2023 | 0.6223 | 0.664 | 0.9638 | 0.7524 | -129.2599 | 1.69 | 5.7306 | 1.8708 | -2.3887 | -0.7457 | 4.8842 |  | 4.3367 | 0.7451 | 4.007 | 3.3657 | 3.33 | 1.0958 | 10.8089 | 14.2761 | 14.8657 | 11.1046 | -0.0003 | -0.0029 | 0.0004 | 0.0041 | 0.0006 | -0.0003 | 0.0272 | -0.013 | 0.0001 | -360.2327 | 17.448 | -360.5004 | 17.6677 | -360.8143 | 18.1337 | -360.7866 | 17.5978 | -352.6629 | 18.7395 | -352.6813 | 16.8238
12:57 | 5847 | 50.0759 | 203.025 | 449.4021 | 452.1785 | -16.8123 | -38.7501 | 11.8827 | 8.0488 | 2.3648 | 0.6146 | 2.7854 | -1.0453 | 12.2412 | 5.1731 | 0.6239 | 0.6659 | 0.9664 | 0.7522 | -129.2442 | 1.6813 | 5.6832 | 1.8784 | -2.5081 | -0.8598 | 4.9276 |  | 4.3372 | 0.8394 | 4.0055 | 3.3666 | 3.3369 | 1.0955 | 10.7868 | 14.2776 | 14.8692 | 11.1049 | 0.0002 | -0.0029 | 0.0011 | 0.0041 | 0.001 | -0.0008 | 0.0188 | 0.0007 | 0.0034 | -360.1373 | 17.4069 | -360.4481 | 17.6636 | -360.8758 | 18.1871 | -360.8666 | 17.5999 | -352.629 | 18.6881 | -352.6475 | 16.8258
12:57 | 5848 | 50.0142 | 203.0502 | 449.3435 | 452.1994 | -16.8485 | -38.7552 | 11.898 | 8.0879 | 2.3732 | 0.5773 | 2.7899 | -1.0207 | 12.216 | 5.18 | 0.6235 | 0.6641 | 0.968 | 0.7525 | -129.155 | 1.6603 | 5.766 | 1.9572 | -2.4571 | -0.76 | 4.97 |  | 4.4024 | 0.8854 | 4.0063 | 3.3694 | 3.3368 | 1.0945 | 10.7879 | 14.2674 | 14.8311 | 11.0883 | 0.0002 | -0.0027 | 0.0008 | 0.0037 | 0.0006 | -0.0004 | 0.0043 | 0.0001 | -0.0114 | -360.2542 | 17.4336 | -360.4481 | 17.6328 | -360.7773 | 18.1481 | -360.8358 | 17.6286 | -352.666 | 18.7169 | -352.6383 | 16.795
12:57 | 5849 | 50.0015 | 202.98 | 449.3905 | 452.1719 | -16.9576 | -38.8985 | 11.7827 | 8.1643 | 2.4732 | 0.6092 | 2.9179 | -0.8984 | 12.2951 | 5.3234 | 0.6237 | 0.6622 | 0.9643 | 0.7516 | -129.2032 | 1.6528 | 5.7672 | 1.953 | -2.4441 | -0.8465 | 4.9108 |  | 4.3933 | 0.8841 | 4.0073 | 3.3674 | 3.3341 | 1.0949 | 10.7823 | 14.2899 | 14.8385 | 11.084 | -0.0005 | -0.0027 | 0.0005 | 0.0038 | 0.0009 | -0.0009 | 0.0024 | -0.0088 | -0.0072 | -360.1773 | 17.4397 | -360.4973 | 17.6841 | -360.8697 | 18.144 | -360.8081 | 17.5896 | -352.6229 | 18.7271 | -352.709 | 16.8484
12:57 | 5850 | 50.0051 | 203.0509 | 449.4107 | 452.2531 | -17.0178 | -38.8493 | 11.759 | 8.1069 | 2.4992 | 0.5794 | 2.8869 | -0.8844 | 12.2986 | 5.3769 | 0.6253 | 0.6659 | 0.9673 | 0.7524 | -129.1839 | 1.6533 | 5.725 | 1.8375 | -2.3835 | -0.693 | 4.9021 |  | 4.4728 | 0.9391 | 4.0075 | 3.3674 | 3.3359 | 1.0934 | 10.7776 | 14.2569 | 14.872 | 11.0666 | 0 | -0.0029 | 0.0012 | 0.0037 | 0.0008 | -0.0001 | 0.015 | -0.004 | -0.0207 | -360.165 | 17.3905 | -360.3989 | 17.6553 | -360.8235 | 18.1892 | -360.9189 | 17.6163 | -352.6229 | 18.682 | -352.589 | 16.8135
12:57 | 5851 | 50.025 | 203.0653 | 449.3814 | 452.2618 | -16.9113 | -38.8413 | 11.6826 | 8.0635 | 2.5437 | 0.5717 | 2.872 | -0.8541 | 12.3375 | 5.3194 | 0.6236 | 0.6653 | 0.9655 | 0.7506 | -129.2171 | 1.713 | 5.7346 | 1.7947 | -2.3685 | -0.7633 | 4.8489 |  | 4.4594 | 0.8985 | 4.0072 | 3.3634 | 3.3355 | 1.0951 | 10.7937 | 14.3021 | 14.8775 | 11.1114 | -0.0003 | -0.0032 | 0.0012 | 0.004 | 0.0009 | -0.0007 | 0.0103 | -0.0124 | -0.0112 | -360.2512 | 17.4459 | -360.4819 | 17.6574 | -360.7958 | 18.1276 | -360.8327 | 17.6204 | -352.629 | 18.7312 | -352.6752 | 16.8053
12:57 | 5852 | 50.0661 | 202.9565 | 449.3767 | 452.208 | -16.845 | -38.6539 | 11.8795 | 8.0864 | 2.5946 | 0.6317 | 2.8573 | -0.9595 | 12.3061 | 5.3422 | 0.6258 | 0.667 | 0.9679 | 0.7527 | -129.2224 | 1.6949 | 5.7945 | 1.7669 | -2.3355 | -0.7792 | 4.8765 |  | 4.514 | 0.9428 | 4.0071 | 3.3667 | 3.3329 | 1.093 | 10.8043 | 14.2831 | 14.8613 | 11.0826 | 0 | -0.003 | 0.0012 | 0.0046 | 0.0004 | -0.0002 | -0.0051 | -0.003 | 0.0062 | -360.1773 | 17.4192 | -360.4942 | 17.6985 | -360.9004 | 18.1625 | -360.8727 | 17.5896 | -352.5952 | 18.7087 | -352.669 | 16.8505
12:57 | 5853 | 50.1415 | 203.0542 | 449.4854 | 452.2202 | -16.9465 | -38.6719 | 11.8855 | 8.1055 | 2.6037 | 0.6686 | 2.8872 | -1.1244 | 12.3132 | 5.2823 | 0.6236 | 0.6664 | 0.9685 | 0.7522 | -129.3398 | 1.6045 | 5.7895 | 1.8751 | -2.3681 | -0.8106 | 4.9086 |  | 4.4403 | 0.774 | 4.0074 | 3.368 | 3.3326 | 1.095 | 10.8214 | 14.3072 | 14.8967 | 11.115 | -0.0003 | -0.0026 | 0.0007 | 0.0037 | 0.0011 | -0.0005 | 0.0156 | 0.0076 | 0.0116 | -360.2173 | 17.411 | -360.4019 | 17.643 | -360.8174 | 18.1748 | -360.8758 | 17.6184 | -352.6444 | 18.7025 | -352.5829 | 16.7991
12:57 | 5854 | 50.1705 | 203.0921 | 449.562 | 452.2529 | -16.9478 | -38.6363 | 11.8097 | 8.104 | 2.662 | 0.645 | 2.9312 | -1.0492 | 12.2977 | 5.265 | 0.6261 | 0.6689 | 0.9717 | 0.7525 | -129.2515 | 1.6498 | 5.799 | 1.9131 | -2.4203 | -0.7276 | 4.91 |  | 4.4416 | 0.8045 | 4.0058 | 3.3666 | 3.3325 | 1.0955 | 10.8111 | 14.3077 | 14.8706 | 11.1233 | -0.0001 | -0.0028 | 0.0004 | 0.0036 | 0.0003 | -0.0006 | 0.0095 | -0.0011 | 0.0103 | -360.2419 | 17.4459 | -360.4912 | 17.6636 | -360.7989 | 18.1379 | -360.845 | 17.6102 | -352.6567 | 18.7456 | -352.669 | 16.8156
12:57 | 5855 | 50.2405 | 203.0461 | 449.5508 | 452.2126 | -16.9291 | -38.6964 | 11.9278 | 8.1578 | 2.5933 | 0.738 | 2.8091 | -1.0014 | 12.2881 | 5.1852 | 0.6253 | 0.6633 | 0.9656 | 0.7523 | -129.24 | 1.7565 | 5.7763 | 1.9333 | -2.3435 | -0.7225 | 4.8994 |  | 4.4193 | 0.8008 | 4.0065 | 3.3689 | 3.3311 | 1.0955 | 10.7881 | 14.2843 | 14.8511 | 11.0894 | 0.0002 | -0.0033 | 0.0009 | 0.0041 | 0.0008 | -0.0003 | 0.014 | -0.0157 | -0.0138 | -360.1311 | 17.411 | -360.485 | 17.6841 | -360.8943 | 18.1748 | -360.8327 | 17.5896 | -352.5921 | 18.6963 | -352.6721 | 16.8423
12:57 | 5856 | 50.1462 | 203.0801 | 449.5065 | 452.2672 | -16.8777 | -38.6633 | 12.014 | 8.0789 | 2.6489 | 0.6335 | 2.8514 | -1.0092 | 12.3621 | 5.2888 | 0.6252 | 0.6638 | 0.9676 | 0.7531 | -129.204 | 1.7965 | 5.7319 | 2.1077 | -2.3775 | -0.77 | 4.9834 |  | 4.4454 | 0.8918 | 4.0073 | 3.3687 | 3.3366 | 1.0951 | 10.7891 | 14.2858 | 14.8546 | 11.1302 | 0.0001 | -0.003 | 0.0006 | 0.0039 | 0.001 | -0.0006 | 0.0145 | -0.0031 | -0.0182 | -360.2081 | 17.409 | -360.4266 | 17.643 | -360.7989 | 18.1728 | -360.8943 | 17.6389 | -352.6352 | 18.7087 | -352.629 | 16.795
12:57 | 5857 | 50.1425 | 203.0181 | 449.4496 | 452.1615 | -16.9023 | -38.727 | 11.8998 | 8.1313 | 2.6772 | 0.6873 | 2.8162 | -1.0432 | 12.3421 | 5.3482 | 0.6252 | 0.6642 | 0.9697 | 0.7527 | -129.3088 | 1.863 | 5.7124 | 1.9901 | -2.5015 | -0.7429 | 4.8986 |  | 4.4598 | 0.822 | 4.0071 | 3.3653 | 3.332 | 1.0945 | 10.7834 | 14.245 | 14.8467 | 11.0963 | -0.0004 | -0.0026 | 0.0006 | 0.0037 | 0.0007 | -0.0003 | 0.0039 | -0.0096 | -0.0111 | -360.2358 | 17.4664 | -360.485 | 17.6677 | -360.8235 | 18.142 | -360.8174 | 17.6143 | -352.6844 | 18.7395 | -352.7121 | 16.8238
12:57 | 5858 | 50.098 | 203.0258 | 449.4461 | 452.1368 | -16.9785 | -38.8057 | 11.7469 | 8.1305 | 2.6019 | 0.7211 | 2.8378 | -1.1025 | 12.3164 | 5.246 | 0.6268 | 0.6673 | 0.9692 | 0.7527 | -129.3183 | 1.9042 | 5.615 | 1.7958 | -2.4832 | -0.7921 | 4.8784 |  | 4.4767 | 0.8722 | 4.0059 | 3.3671 | 3.3346 | 1.0958 | 10.7625 | 14.2535 | 14.811 | 11.0919 | -0.0001 | -0.0026 | 0.0014 | 0.0041 | 0.0015 | -0.0007 | 0.0283 | -0.0095 | -0.0172 | -360.1188 | 17.4048 | -360.4573 | 17.6738 | -360.9097 | 18.183 | -360.8666 | 17.5937 | -352.586 | 18.7004 | -352.6383 | 16.8299
12:57 | 5859 | 50.0201 | 202.9699 | 449.4297 | 452.161 | -17.0606 | -38.9137 | 11.7165 | 8.1671 | 2.6578 | 0.7311 | 2.9118 | -1.053 | 12.3039 | 5.286 | 0.6256 | 0.6648 | 0.9671 | 0.7511 | -129.3126 | 1.8838 | 5.6828 | 1.7509 | -2.5419 | -0.8918 | 4.8507 |  | 4.4454 | 0.9294 | 4.0087 | 3.3663 | 3.3341 | 1.0966 | 10.8191 | 14.2874 | 14.865 | 11.1013 | 0.0006 | -0.0027 | 0.0012 | 0.0037 | 0.0007 | -0.0001 | 0.0085 | -0.0075 | -0.0133 | -360.2296 | 17.4069 | -360.4296 | 17.6471 | -360.7958 | 18.1728 | -360.9066 | 17.6389 | -352.6629 | 18.7066 | -352.6013 | 16.7971
12:57 | 5860 | 50.0764 | 203.04 | 449.454 | 452.1519 | -17.0546 | -38.8149 | 11.668 | 8.0782 | 2.5749 | 0.6751 | 2.8301 | -1.0379 | 12.3205 | 5.3077 | 0.6259 | 0.6661 | 0.9672 | 0.7541 | -129.3552 | 1.8771 | 5.647 | 1.8068 | -2.5495 | -0.8733 | 4.8332 |  | 4.4499 | 0.9963 | 4.0066 | 3.3691 | 3.332 | 1.0958 | 10.788 | 14.296 | 14.8348 | 11.1064 | 0.0001 | -0.0031 | 0.0005 | 0.0033 | 0.001 | -0.0004 | 0.0266 | -0.0041 | -0.0241 | -360.1835 | 17.4582 | -360.5158 | 17.6759 | -360.8574 | 18.1317 | -360.7958 | 17.5978 | -352.6721 | 18.7436 | -352.709 | 16.832
12:57 | 5861 | 50.1925 | 203.0452 | 449.4555 | 452.183 | -17.0514 | -38.9055 | 11.7432 | 8.1747 | 2.6505 | 0.7385 | 2.792 | -1.0139 | 12.3032 | 5.2994 | 0.6268 | 0.6667 | 0.966 | 0.752 | -129.3058 | 1.879 | 5.6578 | 1.9272 | -2.4826 | -0.7565 | 4.9842 |  | 4.4192 | 0.9935 | 4.0072 | 3.3657 | 3.3356 | 1.0957 | 10.7903 | 14.2985 | 14.8676 | 11.1024 | -0.0002 | -0.0027 | 0.001 | 0.0041 | 0.0005 | -0.0002 | 0.0083 | -0.0087 | -0.0225 | -360.1773 | 17.3905 | -360.4389 | 17.6779 | -360.8543 | 18.181 | -360.8635 | 17.5937 | -352.586 | 18.6881 | -352.6383 | 16.8258
12:57 | 5862 | 50.1203 | 203 | 449.4251 | 452.1262 | -17.0992 | -38.852 | 11.7138 | 8.1437 | 2.641 | 0.6122 | 2.8083 | -1.1175 | 12.2853 | 5.2566 | 0.6257 | 0.6644 | 0.9639 | 0.7525 | -129.2824 | 1.9263 | 5.6991 | 1.979 | -2.476 | -0.8867 | 4.938 |  | 4.444 | 0.9631 | 4.0069 | 3.3696 | 3.3339 | 1.0966 | 10.788 | 14.273 | 14.8417 | 11.1175 | 0.0002 | -0.0021 | 0.0003 | 0.004 | 0.0009 | -0.0004 | 0.032 | -0.0175 | -0.017 | -360.2296 | 17.4069 | -360.4358 | 17.641 | -360.805 | 18.1666 | -360.8912 | 17.6369 | -352.6783 | 18.7087 | -352.6075 | 16.8012
12:57 | 5863 | 50.1504 | 202.9603 | 449.52 | 452.0987 | -17.06 | -38.8951 | 11.7792 | 8.1606 | 2.6169 | 0.6164 | 2.8434 | -1.0704 | 12.2557 | 5.2557 | 0.6272 | 0.6661 | 0.9663 | 0.7524 | -129.2665 | 1.8445 | 5.7094 | 1.8745 | -2.4239 | -0.8945 | 4.9283 |  | 4.3904 | 0.98 | 4.0075 | 3.3652 | 3.3312 | 1.096 | 10.7846 | 14.2634 | 14.8586 | 11.1093 | 0 | -0.0032 | 0.0009 | 0.004 | 0.0005 | -0.0004 | 0.0067 | -0.0168 | -0.0016 | -360.1711 | 17.4439 | -360.5219 | 17.6779 | -360.8204 | 18.1255 | -360.7804 | 17.5937 | -352.6413 | 18.7395 | -352.7152 | 16.8279
12:57 | 5864 | 50.189 | 203.038 | 449.3991 | 452.0652 | -16.993 | -38.8623 | 11.7745 | 8.1635 | 2.6037 | 0.8187 | 2.9452 | -1.0664 | 12.2488 | 5.2208 | 0.6267 | 0.6675 | 0.9652 | 0.7538 | -129.278 | 1.809 | 5.6973 | 1.8709 | -2.4948 | -0.8499 | 4.9217 |  | 4.4608 | 0.9776 | 4.0062 | 3.3664 | 3.3316 | 1.0957 | 10.7914 | 14.2592 | 14.8689 | 11.063 | 0.0003 | -0.0027 | 0.0014 | 0.0044 | 0.0013 | -0.0007 | 0.0211 | -0.0092 | -0.0078 | -360.1465 | 17.3823 | -360.4604 | 17.6779 | -360.8758 | 18.1851 | -360.8543 | 17.5978 | -352.5983 | 18.6922 | -352.6383 | 16.8361
12:57 | 5865 | 50.2016 | 203.0897 | 449.5165 | 452.0254 | -17.072 | -38.8992 | 11.7648 | 8.15 | 2.6283 | 0.8462 | 2.8978 | -1.0471 | 12.2944 | 5.2114 | 0.6268 | 0.667 | 0.9668 | 0.7532 | -129.3115 | 1.8412 | 5.6938 | 2.0144 | -2.5107 | -0.9115 | 4.9145 |  | 4.419 | 1.0091 | 4.0064 | 3.3662 | 3.3279 | 1.0941 | 10.8054 | 14.2787 | 14.8638 | 11.1006 | -0.0003 | -0.0028 | 0.0009 | 0.0034 | 0.0007 | -0.0003 | 0.0227 | 0.004 | -0.0108 | -360.2481 | 17.4172 | -360.4542 | 17.6471 | -360.7773 | 18.1563 | -360.845 | 17.6328 | -352.6813 | 18.7107 | -352.6537 | 16.8115
12:57 | 5866 | 50.1366 | 203.1318 | 449.4239 | 452.0964 | -17.0764 | -38.8713 | 11.7462 | 8.082 | 2.5376 | 0.8176 | 2.8644 | -1.1004 | 12.2298 | 5.2951 | 0.6254 | 0.6662 | 0.9684 | 0.7544 | -129.3052 | 1.8483 | 5.6913 | 2.015 | -2.4285 | -0.8482 | 5.0052 |  | 4.3259 | 0.9053 | 4.0064 | 3.367 | 3.3278 | 1.0966 | 10.7579 | 14.2487 | 14.8345 | 11.0934 | -0.0002 | -0.0021 | 0.0011 | 0.0042 | 0.0007 | -0.0009 | 0.0128 | 0.0002 | 0 | -360.1988 | 17.4521 | -360.5189 | 17.6882 | -360.8543 | 18.1358 | -360.802 | 17.5917 | -352.629 | 18.7292 | -352.6967 | 16.8484
12:57 | 5867 | 50.1834 | 203.1227 | 449.4235 | 452.1219 | -17.0009 | -38.786 | 11.8111 | 8.1337 | 2.5488 | 0.7492 | 2.8602 | -1.1153 | 12.2369 | 5.216 | 0.6244 | 0.6677 | 0.9675 | 0.7551 | -129.2317 | 1.8749 | 5.7363 | 2.0103 | -2.5401 | -0.8764 | 4.9267 |  | 4.3994 | 1.0048 | 4.0062 | 3.3674 | 3.3321 | 1.0952 | 10.8041 | 14.2836 | 14.8587 | 11.1103 | 0.0003 | -0.0027 | 0.0014 | 0.0039 | 0.0007 | -0.0001 | 0.0193 | -0.0076 | -0.0181 | -360.1527 | 17.3966 | -360.4542 | 17.6677 | -360.8697 | 18.1789 | -360.8758 | 17.6102 | -352.5952 | 18.6881 | -352.6352 | 16.8402
12:58 | 5868 | 50.0905 | 203.0808 | 449.4719 | 452.0685 | -16.9605 | -38.7797 | 11.8619 | 8.0486 | 2.6517 | 0.7763 | 2.8024 | -1.1092 | 12.1973 | 5.264 | 0.6256 | 0.6664 | 0.9673 | 0.7534 | -129.3399 | 1.8313 | 5.7747 | 1.7943 | -2.5458 | -0.8944 | 4.9063 |  | 4.4113 | 0.9518 | 4.0067 | 3.3724 | 3.3274 | 1.0958 | 10.7926 | 14.3067 | 14.8877 | 11.1161 | -0.0001 | -0.0034 | 0.0005 | 0.0037 | 0.0009 | -0.0003 | 0.0094 | -0.0121 | -0.0269 | -360.2665 | 17.4295 | -360.4573 | 17.6451 | -360.7804 | 18.1584 | -360.8604 | 17.641 | -352.6967 | 18.7189 | -352.6352 | 16.8156
12:58 | 5869 | 50.1538 | 203.1668 | 449.4821 | 452.1351 | -16.9082 | -38.8537 | 11.8021 | 7.9294 | 2.5839 | 0.7862 | 2.8655 | -1.0522 | 12.2133 | 5.3401 | 0.6247 | 0.6667 | 0.965 | 0.7536 | -129.2402 | 1.7994 | 5.7296 | 1.7855 | -2.6088 | -0.9085 | 4.8456 |  | 4.4502 | 0.897 | 4.0068 | 3.3707 | 3.3339 | 1.0959 | 10.8076 | 14.2929 | 14.8513 | 11.0904 | 0.0001 | -0.0027 | 0.001 | 0.0041 | 0.0011 | -0.0005 | -0.0055 | -0.02 | -0.0217 | -360.1711 | 17.4397 | -360.5189 | 17.6882 | -360.8666 | 18.144 | -360.802 | 17.5855 | -352.6229 | 18.7169 | -352.6783 | 16.8587
12:58 | 5870 | 50.2408 | 203.1702 | 449.627 | 452.1241 | -16.9051 | -38.7827 | 11.8541 | 8.005 | 2.5904 | 0.7901 | 2.8675 | -1.1363 | 12.2318 | 5.3627 | 0.6257 | 0.6661 | 0.9667 | 0.7549 | -129.2519 | 1.8556 | 5.745 | 1.9138 | -2.5728 | -0.9101 | 4.8042 |  | 4.4201 | 1.0397 | 4.0057 | 3.3674 | 3.3315 | 1.0959 | 10.7903 | 14.2868 | 14.8318 | 11.0912 | -0.0005 | -0.0028 | 0.0005 | 0.0038 | 0.0005 | -0.0001 | -0.0051 | -0.004 | -0.0144 | -360.1988 | 17.3925 | -360.4081 | 17.6718 | -360.8512 | 18.1912 | -360.8789 | 17.6184 | -352.6013 | 18.682 | -352.626 | 16.834
12:58 | 5871 | 50.2062 | 203.119 | 449.5449 | 452.209 | -16.9335 | -38.7954 | 11.7987 | 8.0801 | 2.6511 | 0.7933 | 2.8694 | -1.1415 | 12.2235 | 5.2327 | 0.6256 | 0.6644 | 0.9663 | 0.7535 | -129.2809 | 1.8351 | 5.6946 | 1.7586 | -2.5208 | -0.9334 | 4.8675 |  | 4.4665 | 0.92 | 4.0073 | 3.3664 | 3.3308 | 1.0962 | 10.7846 | 14.2925 | 14.8712 | 11.1378 | -0.0001 | -0.0032 | 0.0009 | 0.0041 | 0.001 | -0.0007 | 0.008 | -0.0091 | -0.0267 | -360.2019 | 17.4377 | -360.4758 | 17.6492 | -360.7712 | 18.1502 | -360.8481 | 17.6307 | -352.6752 | 18.7107 | -352.6506 | 16.8197
12:58 | 5872 | 50.2666 | 203.199 | 449.5975 | 452.2373 | -16.9458 | -38.7493 | 11.9052 | 8.0113 | 2.6047 | 0.8084 | 2.9008 | -1.075 | 12.2933 | 5.2169 | 0.626 | 0.6652 | 0.9647 | 0.7542 | -129.2862 | 1.8079 | 5.659 | 1.6952 | -2.5283 | -0.9658 | 4.8001 |  | 4.4122 | 0.9601 | 4.0074 | 3.3687 | 3.3286 | 1.0955 | 10.7477 | 14.2551 | 14.8027 | 11.0728 | 0.0002 | -0.0034 | 0.0012 | 0.0045 | 0.0008 | -0.0002 | -0.0103 | -0.0133 | -0.0202 | -360.1927 | 17.4274 | -360.5281 | 17.7149 | -360.8727 | 18.1584 | -360.8204 | 17.5876 | -352.6044 | 18.7128 | -352.6998 | 16.8689
12:58 | 5873 | 50.2714 | 203.1943 | 449.5836 | 452.1519 | -17.0342 | -38.8112 | 11.8552 | 8.0349 | 2.5966 | 0.8791 | 2.9625 | -1.0945 | 12.2425 | 5.1596 | 0.6245 | 0.6678 | 0.9656 | 0.7535 | -129.3115 | 1.816 | 5.5704 | 1.8341 | -2.4676 | -0.9476 | 4.9288 |  | 4.3553 | 0.973 | 4.0091 | 3.3678 | 3.3339 | 1.0951 | 10.7673 | 14.2692 | 14.8528 | 11.0746 | 0.0001 | -0.0029 | 0.001 | 0.0041 | 0.001 | -0.0006 | -0.003 | -0.0025 | -0.0196 | -360.2204 | 17.4007 | -360.4173 | 17.6594 | -360.8174 | 18.1953 | -360.8943 | 17.6286 | -352.6629 | 18.6861 | -352.5952 | 16.8217
12:58 | 5874 | 50.2311 | 203.1648 | 449.6893 | 452.1763 | -17.0179 | -38.8351 | 11.8791 | 8.0386 | 2.5645 | 0.8561 | 2.908 | -1.0194 | 12.2756 | 5.2954 | 0.6271 | 0.6678 | 0.9687 | 0.7547 | -129.3332 | 1.8314 | 5.5473 | 1.852 | -2.5147 | -0.992 | 4.8743 |  | 4.3987 | 0.9593 | 4.006 | 3.3675 | 3.3317 | 1.0942 | 10.7522 | 14.2428 | 14.7987 | 11.0706 | -0.0003 | -0.0028 | 0.0015 | 0.0045 | 0.0003 | -0.0007 | 0.0035 | -0.0093 | -0.0104 | -360.2111 | 17.4418 | -360.4696 | 17.6738 | -360.7773 | 18.1399 | -360.8389 | 17.6081 | -352.6906 | 18.7251 | -352.666 | 16.8279
12:58 | 5875 | 50.1118 | 203.0995 | 449.6284 | 452.0867 | -17.0937 | -38.8657 | 11.8061 | 8.0547 | 2.5498 | 0.749 | 2.8933 | -1.0365 | 12.3313 | 5.3116 | 0.6255 | 0.667 | 0.9674 | 0.7545 | -129.3279 | 1.795 | 5.6881 | 1.8398 | -2.557 | -1.2182 | 4.802 |  | 4.3523 | 0.8997 | 4.0058 | 3.3694 | 3.3326 | 1.0959 | 10.8191 | 14.2815 | 14.9044 | 11.0958 | -0.0001 | -0.0029 | 0.0011 | 0.0042 | 0.0011 | -0.0005 | 0.0132 | -0.0035 | -0.0059 | -360.1558 | 17.4151 | -360.5158 | 17.7087 | -360.8943 | 18.1748 | -360.8574 | 17.5855 | -352.6229 | 18.7087 | -352.6752 | 16.8607
12:58 | 5876 | 50.1754 | 203.1311 | 449.5698 | 452.0989 | -16.9699 | -38.8699 | 11.8051 | 8.0282 | 2.397 | 0.6813 | 2.8791 | -1.063 | 12.3264 | 5.2585 | 0.6254 | 0.6663 | 0.9695 | 0.7537 | -129.3094 | 1.7314 | 5.6651 | 1.8841 | -2.54 | -0.8709 | 4.892 |  | 4.3662 | 0.8349 | 4.0073 | 3.3706 | 3.3322 | 1.095 | 10.8329 | 14.3189 | 14.8919 | 11.1262 | 0.0006 | -0.0024 | 0.0004 | 0.004 | 0.0007 | -0.0001 | 0.0142 | -0.0063 | 0.0068 | -360.1988 | 17.411 | -360.4142 | 17.6451 | -360.805 | 18.1769 | -360.9097 | 17.6307 | -352.6475 | 18.6963 | -352.5983 | 16.8156
12:58 | 5877 | 50.1032 | 203.084 | 449.4597 | 452.0143 | -16.9984 | -38.844 | 11.8355 | 8.0266 | 2.4394 | 0.7595 | 2.9061 | -1.0731 | 12.231 | 5.2893 | 0.6249 | 0.6658 | 0.9673 | 0.7538 | -129.1967 | 1.8681 | 5.6434 | 1.8917 | -2.5564 | -0.9203 | 4.856 |  | 4.3623 | 0.8996 | 4.0061 | 3.3688 | 3.3328 | 1.0953 | 10.7857 | 14.3111 | 14.8679 | 11.1212 | -0.0004 | -0.0031 | 0.0006 | 0.0039 | 0.0005 | -0.0007 | -0.0058 | -0.0103 | -0.0189 | -360.205 | 17.4623 | -360.5435 | 17.682 | -360.805 | 18.1461 | -360.7958 | 17.5978 | -352.6598 | 18.7477 | -352.7183 | 16.8423
12:58 | 5878 | 50.209 | 203.1673 | 449.4704 | 452.052 | -16.966 | -38.7437 | 11.9241 | 8.0395 | 2.4686 | 0.78 | 2.8951 | -1.1263 | 12.2368 | 5.3673 | 0.6236 | 0.6641 | 0.9644 | 0.7534 | -129.2612 | 1.8152 | 5.692 | 1.8476 | -2.6161 | -0.9559 | 4.8133 |  | 4.381 | 0.7974 | 4.0073 | 3.369 | 3.3345 | 1.0955 | 10.7868 | 14.2892 | 14.875 | 11.1165 | -0.0003 | -0.0026 | 0.0001 | 0.0033 | 0.0006 | -0.0003 | 0.021 | -0.0047 | -0.0114 | -360.1373 | 17.4007 | -360.4512 | 17.6861 | -360.885 | 18.1871 | -360.845 | 17.5896 | -352.5921 | 18.682 | -352.6352 | 16.8505
12:58 | 5879 | 50.2346 | 203.0992 | 449.5927 | 452.0941 | -16.8999 | -38.732 | 11.8319 | 8.0699 | 2.5304 | 0.9335 | 2.8929 | -1.1038 | 12.178 | 5.3864 | 0.6252 | 0.6692 | 0.9674 | 0.7552 | -129.206 | 1.9241 | 5.6607 | 1.8724 | -2.6525 | -0.9919 | 4.8438 |  | 4.4114 | 0.8497 | 4.0069 | 3.3702 | 3.3327 | 1.0958 | 10.7695 | 14.2544 | 14.8334 | 11.0591 | 0.0001 | -0.0029 | 0.0006 | 0.0039 | 0.0007 | -0.0002 | 0.0005 | -0.0062 | -0.0063 | -360.2111 | 17.4213 | -360.4296 | 17.6471 | -360.8112 | 18.1666 | -360.8574 | 17.643 | -352.6967 | 18.6943 | -352.6413 | 16.8238
12:58 | 5880 | 50.2435 | 203.1588 | 449.595 | 452.1446 | -16.894 | -38.7385 | 11.8546 | 8.0494 | 2.4443 | 0.794 | 2.8424 | -1.0973 | 12.2736 | 5.412 | 0.6257 | 0.6691 | 0.9644 | 0.7525 | -129.2189 | 1.7363 | 5.6209 | 1.9364 | -2.6371 | -0.9701 | 4.8237 |  | 4.3421 | 0.9793 | 4.0062 | 3.3694 | 3.3266 | 1.0956 | 10.7753 | 14.2603 | 14.875 | 11.1107 | 0 | -0.003 | 0.0009 | 0.0039 | 0.0011 | -0.0005 | -0.0084 | -0.0033 | -0.0163 | -360.1958 | 17.4562 | -360.5219 | 17.6759 | -360.845 | 18.1317 | -360.8081 | 17.5917 | -352.6567 | 18.7271 | -352.706 | 16.8628
12:58 | 5881 | 50.3219 | 203.1938 | 449.6555 | 452.1601 | -16.9659 | -38.75 | 11.8865 | 8.0172 | 2.4628 | 0.6378 | 2.9218 | -1.0683 | 12.302 | 5.459 | 0.6249 | 0.667 | 0.9658 | 0.753 | -129.2895 | 1.8089 | 5.6581 | 1.9666 | -2.5787 | -0.907 | 4.8463 |  | 4.416 | 1.019 | 4.0062 | 3.368 | 3.3295 | 1.0959 | 10.7798 | 14.2708 | 14.7995 | 11.0803 | 0 | -0.0025 | 0.001 | 0.0039 | 0.0005 | -0.0007 | 0.013 | -0.0095 | -0.0069 | -360.1527 | 17.3946 | -360.4296 | 17.6718 | -360.8512 | 18.181 | -360.8666 | 17.6081 | -352.6106 | 18.682 | -352.629 | 16.8443
12:58 | 5882 | 50.2796 | 203.1064 | 449.5709 | 452.182 | -17.135 | -38.8412 | 11.7659 | 7.9979 | 2.4903 | 0.6645 | 2.8627 | -1.0312 | 12.3184 | 5.434 | 0.6245 | 0.6643 | 0.969 | 0.7537 | -129.1957 | 1.7774 | 5.6252 | 2.0505 | -2.5133 | -0.8656 | 4.8602 |  | 4.3211 | 0.9383 | 4.007 | 3.3699 | 3.3376 | 1.0964 | 10.7742 | 14.2704 | 14.8252 | 11.0699 | -0.0003 | -0.0024 | 0.0007 | 0.0034 | 0.0011 | -0.0006 | 0.006 | -0.0217 | -0.0098 | -360.2419 | 17.4254 | -360.4389 | 17.641 | -360.7866 | 18.1502 | -360.8635 | 17.6328 | -352.666 | 18.7025 | -352.629 | 16.8258
12:58 | 5883 | 50.2378 | 203.1031 | 449.5614 | 452.1687 | -17.1468 | -38.8778 | 11.7778 | 8.0312 | 2.5886 | 0.8065 | 2.9172 | -1.0922 | 12.2885 | 5.3548 | 0.6242 | 0.666 | 0.9658 | 0.752 | -129.2071 | 1.7171 | 5.5935 | 2.0903 | -2.4915 | -0.8015 | 4.9787 |  | 4.2241 | 0.8461 | 4.0079 | 3.3678 | 3.3303 | 1.0954 | 10.826 | 14.283 | 14.8732 | 11.0731 | 0.0003 | -0.0023 | 0.0005 | 0.0039 | 0.0006 | 0 | 0.0158 | -0.0046 | 0.0105 | -360.1711 | 17.4274 | -360.4881 | 17.6985 | -360.8727 | 18.1337 | -360.8204 | 17.5855 | -352.5983 | 18.7025 | -352.709 | 16.8689
12:58 | 5884 | 50.2388 | 203.114 | 449.5872 | 452.1644 | -17.0919 | -38.8568 | 11.7491 | 7.9566 | 2.5413 | 0.7543 | 2.8655 | -1.0849 | 12.241 | 5.3228 | 0.6259 | 0.6646 | 0.9647 | 0.7525 | -129.1988 | 1.719 | 5.5948 | 2.0422 | -2.5267 | -0.8144 | 4.9601 |  | 4.2655 | 0.7601 | 4.006 | 3.368 | 3.3346 | 1.0959 | 10.8203 | 14.2999 | 14.8932 | 11.1493 | 0.0005 | -0.0031 | 0.0003 | 0.0037 | 0.0013 | -0.0004 | 0.0119 | -0.0065 | -0.006 | -360.1496 | 17.3884 | -360.4019 | 17.6615 | -360.8297 | 18.1912 | -360.9004 | 17.6204 | -352.6229 | 18.6758 | -352.6106 | 16.834
12:58 | 5885 | 50.241 | 203.0416 | 449.5884 | 452.1216 | -17.0505 | -38.7971 | 11.843 | 7.9439 | 2.4898 | 0.8484 | 2.941 | -0.9961 | 12.2761 | 5.3403 | 0.624 | 0.6681 | 0.9659 | 0.7544 | -129.2043 | 1.7346 | 5.6939 | 2.0487 | -2.5303 | -0.8608 | 4.8672 |  | 4.3227 | 0.7789 | 4.0071 | 3.3684 | 3.3312 | 1.0961 | 10.7741 | 14.288 | 14.8737 | 11.1038 | 0.0002 | -0.0028 | 0.0006 | 0.0036 | 0.0009 | 0.0004 | 0.0155 | -0.0031 | -0.0134 | -360.2481 | 17.4336 | -360.4666 | 17.6512 | -360.762 | 18.1296 | -360.8358 | 17.604 | -352.6567 | 18.723 | -352.6629 | 16.8299
12:58 | 5886 | 50.3279 | 203.091 | 449.5543 | 452.1635 | -17.0347 | -38.7282 | 11.9318 | 7.978 | 2.4794 | 0.8366 | 2.856 | -1.0525 | 12.2049 | 5.2823 | 0.6254 | 0.669 | 0.9692 | 0.7555 | -129.267 | 1.7446 | 5.6526 | 1.9726 | -2.4864 | -0.8943 | 4.8732 |  | 4.2259 | 0.7664 | 4.0062 | 3.3694 | 3.3334 | 1.0958 | 10.796 | 14.3104 | 14.9044 | 11.1363 | -0.0002 | -0.0024 | 0.0005 | 0.0041 | 0.0012 | -0.0004 | 0.0077 | -0.0137 | -0.0003 | -360.1342 | 17.3987 | -360.4758 | 17.6964 | -360.885 | 18.1687 | -360.8297 | 17.5855 | -352.5952 | 18.6881 | -352.6844 | 16.8669
12:58 | 5887 | 50.2616 | 203.1004 | 449.5034 | 452.1672 | -16.9597 | -38.5248 | 11.9597 | 8.0016 | 2.4928 | 0.8311 | 2.8847 | -1.0163 | 12.3168 | 5.3849 | 0.6242 | 0.6696 | 0.9684 | 0.7542 | -129.269 | 1.7512 | 5.6216 | 2.0728 | -2.4812 | -1.0096 | 4.8238 |  | 4.158 | 0.6873 | 4.0056 | 3.3671 | 3.3337 | 1.096 | 10.7696 | 14.2658 | 14.8497 | 11.0826 | 0.0001 | -0.0028 | 0.0008 | 0.004 | 0.0003 | -0.0003 | 0.0167 | -0.0088 | -0.0094 | -360.1681 | 17.3905 | -360.405 | 17.6451 | -360.7866 | 18.1604 | -360.8789 | 17.6266 | -352.6413 | 18.682 | -352.6136 | 16.8217
12:58 | 5888 | 50.2776 | 203.1177 | 449.5145 | 452.1776 | -16.8816 | -38.4813 | 11.9498 | 8.0053 | 2.4716 | 0.6999 | 2.9428 | -1.0287 | 12.2077 | 5.3098 | 0.6255 | 0.6685 | 0.9682 | 0.7534 | -129.2065 | 1.7772 | 5.6746 | 2.0239 | -2.6019 | -1.0031 | 4.8572 |  | 4.1845 | 0.7736 | 4.0068 | 3.3689 | 3.3329 | 1.0972 | 10.759 | 14.2616 | 14.8485 | 11.0825 | 0.0007 | -0.0026 | 0.0018 | 0.0046 | 0.0011 | -0.0004 | 0.0061 | -0.0085 | -0.0015 | -360.1619 | 17.4397 | -360.5096 | 17.6759 | -360.802 | 18.1214 | -360.8143 | 17.5958 | -352.6444 | 18.7251 | -352.6906 | 16.8525
12:58 | 5889 | 50.2663 | 203.046 | 449.5654 | 452.1532 | -16.8844 | -38.4864 | 11.9751 | 8.038 | 2.4306 | 0.7389 | 2.9023 | -1.0757 | 12.2314 | 5.321 | 0.6249 | 0.6703 | 0.9652 | 0.7534 | -129.3396 | 1.6902 | 5.6827 | 2.0903 | -2.4655 | -0.9216 | 4.8422 |  | 4.2253 | 0.8166 | 4.0059 | 3.3682 | 3.3301 | 1.0961 | 10.7857 | 14.2763 | 14.8379 | 11.0984 | 0.0001 | -0.0034 | 0.0013 | 0.0041 | 0.0005 | -0.0008 | -0.001 | -0.0081 | 0.0126 | -360.125 | 17.3782 | -360.4266 | 17.6574 | -360.8481 | 18.1645 | -360.8512 | 17.5814 | -352.5675 | 18.6614 | -352.6229 | 16.8464
12:58 | 5890 | 50.3338 | 203.1294 | 449.6106 | 452.2609 | -16.8571 | -38.4265 | 12.0921 | 8.0072 | 2.4099 | 0.7424 | 2.8136 | -1.0446 | 12.2604 | 5.2855 | 0.6252 | 0.6664 | 0.9646 | 0.7522 | -129.3119 | 1.7116 | 5.5705 | 2.0694 | -2.522 | -0.8772 | 4.8284 |  | 4.253 | 0.8439 | 4.0041 | 3.3697 | 3.3344 | 1.0945 | 10.7938 | 14.2671 | 14.8522 | 11.1006 | -0.0004 | -0.0026 | 0.0009 | 0.0034 | 0.001 | -0.0005 | 0.0211 | -0.0053 | -0.024 | -360.1896 | 17.3987 | -360.4019 | 17.6245 | -360.7835 | 18.144 | -360.8543 | 17.6286 | -352.6537 | 18.684 | -352.5829 | 16.8176
12:58 | 5891 | 50.2912 | 203.1675 | 449.5405 | 452.1825 | -16.9317 | -38.4991 | 12.091 | 8.093 | 2.5999 | 0.8853 | 2.9305 | -1.0943 | 12.3293 | 5.2914 | 0.6264 | 0.6694 | 0.9696 | 0.7552 | -129.2281 | 1.831 | 5.5852 | 2.0244 | -2.4946 | -0.8633 | 4.8921 |  | 4.1942 | 0.7767 | 4.0049 | 3.3665 | 3.331 | 1.0951 | 10.7718 | 14.2684 | 14.8199 | 11.1129 | 0.0001 | -0.0027 | 0.0007 | 0.0042 | 0.0009 | -0.0003 | 0.0195 | -0.0071 | -0.0016 | -360.165 | 17.4213 | -360.4512 | 17.6492 | -360.8081 | 18.1091 | -360.765 | 17.5814 | -352.6198 | 18.6902 | -352.6598 | 16.8464
12:58 | 5892 | 50.3317 | 203.2242 | 449.6183 | 452.1591 | -16.8771 | -38.559 | 12.0684 | 8.1768 | 2.586 | 0.6788 | 2.9034 | -1.0767 | 12.3056 | 5.2603 | 0.6252 | 0.6672 | 0.9717 | 0.7542 | -129.1938 | 1.8051 | 5.5401 | 1.9702 | -2.5808 | -0.9087 | 4.8572 |  | 4.2514 | 0.8164 | 4.0056 | 3.3687 | 3.3326 | 1.0967 | 10.8238 | 14.2974 | 14.8836 | 11.1302 | 0 | -0.0031 | 0.0004 | 0.0035 | 0.0008 | -0.0006 | 0.0094 | -0.0107 | -0.0128 | -360.1004 | 17.3576 | -360.4019 | 17.6348 | -360.8081 | 18.1543 | -360.8358 | 17.5773 | -352.5767 | 18.645 | -352.5829 | 16.8423
12:58 | 5893 | 50.4088 | 203.2213 | 449.6398 | 452.2758 | -16.8942 | -38.6886 | 12.0046 | 8.1968 | 2.5732 | 0.78 | 2.8898 | -1.0229 | 12.3427 | 5.3541 | 0.6271 | 0.6713 | 0.9719 | 0.7551 | -129.2193 | 1.9229 | 5.5976 | 1.9707 | -2.5285 | -0.9689 | 4.8357 |  | 4.2904 | 0.7926 | 4.0066 | 3.3703 | 3.3326 | 1.0952 | 10.7984 | 14.2717 | 14.8508 | 11.0937 | 0.0002 | -0.0029 | 0.001 | 0.0041 | 0.0009 | -0.0003 | 0.0034 | -0.0001 | -0.005 | -360.1588 | 17.3946 | -360.3989 | 17.5917 | -360.7281 | 18.1255 | -360.7897 | 17.5999 | -352.6044 | 18.682 | -352.5798 | 16.8135
12:58 | 5894 | 50.3983 | 203.1877 | 449.6243 | 452.2209 | -16.9107 | -38.4672 | 12.0246 | 8.2271 | 2.6469 | 0.8145 | 2.9673 | -1.0101 | 12.2943 | 5.3055 | 0.6273 | 0.6718 | 0.969 | 0.7552 | -129.1798 | 1.9003 | 5.7523 | 2.0237 | -2.4888 | -0.8614 | 4.8745 |  | 4.2251 | 0.7418 | 4.0067 | 3.3671 | 3.3316 | 1.0946 | 10.7892 | 14.2508 | 14.8641 | 11.0789 | -0.0008 | -0.0029 | 0.0009 | 0.0042 | 0.0007 | -0.0003 | 0.0031 | -0.0073 | -0.0103 | -360.1004 | 17.4048 | -360.4542 | 17.6328 | -360.805 | 18.1153 | -360.7404 | 17.5568 | -352.5583 | 18.6799 | -352.6167 | 16.8505
12:58 | 5895 | 50.3248 | 203.1913 | 449.6218 | 452.2459 | -16.8772 | -38.4576 | 12.0186 | 8.1664 | 2.6469 | 0.7958 | 2.9582 | -0.9807 | 12.2448 | 5.2756 | 0.6257 | 0.6714 | 0.9677 | 0.7544 | -129.3096 | 1.8988 | 5.6656 | 1.9815 | -2.4731 | -0.8306 | 4.8693 |  | 4.1539 | 0.7593 | 4.0066 | 3.369 | 3.335 | 1.0933 | 10.7638 | 14.2656 | 14.8197 | 11.0887 | -0.0003 | -0.0025 | 0.0005 | 0.0035 | 0.0012 | -0.0004 | 0.0074 | -0.0172 | -0.0018 | -360.1435 | 17.372 | -360.3712 | 17.6122 | -360.802 | 18.1604 | -360.8358 | 17.5835 | -352.5521 | 18.6388 | -352.5675 | 16.8217
12:58 | 5896 | 50.3307 | 203.2028 | 449.6774 | 452.3532 | -16.8676 | -38.4074 | 11.9925 | 8.2012 | 2.6333 | 0.7125 | 2.9312 | -1.0275 | 12.3105 | 5.308 | 0.6258 | 0.6658 | 0.9667 | 0.7546 | -129.2806 | 1.8977 | 5.6837 | 1.8823 | -2.4829 | -0.8392 | 4.9063 |  | 4.2147 | 0.7971 | 4.0067 | 3.3691 | 3.3316 | 1.0952 | 10.788 | 14.2787 | 14.829 | 11.1121 | 0 | -0.0032 | 0.0014 | 0.0042 | 0.0005 | -0.0002 | 0.006 | -0.0197 | -0.0159 | -360.1804 | 17.409 | -360.4081 | 17.5896 | -360.7158 | 18.1173 | -360.7835 | 17.5999 | -352.589 | 18.6737 | -352.5767 | 16.7991
12:58 | 5897 | 50.283 | 203.2511 | 449.6579 | 452.29 | -16.9381 | -38.5074 | 11.9691 | 8.1677 | 2.672 | 0.6779 | 2.9436 | -1.0653 | 12.3284 | 5.2165 | 0.6253 | 0.6664 | 0.9648 | 0.753 | -129.2111 | 1.8955 | 5.6911 | 1.8537 | -2.4699 | -0.8884 | 4.9014 |  | 4.2602 | 0.75 | 4.0057 | 3.3692 | 3.3311 | 1.0944 | 10.7637 | 14.2659 | 14.8392 | 11.1053 | 0.0001 | -0.0029 | 0.0007 | 0.0036 | 0.0013 | -0.0006 | -0.0029 | -0.0197 | -0.0147 | -360.1373 | 17.4028 | -360.4666 | 17.641 | -360.8204 | 18.1255 | -360.7589 | 17.5691 | -352.5613 | 18.6799 | -352.6721 | 16.8443
12:58 | 5898 | 50.328 | 203.2144 | 449.7984 | 452.3826 | -16.944 | -38.5227 | 11.9524 | 8.205 | 2.7003 | 0.7362 | 3 | -1.0656 | 12.3704 | 5.2274 | 0.625 | 0.6669 | 0.9692 | 0.754 | -129.1869 | 1.888 | 5.7389 | 1.8673 | -2.3902 | -0.8023 | 4.8977 |  | 4.2451 | 0.7802 | 4.0068 | 3.3683 | 3.3362 | 1.0947 | 10.788 | 14.2904 | 14.859 | 11.1233 | -0.0003 | -0.003 | 0.0007 | 0.0036 | 0.0009 | 0 | 0.0018 | -0.0189 | -0.0227 | -360.1558 | 17.3782 | -360.4019 | 17.6245 | -360.805 | 18.1687 | -360.8266 | 17.5896 | -352.6075 | 18.6594 | -352.5952 | 16.8279
12:58 | 5899 | 50.2655 | 203.1672 | 449.7041 | 452.4628 | -16.9714 | -38.4955 | 11.9651 | 8.225 | 2.6551 | 0.7347 | 2.9946 | -1.0542 | 12.3789 | 5.2646 | 0.6252 | 0.6641 | 0.9642 | 0.7528 | -129.206 | 1.9203 | 5.6681 | 1.9133 | -2.4305 | -0.891 | 4.8741 |  | 4.1562 | 0.6947 | 4.0073 | 3.3675 | 3.3307 | 1.0956 | 10.7833 | 14.2684 | 14.8778 | 11.0782 | -0.0002 | -0.0025 | 0.0007 | 0.0039 | 0.0009 | -0.0009 | 0.0156 | -0.0166 | 0.0045 | -360.1988 | 17.4295 | -360.4327 | 17.5978 | -360.7527 | 18.1337 | -360.8204 | 17.6225 | -352.6629 | 18.6881 | -352.6167 | 16.8094
12:58 | 5900 | 50.3304 | 203.1284 | 449.6537 | 452.3721 | -16.9567 | -38.4598 | 11.9093 | 8.2424 | 2.6496 | 0.6773 | 2.962 | -1.0308 | 12.4376 | 5.2942 | 0.6257 | 0.6644 | 0.9686 | 0.7533 | -129.1185 | 1.87 | 5.6348 | 1.874 | -2.4576 | -0.8578 | 4.8827 |  | 4.2234 | 0.79 | 4.0047 | 3.3664 | 3.3325 | 1.0939 | 10.8387 | 14.3245 | 14.9256 | 11.115 | 0.0004 | -0.0026 | 0.0002 | 0.0037 | 0.0005 | 0.0001 | 0.0068 | -0.0101 | -0.0122 | -360.1558 | 17.4192 | -360.4789 | 17.6594 | -360.8481 | 18.1543 | -360.7927 | 17.5753 | -352.6044 | 18.6943 | -352.6444 | 16.8525
12:58 | 5901 | 50.2871 | 203.1187 | 449.6849 | 452.3304 | -16.966 | -38.5554 | 11.9443 | 8.233 | 2.6454 | 0.6746 | 3.0102 | -1.1184 | 12.4195 | 5.3546 | 0.6244 | 0.6692 | 0.9672 | 0.7535 | -129.257 | 1.9468 | 5.6548 | 1.8294 | -2.4958 | -0.8818 | 4.8513 |  | 4.2076 | 0.7165 | 4.0078 | 3.3677 | 3.3315 | 1.0938 | 10.7925 | 14.2954 | 14.8956 | 11.1269 | 0.0001 | -0.0033 | 0.001 | 0.004 | 0.0014 | -0.0002 | 0.0129 | -0.0051 | -0.0213 | -360.1681 | 17.3925 | -360.4204 | 17.6369 | -360.8512 | 18.1728 | -360.8727 | 17.5896 | -352.6106 | 18.6758 | -352.6013 | 16.8361
12:58 | 5902 | 50.3914 | 203.1309 | 449.6354 | 452.3584 | -16.9443 | -38.4273 | 11.8993 | 8.2104 | 2.6542 | 0.7618 | 3.0294 | -1.0466 | 12.3386 | 5.3176 | 0.6244 | 0.6629 | 0.9698 | 0.753 | -129.2619 | 2.0069 | 5.66 | 1.8953 | -2.4788 | -0.8351 | 4.8683 |  | 4.2109 | 0.8154 | 4.0063 | 3.3669 | 3.3329 | 1.0942 | 10.7741 | 14.2996 | 14.8389 | 11.0865 | -0.0001 | -0.0025 | 0.0008 | 0.0043 | 0.0005 | -0.0006 | 0.0015 | -0.0254 | 0.0056 | -360.1804 | 17.4233 | -360.4512 | 17.602 | -360.7589 | 18.1522 | -360.8481 | 17.5937 | -352.6352 | 18.7066 | -352.6106 | 16.8012
12:58 | 5903 | 50.4208 | 203.1775 | 449.6675 | 452.3299 | -16.9257 | -38.5309 | 11.8835 | 8.1826 | 2.6512 | 0.7689 | 2.9811 | -1.026 | 12.3041 | 5.28 | 0.6254 | 0.6678 | 0.9695 | 0.7536 | -129.2558 | 1.9515 | 5.6158 | 2.1285 | -2.4876 | -0.8397 | 4.8683 |  | 4.2149 | 0.834 | 4.0072 | 3.3688 | 3.333 | 1.0943 | 10.7984 | 14.2778 | 14.8703 | 11.1103 | 0 | -0.0024 | 0.0009 | 0.0038 | 0.0011 | -0.0005 | 0.023 | -0.0148 | 0.0126 | -360.1681 | 17.4213 | -360.4973 | 17.6574 | -360.8327 | 18.1461 | -360.805 | 17.5732 | -352.6075 | 18.6963 | -352.6567 | 16.8464
12:58 | 5904 | 50.3686 | 203.1401 | 449.6857 | 452.3977 | -16.9819 | -38.5924 | 11.9541 | 8.2676 | 2.6978 | 0.752 | 2.993 | -1.0366 | 12.3602 | 5.2351 | 0.6261 | 0.6652 | 0.9666 | 0.7532 | -129.2598 | 1.9246 | 5.6961 | 2.0727 | -2.4385 | -0.8149 | 4.907 |  | 4.1829 | 0.8053 | 4.0065 | 3.3681 | 3.3343 | 1.0943 | 10.7684 | 14.2647 | 14.8321 | 11.0695 | 0.0002 | -0.0031 | 0.0008 | 0.0037 | 0.0009 | -0.0003 | 0.0032 | 0.0028 | -0.0209 | -360.1742 | 17.4069 | -360.4266 | 17.6328 | -360.8512 | 18.183 | -360.8543 | 17.5794 | -352.6013 | 18.6779 | -352.6229 | 16.834
12:58 | 5905 | 50.2954 | 203.0974 | 449.5609 | 452.3078 | -16.9077 | -38.4769 | 11.995 | 8.1416 | 2.6273 | 0.6489 | 3.0304 | -1.0447 | 12.3031 | 5.2344 | 0.6255 | 0.67 | 0.9687 | 0.7547 | -129.2929 | 1.9818 | 5.6308 | 2.0494 | -2.5171 | -0.9336 | 4.8256 |  | 4.1842 | 0.7929 | 4.0069 | 3.3667 | 3.3313 | 1.0945 | 10.7742 | 14.2647 | 14.861 | 11.0638 | 0.0005 | -0.003 | 0.0007 | 0.0037 | 0.0007 | -0.0005 | 0.0074 | -0.0036 | 0.0013 | -360.2081 | 17.4172 | -360.4389 | 17.6081 | -360.7835 | 18.1563 | -360.845 | 17.6061 | -352.6198 | 18.6963 | -352.626 | 16.8012
12:58 | 5906 | 50.286 | 203.2048 | 449.5351 | 452.3039 | -16.9568 | -38.5501 | 11.9408 | 8.2122 | 2.567 | 0.6242 | 2.935 | -1.0803 | 12.2666 | 5.2717 | 0.6255 | 0.6641 | 0.97 | 0.7534 | -129.2776 | 1.8854 | 5.6204 | 2.0454 | -2.4623 | -0.8646 | 4.97 |  | 4.2915 | 0.8597 | 4.0064 | 3.3653 | 3.3314 | 1.0943 | 10.7754 | 14.26 | 14.815 | 11.1057 | -0.0004 | -0.0028 | 0.0009 | 0.004 | 0.0014 | -0.0004 | -0.001 | -0.0071 | -0.0043 | -360.1527 | 17.4233 | -360.4573 | 17.6574 | -360.8574 | 18.1502 | -360.8112 | 17.5855 | -352.5798 | 18.684 | -352.6752 | 16.8443
12:58 | 5907 | 50.3197 | 203.183 | 449.6433 | 452.2297 | -16.9663 | -38.632 | 11.9685 | 8.2679 | 2.6619 | 0.6271 | 2.9671 | -1.1229 | 12.3062 | 5.269 | 0.6245 | 0.6668 | 0.9715 | 0.7536 | -129.2681 | 1.9603 | 5.7898 | 2.0793 | -2.5165 | -0.8371 | 4.9362 |  | 4.2615 | 0.8246 | 4.0056 | 3.3661 | 3.3347 | 1.0957 | 10.773 | 14.2868 | 14.8607 | 11.1143 | -0.0001 | -0.0024 | 0.0006 | 0.0039 | 0.0004 | -0.0004 | 0.0108 | -0.0191 | -0.0227 | -360.1496 | 17.3987 | -360.4512 | 17.6328 | -360.8174 | 18.1687 | -360.845 | 17.5855 | -352.586 | 18.6676 | -352.5983 | 16.832
12:58 | 5908 | 50.2522 | 203.135 | 449.6581 | 452.3337 | -17.0072 | -38.7027 | 11.9548 | 8.136 | 2.6043 | 0.8472 | 3.0222 | -1.0625 | 12.3099 | 5.3208 | 0.6269 | 0.6675 | 0.9672 | 0.7543 | -129.2763 | 1.9076 | 5.6535 | 1.9401 | -2.4752 | -0.8586 | 4.9548 |  | 4.2857 | 0.7977 | 4.0068 | 3.3671 | 3.3358 | 1.0947 | 10.7764 | 14.2557 | 14.8301 | 11.1118 | 0.0004 | -0.0027 | 0.0007 | 0.0039 | 0.001 | -0.0006 | 0.0049 | -0.0016 | -0.0125 | -360.1896 | 17.4069 | -360.4204 | 17.5999 | -360.7589 | 18.144 | -360.8266 | 17.5937 | -352.6106 | 18.6799 | -352.6044 | 16.8135
12:58 | 5909 | 50.3385 | 203.1952 | 449.6614 | 452.3422 | -17.0015 | -38.6629 | 11.8572 | 8.1634 | 2.6356 | 0.7332 | 2.949 | -1.0603 | 12.3566 | 5.3188 | 0.6265 | 0.6685 | 0.968 | 0.7539 | -129.3538 | 1.8997 | 5.5858 | 1.9159 | -2.5989 | -0.8505 | 4.8376 |  | 4.2685 | 0.8436 | 4.0061 | 3.3696 | 3.3322 | 1.0935 | 10.8133 | 14.2873 | 14.8813 | 11.1132 | 0.0005 | -0.0026 | 0.0011 | 0.0043 | 0.001 | 0.0003 | 0.0044 | -0.0167 | -0.0109 | -360.1496 | 17.3966 | -360.4573 | 17.6451 | -360.7927 | 18.144 | -360.8112 | 17.5691 | -352.5736 | 18.684 | -352.6075 | 16.832
12:58 | 5910 | 50.232 | 203.1614 | 449.6119 | 452.3612 | -17.0275 | -38.6716 | 11.8604 | 8.1839 | 2.5517 | 0.7432 | 2.8813 | -1.0811 | 12.1934 | 5.2642 | 0.6256 | 0.6686 | 0.967 | 0.7535 | -129.3565 | 1.8593 | 5.5577 | 1.8738 | -2.587 | -0.9707 | 4.7495 |  | 4.2824 | 0.8101 | 4.0074 | 3.3678 | 3.3353 | 1.0945 | 10.795 | 14.2972 | 14.9056 | 11.1132 | -0.0001 | -0.0029 | 0.0007 | 0.0037 | 0.0012 | -0.0007 | 0.0144 | 0.0034 | -0.0248 | -360.1404 | 17.3946 | -360.4173 | 17.6266 | -360.8112 | 18.1563 | -360.8358 | 17.5753 | -352.5767 | 18.6758 | -352.6075 | 16.8217
12:58 | 5911 | 50.3057 | 203.0912 | 449.5461 | 452.2704 | -16.9355 | -38.6256 | 11.8335 | 8.1222 | 2.6639 | 0.7271 | 2.8927 | -1.0983 | 12.2358 | 5.3263 | 0.6267 | 0.6677 | 0.967 | 0.7533 | -129.318 | 1.9814 | 5.5794 | 1.9029 | -2.5874 | -0.9085 | 4.7982 |  | 4.3629 | 0.9285 | 4.0069 | 3.3662 | 3.335 | 1.094 | 10.7891 | 14.2859 | 14.873 | 11.124 | -0.0003 | -0.0025 | 0.001 | 0.0039 | 0.0008 | -0.0001 | 0.0139 | 0.0044 | -0.0097 | -360.1773 | 17.409 | -360.4173 | 17.6122 | -360.7866 | 18.144 | -360.8297 | 17.5876 | -352.6013 | 18.684 | -352.6075 | 16.8238
12:58 | 5912 | 50.2254 | 203.1026 | 449.5478 | 452.3913 | -16.8766 | -38.6166 | 11.9244 | 8.2463 | 2.6314 | 0.7137 | 2.9713 | -1.1188 | 12.2557 | 5.2498 | 0.6263 | 0.6658 | 0.971 | 0.7542 | -129.3547 | 1.8839 | 5.5811 | 1.9779 | -2.5512 | -0.8931 | 4.9104 |  | 4.3291 | 0.8677 | 4.0057 | 3.3653 | 3.3359 | 1.0939 | 10.8204 | 14.3111 | 14.8794 | 11.0981 | 0.0003 | -0.0029 | 0.0009 | 0.0039 | 0.0005 | -0.0008 | 0.0068 | -0.0133 | 0.0021 | -360.1835 | 17.4213 | -360.4512 | 17.6471 | -360.842 | 18.1522 | -360.845 | 17.5876 | -352.5706 | 18.6922 | -352.6198 | 16.8299
12:58 | 5913 | 50.2529 | 203.0912 | 449.604 | 452.4611 | -16.9645 | -38.6576 | 11.9777 | 8.194 | 2.5141 | 0.727 | 2.9418 | -1.1203 | 12.3539 | 5.2734 | 0.6256 | 0.6676 | 0.9687 | 0.7546 | -129.2882 | 1.9448 | 5.6441 | 2.0327 | -2.5893 | -0.9619 | 4.8344 |  | 4.326 | 0.8283 | 4.0063 | 3.3684 | 3.3346 | 1.0928 | 10.8007 | 14.2914 | 14.8593 | 11.1017 | 0.0001 | -0.0035 | 0.0012 | 0.0034 | 0.0007 | -0.0003 | 0.014 | -0.0136 | -0.0198 | -360.1742 | 17.4131 | -360.445 | 17.6328 | -360.8204 | 18.1625 | -360.8574 | 17.5917 | -352.586 | 18.6943 | -352.6044 | 16.832
12:58 | 5914 | 50.2356 | 203.0774 | 449.6089 | 452.3606 | -16.9839 | -38.6413 | 11.9163 | 8.1554 | 2.5955 | 0.8208 | 2.8843 | -1.1332 | 12.2714 | 5.2356 | 0.625 | 0.6688 | 0.9675 | 0.7537 | -129.4104 | 1.8402 | 5.5525 | 2.0447 | -2.622 | -1.0024 | 4.8109 |  | 4.3016 | 0.8243 | 4.0072 | 3.3693 | 3.3342 | 1.0952 | 10.7926 | 14.2718 | 14.8403 | 11.0876 | -0.0002 | -0.003 | 0.0006 | 0.0035 | 0.0011 | -0.0006 | 0.014 | -0.0108 | -0.0079 | -360.1988 | 17.4192 | -360.4696 | 17.641 | -360.7897 | 18.1666 | -360.842 | 17.5917 | -352.586 | 18.7004 | -352.6321 | 16.8443
12:58 | 5915 | 50.4126 | 203.1625 | 449.6549 | 452.3762 | -16.9348 | -38.65 | 12.0229 | 8.1698 | 2.5991 | 0.7927 | 2.9158 | -1.0858 | 12.269 | 5.3338 | 0.6256 | 0.6688 | 0.9684 | 0.7552 | -129.2972 | 1.8638 | 5.6099 | 2.1211 | -2.5939 | -0.8614 | 4.8533 |  | 4.2659 | 0.8489 | 4.0067 | 3.367 | 3.3344 | 1.094 | 10.7997 | 14.2841 | 14.8327 | 11.1071 | -0.0006 | -0.0028 | 0.0007 | 0.0039 | 0.0006 | -0.0006 | -0.0001 | -0.0031 | -0.0224 | -360.2142 | 17.4151 | -360.4666 | 17.6512 | -360.842 | 18.1707 | -360.8666 | 17.5917 | -352.6352 | 18.7066 | -352.6475 | 16.8525
12:58 | 5916 | 50.4504 | 203.1179 | 449.6568 | 452.4017 | -16.9714 | -38.6188 | 11.9266 | 8.1651 | 2.6749 | 0.9035 | 2.9657 | -1.1673 | 12.1366 | 5.2085 | 0.6254 | 0.6683 | 0.9686 | 0.7546 | -129.2722 | 1.937 | 5.6424 | 2.1356 | -2.5412 | -0.9074 | 4.912 |  | 4.2664 | 0.834 | 4.0067 | 3.3661 | 3.3311 | 1.0958 | 10.7776 | 14.2858 | 14.8951 | 11.1013 | 0.0002 | -0.0028 | 0.0007 | 0.004 | 0.0008 | -0.0006 | 0.0097 | -0.0105 | -0.0107 | -360.1742 | 17.409 | -360.4542 | 17.6286 | -360.8174 | 18.1748 | -360.8512 | 17.6081 | -352.6044 | 18.7087 | -352.6383 | 16.8464
12:58 | 5917 | 50.4991 | 203.1235 | 449.6992 | 452.3952 | -16.9022 | -38.6405 | 12.0012 | 8.1227 | 2.6706 | 0.781 | 2.9205 | -1.0937 | 12.181 | 5.187 | 0.6262 | 0.666 | 0.9633 | 0.7535 | -129.2715 | 1.961 | 5.6445 | 2.2146 | -2.4712 | -0.7959 | 4.9513 |  | 4.3501 | 0.9593 | 4.0059 | 3.3681 | 3.336 | 1.0944 | 10.781 | 14.295 | 14.8577 | 11.0934 | 0.0002 | -0.0033 | 0.0009 | 0.0044 | 0.0009 | -0.0002 | 0.0224 | -0.0171 | -0.0305 | -360.205 | 17.4274 | -360.4881 | 17.6471 | -360.8204 | 18.1687 | -360.842 | 17.602 | -352.6167 | 18.7189 | -352.666 | 16.8648
12:58 | 5918 | 50.4118 | 203.0869 | 449.6785 | 452.3076 | -16.9849 | -38.7687 | 11.9232 | 8.1043 | 2.6492 | 0.6646 | 2.7904 | -1.1729 | 12.1515 | 5.1724 | 0.626 | 0.666 | 0.9684 | 0.7535 | -129.3498 | 1.9899 | 5.5933 | 2.087 | -2.5278 | -0.7912 | 4.8735 |  | 4.3393 | 0.9845 | 4.0053 | 3.3644 | 3.3342 | 1.0941 | 10.7799 | 14.2938 | 14.891 | 11.1212 | -0.0002 | -0.0032 | 0.0008 | 0.0042 | 0.0009 | 0 | 0.0029 | 0.0006 | -0.0177 | -360.1804 | 17.4151 | -360.4727 | 17.643 | -360.8512 | 18.1728 | -360.8327 | 17.6081 | -352.629 | 18.6881 | -352.6352 | 16.8772
12:58 | 5919 | 50.4537 | 203.1788 | 449.6472 | 452.4175 | -16.9446 | -38.7341 | 11.945 | 8.0736 | 2.5447 | 0.6234 | 2.7087 | -1.0583 | 12.3097 | 5.3146 | 0.6259 | 0.6683 | 0.9663 | 0.7537 | -129.2901 | 1.9692 | 5.5798 | 2.0185 | -2.5735 | -0.9079 | 4.803 |  | 4.3574 | 0.858 | 4.0054 | 3.3651 | 3.3352 | 1.0946 | 10.811 | 14.256 | 14.8843 | 11.1226 | 0.0001 | -0.0023 | 0.0007 | 0.0036 | 0.0015 | -0.0003 | 0.0169 | -0.0022 | -0.0196 | -360.2111 | 17.4151 | -360.4327 | 17.6204 | -360.8327 | 18.1645 | -360.842 | 17.6143 | -352.6383 | 18.6963 | -352.626 | 16.8525
12:58 | 5920 | 50.4207 | 203.2231 | 449.6407 | 452.4092 | -16.927 | -38.7076 | 12.0345 | 8.1042 | 2.5349 | 0.5747 | 2.7384 | -1.1025 | 12.3114 | 5.272 | 0.6272 | 0.6691 | 0.9707 | 0.7538 | -129.3626 | 1.9952 | 5.5866 | 2.079 | -2.5803 | -0.8585 | 4.7916 |  | 4.3282 | 0.9483 | 4.0059 | 3.3664 | 3.3318 | 1.0954 | 10.8111 | 14.3135 | 14.8996 | 11.1407 | -0.0007 | -0.003 | 0.0009 | 0.0041 | 0.0004 | -0.0002 | 0.0285 | 0.0018 | -0.0128 | -360.165 | 17.4151 | -360.485 | 17.6389 | -360.8112 | 18.1461 | -360.802 | 17.5917 | -352.629 | 18.7107 | -352.6721 | 16.871
12:58 | 5921 | 50.3395 | 203.2827 | 449.5644 | 452.2951 | -16.9007 | -38.6996 | 11.9676 | 8.1677 | 2.5674 | 0.667 | 2.7424 | -1.1094 | 12.2706 | 5.2293 | 0.6268 | 0.6653 | 0.9664 | 0.7528 | -129.3972 | 1.9776 | 5.4826 | 2.1012 | -2.5146 | -0.8484 | 4.845 |  | 4.3932 | 0.8352 | 4.0057 | 3.3657 | 3.3338 | 1.0959 | 10.7799 | 14.2589 | 14.8436 | 11.0869 | 0.0002 | -0.0031 | 0.0007 | 0.0033 | 0.0012 | -0.0006 | 0.0089 | -0.0084 | 0.0072 | -360.1219 | 17.3864 | -360.4358 | 17.6204 | -360.842 | 18.1707 | -360.8389 | 17.5855 | -352.6106 | 18.682 | -352.6229 | 16.8669
12:58 | 5922 | 50.442 | 203.1715 | 449.5939 | 452.3145 | -17.0463 | -38.8216 | 11.877 | 8.2576 | 2.5741 | 0.6436 | 2.7003 | -1.1614 | 12.2852 | 5.322 | 0.6264 | 0.6652 | 0.9702 | 0.7543 | -129.3774 | 1.9883 | 5.5541 | 1.9741 | -2.5459 | -0.8408 | 4.8262 |  | 4.2829 | 0.8046 | 4.005 | 3.3651 | 3.3336 | 1.0946 | 10.7787 | 14.281 | 14.8607 | 11.1028 | 0.0001 | -0.0028 | 0.0007 | 0.004 | 0.0008 | -0.0002 | 0.013 | -0.0113 | 0.0046 | -360.1835 | 17.3884 | -360.4112 | 17.5978 | -360.7712 | 18.1604 | -360.8635 | 17.602 | -352.629 | 18.6881 | -352.6136 | 16.8381
12:58 | 5923 | 50.4236 | 203.1969 | 449.5043 | 452.2884 | -17.1675 | -38.9596 | 11.7169 | 8.2665 | 2.5871 | 0.6798 | 2.826 | -1.1991 | 12.2924 | 5.3141 | 0.6265 | 0.665 | 0.9682 | 0.7545 | -129.393 | 1.9465 | 5.5553 | 1.9732 | -2.5398 | -0.9229 | 4.7748 |  | 4.3315 | 0.8975 | 4.006 | 3.3671 | 3.3345 | 1.0949 | 10.7938 | 14.2787 | 14.8348 | 11.1237 | -0.0002 | -0.0024 | 0.0007 | 0.0041 | 0.0013 | -0.0006 | 0.0266 | -0.008 | -0.0127 | -360.1496 | 17.409 | -360.4327 | 17.6204 | -360.8081 | 18.1214 | -360.7958 | 17.5794 | -352.6229 | 18.6881 | -352.6229 | 16.8525
12:58 | 5924 | 50.3863 | 203.1526 | 449.5469 | 452.361 | -17.1502 | -39.0658 | 11.7268 | 8.3226 | 2.5903 | 0.6756 | 2.7958 | -1.1388 | 12.2511 | 5.2951 | 0.6253 | 0.6682 | 0.9669 | 0.7563 | -129.3193 | 1.9792 | 5.6242 | 1.9632 | -2.5495 | -1.0568 | 4.792 |  | 4.3705 | 0.9363 | 4.0063 | 3.3675 | 3.3308 | 1.0945 | 10.7532 | 14.2733 | 14.8264 | 11.0648 | 0.0004 | -0.0026 | 0.0008 | 0.0041 | 0.0006 | -0.0002 | 0.0262 | -0.0084 | 0.0101 | -360.1065 | 17.3843 | -360.4204 | 17.6061 | -360.7897 | 18.1522 | -360.802 | 17.5486 | -352.546 | 18.6696 | -352.5952 | 16.8525
12:58 | 5925 | 50.3707 | 203.1559 | 449.6234 | 452.4582 | -17.1415 | -38.8954 | 11.7942 | 8.3753 | 2.6625 | 0.7147 | 2.7983 | -1.1543 | 12.279 | 5.3302 | 0.6258 | 0.6687 | 0.9688 | 0.7532 | -129.2281 | 2.0082 | 5.689 | 1.9656 | -2.535 | -0.9396 | 4.7706 |  | 4.3539 | 0.9098 | 4.0046 | 3.3689 | 3.334 | 1.0944 | 10.788 | 14.2962 | 14.888 | 11.1233 | 0.0002 | -0.003 | 0.0004 | 0.0038 | 0.0014 | -0.0004 | 0.0097 | -0.0145 | -0.0173 | -360.1681 | 17.374 | -360.3835 | 17.5876 | -360.7312 | 18.1502 | -360.842 | 17.5835 | -352.586 | 18.6696 | -352.5583 | 16.8238
12:58 | 5926 | 50.4471 | 203.1125 | 449.6203 | 452.3591 | -17.0364 | -38.7927 | 11.8055 | 8.2788 | 2.6677 | 0.6721 | 2.7591 | -1.1779 | 12.2329 | 5.2513 | 0.6258 | 0.6671 | 0.9669 | 0.7528 | -129.2587 | 1.9772 | 5.5521 | 1.9581 | -2.5575 | -0.8962 | 4.7896 |  | 4.3291 | 0.871 | 4.0051 | 3.3674 | 3.3338 | 1.0944 | 10.8007 | 14.2859 | 14.873 | 11.0951 | 0.0003 | -0.0024 | 0.0009 | 0.0038 | 0.0009 | -0.0001 | 0.0025 | -0.0092 | 0.0053 | -360.1558 | 17.4048 | -360.4419 | 17.6061 | -360.762 | 18.1153 | -360.7743 | 17.5629 | -352.589 | 18.7066 | -352.6167 | 16.8464
12:58 | 5927 | 50.3857 | 203.1129 | 449.5992 | 452.3699 | -17.0285 | -38.7551 | 11.8149 | 8.2518 | 2.7194 | 0.6934 | 2.7239 | -1.1801 | 12.317 | 5.257 | 0.6262 | 0.6643 | 0.9643 | 0.7552 | -129.3438 | 1.8534 | 5.5408 | 2.0221 | -2.5089 | -0.9712 | 4.7053 |  | 4.3453 | 0.872 | 4.0051 | 3.3682 | 3.3318 | 1.0921 | 10.7949 | 14.2917 | 14.873 | 11.1009 | -0.0001 | -0.0024 | 0.0009 | 0.0035 | 0.001 | -0.0003 | 0.027 | -0.0001 | -0.0088 | -360.1065 | 17.3802 | -360.4204 | 17.6102 | -360.8143 | 18.1604 | -360.7773 | 17.5547 | -352.5398 | 18.6655 | -352.5921 | 16.8525
12:59 | 5928 | 50.4045 | 203.1631 | 449.6078 | 452.3996 | -17.0346 | -38.6934 | 11.8643 | 8.285 | 2.6755 | 0.714 | 2.6928 | -1.051 | 12.3052 | 5.3561 | 0.6252 | 0.6656 | 0.9704 | 0.7549 | -129.3147 | 1.9389 | 5.6123 | 2.0053 | -2.5794 | -0.8569 | 4.7253 |  | 4.3213 | 0.877 | 4.0053 | 3.3664 | 3.3331 | 1.0933 | 10.7765 | 14.2787 | 14.8522 | 11.0601 | -0.0001 | -0.0025 | 0.0012 | 0.0039 | 0.0006 | -0.0003 | 0.0104 | -0.0073 | -0.0079 | -360.205 | 17.3699 | -360.3989 | 17.5773 | -360.7189 | 18.1563 | -360.8697 | 17.5978 | -352.6136 | 18.6758 | -352.5736 | 16.8176
12:59 | 5929 | 50.4657 | 203.21 | 449.7177 | 452.4531 | -17.0692 | -38.6989 | 11.8322 | 8.1964 | 2.6714 | 0.641 | 2.706 | -1.0817 | 12.2532 | 5.3933 | 0.6261 | 0.668 | 0.9703 | 0.7539 | -129.2847 | 1.8609 | 5.5909 | 1.872 | -2.5463 | -0.88 | 4.7663 |  | 4.2094 | 0.9804 | 4.0058 | 3.3673 | 3.3328 | 1.0953 | 10.7938 | 14.3019 | 14.8764 | 11.1118 | 0.0002 | -0.0032 | 0.0009 | 0.0038 | 0.001 | -0.0005 | 0.0038 | -0.0149 | -0.0178 | -360.1804 | 17.4172 | -360.4635 | 17.6122 | -360.7958 | 18.1296 | -360.765 | 17.5568 | -352.626 | 18.7025 | -352.6136 | 16.8525
12:59 | 5930 | 50.5018 | 203.1503 | 449.5965 | 452.3569 | -17.0958 | -38.7116 | 11.7174 | 8.2211 | 2.6216 | 0.7604 | 2.6901 | -1.1115 | 12.2572 | 5.397 | 0.6267 | 0.6703 | 0.9704 | 0.7537 | -129.2625 | 1.941 | 5.6451 | 1.7932 | -2.5519 | -0.787 | 4.76 |  | 4.2659 | 0.8587 | 4.0051 | 3.3675 | 3.3343 | 1.0948 | 10.7812 | 14.2714 | 14.8603 | 11.0772 | -0.0004 | -0.0032 | 0.0003 | 0.0038 | 0.0007 | -0.0003 | 0.0176 | -0.0122 | -0.0063 | -360.1219 | 17.3823 | -360.4235 | 17.6266 | -360.8358 | 18.1604 | -360.8235 | 17.5527 | -352.5644 | 18.6614 | -352.6044 | 16.8587
12:59 | 5931 | 50.4829 | 203.2122 | 449.6221 | 452.4065 | -17.1578 | -38.7333 | 11.7298 | 8.2026 | 2.6465 | 0.8441 | 2.7053 | -1.1433 | 12.316 | 5.2998 | 0.6263 | 0.6653 | 0.9715 | 0.7544 | -129.3168 | 1.9619 | 5.6705 | 1.7275 | -2.5564 | -0.9176 | 4.7365 |  | 4.2607 | 0.8242 | 4.006 | 3.3674 | 3.333 | 1.0954 | 10.7637 | 14.2601 | 14.8277 | 11.0764 | -0.0001 | -0.0024 | 0.0007 | 0.004 | 0.0009 | 0 | 0.0252 | -0.0154 | -0.0146 | -360.1835 | 17.3966 | -360.405 | 17.5876 | -360.7773 | 18.1604 | -360.8543 | 17.604 | -352.589 | 18.6737 | -352.5736 | 16.8156
12:59 | 5932 | 50.5296 | 203.2349 | 449.7017 | 452.4214 | -17.1139 | -38.7068 | 11.7699 | 8.2085 | 2.673 | 0.7777 | 2.631 | -1.1463 | 12.2653 | 5.2993 | 0.6252 | 0.6696 | 0.9719 | 0.754 | -129.3165 | 1.8957 | 5.7014 | 1.6987 | -2.4893 | -1.0046 | 4.737 |  | 4.169 | 0.8319 | 4.0057 | 3.3694 | 3.3357 | 1.0962 | 10.7892 | 14.2566 | 14.8409 | 11.1136 | -0.0001 | -0.0029 | 0.0004 | 0.0039 | 0.0009 | -0.0009 | -0.0017 | -0.0111 | -0.0192 | -360.2081 | 17.4295 | -360.4696 | 17.6163 | -360.805 | 18.1276 | -360.7927 | 17.5794 | -352.6075 | 18.7045 | -352.6413 | 16.8505
12:59 | 5933 | 50.5329 | 203.1367 | 449.7437 | 452.5168 | -17.1375 | -38.8738 | 11.7621 | 8.2455 | 2.6287 | 0.7915 | 2.7447 | -1.156 | 12.3246 | 5.246 | 0.6265 | 0.6684 | 0.9698 | 0.754 | -129.3479 | 1.9133 | 5.6738 | 1.6491 | -2.5112 | -0.9667 | 4.7656 |  | 4.1856 | 0.8565 | 4.0058 | 3.3674 | 3.3345 | 1.0937 | 10.8088 | 14.2939 | 14.8747 | 11.1208 | -0.0001 | -0.0032 | 0.0011 | 0.0039 | 0.0008 | -0.0001 | 0.0117 | 0.002 | -0.0173 | -360.1373 | 17.3946 | -360.4512 | 17.6369 | -360.8481 | 18.1563 | -360.8081 | 17.5568 | -352.5398 | 18.6655 | -352.6229 | 16.8607
12:59 | 5934 | 50.4763 | 203.1806 | 449.6796 | 452.4558 | -17.1431 | -38.7672 | 11.8137 | 8.2071 | 2.6971 | 0.7817 | 2.7527 | -1.094 | 12.2914 | 5.2866 | 0.627 | 0.6666 | 0.9698 | 0.7535 | -129.3857 | 1.8925 | 5.6146 | 1.7391 | -2.5483 | -0.885 | 4.8281 |  | 4.3126 | 0.772 | 4.007 | 3.3689 | 3.3331 | 1.0964 | 10.788 | 14.2846 | 14.8764 | 11.1407 | 0 | -0.0029 | 0.0006 | 0.0038 | 0.0012 | -0.0007 | 0.0232 | -0.0053 | -0.0192 | -360.2019 | 17.3843 | -360.3804 | 17.5917 | -360.7466 | 18.1645 | -360.8758 | 17.602 | -352.6167 | 18.6799 | -352.5521 | 16.8135
12:59 | 5935 | 50.4714 | 203.0831 | 449.5584 | 452.4666 | -16.8719 | -38.6085 | 11.9436 | 8.1797 | 2.7185 | 0.6791 | 2.734 | -1.0916 | 12.2866 | 5.3557 | 0.6264 | 0.6673 | 0.9685 | 0.754 | -129.3905 | 1.8488 | 5.7047 | 1.765 | -2.5856 | -0.8952 | 4.8368 |  | 4.2758 | 0.8613 | 4.0072 | 3.3663 | 3.3307 | 1.096 | 10.7973 | 14.288 | 14.8563 | 11.0981 | -0.0006 | -0.0028 | 0.0008 | 0.0034 | 0.0006 | -0.0001 | 0.0119 | -0.0114 | -0.0213 | -360.2142 | 17.4377 | -360.4635 | 17.6286 | -360.7958 | 18.1276 | -360.7989 | 17.5855 | -352.629 | 18.723 | -352.669 | 16.8423
12:59 | 5936 | 50.5193 | 203.1502 | 449.646 | 452.4827 | -16.788 | -38.5479 | 11.9337 | 8.2207 | 2.7283 | 0.7868 | 2.6149 | -1.1079 | 12.2131 | 5.2572 | 0.6249 | 0.6662 | 0.9715 | 0.7536 | -129.3728 | 1.8501 | 5.6546 | 1.8541 | -2.5592 | -0.9109 | 4.8233 |  | 4.2117 | 0.8572 | 4.0049 | 3.3681 | 3.3353 | 1.0946 | 10.8134 | 14.2928 | 14.8386 | 11.1082 | -0.0005 | -0.0028 | 0.0008 | 0.0041 | 0.0011 | -0.0004 | 0.0097 | -0.0025 | -0.008 | -360.1281 | 17.4069 | -360.4604 | 17.6512 | -360.8543 | 18.1604 | -360.7927 | 17.5712 | -352.5644 | 18.6922 | -352.6475 | 16.871
12:59 | 5937 | 50.4592 | 203.0944 | 449.699 | 452.4518 | -16.8075 | -38.6327 | 12.0236 | 8.2498 | 2.7305 | 0.7878 | 2.6839 | -1.1504 | 12.1832 | 5.2082 | 0.6264 | 0.6666 | 0.9682 | 0.7535 | -129.3247 | 2.0067 | 5.6527 | 1.8308 | -2.6372 | -0.9005 | 4.7871 |  | 4.215 | 0.8726 | 4.0061 | 3.3703 | 3.3351 | 1.0945 | 10.7753 | 14.2775 | 14.8334 | 11.088 | 0 | -0.0033 | 0.0009 | 0.004 | 0.0002 | -0.0005 | 0.0007 | -0.0074 | -0.0022 | -360.2419 | 17.4028 | -360.4019 | 17.5978 | -360.8143 | 18.1748 | -360.8727 | 17.6102 | -352.6413 | 18.682 | -352.586 | 16.8279
12:59 | 5938 | 50.4566 | 203.1419 | 449.5862 | 452.4496 | -16.9046 | -38.6523 | 12.0802 | 8.19 | 2.7182 | 0.878 | 2.7367 | -1.0354 | 12.2258 | 5.267 | 0.6274 | 0.6727 | 0.9702 | 0.7543 | -129.3288 | 1.9922 | 5.6995 | 1.9113 | -2.684 | -0.9225 | 4.7967 |  | 4.2427 | 0.8674 | 4.006 | 3.3697 | 3.3329 | 1.0938 | 10.8008 | 14.2681 | 14.8293 | 11.0963 | 0 | -0.0029 | 0.0002 | 0.0038 | 0.0009 | -0.0007 | 0.0156 | -0.0059 | -0.0092 | -360.2481 | 17.4459 | -360.5066 | 17.643 | -360.8297 | 18.144 | -360.8235 | 17.5917 | -352.6475 | 18.7333 | -352.6721 | 16.8546
12:59 | 5939 | 50.5186 | 203.2197 | 449.74 | 452.4912 | -16.9811 | -38.726 | 11.9259 | 8.2561 | 2.6735 | 0.8474 | 2.6927 | -1.0364 | 12.224 | 5.3368 | 0.6252 | 0.6697 | 0.9694 | 0.753 | -129.2927 | 2.0104 | 5.7061 | 1.916 | -2.6845 | -0.9302 | 4.8635 |  | 4.2881 | 0.8591 | 4.0064 | 3.3712 | 3.3314 | 1.0945 | 10.7706 | 14.2673 | 14.8301 | 11.106 | -0.0003 | -0.0027 | 0.0006 | 0.0042 | 0.0005 | -0.0004 | 0.0163 | -0.0119 | -0.0179 | -360.1527 | 17.409 | -360.4881 | 17.6636 | -360.8974 | 18.1748 | -360.8235 | 17.5773 | -352.6013 | 18.6922 | -352.6721 | 16.8833
12:59 | 5940 | 50.4406 | 203.2061 | 449.742 | 452.5515 | -17.0451 | -38.7387 | 11.7015 | 8.2589 | 2.6703 | 0.7442 | 2.7207 | -1.1272 | 12.2542 | 5.3082 | 0.6261 | 0.6726 | 0.9647 | 0.7556 | -129.3748 | 1.8549 | 5.6007 | 1.9201 | -2.6978 | -0.8535 | 4.8471 |  | 4.2533 | 0.9367 | 4.0058 | 3.3694 | 3.3338 | 1.0956 | 10.7995 | 14.2904 | 14.8475 | 11.106 | -0.0004 | -0.0027 | 0.0006 | 0.0037 | 0.0006 | -0.0008 | 0.0229 | 0.0067 | -0.0244 | -360.165 | 17.3987 | -360.405 | 17.6225 | -360.8081 | 18.1851 | -360.8789 | 17.6204 | -352.6229 | 18.6881 | -352.589 | 16.8381
12:59 | 5941 | 50.5058 | 203.0678 | 449.6503 | 452.4528 | -17.0589 | -38.754 | 11.7573 | 8.2628 | 2.589 | 0.4946 | 2.6798 | -1.1589 | 12.2505 | 5.2715 | 0.6251 | 0.6712 | 0.9688 | 0.7538 | -129.323 | 1.9321 | 5.6778 | 1.9456 | -2.6992 | -0.9117 | 4.864 |  | 4.2404 | 0.8879 | 4.0072 | 3.368 | 3.3336 | 1.0962 | 10.788 | 14.2729 | 14.8695 | 11.0948 | 0.0002 | -0.0031 | 0.0003 | 0.0037 | 0.0009 | -0.0005 | 0.0132 | -0.0138 | -0.0026 | -360.2019 | 17.4603 | -360.5035 | 17.6369 | -360.8358 | 18.1379 | -360.8174 | 17.6102 | -352.6721 | 18.7374 | -352.6875 | 16.8587
12:59 | 5942 | 50.4935 | 203.2188 | 449.6348 | 452.5299 | -17.0463 | -38.755 | 11.7438 | 8.2335 | 2.5651 | 0.3452 | 2.7426 | -1.0949 | 12.2447 | 5.2611 | 0.6266 | 0.6712 | 0.9693 | 0.7543 | -129.4113 | 1.8262 | 5.5795 | 1.7948 | -2.6482 | -0.9554 | 4.8304 |  | 4.1578 | 0.7526 | 4.0048 | 3.37 | 3.3343 | 1.0948 | 10.7568 | 14.2646 | 14.8252 | 11.0988 | 0 | -0.0033 | 0.0008 | 0.0036 | 0.0007 | -0.0006 | 0.0253 | 0.008 | -0.0111 | -360.1558 | 17.4069 | -360.485 | 17.6533 | -360.8974 | 18.181 | -360.8297 | 17.5732 | -352.6013 | 18.7045 | -352.6598 | 16.8874
12:59 | 5943 | 50.4429 | 203.2066 | 449.6636 | 452.5248 | -16.9537 | -38.8515 | 11.7277 | 8.1697 | 2.5142 | 0.4034 | 2.7015 | -1.1586 | 12.2975 | 5.2002 | 0.6256 | 0.6688 | 0.9701 | 0.7547 | -129.3506 | 1.8809 | 5.6426 | 1.703 | -2.5893 | -0.823 | 4.8541 |  | 4.2422 | 0.8037 | 4.0067 | 3.3688 | 3.3349 | 1.0949 | 10.7741 | 14.288 | 14.8679 | 11.1038 | -0.0002 | -0.0028 | 0.0007 | 0.0032 | 0.0011 | -0.0004 | 0.0068 | 0.0051 | 0.0065 | -360.2173 | 17.4028 | -360.4204 | 17.5958 | -360.7866 | 18.1851 | -360.9127 | 17.6286 | -352.6383 | 18.6902 | -352.6106 | 16.8423
12:59 | 5944 | 50.3944 | 203.0253 | 449.5148 | 452.3914 | -16.8603 | -38.8718 | 11.7959 | 8.2361 | 2.5988 | 0.4638 | 2.6985 | -1.0602 | 12.2899 | 5.2947 | 0.6246 | 0.6669 | 0.9656 | 0.7516 | -129.3285 | 1.9584 | 5.6711 | 1.7238 | -2.5743 | -0.8682 | 4.8183 |  | 4.2619 | 0.7735 | 4.0059 | 3.3694 | 3.3347 | 1.0959 | 10.773 | 14.2926 | 14.8491 | 11.1085 | -0.0004 | -0.0027 | 0.001 | 0.004 | 0.0009 | -0.0002 | -0.0026 | -0.0014 | -0.0089 | -360.2296 | 17.448 | -360.4942 | 17.6266 | -360.8235 | 18.1379 | -360.8112 | 17.604 | -352.6875 | 18.7353 | -352.6844 | 16.8546
12:59 | 5945 | 50.4388 | 203.0541 | 449.5487 | 452.4736 | -16.8039 | -38.7919 | 11.9082 | 8.2575 | 2.6727 | 0.454 | 2.6555 | -1.163 | 12.2622 | 5.2767 | 0.6258 | 0.67 | 0.9679 | 0.7527 | -129.2501 | 1.9589 | 5.6886 | 1.7838 | -2.5271 | -0.8898 | 4.816 |  | 4.2793 | 0.6846 | 4.0058 | 3.3702 | 3.3344 | 1.0965 | 10.8076 | 14.2813 | 14.857 | 11.1136 | 0.0003 | -0.0028 | 0.0016 | 0.0043 | 0.0012 | -0.0003 | 0.0106 | -0.0135 | -0.0126 | -360.1281 | 17.4048 | -360.4789 | 17.6369 | -360.8697 | 18.1687 | -360.8327 | 17.5753 | -352.6075 | 18.6984 | -352.6537 | 16.8792
12:59 | 5946 | 50.487 | 203.0565 | 449.4514 | 452.4691 | -16.7104 | -38.7689 | 12.0178 | 8.1741 | 2.6063 | 0.5072 | 2.6645 | -1.1727 | 12.2349 | 5.1889 | 0.6261 | 0.6704 | 0.9682 | 0.7539 | -129.2773 | 2.0309 | 5.7118 | 1.7661 | -2.5767 | -0.8874 | 4.8144 |  | 4.3024 | 0.735 | 4.0055 | 3.3676 | 3.3369 | 1.0968 | 10.8064 | 14.2859 | 14.8557 | 11.0894 | 0.0002 | -0.0034 | 0.0009 | 0.0041 | 0.0005 | -0.0003 | 0.0107 | 0.0014 | -0.0209 | -360.1896 | 17.3925 | -360.4081 | 17.604 | -360.7712 | 18.1769 | -360.885 | 17.6143 | -352.6383 | 18.6881 | -352.6198 | 16.8443
12:59 | 5947 | 50.4641 | 203.0457 | 449.5981 | 452.5275 | -16.8832 | -38.9693 | 11.8384 | 8.1913 | 2.6659 | 0.4959 | 2.797 | -1.1661 | 12.2309 | 5.2378 | 0.6257 | 0.6648 | 0.9645 | 0.7534 | -129.2019 | 1.9529 | 5.6677 | 1.7202 | -2.5517 | -1.0656 | 4.7754 |  | 4.3285 | 0.8353 | 4.0063 | 3.3682 | 3.3361 | 1.0975 | 10.7753 | 14.2834 | 14.8866 | 11.1338 | -0.0001 | -0.0028 | 0.0004 | 0.004 | 0.0009 | -0.001 | 0.0078 | -0.01 | -0.0006 | -360.2727 | 17.4397 | -360.4758 | 17.6245 | -360.805 | 18.142 | -360.8204 | 17.604 | -352.6844 | 18.7374 | -352.6906 | 16.8525
12:59 | 5948 | 50.477 | 203.0754 | 449.5424 | 452.4753 | -16.9332 | -38.9188 | 11.8897 | 8.1256 | 2.6591 | 0.4447 | 2.7888 | -1.0884 | 12.2936 | 5.2353 | 0.6243 | 0.6672 | 0.9662 | 0.7534 | -129.3187 | 1.8572 | 5.5698 | 1.7524 | -2.5177 | -0.9622 | 4.8127 |  | 4.2772 | 0.8208 | 4.0054 | 3.3684 | 3.3359 | 1.0976 | 10.7984 | 14.2547 | 14.8529 | 11.1045 | 0 | -0.0024 | 0.0011 | 0.0038 | 0.0007 | 0 | 0.0182 | -0.0094 | -0.0064 | -360.1496 | 17.3987 | -360.4666 | 17.6286 | -360.8327 | 18.1892 | -360.8512 | 17.5773 | -352.589 | 18.7004 | -352.6598 | 16.871
12:59 | 5949 | 50.4864 | 203.0257 | 449.5545 | 452.4665 | -16.8959 | -38.9171 | 11.8308 | 8.0984 | 2.6355 | 0.4464 | 2.7017 | -1.0287 | 12.3735 | 5.3246 | 0.6254 | 0.6696 | 0.9657 | 0.7527 | -129.278 | 1.8855 | 5.5582 | 1.7407 | -2.5448 | -0.9867 | 4.7992 |  | 4.2344 | 0.7907 | 4.0057 | 3.366 | 3.3322 | 1.0958 | 10.7614 | 14.304 | 14.8596 | 11.1205 | 0.0003 | -0.0027 | 0.0004 | 0.0036 | 0.0009 | -0.001 | 0.0049 | -0.0104 | -0.0184 | -360.1988 | 17.3966 | -360.4235 | 17.6081 | -360.7835 | 18.1953 | -360.8912 | 17.6204 | -352.6721 | 18.6963 | -352.6229 | 16.8423
12:59 | 5950 | 50.5608 | 203.0184 | 449.4689 | 452.5557 | -16.8487 | -38.8063 | 11.8655 | 8.109 | 2.5821 | 0.4874 | 2.6333 | -1.0026 | 12.3115 | 5.2652 | 0.6273 | 0.6693 | 0.9685 | 0.7537 | -129.3265 | 1.7954 | 5.5492 | 1.7359 | -2.476 | -0.9568 | 4.8493 |  | 4.1737 | 0.7092 | 4.0064 | 3.368 | 3.3323 | 1.0962 | 10.7753 | 14.2545 | 14.875 | 11.0818 | 0.0006 | -0.0028 | 0.0009 | 0.0035 | 0.0004 | -0.0006 | 0.0289 | -0.0086 | -0.0015 | -360.2358 | 17.4418 | -360.4789 | 17.6225 | -360.842 | 18.1543 | -360.805 | 17.604 | -352.6537 | 18.7312 | -352.666 | 16.8566
12:59 | 5951 | 50.5784 | 203.174 | 449.659 | 452.6092 | -16.8814 | -38.6897 | 11.8826 | 8.1321 | 2.4715 | 0.5069 | 2.6779 | -1.0948 | 12.2269 | 5.1828 | 0.6254 | 0.6715 | 0.9709 | 0.7539 | -129.2801 | 1.8447 | 5.5906 | 1.805 | -2.4319 | -0.8709 | 4.8569 |  | 4.303 | 0.8496 | 4.0062 | 3.3663 | 3.3344 | 1.0958 | 10.7718 | 14.2625 | 14.813 | 11.0901 | -0.0003 | -0.0029 | 0.0012 | 0.004 | 0.0012 | -0.0004 | 0.0137 | -0.0059 | -0.0023 | -360.1373 | 17.4069 | -360.4727 | 17.6389 | -360.8697 | 18.2015 | -360.8604 | 17.5835 | -352.6229 | 18.7025 | -352.6383 | 16.8566
12:59 | 5952 | 50.562 | 203.11 | 449.5975 | 452.5145 | -17.06 | -38.8261 | 11.7715 | 8.2218 | 2.503 | 0.5578 | 2.759 | -1.1052 | 12.2867 | 5.2409 | 0.6256 | 0.6677 | 0.969 | 0.7534 | -129.343 | 1.9803 | 5.6045 | 1.8789 | -2.5427 | -0.9358 | 4.8869 |  | 4.145 | 0.6889 | 4.0059 | 3.3667 | 3.3318 | 1.0952 | 10.7846 | 14.2635 | 14.8307 | 11.08 | -0.0001 | -0.0022 | 0.0007 | 0.0039 | 0.0009 | -0.0005 | 0.0188 | -0.0015 | 0.008 | -360.2142 | 17.409 | -360.4696 | 17.6184 | -360.802 | 18.1933 | -360.8974 | 17.6163 | -352.6506 | 18.7169 | -352.6444 | 16.8381
12:59 | 5953 | 50.584 | 203.1189 | 449.5782 | 452.5535 | -17.168 | -38.9795 | 11.7867 | 8.2421 | 2.5013 | 0.4951 | 2.7455 | -1.1113 | 12.3064 | 5.2884 | 0.6265 | 0.6686 | 0.9688 | 0.7549 | -129.2793 | 1.9362 | 5.6662 | 1.8595 | -2.6144 | -0.9555 | 4.7539 |  | 4.2105 | 0.8523 | 4.0062 | 3.3687 | 3.3325 | 1.0967 | 10.7914 | 14.2939 | 14.8458 | 11.0861 | 0.0001 | -0.0028 | 0.0009 | 0.0046 | 0.001 | 0 | 0.0292 | -0.0146 | 0.0042 | -360.1804 | 17.4418 | -360.4912 | 17.6348 | -360.8635 | 18.1666 | -360.8235 | 17.5917 | -352.626 | 18.7189 | -352.6413 | 16.8587
12:59 | 5954 | 50.5068 | 203.2029 | 449.6641 | 452.5154 | -17.1698 | -38.8772 | 11.7123 | 8.234 | 2.5205 | 0.5653 | 2.6964 | -1.1384 | 12.2854 | 5.2188 | 0.6254 | 0.6645 | 0.9702 | 0.7542 | -129.3207 | 1.9841 | 5.6113 | 1.8845 | -2.7292 | -0.9373 | 4.7715 |  | 4.2942 | 0.8267 | 4.0044 | 3.3711 | 3.3302 | 1.0955 | 10.7878 | 14.2793 | 14.8333 | 11.0818 | 0.0008 | -0.0023 | 0.0006 | 0.004 | 0.0008 | -0.0003 | 0.0106 | -0.0111 | 0.009 | -360.1527 | 17.4192 | -360.4666 | 17.6369 | -360.8758 | 18.2138 | -360.8512 | 17.5855 | -352.6106 | 18.7025 | -352.6475 | 16.8566
12:59 | 5955 | 50.5407 | 203.2378 | 449.5653 | 452.4774 | -17.1079 | -38.858 | 11.6904 | 8.2844 | 2.544 | 0.5905 | 2.6934 | -1.0637 | 12.2505 | 5.1893 | 0.6249 | 0.669 | 0.9687 | 0.754 | -129.3531 | 1.9822 | 5.6728 | 1.7383 | -2.6573 | -1.0985 | 4.7564 |  | 4.2932 | 0.7802 | 4.0055 | 3.3692 | 3.3327 | 1.097 | 10.7743 | 14.2585 | 14.8752 | 11.0707 | -0.0002 | -0.003 | 0.0004 | 0.0035 | 0.0007 | -0.0008 | 0.0033 | -0.0037 | -0.0074 | -360.2019 | 17.4213 | -360.4512 | 17.6143 | -360.8081 | 18.1851 | -360.8789 | 17.5978 | -352.6352 | 18.6963 | -352.6229 | 16.8381
12:59 | 5956 | 50.607 | 203.1529 | 449.6243 | 452.4883 | -17.1496 | -38.876 | 11.7447 | 8.1954 | 2.4767 | 0.5625 | 2.753 | -1.0308 | 12.3215 | 5.2215 | 0.6266 | 0.6697 | 0.9696 | 0.7547 | -129.4318 | 1.9491 | 5.6505 | 1.8553 | -2.6653 | -1.1174 | 4.8025 |  | 4.2761 | 0.7981 | 4.0046 | 3.3656 | 3.3313 | 1.0951 | 10.7961 | 14.2812 | 14.856 | 11.085 | -0.0004 | -0.0025 | 0.001 | 0.0037 | 0.001 | -0.0003 | 0.0209 | -0.0107 | -0.0017 | -360.2173 | 17.4213 | -360.485 | 17.6307 | -360.8574 | 18.181 | -360.8204 | 17.5814 | -352.6352 | 18.7066 | -352.6537 | 16.8525
12:59 | 5957 | 50.583 | 203.1449 | 449.6559 | 452.4492 | -17.1084 | -38.9046 | 11.7336 | 8.1658 | 2.5402 | 0.5383 | 2.6996 | -0.9728 | 12.328 | 5.2776 | 0.625 | 0.6676 | 0.9674 | 0.754 | -129.324 | 1.8781 | 5.665 | 1.866 | -2.6368 | -0.9706 | 4.8486 |  | 4.3308 | 0.7883 | 4.0044 | 3.3671 | 3.3335 | 1.0947 | 10.7741 | 14.2996 | 14.8563 | 11.1212 | 0.0001 | -0.0028 | 0.0007 | 0.0036 | 0.0008 | -0.0003 | 0.0245 | -0.0138 | -0.0089 | -360.1711 | 17.4069 | -360.4758 | 17.6184 | -360.8389 | 18.2118 | -360.8481 | 17.5814 | -352.629 | 18.7025 | -352.629 | 16.8525
12:59 | 5958 | 50.5755 | 203.188 | 449.6437 | 452.5745 | -17.1349 | -38.864 | 11.6424 | 8.1351 | 2.4856 | 0.6051 | 2.7284 | -0.9657 | 12.2605 | 5.2238 | 0.625 | 0.6687 | 0.9702 | 0.754 | -129.3465 | 1.8751 | 5.6542 | 1.8145 | -2.6655 | -0.9272 | 4.7948 |  | 4.2852 | 0.7532 | 4.0054 | 3.3694 | 3.329 | 1.0966 | 10.7789 | 14.2806 | 14.8344 | 11.075 | -0.0001 | -0.0033 | 0.0009 | 0.0041 | 0.0008 | -0.0005 | 0.0135 | -0.0126 | -0.0067 | -360.1619 | 17.4192 | -360.4696 | 17.6204 | -360.7989 | 18.183 | -360.8666 | 17.5896 | -352.6229 | 18.7025 | -352.6506 | 16.8525
12:59 | 5959 | 50.5272 | 203.0728 | 449.6295 | 452.5916 | -16.9796 | -38.7134 | 11.9593 | 8.1727 | 2.3639 | 0.4549 | 2.6897 | -1.0433 | 12.2932 | 5.3218 | 0.6259 | 0.6691 | 0.967 | 0.7548 | -129.3388 | 1.9503 | 5.7096 | 1.7619 | -2.6959 | -1.0323 | 4.8347 |  | 4.3256 | 0.7871 | 4.005 | 3.3695 | 3.3344 | 1.0962 | 10.7867 | 14.2837 | 14.8829 | 11.1099 | 0.0001 | -0.0028 | 0.0011 | 0.0039 | 0.0007 | -0.0001 | 0.0158 | -0.014 | -0.005 | -360.1835 | 17.4172 | -360.4696 | 17.6245 | -360.845 | 18.1974 | -360.8697 | 17.5732 | -352.6413 | 18.7045 | -352.6383 | 16.8587
12:59 | 5960 | 50.5649 | 203.1057 | 449.5764 | 452.556 | -16.9455 | -38.7181 | 11.9613 | 8.2254 | 2.3601 | 0.5476 | 2.7263 | -1.0371 | 12.2191 | 5.2409 | 0.6254 | 0.6657 | 0.97 | 0.754 | -129.4391 | 1.9107 | 5.5736 | 1.7832 | -2.6834 | -0.9189 | 4.864 |  | 4.3901 | 0.7894 | 4.0062 | 3.3685 | 3.3295 | 1.0979 | 10.7822 | 14.3076 | 14.8753 | 11.0948 | 0 | -0.0024 | 0.0008 | 0.0039 | 0.0007 | -0.0012 | 0.0125 | -0.0001 | -0.0034 | -360.1865 | 17.4254 | -360.4327 | 17.6245 | -360.8266 | 18.1953 | -360.8543 | 17.5794 | -352.6198 | 18.7128 | -352.6475 | 16.8423
12:59 | 5961 | 50.5176 | 203.1845 | 449.6343 | 452.6186 | -16.9082 | -38.5649 | 11.9152 | 8.0564 | 2.3793 | 0.4877 | 2.6937 | -1.0769 | 12.2051 | 5.2334 | 0.626 | 0.6677 | 0.9712 | 0.7556 | -129.2622 | 2.0006 | 5.6984 | 1.8285 | -2.6307 | -0.9394 | 4.9127 |  | 4.3536 | 0.7486 | 4.0054 | 3.3676 | 3.3342 | 1.0969 | 10.7707 | 14.2671 | 14.8232 | 11.089 | -0.0004 | -0.0032 | 0.0014 | 0.0046 | 0.0008 | 0.0002 | -0.0088 | -0.0088 | -0.0116 | -360.1988 | 17.4151 | -360.4666 | 17.6163 | -360.802 | 18.181 | -360.8481 | 17.5773 | -352.6075 | 18.7189 | -352.629 | 16.8505
12:59 | 5962 | 50.5799 | 203.0593 | 449.4946 | 452.5801 | -16.8953 | -38.557 | 11.9052 | 8.033 | 2.4354 | 0.4648 | 2.7084 | -1.0679 | 12.2642 | 5.2814 | 0.6266 | 0.6672 | 0.9707 | 0.7558 | -129.2705 | 1.9383 | 5.7345 | 1.8769 | -2.5197 | -0.9266 | 4.8315 |  | 4.3652 | 0.7594 | 4.0052 | 3.366 | 3.332 | 1.0963 | 10.7832 | 14.3092 | 14.8336 | 11.089 | 0.0002 | -0.0029 | 0.0008 | 0.0039 | 0.0008 | -0.0005 | 0.0059 | -0.0081 | -0.0273 | -360.1527 | 17.411 | -360.4389 | 17.6204 | -360.845 | 18.2015 | -360.842 | 17.5773 | -352.6136 | 18.7128 | -352.5983 | 16.8525
12:59 | 5963 | 50.5586 | 203.0281 | 449.6633 | 452.625 | -16.8991 | -38.5734 | 12.0098 | 8.1373 | 2.4531 | 0.5733 | 2.6598 | -1.0758 | 12.2132 | 5.2445 | 0.6262 | 0.6691 | 0.9697 | 0.7547 | -129.3646 | 2.0138 | 5.594 | 1.909 | -2.5378 | -0.92 | 4.8852 |  | 4.2877 | 0.687 | 4.0037 | 3.3654 | 3.3293 | 1.095 | 10.7927 | 14.2947 | 14.8729 | 11.1114 | -0.0006 | -0.0034 | 0.0005 | 0.0033 | 0.0008 | -0.0003 | 0.0193 | -0.0176 | -0.0221 | -360.1865 | 17.4151 | -360.4481 | 17.5999 | -360.8081 | 18.1871 | -360.842 | 17.5732 | -352.6229 | 18.7189 | -352.6198 | 16.8361
12:59 | 5964 | 50.6028 | 203.176 | 449.5203 | 452.6518 | -17.1115 | -38.6928 | 11.8495 | 8.1294 | 2.5355 | 0.5913 | 2.7105 | -1.132 | 12.2818 | 5.2286 | 0.627 | 0.6676 | 0.9676 | 0.7543 | -129.4263 | 1.9148 | 5.5136 | 1.9594 | -2.4348 | -0.8813 | 4.9068 |  | 4.3171 | 0.674 | 4.0052 | 3.3674 | 3.3332 | 1.0955 | 10.7787 | 14.2696 | 14.827 | 11.1255 | 0 | -0.0024 | 0.001 | 0.0039 | 0.0011 | -0.0004 | 0.0118 | -0.0018 | 0.0072 | -360.205 | 17.4315 | -360.4727 | 17.6143 | -360.8143 | 18.1748 | -360.8266 | 17.5712 | -352.6013 | 18.7271 | -352.6567 | 16.8566
12:59 | 5965 | 50.5485 | 203.1564 | 449.5641 | 452.6418 | -16.9565 | -38.5231 | 11.9259 | 8.0429 | 2.4695 | 0.4537 | 2.6686 | -1.1529 | 12.3153 | 5.3047 | 0.6264 | 0.6674 | 0.9674 | 0.7519 | -129.3755 | 1.8768 | 5.5737 | 1.9531 | -2.5468 | -0.8767 | 4.9195 |  | 4.2588 | 0.7206 | 4.0039 | 3.3693 | 3.3337 | 1.096 | 10.7811 | 14.2833 | 14.8682 | 11.1168 | -0.0002 | -0.0033 | 0.0009 | 0.0038 | 0.0006 | -0.0007 | 0.0239 | -0.0148 | -0.0174 | -360.1435 | 17.3966 | -360.4389 | 17.6204 | -360.8543 | 18.2015 | -360.8389 | 17.5773 | -352.5798 | 18.7066 | -352.5798 | 16.8587
12:59 | 5966 | 50.5988 | 203.139 | 449.5721 | 452.6817 | -17.0177 | -38.5949 | 11.8911 | 8.1374 | 2.5393 | 0.6054 | 2.7283 | -1.1344 | 12.2784 | 5.1974 | 0.6262 | 0.6725 | 0.968 | 0.7531 | -129.4029 | 1.8571 | 5.5379 | 1.9532 | -2.4808 | -0.8301 | 4.9327 |  | 4.2941 | 0.6632 | 4.0055 | 3.3678 | 3.3314 | 1.0955 | 10.7927 | 14.2775 | 14.8392 | 11.1168 | -0.0001 | -0.0031 | 0.0004 | 0.0036 | 0.0007 | -0.0003 | 0.0048 | -0.0245 | -0.0066 | -360.2573 | 17.4377 | -360.4635 | 17.5978 | -360.802 | 18.1892 | -360.8727 | 17.5917 | -352.6475 | 18.7169 | -352.6321 | 16.8484
12:59 | 5967 | 50.5109 | 203.0806 | 449.4758 | 452.6019 | -16.9779 | -38.6367 | 11.9273 | 8.1789 | 2.5679 | 0.7654 | 2.7559 | -1.1771 | 12.2136 | 5.1956 | 0.6268 | 0.6663 | 0.967 | 0.7521 | -129.4138 | 1.9263 | 5.5506 | 1.974 | -2.5348 | -0.9709 | 4.877 |  | 4.3327 | 0.7606 | 4.0054 | 3.3679 | 3.3289 | 1.0961 | 10.7498 | 14.2523 | 14.8212 | 11.0966 | 0.0001 | -0.003 | 0.0011 | 0.0038 | 0.0011 | -0.0004 | -0.0068 | -0.0019 | -0.0046 | -360.2081 | 17.4254 | -360.5066 | 17.6307 | -360.842 | 18.181 | -360.8327 | 17.5691 | -352.6106 | 18.7292 | -352.6752 | 16.8813
12:59 | 5968 | 50.601 | 203.0756 | 449.5526 | 452.6071 | -16.8937 | -38.6026 | 11.9491 | 8.1662 | 2.6299 | 0.7073 | 2.7411 | -1.1802 | 12.2459 | 5.1938 | 0.6265 | 0.669 | 0.9671 | 0.7532 | -129.3252 | 1.9189 | 5.4302 | 1.9129 | -2.5321 | -0.9053 | 4.8404 |  | 4.3371 | 0.6804 | 4.0059 | 3.3655 | 3.3298 | 1.0952 | 10.8158 | 14.295 | 14.8808 | 11.1165 | -0.0004 | -0.0025 | 0.0007 | 0.0037 | 0.0007 | -0.0001 | 0.0073 | -0.0123 | -0.0254 | -360.1988 | 17.3884 | -360.4358 | 17.6184 | -360.842 | 18.2282 | -360.9004 | 17.5876 | -352.6198 | 18.6943 | -352.5798 | 16.8689
12:59 | 5969 | 50.6176 | 203.1409 | 449.6926 | 452.6773 | -16.8928 | -38.6457 | 11.8634 | 8.1226 | 2.6549 | 0.7146 | 2.6754 | -1.2191 | 12.2153 | 5.1893 | 0.6271 | 0.6676 | 0.9682 | 0.7532 | -129.2682 | 1.9674 | 5.5744 | 1.9513 | -2.6107 | -0.9426 | 4.8377 |  | 4.2627 | 0.8471 | 4.0065 | 3.3666 | 3.3328 | 1.0955 | 10.8145 | 14.3058 | 14.8884 | 11.1258 | 0.0001 | -0.0025 | 0.0009 | 0.0043 | 0.0012 | -0.0002 | 0.0221 | 0.0017 | 0.0025 | -360.245 | 17.4377 | -360.4635 | 17.602 | -360.7804 | 18.1645 | -360.8204 | 17.5917 | -352.6598 | 18.7415 | -352.6721 | 16.8546
12:59 | 5970 | 50.6642 | 203.097 | 449.6782 | 452.6909 | -16.826 | -38.4562 | 11.9539 | 8.113 | 2.6491 | 0.7437 | 2.6347 | -1.1988 | 12.2862 | 5.179 | 0.6259 | 0.6693 | 0.9692 | 0.7532 | -129.3497 | 1.9828 | 5.5755 | 1.9913 | -2.5279 | -0.9163 | 4.8955 |  | 4.2603 | 0.7509 | 4.0052 | 3.3664 | 3.3328 | 1.0954 | 10.8053 | 14.3137 | 14.8601 | 11.1403 | 0.0001 | -0.0033 | 0.0008 | 0.0043 | 0.0005 | -0.0001 | 0.0036 | -0.0094 | -0.0252 | -360.1311 | 17.409 | -360.4973 | 17.6492 | -360.8574 | 18.1974 | -360.8235 | 17.5547 | -352.586 | 18.7169 | -352.6813 | 16.8956
12:59 | 5971 | 50.6268 | 203.2033 | 449.7168 | 452.7221 | -16.9183 | -38.5945 | 11.9358 | 8.1513 | 2.5815 | 0.711 | 2.6339 | -1.2496 | 12.2516 | 5.1524 | 0.6266 | 0.6673 | 0.9651 | 0.7521 | -129.3339 | 1.9377 | 5.6594 | 1.9956 | -2.4544 | -0.9226 | 4.848 |  | 4.3369 | 0.7854 | 4.0059 | 3.3703 | 3.3301 | 1.0947 | 10.8041 | 14.3184 | 14.8656 | 11.1157 | -0.0001 | -0.0027 | 0.0007 | 0.0036 | 0.0011 | -0.0005 | 0.0075 | -0.0101 | -0.021 | -360.1988 | 17.4007 | -360.405 | 17.5937 | -360.802 | 18.2077 | -360.8789 | 17.6143 | -352.6506 | 18.7045 | -352.5952 | 16.8443
12:59 | 5972 | 50.6279 | 203.1691 | 449.6216 | 452.6933 | -16.9217 | -38.5808 | 11.9019 | 8.1129 | 2.6824 | 0.7194 | 2.6651 | -1.1696 | 12.2378 | 5.2322 | 0.626 | 0.6683 | 0.971 | 0.752 | -129.3676 | 1.9206 | 5.5969 | 1.9652 | -2.5863 | -0.9519 | 4.8176 |  | 4.3175 | 0.934 | 4.0043 | 3.3682 | 3.3354 | 1.0959 | 10.7856 | 14.2708 | 14.8284 | 11.0919 | -0.0003 | -0.0029 | 0.001 | 0.0038 | 0.0008 | -0.0001 | 0.0092 | -0.0018 | -0.0048 | -360.1927 | 17.4356 | -360.5035 | 17.6307 | -360.8235 | 18.1666 | -360.802 | 17.5671 | -352.6629 | 18.7415 | -352.6875 | 16.8772
12:59 | 5973 | 50.6027 | 203.1394 | 449.5445 | 452.777 | -16.8545 | -38.5399 | 11.8661 | 8.1508 | 2.6332 | 0.709 | 2.7059 | -1.2542 | 12.2238 | 5.2441 | 0.6265 | 0.6711 | 0.9672 | 0.7537 | -129.2903 | 1.8991 | 5.5949 | 2.0347 | -2.542 | -0.9847 | 4.8462 |  | 4.2433 | 0.8335 | 4.0057 | 3.3693 | 3.3338 | 1.0946 | 10.7581 | 14.2712 | 14.8245 | 11.0891 | -0.0003 | -0.003 | 0.0009 | 0.0037 | 0.001 | -0.0006 | 0.0126 | -0.0097 | -0.0012 | -360.1342 | 17.3823 | -360.4266 | 17.6163 | -360.8481 | 18.2138 | -360.8727 | 17.5691 | -352.5829 | 18.6922 | -352.6444 | 16.871
12:59 | 5974 | 50.5834 | 203.0984 | 449.5643 | 452.6788 | -16.9151 | -38.4513 | 11.8976 | 8.1666 | 2.7095 | 0.7958 | 2.7375 | -1.2836 | 12.2325 | 5.1874 | 0.6263 | 0.6736 | 0.9673 | 0.7522 | -129.401 | 1.9256 | 5.578 | 1.9727 | -2.5054 | -0.9527 | 4.9092 |  | 4.2614 | 0.8638 | 4.0057 | 3.3681 | 3.3332 | 1.0935 | 10.7719 | 14.2913 | 14.8351 | 11.0501 | 0.0005 | -0.0027 | 0.0008 | 0.0039 | 0.0007 | -0.0002 | 0.0218 | -0.0108 | 0.0146 | -360.2235 | 17.4274 | -360.4512 | 17.5855 | -360.7835 | 18.1604 | -360.842 | 17.5937 | -352.6598 | 18.7271 | -352.6506 | 16.8381
12:59 | 5975 | 50.556 | 203.0801 | 449.5146 | 452.6805 | -16.9695 | -38.6208 | 11.8412 | 8.1498 | 2.6511 | 0.7541 | 2.7214 | -1.2426 | 12.2192 | 5.1742 | 0.6271 | 0.6732 | 0.9696 | 0.7542 | -129.3021 | 1.9275 | 5.6711 | 2.0033 | -2.5251 | -0.9334 | 4.9076 |  | 4.2717 | 0.7812 | 4.0054 | 3.3675 | 3.3322 | 1.0937 | 10.7707 | 14.2787 | 14.8406 | 11.089 | 0.0002 | -0.003 | 0.0008 | 0.0042 | 0.0008 | -0.0007 | 0.0012 | -0.0026 | 0.0069 | -360.1773 | 17.4192 | -360.4727 | 17.6369 | -360.8635 | 18.183 | -360.7835 | 17.5568 | -352.6075 | 18.7148 | -352.6844 | 16.8833
12:59 | 5976 | 50.615 | 203.0923 | 449.6234 | 452.7144 | -16.9723 | -38.6907 | 11.9189 | 8.2211 | 2.6651 | 0.7798 | 2.7516 | -1.2122 | 12.2268 | 5.1742 | 0.6263 | 0.6681 | 0.9674 | 0.7532 | -129.3187 | 1.9014 | 5.6344 | 2.0379 | -2.5054 | -0.8516 | 4.8907 |  | 4.2223 | 0.7496 | 4.0051 | 3.3665 | 3.3308 | 1.0942 | 10.7787 | 14.287 | 14.8386 | 11.1197 | 0.0004 | -0.002 | 0.0008 | 0.0039 | 0.0011 | 0.0003 | 0.0093 | 0.0083 | -0.0106 | -360.1465 | 17.3823 | -360.3835 | 17.5896 | -360.7989 | 18.2097 | -360.8758 | 17.5876 | -352.6506 | 18.6943 | -352.5829 | 16.8443
12:59 | 5977 | 50.6089 | 203.137 | 449.6635 | 452.7795 | -16.9718 | -38.6425 | 11.8856 | 8.2215 | 2.5401 | 0.7574 | 2.7407 | -1.1844 | 12.2287 | 5.2089 | 0.6255 | 0.6677 | 0.9703 | 0.7534 | -129.2678 | 2.0149 | 5.6661 | 1.9297 | -2.5088 | -0.964 | 4.8111 |  | 4.2519 | 0.8273 | 4.0058 | 3.3689 | 3.3323 | 1.0952 | 10.8018 | 14.2756 | 14.8802 | 11.1193 | 0.0001 | -0.0026 | 0.0008 | 0.004 | 0.0009 | -0.0006 | 0.01 | 0.002 | -0.0216 | -360.2235 | 17.4356 | -360.4696 | 17.6081 | -360.8112 | 18.1584 | -360.7927 | 17.5732 | -352.6598 | 18.7333 | -352.6844 | 16.8607
12:59 | 5978 | 50.6148 | 203.1057 | 449.4506 | 452.7387 | -16.8647 | -38.6546 | 11.9787 | 8.2624 | 2.6328 | 0.7152 | 2.7474 | -1.2927 | 12.2639 | 5.2198 | 0.6271 | 0.668 | 0.9711 | 0.7524 | -129.2852 | 1.9348 | 5.6552 | 1.8664 | -2.5839 | -1.001 | 4.847 |  | 4.2446 | 0.7884 | 4.0053 | 3.3656 | 3.331 | 1.0954 | 10.8353 | 14.2861 | 14.8915 | 11.1294 | 0.0003 | -0.0028 | 0.0008 | 0.0038 | 0.0009 | -0.0001 | 0.0164 | -0.0127 | 0.001 | -360.1342 | 17.3843 | -360.4512 | 17.6328 | -360.8512 | 18.2056 | -360.8297 | 17.5547 | -352.5829 | 18.6963 | -352.6013 | 16.8751
12:59 | 5979 | 50.5525 | 203.104 | 449.4978 | 452.7204 | -16.9257 | -38.7472 | 11.9927 | 8.3487 | 2.6597 | 0.7908 | 2.7464 | -1.2442 | 12.2753 | 5.2167 | 0.6267 | 0.6718 | 0.9716 | 0.7534 | -129.2614 | 2.0252 | 5.7416 | 1.8103 | -2.5896 | -0.9541 | 4.8165 |  | 4.2915 | 0.8809 | 4.0054 | 3.366 | 3.333 | 1.0959 | 10.8135 | 14.2868 | 14.8954 | 11.0912 | 0.0002 | -0.0029 | 0.0006 | 0.0035 | 0.0008 | -0.0001 | -0.0009 | -0.0094 | -0.0155 | -360.1958 | 17.3946 | -360.4235 | 17.5814 | -360.7866 | 18.1933 | -360.8789 | 17.5978 | -352.6506 | 18.7025 | -352.5952 | 16.8484
12:59 | 5980 | 50.5233 | 203.1238 | 449.4713 | 452.6847 | -16.9214 | -38.6771 | 12.0034 | 8.3214 | 2.6049 | 0.8573 | 2.7518 | -1.218 | 12.2175 | 5.2516 | 0.6261 | 0.6678 | 0.9673 | 0.7527 | -129.2643 | 1.9822 | 5.6532 | 1.8402 | -2.5866 | -1.051 | 4.778 |  | 4.3563 | 0.7759 | 4.0054 | 3.3647 | 3.332 | 1.0956 | 10.7927 | 14.2833 | 14.8797 | 11.1168 | -0.0005 | -0.0027 | 0.0011 | 0.0042 | 0.0011 | -0.0008 | 0.0148 | -0.002 | -0.0328 | -360.1896 | 17.4295 | -360.5004 | 17.6163 | -360.8112 | 18.1666 | -360.8143 | 17.565 | -352.6383 | 18.7395 | -352.7029 | 16.8689
12:59 | 5981 | 50.5904 | 203.0991 | 449.5684 | 452.7444 | -16.9977 | -38.6675 | 11.8599 | 8.2156 | 2.4278 | 0.8452 | 2.7627 | -1.1921 | 12.2201 | 5.2992 | 0.6265 | 0.6672 | 0.9656 | 0.7531 | -129.2757 | 1.8983 | 5.6032 | 1.791 | -2.5928 | -0.9648 | 4.7678 |  | 4.3673 | 0.926 | 4.0055 | 3.3643 | 3.3325 | 1.0957 | 10.7867 | 14.2895 | 14.8656 | 11.1157 | -0.0001 | -0.0025 | 0.0009 | 0.004 | 0.0011 | 0.0001 | 0.0121 | -0.005 | -0.006 | -360.1619 | 17.3884 | -360.4327 | 17.6245 | -360.8512 | 18.2159 | -360.8543 | 17.5629 | -352.5983 | 18.6963 | -352.6567 | 16.8792
12:59 | 5982 | 50.4669 | 203.105 | 449.5368 | 452.656 | -17.0278 | -38.5958 | 11.9341 | 8.209 | 2.4463 | 0.7846 | 2.7996 | -1.2655 | 12.297 | 5.2909 | 0.6261 | 0.6662 | 0.9673 | 0.7515 | -129.245 | 1.9417 | 5.6547 | 1.8985 | -2.5338 | -0.87 | 4.843 |  | 4.3206 | 0.9039 | 4.0053 | 3.3666 | 3.3298 | 1.0956 | 10.8066 | 14.2566 | 14.8583 | 11.1194 | -0.0001 | -0.0034 | 0.0005 | 0.004 | 0.0007 | -0.001 | 0.0078 | -0.0065 | -0.0159 | -360.2019 | 17.4172 | -360.4512 | 17.5978 | -360.7927 | 18.1769 | -360.8543 | 17.5917 | -352.666 | 18.7251 | -352.6383 | 16.8505
12:59 | 5983 | 50.5671 | 203.1538 | 449.5591 | 452.6715 | -16.9951 | -38.5292 | 11.9674 | 8.1986 | 2.4149 | 0.9407 | 2.6875 | -1.1352 | 12.2832 | 5.2471 | 0.6276 | 0.6685 | 0.9674 | 0.7527 | -129.2889 | 1.9006 | 5.6925 | 1.8558 | -2.4818 | -0.8949 | 4.8385 |  | 4.2725 | 0.8653 | 4.005 | 3.3679 | 3.3341 | 1.0963 | 10.773 | 14.2695 | 14.8549 | 11.0739 | 0.0001 | -0.003 | 0.0012 | 0.0046 | 0.0006 | -0.0003 | 0.0172 | -0.0113 | -0.0066 | -360.1835 | 17.4069 | -360.4758 | 17.6225 | -360.8204 | 18.1728 | -360.8112 | 17.565 | -352.6044 | 18.7128 | -352.6321 | 16.8751
12:59 | 5984 | 50.5317 | 203.1475 | 449.6662 | 452.6748 | -16.9689 | -38.548 | 12.0291 | 8.1087 | 2.3958 | 0.8743 | 2.7475 | -1.1505 | 12.2745 | 5.2426 | 0.6254 | 0.6682 | 0.9645 | 0.7529 | -129.2571 | 1.9403 | 5.6168 | 1.8566 | -2.5151 | -0.9332 | 4.858 |  | 4.2769 | 0.8859 | 4.0055 | 3.3664 | 3.3335 | 1.0961 | 10.7915 | 14.2707 | 14.8679 | 11.0807 | -0.0005 | -0.0032 | 0.0008 | 0.0036 | 0.0008 | -0.0006 | 0.0078 | -0.0104 | -0.0017 | -360.1896 | 17.3782 | -360.4266 | 17.6081 | -360.7958 | 18.1974 | -360.845 | 17.5773 | -352.6321 | 18.7025 | -352.6136 | 16.8607
12:59 | 5985 | 50.5436 | 203.2116 | 449.5817 | 452.7137 | -16.9618 | -38.4543 | 12.1291 | 8.2173 | 2.3762 | 0.7725 | 2.7526 | -1.132 | 12.3269 | 5.1563 | 0.6264 | 0.6651 | 0.9659 | 0.7542 | -129.3256 | 1.8724 | 5.6955 | 1.9023 | -2.5015 | -0.9933 | 4.9002 |  | 4.2708 | 0.8584 | 4.0041 | 3.3683 | 3.333 | 1.0958 | 10.7753 | 14.2661 | 14.8403 | 11.0991 | -0.0005 | -0.0028 | 0.0004 | 0.0035 | 0.0008 | -0.0001 | 0.0126 | -0.0072 | -0.0247 | -360.1342 | 17.4028 | -360.4419 | 17.602 | -360.7958 | 18.1789 | -360.8081 | 17.5732 | -352.6321 | 18.7066 | -352.626 | 16.8628
12:59 | 5986 | 50.5877 | 203.1318 | 449.5418 | 452.6692 | -16.8591 | -38.3461 | 12.2091 | 8.2273 | 2.4201 | 0.8227 | 2.7396 | -1.1749 | 12.3245 | 5.2774 | 0.6276 | 0.6669 | 0.9658 | 0.754 | -129.3485 | 2.0064 | 5.7605 | 1.8945 | -2.5308 | -0.8844 | 4.9092 |  | 4.2549 | 0.8122 | 4.0041 | 3.3662 | 3.3328 | 1.0966 | 10.7902 | 14.2756 | 14.857 | 11.0904 | 0.0004 | -0.0029 | 0.001 | 0.0039 | 0.001 | -0.0006 | -0.0013 | -0.006 | 0.001 | -360.125 | 17.4028 | -360.4296 | 17.6143 | -360.8143 | 18.1707 | -360.8297 | 17.5753 | -352.5983 | 18.7148 | -352.6475 | 16.8689
12:59 | 5987 | 50.6032 | 203.2127 | 449.5974 | 452.6732 | -16.979 | -38.4629 | 12.1257 | 8.1292 | 2.4431 | 0.794 | 2.7816 | -1.149 | 12.244 | 5.2368 | 0.6266 | 0.6675 | 0.967 | 0.7538 | -129.2857 | 1.9702 | 5.7251 | 1.9 | -2.5298 | -0.9813 | 4.8029 |  | 4.2891 | 0.7957 | 4.0048 | 3.3654 | 3.3331 | 1.096 | 10.8054 | 14.2787 | 14.8638 | 11.089 | -0.0003 | -0.0034 | 0.0007 | 0.0038 | 0.0008 | -0.0001 | 0.0172 | -0.0087 | -0.0109 | -360.1711 | 17.3966 | -360.4235 | 17.5978 | -360.7866 | 18.181 | -360.8358 | 17.5712 | -352.589 | 18.7128 | -352.6136 | 16.8443
13:00 | 5988 | 50.6494 | 203.127 | 449.6029 | 452.69 | -17.0957 | -38.592 | 12.1147 | 8.1348 | 2.4143 | 0.8621 | 2.7222 | -1.1687 | 12.1979 | 5.231 | 0.627 | 0.6674 | 0.9714 | 0.7562 | -129.2863 | 2.0435 | 5.8111 | 1.8491 | -2.5701 | -0.9364 | 4.7643 |  | 4.3086 | 0.7663 | 4.0046 | 3.3656 | 3.3352 | 1.0951 | 10.7741 | 14.2649 | 14.8505 | 11.1154 | -0.0001 | -0.0024 | 0.0007 | 0.004 | 0.0014 | -0.0005 | 0.0111 | -0.005 | -0.0132 | -360.1588 | 17.3966 | -360.4327 | 17.5937 | -360.7558 | 18.1543 | -360.7927 | 17.5629 | -352.6475 | 18.7087 | -352.6383 | 16.8546
13:00 | 5989 | 50.6742 | 203.1157 | 449.551 | 452.6333 | -17.0537 | -38.6741 | 12.0636 | 8.1358 | 2.4349 | 0.6282 | 2.7554 | -1.1856 | 12.2899 | 5.2087 | 0.6276 | 0.6651 | 0.9663 | 0.7546 | -129.2883 | 2.0292 | 5.7899 | 1.7758 | -2.5378 | -0.9981 | 4.7345 |  | 4.2687 | 0.7382 | 4.004 | 3.3623 | 3.3316 | 1.0961 | 10.7556 | 14.2581 | 14.8618 | 11.0908 | -0.0002 | -0.0026 | 0.0005 | 0.0037 | 0.0009 | 0.0002 | 0.0149 | -0.0208 | -0.0188 | -360.0973 | 17.3946 | -360.4481 | 17.6102 | -360.7989 | 18.1871 | -360.8112 | 17.5424 | -352.5767 | 18.6943 | -352.6475 | 16.8648
13:00 | 5990 | 50.5995 | 203.0911 | 449.5283 | 452.7349 | -17.0626 | -38.6711 | 12.0922 | 8.1151 | 2.4488 | 0.6686 | 2.8019 | -1.1464 | 12.3069 | 5.1844 | 0.6263 | 0.6703 | 0.9672 | 0.7539 | -129.1888 | 1.9868 | 5.7501 | 1.6701 | -2.5814 | -0.9825 | 4.7223 |  | 4.2478 | 0.7317 | 4.0041 | 3.3688 | 3.3367 | 1.0957 | 10.7995 | 14.2849 | 14.8901 | 11.1284 | 0.0001 | -0.0027 | 0.0009 | 0.0044 | 0.0005 | -0.0006 | 0.0055 | -0.0177 | -0.0095 | -360.1311 | 17.3679 | -360.3989 | 17.5917 | -360.7897 | 18.1912 | -360.8112 | 17.5547 | -352.5829 | 18.6799 | -352.5952 | 16.8546
13:00 | 5991 | 50.6137 | 203.1879 | 449.5744 | 452.6956 | -17.0084 | -38.6069 | 12.102 | 8.1508 | 2.5476 | 0.6856 | 2.8452 | -1.1552 | 12.3309 | 5.2424 | 0.6271 | 0.6624 | 0.9655 | 0.7539 | -129.2292 | 1.9731 | 5.7423 | 1.707 | -2.6182 | -0.9438 | 4.7019 |  | 4.2511 | 0.7138 | 4.0058 | 3.3704 | 3.3345 | 1.0944 | 10.7754 | 14.2658 | 14.844 | 11.1057 | 0.0003 | -0.0029 | 0.0007 | 0.0041 | 0.001 | -0.0002 | 0.0008 | -0.012 | 0.009 | -360.1804 | 17.4192 | -360.445 | 17.5814 | -360.7466 | 18.1461 | -360.7866 | 17.5712 | -352.6537 | 18.7251 | -352.629 | 16.8443
13:00 | 5992 | 50.6012 | 203.0476 | 449.5223 | 452.6458 | -16.9666 | -38.5889 | 12.1036 | 8.1984 | 2.5621 | 0.6766 | 2.714 | -1.1602 | 12.2774 | 5.1798 | 0.6268 | 0.6677 | 0.9656 | 0.7561 | -129.2955 | 1.9176 | 5.6425 | 1.7759 | -2.684 | -1.0085 | 4.7352 |  | 4.2822 | 0.7575 | 4.0057 | 3.364 | 3.3303 | 1.0949 | 10.7844 | 14.2813 | 14.8802 | 11.1136 | -0.0002 | -0.0029 | 0.0003 | 0.0035 | 0.001 | -0.0004 | -0.0081 | -0.0076 | -0.0072 | -360.1158 | 17.3823 | -360.4389 | 17.6245 | -360.805 | 18.1707 | -360.7989 | 17.528 | -352.5398 | 18.6943 | -352.6352 | 16.8731
13:00 | 5993 | 50.6202 | 203.0664 | 449.5645 | 452.6615 | -16.902 | -38.5539 | 12.1555 | 8.1649 | 2.5815 | 0.6593 | 2.7074 | -1.084 | 12.2597 | 5.2794 | 0.6271 | 0.6646 | 0.9646 | 0.7553 | -129.3154 | 1.9309 | 5.622 | 2.0014 | -2.5111 | -0.902 | 4.8688 |  | 4.327 | 0.7679 | 4.005 | 3.3664 | 3.3319 | 1.0958 | 10.7892 | 14.2972 | 14.8767 | 11.0728 | 0 | -0.0024 | 0.0009 | 0.0041 | 0.0006 | -0.0009 | 0.0023 | -0.0139 | -0.0067 | -360.165 | 17.3658 | -360.3619 | 17.565 | -360.7466 | 18.1707 | -360.842 | 17.5732 | -352.5644 | 18.6676 | -352.546 | 16.8197
13:00 | 5994 | 50.6343 | 203.1838 | 449.5351 | 452.7644 | -16.7965 | -38.3671 | 12.315 | 8.201 | 2.5896 | 0.629 | 2.7531 | -1.1422 | 12.304 | 5.2751 | 0.6269 | 0.6639 | 0.9677 | 0.755 | -129.2513 | 2.0461 | 5.7 | 2.0197 | -2.5329 | -0.9014 | 4.8078 |  | 4.2735 | 0.7743 | 4.0052 | 3.3677 | 3.3319 | 1.0964 | 10.7961 | 14.2812 | 14.8386 | 11.0966 | 0.0001 | -0.0028 | 0.001 | 0.0037 | 0.0008 | -0.0002 | 0.0097 | -0.0094 | -0.0029 | -360.1496 | 17.4254 | -360.4389 | 17.602 | -360.7681 | 18.1379 | -360.7804 | 17.5465 | -352.5921 | 18.723 | -352.6413 | 16.8505
13:00 | 5995 | 50.6427 | 203.1124 | 449.5521 | 452.734 | -16.6579 | -38.2894 | 12.3381 | 8.2454 | 2.5638 | 0.7592 | 2.7233 | -1.1592 | 12.3365 | 5.2138 | 0.6257 | 0.6705 | 0.9681 | 0.7562 | -129.3803 | 2.0262 | 5.6702 | 1.8518 | -2.6544 | -0.9522 | 4.7734 |  | 4.2484 | 0.827 | 4.0051 | 3.3665 | 3.3331 | 1.0955 | 10.795 | 14.2567 | 14.8593 | 11.1132 | 0.0003 | -0.0026 | 0.0011 | 0.0038 | 0.0009 | -0.0006 | 0.0113 | -0.0068 | -0.0077 | -360.0604 | 17.3597 | -360.3896 | 17.604 | -360.8143 | 18.183 | -360.8174 | 17.5301 | -352.5121 | 18.6737 | -352.589 | 16.8566
13:00 | 5996 | 50.6839 | 203.1127 | 449.4878 | 452.7221 | -16.7623 | -38.4257 | 12.339 | 8.2215 | 2.6058 | 0.822 | 2.7664 | -1.1922 | 12.2893 | 5.2226 | 0.626 | 0.6649 | 0.9659 | 0.7543 | -129.3167 | 2.1134 | 5.6939 | 1.8529 | -2.6289 | -0.9526 | 4.7415 |  | 4.2661 | 0.74 | 4.0063 | 3.3655 | 3.3292 | 1.0965 | 10.7834 | 14.2799 | 14.8535 | 11.1132 | -0.0002 | -0.0027 | 0.0009 | 0.0038 | 0.0006 | -0.0001 | 0.0339 | 0.0036 | -0.0257 | -360.2173 | 17.3946 | -360.405 | 17.5773 | -360.7435 | 18.1666 | -360.8481 | 17.5773 | -352.6321 | 18.7045 | -352.5952 | 16.8299
13:00 | 5997 | 50.661 | 203.1808 | 449.5685 | 452.7597 | -16.8127 | -38.5393 | 12.2771 | 8.1698 | 2.6174 | 0.7296 | 2.7882 | -1.2607 | 12.1549 | 5.1236 | 0.6259 | 0.6713 | 0.9658 | 0.7548 | -129.3741 | 2.0178 | 5.665 | 1.8079 | -2.6489 | -0.9983 | 4.7079 |  | 4.2405 | 0.6962 | 4.0067 | 3.3674 | 3.3305 | 1.0967 | 10.7579 | 14.2661 | 14.8461 | 11.1165 | 0.0001 | -0.0024 | 0.0006 | 0.0036 | 0.0012 | -0.0007 | 0.0187 | -0.0043 | -0.0074 | -360.1342 | 17.4028 | -360.4512 | 17.6081 | -360.8143 | 18.1337 | -360.762 | 17.5321 | -352.5521 | 18.7087 | -352.6444 | 16.8566
13:00 | 5998 | 50.638 | 203.2173 | 449.6174 | 452.7197 | -16.796 | -38.494 | 12.2179 | 8.0728 | 2.525 | 0.5233 | 2.6979 | -1.1726 | 12.1769 | 5.2227 | 0.6273 | 0.6695 | 0.9659 | 0.7546 | -129.3355 | 1.9343 | 5.7089 | 1.8015 | -2.6405 | -1.0006 | 4.7561 |  | 4.2583 | 0.6402 | 4.005 | 3.3658 | 3.3317 | 1.096 | 10.7845 | 14.2579 | 14.8433 | 11.0912 | 0 | -0.0031 | 0.0009 | 0.0039 | 0.0007 | -0.0003 | 0.0081 | -0.0112 | 0.0015 | -360.1281 | 17.3617 | -360.3742 | 17.5917 | -360.8081 | 18.2015 | -360.8574 | 17.5588 | -352.5736 | 18.6676 | -352.5675 | 16.8484
13:00 | 5999 | 50.6633 | 203.209 | 449.656 | 452.6715 | -16.8294 | -38.4816 | 12.1757 | 8.074 | 2.5723 | 0.4582 | 2.7818 | -1.1979 | 12.2707 | 5.1417 | 0.627 | 0.6678 | 0.9667 | 0.7544 | -129.2481 | 2.0056 | 5.7334 | 1.7341 | -2.6352 | -1.0032 | 4.7829 |  | 4.2853 | 0.6329 | 4.0049 | 3.3687 | 3.3282 | 1.097 | 10.7695 | 14.2717 | 14.845 | 11.0937 | 0.0003 | -0.0033 | 0.0004 | 0.0037 | 0.0011 | -0.0004 | -0.0028 | -0.0108 | -0.003 | -360.2111 | 17.411 | -360.3989 | 17.5671 | -360.7435 | 18.1707 | -360.7897 | 17.5773 | -352.6721 | 18.7107 | -352.6106 | 16.8279
13:00 | 6000 | 50.6999 | 203.2002 | 449.6749 | 452.6547 | -16.7898 | -38.4287 | 12.3086 | 8.0984 | 2.5832 | 0.5216 | 2.811 | -1.2045 | 12.1858 | 5.166 | 0.627 | 0.6688 | 0.9649 | 0.7538 | -129.2815 | 2.0043 | 5.5945 | 1.5792 | -2.658 | -1.0587 | 4.7348 |  | 4.2672 | 0.7176 | 4.0045 | 3.3697 | 3.3277 | 1.0967 | 10.7729 | 14.287 | 14.8676 | 11.1255 | 0.0002 | -0.0029 | 0.0009 | 0.0038 | 0.0008 | -0.0002 | 0.0182 | 0.0072 | 0.0009 | -360.1342 | 17.3966 | -360.4419 | 17.6184 | -360.8174 | 18.183 | -360.7804 | 17.5404 | -352.5706 | 18.7004 | -352.6475 | 16.871
13:00 | 6001 | 50.6827 | 203.1017 | 449.5628 | 452.6951 | -16.8252 | -38.4561 | 12.2979 | 8.1846 | 2.6856 | 0.5043 | 2.7703 | -1.2384 | 12.3145 | 5.2908 | 0.6273 | 0.6669 | 0.9663 | 0.754 | -129.3487 | 1.996 | 5.6186 | 1.5869 | -2.5515 | -1.031 | 4.7395 |  | 4.2302 | 0.6763 | 4.0038 | 3.3694 | 3.3329 | 1.0962 | 10.765 | 14.261 | 14.8211 | 11.0782 | -0.0007 | -0.003 | 0.0008 | 0.004 | 0.0007 | -0.0007 | 0.0017 | 0.0017 | 0.0005 | -360.1219 | 17.3576 | -360.3742 | 17.5999 | -360.7897 | 18.2077 | -360.8358 | 17.5691 | -352.589 | 18.6696 | -352.6044 | 16.8402
13:00 | 6002 | 50.6384 | 203.2 | 449.7417 | 452.7478 | -16.8479 | -38.524 | 12.2815 | 8.2596 | 2.7378 | 0.6203 | 2.8233 | -1.1816 | 12.2592 | 5.3254 | 0.6281 | 0.6651 | 0.9683 | 0.7544 | -129.2617 | 2.1515 | 5.7494 | 1.6926 | -2.4996 | -0.8769 | 4.7949 |  | 4.1767 | 0.7255 | 4.0048 | 3.3666 | 3.3302 | 1.0975 | 10.8063 | 14.3267 | 14.881 | 11.1117 | 0.0001 | -0.0025 | 0.0013 | 0.0043 | 0.0006 | -0.0004 | 0.0119 | -0.0235 | -0.0268 | -360.1958 | 17.4172 | -360.4204 | 17.5937 | -360.7773 | 18.1851 | -360.7958 | 17.5732 | -352.6352 | 18.7128 | -352.626 | 16.8381
13:00 | 6003 | 50.6266 | 203.1964 | 449.5321 | 452.6864 | -16.8978 | -38.4434 | 12.2104 | 8.1697 | 2.7122 | 0.5371 | 2.8305 | -1.2605 | 12.1467 | 5.2308 | 0.6259 | 0.6646 | 0.9693 | 0.7549 | -129.2156 | 2.1192 | 5.7516 | 1.6424 | -2.5729 | -0.878 | 4.7967 |  | 4.2112 | 0.7676 | 4.0034 | 3.3663 | 3.3315 | 1.0948 | 10.8099 | 14.2836 | 14.8356 | 11.0988 | 0.0002 | -0.003 | 0.0009 | 0.0038 | 0.0008 | -0.0004 | -0.002 | -0.0174 | -0.0076 | -360.1404 | 17.3843 | -360.4358 | 17.6204 | -360.802 | 18.2056 | -360.8174 | 17.5527 | -352.5675 | 18.6922 | -352.6106 | 16.8648
13:00 | 6004 | 50.6717 | 203.2001 | 449.6116 | 452.6807 | -16.8741 | -38.3962 | 12.1791 | 8.1746 | 2.6613 | 0.5621 | 2.8272 | -1.2366 | 12.2704 | 5.3381 | 0.6255 | 0.6645 | 0.9651 | 0.7541 | -129.29 | 1.9753 | 5.6533 | 1.6674 | -2.5024 | -0.8462 | 4.8656 |  | 4.2628 | 0.6712 | 4.0052 | 3.3666 | 3.3304 | 1.096 | 10.8157 | 14.2837 | 14.8887 | 11.1388 | -0.0002 | -0.0029 | 0.0012 | 0.0045 | 0.0009 | -0.0005 | 0.0141 | -0.0084 | -0.0263 | -360.1773 | 17.3946 | -360.4266 | 17.6061 | -360.805 | 18.2097 | -360.8604 | 17.5732 | -352.6167 | 18.6984 | -352.6383 | 16.8587
13:00 | 6005 | 50.7313 | 203.1974 | 449.4986 | 452.7159 | -17.0639 | -38.5708 | 11.9599 | 8.1391 | 2.666 | 0.5254 | 2.7435 | -1.1474 | 12.3445 | 5.3664 | 0.6274 | 0.6654 | 0.9646 | 0.7551 | -129.3524 | 1.9806 | 5.5072 | 1.6662 | -2.4695 | -0.9011 | 4.9034 |  | 4.2564 | 0.6935 | 4.0044 | 3.3647 | 3.3297 | 1.0947 | 10.8018 | 14.2756 | 14.8744 | 11.1193 | -0.0003 | -0.0025 | 0.0006 | 0.0038 | 0.0004 | -0.0009 | 0.0077 | -0.0153 | -0.0278 | -360.1865 | 17.4048 | -360.4358 | 17.6102 | -360.805 | 18.2015 | -360.845 | 17.5547 | -352.6106 | 18.7169 | -352.6413 | 16.8505
13:00 | 6006 | 50.7254 | 203.2031 | 449.5739 | 452.6539 | -16.9543 | -38.4442 | 12.0425 | 8.14 | 2.623 | 0.6108 | 2.7943 | -1.2047 | 12.2158 | 5.2732 | 0.6266 | 0.6692 | 0.9681 | 0.7561 | -129.2303 | 1.918 | 5.6361 | 1.6141 | -2.4155 | -0.8876 | 4.8849 |  | 4.2463 | 0.7734 | 4.0054 | 3.3669 | 3.329 | 1.0962 | 10.8099 | 14.2836 | 14.8877 | 11.1045 | -0.0002 | -0.0028 | 0.0009 | 0.0037 | 0.0012 | -0.0005 | 0.0259 | -0.0018 | -0.005 | -360.165 | 17.411 | -360.4389 | 17.6204 | -360.8081 | 18.2138 | -360.8481 | 17.5629 | -352.6352 | 18.7128 | -352.6506 | 16.8751
13:00 | 6007 | 50.6808 | 203.2316 | 449.5842 | 452.7576 | -16.8875 | -38.4016 | 12.0086 | 8.1223 | 2.6094 | 0.691 | 2.7902 | -1.1621 | 12.305 | 5.2724 | 0.6263 | 0.6642 | 0.9687 | 0.7546 | -129.242 | 1.9075 | 5.6947 | 1.6618 | -2.5248 | -0.9046 | 4.8975 |  | 4.2001 | 0.7187 | 4.0045 | 3.3637 | 3.3343 | 1.0968 | 10.7927 | 14.2369 | 14.8324 | 11.071 | 0.0002 | -0.0032 | 0.0008 | 0.0042 | 0.0009 | -0.0004 | 0.0313 | -0.0081 | 0.0057 | -360.1865 | 17.409 | -360.4696 | 17.6204 | -360.8143 | 18.2077 | -360.842 | 17.5547 | -352.6321 | 18.721 | -352.6475 | 16.871
13:00 | 6008 | 50.6353 | 203.1613 | 449.5598 | 452.7091 | -17.0224 | -38.5471 | 11.946 | 8.0342 | 2.5981 | 0.647 | 2.7468 | -1.228 | 12.2287 | 5.2465 | 0.6259 | 0.6665 | 0.9659 | 0.7573 | -129.2674 | 2.0832 | 5.6799 | 1.6784 | -2.5292 | -0.8853 | 4.8205 |  | 4.274 | 0.7257 | 4.0053 | 3.3676 | 3.3302 | 1.0956 | 10.7753 | 14.2545 | 14.8229 | 11.1107 | 0 | -0.0031 | 0.0013 | 0.0041 | 0.0012 | -0.0008 | 0.0242 | -0.016 | -0.0032 | -360.1896 | 17.4007 | -360.4389 | 17.6307 | -360.8481 | 18.2179 | -360.845 | 17.5486 | -352.6136 | 18.7087 | -352.6506 | 16.8731
13:00 | 6009 | 50.6067 | 203.1761 | 449.5864 | 452.6518 | -17.0158 | -38.6423 | 11.8233 | 8.0536 | 2.6283 | 0.6912 | 2.7066 | -1.2143 | 12.1638 | 5.2469 | 0.6268 | 0.6641 | 0.9656 | 0.7555 | -129.3135 | 2.1159 | 5.6193 | 1.7107 | -2.6309 | -0.9258 | 4.8279 |  | 4.387 | 0.7924 | 4.0054 | 3.3675 | 3.3341 | 1.0972 | 10.7787 | 14.2695 | 14.8549 | 11.0912 | -0.0002 | -0.0026 | 0.001 | 0.0036 | 0.0004 | 0.0001 | -0.0017 | -0.0061 | -0.0174 | -360.1558 | 17.4151 | -360.4635 | 17.602 | -360.802 | 18.22 | -360.8574 | 17.5609 | -352.6413 | 18.7148 | -352.629 | 16.8566
13:00 | 6010 | 50.6846 | 203.1774 | 449.5091 | 452.6169 | -17.0737 | -38.7008 | 11.8554 | 7.9545 | 2.576 | 0.6303 | 2.7104 | -1.1704 | 12.2415 | 5.3466 | 0.6277 | 0.6681 | 0.9661 | 0.7561 | -129.3049 | 2.0818 | 5.7233 | 1.8258 | -2.6454 | -1.0567 | 4.8839 |  | 4.2537 | 0.8151 | 4.0057 | 3.3649 | 3.3303 | 1.0961 | 10.7869 | 14.2544 | 14.8508 | 11.088 | 0.0001 | -0.0027 | 0.0013 | 0.004 | 0.001 | -0.0008 | 0.0129 | 0.0051 | -0.0155 | -360.245 | 17.4254 | -360.4758 | 17.6286 | -360.8266 | 18.1953 | -360.8081 | 17.5609 | -352.6537 | 18.7415 | -352.666 | 16.8731
13:00 | 6011 | 50.6807 | 203.1045 | 449.4898 | 452.545 | -16.9673 | -38.4993 | 11.9707 | 8.0534 | 2.6129 | 0.7284 | 2.778 | -1.231 | 12.2998 | 5.3932 | 0.6262 | 0.6669 | 0.9656 | 0.7557 | -129.3861 | 2.1054 | 5.8033 | 1.7593 | -2.7141 | -0.9606 | 4.7688 |  | 4.3041 | 0.7913 | 4.0066 | 3.3644 | 3.328 | 1.0963 | 10.7868 | 14.2489 | 14.8587 | 11.0814 | 0.0001 | -0.0031 | 0.001 | 0.0038 | 0.0009 | 0.0005 | 0.0168 | 0.004 | -0.0005 | -360.1496 | 17.4007 | -360.4481 | 17.6307 | -360.8697 | 18.2323 | -360.845 | 17.5486 | -352.586 | 18.7107 | -352.6444 | 16.8833
13:00 | 6012 | 50.6625 | 203.1444 | 449.3921 | 452.511 | -17.0356 | -38.4962 | 11.961 | 8.0844 | 2.6343 | 0.7675 | 2.7399 | -1.1486 | 12.2469 | 5.2446 | 0.6266 | 0.6674 | 0.9668 | 0.7563 | -129.3309 | 2.074 | 5.7419 | 1.7725 | -2.6905 | -0.9808 | 4.7246 |  | 4.2664 | 0.8055 | 4.0057 | 3.3659 | 3.3284 | 1.0966 | 10.8087 | 14.3057 | 14.9105 | 11.0915 | 0.0001 | -0.0028 | 0.0005 | 0.004 | 0.0008 | -0.0008 | 0.0098 | -0.0179 | -0.0006 | -360.2265 | 17.4233 | -360.4419 | 17.5937 | -360.7897 | 18.2179 | -360.8512 | 17.5876 | -352.6783 | 18.7333 | -352.6352 | 16.8525
13:00 | 6013 | 50.608 | 203.1629 | 449.4153 | 452.5654 | -16.9672 | -38.4561 | 11.9994 | 8.0725 | 2.6514 | 0.6897 | 2.7979 | -1.2689 | 12.2059 | 5.1985 | 0.6269 | 0.6653 | 0.9705 | 0.7564 | -129.3471 | 2.0412 | 5.7971 | 1.8786 | -2.5684 | -0.9468 | 4.8283 |  | 4.237 | 0.7196 | 4.0048 | 3.363 | 3.3293 | 1.0958 | 10.7938 | 14.2904 | 14.859 | 11.0944 | -0.0003 | -0.0028 | 0.0007 | 0.004 | 0.0006 | -0.0003 | -0.0079 | -0.0033 | -0.0279 | -360.1896 | 17.4274 | -360.525 | 17.6471 | -360.882 | 18.2077 | -360.8143 | 17.5445 | -352.6352 | 18.7374 | -352.6875 | 16.8936
13:00 | 6014 | 50.6678 | 203.158 | 449.3086 | 452.5927 | -16.925 | -38.4406 | 12.0795 | 8.0374 | 2.4804 | 0.6668 | 2.7679 | -1.1828 | 12.2451 | 5.2362 | 0.6263 | 0.6672 | 0.967 | 0.7547 | -129.3333 | 2.0584 | 5.6757 | 1.9367 | -2.6792 | -0.9175 | 4.8252 |  | 4.1858 | 0.7719 | 4.0062 | 3.3683 | 3.3296 | 1.0973 | 10.7833 | 14.2627 | 14.8546 | 11.0955 | 0 | -0.0023 | 0.0005 | 0.0033 | 0.0008 | -0.0006 | 0.0166 | -0.0123 | -0.0173 | -360.2019 | 17.3884 | -360.3989 | 17.5958 | -360.8204 | 18.2405 | -360.9158 | 17.5937 | -352.626 | 18.6943 | -352.6106 | 16.8381
13:00 | 6015 | 50.5047 | 203.0602 | 449.358 | 452.5141 | -16.822 | -38.4265 | 12.1216 | 8.0636 | 2.5271 | 0.7149 | 2.7375 | -1.1249 | 12.2071 | 5.1736 | 0.6268 | 0.6691 | 0.9685 | 0.7564 | -129.2763 | 2.0142 | 5.6527 | 1.9738 | -2.5866 | -1.0282 | 4.8603 |  | 4.1809 | 0.7941 | 4.0053 | 3.3664 | 3.3286 | 1.0967 | 10.7812 | 14.2656 | 14.8313 | 11.0714 | 0 | -0.003 | 0.0007 | 0.0039 | 0.0006 | -0.0008 | 0.013 | -0.0101 | -0.0149 | -360.2296 | 17.4582 | -360.5004 | 17.6286 | -360.8112 | 18.1892 | -360.7927 | 17.5547 | -352.6444 | 18.7538 | -352.6875 | 16.8566
13:00 | 6016 | 50.6272 | 203.1368 | 449.431 | 452.5929 | -16.9388 | -38.4272 | 12.1155 | 8.128 | 2.6104 | 0.8472 | 2.8217 | -1.1848 | 12.2468 | 5.2416 | 0.6251 | 0.6634 | 0.9672 | 0.7539 | -129.2841 | 1.9334 | 5.7248 | 1.9597 | -2.5802 | -1.112 | 4.8423 |  | 4.2238 | 0.8691 | 4.0041 | 3.3653 | 3.3303 | 1.096 | 10.7868 | 14.2718 | 14.8287 | 11.0991 | 0 | -0.0031 | 0.0012 | 0.0041 | 0.0003 | -0.0007 | 0.012 | -0.0125 | 0.0083 | -360.1496 | 17.3782 | -360.4296 | 17.6204 | -360.8481 | 18.2426 | -360.8543 | 17.5486 | -352.5767 | 18.6963 | -352.5736 | 16.8607
13:00 | 6017 | 50.706 | 203.1429 | 449.3947 | 452.5479 | -16.9689 | -38.5424 | 12.0711 | 8.1212 | 2.5337 | 0.6785 | 2.7087 | -1.2375 | 12.2443 | 5.226 | 0.6258 | 0.6654 | 0.967 | 0.7545 | -129.2321 | 1.92 | 5.6462 | 1.88 | -2.6298 | -1.0357 | 4.796 |  | 4.2579 | 0.8354 | 4.006 | 3.3645 | 3.3253 | 1.0954 | 10.7728 | 14.2931 | 14.8581 | 11.1132 | 0.0003 | -0.0025 | 0.0012 | 0.004 | 0.0008 | -0.0004 | -0.0099 | -0.0134 | -0.0087 | -360.1681 | 17.4233 | -360.4296 | 17.5773 | -360.762 | 18.1912 | -360.8389 | 17.5609 | -352.6229 | 18.7251 | -352.6136 | 16.8197
13:00 | 6018 | 50.7008 | 203.1842 | 449.4703 | 452.594 | -17.1064 | -38.6712 | 11.9923 | 8.187 | 2.583 | 0.7855 | 2.7414 | -1.2626 | 12.2872 | 5.2897 | 0.6268 | 0.6657 | 0.9684 | 0.7547 | -129.2548 | 1.9025 | 5.626 | 1.7795 | -2.5759 | -0.9498 | 4.7955 |  | 4.2936 | 0.6937 | 4.0043 | 3.3658 | 3.332 | 1.0969 | 10.7857 | 14.2705 | 14.8321 | 11.0869 | -0.0001 | -0.0025 | 0.0008 | 0.0039 | 0.0004 | -0.0004 | 0.0099 | -0.0114 | -0.0079 | -360.1342 | 17.3843 | -360.4696 | 17.6307 | -360.8574 | 18.2056 | -360.805 | 17.5116 | -352.5613 | 18.7045 | -352.6229 | 16.8628
13:00 | 6019 | 50.7313 | 203.077 | 449.4607 | 452.5785 | -17.0419 | -38.6445 | 11.923 | 8.1681 | 2.6258 | 0.8433 | 2.724 | -1.256 | 12.2473 | 5.2451 | 0.6262 | 0.6675 | 0.9678 | 0.7552 | -129.2767 | 1.9014 | 5.6666 | 1.6918 | -2.6541 | -0.9917 | 4.7716 |  | 4.2459 | 0.6865 | 4.0056 | 3.3669 | 3.3328 | 1.097 | 10.7752 | 14.2662 | 14.8645 | 11.1103 | 0.0006 | -0.0027 | 0.0006 | 0.0037 | 0.0008 | -0.0007 | 0.0253 | -0.0176 | -0.003 | -360.1681 | 17.3638 | -360.365 | 17.5629 | -360.7343 | 18.1994 | -360.8666 | 17.5732 | -352.5829 | 18.6922 | -352.5521 | 16.8074
13:00 | 6020 | 50.7958 | 203.1578 | 449.4648 | 452.6123 | -16.8694 | -38.4019 | 12.1029 | 8.1933 | 2.655 | 0.837 | 2.8238 | -1.074 | 12.2757 | 5.2874 | 0.6266 | 0.6703 | 0.9645 | 0.7539 | -129.2387 | 1.9992 | 5.6467 | 1.7534 | -2.6245 | -0.9305 | 4.8381 |  | 4.2788 | 0.6962 | 4.0067 | 3.3657 | 3.3323 | 1.0961 | 10.8111 | 14.2788 | 14.8706 | 11.1349 | 0.0001 | -0.0029 | 0.0004 | 0.0037 | 0.0004 | -0.0003 | 0.0167 | -0.0182 | -0.01 | -360.1619 | 17.4151 | -360.4512 | 17.5937 | -360.7681 | 18.1687 | -360.7466 | 17.5157 | -352.5921 | 18.7292 | -352.629 | 16.8546
13:00 | 6021 | 50.6649 | 203.146 | 449.4619 | 452.581 | -16.8478 | -38.4994 | 12.1387 | 8.1875 | 2.6187 | 0.8173 | 2.7686 | -1.1306 | 12.3201 | 5.2184 | 0.627 | 0.6668 | 0.9662 | 0.7543 | -129.3037 | 1.968 | 5.6751 | 1.7604 | -2.5613 | -0.9368 | 4.8373 |  | 4.1894 | 0.7028 | 4.0045 | 3.3695 | 3.3298 | 1.0953 | 10.7985 | 14.2773 | 14.8729 | 11.0941 | -0.0004 | -0.003 | 0.0009 | 0.004 | 0.0012 | -0.0007 | -0.0057 | 0.0078 | -0.0212 | -360.0911 | 17.3597 | -360.3558 | 17.5855 | -360.7958 | 18.2159 | -360.8389 | 17.5342 | -352.5521 | 18.6635 | -352.5583 | 16.8546
13:00 | 6022 | 50.6785 | 203.1226 | 449.4137 | 452.6092 | -16.8059 | -38.5016 | 12.0911 | 8.2686 | 2.6078 | 0.7421 | 2.798 | -1.1979 | 12.2579 | 5.3072 | 0.6266 | 0.6607 | 0.9673 | 0.7549 | -129.3123 | 2.0299 | 5.7403 | 1.8361 | -2.5396 | -1.0047 | 4.8228 |  | 4.2273 | 0.5993 | 4.0045 | 3.3659 | 3.3282 | 1.0948 | 10.8007 | 14.2742 | 14.8893 | 11.084 | -0.0002 | -0.0026 | 0.0008 | 0.0036 | 0.0006 | -0.0002 | 0.0059 | -0.0161 | -0.0081 | -360.1804 | 17.411 | -360.4081 | 17.5609 | -360.7527 | 18.1707 | -360.802 | 17.5568 | -352.6044 | 18.723 | -352.5921 | 16.8238
13:00 | 6023 | 50.7426 | 203.1776 | 449.428 | 452.5691 | -16.9105 | -38.4937 | 11.9668 | 8.213 | 2.5703 | 0.7183 | 2.7626 | -1.0533 | 12.3125 | 5.2443 | 0.6264 | 0.6676 | 0.9705 | 0.7545 | -129.3323 | 2.0312 | 5.7185 | 1.8749 | -2.6791 | -1.0633 | 4.7498 |  | 4.2452 | 0.7247 | 4.0057 | 3.3631 | 3.3309 | 1.097 | 10.78 | 14.276 | 14.8242 | 11.0992 | -0.0003 | -0.0031 | 0.001 | 0.0037 | 0.0007 | -0.001 | -0.0021 | -0.0033 | -0.0133 | -360.1034 | 17.3864 | -360.4358 | 17.6204 | -360.842 | 18.1851 | -360.7773 | 17.5198 | -352.549 | 18.6963 | -352.629 | 16.8669
13:00 | 6024 | 50.6845 | 203.0492 | 449.4927 | 452.6182 | -16.9414 | -38.4735 | 12.0418 | 8.2691 | 2.6235 | 0.8005 | 2.7942 | -1.1897 | 12.2138 | 5.1991 | 0.6251 | 0.6671 | 0.9686 | 0.7541 | -129.2782 | 1.9837 | 5.6901 | 1.8272 | -2.6448 | -0.9756 | 4.6771 |  | 4.2525 | 0.8014 | 4.0042 | 3.3655 | 3.3324 | 1.0978 | 10.7799 | 14.2707 | 14.8563 | 11.0981 | 0.0001 | -0.003 | 0.0013 | 0.0038 | 0.0005 | -0.0004 | 0.0176 | -0.0073 | -0.0063 | -360.165 | 17.3782 | -360.3742 | 17.5794 | -360.7558 | 18.2056 | -360.8697 | 17.5588 | -352.6444 | 18.6963 | -352.5583 | 16.8279
13:00 | 6025 | 50.6348 | 203.0458 | 449.4866 | 452.5939 | -16.964 | -38.5071 | 12.0768 | 8.2505 | 2.7142 | 0.8137 | 2.8537 | -1.2209 | 12.3174 | 5.2281 | 0.6265 | 0.6696 | 0.9695 | 0.7547 | -129.3547 | 2.0049 | 5.6665 | 1.7443 | -2.647 | -1.0809 | 4.6628 |  | 4.1396 | 0.6665 | 4.0056 | 3.3651 | 3.3287 | 1.0964 | 10.7995 | 14.2907 | 14.8438 | 11.111 | -0.0002 | -0.0029 | 0.001 | 0.0038 | 0.0012 | -0.0005 | 0.0115 | -0.0105 | 0.003 | -360.1342 | 17.4151 | -360.4758 | 17.6184 | -360.7989 | 18.1687 | -360.762 | 17.5239 | -352.6013 | 18.723 | -352.669 | 16.8669
13:00 | 6026 | 50.7139 | 203.0912 | 449.5388 | 452.635 | -16.9352 | -38.587 | 11.964 | 8.269 | 2.7465 | 0.7625 | 2.8204 | -1.2239 | 12.3409 | 5.1397 | 0.6274 | 0.6678 | 0.9697 | 0.7548 | -129.2572 | 1.9436 | 5.7003 | 1.8096 | -2.6039 | -1.064 | 4.6572 |  | 4.2331 | 0.8081 | 4.0052 | 3.3633 | 3.3308 | 1.0969 | 10.7753 | 14.2834 | 14.8519 | 11.1107 | -0.0002 | -0.0025 | 0.001 | 0.0044 | 0.0007 | -0.0004 | 0.0038 | -0.0149 | -0.0085 | -360.1558 | 17.3679 | -360.3896 | 17.5917 | -360.802 | 18.2118 | -360.8481 | 17.5506 | -352.6013 | 18.6922 | -352.5798 | 16.8361
13:00 | 6027 | 50.6439 | 203.1124 | 449.5125 | 452.6158 | -16.9875 | -38.6523 | 11.952 | 8.2779 | 2.7308 | 0.8301 | 2.8064 | -1.1756 | 12.2767 | 5.1765 | 0.627 | 0.669 | 0.9646 | 0.7547 | -129.2508 | 2.0622 | 5.7131 | 1.8393 | -2.5935 | -0.9808 | 4.7301 |  | 4.2765 | 0.6718 | 4.0044 | 3.3658 | 3.3281 | 1.095 | 10.8041 | 14.2839 | 14.8666 | 11.1327 | 0 | -0.0032 | 0.0011 | 0.0039 | 0.001 | -0.0001 | 0.0203 | -0.0016 | -0.0188 | -360.1681 | 17.4172 | -360.4266 | 17.5855 | -360.7804 | 18.181 | -360.805 | 17.5568 | -352.6321 | 18.723 | -352.6198 | 16.8361
13:00 | 6028 | 50.6476 | 203.176 | 449.4891 | 452.6429 | -16.9944 | -38.7319 | 11.9991 | 8.3731 | 2.6841 | 0.7809 | 2.8679 | -1.2002 | 12.3244 | 5.1304 | 0.6275 | 0.6668 | 0.9665 | 0.7541 | -129.2367 | 2.1418 | 5.7259 | 1.9797 | -2.5626 | -0.9268 | 4.7952 |  | 4.2789 | 0.7599 | 4.0052 | 3.364 | 3.3294 | 1.0968 | 10.825 | 14.3101 | 14.856 | 11.137 | 0.0004 | -0.0029 | 0.0002 | 0.0033 | 0.0007 | -0.0007 | -0.0007 | -0.01 | -0.0066 | -360.1219 | 17.3905 | -360.4358 | 17.604 | -360.7927 | 18.2015 | -360.7866 | 17.5219 | -352.5921 | 18.7025 | -352.6136 | 16.8607
13:00 | 6029 | 50.6363 | 203.1092 | 449.5 | 452.5966 | -16.8915 | -38.6963 | 12.0687 | 8.336 | 2.7526 | 0.8127 | 2.9214 | -1.1289 | 12.3507 | 5.2115 | 0.6271 | 0.6677 | 0.9656 | 0.7558 | -129.1435 | 2.1327 | 5.7374 | 2.0042 | -2.513 | -0.8902 | 4.7578 |  | 4.2631 | 0.7472 | 4.0044 | 3.3635 | 3.3297 | 1.0952 | 10.7892 | 14.2741 | 14.8651 | 11.0959 | -0.0002 | -0.0025 | 0.0006 | 0.0037 | 0.0006 | -0.0005 | 0.0189 | -0.0107 | -0.0116 | -360.1527 | 17.3905 | -360.3773 | 17.5937 | -360.7866 | 18.2015 | -360.845 | 17.5732 | -352.6044 | 18.7045 | -352.6136 | 16.8402
13:00 | 6030 | 50.7195 | 203.1166 | 449.4543 | 452.6686 | -16.9263 | -38.6261 | 11.9835 | 8.3087 | 2.7514 | 0.7845 | 2.828 | -1.1987 | 12.2593 | 5.1868 | 0.6256 | 0.6653 | 0.9665 | 0.7552 | -129.2163 | 2.0498 | 5.8119 | 2.0681 | -2.4927 | -0.8731 | 4.8183 |  | 4.2142 | 0.6596 | 4.0044 | 3.3641 | 3.3331 | 1.0965 | 10.7891 | 14.2917 | 14.8267 | 11.1009 | -0.0008 | -0.0028 | 0.0006 | 0.0036 | 0.0012 | -0.0003 | 0.0017 | -0.0043 | -0.0198 | -360.1465 | 17.3905 | -360.4173 | 17.6061 | -360.7897 | 18.1851 | -360.7835 | 17.5404 | -352.6106 | 18.7189 | -352.6383 | 16.8566
13:00 | 6031 | 50.6762 | 203.0658 | 449.4598 | 452.6644 | -16.9414 | -38.6283 | 12.0203 | 8.2685 | 2.7357 | 0.9343 | 2.8512 | -1.1455 | 12.381 | 5.1435 | 0.6268 | 0.669 | 0.9694 | 0.7552 | -129.2695 | 2.0779 | 5.8034 | 1.8572 | -2.5118 | -0.8384 | 4.817 |  | 4.2242 | 0.7127 | 4.0049 | 3.3686 | 3.3289 | 1.0971 | 10.7452 | 14.2589 | 14.8436 | 11.11 | 0.0001 | -0.0029 | 0.0006 | 0.0039 | 0.0006 | -0.0004 | 0.002 | -0.0019 | -0.0052 | -360.1158 | 17.3823 | -360.4081 | 17.5896 | -360.805 | 18.2077 | -360.845 | 17.5445 | -352.5706 | 18.7066 | -352.5829 | 16.8505
13:00 | 6032 | 50.7334 | 203.1163 | 449.5615 | 452.6558 | -16.9339 | -38.629 | 11.9871 | 8.2326 | 2.7927 | 0.9167 | 2.8148 | -1.1636 | 12.328 | 5.2076 | 0.6274 | 0.6649 | 0.9666 | 0.7554 | -129.2187 | 2.1032 | 5.698 | 1.7743 | -2.5203 | -0.8879 | 4.8182 |  | 4.2287 | 0.7312 | 4.0046 | 3.3691 | 3.332 | 1.0979 | 10.7752 | 14.272 | 14.8124 | 11.1045 | 0.0001 | -0.0029 | 0.0012 | 0.0039 | 0.0012 | -0.0005 | 0.0011 | -0.0042 | -0.018 | -360.1281 | 17.3843 | -360.4266 | 17.5896 | -360.7589 | 18.1912 | -360.8112 | 17.5383 | -352.6013 | 18.7169 | -352.5983 | 16.8361
13:00 | 6033 | 50.7832 | 203.1591 | 449.4971 | 452.6505 | -16.9196 | -38.667 | 11.8991 | 8.2339 | 2.7999 | 0.9128 | 2.8361 | -1.1676 | 12.261 | 5.2183 | 0.6276 | 0.6672 | 0.9714 | 0.7545 | -129.2788 | 2.0764 | 5.6572 | 1.7839 | -2.5245 | -0.9666 | 4.8451 |  | 4.2749 | 0.7322 | 4.0051 | 3.3655 | 3.33 | 1.0973 | 10.796 | 14.3104 | 14.8465 | 11.119 | 0 | -0.0026 | 0.001 | 0.0038 | 0.0009 | -0.0001 | 0.0092 | 0.0017 | -0.0162 | -360.165 | 17.3864 | -360.3989 | 17.5958 | -360.7897 | 18.1994 | -360.7989 | 17.5363 | -352.5583 | 18.7004 | -352.6136 | 16.8546
13:00 | 6034 | 50.8101 | 203.0828 | 449.4627 | 452.6889 | -16.924 | -38.6546 | 11.928 | 8.2873 | 2.7342 | 0.8726 | 2.8187 | -1.2089 | 12.3263 | 5.2059 | 0.6254 | 0.6672 | 0.9708 | 0.7558 | -129.2044 | 2.1366 | 5.6803 | 1.8446 | -2.6132 | -0.9276 | 4.8149 |  | 4.2773 | 0.7591 | 4.0036 | 3.3682 | 3.3295 | 1.0971 | 10.7742 | 14.2763 | 14.89 | 11.0984 | 0 | -0.0026 | 0.0002 | 0.0039 | 0.0009 | -0.0004 | 0.0195 | -0.0052 | -0.0148 | -360.1404 | 17.3864 | -360.3865 | 17.5773 | -360.7681 | 18.1871 | -360.8112 | 17.5506 | -352.5706 | 18.7148 | -352.6136 | 16.832
13:00 | 6035 | 50.7107 | 203.1189 | 449.5275 | 452.6338 | -16.9448 | -38.6065 | 11.9404 | 8.3531 | 2.7802 | 0.8977 | 2.9578 | -1.2448 | 12.2806 | 5.265 | 0.6265 | 0.6686 | 0.9679 | 0.7546 | -129.2298 | 2.188 | 5.7369 | 1.835 | -2.6184 | -0.9424 | 4.8018 |  | 4.2831 | 0.7914 | 4.0063 | 3.3654 | 3.3294 | 1.0966 | 10.8086 | 14.3002 | 14.8895 | 11.1255 | 0.0002 | -0.0027 | 0.0009 | 0.0041 | 0.0012 | 0.0002 | 0.0126 | -0.0046 | 0.0122 | -360.1496 | 17.3946 | -360.4327 | 17.5937 | -360.7804 | 18.2015 | -360.8112 | 17.5157 | -352.589 | 18.7148 | -352.629 | 16.8628
13:00 | 6036 | 50.7767 | 203.0975 | 449.5683 | 452.6006 | -16.893 | -38.4612 | 12.0021 | 8.229 | 2.7605 | 0.8744 | 2.9095 | -1.1704 | 12.2991 | 5.2602 | 0.6273 | 0.6684 | 0.9669 | 0.7552 | -129.2467 | 2.1902 | 5.8638 | 1.9218 | -2.6397 | -0.9929 | 4.712 |  | 4.2913 | 0.812 | 4.0045 | 3.3659 | 3.3254 | 1.0959 | 10.8053 | 14.2788 | 14.8764 | 11.1118 | 0.0003 | -0.0028 | 0.0002 | 0.0034 | 0.0007 | -0.0009 | 0.0225 | -0.0147 | 0.0055 | -360.125 | 17.374 | -360.3865 | 17.5876 | -360.7927 | 18.2077 | -360.8604 | 17.5629 | -352.6044 | 18.7004 | -352.6229 | 16.8464
13:00 | 6037 | 50.8329 | 203.1265 | 449.6481 | 452.6614 | -16.8688 | -38.5395 | 11.9776 | 8.2091 | 2.7691 | 0.8394 | 2.8293 | -1.2285 | 12.3049 | 5.2249 | 0.6259 | 0.6694 | 0.9663 | 0.7557 | -129.2458 | 2.2431 | 5.8753 | 2.0115 | -2.6888 | -1.0184 | 4.6755 |  | 4.2597 | 0.8384 | 4.0052 | 3.3645 | 3.328 | 1.0967 | 10.7927 | 14.2831 | 14.8613 | 11.1288 | 0 | -0.0031 | 0.0007 | 0.0039 | 0.0004 | -0.0003 | 0.0231 | -0.0048 | -0.0067 | -360.1927 | 17.4069 | -360.405 | 17.5896 | -360.7897 | 18.1994 | -360.8235 | 17.5547 | -352.629 | 18.7333 | -352.6106 | 16.8361
13:00 | 6038 | 50.7647 | 203.1098 | 449.4873 | 452.598 | -16.8232 | -38.4789 | 11.9872 | 8.2656 | 2.813 | 0.7621 | 2.8468 | -1.3218 | 12.2611 | 5.2273 | 0.6263 | 0.6674 | 0.9654 | 0.7549 | -129.1636 | 2.2509 | 5.757 | 1.8942 | -2.6731 | -1.0652 | 4.7014 |  | 4.2525 | 0.8344 | 4.0046 | 3.3673 | 3.3279 | 1.096 | 10.766 | 14.2511 | 14.8141 | 11.0897 | 0 | -0.0022 | 0.0014 | 0.0043 | 0.001 | -0.0007 | 0.0049 | -0.0069 | -0.0152 | -360.1311 | 17.4048 | -360.485 | 17.6328 | -360.8327 | 18.2118 | -360.802 | 17.5321 | -352.6167 | 18.723 | -352.669 | 16.8895
13:00 | 6039 | 50.74 | 202.989 | 449.4763 | 452.5951 | -16.8294 | -38.4126 | 12.0761 | 8.3392 | 2.7603 | 0.7763 | 2.8327 | -1.1847 | 12.3297 | 5.2274 | 0.6256 | 0.6677 | 0.9673 | 0.7545 | -129.1487 | 2.2025 | 5.7882 | 1.7864 | -2.6881 | -0.9661 | 4.7127 |  | 4.3608 | 0.9038 | 4.0055 | 3.364 | 3.3308 | 1.097 | 10.7835 | 14.2391 | 14.8456 | 11.0851 | 0 | -0.0029 | 0.0009 | 0.0034 | 0.0004 | -0.0007 | 0.009 | -0.0103 | -0.0092 | -360.1742 | 17.4028 | -360.4019 | 17.5937 | -360.8112 | 18.2282 | -360.9189 | 17.5814 | -352.6506 | 18.7148 | -352.5829 | 16.8443
13:00 | 6040 | 50.7419 | 203.0598 | 449.5054 | 452.6303 | -16.9363 | -38.4231 | 11.9503 | 8.2931 | 2.7249 | 0.6835 | 2.8213 | -1.1972 | 12.2376 | 5.2149 | 0.6267 | 0.6653 | 0.9685 | 0.7557 | -129.2097 | 2.172 | 5.7654 | 1.7534 | -2.6972 | -1.063 | 4.641 |  | 4.2332 | 0.8282 | 4.0044 | 3.3652 | 3.3319 | 1.0967 | 10.7718 | 14.2858 | 14.8372 | 11.1129 | 0.0005 | -0.0026 | 0.0017 | 0.0047 | 0.0011 | -0.0008 | 0.0181 | -0.0083 | -0.0101 | -360.2173 | 17.4521 | -360.4881 | 17.6245 | -360.8481 | 18.2015 | -360.8204 | 17.5588 | -352.6413 | 18.7559 | -352.706 | 16.8772
13:00 | 6041 | 50.7598 | 203.0957 | 449.5015 | 452.6288 | -16.918 | -38.5789 | 11.9554 | 8.3212 | 2.7642 | 0.7189 | 2.7966 | -1.2215 | 12.3076 | 5.2657 | 0.6269 | 0.666 | 0.9694 | 0.7558 | -129.2089 | 2.2263 | 5.7373 | 1.8935 | -2.7236 | -0.9672 | 4.6868 |  | 4.2858 | 0.8434 | 4.0045 | 3.3682 | 3.3339 | 1.0974 | 10.7879 | 14.2905 | 14.8601 | 11.123 | 0 | -0.003 | 0.0008 | 0.0035 | 0.0008 | -0.0006 | -0.0064 | 0.0009 | -0.0199 | -360.165 | 17.4007 | -360.4358 | 17.6163 | -360.8666 | 18.2405 | -360.8943 | 17.5629 | -352.5983 | 18.7128 | -352.6136 | 16.871
13:00 | 6042 | 50.7886 | 203.0317 | 449.4516 | 452.5769 | -16.9599 | -38.5971 | 11.9035 | 8.2533 | 2.734 | 0.7168 | 2.7771 | -1.3034 | 12.2082 | 5.2488 | 0.6262 | 0.6666 | 0.9669 | 0.7545 | -129.187 | 2.1615 | 5.6333 | 1.9002 | -2.7187 | -0.9735 | 4.6471 |  | 4.3034 | 0.8505 | 4.0053 | 3.3657 | 3.3306 | 1.0984 | 10.7672 | 14.2751 | 14.8307 | 11.1089 | -0.0004 | -0.0026 | 0.0003 | 0.0038 | 0.0008 | -0.0001 | 0.0093 | -0.0097 | -0.0006 | -360.2111 | 17.4418 | -360.4819 | 17.5835 | -360.7712 | 18.1912 | -360.8481 | 17.5773 | -352.6721 | 18.7538 | -352.6198 | 16.834
13:00 | 6043 | 50.7474 | 203.0468 | 449.5995 | 452.64 | -17.1175 | -38.7042 | 11.7507 | 8.2236 | 2.8186 | 0.8276 | 2.8181 | -1.172 | 12.1348 | 5.1951 | 0.6272 | 0.6689 | 0.9738 | 0.7566 | -129.1953 | 2.1927 | 5.537 | 1.806 | -2.6979 | -0.9825 | 4.6755 |  | 4.2585 | 0.7469 | 4.0039 | 3.3612 | 3.333 | 1.0968 | 10.8018 | 14.2871 | 14.8281 | 11.1078 | 0.0001 | -0.0027 | 0.0007 | 0.004 | 0.0009 | -0.0006 | 0.0095 | -0.0202 | -0.0176 | -360.1773 | 17.4048 | -360.4789 | 17.6533 | -360.882 | 18.2077 | -360.8266 | 17.5301 | -352.5706 | 18.7189 | -352.666 | 16.8648
13:00 | 6044 | 50.7285 | 203.0547 | 449.5119 | 452.612 | -17.1391 | -38.5288 | 11.7856 | 8.251 | 2.809 | 0.7795 | 2.8865 | -1.2329 | 12.203 | 5.1261 | 0.6275 | 0.6646 | 0.9678 | 0.7568 | -129.2437 | 2.1148 | 5.6228 | 1.9032 | -2.6884 | -0.9769 | 4.6992 |  | 4.1828 | 0.7688 | 4.0047 | 3.3649 | 3.3335 | 1.0956 | 10.8055 | 14.2726 | 14.8616 | 11.1302 | 0 | -0.0034 | 0.0004 | 0.0037 | 0.0006 | -0.0001 | 0.0166 | -0.0098 | -0.0163 | -360.2204 | 17.3966 | -360.405 | 17.5835 | -360.7743 | 18.2138 | -360.8512 | 17.5732 | -352.6475 | 18.6963 | -352.5583 | 16.8197
13:00 | 6045 | 50.8497 | 203.1382 | 449.5393 | 452.6745 | -17.1115 | -38.5479 | 11.7501 | 8.2232 | 2.8155 | 0.7916 | 2.8606 | -1.3384 | 12.163 | 5.0938 | 0.6249 | 0.6672 | 0.9658 | 0.7562 | -129.2545 | 2.1662 | 5.5561 | 2.0061 | -2.6174 | -0.881 | 4.7482 |  | 4.2217 | 0.8284 | 4.0052 | 3.3698 | 3.3307 | 1.0978 | 10.7776 | 14.2683 | 14.8478 | 11.0843 | 0.0002 | -0.0029 | 0.001 | 0.004 | 0.0012 | -0.0007 | 0.0124 | 0.0013 | -0.0121 | -360.2235 | 17.4295 | -360.4696 | 17.6163 | -360.7989 | 18.1604 | -360.7681 | 17.5486 | -352.589 | 18.7436 | -352.6844 | 16.8402
13:00 | 6046 | 50.802 | 203.0517 | 449.4579 | 452.6978 | -17.0025 | -38.4418 | 11.8019 | 8.2524 | 2.7847 | 0.7224 | 2.8483 | -1.3593 | 12.2013 | 5.0787 | 0.6266 | 0.6671 | 0.965 | 0.7567 | -129.2313 | 2.2638 | 5.5184 | 1.9941 | -2.6173 | -0.957 | 4.7288 |  | 4.2603 | 0.8146 | 4.0038 | 3.3647 | 3.3262 | 1.0965 | 10.7696 | 14.2425 | 14.8197 | 11.0772 | -0.0004 | -0.0027 | 0.0011 | 0.0037 | 0.0008 | -0.0003 | 0.012 | -0.0139 | -0.0171 | -360.0973 | 17.3597 | -360.3896 | 17.6143 | -360.842 | 18.2179 | -360.845 | 17.526 | -352.546 | 18.6758 | -352.5644 | 16.8423
13:00 | 6047 | 50.866 | 203.0806 | 449.4576 | 452.6558 | -16.9202 | -38.3783 | 11.9498 | 8.2131 | 2.8393 | 0.8052 | 2.8527 | -1.2795 | 12.183 | 5.2105 | 0.6268 | 0.6645 | 0.966 | 0.7555 | -129.2744 | 2.2092 | 5.6178 | 1.8751 | -2.5928 | -1.0175 | 4.7876 |  | 4.2077 | 0.7168 | 4.005 | 3.3662 | 3.3318 | 1.0976 | 10.8007 | 14.3031 | 14.8546 | 11.1186 | -0.0004 | -0.0031 | 0.0011 | 0.0037 | 0.0011 | -0.0006 | 0.0112 | -0.0103 | -0.0079 | -360.1988 | 17.4028 | -360.3989 | 17.5753 | -360.7312 | 18.1789 | -360.805 | 17.5753 | -352.6167 | 18.7128 | -352.5921 | 16.8074
13:01 | 6048 | 50.8821 | 203.0737 | 449.5145 | 452.7745 | -16.89 | -38.2654 | 11.9281 | 8.2283 | 2.7743 | 0.7164 | 2.8742 | -1.325 | 12.2058 | 5.1284 | 0.626 | 0.6668 | 0.9651 | 0.7561 | -129.1522 | 2.2577 | 5.5923 | 1.7496 | -2.5967 | -1.0375 | 4.7412 |  | 4.242 | 0.7886 | 4.0044 | 3.3645 | 3.3313 | 1.0969 | 10.7798 | 14.2882 | 14.8631 | 11.1092 | 0.0003 | -0.0028 | 0.0014 | 0.0045 | 0.0003 | -0.0006 | 0.0151 | 0.0033 | -0.019 | -360.1065 | 17.4007 | -360.4542 | 17.6184 | -360.8174 | 18.1769 | -360.7558 | 17.5096 | -352.546 | 18.721 | -352.6321 | 16.8648
13:01 | 6049 | 50.8286 | 203.069 | 449.5596 | 452.8102 | -16.942 | -38.3788 | 11.9877 | 8.1385 | 2.8 | 0.7771 | 2.9083 | -1.2725 | 12.2393 | 5.1536 | 0.6263 | 0.6646 | 0.9661 | 0.756 | -129.1957 | 2.2145 | 5.6552 | 1.7552 | -2.7258 | -1.0909 | 4.7088 |  | 4.2518 | 0.8054 | 4.0047 | 3.3653 | 3.3343 | 1.0973 | 10.7752 | 14.3184 | 14.8424 | 11.1215 | -0.0004 | -0.003 | 0.0008 | 0.0038 | 0.0008 | -0.0008 | 0.031 | 0.0003 | 0.0134 | -360.0881 | 17.3556 | -360.3681 | 17.5835 | -360.765 | 18.22 | -360.8512 | 17.5445 | -352.5767 | 18.684 | -352.549 | 16.832
13:01 | 6050 | 50.7218 | 203.0544 | 449.5134 | 452.6435 | -17.0225 | -38.4666 | 11.8509 | 8.1895 | 2.8069 | 0.7913 | 2.8758 | -1.2895 | 12.2274 | 5.0919 | 0.6275 | 0.6672 | 0.9654 | 0.7565 | -129.2778 | 2.1948 | 5.5916 | 1.8618 | -2.7544 | -0.9938 | 4.7554 |  | 4.2576 | 0.7885 | 4.003 | 3.3678 | 3.3303 | 1.0982 | 10.7914 | 14.2997 | 14.8805 | 11.1092 | 0 | -0.0024 | 0.0002 | 0.0034 | 0.0008 | -0.0002 | 0.0109 | -0.0101 | 0.0039 | -360.165 | 17.4192 | -360.4266 | 17.5732 | -360.7343 | 18.1625 | -360.7773 | 17.5527 | -352.6136 | 18.7292 | -352.5829 | 16.8238
13:01 | 6051 | 50.7589 | 203.1214 | 449.4755 | 452.7671 | -16.8846 | -38.6085 | 11.8605 | 8.2123 | 2.712 | 0.7079 | 2.8471 | -1.2178 | 12.2747 | 5.2899 | 0.6253 | 0.6686 | 0.9689 | 0.7564 | -129.3329 | 2.1659 | 5.4879 | 1.8739 | -2.715 | -1.0046 | 4.7207 |  | 4.2747 | 0.7882 | 4.0043 | 3.3627 | 3.3315 | 1.0962 | 10.7787 | 14.3042 | 14.8897 | 11.1143 | -0.0002 | -0.0031 | 0.0007 | 0.0038 | 0.0009 | -0.0008 | -0.0084 | -0.0065 | -0.0261 | -360.1158 | 17.3802 | -360.4266 | 17.6245 | -360.8235 | 18.2097 | -360.7927 | 17.5157 | -352.5613 | 18.7066 | -352.6321 | 16.8607
13:01 | 6052 | 50.7203 | 203.0208 | 449.5308 | 452.8042 | -16.9233 | -38.4339 | 11.9316 | 8.2756 | 2.8697 | 0.8109 | 2.9436 | -1.2475 | 12.2599 | 5.2492 | 0.6257 | 0.6649 | 0.9688 | 0.7577 | -129.3352 | 2.2112 | 5.5938 | 1.8688 | -2.6465 | -0.9871 | 4.6749 |  | 4.2817 | 0.76 | 4.0046 | 3.3623 | 3.3292 | 1.0976 | 10.8087 | 14.3116 | 14.8826 | 11.1374 | 0.0004 | -0.0032 | 0.0006 | 0.0041 | 0.0009 | -0.0002 | -0.0084 | -0.0027 | -0.0054 | -360.1496 | 17.372 | -360.3619 | 17.5814 | -360.7804 | 18.2159 | -360.8697 | 17.565 | -352.5952 | 18.6943 | -352.5675 | 16.8258
13:01 | 6053 | 50.7942 | 203.0638 | 449.5093 | 452.7036 | -16.9483 | -38.554 | 11.9085 | 8.2023 | 2.8365 | 0.8316 | 2.8777 | -1.2159 | 12.342 | 5.289 | 0.6251 | 0.6655 | 0.9688 | 0.7556 | -129.3443 | 2.1924 | 5.5387 | 1.851 | -2.6859 | -0.9607 | 4.7205 |  | 4.2111 | 0.8126 | 4.0043 | 3.3618 | 3.3328 | 1.0983 | 10.7626 | 14.2821 | 14.8436 | 11.1158 | -0.0001 | -0.0034 | 0.0006 | 0.0036 | 0.0005 | -0.0007 | 0.0163 | -0.0066 | -0.0157 | -360.1804 | 17.4192 | -360.4512 | 17.6102 | -360.765 | 18.1912 | -360.7681 | 17.5404 | -352.6229 | 18.7353 | -352.6506 | 16.8443
13:01 | 6054 | 50.8203 | 203.153 | 449.5218 | 452.7632 | -16.8874 | -38.4703 | 11.9597 | 8.1763 | 2.702 | 0.7226 | 2.8908 | -1.2601 | 12.2603 | 5.2361 | 0.6256 | 0.6683 | 0.9688 | 0.7565 | -129.3241 | 2.2714 | 5.5923 | 1.8854 | -2.549 | -0.8149 | 4.7253 |  | 4.2699 | 0.7139 | 4.004 | 3.3623 | 3.3307 | 1.0976 | 10.788 | 14.2787 | 14.8522 | 11.1121 | -0.0004 | -0.0027 | 0.001 | 0.0037 | 0.0008 | -0.0004 | 0.013 | -0.0016 | -0.0074 | -360.085 | 17.3823 | -360.4112 | 17.6204 | -360.8512 | 18.2344 | -360.8143 | 17.5424 | -352.5767 | 18.6922 | -352.629 | 16.8607
13:01 | 6055 | 50.7632 | 203.1057 | 449.4724 | 452.7354 | -16.7435 | -38.3816 | 12.1248 | 8.1623 | 2.6857 | 0.7895 | 2.8742 | -1.3262 | 12.3247 | 5.1435 | 0.6259 | 0.6666 | 0.9694 | 0.7572 | -129.2595 | 2.2013 | 5.7078 | 1.9329 | -2.5826 | -0.7797 | 4.8323 |  | 4.2495 | 0.7836 | 4.0036 | 3.3618 | 3.3287 | 1.0979 | 10.7949 | 14.3033 | 14.8615 | 11.1125 | 0.0001 | -0.0024 | 0.001 | 0.0038 | 0.0009 | -0.0001 | 0.0155 | -0.0097 | 0.0137 | -360.1927 | 17.4069 | -360.4142 | 17.602 | -360.765 | 18.2097 | -360.8481 | 17.5753 | -352.6506 | 18.7251 | -352.6136 | 16.8361
13:01 | 6056 | 50.7837 | 203.0906 | 449.5089 | 452.7183 | -16.7432 | -38.2652 | 12.0279 | 8.0886 | 2.6061 | 0.7427 | 2.835 | -1.2635 | 12.2741 | 5.2801 | 0.6252 | 0.6661 | 0.9687 | 0.7551 | -129.2415 | 2.3166 | 5.7407 | 1.885 | -2.6427 | -0.8773 | 4.7573 |  | 4.253 | 0.7276 | 4.0042 | 3.3645 | 3.3312 | 1.0979 | 10.7754 | 14.2831 | 14.8845 | 11.1114 | 0.0002 | -0.0031 | 0.0007 | 0.0037 | 0.0007 | -0.0008 | 0.0291 | -0.018 | -0.0083 | -360.1588 | 17.4336 | -360.4912 | 17.641 | -360.842 | 18.2138 | -360.802 | 17.5465 | -352.6352 | 18.7395 | -352.6937 | 16.8792
13:01 | 6057 | 50.797 | 203.1598 | 449.5511 | 452.7645 | -16.7004 | -38.3784 | 12.053 | 8.1143 | 2.6682 | 0.8504 | 2.7926 | -1.3106 | 12.3421 | 5.2118 | 0.6265 | 0.6633 | 0.9703 | 0.7552 | -129.1113 | 2.2981 | 5.6794 | 1.8498 | -2.6538 | -0.9066 | 4.7343 |  | 4.2798 | 0.7841 | 4.0036 | 3.3656 | 3.3308 | 1.0978 | 10.8249 | 14.2932 | 14.8881 | 11.1359 | 0.0001 | -0.0027 | 0.0009 | 0.004 | 0.0013 | 0 | 0.0128 | -0.0114 | -0.006 | -360.1681 | 17.3823 | -360.4019 | 17.6225 | -360.8327 | 18.2426 | -360.885 | 17.5568 | -352.626 | 18.7025 | -352.6229 | 16.8546
13:01 | 6058 | 50.7758 | 203.124 | 449.5319 | 452.7146 | -16.7307 | -38.319 | 12.1658 | 8.2714 | 2.672 | 0.8346 | 2.831 | -1.2005 | 12.2716 | 5.2778 | 0.6266 | 0.6607 | 0.9691 | 0.7561 | -129.1569 | 2.2664 | 5.6385 | 1.8089 | -2.6479 | -0.9644 | 4.7257 |  | 4.2556 | 0.753 | 4.0041 | 3.3626 | 3.3317 | 1.0964 | 10.8088 | 14.288 | 14.8737 | 11.1327 | -0.0003 | -0.0029 | 0.0002 | 0.0037 | 0.001 | -0.0005 | 0.012 | 0.0008 | -0.0034 | -360.2081 | 17.4397 | -360.4573 | 17.6122 | -360.7958 | 18.2077 | -360.8358 | 17.5671 | -352.669 | 18.7559 | -352.666 | 16.8525
13:01 | 6059 | 50.8082 | 203.0841 | 449.5267 | 452.7228 | -16.8322 | -38.6234 | 12.028 | 8.2162 | 2.6218 | 0.869 | 2.8446 | -1.2072 | 12.2796 | 5.3567 | 0.6269 | 0.6638 | 0.969 | 0.7567 | -129.2367 | 2.1625 | 5.6925 | 1.8422 | -2.6714 | -1.0079 | 4.7369 |  | 4.2732 | 0.7528 | 4.0053 | 3.3655 | 3.3312 | 1.0974 | 10.7845 | 14.2926 | 14.8665 | 11.1085 | -0.0002 | -0.0027 | 0.0007 | 0.0042 | 0.0002 | -0.0005 | -0.0009 | -0.0037 | 0.0116 | -360.1496 | 17.411 | -360.4696 | 17.6389 | -360.8635 | 18.2405 | -360.8481 | 17.5527 | -352.6106 | 18.723 | -352.666 | 16.871
13:01 | 6060 | 50.7827 | 203.1492 | 449.5325 | 452.7438 | -16.8489 | -38.6526 | 12.0866 | 8.1483 | 2.7677 | 0.9244 | 2.8604 | -1.1878 | 12.3509 | 5.3692 | 0.6271 | 0.6614 | 0.9667 | 0.7547 | -129.2227 | 2.2651 | 5.6704 | 1.9216 | -2.7652 | -1.0254 | 4.6733 |  | 4.2576 | 0.7904 | 4.0055 | 3.364 | 3.3299 | 1.0983 | 10.7972 | 14.2652 | 14.8353 | 11.0857 | 0.0007 | -0.0023 | 0.0008 | 0.004 | 0.0011 | -0.0008 | 0.0171 | -0.0121 | -0.0197 | -360.2235 | 17.4131 | -360.4604 | 17.6184 | -360.8204 | 18.2405 | -360.8697 | 17.5794 | -352.6413 | 18.7251 | -352.6321 | 16.8566
13:01 | 6061 | 50.8214 | 203.0444 | 449.609 | 452.7904 | -16.7227 | -38.6181 | 12.1341 | 8.1292 | 2.7232 | 0.8129 | 2.8439 | -1.2095 | 12.2885 | 5.2821 | 0.6271 | 0.6617 | 0.9681 | 0.7549 | -129.2347 | 2.2239 | 5.5807 | 1.8524 | -2.7127 | -1.0739 | 4.6516 |  | 4.2795 | 0.7526 | 4.005 | 3.3657 | 3.3359 | 1.0982 | 10.8043 | 14.2658 | 14.8613 | 11.1114 | 0 | -0.0032 | 0.0012 | 0.0036 | 0.0004 | -0.0007 | 0.0178 | -0.007 | -0.0187 | -360.2081 | 17.4377 | -360.4758 | 17.6348 | -360.8574 | 18.2138 | -360.8112 | 17.5588 | -352.6352 | 18.7477 | -352.669 | 16.8607
13:01 | 6062 | 50.7198 | 203.105 | 449.6098 | 452.7558 | -16.7307 | -38.4838 | 12.1607 | 8.1945 | 2.6854 | 0.8368 | 2.8596 | -1.2511 | 12.2516 | 5.2423 | 0.625 | 0.6637 | 0.9698 | 0.7534 | -129.1769 | 2.3472 | 5.6725 | 1.8092 | -2.6529 | -0.9009 | 4.6859 |  | 4.3743 | 0.7747 | 4.0042 | 3.3646 | 3.3308 | 1.0989 | 10.7625 | 14.236 | 14.8158 | 11.1038 | 0 | -0.0024 | 0.0014 | 0.004 | 0.0012 | -0.0007 | 0.0144 | -0.0079 | -0.0025 | -360.1311 | 17.4007 | -360.4666 | 17.6307 | -360.885 | 18.2631 | -360.8512 | 17.5691 | -352.6413 | 18.723 | -352.6475 | 16.8648
13:01 | 6063 | 50.8337 | 203.1371 | 449.5474 | 452.804 | -16.7505 | -38.5481 | 12.1273 | 8.1659 | 2.7081 | 0.8791 | 2.8569 | -1.258 | 12.2351 | 5.2577 | 0.627 | 0.6609 | 0.9702 | 0.7526 | -129.2151 | 2.265 | 5.6018 | 1.6656 | -2.71 | -0.9813 | 4.647 |  | 4.2456 | 0.7575 | 4.0032 | 3.3658 | 3.3313 | 1.0964 | 10.7834 | 14.3028 | 14.8351 | 11.0789 | -0.0003 | -0.0026 | 0.001 | 0.0035 | 0.0004 | -0.0007 | -0.0034 | -0.0015 | -0.0136 | -360.2542 | 17.4192 | -360.4358 | 17.6061 | -360.8204 | 18.2261 | -360.8666 | 17.5671 | -352.6198 | 18.7333 | -352.6321 | 16.8443
13:01 | 6064 | 50.742 | 203.14 | 449.4707 | 452.7407 | -16.794 | -38.5201 | 12.1294 | 8.2113 | 2.7622 | 0.901 | 2.8436 | -1.2792 | 12.2036 | 5.2689 | 0.6279 | 0.6646 | 0.9688 | 0.7542 | -129.1619 | 2.4005 | 5.6696 | 1.8549 | -2.679 | -1.0349 | 4.7034 |  | 4.1852 | 0.7705 | 4.0018 | 3.3645 | 3.3296 | 1.0995 | 10.7719 | 14.2796 | 14.8283 | 11.0966 | 0.0001 | -0.0032 | 0.0007 | 0.0037 | 0.0009 | -0.0007 | -0.0097 | -0.0175 | -0.0106 | -360.1988 | 17.4233 | -360.4881 | 17.643 | -360.8574 | 18.222 | -360.8389 | 17.5568 | -352.6352 | 18.7415 | -352.6752 | 16.8628
13:01 | 6065 | 50.7592 | 203.173 | 449.545 | 452.7397 | -16.7862 | -38.4238 | 12.1609 | 8.2271 | 2.775 | 0.8465 | 2.8659 | -1.289 | 12.1907 | 5.2213 | 0.6256 | 0.6653 | 0.9678 | 0.7553 | -129.1421 | 2.3351 | 5.61 | 1.8104 | -2.75 | -1.0152 | 4.7111 |  | 4.2622 | 0.8361 | 4.0041 | 3.3643 | 3.3286 | 1.0979 | 10.8007 | 14.2802 | 14.8615 | 11.0836 | 0.0002 | -0.0029 | 0.0008 | 0.0039 | 0.0009 | -0.0006 | 0.0039 | -0.0162 | 0.0008 | -360.1958 | 17.4028 | -360.3958 | 17.6184 | -360.8266 | 18.2364 | -360.8635 | 17.5732 | -352.6106 | 18.7169 | -352.629 | 16.8464
13:01 | 6066 | 50.7883 | 203.0449 | 449.5301 | 452.7773 | -16.775 | -38.4664 | 12.2752 | 8.365 | 2.8544 | 1.0225 | 2.8987 | -1.2636 | 12.2216 | 5.2721 | 0.6263 | 0.663 | 0.9681 | 0.7541 | -129.083 | 2.3285 | 5.6751 | 1.8242 | -2.686 | -0.9752 | 4.7212 |  | 4.3523 | 0.8751 | 4.0038 | 3.3659 | 3.3306 | 1.0977 | 10.7684 | 14.2821 | 14.8784 | 11.1331 | -0.0005 | -0.0028 | 0.0001 | 0.0037 | 0.0007 | -0.0004 | 0.0192 | -0.0028 | -0.0129 | -360.1927 | 17.4377 | -360.4573 | 17.6225 | -360.8204 | 18.2302 | -360.8297 | 17.5712 | -352.6537 | 18.7477 | -352.6444 | 16.8566
13:01 | 6067 | 50.8378 | 203.1434 | 449.5275 | 452.8886 | -16.6963 | -38.4203 | 12.2459 | 8.2728 | 2.7715 | 1.1255 | 2.8829 | -1.3048 | 12.1439 | 5.3073 | 0.6259 | 0.667 | 0.9639 | 0.7536 | -129.0766 | 2.3057 | 5.6869 | 1.8319 | -2.734 | -1.096 | 4.6405 |  | 4.2388 | 0.7133 | 4.0031 | 3.3649 | 3.3326 | 1.0974 | 10.7845 | 14.2696 | 14.8444 | 11.1024 | -0.0003 | -0.0027 | 0.0011 | 0.0044 | 0.0009 | -0.0001 | 0.0092 | 0.0024 | -0.0265 | -360.205 | 17.4172 | -360.445 | 17.6225 | -360.8604 | 18.2282 | -360.8574 | 17.5527 | -352.589 | 18.7169 | -352.629 | 16.8566
13:01 | 6068 | 50.8438 | 203.1359 | 449.5484 | 452.7932 | -16.7084 | -38.3125 | 12.2536 | 8.2117 | 2.7531 | 1.0521 | 2.8434 | -1.2656 | 12.2569 | 5.3044 | 0.6251 | 0.6652 | 0.9667 | 0.7543 | -129.0298 | 2.3431 | 5.7308 | 1.8373 | -2.754 | -0.9694 | 4.714 |  | 4.2545 | 0.8367 | 4.0034 | 3.3642 | 3.3296 | 1.0976 | 10.758 | 14.2658 | 14.8555 | 11.0883 | -0.0002 | -0.0033 | 0.0008 | 0.0037 | 0.0006 | -0.0006 | 0.0297 | -0.0022 | -0.0222 | -360.1865 | 17.4069 | -360.4389 | 17.6184 | -360.8266 | 18.2323 | -360.882 | 17.5691 | -352.6167 | 18.7271 | -352.6229 | 16.8423
13:01 | 6069 | 50.8043 | 203.0991 | 449.4936 | 452.7908 | -16.7144 | -38.3479 | 12.2038 | 8.1905 | 2.7712 | 0.9352 | 2.8752 | -1.1984 | 12.2406 | 5.2825 | 0.6261 | 0.6652 | 0.97 | 0.7561 | -129.0243 | 2.4831 | 5.6646 | 1.8099 | -2.6911 | -1.0151 | 4.7448 |  | 4.2227 | 0.8274 | 4.004 | 3.3675 | 3.3301 | 1.0971 | 10.8308 | 14.287 | 14.8734 | 11.1486 | 0.0003 | -0.0029 | 0.001 | 0.0039 | 0.001 | -0.0003 | 0.0139 | -0.0002 | -0.0009 | -360.1865 | 17.4172 | -360.4789 | 17.6225 | -360.8235 | 18.2159 | -360.8235 | 17.5424 | -352.6198 | 18.7374 | -352.6567 | 16.8484
13:01 | 6070 | 50.7813 | 203.1038 | 449.4875 | 452.7898 | -16.6906 | -38.2543 | 12.2668 | 8.187 | 2.7797 | 1.0172 | 2.9136 | -1.2299 | 12.2464 | 5.2934 | 0.6253 | 0.6644 | 0.9683 | 0.7554 | -129.0836 | 2.351 | 5.7038 | 1.7077 | -2.7852 | -1.0796 | 4.6972 |  | 4.3129 | 0.8453 | 4.004 | 3.3676 | 3.3335 | 1.0982 | 10.7661 | 14.2508 | 14.8293 | 11.0732 | -0.0006 | -0.0031 | 0.0011 | 0.0043 | 0.0007 | -0.0001 | -0.0087 | -0.0155 | -0.0232 | -360.1558 | 17.4131 | -360.4327 | 17.6307 | -360.8512 | 18.2344 | -360.8666 | 17.5588 | -352.5921 | 18.7148 | -352.6444 | 16.8464
13:01 | 6071 | 50.8202 | 203.1404 | 449.4284 | 452.7761 | -16.6439 | -38.2024 | 12.1533 | 8.1528 | 2.9022 | 0.9486 | 2.8854 | -1.3434 | 12.2754 | 5.1683 | 0.6244 | 0.6629 | 0.9703 | 0.7561 | -129.0353 | 2.3297 | 5.6964 | 1.7496 | -2.7328 | -0.9916 | 4.7043 |  | 4.319 | 0.7836 | 4.0037 | 3.3695 | 3.3334 | 1.0977 | 10.7684 | 14.253 | 14.8426 | 11.093 | -0.0005 | -0.0027 | 0.0007 | 0.0037 | 0.001 | -0.0007 | 0.0079 | -0.0138 | 0.0084 | -360.1804 | 17.4172 | -360.4666 | 17.6184 | -360.8081 | 18.22 | -360.8574 | 17.5671 | -352.6321 | 18.7271 | -352.6229 | 16.8361
13:01 | 6072 | 50.7568 | 203.1421 | 449.4612 | 452.7583 | -16.6977 | -38.1902 | 12.1938 | 8.1522 | 2.8522 | 0.906 | 2.8272 | -1.32 | 12.29 | 5.1683 | 0.6254 | 0.6636 | 0.9696 | 0.7548 | -129.0069 | 2.4273 | 5.7257 | 1.8014 | -2.7539 | -0.9396 | 4.7517 |  | 4.2427 | 0.7387 | 4.0042 | 3.3673 | 3.3348 | 1.0968 | 10.8064 | 14.2802 | 14.8499 | 11.1067 | 0.0004 | -0.0024 | 0.0008 | 0.004 | 0.0009 | 0.0002 | 0.0106 | -0.007 | 0.0028 | -360.1681 | 17.411 | -360.4666 | 17.6245 | -360.8235 | 18.222 | -360.8327 | 17.5465 | -352.6106 | 18.7292 | -352.6229 | 16.8484
13:01 | 6073 | 50.7966 | 203.1139 | 449.5586 | 452.7928 | -16.7223 | -38.3095 | 12.0977 | 8.1787 | 2.8232 | 0.8507 | 2.8434 | -1.2839 | 12.3108 | 5.2203 | 0.6249 | 0.6666 | 0.9725 | 0.7565 | -128.9987 | 2.412 | 5.6773 | 1.8471 | -2.7774 | -1.0206 | 4.7945 |  | 4.3423 | 0.8953 | 4.004 | 3.3636 | 3.3319 | 1.0964 | 10.7845 | 14.31 | 14.8549 | 11.1143 | -0.0001 | -0.0033 | 0.0005 | 0.0039 | 0.0007 | -0.0012 | -0.0089 | -0.0107 | -0.0013 | -360.1865 | 17.4069 | -360.4358 | 17.6184 | -360.8358 | 18.2302 | -360.8543 | 17.5568 | -352.6075 | 18.7107 | -352.6352 | 16.8381
13:01 | 6074 | 50.8178 | 203.1872 | 449.4756 | 452.7865 | -16.6555 | -38.2538 | 12.142 | 8.2711 | 2.8393 | 0.9489 | 2.9569 | -1.2012 | 12.3447 | 5.3282 | 0.6261 | 0.6649 | 0.9719 | 0.7558 | -129.0806 | 2.3468 | 5.64 | 1.6966 | -2.7866 | -0.9918 | 4.6177 |  | 4.362 | 0.854 | 4.0033 | 3.363 | 3.3273 | 1.096 | 10.8145 | 14.3114 | 14.8874 | 11.0857 | 0 | -0.0027 | 0.0009 | 0.0041 | 0.0006 | -0.0001 | 0.021 | 0.0072 | -0.0087 | -360.1896 | 17.4151 | -360.4481 | 17.6102 | -360.7835 | 18.22 | -360.8327 | 17.5609 | -352.6044 | 18.7128 | -352.629 | 16.832
13:01 | 6075 | 50.8956 | 203.1298 | 449.4876 | 452.8476 | -16.729 | -38.237 | 12.0566 | 8.2503 | 2.8334 | 0.7742 | 2.9287 | -1.3415 | 12.2794 | 5.1931 | 0.6249 | 0.6621 | 0.9701 | 0.7538 | -129.0082 | 2.3211 | 5.6554 | 1.7725 | -2.7615 | -1.1126 | 4.6246 |  | 4.3054 | 0.8503 | 4.0036 | 3.3624 | 3.3324 | 1.0976 | 10.8029 | 14.2942 | 14.8711 | 11.1432 | -0.0004 | -0.0029 | 0.0011 | 0.0042 | 0.0011 | -0.0003 | 0.0289 | -0.0092 | -0.0088 | -360.1865 | 17.4131 | -360.4635 | 17.6328 | -360.8112 | 18.2241 | -360.845 | 17.5465 | -352.6075 | 18.7128 | -352.6198 | 16.8423
13:01 | 6076 | 50.9496 | 203.141 | 449.5069 | 452.8474 | -16.8536 | -38.2992 | 11.9809 | 8.272 | 2.8305 | 0.789 | 2.9161 | -1.2279 | 12.3105 | 5.2574 | 0.6275 | 0.6678 | 0.9664 | 0.7554 | -128.9706 | 2.3818 | 5.6113 | 1.9188 | -2.6752 | -1.0775 | 4.6918 |  | 4.3758 | 0.9523 | 4.0039 | 3.3686 | 3.3325 | 1.0952 | 10.795 | 14.2508 | 14.8467 | 11.0963 | -0.0001 | -0.0029 | 0.0008 | 0.0035 | 0.0008 | 0.0001 | 0.0153 | -0.0049 | -0.0074 | -360.1988 | 17.3946 | -360.4204 | 17.6163 | -360.8204 | 18.2261 | -360.8235 | 17.5465 | -352.5921 | 18.7107 | -352.5952 | 16.8299
13:01 | 6077 | 50.8602 | 203.1444 | 449.5446 | 452.8237 | -16.8881 | -38.3063 | 11.9491 | 8.1205 | 2.7232 | 0.7163 | 2.8072 | -1.3498 | 12.2988 | 5.1901 | 0.6262 | 0.6667 | 0.9689 | 0.7547 | -128.9924 | 2.3576 | 5.7331 | 1.9451 | -2.7161 | -0.9468 | 4.7415 |  | 4.2797 | 0.9126 | 4.0031 | 3.3671 | 3.3351 | 1.0969 | 10.7752 | 14.2604 | 14.8356 | 11.093 | 0.0006 | -0.0028 | 0.0008 | 0.0035 | 0.001 | -0.0004 | 0.0154 | -0.0171 | -0.0171 | -360.1773 | 17.4172 | -360.4635 | 17.6143 | -360.7897 | 18.2097 | -360.8174 | 17.5486 | -352.5983 | 18.7169 | -352.6136 | 16.832
13:01 | 6078 | 50.8218 | 203.1507 | 449.523 | 452.7963 | -16.9412 | -38.3791 | 12.0189 | 8.1245 | 2.7035 | 0.7455 | 2.8539 | -1.3539 | 12.3257 | 5.1712 | 0.6259 | 0.6647 | 0.969 | 0.7545 | -128.9616 | 2.2299 | 5.7351 | 2.0003 | -2.7752 | -0.975 | 4.7814 |  | 4.3463 | 0.8094 | 4.0045 | 3.367 | 3.331 | 1.0964 | 10.7938 | 14.2788 | 14.8532 | 11.1002 | 0 | -0.0024 | 0.0011 | 0.0039 | 0.001 | -0.0002 | 0.0246 | -0.009 | -0.0114 | -360.1373 | 17.3823 | -360.4296 | 17.6163 | -360.7743 | 18.2097 | -360.8081 | 17.5383 | -352.5798 | 18.7004 | -352.6198 | 16.8361
13:01 | 6079 | 50.8393 | 203.1341 | 449.425 | 452.7815 | -16.9993 | -38.4258 | 11.9621 | 8.1265 | 2.6942 | 0.7228 | 2.7844 | -1.3583 | 12.2687 | 5.2119 | 0.6256 | 0.6637 | 0.971 | 0.7553 | -129.0785 | 2.281 | 5.6528 | 1.9835 | -2.7869 | -0.8347 | 4.7204 |  | 4.295 | 0.8098 | 4.0051 | 3.3704 | 3.3315 | 1.0975 | 10.7614 | 14.252 | 14.8133 | 11.0569 | -0.0002 | -0.0026 | 0.0007 | 0.0034 | 0.0006 | -0.0007 | 0.0154 | -0.0005 | 0.0148 | -360.1465 | 17.3925 | -360.4266 | 17.6061 | -360.7835 | 18.2077 | -360.7835 | 17.5465 | -352.5767 | 18.6984 | -352.5983 | 16.8217
13:01 | 6080 | 50.9014 | 203.1534 | 449.4212 | 452.8504 | -16.9929 | -38.5283 | 11.9683 | 8.1792 | 2.7536 | 0.7365 | 2.8446 | -1.2907 | 12.315 | 5.1567 | 0.626 | 0.662 | 0.968 | 0.7552 | -129.0467 | 2.3908 | 5.6725 | 2.0198 | -2.8106 | -0.8841 | 4.7626 |  | 4.3039 | 0.8131 | 4.0037 | 3.367 | 3.3333 | 1.0968 | 10.7707 | 14.2612 | 14.828 | 11.0605 | 0.0001 | -0.0029 | 0.0005 | 0.0037 | 0.0009 | -0.0006 | 0.0007 | -0.0094 | -0.0003 | -360.1404 | 17.3946 | -360.4081 | 17.6102 | -360.7804 | 18.2036 | -360.805 | 17.5383 | -352.549 | 18.6963 | -352.5798 | 16.8258
13:01 | 6081 | 50.9421 | 203.1471 | 449.5019 | 452.926 | -16.9757 | -38.5839 | 12.0076 | 8.135 | 2.7417 | 0.7135 | 2.8227 | -1.2832 | 12.4031 | 5.193 | 0.6265 | 0.665 | 0.9696 | 0.7541 | -129.0605 | 2.3797 | 5.6619 | 1.9844 | -2.8912 | -0.9772 | 4.7473 |  | 4.2789 | 0.9434 | 4.0037 | 3.3688 | 3.3315 | 1.0971 | 10.8041 | 14.2836 | 14.8587 | 11.1045 | 0.0005 | -0.0025 | 0.0008 | 0.0043 | 0.0005 | -0.0006 | 0.011 | 0.0064 | 0.0003 | -360.1865 | 17.3925 | -360.4081 | 17.6102 | -360.7681 | 18.2056 | -360.7958 | 17.5363 | -352.5798 | 18.7004 | -352.5983 | 16.834
13:01 | 6082 | 50.8482 | 203.1468 | 449.4344 | 452.9009 | -16.9483 | -38.6782 | 11.9503 | 8.1308 | 2.8025 | 0.7469 | 2.8313 | -1.3119 | 12.2722 | 5.2132 | 0.627 | 0.6637 | 0.9721 | 0.7555 | -129.0624 | 2.3663 | 5.6176 | 1.9486 | -2.7863 | -1.0218 | 4.8156 |  | 4.3307 | 0.9101 | 4.0046 | 3.3649 | 3.3313 | 1.0955 | 10.81 | 14.2776 | 14.8519 | 11.0991 | -0.0003 | -0.0032 | 0.0009 | 0.0039 | 0.0011 | -0.0004 | -0.0009 | -0.0174 | -0.0323 | -360.1465 | 17.3884 | -360.4235 | 17.6122 | -360.7743 | 18.2118 | -360.7989 | 17.5363 | -352.589 | 18.7087 | -352.6136 | 16.8361
13:01 | 6083 | 50.7707 | 203.1581 | 449.5859 | 452.8291 | -16.9387 | -38.6152 | 11.9317 | 8.1348 | 2.7522 | 0.671 | 2.8902 | -1.3185 | 12.2168 | 5.1816 | 0.6272 | 0.6639 | 0.9695 | 0.7549 | -129.0927 | 2.4118 | 5.6776 | 1.8995 | -2.819 | -1.0732 | 4.6771 |  | 4.3242 | 0.8451 | 4.0045 | 3.3639 | 3.3291 | 1.0951 | 10.7613 | 14.2696 | 14.8386 | 11.1082 | -0.0001 | -0.0023 | 0.0012 | 0.0043 | 0.0007 | -0.0002 | 0.0158 | 0.0106 | -0.003 | -360.1835 | 17.3925 | -360.4296 | 17.6225 | -360.7897 | 18.2159 | -360.8204 | 17.5486 | -352.5952 | 18.7045 | -352.626 | 16.8464
13:01 | 6084 | 50.8778 | 203.1515 | 449.5404 | 452.8603 | -16.9741 | -38.6285 | 11.9202 | 8.2709 | 2.6925 | 0.7131 | 2.9289 | -1.3107 | 12.1495 | 5.2552 | 0.6271 | 0.6656 | 0.9661 | 0.7539 | -128.9983 | 2.3621 | 5.669 | 2.0343 | -2.7104 | -1.0446 | 4.6989 |  | 4.2979 | 0.8756 | 4.0037 | 3.3631 | 3.3272 | 1.0947 | 10.7938 | 14.2904 | 14.8706 | 11.1118 | -0.0001 | -0.0029 | 0.0007 | 0.0039 | 0.0011 | -0.0005 | 0.0021 | -0.0023 | -0.0152 | -360.165 | 17.4007 | -360.4389 | 17.6143 | -360.805 | 18.2179 | -360.8327 | 17.5547 | -352.6106 | 18.7128 | -352.626 | 16.8505
13:01 | 6085 | 50.8832 | 203.1627 | 449.4638 | 452.8796 | -16.9229 | -38.5241 | 11.9184 | 8.3071 | 2.6933 | 0.6163 | 2.9606 | -1.311 | 12.2616 | 5.2316 | 0.6262 | 0.6642 | 0.9679 | 0.7553 | -129.0492 | 2.4344 | 5.6429 | 2.0109 | -2.6952 | -0.9713 | 4.7506 |  | 4.2916 | 0.8962 | 4.0051 | 3.3651 | 3.3302 | 1.0965 | 10.7915 | 14.2764 | 14.8447 | 11.0923 | 0.0002 | -0.003 | 0.0008 | 0.0035 | 0.0005 | 0 | 0.0137 | 0.0011 | -0.0222 | -360.1804 | 17.4131 | -360.4358 | 17.6348 | -360.8174 | 18.22 | -360.845 | 17.5629 | -352.6383 | 18.723 | -352.6413 | 16.8484
13:01 | 6086 | 50.836 | 203.1427 | 449.4425 | 452.8173 | -17.0136 | -38.4662 | 11.8863 | 8.2099 | 2.7171 | 0.5548 | 2.8705 | -1.3613 | 12.1774 | 5.1296 | 0.6264 | 0.6633 | 0.9678 | 0.7558 | -129.059 | 2.3492 | 5.6224 | 1.9137 | -2.7069 | -1.0673 | 4.685 |  | 4.294 | 0.8949 | 4.0033 | 3.3649 | 3.3313 | 1.097 | 10.7914 | 14.2766 | 14.8863 | 11.115 | 0.0005 | -0.0025 | 0.0011 | 0.0038 | 0.001 | -0.001 | 0.0039 | -0.0044 | -0.0114 | -360.2081 | 17.4233 | -360.4758 | 17.641 | -360.8266 | 18.2385 | -360.8881 | 17.5588 | -352.626 | 18.7374 | -352.6598 | 16.8546
13:01 | 6087 | 50.869 | 203.1675 | 449.4371 | 452.8845 | -16.8732 | -38.3742 | 11.9465 | 8.2987 | 2.794 | 0.6692 | 2.8964 | -1.3661 | 12.1964 | 5.2177 | 0.6272 | 0.6661 | 0.9654 | 0.7551 | -129.0632 | 2.4395 | 5.6865 | 2.0317 | -2.6929 | -1.1505 | 4.7113 |  | 4.2744 | 0.7873 | 4.0049 | 3.3659 | 3.3309 | 1.098 | 10.7788 | 14.2923 | 14.847 | 11.0862 | -0.0004 | -0.0029 | 0.0007 | 0.0037 | 0.0005 | -0.0001 | 0.0048 | -0.0113 | -0.0257 | -360.1742 | 17.411 | -360.4912 | 17.641 | -360.8112 | 18.2323 | -360.8543 | 17.5629 | -352.6506 | 18.7312 | -352.6229 | 16.8546
13:01 | 6088 | 50.873 | 203.1174 | 449.5468 | 452.857 | -16.9575 | -38.5887 | 11.8322 | 8.2199 | 2.7142 | 0.6248 | 2.8716 | -1.3975 | 12.1537 | 5.2169 | 0.6269 | 0.6666 | 0.9682 | 0.7552 | -129.106 | 2.2575 | 5.5604 | 2.1165 | -2.6395 | -0.9709 | 4.6987 |  | 4.3372 | 0.8452 | 4.0055 | 3.3671 | 3.3298 | 1.0969 | 10.7834 | 14.2625 | 14.8478 | 11.0786 | -0.0001 | -0.0027 | 0.0006 | 0.0042 | 0.0008 | -0.0008 | 0.0001 | -0.0136 | -0.0035 | -360.2204 | 17.4172 | -360.485 | 17.6471 | -360.8389 | 18.2323 | -360.8481 | 17.5568 | -352.6229 | 18.7333 | -352.6475 | 16.8546
13:01 | 6089 | 50.8966 | 203.2239 | 449.5658 | 452.915 | -16.9412 | -38.4209 | 11.9806 | 8.2288 | 2.7002 | 0.5386 | 2.9025 | -1.3399 | 12.2279 | 5.1859 | 0.6259 | 0.6674 | 0.9667 | 0.7542 | -129.1152 | 2.3633 | 5.6112 | 2.0488 | -2.5792 | -0.9303 | 4.737 |  | 4.2644 | 0.7676 | 4.0047 | 3.3649 | 3.3292 | 1.0987 | 10.7961 | 14.2695 | 14.8781 | 11.097 | 0.0002 | -0.0031 | 0.0013 | 0.0043 | 0.001 | -0.0001 | 0.0052 | -0.0229 | -0.0196 | -360.1927 | 17.409 | -360.4358 | 17.6081 | -360.7989 | 18.2282 | -360.8266 | 17.5506 | -352.6106 | 18.7189 | -352.6229 | 16.8258
13:01 | 6090 | 50.952 | 203.2435 | 449.5043 | 452.9959 | -16.8778 | -38.4232 | 11.977 | 8.3023 | 2.75 | 0.6112 | 2.9729 | -1.3502 | 12.2488 | 5.2405 | 0.6269 | 0.6663 | 0.9715 | 0.7546 | -129.0939 | 2.265 | 5.5557 | 2.0671 | -2.5708 | -0.9809 | 4.6957 |  | 4.2897 | 0.7697 | 4.004 | 3.3667 | 3.3311 | 1.0974 | 10.8018 | 14.2754 | 14.827 | 11.0966 | -0.0001 | -0.0031 | 0.0012 | 0.004 | 0.0013 | -0.0003 | 0.0026 | 0.0003 | -0.013 | -360.1681 | 17.4069 | -360.4419 | 17.6102 | -360.8204 | 18.1994 | -360.7897 | 17.5383 | -352.5552 | 18.7087 | -352.629 | 16.832
13:01 | 6091 | 50.9498 | 203.2548 | 449.5246 | 452.9717 | -16.7766 | -38.393 | 12.004 | 8.2276 | 2.7452 | 0.6383 | 2.9827 | -1.3122 | 12.2445 | 5.2154 | 0.6266 | 0.6653 | 0.968 | 0.7553 | -129.116 | 2.3073 | 5.5303 | 2.0241 | -2.5695 | -0.9394 | 4.811 |  | 4.3651 | 0.8283 | 4.0033 | 3.3631 | 3.3327 | 1.0966 | 10.7765 | 14.2844 | 14.8406 | 11.1006 | -0.0006 | -0.0026 | 0.0012 | 0.0043 | 0.0005 | -0.0004 | 0.0256 | -0.0084 | 0.003 | -360.1681 | 17.3905 | -360.4142 | 17.602 | -360.7958 | 18.2179 | -360.802 | 17.5383 | -352.5798 | 18.6984 | -352.5736 | 16.8238
13:01 | 6092 | 50.935 | 203.201 | 449.5472 | 452.979 | -16.6792 | -38.2559 | 12.077 | 8.2157 | 2.8419 | 0.7159 | 3.0409 | -1.3602 | 12.2026 | 5.1479 | 0.6261 | 0.6671 | 0.9695 | 0.7547 | -129.0937 | 2.224 | 5.6327 | 1.9071 | -2.5948 | -0.9628 | 4.822 |  | 4.3391 | 0.7989 | 4.0033 | 3.3657 | 3.3311 | 1.0968 | 10.7787 | 14.2926 | 14.8433 | 11.1085 | -0.0004 | -0.0028 | 0.0006 | 0.0037 | 0.001 | 0 | 0.0161 | 0.0023 | -0.0101 | -360.1219 | 17.3884 | -360.4142 | 17.604 | -360.7835 | 18.1851 | -360.765 | 17.5342 | -352.5983 | 18.7004 | -352.5767 | 16.8361
13:01 | 6093 | 50.9185 | 203.2646 | 449.5465 | 453.0154 | -16.7611 | -38.3434 | 12.1356 | 8.2001 | 2.7444 | 0.692 | 2.9808 | -1.4145 | 12.1658 | 5.1824 | 0.6276 | 0.6648 | 0.9729 | 0.7555 | -129.1565 | 2.2586 | 5.4947 | 1.9281 | -2.6901 | -0.9871 | 4.7503 |  | 4.3081 | 0.6431 | 4.0032 | 3.3656 | 3.3302 | 1.0978 | 10.811 | 14.2907 | 14.8612 | 11.0995 | 0.0004 | -0.0029 | 0.0007 | 0.0034 | 0.0007 | -0.0004 | 0.0146 | -0.0021 | -0.0074 | -360.1219 | 17.3761 | -360.4296 | 17.6286 | -360.805 | 18.2097 | -360.8174 | 17.5383 | -352.5706 | 18.7025 | -352.6106 | 16.8464
13:01 | 6094 | 50.8472 | 203.2157 | 449.4156 | 452.8825 | -16.7531 | -38.3817 | 12.1096 | 8.2133 | 2.7474 | 0.6921 | 2.9963 | -1.3638 | 12.2195 | 5.2476 | 0.6269 | 0.662 | 0.9664 | 0.7568 | -129.1456 | 2.3708 | 5.636 | 1.9566 | -2.6572 | -0.9193 | 4.7277 |  | 4.299 | 0.8442 | 4.0035 | 3.3662 | 3.3305 | 1.0977 | 10.7776 | 14.2913 | 14.8351 | 11.1078 | 0.0001 | -0.0032 | 0.0006 | 0.004 | 0.0004 | -0.0003 | 0.0139 | -0.0117 | -0.016 | -360.1742 | 17.411 | -360.4235 | 17.6061 | -360.7712 | 18.2179 | -360.7866 | 17.5588 | -352.6567 | 18.723 | -352.6413 | 16.8197
13:01 | 6095 | 50.9345 | 203.2256 | 449.6261 | 452.979 | -16.8146 | -38.4769 | 12.0783 | 8.1759 | 2.82 | 0.7576 | 3.0267 | -1.3165 | 12.2001 | 5.2198 | 0.6276 | 0.6714 | 0.9694 | 0.7559 | -129.1048 | 2.3719 | 5.6832 | 1.9968 | -2.6191 | -0.9852 | 4.8113 |  | 4.3287 | 0.8796 | 4.0028 | 3.3654 | 3.3302 | 1.0969 | 10.7995 | 14.2963 | 14.8717 | 11.1114 | -0.0003 | -0.0027 | 0.0007 | 0.0038 | 0.0007 | -0.0005 | -0.0033 | -0.0081 | -0.019 | -360.1188 | 17.4028 | -360.445 | 17.6533 | -360.8204 | 18.2159 | -360.8081 | 17.5363 | -352.5952 | 18.723 | -352.6813 | 16.8505
13:01 | 6096 | 50.8745 | 203.1644 | 449.5185 | 452.9365 | -16.8907 | -38.5353 | 12.028 | 8.2036 | 2.7835 | 0.7377 | 3.0551 | -1.3237 | 12.2499 | 5.2025 | 0.6264 | 0.669 | 0.9681 | 0.7549 | -129.0973 | 2.398 | 5.6197 | 1.9321 | -2.6136 | -0.9408 | 4.8452 |  | 4.3363 | 0.8218 | 4.0022 | 3.3658 | 3.3326 | 1.0966 | 10.7683 | 14.288 | 14.8447 | 11.1327 | -0.0002 | -0.003 | 0.0007 | 0.0041 | 0.0005 | -0.0005 | 0.0064 | -0.0006 | -0.0086 | -360.1342 | 17.3987 | -360.4481 | 17.6471 | -360.8204 | 18.2508 | -360.8943 | 17.5671 | -352.6167 | 18.7128 | -352.6136 | 16.8525
13:01 | 6097 | 50.8492 | 203.1759 | 449.5527 | 452.9842 | -16.9239 | -38.4656 | 12.0963 | 8.1928 | 2.8365 | 0.8754 | 3.116 | -1.2713 | 12.1779 | 5.1651 | 0.6268 | 0.6699 | 0.9714 | 0.7537 | -129.0924 | 2.4081 | 5.6015 | 1.9926 | -2.5075 | -0.8806 | 4.8486 |  | 4.3039 | 0.8981 | 4.0039 | 3.3673 | 3.3306 | 1.0978 | 10.7845 | 14.3043 | 14.8849 | 11.1024 | 0.0001 | -0.0029 | 0.001 | 0.0042 | 0.0013 | -0.0008 | 0.0254 | -0.0096 | -0.0123 | -360.2296 | 17.4356 | -360.4727 | 17.6553 | -360.805 | 18.2159 | -360.8297 | 17.5712 | -352.6537 | 18.7477 | -352.6813 | 16.8484
13:01 | 6098 | 50.935 | 203.1808 | 449.4985 | 452.9447 | -16.7423 | -38.3052 | 12.1519 | 8.1817 | 2.7266 | 0.8796 | 3.048 | -1.2956 | 12.1111 | 5.2077 | 0.6263 | 0.6666 | 0.971 | 0.7535 | -129.088 | 2.4211 | 5.6301 | 1.9351 | -2.497 | -0.977 | 4.8142 |  | 4.3292 | 0.8749 | 4.0042 | 3.367 | 3.3339 | 1.0986 | 10.8052 | 14.2793 | 14.8217 | 11.0818 | 0.0003 | -0.0026 | 0.0013 | 0.0043 | 0.0008 | -0.0001 | 0.0053 | -0.0086 | -0.0213 | -360.1527 | 17.4048 | -360.4789 | 17.6759 | -360.8574 | 18.2405 | -360.885 | 17.5445 | -352.5952 | 18.7333 | -352.6444 | 16.8689
13:01 | 6099 | 51.0061 | 203.1122 | 449.6354 | 452.9689 | -16.7631 | -38.3402 | 12.0949 | 8.221 | 2.771 | 1.0546 | 3.0056 | -1.198 | 12.2134 | 5.2392 | 0.6272 | 0.6667 | 0.9678 | 0.755 | -129.1135 | 2.3353 | 5.6466 | 1.9113 | -2.5321 | -0.9341 | 4.803 |  | 4.2279 | 0.8558 | 4.0031 | 3.3658 | 3.3297 | 1.0987 | 10.7869 | 14.2659 | 14.8855 | 11.1226 | -0.0001 | -0.0026 | 0.0003 | 0.0036 | 0.0012 | -0.0006 | 0.0188 | -0.0119 | -0.0124 | -360.1988 | 17.4069 | -360.4327 | 17.6553 | -360.802 | 18.2446 | -360.8943 | 17.5835 | -352.6721 | 18.7292 | -352.6321 | 16.8381
13:01 | 6100 | 50.9979 | 203.1036 | 449.6226 | 453.01 | -16.7291 | -38.3622 | 12.1834 | 8.1673 | 2.7212 | 1.0045 | 3.0867 | -1.1774 | 12.2181 | 5.1737 | 0.6276 | 0.6681 | 0.966 | 0.7556 | -129.1007 | 2.3544 | 5.6393 | 1.7871 | -2.5566 | -1.0081 | 4.843 |  | 4.2779 | 0.7777 | 4.0032 | 3.3636 | 3.3287 | 1.0983 | 10.8133 | 14.2815 | 14.8755 | 11.1305 | 0 | -0.0027 | 0.0013 | 0.004 | 0.0011 | 0.0004 | 0.0146 | -0.015 | -0.017 | -360.1896 | 17.4254 | -360.5004 | 17.68 | -360.8481 | 18.2015 | -360.8081 | 17.5486 | -352.6475 | 18.7415 | -352.6721 | 16.8628
13:01 | 6101 | 51.0396 | 203.1593 | 449.5514 | 453.0235 | -16.7136 | -38.3272 | 12.2016 | 8.2529 | 2.774 | 1.072 | 3.1002 | -1.233 | 12.2329 | 5.101 | 0.6274 | 0.6685 | 0.9701 | 0.7558 | -129.1382 | 2.4369 | 5.6337 | 1.7975 | -2.5782 | -0.9204 | 4.7823 |  | 4.282 | 0.7295 | 4.0033 | 3.3634 | 3.3354 | 1.098 | 10.8007 | 14.303 | 14.8362 | 11.119 | 0.0001 | -0.0031 | 0.0007 | 0.0033 | 0.0008 | -0.0008 | -0.0073 | 0.0026 | 0.0174 | -360.165 | 17.3884 | -360.4142 | 17.6615 | -360.8574 | 18.2467 | -360.8635 | 17.5691 | -352.6106 | 18.7004 | -352.5952 | 16.8381
13:01 | 6102 | 50.8527 | 203.1306 | 449.5015 | 453.0698 | -16.7519 | -38.3604 | 12.187 | 8.1971 | 2.7802 | 0.919 | 3.0274 | -1.3265 | 12.2483 | 5.0783 | 0.6263 | 0.666 | 0.9696 | 0.7551 | -129.191 | 2.2542 | 5.4844 | 1.8407 | -2.5217 | -0.9091 | 4.7526 |  | 4.3597 | 0.8724 | 4.0047 | 3.3665 | 3.3325 | 1.0986 | 10.7984 | 14.2775 | 14.8624 | 11.1053 | 0.0002 | -0.003 | 0.0006 | 0.0042 | 0.0006 | 0 | 0.0003 | 0.0021 | 0.0015 | -360.2173 | 17.4397 | -360.485 | 17.6512 | -360.7927 | 18.1994 | -360.8235 | 17.5629 | -352.629 | 18.7497 | -352.6475 | 16.832
13:01 | 6103 | 50.8722 | 203.1486 | 449.579 | 453.0998 | -16.7145 | -38.4287 | 12.1931 | 8.2439 | 2.7427 | 1.0147 | 2.9902 | -1.2227 | 12.249 | 5.2378 | 0.6272 | 0.666 | 0.968 | 0.7529 | -129.2027 | 2.4027 | 5.4981 | 1.9384 | -2.597 | -0.9395 | 4.7763 |  | 4.3097 | 0.8821 | 4.0042 | 3.3689 | 3.3297 | 1.0968 | 10.7845 | 14.2523 | 14.8155 | 11.1024 | 0.0001 | -0.0027 | 0.0012 | 0.004 | 0.0007 | -0.0006 | 0.0232 | -0.0059 | -0.0023 | -360.1127 | 17.4007 | -360.4573 | 17.6677 | -360.8574 | 18.2118 | -360.8235 | 17.5301 | -352.5521 | 18.7004 | -352.6475 | 16.8505
13:01 | 6104 | 50.9319 | 203.1068 | 449.6005 | 453.0271 | -16.7336 | -38.3952 | 12.2713 | 8.2965 | 2.789 | 1.044 | 3.0671 | -1.271 | 12.3177 | 5.2216 | 0.6275 | 0.6659 | 0.9706 | 0.7527 | -129.1428 | 2.375 | 5.6764 | 1.8566 | -2.6647 | -0.9248 | 4.6669 |  | 4.2514 | 0.818 | 4.0035 | 3.3689 | 3.3286 | 1.097 | 10.7858 | 14.253 | 14.831 | 11.093 | -0.0001 | -0.0025 | 0.0005 | 0.0039 | 0.0009 | -0.0005 | 0.0044 | -0.0141 | -0.0026 | -360.1896 | 17.3905 | -360.3958 | 17.604 | -360.762 | 18.2118 | -360.8512 | 17.5773 | -352.6383 | 18.7004 | -352.5644 | 16.8032
13:01 | 6105 | 50.9472 | 203.129 | 449.5264 | 453.0682 | -16.6082 | -38.1928 | 12.1904 | 8.3411 | 2.6669 | 1.0509 | 2.9881 | -1.3423 | 12.2986 | 5.2001 | 0.6252 | 0.6669 | 0.9692 | 0.7523 | -129.1258 | 2.4197 | 5.6847 | 1.7664 | -2.663 | -0.9733 | 4.7268 |  | 4.2928 | 0.8297 | 4.0036 | 3.3676 | 3.3278 | 1.0977 | 10.7984 | 14.2892 | 14.8634 | 11.1049 | 0.0004 | -0.003 | 0.0009 | 0.004 | 0.0006 | -0.0005 | 0.0054 | 0.0017 | -0.0153 | -360.1558 | 17.4172 | -360.4881 | 17.6697 | -360.7897 | 18.1748 | -360.7404 | 17.5178 | -352.5798 | 18.723 | -352.6383 | 16.8402
13:01 | 6106 | 50.9504 | 203.0822 | 449.6609 | 453.0366 | -16.6271 | -38.2625 | 12.0788 | 8.2587 | 2.7002 | 0.9414 | 3.0479 | -1.2677 | 12.2553 | 5.1471 | 0.6264 | 0.6696 | 0.9705 | 0.7543 | -129.1438 | 2.3879 | 5.7117 | 1.7805 | -2.6988 | -0.9898 | 4.7158 |  | 4.2721 | 0.7624 | 4.0034 | 3.367 | 3.3274 | 1.0964 | 10.8041 | 14.2953 | 14.8829 | 11.0984 | 0.0002 | -0.003 | 0.001 | 0.0034 | 0.0009 | -0.0008 | 0.0027 | -0.0086 | -0.006 | -360.1127 | 17.374 | -360.3958 | 17.641 | -360.8174 | 18.2179 | -360.8389 | 17.5506 | -352.549 | 18.6861 | -352.5552 | 16.8176
13:01 | 6107 | 50.9432 | 203.0386 | 449.5912 | 453.004 | -16.6168 | -38.1497 | 12.0677 | 8.2621 | 2.6879 | 0.8486 | 3.0482 | -1.2167 | 12.2987 | 5.3342 | 0.6272 | 0.6668 | 0.9671 | 0.7534 | -129.1138 | 2.4218 | 5.7683 | 1.72 | -2.7149 | -1.0125 | 4.7364 |  | 4.2373 | 0.8264 | 4.003 | 3.3679 | 3.3302 | 1.0974 | 10.8007 | 14.2856 | 14.8593 | 11.119 | -0.0001 | -0.0023 | 0.0006 | 0.0039 | 0.0008 | -0.0002 | 0.0171 | 0.0039 | 0 | -360.1773 | 17.4213 | -360.4389 | 17.6143 | -360.765 | 18.1645 | -360.7743 | 17.5568 | -352.6136 | 18.7292 | -352.6013 | 16.8115
13:02 | 6108 | 50.9528 | 203.0502 | 449.6248 | 453.0952 | -16.6885 | -38.1485 | 12.1581 | 8.2603 | 2.7183 | 0.9097 | 3.0152 | -1.2159 | 12.2895 | 5.2997 | 0.6265 | 0.6669 | 0.9692 | 0.7547 | -129.1896 | 2.423 | 5.7912 | 1.6626 | -2.6926 | -1.0302 | 4.6992 |  | 4.3469 | 0.8638 | 4.0036 | 3.3661 | 3.3306 | 1.0973 | 10.811 | 14.2907 | 14.867 | 11.1226 | -0.0003 | -0.0026 | 0.0012 | 0.0041 | 0.0011 | -0.0003 | 0.0138 | 0.0024 | -0.0206 | -360.0881 | 17.3843 | -360.4204 | 17.6574 | -360.8389 | 18.1974 | -360.7681 | 17.528 | -352.5183 | 18.6984 | -352.6229 | 16.8505
13:02 | 6109 | 51.0245 | 203.0662 | 449.6381 | 453.0825 | -16.7196 | -38.2301 | 12.0637 | 8.335 | 2.798 | 0.9857 | 3.0393 | -1.1874 | 12.2374 | 5.1966 | 0.6281 | 0.6661 | 0.9659 | 0.7532 | -129.1705 | 2.3896 | 5.7217 | 1.8139 | -2.6377 | -0.9744 | 4.764 |  | 4.2549 | 0.826 | 4.0042 | 3.368 | 3.3291 | 1.0981 | 10.8053 | 14.3019 | 14.8938 | 11.1118 | -0.0002 | -0.003 | 0.0008 | 0.0039 | 0.0007 | -0.0004 | 0.0194 | -0.0043 | 0.0105 | -360.1773 | 17.3761 | -360.365 | 17.5978 | -360.7343 | 18.2056 | -360.8543 | 17.5712 | -352.6167 | 18.7025 | -352.549 | 16.7909
13:02 | 6110 | 51.0153 | 203.013 | 449.6926 | 453.1123 | -16.7209 | -38.3309 | 12.1017 | 8.2525 | 2.7282 | 0.8299 | 2.9699 | -1.1905 | 12.3023 | 5.2307 | 0.6277 | 0.6673 | 0.9678 | 0.7556 | -129.241 | 2.3652 | 5.6061 | 1.7954 | -2.6947 | -0.9555 | 4.7496 |  | 4.2793 | 0.8156 | 4.003 | 3.365 | 3.3308 | 1.0986 | 10.796 | 14.3162 | 14.8407 | 11.1247 | 0.0004 | -0.0029 | 0.0011 | 0.0045 | 0.0012 | -0.0004 | -0.006 | -0.009 | -0.0049 | -360.1619 | 17.4048 | -360.4573 | 17.643 | -360.7589 | 18.1707 | -360.7743 | 17.5301 | -352.5983 | 18.723 | -352.6752 | 16.8361
13:02 | 6111 | 51.0009 | 203.1067 | 449.6564 | 453.0744 | -16.7443 | -38.3231 | 12.0292 | 8.2023 | 2.7384 | 0.7274 | 2.9554 | -1.2454 | 12.3063 | 5.1884 | 0.6267 | 0.665 | 0.969 | 0.7546 | -129.2159 | 2.4232 | 5.6558 | 1.9184 | -2.5078 | -0.9096 | 4.7133 |  | 4.2611 | 0.7626 | 4.0028 | 3.3658 | 3.3304 | 1.098 | 10.7637 | 14.2775 | 14.8682 | 11.1168 | -0.0002 | -0.0028 | 0.001 | 0.0041 | 0.0004 | -0.0006 | 0.0263 | -0.008 | -0.0113 | -360.1219 | 17.3679 | -360.3835 | 17.643 | -360.8266 | 18.2241 | -360.842 | 17.5527 | -352.5767 | 18.6861 | -352.6167 | 16.8402
13:02 | 6112 | 50.9231 | 203.0825 | 449.6454 | 453.0116 | -16.773 | -38.2568 | 12.088 | 8.1965 | 2.7561 | 0.6982 | 2.997 | -1.1919 | 12.356 | 5.1398 | 0.6274 | 0.666 | 0.9686 | 0.7548 | -129.1389 | 2.4484 | 5.6741 | 1.9562 | -2.5789 | -0.8976 | 4.7487 |  | 4.3719 | 0.809 | 4.0041 | 3.3664 | 3.3286 | 1.0978 | 10.7833 | 14.2974 | 14.843 | 11.1071 | -0.0005 | -0.0027 | 0.0006 | 0.0041 | 0.0012 | -0.0005 | 0.0209 | -0.0092 | -0.0076 | -360.1835 | 17.4048 | -360.4142 | 17.6163 | -360.722 | 18.1871 | -360.802 | 17.5691 | -352.6506 | 18.723 | -352.6013 | 16.8156
13:02 | 6113 | 51.0061 | 203.1202 | 449.6252 | 453.0582 | -16.8329 | -38.3377 | 11.9092 | 8.1595 | 2.7976 | 0.8754 | 3.022 | -1.2023 | 12.3111 | 5.0691 | 0.6264 | 0.6647 | 0.9696 | 0.7545 | -129.1175 | 2.4177 | 5.5996 | 1.9953 | -2.5564 | -0.9275 | 4.6982 |  | 4.4616 | 0.8373 | 4.0023 | 3.3635 | 3.3298 | 1.0991 | 10.7591 | 14.2555 | 14.829 | 11.0775 | 0.0002 | -0.0033 | 0.0012 | 0.0044 | 0.0009 | -0.0002 | 0.0108 | 0.0065 | 0.0063 | -360.1219 | 17.3946 | -360.4573 | 17.6677 | -360.8297 | 18.2077 | -360.805 | 17.5363 | -352.5983 | 18.7128 | -352.6844 | 16.8628
13:02 | 6114 | 50.9681 | 203.0439 | 449.5638 | 453.0059 | -16.8253 | -38.3429 | 11.9087 | 8.2073 | 2.7527 | 0.818 | 3.0536 | -1.2273 | 12.3043 | 5.1188 | 0.6257 | 0.668 | 0.9674 | 0.7534 | -129.1581 | 2.4242 | 5.5116 | 2.0204 | -2.618 | -0.9486 | 4.7201 |  | 4.4329 | 0.8828 | 4.0034 | 3.3654 | 3.3296 | 1.0975 | 10.7973 | 14.2532 | 14.8436 | 11.11 | 0.0004 | -0.0029 | 0.001 | 0.0039 | 0.001 | -0.0007 | 0.0278 | -0.0167 | -0.0043 | -360.1558 | 17.3946 | -360.4081 | 17.641 | -360.805 | 18.2241 | -360.8635 | 17.5917 | -352.6567 | 18.7107 | -352.6167 | 16.832
13:02 | 6115 | 51.027 | 203.0776 | 449.6213 | 452.9876 | -16.8084 | -38.5053 | 11.9366 | 8.2219 | 2.7007 | 0.7419 | 2.988 | -1.189 | 12.3438 | 5.1708 | 0.6264 | 0.6638 | 0.9664 | 0.7534 | -129.0777 | 2.3347 | 5.5702 | 1.9546 | -2.5921 | -0.8912 | 4.7153 |  | 4.4013 | 0.7959 | 4.0037 | 3.3618 | 3.3306 | 1.0992 | 10.8018 | 14.2812 | 14.8676 | 11.1082 | -0.0002 | -0.0028 | 0.0007 | 0.0035 | 0.0013 | -0.0001 | 0.0176 | -0.0088 | 0.0018 | -360.2142 | 17.4295 | -360.4819 | 17.6656 | -360.8235 | 18.1994 | -360.8266 | 17.5732 | -352.6321 | 18.7395 | -352.6475 | 16.8546
13:02 | 6116 | 50.9334 | 203.0577 | 449.643 | 452.9276 | -16.7689 | -38.5045 | 11.8849 | 8.1798 | 2.6903 | 0.79 | 2.9793 | -1.3057 | 12.2963 | 5.1197 | 0.6269 | 0.668 | 0.9703 | 0.7559 | -129.1094 | 2.3477 | 5.6279 | 1.8443 | -2.617 | -0.8862 | 4.7977 |  | 4.3984 | 0.8272 | 4.0047 | 3.3642 | 3.3279 | 1.0981 | 10.8249 | 14.316 | 14.8686 | 11.1367 | -0.0004 | -0.0027 | 0.0008 | 0.0037 | 0.0005 | -0.0005 | 0.0214 | -0.009 | -0.0044 | -360.1711 | 17.4172 | -360.4789 | 17.6636 | -360.8604 | 18.2385 | -360.8143 | 17.5732 | -352.6321 | 18.7251 | -352.6629 | 16.8607
13:02 | 6117 | 50.9917 | 203.0517 | 449.6249 | 453.0027 | -16.8406 | -38.5395 | 11.954 | 8.2039 | 2.5948 | 0.8142 | 2.9985 | -1.2688 | 12.2137 | 5.1705 | 0.6268 | 0.6693 | 0.9695 | 0.755 | -129.0814 | 2.314 | 5.7172 | 1.8683 | -2.7057 | -0.9855 | 4.835 |  | 4.3323 | 0.7693 | 4.0027 | 3.3661 | 3.3335 | 1.0985 | 10.7938 | 14.2557 | 14.8301 | 11.1118 | 0.0003 | -0.0028 | 0.0011 | 0.004 | 0.0006 | -0.0002 | 0.0082 | 0.0035 | -0.009 | -360.2173 | 17.4295 | -360.4512 | 17.6533 | -360.8143 | 18.2138 | -360.8174 | 17.5794 | -352.6383 | 18.723 | -352.6598 | 16.8423
13:02 | 6118 | 50.9285 | 203.1028 | 449.6059 | 452.9666 | -16.8107 | -38.4992 | 11.9639 | 8.1458 | 2.5849 | 0.7837 | 2.9852 | -1.3205 | 12.3024 | 5.2988 | 0.6264 | 0.6653 | 0.9696 | 0.756 | -129.067 | 2.4038 | 5.6865 | 1.852 | -2.6606 | -0.844 | 4.7913 |  | 4.3899 | 0.7416 | 4.0045 | 3.3647 | 3.3326 | 1.0986 | 10.8134 | 14.2929 | 14.8744 | 11.102 | 0.0002 | -0.0031 | 0.001 | 0.0041 | 0.0008 | -0.0001 | 0.0164 | 0.0023 | -0.0118 | -360.2142 | 17.4213 | -360.4819 | 17.682 | -360.8543 | 18.2179 | -360.8697 | 17.5773 | -352.5921 | 18.7292 | -352.6721 | 16.8423
13:02 | 6119 | 51.0207 | 203.0942 | 449.7102 | 453.0172 | -16.8272 | -38.524 | 11.9538 | 8.1943 | 2.7068 | 0.8232 | 2.9882 | -1.2941 | 12.1645 | 5.241 | 0.6278 | 0.6677 | 0.9715 | 0.7554 | -129.0938 | 2.3102 | 5.7087 | 1.987 | -2.7049 | -0.9436 | 4.7734 |  | 4.314 | 0.6503 | 4.0032 | 3.364 | 3.3278 | 1.0988 | 10.7684 | 14.2589 | 14.8379 | 11.0869 | -0.0001 | -0.0029 | 0.001 | 0.0043 | 0.0008 | -0.0006 | 0.0072 | -0.0201 | -0.0143 | -360.2265 | 17.4213 | -360.4573 | 17.6492 | -360.8174 | 18.222 | -360.8143 | 17.5732 | -352.6383 | 18.721 | -352.5983 | 16.8258
13:02 | 6120 | 50.9963 | 203.109 | 449.7211 | 452.879 | -16.7553 | -38.4202 | 11.9994 | 8.1469 | 2.6843 | 0.8593 | 2.9867 | -1.2452 | 12.248 | 5.3116 | 0.6272 | 0.6675 | 0.971 | 0.7562 | -128.9637 | 2.3783 | 5.8 | 1.943 | -2.6873 | -0.885 | 4.7554 |  | 4.35 | 0.6496 | 4.0053 | 3.3669 | 3.3303 | 1.0994 | 10.7914 | 14.2652 | 14.8932 | 11.1031 | 0 | -0.0026 | 0.001 | 0.0043 | 0.001 | -0.0001 | 0.0112 | -0.0012 | -0.0126 | -360.1896 | 17.4151 | -360.4542 | 17.6451 | -360.7897 | 18.2056 | -360.8266 | 17.565 | -352.586 | 18.7148 | -352.6383 | 16.8135
13:02 | 6121 | 50.9924 | 203.1415 | 449.7239 | 452.9507 | -16.7772 | -38.358 | 11.944 | 8.162 | 2.7121 | 0.9338 | 3.0451 | -1.2571 | 12.2039 | 5.2481 | 0.6267 | 0.6672 | 0.9693 | 0.7552 | -129.0798 | 2.5157 | 5.7185 | 1.9374 | -2.723 | -1.0174 | 4.7589 |  | 4.3896 | 0.7366 | 4.0033 | 3.3669 | 3.3315 | 1.0988 | 10.7984 | 14.2893 | 14.8761 | 11.0872 | 0.0002 | -0.0028 | 0.0007 | 0.0036 | 0.0014 | -0.0008 | 0.0158 | -0.0049 | -0.0173 | -360.1342 | 17.3905 | -360.4019 | 17.6266 | -360.7712 | 18.2097 | -360.8327 | 17.5527 | -352.5613 | 18.7004 | -352.6044 | 16.8074
13:02 | 6122 | 51.0223 | 203.1147 | 449.6732 | 452.9385 | -16.8798 | -38.478 | 11.9849 | 8.1886 | 2.6375 | 0.7542 | 3.0454 | -1.2792 | 12.1777 | 5.1515 | 0.6271 | 0.6659 | 0.9672 | 0.7539 | -129.1075 | 2.4037 | 5.6837 | 1.9684 | -2.612 | -0.9425 | 4.7472 |  | 4.3621 | 0.6287 | 4.0026 | 3.3664 | 3.3324 | 1.0981 | 10.7741 | 14.2649 | 14.8447 | 11.0692 | 0.0002 | -0.0031 | 0.001 | 0.0036 | 0.0003 | -0.0003 | 0.0115 | -0.0079 | -0.0003 | -360.1681 | 17.3843 | -360.4204 | 17.6204 | -360.7681 | 18.1892 | -360.7958 | 17.5486 | -352.589 | 18.7066 | -352.5921 | 16.8053
13:02 | 6123 | 51.048 | 203.1363 | 449.6453 | 452.9442 | -16.8324 | -38.4619 | 12.0542 | 8.2179 | 2.7826 | 0.806 | 3.0041 | -1.2998 | 12.2221 | 5.1568 | 0.6273 | 0.6657 | 0.9688 | 0.7538 | -129.1007 | 2.3801 | 5.7707 | 1.8229 | -2.6458 | -0.9487 | 4.8223 |  | 4.301 | 0.7399 | 4.0028 | 3.3671 | 3.3319 | 1.0999 | 10.7822 | 14.2846 | 14.8301 | 11.0944 | 0 | -0.003 | 0.0005 | 0.0035 | 0.0014 | -0.0007 | 0 | -0.0046 | 0.0013 | -360.1219 | 17.3843 | -360.3927 | 17.6348 | -360.7958 | 18.2097 | -360.7958 | 17.5342 | -352.546 | 18.6922 | -352.5952 | 16.8197
13:02 | 6124 | 50.9406 | 203.1886 | 449.6538 | 452.8916 | -16.8262 | -38.3184 | 12.0554 | 8.2099 | 2.7463 | 0.8296 | 3.0739 | -1.3086 | 12.239 | 5.2128 | 0.6275 | 0.6701 | 0.9711 | 0.7544 | -128.9691 | 2.5117 | 5.8362 | 1.8626 | -2.5239 | -0.9978 | 4.7749 |  | 4.3084 | 0.6823 | 4.004 | 3.3665 | 3.3278 | 1.0992 | 10.7822 | 14.2846 | 14.8648 | 11.1233 | -0.0002 | -0.0026 | 0.0012 | 0.0039 | 0.0007 | -0.0003 | 0.0024 | -0.0102 | -0.0164 | -360.1527 | 17.3864 | -360.3927 | 17.6102 | -360.7589 | 18.1851 | -360.805 | 17.5527 | -352.589 | 18.6943 | -352.5829 | 16.8012
13:02 | 6125 | 50.9725 | 203.1239 | 449.715 | 452.9256 | -16.8011 | -38.4517 | 12.0687 | 8.2915 | 2.7039 | 0.7713 | 2.994 | -1.1614 | 12.2123 | 5.3142 | 0.6262 | 0.6674 | 0.9699 | 0.7556 | -128.945 | 2.559 | 5.7809 | 1.8212 | -2.5583 | -0.9538 | 4.7802 |  | 4.226 | 0.5856 | 4.0053 | 3.3662 | 3.3289 | 1.0999 | 10.7694 | 14.272 | 14.8587 | 11.1161 | -0.0001 | -0.0028 | 0.0013 | 0.0045 | 0.0013 | -0.0001 | 0.0009 | -0.016 | -0.0046 | -360.1588 | 17.3966 | -360.4081 | 17.6369 | -360.7804 | 18.181 | -360.7773 | 17.5486 | -352.5798 | 18.721 | -352.669 | 16.8238
13:02 | 6126 | 50.9697 | 203.127 | 449.6711 | 452.9509 | -16.8326 | -38.5339 | 12.0273 | 8.2723 | 2.6907 | 0.7663 | 2.964 | -1.2625 | 12.2349 | 5.2484 | 0.6272 | 0.6667 | 0.9728 | 0.7561 | -128.9452 | 2.5401 | 5.8307 | 1.9676 | -2.6176 | -0.9823 | 4.7795 |  | 4.2531 | 0.83 | 4.0039 | 3.3669 | 3.3303 | 1.0998 | 10.758 | 14.2773 | 14.8613 | 11.123 | 0.0001 | -0.003 | 0.0004 | 0.0039 | 0.0007 | -0.0002 | 0.0224 | -0.0134 | -0.0011 | -360.1219 | 17.3679 | -360.3804 | 17.6307 | -360.8112 | 18.2179 | -360.8266 | 17.5486 | -352.5552 | 18.6861 | -352.6013 | 16.8197
13:02 | 6127 | 51.1695 | 203.184 | 449.8093 | 452.9736 | -16.7808 | -38.5277 | 11.9916 | 8.2408 | 2.696 | 0.928 | 3.0388 | -1.1288 | 12.3146 | 5.296 | 0.6263 | 0.6677 | 0.9689 | 0.7568 | -128.9903 | 2.4961 | 5.8497 | 2.0101 | -2.5589 | -0.9098 | 4.7982 |  | 4.2899 | 0.8698 | 4.0045 | 3.3701 | 3.3318 | 1.0985 | 10.8019 | 14.2695 | 14.826 | 11.0796 | 0 | -0.003 | 0.0011 | 0.0043 | 0.0007 | -0.0004 | 0.0051 | -0.0066 | -0.004 | -360.1558 | 17.4069 | -360.4266 | 17.6122 | -360.765 | 18.1892 | -360.802 | 17.5671 | -352.6106 | 18.721 | -352.6106 | 16.8032
13:02 | 6128 | 51.1061 | 203.1831 | 449.7622 | 452.9242 | -16.8016 | -38.4302 | 12.0008 | 8.1767 | 2.7374 | 0.8644 | 2.9718 | -1.2008 | 12.2488 | 5.2328 | 0.6269 | 0.6694 | 0.9713 | 0.7562 | -129.0083 | 2.5141 | 5.8537 | 1.8588 | -2.5913 | -0.923 | 4.8572 |  | 4.324 | 0.8837 | 4.0037 | 3.3649 | 3.3308 | 1.0989 | 10.8088 | 14.2996 | 14.8794 | 11.1269 | -0.0002 | -0.0026 | 0.0009 | 0.0041 | 0.0006 | -0.0004 | 0.0254 | -0.0048 | 0.0059 | -360.1311 | 17.3966 | -360.4419 | 17.6512 | -360.8266 | 18.2036 | -360.8174 | 17.5424 | -352.6136 | 18.721 | -352.6721 | 16.8423
13:02 | 6129 | 51.0633 | 203.037 | 449.511 | 452.9772 | -16.8285 | -38.4461 | 12.05 | 8.1715 | 2.8069 | 0.8725 | 3.0223 | -1.1455 | 12.2096 | 5.2628 | 0.6262 | 0.6698 | 0.9688 | 0.756 | -129.0037 | 2.4319 | 5.8056 | 1.8287 | -2.6203 | -0.9819 | 4.857 |  | 4.3309 | 0.8741 | 4.0063 | 3.368 | 3.3285 | 1.0993 | 10.7799 | 14.2533 | 14.8563 | 11.0634 | 0.0003 | -0.0023 | 0.0007 | 0.0038 | 0.001 | -0.0006 | 0.0119 | -0.0025 | -0.0084 | -360.1496 | 17.3843 | -360.4081 | 17.6328 | -360.802 | 18.2241 | -360.8481 | 17.5732 | -352.6321 | 18.6922 | -352.6044 | 16.8279
13:02 | 6130 | 51.0906 | 203.0822 | 449.5938 | 452.9554 | -16.8458 | -38.4507 | 12.0253 | 8.2478 | 2.7822 | 0.9062 | 3.0602 | -1.201 | 12.2214 | 5.3147 | 0.6261 | 0.668 | 0.9704 | 0.7545 | -129.0131 | 2.413 | 5.8436 | 1.8771 | -2.5703 | -0.8831 | 4.8245 |  | 4.2983 | 0.7292 | 4.0051 | 3.367 | 3.3299 | 1.0993 | 10.7868 | 14.2892 | 14.8924 | 11.128 | 0.0003 | -0.0032 | 0.0007 | 0.0039 | 0.0009 | -0.0005 | 0.0215 | -0.0138 | -0.0053 | -360.2173 | 17.4459 | -360.4789 | 17.641 | -360.8327 | 18.1953 | -360.7989 | 17.5773 | -352.6598 | 18.7497 | -352.6537 | 16.8258
13:02 | 6131 | 51.0876 | 203.1574 | 449.6279 | 452.9833 | -16.7736 | -38.393 | 11.9893 | 8.1495 | 2.815 | 0.9454 | 3.0217 | -1.2428 | 12.1798 | 5.3136 | 0.6264 | 0.6695 | 0.9727 | 0.7556 | -128.9892 | 2.4268 | 5.6977 | 1.8387 | -2.4601 | -0.8816 | 4.7785 |  | 4.3113 | 0.6014 | 4.0048 | 3.3668 | 3.33 | 1.0966 | 10.7904 | 14.2635 | 14.8712 | 11.0685 | 0 | -0.0029 | 0.0007 | 0.0037 | 0.0008 | -0.0006 | 0.0207 | 0.001 | -0.0089 | -360.1588 | 17.4007 | -360.4604 | 17.6574 | -360.8727 | 18.2364 | -360.8574 | 17.5568 | -352.6136 | 18.7107 | -352.6136 | 16.8505
13:02 | 6132 | 51.0505 | 203.1537 | 449.6081 | 452.9552 | -16.7861 | -38.4242 | 11.9808 | 8.1447 | 2.7523 | 0.8669 | 3.0455 | -1.3105 | 12.1703 | 5.3434 | 0.6273 | 0.668 | 0.9683 | 0.7571 | -129.0209 | 2.4206 | 5.8433 | 1.7998 | -2.5316 | -0.9077 | 4.7928 |  | 4.2779 | 0.6814 | 4.0057 | 3.3721 | 3.3334 | 1.099 | 10.7742 | 14.2704 | 14.831 | 11.1104 | -0.0006 | -0.0026 | 0.0005 | 0.004 | 0.0012 | -0.0004 | 0.0112 | -0.0059 | -0.0098 | -360.2665 | 17.4274 | -360.4512 | 17.6307 | -360.8143 | 18.2118 | -360.8358 | 17.5999 | -352.6721 | 18.7251 | -352.6444 | 16.8156
13:02 | 6133 | 51.0443 | 203.1773 | 449.6047 | 453.0021 | -16.8025 | -38.564 | 12.0065 | 8.1511 | 2.7195 | 0.7483 | 3.0438 | -1.2352 | 12.2134 | 5.3414 | 0.6256 | 0.6685 | 0.9672 | 0.7566 | -129.0333 | 2.3911 | 5.826 | 1.7686 | -2.4912 | -0.8547 | 4.9265 |  | 4.2906 | 0.6818 | 4.0041 | 3.3654 | 3.3287 | 1.0994 | 10.8076 | 14.2523 | 14.8502 | 11.0966 | -0.0005 | -0.0027 | 0.001 | 0.004 | 0.0007 | -0.0003 | 0.013 | -0.0154 | -0.0139 | -360.205 | 17.4274 | -360.4819 | 17.68 | -360.8574 | 18.2179 | -360.8327 | 17.5629 | -352.6475 | 18.7353 | -352.7121 | 16.8607
13:02 | 6134 | 51.1236 | 203.1919 | 449.6026 | 452.9765 | -16.8655 | -38.4694 | 11.9639 | 8.1872 | 2.7117 | 0.8304 | 3.1692 | -1.273 | 12.2574 | 5.2846 | 0.6265 | 0.6676 | 0.9705 | 0.756 | -128.9573 | 2.4298 | 5.8884 | 1.7029 | -2.5532 | -0.9233 | 4.8294 |  | 4.3598 | 0.6687 | 4.005 | 3.3669 | 3.3314 | 1.1006 | 10.7973 | 14.2822 | 14.8447 | 11.0692 | 0.0002 | -0.0031 | 0.0007 | 0.0038 | 0.0014 | -0.0003 | 0.0015 | -0.006 | -0.0007 | -360.2081 | 17.411 | -360.4235 | 17.6348 | -360.7958 | 18.2323 | -360.8758 | 17.5855 | -352.6475 | 18.7066 | -352.5921 | 16.8115
13:02 | 6135 | 51.1292 | 203.1219 | 449.6984 | 453.0336 | -16.8577 | -38.4435 | 11.9587 | 8.1619 | 2.8264 | 0.7982 | 3.053 | -1.145 | 12.2726 | 5.372 | 0.627 | 0.6673 | 0.9666 | 0.7555 | -129.0323 | 2.4522 | 5.789 | 1.7749 | -2.4559 | -0.9055 | 4.7868 |  | 4.3547 | 0.705 | 4.0049 | 3.367 | 3.3283 | 1.0998 | 10.788 | 14.2729 | 14.8464 | 11.1064 | 0 | -0.0031 | 0.0009 | 0.0041 | 0.001 | 0.0002 | 0.0243 | -0.0146 | -0.0008 | -360.1896 | 17.4356 | -360.4912 | 17.6553 | -360.845 | 18.1933 | -360.7835 | 17.5486 | -352.626 | 18.7415 | -352.6475 | 16.832
13:02 | 6136 | 51.0513 | 203.0791 | 449.5994 | 452.9571 | -16.8345 | -38.5389 | 11.9558 | 8.1553 | 2.7368 | 0.8693 | 3.0014 | -1.1869 | 12.2884 | 5.2546 | 0.6272 | 0.6666 | 0.9704 | 0.7555 | -129.0868 | 2.3673 | 5.8865 | 1.602 | -2.445 | -0.8303 | 4.8832 |  | 4.3416 | 0.7205 | 4.0045 | 3.3663 | 3.3273 | 1.0994 | 10.7866 | 14.2724 | 14.8909 | 11.1381 | 0 | -0.0025 | 0.0007 | 0.0036 | 0.0008 | -0.0006 | 0.0051 | -0.0233 | -0.0004 | -360.1588 | 17.3823 | -360.4019 | 17.6204 | -360.8327 | 18.2302 | -360.8789 | 17.5629 | -352.6044 | 18.682 | -352.5767 | 16.8176
13:02 | 6137 | 51.1145 | 203.1362 | 449.6623 | 453.0066 | -16.8231 | -38.4762 | 11.9478 | 8.1874 | 2.8212 | 0.8631 | 3.0043 | -1.2688 | 12.251 | 5.3124 | 0.626 | 0.6684 | 0.9655 | 0.7545 | -129.0821 | 2.3922 | 5.7228 | 1.6467 | -2.378 | -0.7914 | 4.9136 |  | 4.2909 | 0.7546 | 4.0045 | 3.3638 | 3.3281 | 1.0992 | 10.7892 | 14.2914 | 14.8709 | 11.119 | -0.0004 | -0.003 | 0.0007 | 0.0037 | 0.0011 | 0.0002 | 0.0238 | -0.0083 | -0.013 | -360.1927 | 17.4069 | -360.4296 | 17.6245 | -360.7681 | 18.1645 | -360.7773 | 17.5465 | -352.6013 | 18.7087 | -352.5983 | 16.8115
13:02 | 6138 | 51.1048 | 203.1741 | 449.7761 | 453.1016 | -16.8413 | -38.3392 | 11.9514 | 8.1683 | 2.8361 | 0.8374 | 3.0274 | -1.2603 | 12.2275 | 5.2646 | 0.6262 | 0.6673 | 0.9678 | 0.7551 | -129.1393 | 2.3408 | 5.776 | 1.578 | -2.4355 | -0.8982 | 4.8306 |  | 4.2861 | 0.8024 | 4.0055 | 3.3629 | 3.3298 | 1.0994 | 10.7868 | 14.3009 | 14.824 | 11.1045 | 0.0002 | -0.0028 | 0.0008 | 0.0036 | 0.0013 | -0.0005 | -0.0037 | -0.0081 | -0.0093 | -360.1219 | 17.374 | -360.3958 | 17.6245 | -360.802 | 18.2077 | -360.7835 | 17.5342 | -352.5552 | 18.6861 | -352.5644 | 16.832
13:02 | 6139 | 51.143 | 203.208 | 449.6705 | 453.1094 | -16.9515 | -38.3604 | 11.9369 | 8.1429 | 2.8266 | 0.9092 | 3.0095 | -1.2034 | 12.2943 | 5.2936 | 0.627 | 0.6678 | 0.9711 | 0.7562 | -129.0073 | 2.3549 | 5.8146 | 1.593 | -2.4415 | -0.951 | 4.7912 |  | 4.2322 | 0.7557 | 4.004 | 3.3613 | 3.3273 | 1.0982 | 10.788 | 14.273 | 14.8822 | 11.1002 | 0 | -0.0033 | 0.0011 | 0.0038 | 0.001 | 0.0001 | 0.007 | -0.0059 | -0.0087 | -360.1465 | 17.4028 | -360.4358 | 17.6225 | -360.7497 | 18.1933 | -360.8112 | 17.5609 | -352.6198 | 18.7066 | -352.6229 | 16.8156
13:02 | 6140 | 51.0319 | 203.1243 | 449.7438 | 452.9994 | -16.8462 | -38.3828 | 11.9139 | 8.0603 | 2.7635 | 0.8393 | 3.0353 | -1.2278 | 12.2204 | 5.1515 | 0.6275 | 0.6667 | 0.9707 | 0.7563 | -129.0522 | 2.3854 | 5.7814 | 1.5806 | -2.4678 | -1.0249 | 4.7292 |  | 4.3275 | 0.7992 | 4.0033 | 3.3629 | 3.327 | 1.0999 | 10.7649 | 14.2613 | 14.8406 | 11.1006 | -0.0001 | -0.0027 | 0.0004 | 0.0038 | 0.0007 | -0.0006 | 0.0099 | -0.0129 | -0.0162 | -360.1681 | 17.3843 | -360.4389 | 17.643 | -360.7804 | 18.2015 | -360.7866 | 17.5445 | -352.5952 | 18.7107 | -352.6444 | 16.8484
13:02 | 6141 | 51.1094 | 203.2035 | 449.7999 | 453.1695 | -16.8309 | -38.3362 | 11.9965 | 8.1741 | 2.8295 | 0.9241 | 3.0068 | -1.3288 | 12.0919 | 5.1117 | 0.6258 | 0.6676 | 0.9709 | 0.7569 | -129.1067 | 2.3607 | 5.689 | 1.5772 | -2.454 | -0.8867 | 4.7992 |  | 4.2757 | 0.8042 | 4.0034 | 3.3658 | 3.3283 | 1.0989 | 10.8075 | 14.2932 | 14.8708 | 11.1128 | 0 | -0.0026 | 0.0018 | 0.0044 | 0.0012 | 0 | -0.0036 | -0.0003 | -0.0069 | -360.1711 | 17.3987 | -360.4481 | 17.6369 | -360.7958 | 18.222 | -360.8481 | 17.5753 | -352.6413 | 18.721 | -352.626 | 16.8381
13:02 | 6142 | 51.1079 | 203.2152 | 449.7946 | 453.1158 | -16.727 | -38.2712 | 12.0188 | 8.2009 | 2.856 | 0.8887 | 3.0086 | -1.3403 | 12.0864 | 5.1117 | 0.6263 | 0.6679 | 0.9713 | 0.7552 | -129.0836 | 2.3069 | 5.7094 | 1.628 | -2.5306 | -0.9927 | 4.7479 |  | 4.3041 | 0.755 | 4.0052 | 3.3638 | 3.3303 | 1.0994 | 10.8042 | 14.2892 | 14.9155 | 11.1222 | 0.0003 | -0.003 | 0.001 | 0.004 | 0.0011 | -0.0004 | 0.0204 | -0.005 | -0.0174 | -360.1742 | 17.4131 | -360.4758 | 17.6451 | -360.802 | 18.222 | -360.8389 | 17.5712 | -352.6167 | 18.723 | -352.666 | 16.8484
13:02 | 6143 | 51.0911 | 203.0766 | 449.6522 | 453.0469 | -16.7893 | -38.3408 | 11.9491 | 8.3211 | 2.7842 | 0.8463 | 3.0219 | -1.3891 | 12.1125 | 5.1707 | 0.6249 | 0.6673 | 0.9721 | 0.7547 | -129.0596 | 2.4116 | 5.7448 | 1.7081 | -2.416 | -0.8315 | 4.8282 |  | 4.2651 | 0.8221 | 4.0059 | 3.3676 | 3.3301 | 1.0986 | 10.7971 | 14.3 | 14.8711 | 11.1258 | 0.0002 | -0.0029 | 0.0014 | 0.0044 | 0.0011 | -0.0002 | 0.0203 | 0.0037 | -0.0047 | -360.2142 | 17.4192 | -360.4635 | 17.6594 | -360.8389 | 18.22 | -360.845 | 17.5794 | -352.626 | 18.721 | -352.6413 | 16.8484
13:02 | 6144 | 51.1325 | 203.1572 | 449.5931 | 453.0056 | -16.9009 | -38.3047 | 11.9407 | 8.2489 | 2.7936 | 0.8335 | 3.0501 | -1.2876 | 12.1067 | 5.2333 | 0.6267 | 0.6692 | 0.9686 | 0.755 | -129.0432 | 2.409 | 5.6659 | 1.845 | -2.3325 | -0.8358 | 4.839 |  | 4.2987 | 0.8246 | 4.0048 | 3.3619 | 3.3294 | 1.0978 | 10.8007 | 14.3149 | 14.873 | 11.1298 | -0.0001 | -0.0027 | 0.0009 | 0.0041 | 0.0005 | -0.0003 | -0.0045 | -0.0131 | 0.0094 | -360.2173 | 17.4151 | -360.4666 | 17.6533 | -360.8327 | 18.222 | -360.8604 | 17.5753 | -352.6352 | 18.7128 | -352.6413 | 16.8381
13:02 | 6145 | 51.169 | 203.1336 | 449.6829 | 453.1505 | -16.8657 | -38.1847 | 11.926 | 8.1831 | 2.7457 | 0.8073 | 3.0459 | -1.2847 | 12.093 | 5.2 | 0.6261 | 0.6666 | 0.9668 | 0.7548 | -129.0961 | 2.4458 | 5.6416 | 1.7268 | -2.4187 | -0.9481 | 4.8453 |  | 4.2961 | 0.705 | 4.0055 | 3.3686 | 3.334 | 1.0975 | 10.7904 | 14.3096 | 14.847 | 11.0862 | -0.0005 | -0.0027 | 0.0007 | 0.0032 | 0.0008 | -0.0009 | 0.0153 | -0.0016 | -0.0026 | -360.2111 | 17.4254 | -360.4973 | 17.6759 | -360.8204 | 18.2118 | -360.8358 | 17.5691 | -352.6167 | 18.7271 | -352.6444 | 16.834
13:02 | 6146 | 51.0946 | 203.1925 | 449.7467 | 453.1424 | -16.8145 | -38.3838 | 11.8399 | 8.2743 | 2.7796 | 0.7515 | 3.0689 | -1.258 | 12.1281 | 5.1677 | 0.6268 | 0.6705 | 0.9676 | 0.7542 | -129.1513 | 2.3789 | 5.6762 | 1.7077 | -2.4167 | -1.0359 | 4.7964 |  | 4.3377 | 0.746 | 4.0046 | 3.3659 | 3.3333 | 1.0982 | 10.7348 | 14.2544 | 14.8045 | 11.088 | 0.0005 | -0.0028 | 0.0005 | 0.0039 | 0.0008 | -0.0002 | 0.0098 | -0.0015 | -0.0071 | -360.1527 | 17.411 | -360.4542 | 17.6677 | -360.842 | 18.2261 | -360.8512 | 17.5671 | -352.6136 | 18.7025 | -352.6321 | 16.8361
13:02 | 6147 | 51.1116 | 203.0653 | 449.6642 | 453.081 | -16.8247 | -38.3477 | 11.9218 | 8.2177 | 2.741 | 0.7053 | 2.9775 | -1.253 | 12.1497 | 5.212 | 0.6266 | 0.6677 | 0.9684 | 0.7544 | -129.1368 | 2.5116 | 5.7032 | 1.687 | -2.4164 | -0.8333 | 4.8281 |  | 4.2645 | 0.7075 | 4.0044 | 3.3647 | 3.334 | 1.0993 | 10.7823 | 14.2437 | 14.8037 | 11.0782 | 0.0001 | -0.0033 | 0.0008 | 0.0038 | 0.0008 | -0.0008 | 0.0035 | -0.023 | -0.0102 | -360.1619 | 17.4151 | -360.4358 | 17.6328 | -360.7804 | 18.2118 | -360.8389 | 17.5794 | -352.6383 | 18.7128 | -352.6013 | 16.8053
13:02 | 6148 | 51.1234 | 203.1186 | 449.7093 | 453.0333 | -16.718 | -38.212 | 12.0739 | 8.1441 | 2.7391 | 0.6073 | 2.9805 | -1.2357 | 12.1367 | 5.1721 | 0.6261 | 0.6678 | 0.9659 | 0.7554 | -129.1667 | 2.4442 | 5.6912 | 1.6396 | -2.5187 | -0.9218 | 4.7974 |  | 4.3665 | 0.7553 | 4.0036 | 3.3638 | 3.3352 | 1.0993 | 10.7695 | 14.2544 | 14.8508 | 11.0937 | 0.0001 | -0.0029 | 0.0008 | 0.0037 | 0.0008 | 0.0002 | 0.0103 | -0.0019 | 0.0035 | -360.1773 | 17.411 | -360.4942 | 17.6779 | -360.8235 | 18.2056 | -360.7958 | 17.5547 | -352.5798 | 18.7087 | -352.6567 | 16.8525
13:02 | 6149 | 51.104 | 203.0745 | 449.6275 | 453.1179 | -16.7411 | -38.2312 | 12.0843 | 8.2086 | 2.7921 | 0.7259 | 2.9873 | -1.2414 | 12.1539 | 5.1474 | 0.6258 | 0.6709 | 0.9668 | 0.7546 | -129.0917 | 2.4061 | 5.7325 | 1.7192 | -2.5577 | -0.8702 | 4.8247 |  | 4.3873 | 0.6958 | 4.0054 | 3.3635 | 3.3298 | 1.098 | 10.7776 | 14.2569 | 14.8488 | 11.0955 | -0.0002 | -0.0026 | 0.0012 | 0.0045 | 0.0011 | -0.0009 | 0.0217 | 0.0021 | -0.0155 | -360.1435 | 17.3699 | -360.3773 | 17.6307 | -360.7773 | 18.2118 | -360.8358 | 17.5588 | -352.5767 | 18.6758 | -352.5644 | 16.8094
13:02 | 6150 | 51.0562 | 203.1077 | 449.7018 | 453.1666 | -16.6978 | -38.1993 | 12.0334 | 8.1794 | 2.6888 | 0.7517 | 3.0068 | -1.2772 | 12.1919 | 5.23 | 0.6256 | 0.6679 | 0.9627 | 0.7544 | -129.1807 | 2.3923 | 5.7675 | 1.7367 | -2.4048 | -0.9387 | 4.8881 |  | 4.4007 | 0.822 | 4.0047 | 3.3681 | 3.3336 | 1.0992 | 10.7845 | 14.2868 | 14.8549 | 11.1028 | 0.0005 | -0.0026 | 0.0007 | 0.0038 | 0.001 | 0.0001 | 0.0052 | -0.007 | 0.0084 | -360.1311 | 17.4192 | -360.4481 | 17.6471 | -360.7681 | 18.1625 | -360.7527 | 17.5506 | -352.5921 | 18.7107 | -352.6044 | 16.8197
13:02 | 6151 | 51.0622 | 203.1113 | 449.6877 | 453.1245 | -16.7566 | -38.1627 | 12.0482 | 8.2196 | 2.7543 | 0.7662 | 3.0424 | -1.2577 | 12.1754 | 5.2017 | 0.6251 | 0.6672 | 0.9688 | 0.7545 | -129.1307 | 2.4582 | 5.7208 | 1.737 | -2.5491 | -1.0145 | 4.8072 |  | 4.285 | 0.7237 | 4.005 | 3.367 | 3.3287 | 1.0987 | 10.796 | 14.2871 | 14.8686 | 11.0962 | 0.0002 | -0.0027 | 0.0011 | 0.0042 | 0.0014 | -0.0002 | 0.0106 | -0.0033 | -0.0218 | -360.0973 | 17.3453 | -360.3804 | 17.6615 | -360.8358 | 18.2159 | -360.8174 | 17.5342 | -352.5429 | 18.6717 | -352.5613 | 16.8381
13:02 | 6152 | 51.1646 | 203.1316 | 449.6593 | 453.1385 | -16.4151 | -38.2183 | 12.0069 | 8.2819 | 2.7266 | 0.7572 | 3.0569 | -1.1852 | 12.1737 | 5.2226 | 0.6268 | 0.6647 | 0.9644 | 0.7548 | -129.0658 | 2.4421 | 5.721 | 1.7031 | -2.5598 | -1.0726 | 4.7839 |  | 4.3918 | 0.6962 | 4.0041 | 3.367 | 3.3318 | 1.0995 | 10.8214 | 14.3012 | 14.8377 | 11.1269 | -0.0002 | -0.0026 | 0.0012 | 0.004 | 0.0007 | 0 | 0.028 | 0.0071 | -0.0083 | -360.2081 | 17.4131 | -360.4204 | 17.6369 | -360.7527 | 18.1666 | -360.8297 | 17.5671 | -352.669 | 18.721 | -352.6136 | 16.8115
13:02 | 6153 | 51.1433 | 203.1025 | 449.704 | 453.1455 | -16.3724 | -38.2429 | 11.8802 | 8.2303 | 2.7473 | 0.7714 | 3.0105 | -1.2617 | 12.1511 | 5.2174 | 0.6257 | 0.6655 | 0.9707 | 0.7565 | -129.1481 | 2.4271 | 5.7129 | 1.7582 | -2.5212 | -0.9408 | 4.8352 |  | 4.3598 | 0.7848 | 4.0041 | 3.3668 | 3.3301 | 1.0985 | 10.7961 | 14.2754 | 14.8791 | 11.1428 | -0.0002 | -0.0025 | 0.0007 | 0.0035 | 0.0008 | -0.0005 | 0.0019 | -0.0155 | -0.0163 | -360.1496 | 17.409 | -360.4789 | 17.7046 | -360.8789 | 18.1933 | -360.8112 | 17.5424 | -352.6167 | 18.7087 | -352.6906 | 16.871
13:02 | 6154 | 51.2031 | 203.2218 | 449.7592 | 453.2288 | -16.401 | -38.2915 | 11.789 | 8.1454 | 2.71 | 0.8029 | 3.0777 | -1.2713 | 12.1452 | 5.1887 | 0.6255 | 0.665 | 0.9706 | 0.7571 | -129.0957 | 2.5234 | 5.8233 | 1.7862 | -2.5512 | -0.9093 | 4.7271 |  | 4.3793 | 0.8318 | 4.0048 | 3.3684 | 3.3345 | 1.0981 | 10.7765 | 14.2554 | 14.8569 | 11.0779 | -0.0004 | -0.0032 | 0.001 | 0.004 | 0.0008 | -0.0008 | 0.0129 | 0.0029 | -0.0115 | -360.1742 | 17.3925 | -360.405 | 17.6492 | -360.7835 | 18.2138 | -360.885 | 17.5978 | -352.6598 | 18.6984 | -352.5798 | 16.8238
13:02 | 6155 | 51.205 | 203.2405 | 449.7926 | 453.2754 | -16.3979 | -38.3526 | 11.8641 | 8.1067 | 2.7886 | 0.7526 | 3.027 | -1.299 | 12.0949 | 5.047 | 0.6257 | 0.6652 | 0.9693 | 0.7562 | -129.07 | 2.5521 | 5.769 | 1.9229 | -2.4916 | -0.8753 | 4.7586 |  | 4.424 | 0.7748 | 4.0044 | 3.3696 | 3.3296 | 1.0977 | 10.781 | 14.2776 | 14.8577 | 11.0818 | 0.0001 | -0.0032 | 0.0005 | 0.0041 | 0.0012 | -0.0001 | 0.0056 | -0.0057 | -0.0084 | -360.1988 | 17.4582 | -360.5281 | 17.6985 | -360.845 | 18.1707 | -360.7804 | 17.5753 | -352.6475 | 18.7456 | -352.6721 | 16.8525
13:02 | 6156 | 51.173 | 203.1359 | 449.6191 | 453.1703 | -16.3856 | -38.1605 | 11.9059 | 8.2123 | 2.8085 | 1.0158 | 3.0785 | -1.2001 | 12.199 | 5.1073 | 0.6269 | 0.661 | 0.9709 | 0.7567 | -129.0323 | 2.4326 | 5.7636 | 1.822 | -2.5001 | -0.9334 | 4.7971 |  | 4.3503 | 0.6891 | 4.0047 | 3.368 | 3.3324 | 1.0996 | 10.7603 | 14.2392 | 14.8235 | 11.0905 | -0.0002 | -0.003 | 0.0006 | 0.0038 | 0.0012 | -0.0006 | 0.0248 | -0.0057 | 0.002 | -360.1619 | 17.3925 | -360.4327 | 17.6677 | -360.8389 | 18.222 | -360.8574 | 17.5773 | -352.5921 | 18.6881 | -352.6044 | 16.8381
13:02 | 6157 | 51.1425 | 203.1994 | 449.7187 | 453.2421 | -16.4162 | -38.3212 | 11.7525 | 8.2543 | 2.8599 | 0.9663 | 3.1144 | -1.223 | 12.1549 | 5.1439 | 0.6256 | 0.6614 | 0.9673 | 0.7552 | -129.0672 | 2.5185 | 5.7259 | 1.7736 | -2.5136 | -0.8832 | 4.7305 |  | 4.423 | 0.7362 | 4.0042 | 3.3706 | 3.3292 | 1.0982 | 10.7973 | 14.2649 | 14.8852 | 11.0981 | -0.0002 | -0.0025 | 0.0011 | 0.0045 | 0.0007 | -0.0004 | 0.0068 | -0.0131 | -0.026 | -360.2235 | 17.4295 | -360.4666 | 17.6553 | -360.7927 | 18.1543 | -360.8297 | 17.5917 | -352.6444 | 18.7353 | -352.6413 | 16.8032
13:02 | 6158 | 51.1789 | 203.1638 | 449.7535 | 453.1776 | -16.3211 | -38.2271 | 11.7532 | 8.1582 | 2.7989 | 0.8843 | 3.0492 | -1.212 | 12.1896 | 5.2206 | 0.6253 | 0.6651 | 0.9677 | 0.7562 | -128.9791 | 2.5031 | 5.6972 | 1.7743 | -2.461 | -0.9105 | 4.7496 |  | 4.3473 | 0.7873 | 4.005 | 3.37 | 3.3328 | 1.0986 | 10.8042 | 14.2776 | 14.8345 | 11.1222 | 0.0003 | -0.0027 | 0.0007 | 0.0038 | 0.0007 | -0.0005 | -0.0035 | -0.0075 | -0.0254 | -360.1619 | 17.4007 | -360.4604 | 17.6738 | -360.842 | 18.183 | -360.7958 | 17.5486 | -352.5613 | 18.7004 | -352.6321 | 16.8464
13:02 | 6159 | 51.2558 | 203.1542 | 449.6742 | 453.3039 | -16.2633 | -38.2109 | 11.8734 | 8.1663 | 2.7892 | 0.865 | 2.9992 | -1.2759 | 12.2951 | 5.1892 | 0.6247 | 0.6645 | 0.9682 | 0.7571 | -129.0821 | 2.449 | 5.7051 | 1.7685 | -2.4726 | -0.9578 | 4.8048 |  | 4.3508 | 0.9246 | 4.0042 | 3.3683 | 3.3322 | 1.0996 | 10.8053 | 14.2905 | 14.8717 | 11.123 | -0.0001 | -0.0034 | 0.001 | 0.0039 | 0.0009 | 0 | 0.0224 | -0.0136 | -0.0024 | -360.1865 | 17.3864 | -360.3927 | 17.6307 | -360.7466 | 18.183 | -360.845 | 17.602 | -352.6106 | 18.6902 | -352.6013 | 16.8032
13:02 | 6160 | 51.1724 | 203.1628 | 449.639 | 453.22 | -16.3031 | -38.2005 | 11.9074 | 8.1627 | 2.8599 | 0.8966 | 3.0534 | -1.1479 | 12.2724 | 5.1593 | 0.6253 | 0.6664 | 0.9701 | 0.7573 | -129.0459 | 2.3978 | 5.7709 | 1.8617 | -2.4448 | -0.969 | 4.7264 |  | 4.3866 | 0.8726 | 4.0042 | 3.3667 | 3.3307 | 1.0992 | 10.7902 | 14.3045 | 14.8628 | 11.0962 | 0 | -0.0027 | 0.0013 | 0.0039 | 0.0012 | -0.0004 | 0.0092 | -0.0026 | -0.0126 | -360.1127 | 17.4069 | -360.4573 | 17.6656 | -360.7989 | 18.1502 | -360.725 | 17.5568 | -352.5736 | 18.7004 | -352.6321 | 16.8279
13:02 | 6161 | 51.1691 | 203.1207 | 449.6969 | 453.2252 | -16.7341 | -38.1607 | 11.9261 | 8.1657 | 2.7788 | 0.9863 | 3.0708 | -1.2314 | 12.1954 | 5.2234 | 0.6265 | 0.6698 | 0.9726 | 0.7569 | -128.9915 | 2.4742 | 5.7744 | 1.832 | -2.462 | -0.8457 | 4.7503 |  | 4.3657 | 0.9151 | 4.0042 | 3.3636 | 3.3321 | 1.0991 | 10.7845 | 14.2812 | 14.8676 | 11.1255 | -0.0006 | -0.0028 | 0.0009 | 0.0039 | 0.0008 | -0.0003 | 0.0324 | -0.0053 | 0.0164 | -360.1435 | 17.374 | -360.3835 | 17.6286 | -360.7589 | 18.1707 | -360.8574 | 17.5814 | -352.5644 | 18.682 | -352.546 | 16.8156
13:02 | 6162 | 51.0982 | 203.1547 | 449.6039 | 453.154 | -16.6459 | -38.0905 | 12.1476 | 8.1638 | 2.7939 | 0.9422 | 3.061 | -1.2914 | 12.245 | 5.2307 | 0.627 | 0.6716 | 0.971 | 0.7584 | -129.047 | 2.3697 | 5.695 | 1.8411 | -2.4906 | -0.9569 | 4.7477 |  | 4.4066 | 0.8851 | 4.0036 | 3.3637 | 3.3315 | 1.0993 | 10.7603 | 14.268 | 14.8225 | 11.1082 | 0 | -0.003 | 0.0006 | 0.004 | 0.001 | -0.0007 | 0.0168 | -0.0078 | 0.0016 | -360.1711 | 17.3987 | -360.4204 | 17.6451 | -360.7804 | 18.1563 | -360.762 | 17.5732 | -352.5583 | 18.6922 | -352.6506 | 16.832
13:02 | 6163 | 51.1919 | 203.1649 | 449.6283 | 453.25 | -16.2029 | -38.0643 | 12.1479 | 8.1895 | 2.7565 | 0.9193 | 2.9754 | -1.2905 | 12.2016 | 5.1419 | 0.6267 | 0.6696 | 0.9704 | 0.7572 | -129.0908 | 2.4048 | 5.6958 | 1.8228 | -2.571 | -0.8994 | 4.7072 |  | 4.398 | 1.0891 | 4.0037 | 3.3652 | 3.3311 | 1.0988 | 10.796 | 14.322 | 14.8755 | 11.1247 | 0 | -0.0031 | 0.0009 | 0.0041 | 0.0009 | 0 | 0.0034 | -0.002 | 0.0005 | -360.125 | 17.3925 | -360.4419 | 17.641 | -360.7743 | 18.1707 | -360.8112 | 17.565 | -352.5798 | 18.6861 | -352.6013 | 16.8258
13:02 | 6164 | 51.2359 | 203.1905 | 449.6279 | 453.1821 | -16.2414 | -38.1581 | 12.0589 | 8.2046 | 2.7355 | 1.0341 | 3.0385 | -1.3816 | 12.2301 | 5.1663 | 0.6261 | 0.6684 | 0.9683 | 0.7557 | -129.0497 | 2.3778 | 5.6895 | 1.8155 | -2.6241 | -0.9587 | 4.7367 |  | 4.3042 | 0.8178 | 4.004 | 3.366 | 3.3329 | 1.0985 | 10.7938 | 14.2902 | 14.8811 | 11.089 | -0.0001 | -0.003 | 0.001 | 0.0039 | 0.001 | -0.0008 | 0.0038 | -0.0005 | -0.0024 | -360.165 | 17.3987 | -360.4266 | 17.6553 | -360.805 | 18.183 | -360.8481 | 17.5835 | -352.6106 | 18.6922 | -352.6198 | 16.8299
13:02 | 6165 | 51.2367 | 203.2076 | 449.6559 | 453.2023 | -16.3148 | -38.2426 | 11.9578 | 8.3239 | 2.7823 | 1.1824 | 3.1037 | -1.3903 | 12.0863 | 5.1396 | 0.6247 | 0.6649 | 0.9685 | 0.7567 | -129.0657 | 2.4649 | 5.6469 | 1.866 | -2.4954 | -0.842 | 4.8088 |  | 4.4349 | 0.8481 | 4.0043 | 3.3664 | 3.3314 | 1.0983 | 10.7603 | 14.2739 | 14.8004 | 11.0905 | -0.0003 | -0.0029 | 0.0008 | 0.0041 | 0.0009 | 0.0001 | 0.021 | -0.0017 | -0.0081 | -360.1681 | 17.409 | -360.4666 | 17.682 | -360.8081 | 18.1584 | -360.8389 | 17.5732 | -352.6167 | 18.6943 | -352.6567 | 16.8402
13:02 | 6166 | 51.3056 | 203.235 | 449.7282 | 453.2593 | -16.3776 | -38.4028 | 11.8868 | 8.2096 | 2.7414 | 0.9224 | 3.0365 | -1.3861 | 12.1362 | 5.1849 | 0.626 | 0.6644 | 0.9681 | 0.7555 | -129.0192 | 2.4529 | 5.6414 | 1.8652 | -2.6123 | -0.8634 | 4.6888 |  | 4.4077 | 0.823 | 4.0052 | 3.3663 | 3.3292 | 1.0986 | 10.7995 | 14.2846 | 14.8706 | 11.0944 | -0.0002 | -0.0025 | 0.0006 | 0.0037 | 0.0007 | -0.0006 | 0.0021 | -0.0032 | -0.0054 | -360.1681 | 17.3987 | -360.4327 | 17.68 | -360.8666 | 18.2159 | -360.8758 | 17.5917 | -352.6106 | 18.6963 | -352.6352 | 16.8423
13:02 | 6167 | 51.3376 | 203.2457 | 449.6801 | 453.2429 | -16.3896 | -38.3073 | 11.9016 | 8.1326 | 2.7446 | 0.9526 | 3.0309 | -1.2484 | 12.1978 | 5.2845 | 0.6262 | 0.668 | 0.9706 | 0.7552 | -129.0287 | 2.5022 | 5.7085 | 1.8265 | -2.5938 | -0.9323 | 4.673 |  | 4.4114 | 0.8201 | 4.0047 | 3.3654 | 3.3331 | 1.0996 | 10.8053 | 14.3137 | 14.9122 | 11.1172 | 0.0003 | -0.0031 | 0.001 | 0.0038 | 0.0007 | -0.0005 | -0.0041 | -0.0069 | -0.0054 | -360.2542 | 17.4356 | -360.4666 | 17.6533 | -360.7989 | 18.1892 | -360.8635 | 17.6184 | -352.6506 | 18.7066 | -352.6444 | 16.8238
13:03 | 6168 | 51.1991 | 203.2739 | 449.66 | 453.2056 | -16.4352 | -38.4326 | 11.7822 | 8.1643 | 2.7273 | 0.9351 | 3.0467 | -1.2821 | 12.1709 | 5.2486 | 0.6266 | 0.6652 | 0.9708 | 0.7574 | -129.0257 | 2.4781 | 5.6696 | 1.8184 | -2.6765 | -1.0387 | 4.6535 |  | 4.3582 | 0.7337 | 4.0041 | 3.3653 | 3.3331 | 1.0981 | 10.7868 | 14.2718 | 14.8461 | 11.0991 | -0.0002 | -0.0029 | 0.0012 | 0.0041 | 0.0013 | 0.0001 | 0.0186 | -0.0135 | -0.0003 | -360.1435 | 17.4192 | -360.4912 | 17.7087 | -360.885 | 18.1994 | -360.8389 | 17.5671 | -352.5952 | 18.6902 | -352.6813 | 16.8566
13:03 | 6169 | 51.1444 | 203.2004 | 449.711 | 453.1986 | -16.3748 | -38.377 | 11.9386 | 8.2194 | 2.7729 | 0.9709 | 3.0186 | -1.2612 | 12.1046 | 5.2516 | 0.6263 | 0.6652 | 0.9723 | 0.7555 | -129.0395 | 2.4857 | 5.6654 | 1.8581 | -2.6003 | -0.8419 | 4.7184 |  | 4.307 | 0.782 | 4.0037 | 3.3653 | 3.3363 | 1.0986 | 10.8007 | 14.2975 | 14.8846 | 11.1183 | -0.0002 | -0.0025 | 0.0012 | 0.0037 | 0.0012 | -0.0005 | 0.0328 | -0.0128 | -0.0231 | -360.2358 | 17.4048 | -360.4204 | 17.6451 | -360.7866 | 18.2036 | -360.8974 | 17.6102 | -352.6537 | 18.6881 | -352.586 | 16.8074
13:03 | 6170 | 51.1999 | 203.2228 | 449.7048 | 453.2356 | -16.4597 | -38.414 | 11.959 | 8.1429 | 2.781 | 1.0362 | 3.0016 | -1.2364 | 12.1591 | 5.2665 | 0.6267 | 0.6679 | 0.9712 | 0.7549 | -129.0357 | 2.4361 | 5.6826 | 1.8405 | -2.5632 | -0.8771 | 4.683 |  | 4.3117 | 0.7841 | 4.0028 | 3.3651 | 3.3308 | 1.0985 | 10.7811 | 14.2889 | 14.8324 | 11.1057 | -0.0001 | -0.003 | 0.001 | 0.0042 | 0.0005 | 0 | 0.0009 | 0.0049 | -0.0072 | -360.1835 | 17.4315 | -360.4912 | 17.6841 | -360.8604 | 18.1666 | -360.7958 | 17.5609 | -352.589 | 18.7169 | -352.6906 | 16.8464
13:03 | 6171 | 51.2127 | 203.3426 | 449.6374 | 453.2767 | -16.5029 | -38.4491 | 11.7907 | 8.1806 | 2.7424 | 0.9519 | 2.9746 | -1.2683 | 12.277 | 5.2513 | 0.6262 | 0.6689 | 0.9714 | 0.754 | -129.0908 | 2.3717 | 5.6457 | 1.8114 | -2.5633 | -0.9293 | 4.6752 |  | 4.3231 | 0.7452 | 4.0041 | 3.3679 | 3.3304 | 1.0993 | 10.7707 | 14.2613 | 14.858 | 11.0717 | 0 | -0.003 | 0.0008 | 0.0039 | 0.0009 | -0.0006 | 0.0101 | -0.0031 | -0.003 | -360.1742 | 17.3864 | -360.3958 | 17.6553 | -360.8266 | 18.2097 | -360.8881 | 17.602 | -352.626 | 18.6676 | -352.5706 | 16.8094
13:03 | 6172 | 51.1408 | 203.2857 | 449.5991 | 453.2582 | -16.4323 | -38.5444 | 11.8599 | 8.1229 | 2.7959 | 1.0138 | 3.0418 | -1.3119 | 12.2009 | 5.2478 | 0.6255 | 0.6674 | 0.9699 | 0.7553 | -129.1321 | 2.3699 | 5.6121 | 1.7908 | -2.6104 | -0.8602 | 4.6778 |  | 4.3623 | 0.7513 | 4.0054 | 3.3659 | 3.3336 | 1.0979 | 10.7904 | 14.2751 | 14.8481 | 11.0627 | 0.0001 | -0.0026 | 0.0007 | 0.0039 | 0.0008 | -0.0003 | 0.0343 | 0.0001 | -0.0173 | -360.2019 | 17.4459 | -360.4942 | 17.6615 | -360.805 | 18.1666 | -360.7804 | 17.5917 | -352.6475 | 18.723 | -352.6783 | 16.8176
13:03 | 6173 | 51.0494 | 203.3327 | 449.6762 | 453.2335 | -16.4009 | -38.4275 | 11.8611 | 8.0931 | 2.7564 | 1.0145 | 2.9995 | -1.2951 | 12.2923 | 5.3148 | 0.6249 | 0.6661 | 0.9681 | 0.7544 | -129.0739 | 2.3809 | 5.6552 | 1.8474 | -2.5892 | -0.9268 | 4.7795 |  | 4.3702 | 0.8422 | 4.0041 | 3.3662 | 3.3333 | 1.098 | 10.7823 | 14.2785 | 14.8685 | 11.101 | -0.0002 | -0.0029 | 0.001 | 0.0037 | 0.0013 | -0.0009 | 0.0133 | -0.006 | -0.013 | -360.1496 | 17.3843 | -360.4204 | 17.6677 | -360.8635 | 18.22 | -360.8512 | 17.5835 | -352.5521 | 18.6635 | -352.586 | 16.8402
13:03 | 6174 | 51.1201 | 203.3256 | 449.6955 | 453.2082 | -16.461 | -38.4867 | 11.8002 | 8.1447 | 2.6695 | 0.9977 | 3.0448 | -1.2905 | 12.2429 | 5.2969 | 0.6254 | 0.669 | 0.9673 | 0.7536 | -129.1265 | 2.3885 | 5.557 | 1.8453 | -2.5893 | -0.8652 | 4.8238 |  | 4.3263 | 0.6725 | 4.0043 | 3.3666 | 3.3328 | 1.0995 | 10.8029 | 14.271 | 14.8642 | 11.132 | 0.0005 | -0.0023 | 0.0009 | 0.0036 | 0.0007 | -0.0001 | 0 | -0.0217 | -0.0084 | -360.2265 | 17.4295 | -360.4419 | 17.6348 | -360.7712 | 18.1584 | -360.8266 | 17.5999 | -352.6475 | 18.723 | -352.629 | 16.7909
13:03 | 6175 | 51.1564 | 203.3438 | 449.6533 | 453.2832 | -16.4478 | -38.557 | 11.7693 | 8.1485 | 2.7362 | 1.0002 | 3.0774 | -1.2301 | 12.2286 | 5.2631 | 0.6257 | 0.6634 | 0.97 | 0.7553 | -129.1407 | 2.508 | 5.6346 | 1.7494 | -2.6241 | -0.8626 | 4.7527 |  | 4.3728 | 0.8396 | 4.004 | 3.3632 | 3.3333 | 1.0988 | 10.7903 | 14.2928 | 14.856 | 11.1197 | 0.0004 | -0.0028 | 0.001 | 0.0039 | 0.0013 | -0.0003 | 0.0245 | -0.0035 | -0.0026 | -360.1096 | 17.3987 | -360.4696 | 17.6923 | -360.8789 | 18.181 | -360.802 | 17.5568 | -352.5644 | 18.682 | -352.6721 | 16.8402
13:03 | 6176 | 51.1424 | 203.3267 | 449.7006 | 453.2805 | -16.5241 | -38.5292 | 11.9012 | 8.2366 | 2.7727 | 1.0065 | 3.0776 | -1.2593 | 12.216 | 5.2912 | 0.626 | 0.669 | 0.9704 | 0.7562 | -129.0236 | 2.5027 | 5.6085 | 1.8732 | -2.5651 | -0.9583 | 4.7045 |  | 4.3533 | 0.8643 | 4.0052 | 3.3644 | 3.3333 | 1.0996 | 10.8204 | 14.2997 | 14.8979 | 11.0977 | 0 | -0.0029 | 0.0012 | 0.0041 | 0.0007 | -0.0003 | 0.0025 | -0.0158 | -0.0086 | -360.2081 | 17.4028 | -360.4266 | 17.6266 | -360.762 | 18.1789 | -360.8358 | 17.5958 | -352.6229 | 18.684 | -352.5952 | 16.795
13:03 | 6177 | 51.221 | 203.2882 | 449.6886 | 453.2157 | -16.4808 | -38.5124 | 11.9521 | 8.2155 | 2.7837 | 1.0675 | 3.1469 | -1.1925 | 12.2722 | 5.2493 | 0.6252 | 0.6663 | 0.9674 | 0.7558 | -129.1242 | 2.3296 | 5.5442 | 1.8928 | -2.6203 | -1.0548 | 4.7265 |  | 4.3603 | 0.9057 | 4.0044 | 3.3635 | 3.3309 | 1.0984 | 10.818 | 14.3092 | 14.8973 | 11.1352 | 0 | -0.0024 | 0.001 | 0.0039 | 0.001 | -0.0007 | 0.0218 | -0.0055 | 0.0061 | -360.1435 | 17.4131 | -360.4942 | 17.6882 | -360.8389 | 18.1584 | -360.762 | 17.5568 | -352.6013 | 18.7004 | -352.6475 | 16.8402
13:03 | 6178 | 51.238 | 203.2293 | 449.6124 | 453.2205 | -16.4492 | -38.5151 | 11.9673 | 8.158 | 2.7579 | 0.9733 | 3.0185 | -1.1919 | 12.2335 | 5.3182 | 0.6243 | 0.6663 | 0.9689 | 0.7563 | -129.0742 | 2.2837 | 5.5614 | 1.6684 | -2.6304 | -1.1115 | 4.6477 |  | 4.4244 | 0.8422 | 4.0051 | 3.3648 | 3.3274 | 1.0986 | 10.7776 | 14.2742 | 14.8488 | 11.1186 | -0.0005 | -0.0028 | 0.0011 | 0.0048 | 0.0006 | -0.0003 | 0.0174 | -0.0203 | -0.0039 | -360.1527 | 17.3802 | -360.4081 | 17.6471 | -360.7958 | 18.1994 | -360.8727 | 17.5876 | -352.6013 | 18.6676 | -352.5675 | 16.8012
13:03 | 6179 | 51.2512 | 203.2642 | 449.71 | 453.2088 | -16.5057 | -38.5302 | 11.9126 | 8.189 | 2.7957 | 0.9175 | 3.1051 | -1.1609 | 12.2415 | 5.2376 | 0.6259 | 0.6642 | 0.9688 | 0.756 | -129.0474 | 2.3823 | 5.6413 | 1.7064 | -2.6472 | -1.0353 | 4.6779 |  | 4.331 | 0.7644 | 4.0045 | 3.3681 | 3.3308 | 1.0991 | 10.7868 | 14.2487 | 14.8577 | 11.1107 | 0.0004 | -0.0029 | 0.0008 | 0.004 | 0.0008 | -0.0006 | 0.0063 | -0.0027 | -0.0139 | -360.1988 | 17.4336 | -360.4727 | 17.6594 | -360.7866 | 18.1543 | -360.765 | 17.5835 | -352.6136 | 18.721 | -352.6475 | 16.8115
13:03 | 6180 | 51.2044 | 203.2177 | 449.6779 | 453.2621 | -16.463 | -38.3955 | 11.9099 | 8.2461 | 2.8321 | 0.8617 | 3.1002 | -1.1283 | 12.2435 | 5.2133 | 0.6264 | 0.6664 | 0.972 | 0.7557 | -129.0458 | 2.4743 | 5.7695 | 1.7423 | -2.7469 | -0.9898 | 4.6813 |  | 4.3275 | 0.7549 | 4.0042 | 3.3665 | 3.3322 | 1.0982 | 10.7686 | 14.2468 | 14.8105 | 11.0595 | -0.0001 | -0.0034 | 0.0003 | 0.0035 | 0.0008 | -0.0004 | 0.0106 | -0.0133 | -0.0135 | -360.1496 | 17.3987 | -360.4296 | 17.6677 | -360.8481 | 18.1994 | -360.8574 | 17.5773 | -352.586 | 18.6676 | -352.6044 | 16.8217
13:03 | 6181 | 51.242 | 203.2096 | 449.7109 | 453.3219 | -16.4992 | -38.4326 | 11.8949 | 8.2865 | 2.8566 | 0.8442 | 3.1039 | -1.1498 | 12.1904 | 5.2504 | 0.6256 | 0.6668 | 0.9683 | 0.7553 | -129.05 | 2.473 | 5.7999 | 1.766 | -2.6262 | -1.0182 | 4.7231 |  | 4.3295 | 0.779 | 4.0048 | 3.367 | 3.3341 | 1.0971 | 10.773 | 14.2579 | 14.8607 | 11.0854 | -0.0003 | -0.0026 | 0.0008 | 0.0036 | 0.0006 | -0.0007 | 0.0228 | -0.0239 | -0.014 | -360.2173 | 17.4274 | -360.4696 | 17.6636 | -360.7897 | 18.1625 | -360.845 | 17.5999 | -352.6321 | 18.723 | -352.6383 | 16.8156
13:03 | 6182 | 51.2188 | 203.2847 | 449.7996 | 453.3418 | -16.5045 | -38.4735 | 11.918 | 8.277 | 2.8367 | 1.0903 | 3.1306 | -1.2389 | 12.1553 | 5.158 | 0.6257 | 0.6654 | 0.9698 | 0.7557 | -129.076 | 2.4028 | 5.8022 | 1.8381 | -2.5839 | -0.9282 | 4.7386 |  | 4.317 | 0.6874 | 4.0056 | 3.3675 | 3.3321 | 1.0987 | 10.7903 | 14.281 | 14.8549 | 11.0681 | -0.0002 | -0.0026 | 0.0015 | 0.0042 | 0.0009 | -0.0008 | 0.0251 | -0.011 | -0.0211 | -360.1342 | 17.4007 | -360.4512 | 17.6718 | -360.8358 | 18.2097 | -360.8389 | 17.5958 | -352.589 | 18.6779 | -352.6506 | 16.8238
13:03 | 6183 | 51.2638 | 203.2603 | 449.7476 | 453.3406 | -16.5984 | -38.5556 | 11.7978 | 8.3013 | 2.8647 | 1.027 | 3.1318 | -1.3235 | 12.1922 | 5.1758 | 0.6267 | 0.6678 | 0.968 | 0.7548 | -128.9333 | 2.5015 | 5.8584 | 1.8531 | -2.5794 | -0.9025 | 4.7307 |  | 4.3051 | 0.7856 | 4.0038 | 3.3726 | 3.3309 | 1.1001 | 10.7833 | 14.2802 | 14.8557 | 11.1183 | 0.0003 | -0.0028 | 0.001 | 0.0037 | 0.0011 | 0.0004 | -0.0009 | -0.0036 | 0.0152 | -360.2265 | 17.4377 | -360.4573 | 17.6594 | -360.802 | 18.181 | -360.8204 | 17.5958 | -352.629 | 18.7128 | -352.6537 | 16.8279
13:03 | 6184 | 51.164 | 203.1781 | 449.6544 | 453.2846 | -16.528 | -38.512 | 11.8758 | 8.2712 | 2.8531 | 0.9829 | 3.0894 | -1.2368 | 12.2129 | 5.1644 | 0.6271 | 0.6687 | 0.9693 | 0.7549 | -129.0079 | 2.4319 | 5.8234 | 1.7618 | -2.6368 | -0.9795 | 4.6138 |  | 4.3462 | 0.8365 | 4.003 | 3.3647 | 3.3277 | 1.0985 | 10.7809 | 14.307 | 14.8551 | 11.0865 | 0.0005 | -0.003 | 0.0014 | 0.0044 | 0.0012 | -0.0004 | 0.003 | -0.0083 | -0.0198 | -360.1865 | 17.411 | -360.4266 | 17.6656 | -360.845 | 18.1933 | -360.8297 | 17.5958 | -352.6198 | 18.6922 | -352.6321 | 16.8217
13:03 | 6185 | 51.2391 | 203.2792 | 449.7416 | 453.2713 | -16.5046 | -38.4098 | 11.8524 | 8.3295 | 2.8368 | 0.8931 | 3.1439 | -1.2024 | 12.2507 | 5.1464 | 0.6271 | 0.6686 | 0.9687 | 0.7558 | -129.0038 | 2.4317 | 5.7886 | 1.7252 | -2.7005 | -1.0354 | 4.6051 |  | 4.3377 | 0.7874 | 4.0029 | 3.3644 | 3.3295 | 1.098 | 10.8318 | 14.3 | 14.8826 | 11.1316 | -0.0004 | -0.0026 | 0.0009 | 0.0041 | 0.0005 | 0.0004 | 0.0139 | 0.0005 | 0.0065 | -360.1896 | 17.4192 | -360.4666 | 17.6656 | -360.7989 | 18.1871 | -360.8174 | 17.5958 | -352.6167 | 18.7087 | -352.6321 | 16.8176
13:03 | 6186 | 51.2716 | 203.3321 | 449.8053 | 453.3144 | -16.4216 | -38.4052 | 11.9844 | 8.3482 | 2.9117 | 0.7707 | 3.1797 | -1.2388 | 12.2601 | 5.2209 | 0.6253 | 0.6683 | 0.9667 | 0.7536 | -129.0439 | 2.3485 | 5.7197 | 1.527 | -2.6866 | -1.018 | 4.5804 |  | 4.3261 | 0.7452 | 4.0041 | 3.3672 | 3.3332 | 1.0979 | 10.7902 | 14.2987 | 14.8802 | 11.1367 | -0.0002 | -0.0028 | 0.0006 | 0.004 | 0.0008 | -0.0009 | 0.02 | -0.0042 | -0.0343 | -360.2019 | 17.4131 | -360.4481 | 17.6718 | -360.8204 | 18.1851 | -360.845 | 17.5896 | -352.5706 | 18.7025 | -352.6475 | 16.8176
13:03 | 6187 | 51.3214 | 203.2609 | 449.7275 | 453.3522 | -16.5277 | -38.5054 | 11.9451 | 8.3608 | 2.9075 | 0.8687 | 3.1968 | -1.2224 | 12.2234 | 5.1982 | 0.6252 | 0.6676 | 0.9661 | 0.7541 | -129.0525 | 2.4719 | 5.7607 | 1.5535 | -2.6244 | -1.042 | 4.6339 |  | 4.3549 | 0.8152 | 4.0051 | 3.3667 | 3.3302 | 1.0986 | 10.7695 | 14.2718 | 14.8461 | 11.0818 | 0.0002 | -0.003 | 0.0012 | 0.0045 | 0.0003 | -0.0005 | 0.0075 | -0.0005 | -0.0313 | -360.1865 | 17.409 | -360.4604 | 17.6594 | -360.8389 | 18.1974 | -360.842 | 17.5855 | -352.6044 | 18.7025 | -352.6167 | 16.8217
13:03 | 6188 | 51.2407 | 203.2272 | 449.7972 | 453.3666 | -16.466 | -38.5234 | 11.9172 | 8.3036 | 2.8684 | 0.8269 | 3.1069 | -1.2813 | 12.2584 | 5.2177 | 0.6253 | 0.6672 | 0.9683 | 0.7534 | -129.0231 | 2.5311 | 5.7916 | 1.6373 | -2.601 | -1.0558 | 4.6697 |  | 4.3213 | 0.7462 | 4.0056 | 3.3648 | 3.333 | 1.0983 | 10.8019 | 14.2868 | 14.8665 | 11.0912 | 0 | -0.0029 | 0.0007 | 0.0038 | 0.0008 | -0.0007 | 0.0135 | -0.0094 | -0.013 | -360.165 | 17.4172 | -360.4666 | 17.6615 | -360.8266 | 18.1851 | -360.8112 | 17.5814 | -352.5983 | 18.7087 | -352.6413 | 16.8176
13:03 | 6189 | 51.3223 | 203.2776 | 449.7585 | 453.4248 | -16.4844 | -38.41 | 11.9133 | 8.3064 | 2.8499 | 0.8844 | 3.092 | -1.261 | 12.2721 | 5.3021 | 0.6271 | 0.6674 | 0.969 | 0.7549 | -129.0599 | 2.512 | 5.8349 | 1.6988 | -2.6865 | -1.0334 | 4.6436 |  | 4.3402 | 0.9377 | 4.0032 | 3.3641 | 3.3331 | 1.0969 | 10.7834 | 14.2799 | 14.8362 | 11.0843 | 0.0002 | -0.0028 | 0.0007 | 0.0036 | 0.0004 | -0.0005 | 0.0042 | -0.0196 | -0.0134 | -360.1773 | 17.4069 | -360.4419 | 17.6636 | -360.845 | 18.1994 | -360.8604 | 17.5896 | -352.6075 | 18.6881 | -352.6198 | 16.8217
13:03 | 6190 | 51.3914 | 203.3299 | 449.7707 | 453.3914 | -16.5101 | -38.3265 | 11.9545 | 8.1911 | 2.8696 | 0.7682 | 3.0502 | -1.3011 | 12.2271 | 5.252 | 0.6259 | 0.6689 | 0.9695 | 0.7551 | -128.9943 | 2.5142 | 5.866 | 1.4808 | -2.659 | -1.0472 | 4.6929 |  | 4.3107 | 0.7896 | 4.0041 | 3.3655 | 3.3334 | 1.0973 | 10.7764 | 14.2501 | 14.8717 | 11.0883 | -0.0003 | -0.0026 | 0.0013 | 0.0039 | 0.0009 | -0.0005 | 0.0174 | -0.0201 | -0.0024 | -360.2235 | 17.4295 | -360.4604 | 17.6492 | -360.7927 | 18.183 | -360.8327 | 17.5835 | -352.6167 | 18.7066 | -352.6229 | 16.8156
13:03 | 6191 | 51.2918 | 203.1601 | 449.6639 | 453.2712 | -16.4133 | -38.4728 | 11.9809 | 8.2247 | 2.8383 | 0.7772 | 3.031 | -1.2487 | 12.1729 | 5.2078 | 0.6259 | 0.667 | 0.9687 | 0.7546 | -129.0165 | 2.4008 | 5.8777 | 1.5213 | -2.6731 | -1.0993 | 4.6224 |  | 4.2986 | 0.7664 | 4.0054 | 3.3646 | 3.332 | 1.0986 | 10.7776 | 14.28 | 14.8315 | 11.0724 | 0.0003 | -0.0028 | 0.001 | 0.0038 | 0.0009 | -0.0002 | 0.0189 | -0.0045 | -0.0124 | -360.1404 | 17.3925 | -360.4419 | 17.6656 | -360.842 | 18.1912 | -360.802 | 17.5629 | -352.5521 | 18.6779 | -352.6075 | 16.8299
13:03 | 6192 | 51.2682 | 203.1688 | 449.6808 | 453.4398 | -16.3767 | -38.3688 | 11.8774 | 8.285 | 2.8382 | 0.8343 | 3.0791 | -1.2879 | 12.1702 | 5.1873 | 0.6238 | 0.6679 | 0.9676 | 0.7538 | -129.0378 | 2.5586 | 5.8617 | 1.5158 | -2.6517 | -1.0199 | 4.599 |  | 4.2291 | 0.6826 | 4.0028 | 3.3645 | 3.3318 | 1.0976 | 10.788 | 14.2613 | 14.8464 | 11.1006 | 0.0004 | -0.003 | 0.0008 | 0.004 | 0.0009 | -0.0004 | 0.0186 | 0.0027 | -0.0017 | -360.1958 | 17.4028 | -360.4204 | 17.6163 | -360.7435 | 18.1707 | -360.8327 | 17.5917 | -352.629 | 18.6922 | -352.586 | 16.7889
13:03 | 6193 | 51.2636 | 203.1952 | 449.7532 | 453.4187 | -16.4612 | -38.3926 | 11.8789 | 8.2363 | 2.8314 | 0.8632 | 3.0682 | -1.2388 | 12.254 | 5.1044 | 0.6264 | 0.6684 | 0.9687 | 0.7545 | -129.0368 | 2.4701 | 5.7325 | 1.5728 | -2.5207 | -0.8843 | 4.6631 |  | 4.2272 | 0.7258 | 4.005 | 3.3655 | 3.3304 | 1.0985 | 10.7995 | 14.3023 | 14.8612 | 11.111 | -0.0002 | -0.0025 | 0.0008 | 0.004 | 0.001 | -0.0002 | 0.0069 | -0.0008 | -0.0092 | -360.1127 | 17.3864 | -360.445 | 17.6677 | -360.8235 | 18.1769 | -360.7804 | 17.5506 | -352.5583 | 18.6737 | -352.5952 | 16.8402
13:03 | 6194 | 51.3204 | 203.1946 | 449.765 | 453.4573 | -16.4636 | -38.4667 | 11.8607 | 8.3219 | 2.8672 | 0.8741 | 3.1703 | -1.2849 | 12.2176 | 5.1452 | 0.6271 | 0.6673 | 0.97 | 0.7539 | -129.0538 | 2.4676 | 5.8057 | 1.5278 | -2.6439 | -0.9704 | 4.6198 |  | 4.2346 | 0.773 | 4.0051 | 3.3676 | 3.3382 | 1.0986 | 10.8007 | 14.3091 | 14.873 | 11.1356 | -0.0004 | -0.0025 | 0.0006 | 0.0042 | 0.0012 | -0.0001 | 0.0051 | -0.0056 | -0.0037 | -360.1773 | 17.3987 | -360.3896 | 17.6102 | -360.762 | 18.1604 | -360.8235 | 17.5999 | -352.5921 | 18.6779 | -352.5644 | 16.7889
13:03 | 6195 | 51.2609 | 203.2898 | 449.7656 | 453.465 | -16.3782 | -38.4373 | 11.8959 | 8.3036 | 2.8981 | 0.9066 | 3.24 | -1.3045 | 12.1952 | 5.1758 | 0.6259 | 0.6724 | 0.971 | 0.755 | -129.1198 | 2.447 | 5.8146 | 1.4492 | -2.586 | -0.9769 | 4.606 |  | 4.2364 | 0.7415 | 4.0044 | 3.3639 | 3.3338 | 1.0982 | 10.7649 | 14.2727 | 14.8337 | 11.0952 | 0.0001 | -0.0029 | 0.0008 | 0.004 | 0.001 | -0.0007 | 0.0133 | 0.0089 | -0.0188 | -360.1404 | 17.3946 | -360.4573 | 17.6533 | -360.805 | 18.1666 | -360.765 | 17.5445 | -352.5736 | 18.6902 | -352.6413 | 16.8238
13:03 | 6196 | 51.3256 | 203.2777 | 449.7734 | 453.4381 | -16.4268 | -38.4285 | 11.803 | 8.2289 | 2.8086 | 0.9437 | 3.2506 | -1.2557 | 12.2734 | 5.2338 | 0.6258 | 0.6695 | 0.9665 | 0.7545 | -129.0408 | 2.4139 | 5.7235 | 1.488 | -2.5414 | -0.8771 | 4.7342 |  | 4.1778 | 0.838 | 4.0039 | 3.3662 | 3.33 | 1.0998 | 10.7787 | 14.287 | 14.8676 | 11.1139 | 0.0002 | -0.003 | 0.0005 | 0.0034 | 0.0007 | -0.0002 | 0.0103 | -0.0145 | -0.0037 | -360.1496 | 17.3597 | -360.3496 | 17.6184 | -360.7712 | 18.1851 | -360.8389 | 17.5814 | -352.5921 | 18.6614 | -352.5306 | 16.7909
13:03 | 6197 | 51.3873 | 203.2229 | 449.7227 | 453.4647 | -16.4194 | -38.4429 | 11.8953 | 8.2244 | 2.8323 | 0.9728 | 3.2159 | -1.1628 | 12.2594 | 5.3542 | 0.6278 | 0.6708 | 0.9688 | 0.7546 | -129.0393 | 2.4001 | 5.7915 | 1.6018 | -2.6068 | -0.8764 | 4.6537 |  | 4.2149 | 0.7772 | 4.0053 | 3.3654 | 3.3369 | 1.0981 | 10.7581 | 14.2539 | 14.8129 | 11.0891 | -0.0002 | -0.0029 | 0.0007 | 0.0041 | 0.0007 | -0.0009 | 0.007 | -0.0065 | -0.0027 | -360.1496 | 17.4274 | -360.4419 | 17.6533 | -360.7773 | 18.1399 | -360.765 | 17.5671 | -352.5829 | 18.7107 | -352.629 | 16.8176
13:03 | 6198 | 51.4098 | 203.2556 | 449.7041 | 453.4457 | -16.5223 | -38.4965 | 11.872 | 8.1853 | 2.8323 | 0.8717 | 3.2036 | -1.1318 | 12.2963 | 5.3592 | 0.6285 | 0.6672 | 0.9703 | 0.7556 | -129.0352 | 2.4397 | 5.8238 | 1.5355 | -2.577 | -0.9106 | 4.7022 |  | 4.2197 | 0.6478 | 4.0046 | 3.3646 | 3.3316 | 1.0991 | 10.788 | 14.2904 | 14.8359 | 11.1175 | -0.0004 | -0.0025 | 0.0014 | 0.0042 | 0.0005 | -0.0005 | 0.0015 | -0.0108 | -0.0096 | -360.1281 | 17.3638 | -360.3619 | 17.6389 | -360.7989 | 18.2159 | -360.8481 | 17.5855 | -352.5829 | 18.6594 | -352.5798 | 16.8156
13:03 | 6199 | 51.2947 | 203.2519 | 449.6504 | 453.4426 | -16.5615 | -38.428 | 11.8494 | 8.2143 | 2.865 | 0.9663 | 3.1924 | -1.2638 | 12.1084 | 5.1837 | 0.6261 | 0.6696 | 0.9721 | 0.7536 | -129.0396 | 2.4149 | 5.817 | 1.6001 | -2.5608 | -0.9658 | 4.6758 |  | 4.2562 | 0.6872 | 4.0055 | 3.3673 | 3.3323 | 1.0995 | 10.8053 | 14.2732 | 14.8717 | 11.1056 | 0.0002 | -0.0029 | 0.0014 | 0.0041 | 0.0012 | -0.0006 | 0.0162 | -0.0086 | -0.0212 | -360.2204 | 17.4336 | -360.4666 | 17.643 | -360.7497 | 18.1502 | -360.7866 | 17.5917 | -352.6783 | 18.7271 | -352.666 | 16.8094
Note on A2: Ramesh, Selvarajah (IntlAssoc): Mechanical Load Increase
Note on A401: Ramesh, Selvarajah (IntlAssoc): Mechanical Load Constant
Note on A6201: Ramesh, Selvarajah (IntlAssoc): End of Ambient Load DATA file

## CB-DA-SC-FireLoadingData
Time (Date:1/12/2018 ) | Test Time (s) | SGW2 (microstrain) | ColW1 (microstrain) | ColW2 (microstrain) | ColW3 (microstrain) | ColW4 (microstrain) | ColW5 (microstrain) | ColW6 (microstrain) | ColW7 (microstrain) | ColW8 (microstrain) | LCW1 (kN) | LCW2 (kN) | LCW3 (kN) | LCW4 (kN) | SGE1 (microstrain) | SGE2 (microstrain) | ColE1 (microstrain) | ColE2 (microstrain) | ColE3 (microstrain) | ColE4 (microstrain) | ColE5 (microstrain) | ColE6 (microstrain) | ColE7 (microstrain) | ColE8 (microstrain) | LCE1 (kN) | LCE2 (kN) | LCE3 (kN) | LCE4 (kN) | HeatFlux_Gardon (kW/m2) | TCE_1 (°C) | TCE_2 (°C) | TCE_4 (°C) | TCE_5 (°C) | TCE_6 (°C) | TCE_8 (°C) | TCE_9 (°C) | TC6_21 (°C) | TC8_2 (°C) | TC8_3 (°C) | TC8_4 (°C) | TC8_5 (°C) | TC6_22 (°C) | TC8_7 (°C) | TC8_8 (°C) | TC8_9 (°C) | TC8_10 (°C) | TC8_11 (°C) | TC8_12 (°C) | TC8_13 (°C) | TC8_14 (°C) | TC8_15 (°C) | TC6_23 (°C) | TC8_17 (°C) | TC8_18 (°C) | TC8_19 (°C) | TC8_20 (°C) | TC5_21 (°C) | TC7_2 (°C) | TC7_3 (°C) | TC7_4 (°C) | TC7_5 (°C) | TC5_22 (°C) | TC7_7 (°C) | TC7_8 (°C) | TC7_9 (°C) | TC7_10 (°C) | TC7_11 (°C) | TC7_12 (°C) | TC7_13 (°C) | TC7_15 (°C) | TC5_23 (°C) | TC7_17 (°C) | TC7_18 (°C) | TC7_19 (°C) | TC7_20 (°C) | TC6_1 (°C) | TC6_2 (°C) | TC6_3 (°C) | TC6_4 (°C) | TC6_5 (°C) | TC6_6 (°C) | TC6_7 (°C) | TC6_8 (°C) | TC6_9 (°C) | TC6_10 (°C) | TC6_11 (°C) | TC6_12 (°C) | TC6_13 (°C) | TC6_14 (°C) | TC6_15 (°C) | TC6_16 (°C) | TC6_17 (°C) | TC6_18 (°C) | TC6_19 (°C) | TC6_20 (°C) | TC5_1 (°C) | TC5_2 (°C) | TC5_3 (°C) | TC5_4 (°C) | TC5_5 (°C) | TC5_6 (°C) | TC5_7 (°C) | TC5_8 (°C) | TC5_9 (°C) | TC5_10 (°C) | TC5_11 (°C) | TC5_12 (°C) | TC5_13 (°C) | TC5_14 (°C) | TC5_16 (°C) | TC5_17 (°C) | TC5_18 (°C) | TC5_19 (°C) | TC5_20 (°C) | TC6_26 (°C) | TC6_25 (°C) | TC5_26 (°C) | TC5_25 (°C) | TCC5 (°C) | TCC6 (°C) | TCC11 (°C) | TCC12 (°C) | TCC13 (°C) | TCC14 (°C) | TCC17 (°C) | TCC18 (°C) | TCC19 (°C) | TCC20 (°C) | TCC21 (°C) | TCC22 (°C) | TCC23 (°C) | TCC24 (°C) | TCC25 (°C) | TCC26 (°C) | TCC27 (°C) | TCC28 (°C) | TCW_1 (°C) | TCW_2 (°C) | TCW_3 (°C) | TCW_4 (°C) | TCW_5 (°C) | TCW_6 (°C) | TCW_7 (°C) | TCW_8 (°C) | TCW_9 (°C) | TC3_21 (°C) | TC1_2 (°C) | TC1_4 (°C) | TC1_5 (°C) | TC3_22 (°C) | TC1_7 (°C) | TC1_8 (°C) | TC1_9 (°C) | TC1_10 (°C) | TC1_11 (°C) | TC1_12 (°C) | TC1_13 (°C) | TC1_14 (°C) | TC1_15 (°C) | TC3_23 (°C) | TC1_17 (°C) | TC1_18 (°C) | TC1_19 (°C) | TC1_20 (°C) | TC4_21 (°C) | TC2_2 (°C) | TC2_4 (°C) | TC2_5 (°C) | TC4_22 (°C) | TC2_7 (°C) | TC2_8 (°C) | TC2_9 (°C) | TC2_10 (°C) | TC2_12 (°C) | TC2_13 (°C) | TC2_14 (°C) | TC2_15 (°C) | TC4_23 (°C) | TC2_17 (°C) | TC2_18 (°C) | TC2_19 (°C) | TC2_20 (°C) | TC3_1 (°C) | TC3_2 (°C) | TC3_3 (°C) | TC3_4 (°C) | TC3_5 (°C) | TC3_6 (°C) | TC3_7 (°C) | TC3_8 (°C) | TC3_9 (°C) | TC3_10 (°C) | TC3_11 (°C) | TC3_12 (°C) | TC3_13 (°C) | TC3_14 (°C) | TC3_15 (°C) | TC3_16 (°C) | TC3_17 (°C) | TC3_18 (°C) | TC3_19 (°C) | TC3_20 (°C) | TC4_1 (°C) | TC4_2 (°C) | TC4_3 (°C) | TC4_4 (°C) | TC4_5 (°C) | TC4_6 (°C) | TC4_7 (°C) | TC4_8 (°C) | TC4_9 (°C) | TC4_10 (°C) | TC4_11 (°C) | TC4_12 (°C) | TC4_14 (°C) | TC4_15 (°C) | TC4_16 (°C) | TC4_17 (°C) | TC4_18 (°C) | TC4_19 (°C) | TC4_20 (°C) | TC3_26 (°C) | TC3_25 (°C) | TC4_26 (°C) | TC4_25 (°C) | TCC1 (°C) | TCC7 (°C) | TCC8 (°C) | TCC9 (°C) | TCC10 (°C) | TCC15 (°C) | TCC16 (°C) | TCC3 (°C) | TCC4 (°C) | TCC2 (°C) | RotMTemp (°C) | FBGTopTemp (°C) | FBGBotTemp (°C) | STC1 (°C) | STC2 (°C) | STC3 (°C) | STC4 (°C) | VD2 (mm) | VD3 (mm) | VD4 (mm) | VD5 (mm) | RotSlabWx (rad) | RotSlabWy (rad) | RotSlabEx (rad) | RotSlabEy (rad) | RotSlabMx (rad) | RotSlabMy (rad) | RotLT1 (rad) | RotLT2 (rad) | RotLT3 (rad) | DispNE (mm) | LoadNE (kN) | DispSE (mm) | LoadSE (kN) | DispNW (mm) | LoadNW (kN) | DispSW (mm) | LoadSW (kN) | DispNM (mm) | LoadNM (kN) | DispSM (mm) | LoadSM (kN) | HRR (kW) | HRRburner (kW) | AvgULT (°C) | AvgVDMidspan (mm) | AvgAxialLoad (kN) | AvgBeamTemp (°C)
13:26 | 0 | 36.1416 |  | 8.6637 | 3.551 | 1.146 | 3.3057 | -1.5931 | 12.4722 | 5.5064 | 0.6328 | 0.6755 | 0.9788 | 0.7663 | -128.7969 | 4.9034 | 6.4925 | 1.784 | -2.286 | -0.8751 | 5.1174 |  | 4.9958 | 0.9338 | 3.9923 | 3.3665 | 3.3311 | 1.1061 | -0.5439 | 22.7563 | 22.6256 | 22.4021 | 22.3857 | 22.3026 | 22.2949 | 22.1654 | 22.9541 | 22.6686 | 22.71 | 22.7042 | 22.6893 | 23.0323 | 22.949 | 22.9221 | 22.8091 | 22.696 | 22.6237 | 22.506 | 22.4045 | 22.3296 | 22.2841 | 22.9464 | 22.5768 | 22.6121 | 22.5992 | 22.6011 | 23.1891 | 22.7096 | 22.9228 | 23.0798 | 22.9943 | 23.5204 | 22.8983 | 22.9336 | 22.8989 | 22.8355 | 22.6975 | 22.5896 | 22.4264 | 22.2642 | 23.2627 | 22.6609 | 22.752 | 22.9381 | 23.2814 | 23.3319 | 23.2795 | 23.279 | 23.2184 | 23.1847 | 23.0658 | 23.0733 | 23.113 | 23.0745 | 22.9942 | 22.9017 | 22.7729 | 22.6978 | 22.7008 | 22.8193 | 23.17 | 23.1928 | 23.1629 | 23.0864 | 23.0187 | 23.832 | 23.7271 | 23.739 | 23.6722 | 23.6291 | 23.3091 | 23.3808 | 23.3962 | 23.3522 | 23.3513 | 23.3761 | 23.2657 | 22.978 | 22.7885 | 23.3253 | 23.3708 | 23.3435 | 23.312 | 23.2689 | 23.372 | 23.521 | 22.8368 | 22.8676 | 21.908 | 21.9191 | 23.2492 | 22.7833 | 23.2137 | 22.8492 | 22.2318 | 21.6235 | 21.6266 | 21.3794 | 21.4747 | 21.3006 | 21.0478 | 21.2527 | 21.3884 | 21.555 | 21.2511 | 21.1498 | 22.635 | 22.5161 | 25.3202 | 22.3211 | 22.3048 | 22.2373 | 22.1982 | 22.1235 | 22.2086 | 23.2111 | 22.5543 | 22.4715 | 22.5152 | 22.5144 | 22.7709 | 23.0161 | 22.9227 | 22.8652 | 22.7676 | 22.6726 | 22.6407 | 22.614 | 22.5666 | 23.6844 | 22.7684 | 22.766 | 23.789 | 22.7191 | 23.811 | 22.923 | 23.076 | 23.0307 | 23.909 | 22.9604 | 22.9971 | 22.9793 | 22.9411 | 22.7898 | 22.7033 | 22.6254 | 22.545 | 23.6654 | 22.6477 | 22.7587 | 23.0259 | 23.2235 | 23.8734 | 23.8287 | 23.7467 | 23.6771 | 23.6224 | 23.813 | 23.7801 | 23.6915 | 23.6206 | 23.4893 | 23.322 | 23.0726 | 22.9173 | 22.8599 | 22.9273 | 23.6998 | 23.6218 | 23.5774 | 23.5154 | 23.4809 | 24.1601 | 24.0767 | 23.9565 | 23.8676 | 23.7599 | 23.6416 | 23.8674 | 23.802 | 23.7266 | 23.6708 | 23.6037 | 23.5969 | 23.0714 | 22.9801 | 24.1244 | 24.0393 | 24.0341 | 23.9815 | 23.9628 | 23.4636 | 23.579 | 23.8187 | 23.806 | 22.2392 | 22.3338 | 22.3412 | 23.4311 | 22.8642 | 23.3727 |  | 21.507 | 21.3854 | 21.8689 | 24.7089 | 23.4365 | 23.4613 | 22.5098 | 22.5031 | 21.6158 | 22.2353 | 10.8334 | 14.2806 | 14.8955 | 11.1047 | 0.00047059 | -0.0028953 | 0.0015299 | 0.0040406 | 0.0015561 | -0.00058586 | 0.02143 | 0.0018359 | -0.033739 | -360.1681 | 17.3782 | -360.3681 | 17.602 | -360.7681 | 18.2097 | -360.8481 | 17.5753 | -352.589 | 18.6779 | -352.5675 | 16.7868 | 14.7287 | -0.1731 | 21.9378 | 14.588 | 12.8165 | 22.0594
13:26 | 1 | 36.1553 |  | 8.618 | 3.5274 | 1.0195 | 3.2585 | -1.5677 | 12.623 | 5.5483 | 0.6338 | 0.6776 | 0.984 | 0.7688 | -128.8463 | 4.9075 | 6.496 | 1.8251 | -2.3427 | -0.8454 | 5.0681 |  | 4.9419 | 1.0015 | 3.9914 | 3.3628 | 3.3301 | 1.1051 | -1.1936 | 22.7605 | 22.6222 | 22.4012 | 22.3794 | 22.3068 | 22.2901 | 22.1609 | 22.952 | 22.6639 | 22.7112 | 22.6983 | 22.6898 | 23.033 | 22.9484 | 22.9159 | 22.8048 | 22.6938 | 22.6182 | 22.503 | 22.4017 | 22.3223 | 22.2801 | 22.9435 | 22.5695 | 22.6029 | 22.5967 | 22.5926 | 23.1826 | 22.6998 | 22.9224 | 23.078 | 22.9949 | 23.5174 | 22.8964 | 22.9339 | 22.8942 | 22.8374 | 22.6985 | 22.5895 | 22.4265 | 22.2596 | 23.2618 | 22.6539 | 22.7478 | 22.9339 | 23.2856 | 23.3305 | 23.2784 | 23.2781 | 23.2207 | 23.1853 | 23.0689 | 23.0735 | 23.1129 | 23.0743 | 22.9954 | 22.9025 | 22.7723 | 22.6955 | 22.7007 | 22.8194 | 23.1676 | 23.1953 | 23.163 | 23.0876 | 23.0244 | 23.8315 | 23.7269 | 23.7376 | 23.6719 | 23.6313 | 23.3095 | 23.3785 | 23.3927 | 23.3549 | 23.3519 | 23.3774 | 23.2673 | 22.9759 | 22.7904 | 23.3224 | 23.3716 | 23.344 | 23.3092 | 23.2645 | 23.3718 | 23.5158 | 22.8356 | 22.8661 | 21.9138 | 21.92 | 23.2525 | 22.7865 | 23.2178 | 22.8545 | 22.1776 | 21.6611 | 21.5834 | 21.3576 | 21.4456 | 21.2957 | 21.0411 | 21.236 | 21.3904 | 21.5515 | 21.2583 | 21.1481 | 22.6372 | 22.5174 | 25.2958 | 22.3246 | 22.3119 | 22.2317 | 22.2015 | 22.1246 | 22.2127 | 23.215 | 22.5501 | 22.4697 | 22.5171 | 22.5181 | 22.7745 | 23.0205 | 22.9221 | 22.8699 | 22.7679 | 22.6732 | 22.646 | 22.6152 | 22.5738 | 23.6898 | 22.7662 | 22.7667 | 23.7922 | 22.7256 | 23.8161 | 22.9304 | 23.0709 | 23.0269 | 23.9051 | 22.9552 | 23.0052 | 22.975 | 22.9368 | 22.7892 | 22.7013 | 22.6244 | 22.5446 | 23.6635 | 22.6496 | 22.7628 | 23.0254 | 23.2199 | 23.8677 | 23.8265 | 23.7394 | 23.6759 | 23.619 | 23.8123 | 23.7775 | 23.683 | 23.6162 | 23.4897 | 23.3193 | 23.0652 | 22.9175 | 22.8558 | 22.9215 | 23.7099 | 23.6319 | 23.5838 | 23.5152 | 23.4868 | 24.1731 | 24.0827 | 23.9662 | 23.8762 | 23.7704 | 23.6485 | 23.8721 | 23.8037 | 23.7335 | 23.672 | 23.6023 | 23.5999 | 23.0745 | 22.9818 | 24.1261 | 24.0344 | 24.0372 | 23.9828 | 23.9699 | 23.4623 | 23.5775 | 23.833 | 23.803 | 22.2463 | 22.352 | 22.3482 | 23.4343 | 22.8683 | 23.3837 |  | 21.5094 | 21.3939 | 21.8762 | 24.7125 | 23.4422 | 23.4619 | 22.5202 | 22.5068 | 21.6255 | 22.2381 | 10.8244 | 14.2569 | 14.8762 | 11.0895 | -0.00047407 | -0.0031261 | 0.001384 | 0.0040372 | 0.0013491 | -0.00012295 | 0.012256 | -0.015461 | -0.040893 | -360.1281 | 17.4274 | -360.4942 | 17.7046 | -360.8789 | 18.2077 | -360.7835 | 17.5547 | -352.6013 | 18.721 | -352.6567 | 16.8546 | 3.3664 | 5.5787 | 21.945 | 14.5666 | 12.8026 | 22.0662
13:26 | 2 | 36.0818 |  | 8.5848 | 3.4941 | 1.0359 | 3.2144 | -1.6093 | 12.5574 | 5.4844 | 0.6343 | 0.6799 | 0.9838 | 0.767 | -128.7496 | 4.8918 | 6.5376 | 1.729 | -2.38 | -0.8653 | 5.0508 |  | 4.8962 | 0.9946 | 3.9917 | 3.3684 | 3.3286 | 1.1044 | 0.7586 | 22.7623 | 22.6283 | 22.4101 | 22.3777 | 22.3084 | 22.2944 | 22.1651 | 22.958 | 22.6648 | 22.7167 | 22.7011 | 22.6908 | 23.0382 | 22.9439 | 22.9203 | 22.8076 | 22.695 | 22.623 | 22.501 | 22.4041 | 22.3251 | 22.2794 | 22.949 | 22.5781 | 22.6111 | 22.6014 | 22.5943 | 23.1833 | 22.6978 | 22.9248 | 23.0723 | 22.9916 | 23.512 | 22.8886 | 22.9306 | 22.8895 | 22.8317 | 22.6913 | 22.586 | 22.4228 | 22.2551 | 23.2587 | 22.6467 | 22.7438 | 22.9295 | 23.2942 | 23.3339 | 23.2764 | 23.2785 | 23.2187 | 23.1823 | 23.0658 | 23.077 | 23.1173 | 23.0803 | 22.9992 | 22.9027 | 22.7718 | 22.6896 | 22.7038 | 22.8139 | 23.163 | 23.1873 | 23.1596 | 23.079 | 23.0217 | 23.8313 | 23.7251 | 23.7388 | 23.6688 | 23.6337 | 23.3083 | 23.3746 | 23.39 | 23.3487 | 23.3506 | 23.3718 | 23.2685 | 22.9731 | 22.7872 | 23.3141 | 23.3716 | 23.3357 | 23.3021 | 23.2603 | 23.3731 | 23.506 | 22.8293 | 22.8662 | 21.9214 | 21.9315 | 23.2555 | 22.7892 | 23.227 | 22.8633 | 22.1386 | 21.7848 | 21.5538 | 21.3581 | 21.4313 | 21.2888 | 21.0392 | 21.2236 | 21.3993 | 21.5557 | 21.2637 | 21.1497 | 22.6323 | 22.513 | 25.2862 | 22.3215 | 22.3111 | 22.2305 | 22.1983 | 22.122 | 22.2091 | 23.2143 | 22.5461 | 22.4647 | 22.5178 | 22.513 | 22.7684 | 23.0127 | 22.9183 | 22.8615 | 22.7694 | 22.6758 | 22.6447 | 22.6157 | 22.574 | 23.6867 | 22.7623 | 22.759 | 23.7875 | 22.7277 | 23.815 | 22.9214 | 23.0631 | 23.0231 | 23.9011 | 22.9545 | 22.9971 | 22.974 | 22.9359 | 22.7839 | 22.701 | 22.6248 | 22.5412 | 23.6668 | 22.6428 | 22.7615 | 23.0291 | 23.2194 | 23.8674 | 23.8244 | 23.7387 | 23.6744 | 23.6209 | 23.8115 | 23.7701 | 23.688 | 23.6173 | 23.491 | 23.3195 | 23.0659 | 22.915 | 22.8565 | 22.9262 | 23.7117 | 23.6302 | 23.582 | 23.5194 | 23.4828 | 24.1705 | 24.0787 | 23.961 | 23.8702 | 23.7698 | 23.6498 | 23.8686 | 23.8042 | 23.7334 | 23.672 | 23.6019 | 23.6052 | 23.0779 | 22.9883 | 24.1285 | 24.0397 | 24.0363 | 23.9878 | 23.976 | 23.4699 | 23.5739 | 23.8405 | 23.8062 | 22.2507 | 22.3677 | 22.3593 | 23.4437 | 22.8729 | 23.3859 |  | 21.5192 | 21.4075 | 21.8876 | 24.7118 | 23.4382 | 23.4606 | 22.521 | 22.5099 | 21.6172 | 22.2396 | 10.8334 | 14.2804 | 14.8589 | 11.0981 | -5.5933e-06 | -0.0026863 | 0.001664 | 0.0043878 | 0.00146 | -0.00026405 | 0.009443 | -0.014845 | -0.015226 | -360.1835 | 17.4048 | -360.3865 | 17.6081 | -360.7435 | 18.1974 | -360.8512 | 17.5876 | -352.6167 | 18.6943 | -352.5429 | 16.7807 | 3.3702 | 104.3694 | 21.9556 | 14.5697 | 12.6561 | 22.0635
13:26 | 3 | 36.0659 |  | 8.6592 | 3.4025 | 0.9955 | 3.2083 | -1.5281 | 12.5994 | 5.5678 | 0.6336 | 0.6763 | 0.982 | 0.7666 | -128.7861 | 4.8257 | 6.4396 | 1.7895 | -2.4349 | -0.9886 | 5.0182 |  | 5.002 | 0.9454 | 3.9922 | 3.3666 | 3.3287 | 1.1035 | -0.6778 | 22.7574 | 22.6221 | 22.4035 | 22.3782 | 22.301 | 22.2922 | 22.1611 | 22.9509 | 22.6647 | 22.7113 | 22.6998 | 22.6801 | 23.0305 | 22.9362 | 22.9248 | 22.8098 | 22.7015 | 22.6287 | 22.498 | 22.4088 | 22.33 | 22.2788 | 22.951 | 22.5849 | 22.6206 | 22.6004 | 22.5954 | 23.1854 | 22.7066 | 22.928 | 23.0741 | 22.9933 | 23.5169 | 22.8919 | 22.9291 | 22.8941 | 22.8313 | 22.6926 | 22.5827 | 22.4241 | 22.2606 | 23.2642 | 22.6495 | 22.7488 | 22.9334 | 23.2907 | 23.3342 | 23.2761 | 23.2809 | 23.2168 | 23.1824 | 23.0616 | 23.0815 | 23.118 | 23.0784 | 22.9994 | 22.9067 | 22.7738 | 22.6949 | 22.7087 | 22.8128 | 23.1616 | 23.1839 | 23.1638 | 23.0808 | 23.0194 | 23.8308 | 23.7272 | 23.7423 | 23.6759 | 23.6331 | 23.3101 | 23.3745 | 23.3957 | 23.3494 | 23.3568 | 23.3765 | 23.2672 | 22.98 | 22.7873 | 23.3209 | 23.368 | 23.3385 | 23.306 | 23.2699 | 23.3873 | 23.5043 | 22.8285 | 22.8795 | 21.9316 | 21.9416 | 23.2601 | 22.8043 | 23.2357 | 22.8741 | 22.122 | 21.9717 | 21.5283 | 21.3602 | 21.4229 | 21.2843 | 21.0373 | 21.2202 | 21.4033 | 21.5611 | 21.2719 | 21.1541 | 22.6348 | 22.5144 | 25.282 | 22.3215 | 22.3137 | 22.23 | 22.1948 | 22.12 | 22.2075 | 23.217 | 22.5467 | 22.4676 | 22.5181 | 22.506 | 22.768 | 23.0092 | 22.9174 | 22.8575 | 22.7599 | 22.6713 | 22.6414 | 22.6085 | 22.5673 | 23.6846 | 22.7582 | 22.7532 | 23.7844 | 22.7238 | 23.8098 | 22.916 | 23.0681 | 23.0294 | 23.9091 | 22.9599 | 22.9952 | 22.9763 | 22.9419 | 22.7881 | 22.7038 | 22.6296 | 22.5459 | 23.6678 | 22.6431 | 22.7609 | 23.0378 | 23.2219 | 23.8701 | 23.822 | 23.7389 | 23.6714 | 23.6234 | 23.8041 | 23.7666 | 23.6897 | 23.6224 | 23.4937 | 23.315 | 23.0641 | 22.9134 | 22.8517 | 22.9292 | 23.7038 | 23.6243 | 23.5779 | 23.5234 | 23.4771 | 24.1641 | 24.0793 | 23.9558 | 23.8647 | 23.7595 | 23.6478 | 23.8677 | 23.8032 | 23.7293 | 23.6735 | 23.6024 | 23.5953 | 23.0776 | 22.9861 | 24.1273 | 24.0429 | 24.0326 | 23.9894 | 23.9747 | 23.4749 | 23.5711 | 23.8366 | 23.8061 | 22.2494 | 22.3724 | 22.3662 | 23.4427 | 22.8769 | 23.3813 |  | 21.5182 | 21.412 | 21.8881 | 24.7164 | 23.437 | 23.4546 | 22.5138 | 22.5061 | 21.62 | 22.238 | 10.827 | 14.2886 | 14.9258 | 11.0978 | 0.00038785 | -0.0032168 | 0.0016588 | 0.004663 | 0.001704 | -0.0004794 | 0.0085297 | -0.009653 | -0.039259 | -360.0727 | 17.3761 | -360.4173 | 17.6697 | -360.8235 | 18.2015 | -360.8081 | 17.5404 | -352.5275 | 18.6758 | -352.6229 | 16.832 | -0.68042 | 134.1787 | 21.9599 | 14.6072 | 12.6709 | 22.0631
13:26 | 4 | 36.1057 |  | 8.6564 | 3.4674 | 1.1196 | 3.215 | -1.5486 | 12.5662 | 5.5277 | 0.6344 | 0.6794 | 0.982 | 0.7671 | -128.708 | 4.8173 | 6.4852 | 1.7746 | -2.5035 | -0.9031 | 5.0422 |  | 4.9146 | 0.8956 | 3.9923 | 3.3649 | 3.3279 | 1.105 | -0.6522 | 22.759 | 22.6141 | 22.3941 | 22.3821 | 22.2942 | 22.288 | 22.158 | 22.9476 | 22.6634 | 22.7037 | 22.693 | 22.6809 | 23.0276 | 22.9374 | 22.9139 | 22.8037 | 22.6992 | 22.6204 | 22.4987 | 22.3994 | 22.3256 | 22.2769 | 22.9395 | 22.5767 | 22.6124 | 22.593 | 22.5902 | 23.1796 | 22.7064 | 22.9211 | 23.0744 | 22.994 | 23.5211 | 22.8975 | 22.9312 | 22.8935 | 22.8351 | 22.6982 | 22.5875 | 22.4287 | 22.2631 | 23.2703 | 22.6484 | 22.7459 | 22.9391 | 23.2911 | 23.3324 | 23.2777 | 23.2848 | 23.2159 | 23.1877 | 23.0686 | 23.0844 | 23.1211 | 23.0779 | 22.9967 | 22.9095 | 22.7794 | 22.6982 | 22.71 | 22.8191 | 23.1632 | 23.1884 | 23.1664 | 23.0874 | 23.017 | 23.8283 | 23.7331 | 23.7373 | 23.6789 | 23.6364 | 23.3125 | 23.3777 | 23.3992 | 23.3555 | 23.3598 | 23.3865 | 23.2672 | 22.9878 | 22.7879 | 23.3242 | 23.37 | 23.3459 | 23.3122 | 23.2755 | 23.3967 | 23.5063 | 22.8294 | 22.8857 | 21.9382 | 21.9489 | 23.2688 | 22.8101 | 23.2362 | 22.88 | 22.1304 | 22.1588 | 21.5043 | 21.3489 | 21.3979 | 21.2798 | 21.0336 | 21.1972 | 21.3999 | 21.5608 | 21.269 | 21.1516 | 22.631 | 22.5088 | 25.2661 | 22.316 | 22.3004 | 22.225 | 22.1917 | 22.1231 | 22.2014 | 23.2108 | 22.5446 | 22.4605 | 22.5126 | 22.5014 | 22.7684 | 23.0136 | 22.9219 | 22.8614 | 22.7538 | 22.6672 | 22.644 | 22.6106 | 22.5696 | 23.6859 | 22.7598 | 22.7568 | 23.7883 | 22.7247 | 23.8083 | 22.9188 | 23.0715 | 23.0292 | 23.9098 | 22.9639 | 23.0017 | 22.9747 | 22.9394 | 22.7878 | 22.7058 | 22.6292 | 22.5458 | 23.6646 | 22.6397 | 22.7606 | 23.033 | 23.2255 | 23.8745 | 23.8215 | 23.7408 | 23.6761 | 23.6257 | 23.8077 | 23.768 | 23.6919 | 23.6237 | 23.4963 | 23.3174 | 23.0644 | 22.9202 | 22.8543 | 22.9242 | 23.7029 | 23.6272 | 23.5794 | 23.5249 | 23.4844 | 24.1651 | 24.0782 | 23.9591 | 23.8684 | 23.7638 | 23.6492 | 23.8724 | 23.8011 | 23.727 | 23.673 | 23.6071 | 23.5891 | 23.0723 | 22.9799 | 24.1279 | 24.0426 | 24.0293 | 23.9837 | 23.966 | 23.4756 | 23.5708 | 23.8328 | 23.8058 | 22.2513 | 22.3929 | 22.3772 | 23.4344 | 22.8912 | 23.3853 |  | 21.5291 | 21.4224 | 21.8912 | 24.7143 | 23.4361 | 23.4589 | 22.518 | 22.5102 | 21.6175 | 22.2388 | 10.8123 | 14.2663 | 14.8589 | 11.0911 | 0.00030002 | -0.0032499 | 0.0016172 | 0.0044819 | 0.0010386 | -0.00021707 | 0.025516 | -0.0040989 | -0.022767 | -360.2235 | 17.4459 | -360.4635 | 17.6225 | -360.7743 | 18.1912 | -360.8481 | 17.6061 | -352.7029 | 18.7415 | -352.6198 | 16.795 | -3.1416 | 157.7905 | 21.9689 | 14.5626 | 12.6672 | 22.0638
13:26 | 5 | 36.1202 |  | 8.6141 | 3.4518 | 0.9932 | 3.2053 | -1.5773 | 12.5469 | 5.5423 | 0.6336 | 0.6763 | 0.9807 | 0.7667 | -128.696 | 4.8305 | 6.4616 | 1.7365 | -2.5311 | -0.92 | 5.0152 |  | 4.9311 | 1.0257 | 3.9911 | 3.3686 | 3.3301 | 1.1037 | -0.0385 | 22.7548 | 22.6141 | 22.3947 | 22.374 | 22.2896 | 22.2866 | 22.1585 | 22.9457 | 22.6638 | 22.7029 | 22.6884 | 22.6835 | 23.0246 | 22.9323 | 22.9122 | 22.8006 | 22.6942 | 22.6137 | 22.497 | 22.3967 | 22.3218 | 22.2729 | 22.9388 | 22.5737 | 22.6077 | 22.5915 | 22.591 | 23.1768 | 22.7006 | 22.9155 | 23.0657 | 22.9898 | 23.5155 | 22.8889 | 22.9282 | 22.889 | 22.8309 | 22.6901 | 22.5889 | 22.4171 | 22.2563 | 23.2675 | 22.6492 | 22.738 | 22.9391 | 23.2891 | 23.3365 | 23.2822 | 23.2886 | 23.2226 | 23.1914 | 23.0718 | 23.085 | 23.124 | 23.0805 | 22.9987 | 22.9105 | 22.7824 | 22.7 | 22.71 | 22.825 | 23.1589 | 23.1819 | 23.1586 | 23.077 | 23.0113 | 23.824 | 23.7265 | 23.7305 | 23.6693 | 23.6342 | 23.3061 | 23.3733 | 23.3887 | 23.3505 | 23.3529 | 23.3786 | 23.2622 | 22.9801 | 22.7806 | 23.3152 | 23.3657 | 23.3397 | 23.2982 | 23.2701 | 23.3896 | 23.4999 | 22.8228 | 22.878 | 21.9407 | 21.9541 | 23.2733 | 22.8128 | 23.2384 | 22.8871 | 22.1257 | 22.3535 | 21.4856 | 21.3483 | 21.363 | 21.2708 | 21.0299 | 21.1578 | 21.3925 | 21.5594 | 21.262 | 21.1487 | 22.6249 | 22.5069 | 25.2598 | 22.3153 | 22.2921 | 22.2286 | 22.1953 | 22.1272 | 22.2044 | 23.2128 | 22.5415 | 22.4592 | 22.5125 | 22.5052 | 22.7665 | 23.0148 | 22.9256 | 22.8625 | 22.7636 | 22.6741 | 22.6466 | 22.6126 | 22.5729 | 23.688 | 22.7671 | 22.7652 | 23.7912 | 22.7287 | 23.8094 | 22.9217 | 23.0676 | 23.0255 | 23.9004 | 22.9566 | 22.9953 | 22.9714 | 22.9274 | 22.7825 | 22.6991 | 22.6232 | 22.5368 | 23.6622 | 22.6381 | 22.7532 | 23.0244 | 23.2253 | 23.8748 | 23.8229 | 23.743 | 23.6765 | 23.6256 | 23.8078 | 23.7736 | 23.6913 | 23.6209 | 23.4937 | 23.3221 | 23.0669 | 22.9183 | 22.8597 | 22.9235 | 23.7008 | 23.6221 | 23.5786 | 23.5182 | 23.4846 | 24.1638 | 24.0749 | 23.9528 | 23.8662 | 23.7679 | 23.6477 | 23.8704 | 23.8013 | 23.7241 | 23.669 | 23.6072 | 23.5913 | 23.0731 | 22.9805 | 24.1285 | 24.0422 | 24.0272 | 23.9833 | 23.961 | 23.4782 | 23.5738 | 23.8294 | 23.81 | 22.2553 | 22.415 | 22.3877 | 23.4374 | 22.8988 | 23.3884 |  | 21.539 | 21.4288 | 21.8901 | 24.7048 | 23.437 | 23.4515 | 22.522 | 22.514 | 21.6216 | 22.2354 | 10.8305 | 14.2851 | 14.9088 | 11.1152 | 0.00024977 | -0.0025345 | 0.0014745 | 0.004807 | 0.001518 | -0.00026438 | 0.010159 | -0.0083575 | -0.021163 | -360.0788 | 17.3843 | -360.3958 | 17.6533 | -360.8143 | 18.22 | -360.8143 | 17.5486 | -352.5244 | 18.6758 | -352.5952 | 16.8115 | -4.1586 | 179.9684 | 21.9763 | 14.597 | 12.6101 | 22.0678
13:26 | 6 | 36.2133 |  | 8.5893 | 3.4211 | 1.0875 | 3.2109 | -1.5657 | 12.6107 | 5.5162 | 0.6342 | 0.6755 | 0.9814 | 0.7679 | -128.7074 | 4.8174 | 6.4356 | 1.8028 | -2.4994 | -0.9421 | 5.0137 |  | 4.9293 | 1.043 | 3.9916 | 3.365 | 3.3305 | 1.1053 | -0.0317 | 22.7516 | 22.6138 | 22.4016 | 22.374 | 22.297 | 22.2877 | 22.1607 | 22.9477 | 22.6619 | 22.7028 | 22.69 | 22.6842 | 23.0261 | 22.9302 | 22.9145 | 22.7993 | 22.6939 | 22.6222 | 22.4976 | 22.3983 | 22.3212 | 22.2692 | 22.9441 | 22.5747 | 22.605 | 22.5911 | 22.5895 | 23.1835 | 22.6948 | 22.9184 | 23.0604 | 22.987 | 23.5127 | 22.8828 | 22.9267 | 22.8888 | 22.8253 | 22.6859 | 22.5844 | 22.4101 | 22.2542 | 23.2614 | 22.6478 | 22.7386 | 22.934 | 23.2849 | 23.3385 | 23.2781 | 23.2819 | 23.2239 | 23.1896 | 23.0664 | 23.0776 | 23.1174 | 23.0788 | 22.9979 | 22.9105 | 22.7781 | 22.7019 | 22.707 | 22.8255 | 23.1601 | 23.1841 | 23.1584 | 23.0772 | 23.0159 | 23.828 | 23.7213 | 23.7385 | 23.6703 | 23.6364 | 23.3067 | 23.372 | 23.3958 | 23.3527 | 23.3564 | 23.3794 | 23.2595 | 22.9772 | 22.7846 | 23.315 | 23.3594 | 23.3367 | 23.2964 | 23.2669 | 23.3882 | 23.4934 | 22.8257 | 22.8763 | 21.9469 | 21.9555 | 23.2709 | 22.8183 | 23.2409 | 22.8933 | 22.1255 | 22.5001 | 21.4831 | 21.3657 | 21.3444 | 21.2668 | 21.0282 | 21.121 | 21.3926 | 21.5583 | 21.2633 | 21.1435 | 22.6318 | 22.5158 | 25.2522 | 22.322 | 22.3015 | 22.2371 | 22.2015 | 22.1234 | 22.2155 | 23.2208 | 22.543 | 22.4662 | 22.5158 | 22.5072 | 22.7612 | 23.0134 | 22.929 | 22.8615 | 22.7594 | 22.6752 | 22.6402 | 22.6063 | 22.572 | 23.6868 | 22.7676 | 22.765 | 23.7901 | 22.7262 | 23.8108 | 22.9239 | 23.0679 | 23.0281 | 23.9004 | 22.9502 | 22.9927 | 22.9715 | 22.9262 | 22.7816 | 22.6959 | 22.6251 | 22.5419 | 23.6602 | 22.6409 | 22.7545 | 23.0242 | 23.2183 | 23.876 | 23.8238 | 23.7422 | 23.6738 | 23.619 | 23.8051 | 23.7742 | 23.6898 | 23.6192 | 23.4907 | 23.3171 | 23.0642 | 22.9118 | 22.857 | 22.9254 | 23.7012 | 23.6235 | 23.5775 | 23.5184 | 23.4852 | 24.1663 | 24.0756 | 23.9524 | 23.8664 | 23.7694 | 23.6488 | 23.8717 | 23.8061 | 23.7318 | 23.6714 | 23.6074 | 23.5908 | 23.0744 | 22.9812 | 24.1324 | 24.0414 | 24.0308 | 23.9807 | 23.9667 | 23.4837 | 23.5847 | 23.8401 | 23.8138 | 22.2539 | 22.4267 | 22.3935 | 23.4429 | 22.899 | 23.3891 |  | 21.5494 | 21.4513 | 21.9087 | 24.714 | 23.4447 | 23.4635 | 22.532 | 22.5173 | 21.6264 | 22.245 | 10.8207 | 14.275 | 14.883 | 11.113 | 3.4484e-05 | -0.0024157 | 0.001564 | 0.0043334 | 0.0010509 | -0.00064553 | 0.012103 | -0.0076955 | -0.013145 | -360.1896 | 17.4397 | -360.4173 | 17.6102 | -360.7312 | 18.1522 | -360.802 | 17.5753 | -352.6413 | 18.7374 | -352.6167 | 16.7848 | 0.67136 | 197.0329 | 21.9857 | 14.579 | 12.6652 | 22.0719
13:26 | 7 | 36.2816 |  | 8.6577 | 3.4037 | 1.1152 | 3.3438 | -1.5557 | 12.6804 | 5.6154 | 0.6327 | 0.6755 | 0.9757 | 0.767 | -128.7904 | 4.8309 | 6.3863 | 1.8597 | -2.4729 | -0.8432 | 4.9852 |  | 4.9578 | 0.9727 | 3.9919 | 3.363 | 3.3274 | 1.1043 | 0.5308 | 22.7535 | 22.6087 | 22.402 | 22.3797 | 22.2974 | 22.2893 | 22.1607 | 22.9491 | 22.661 | 22.7018 | 22.6918 | 22.6834 | 23.0235 | 22.9325 | 22.9186 | 22.8056 | 22.7003 | 22.6253 | 22.4962 | 22.3951 | 22.3176 | 22.2695 | 22.9438 | 22.5704 | 22.6022 | 22.5934 | 22.5887 | 23.1846 | 22.6942 | 22.9199 | 23.0614 | 22.9839 | 23.5077 | 22.8813 | 22.917 | 22.8891 | 22.8202 | 22.6852 | 22.5793 | 22.4152 | 22.2578 | 23.2571 | 22.6463 | 22.7426 | 22.9317 | 23.2858 | 23.3376 | 23.2756 | 23.2767 | 23.2166 | 23.187 | 23.0621 | 23.078 | 23.1121 | 23.08 | 22.9976 | 22.9023 | 22.7767 | 22.6971 | 22.7018 | 22.8218 | 23.1588 | 23.19 | 23.1585 | 23.0827 | 23.0225 | 23.828 | 23.7224 | 23.744 | 23.6708 | 23.638 | 23.3077 | 23.3739 | 23.399 | 23.3549 | 23.3598 | 23.3833 | 23.2654 | 22.9801 | 22.7942 | 23.3266 | 23.371 | 23.3435 | 23.3085 | 23.2688 | 23.3949 | 23.4999 | 22.8355 | 22.8871 | 21.9496 | 21.9541 | 23.2715 | 22.8163 | 23.2429 | 22.896 | 22.1837 | 22.6225 | 21.4989 | 21.4022 | 21.3299 | 21.2719 | 21.0267 | 21.1111 | 21.4023 | 21.5691 | 21.2755 | 21.1513 | 22.6302 | 22.5184 | 25.2452 | 22.3203 | 22.3006 | 22.2321 | 22.1965 | 22.1184 | 22.2119 | 23.2174 | 22.5426 | 22.4652 | 22.5125 | 22.5015 | 22.7569 | 23.0131 | 22.9289 | 22.8622 | 22.7593 | 22.6766 | 22.6396 | 22.6081 | 22.5736 | 23.6858 | 22.7699 | 22.7626 | 23.7906 | 22.7221 | 23.8159 | 22.922 | 23.0727 | 23.029 | 23.9068 | 22.9571 | 22.9991 | 22.9725 | 22.936 | 22.7833 | 22.7066 | 22.6255 | 22.5469 | 23.6589 | 22.6406 | 22.7622 | 23.0281 | 23.2196 | 23.8794 | 23.8283 | 23.7479 | 23.6771 | 23.6186 | 23.8055 | 23.7739 | 23.6906 | 23.6223 | 23.4957 | 23.3145 | 23.066 | 22.9181 | 22.8599 | 22.9263 | 23.7033 | 23.6249 | 23.5736 | 23.5203 | 23.4851 | 24.1677 | 24.0727 | 23.9518 | 23.8658 | 23.7708 | 23.6455 | 23.8701 | 23.8027 | 23.7289 | 23.6706 | 23.6072 | 23.5903 | 23.0763 | 22.9781 | 24.1366 | 24.0354 | 24.0379 | 23.9789 | 23.9724 | 23.4882 | 23.5848 | 23.8469 | 23.8105 | 22.262 | 22.4414 | 22.4002 | 23.4459 | 22.9081 | 23.3949 |  | 21.5445 | 21.457 | 21.9043 | 24.7109 | 23.4401 | 23.4661 | 22.5261 | 22.5157 | 21.6151 | 22.2454 | 10.7953 | 14.299 | 14.9005 | 11.1438 | 0.00073753 | -0.0029361 | 0.0016321 | 0.0044015 | 0.0016325 | -0.00045944 | 0.0097625 | -0.0055509 | -0.023987 | -360.1588 | 17.3987 | -360.4512 | 17.6697 | -360.882 | 18.2241 | -360.8481 | 17.5671 | -352.5829 | 18.7025 | -352.6198 | 16.8197 | -1.5664 | 208.2881 | 21.9891 | 14.5998 | 12.8159 | 22.0654
13:26 | 8 | 36.2266 |  | 8.6302 | 3.4026 | 1.1026 | 3.3324 | -1.6566 | 12.5596 | 5.6184 | 0.6338 | 0.6739 | 0.9802 | 0.7661 | -128.7325 | 4.9308 | 6.4745 | 1.9603 | -2.4989 | -0.7926 | 5.0305 |  | 4.9366 | 0.9659 | 3.9929 | 3.3624 | 3.3282 | 1.1061 | 0.144 | 22.7535 | 22.6085 | 22.3964 | 22.3741 | 22.2908 | 22.2831 | 22.1578 | 22.942 | 22.6564 | 22.6957 | 22.6868 | 22.6775 | 23.0184 | 22.9299 | 22.9236 | 22.8024 | 22.6969 | 22.621 | 22.4921 | 22.3952 | 22.3149 | 22.2685 | 22.938 | 22.5676 | 22.6016 | 22.5877 | 22.587 | 23.1775 | 22.6945 | 22.9176 | 23.0584 | 22.981 | 23.5058 | 22.8815 | 22.9117 | 22.8857 | 22.8233 | 22.68 | 22.575 | 22.4188 | 22.2592 | 23.2539 | 22.6495 | 22.7408 | 22.9285 | 23.2846 | 23.3336 | 23.2752 | 23.2742 | 23.2132 | 23.1849 | 23.063 | 23.0841 | 23.1112 | 23.0794 | 22.996 | 22.8963 | 22.7747 | 22.6918 | 22.7031 | 22.8168 | 23.1615 | 23.1875 | 23.1562 | 23.0796 | 23.0199 | 23.8272 | 23.7247 | 23.742 | 23.6679 | 23.6341 | 23.3087 | 23.3791 | 23.3936 | 23.3493 | 23.3608 | 23.3868 | 23.2655 | 22.9778 | 22.7912 | 23.3268 | 23.3716 | 23.3452 | 23.3104 | 23.2714 | 23.3959 | 23.5046 | 22.8335 | 22.8956 | 21.9462 | 21.9527 | 23.2727 | 22.8218 | 23.24 | 22.8953 | 22.2675 | 22.6614 | 21.5002 | 21.435 | 21.317 | 21.2629 | 21.0191 | 21.1132 | 21.4169 | 21.575 | 21.288 | 21.1623 | 22.6264 | 22.5128 | 25.2399 | 22.3144 | 22.2966 | 22.2276 | 22.1918 | 22.1191 | 22.2066 | 23.2154 | 22.5409 | 22.466 | 22.5097 | 22.4992 | 22.7599 | 23.0145 | 22.9212 | 22.8626 | 22.7603 | 22.6732 | 22.6389 | 22.6119 | 22.5703 | 23.6844 | 22.7678 | 22.7607 | 23.7885 | 22.7268 | 23.8162 | 22.9248 | 23.0713 | 23.0272 | 23.9071 | 22.9605 | 23.0004 | 22.9729 | 22.9332 | 22.7864 | 22.7062 | 22.6238 | 22.5422 | 23.6627 | 22.6428 | 22.7641 | 23.0259 | 23.2241 | 23.8758 | 23.8289 | 23.7505 | 23.6775 | 23.6271 | 23.8044 | 23.7746 | 23.6887 | 23.6229 | 23.4956 | 23.3172 | 23.0657 | 22.9173 | 22.8631 | 22.9248 | 23.6976 | 23.6166 | 23.5714 | 23.5176 | 23.4808 | 24.1587 | 24.0667 | 23.9516 | 23.8614 | 23.7612 | 23.6421 | 23.8635 | 23.7933 | 23.7166 | 23.664 | 23.6013 | 23.5974 | 23.0753 | 22.9802 | 24.1312 | 24.0403 | 24.0389 | 23.9838 | 23.9743 | 23.4865 | 23.582 | 23.8445 | 23.8105 | 22.2728 | 22.4525 | 22.41 | 23.4488 | 22.9154 | 23.3978 |  | 21.5588 | 21.4665 | 21.9099 | 24.7135 | 23.4347 | 23.4631 | 22.5297 | 22.5175 | 21.6144 | 22.2486 | 10.8299 | 14.2911 | 14.8701 | 11.1014 | 0.00051461 | -0.0032722 | 0.0017609 | 0.0043201 | 0.00096962 | -0.00028399 | 0.022948 | -0.0061467 | -0.0051985 | -360.1711 | 17.4274 | -360.4419 | 17.6328 | -360.7497 | 18.1645 | -360.7681 | 17.5465 | -352.5952 | 18.721 | -352.5952 | 16.793 | 4.4452 | 223.2107 | 21.9962 | 14.5806 | 12.7773 | 22.066
13:26 | 9 | 36.2263 |  | 8.5785 | 3.3083 | 1.151 | 3.3027 | -1.7014 | 12.526 | 5.64 | 0.6331 | 0.6767 | 0.9806 | 0.7671 | -128.7418 | 4.9192 | 6.5142 | 1.9935 | -2.5237 | -0.8645 | 4.9873 |  | 4.9321 | 1.0162 | 3.993 | 3.3623 | 3.3278 | 1.1058 | -0.4263 | 22.7503 | 22.612 | 22.3957 | 22.371 | 22.291 | 22.2798 | 22.1541 | 22.9401 | 22.653 | 22.695 | 22.6862 | 22.6809 | 23.0207 | 22.9266 | 22.9171 | 22.7945 | 22.6956 | 22.6177 | 22.4913 | 22.3936 | 22.3121 | 22.2711 | 22.9388 | 22.5629 | 22.6046 | 22.5816 | 22.5872 | 23.1796 | 22.694 | 22.9204 | 23.0539 | 22.9806 | 23.5059 | 22.8804 | 22.9161 | 22.8875 | 22.8266 | 22.6799 | 22.5791 | 22.4181 | 22.2565 | 23.2565 | 22.6516 | 22.7406 | 22.9328 | 23.2812 | 23.3292 | 23.2704 | 23.2708 | 23.2132 | 23.1825 | 23.0645 | 23.0798 | 23.117 | 23.0756 | 22.9906 | 22.8975 | 22.7695 | 22.6947 | 22.7069 | 22.8126 | 23.1619 | 23.182 | 23.1504 | 23.0768 | 23.01 | 23.8214 | 23.7284 | 23.7378 | 23.6678 | 23.628 | 23.3045 | 23.3792 | 23.3916 | 23.3432 | 23.3575 | 23.3841 | 23.2646 | 22.9827 | 22.79 | 23.3212 | 23.3671 | 23.3461 | 23.3158 | 23.2726 | 23.4002 | 23.5061 | 22.831 | 22.9014 | 21.9522 | 21.9628 | 23.2798 | 22.8328 | 23.2383 | 22.9018 | 22.3628 | 22.5964 | 21.509 | 21.4599 | 21.3101 | 21.2449 | 21.016 | 21.1123 | 21.4212 | 21.5738 | 21.2885 | 21.1711 | 22.6308 | 22.5145 | 25.2224 | 22.3186 | 22.3039 | 22.2317 | 22.1974 | 22.1218 | 22.215 | 23.2198 | 22.5506 | 22.4677 | 22.5116 | 22.5034 | 22.7631 | 23.0119 | 22.9209 | 22.8635 | 22.7509 | 22.666 | 22.6351 | 22.6074 | 22.5668 | 23.6851 | 22.7603 | 22.7551 | 23.7828 | 22.7276 | 23.8145 | 22.9168 | 23.0717 | 23.0312 | 23.9087 | 22.9559 | 22.9953 | 22.9721 | 22.932 | 22.7863 | 22.7058 | 22.6305 | 22.5453 | 23.6689 | 22.6445 | 22.7625 | 23.0222 | 23.2318 | 23.8816 | 23.831 | 23.7479 | 23.6784 | 23.6261 | 23.8083 | 23.7783 | 23.69 | 23.6264 | 23.4942 | 23.324 | 23.0677 | 22.921 | 22.8628 | 22.9225 | 23.6987 | 23.6206 | 23.5735 | 23.5156 | 23.4784 | 24.1576 | 24.07 | 23.9538 | 23.8592 | 23.7582 | 23.637 | 23.8663 | 23.797 | 23.7202 | 23.665 | 23.5992 | 23.6004 | 23.0718 | 22.9789 | 24.1256 | 24.0446 | 24.0323 | 23.9854 | 23.9697 | 23.4812 | 23.581 | 23.8387 | 23.8099 | 22.2744 | 22.4661 | 22.4218 | 23.4481 | 22.9185 | 23.3946 |  | 21.5637 | 21.4757 | 21.9163 | 24.7091 | 23.4382 | 23.4577 | 22.5351 | 22.5134 | 21.6196 | 22.2444 | 10.8687 | 14.2945 | 14.8659 | 11.1192 | 0.00034704 | -0.0026393 | 0.0015469 | 0.0038234 | 0.0012961 | -0.00075737 | 0.022654 | -0.013269 | -0.017613 | -360.125 | 17.3864 | -360.4235 | 17.6512 | -360.8235 | 18.2118 | -360.805 | 17.5671 | -352.5983 | 18.6902 | -352.6136 | 16.8074 | 10.7828 | 245.2385 | 22.0041 | 14.5802 | 12.7038 | 22.0665
13:26 | 10 | 36.2629 |  | 8.6394 | 3.4342 | 1.2405 | 3.27 | -1.6045 | 12.5818 | 5.6809 | 0.6325 | 0.6749 | 0.9825 | 0.7651 | -128.7483 | 4.8785 | 6.4456 | 1.9965 | -2.4426 | -0.8012 | 5.0104 |  | 4.8513 | 0.9532 | 3.993 | 3.3649 | 3.3274 | 1.1069 | 0.6577 | 22.753 | 22.6179 | 22.4044 | 22.378 | 22.292 | 22.2845 | 22.1583 | 22.9453 | 22.6576 | 22.7048 | 22.6914 | 22.6831 | 23.0293 | 22.9342 | 22.9109 | 22.7975 | 22.6918 | 22.6169 | 22.489 | 22.3924 | 22.3114 | 22.2704 | 22.937 | 22.5621 | 22.6043 | 22.5824 | 22.5902 | 23.1754 | 22.693 | 22.9204 | 23.0557 | 22.9788 | 23.4985 | 22.8763 | 22.9098 | 22.8862 | 22.8223 | 22.6775 | 22.5775 | 22.4103 | 22.2511 | 23.2541 | 22.649 | 22.7405 | 22.9341 | 23.2799 | 23.3252 | 23.2736 | 23.2746 | 23.2136 | 23.182 | 23.0611 | 23.0718 | 23.118 | 23.0765 | 22.9912 | 22.9018 | 22.7728 | 22.6997 | 22.7131 | 22.8168 | 23.1538 | 23.1777 | 23.144 | 23.075 | 23.0071 | 23.8177 | 23.7219 | 23.7299 | 23.6653 | 23.6226 | 23.2984 | 23.3679 | 23.3813 | 23.3433 | 23.3482 | 23.3728 | 23.267 | 22.9849 | 22.7923 | 23.3239 | 23.3713 | 23.3479 | 23.3172 | 23.2743 | 23.4059 | 23.5103 | 22.8302 | 22.9057 | 21.9587 | 21.974 | 23.2926 | 22.8459 | 23.2445 | 22.9134 | 22.5097 | 22.5247 | 21.5239 | 21.4954 | 21.3027 | 21.2368 | 21.0237 | 21.1149 | 21.4173 | 21.5773 | 21.2844 | 21.1719 | 22.6314 | 22.524 | 25.1994 | 22.3279 | 22.3117 | 22.2397 | 22.1983 | 22.1214 | 22.2184 | 23.221 | 22.5563 | 22.4712 | 22.5107 | 22.5079 | 22.7656 | 23.0087 | 22.9217 | 22.864 | 22.7531 | 22.6675 | 22.6347 | 22.6049 | 22.5659 | 23.6842 | 22.7585 | 22.7594 | 23.7824 | 22.7256 | 23.8132 | 22.913 | 23.07 | 23.0319 | 23.9059 | 22.9489 | 22.9916 | 22.9662 | 22.9327 | 22.7833 | 22.705 | 22.6274 | 22.5432 | 23.6623 | 22.6415 | 22.7583 | 23.0233 | 23.2393 | 23.885 | 23.8277 | 23.743 | 23.6813 | 23.6238 | 23.8103 | 23.7746 | 23.6924 | 23.6307 | 23.4896 | 23.3249 | 23.0686 | 22.925 | 22.8598 | 22.9226 | 23.7085 | 23.6273 | 23.5776 | 23.5148 | 23.4805 | 24.1654 | 24.0727 | 23.9573 | 23.868 | 23.7657 | 23.6349 | 23.8702 | 23.807 | 23.7269 | 23.6677 | 23.6064 | 23.5969 | 23.0744 | 22.9797 | 24.1284 | 24.0436 | 24.0319 | 23.9902 | 23.9673 | 23.4845 | 23.5792 | 23.8411 | 23.8114 | 22.2812 | 22.4829 | 22.4336 | 23.4534 | 22.9288 | 23.4042 |  | 21.566 | 21.4887 | 21.9208 | 24.7061 | 23.4348 | 23.4572 | 22.5366 | 22.5156 | 21.6204 | 22.2467 | 10.8369 | 14.2981 | 14.8913 | 11.1155 | -9.6649e-05 | -0.0026147 | 0.0014799 | 0.0044377 | 0.0011335 | -0.00019002 | 0.017606 | 0.0058894 | -0.005819 | -360.1804 | 17.4521 | -360.4789 | 17.6656 | -360.8297 | 18.1933 | -360.8512 | 17.5814 | -352.6075 | 18.7395 | -352.6475 | 16.8156 | -6.163 | 260.0806 | 22.0132 | 14.5947 | 12.843 | 22.068
13:26 | 11 | 36.3398 |  | 8.5709 | 3.3601 | 1.1818 | 3.2759 | -1.6401 | 12.5834 | 5.6493 | 0.6344 | 0.6771 | 0.9784 | 0.7661 | -128.7771 | 4.9388 | 6.4988 | 1.9865 | -2.5107 | -0.8144 | 4.9976 |  | 4.9822 | 0.9611 | 3.9916 | 3.3664 | 3.3293 | 1.1051 | -0.0914 | 22.761 | 22.6192 | 22.4094 | 22.3823 | 22.294 | 22.2831 | 22.1658 | 22.9505 | 22.663 | 22.7083 | 22.6964 | 22.6861 | 23.0376 | 22.9434 | 22.9076 | 22.8 | 22.6857 | 22.6184 | 22.4861 | 22.3924 | 22.3111 | 22.2686 | 22.9309 | 22.5606 | 22.6081 | 22.5837 | 22.5841 | 23.1676 | 22.6915 | 22.9153 | 23.0586 | 22.9794 | 23.4991 | 22.8764 | 22.9125 | 22.8823 | 22.8239 | 22.6807 | 22.5763 | 22.4128 | 22.2551 | 23.2544 | 22.6477 | 22.7397 | 22.9315 | 23.278 | 23.322 | 23.2725 | 23.2753 | 23.2118 | 23.1855 | 23.0571 | 23.0721 | 23.1159 | 23.0743 | 22.9933 | 22.9005 | 22.7763 | 22.6994 | 22.7143 | 22.8217 | 23.1493 | 23.176 | 23.1472 | 23.0734 | 23.0045 | 23.8223 | 23.722 | 23.7303 | 23.6608 | 23.6251 | 23.2968 | 23.3668 | 23.3796 | 23.3489 | 23.3517 | 23.3768 | 23.2622 | 22.9816 | 22.7903 | 23.3183 | 23.3676 | 23.3413 | 23.3079 | 23.2745 | 23.4167 | 23.518 | 22.8292 | 22.9045 | 21.9658 | 21.9757 | 23.2964 | 22.8592 | 23.2494 | 22.9151 | 22.6659 | 22.4529 | 21.5174 | 21.5034 | 21.3023 | 21.2303 | 21.0544 | 21.1681 | 21.4108 | 21.5765 | 21.2803 | 21.1645 | 22.6288 | 22.5174 | 25.1946 | 22.3269 | 22.3053 | 22.2372 | 22.1867 | 22.1171 | 22.2119 | 23.212 | 22.5436 | 22.4672 | 22.5068 | 22.4999 | 22.7608 | 23.0146 | 22.9207 | 22.8585 | 22.7566 | 22.6631 | 22.6408 | 22.6179 | 22.5738 | 23.6861 | 22.7619 | 22.7609 | 23.7905 | 22.7289 | 23.8135 | 22.92 | 23.0691 | 23.0288 | 23.9044 | 22.9508 | 22.991 | 22.9663 | 22.9317 | 22.7856 | 22.6957 | 22.6259 | 22.5358 | 23.6547 | 22.6385 | 22.7508 | 23.0236 | 23.2325 | 23.8744 | 23.8218 | 23.7415 | 23.6834 | 23.624 | 23.8067 | 23.7707 | 23.6863 | 23.6292 | 23.4838 | 23.3187 | 23.0624 | 22.9167 | 22.8529 | 22.9211 | 23.7041 | 23.6246 | 23.5784 | 23.5128 | 23.4801 | 24.1621 | 24.0652 | 23.9566 | 23.8691 | 23.7662 | 23.6361 | 23.8676 | 23.8028 | 23.7213 | 23.6651 | 23.606 | 23.6012 | 23.074 | 22.9806 | 24.1227 | 24.0489 | 24.0311 | 23.9911 | 23.9703 | 23.4923 | 23.5891 | 23.8515 | 23.8155 | 22.2931 | 22.4923 | 22.4414 | 23.455 | 22.9367 | 23.4083 |  | 21.5812 | 21.5069 | 21.9283 | 24.7147 | 23.4443 | 23.4641 | 22.5513 | 22.5286 | 21.6277 | 22.2551 | 10.849 | 14.2678 | 14.8958 | 11.1487 | 0.00054571 | -0.002606 | 0.0016747 | 0.0044924 | 0.001423 | -0.0012399 | 0.02921 | 0.0043285 | -0.037734 | -360.125 | 17.3823 | -360.4019 | 17.6266 | -360.7681 | 18.1994 | -360.8112 | 17.5506 | -352.5798 | 18.6963 | -352.5736 | 16.7909 | -4.9337 | 273.8441 | 22.0231 | 14.5818 | 12.7751 | 22.0782
13:26 | 12 | 36.355 |  | 8.5469 | 3.3952 | 1.1899 | 3.2934 | -1.6384 | 12.5917 | 5.67 | 0.6343 | 0.6753 | 0.9795 | 0.7682 | -128.8723 | 4.8514 | 6.3106 | 2.085 | -2.5061 | -0.8102 | 5.0144 |  | 4.9113 | 0.9683 | 3.9936 | 3.3652 | 3.3302 | 1.1055 | -0.1049 | 22.7535 | 22.6121 | 22.4019 | 22.3808 | 22.2953 | 22.2793 | 22.1629 | 22.9457 | 22.6676 | 22.7038 | 22.6966 | 22.6849 | 23.0305 | 22.9402 | 22.8986 | 22.7975 | 22.6823 | 22.6118 | 22.4811 | 22.3862 | 22.3084 | 22.2618 | 22.9251 | 22.5547 | 22.6024 | 22.5761 | 22.5802 | 23.1636 | 22.6861 | 22.9114 | 23.0571 | 22.9817 | 23.5015 | 22.8758 | 22.9177 | 22.8844 | 22.824 | 22.6841 | 22.5783 | 22.4213 | 22.2557 | 23.2578 | 22.6495 | 22.7399 | 22.9306 | 23.2736 | 23.3193 | 23.2627 | 23.2726 | 23.2107 | 23.1857 | 23.055 | 23.0722 | 23.1147 | 23.0749 | 22.9904 | 22.8963 | 22.7786 | 22.6909 | 22.7051 | 22.819 | 23.1466 | 23.1787 | 23.152 | 23.0674 | 23.0029 | 23.8191 | 23.728 | 23.7316 | 23.6605 | 23.6302 | 23.2989 | 23.3746 | 23.387 | 23.3484 | 23.3531 | 23.3866 | 23.2602 | 22.9805 | 22.7831 | 23.3168 | 23.3684 | 23.3376 | 23.3052 | 23.274 | 23.434 | 23.5387 | 22.8221 | 22.9028 | 21.9689 | 21.9814 | 23.307 | 22.8816 | 23.254 | 22.9255 | 22.915 | 22.4947 | 21.4994 | 21.5327 | 21.3084 | 21.2361 | 21.1598 | 21.3642 | 21.4151 | 21.5811 | 21.2898 | 21.1698 | 22.623 | 22.507 | 25.2078 | 22.3183 | 22.2966 | 22.2264 | 22.1836 | 22.1147 | 22.2032 | 23.2096 | 22.5302 | 22.4568 | 22.4997 | 22.4944 | 22.75 | 23.0182 | 22.9201 | 22.8559 | 22.7542 | 22.6638 | 22.6398 | 22.6154 | 22.577 | 23.6841 | 22.7656 | 22.7592 | 23.7919 | 22.7314 | 23.8177 | 22.922 | 23.0641 | 23.0266 | 23.9036 | 22.9562 | 22.9901 | 22.9682 | 22.9339 | 22.7841 | 22.6896 | 22.625 | 22.5355 | 23.6548 | 22.6364 | 22.7459 | 23.0188 | 23.2245 | 23.8643 | 23.8211 | 23.74 | 23.678 | 23.6197 | 23.8015 | 23.7687 | 23.6816 | 23.6223 | 23.486 | 23.3106 | 23.0598 | 22.9129 | 22.8472 | 22.9185 | 23.696 | 23.62 | 23.5693 | 23.5109 | 23.4727 | 24.1536 | 24.0583 | 23.9484 | 23.8586 | 23.7558 | 23.6334 | 23.8617 | 23.7922 | 23.7204 | 23.6611 | 23.5968 | 23.5973 | 23.0775 | 22.9805 | 24.1237 | 24.0484 | 24.0338 | 23.9852 | 23.9759 | 23.5069 | 23.6273 | 23.8562 | 23.8184 | 22.2999 | 22.5084 | 22.4498 | 23.4578 | 22.9425 | 23.4117 |  | 21.5839 | 21.5192 | 21.9403 | 24.7117 | 23.4505 | 23.4666 | 22.5572 | 22.5284 | 21.6293 | 22.2583 | 10.8235 | 14.2779 | 14.8864 | 11.1227 | 0.00026729 | -0.0033824 | 0.0016321 | 0.0043544 | 0.0014452 | 1.0454e-05 | 0.020686 | -0.014818 | -0.02351 | -360.1373 | 17.4131 | -360.4327 | 17.643 | -360.7897 | 18.1892 | -360.8235 | 17.565 | -352.5983 | 18.7271 | -352.6075 | 16.8032 | 12.0342 | 294.8227 | 22.0315 | 14.5821 | 12.8134 | 22.0788
13:26 | 13 | 36.2981 |  | 8.5283 | 3.3109 | 1.1496 | 3.1845 | -1.6238 | 12.6285 | 5.7333 | 0.6336 | 0.6721 | 0.9784 | 0.7671 | -128.9194 | 4.8452 | 6.4551 | 1.9917 | -2.5264 | -0.93 | 4.9325 |  | 4.9527 | 1.0414 | 3.9915 | 3.3673 | 3.3277 | 1.107 | -0.8944 | 22.7452 | 22.6032 | 22.3956 | 22.3763 | 22.2934 | 22.2785 | 22.1616 | 22.9387 | 22.6663 | 22.7012 | 22.6918 | 22.6763 | 23.0257 | 22.9304 | 22.905 | 22.7966 | 22.6839 | 22.6133 | 22.4818 | 22.3834 | 22.3081 | 22.2574 | 22.9265 | 22.5628 | 22.5943 | 22.5754 | 22.5853 | 23.1665 | 22.6855 | 22.9155 | 23.0575 | 22.9898 | 23.5064 | 22.8828 | 22.9158 | 22.8895 | 22.831 | 22.686 | 22.5831 | 22.4201 | 22.2558 | 23.2624 | 22.6591 | 22.7456 | 22.9386 | 23.2727 | 23.3221 | 23.2682 | 23.27 | 23.2119 | 23.1832 | 23.0575 | 23.0735 | 23.1146 | 23.0777 | 22.991 | 22.9019 | 22.7811 | 22.6907 | 22.7041 | 22.8181 | 23.1458 | 23.1835 | 23.1534 | 23.0647 | 23.0084 | 23.8184 | 23.7298 | 23.7325 | 23.6658 | 23.6336 | 23.3081 | 23.3746 | 23.3961 | 23.3508 | 23.3514 | 23.3873 | 23.2553 | 22.9747 | 22.7788 | 23.3188 | 23.3708 | 23.3372 | 23.3073 | 23.2701 | 23.4453 | 23.5582 | 22.8221 | 22.9073 | 21.9691 | 21.9922 | 23.32 | 22.9043 | 23.2584 | 22.9404 | 23.248 | 22.6218 | 21.4811 | 21.5912 | 21.3154 | 21.2518 | 21.3113 | 21.5665 | 21.425 | 21.5806 | 21.3028 | 21.1758 | 22.6273 | 22.5128 | 25.2097 | 22.316 | 22.2956 | 22.2282 | 22.1924 | 22.1125 | 22.1988 | 23.206 | 22.5312 | 22.4568 | 22.4995 | 22.4902 | 22.7458 | 23.014 | 22.9221 | 22.8627 | 22.7595 | 22.6695 | 22.6444 | 22.6065 | 22.5722 | 23.6827 | 22.7628 | 22.7652 | 23.7941 | 22.7338 | 23.8186 | 22.921 | 23.0647 | 23.0275 | 23.9044 | 22.956 | 22.9932 | 22.9709 | 22.9347 | 22.7832 | 22.6925 | 22.622 | 22.5418 | 23.6594 | 22.6427 | 22.7517 | 23.0179 | 23.2304 | 23.8667 | 23.8199 | 23.7379 | 23.6707 | 23.6187 | 23.8038 | 23.7712 | 23.684 | 23.6105 | 23.4911 | 23.3065 | 23.0587 | 22.9114 | 22.8458 | 22.9191 | 23.7045 | 23.6214 | 23.5714 | 23.5155 | 23.4733 | 24.1573 | 24.0693 | 23.9497 | 23.8615 | 23.753 | 23.6397 | 23.8629 | 23.7964 | 23.7283 | 23.6671 | 23.6 | 23.59 | 23.0775 | 22.9807 | 24.1267 | 24.0445 | 24.0358 | 23.9801 | 23.9745 | 23.5218 | 23.6693 | 23.86 | 23.8191 | 22.306 | 22.5284 | 22.4642 | 23.4675 | 22.9578 | 23.4179 |  | 21.5805 | 21.5127 | 21.939 | 24.6955 | 23.4399 | 23.451 | 22.553 | 22.5182 | 21.6169 | 22.2512 | 10.8123 | 14.2663 | 14.9012 | 11.1192 | 0.00011195 | -0.0029681 | 0.0007974 | 0.0044819 | 0.0014366 | -0.00066341 | 0.017408 | -0.01814 | -0.0037234 | -360.1988 | 17.4213 | -360.4481 | 17.6574 | -360.8358 | 18.2179 | -360.8389 | 17.5691 | -352.6229 | 18.723 | -352.6136 | 16.8074 | -3.8188 | 301.9012 | 22.0365 | 14.5838 | 12.712 | 22.0676
13:26 | 14 | 36.327 |  | 8.4694 | 3.3827 | 1.1837 | 3.24 | -1.5498 | 12.531 | 5.6721 | 0.6328 | 0.6781 | 0.9804 | 0.7668 | -128.7658 | 4.885 | 6.4967 | 1.9925 | -2.4841 | -0.9859 | 5.0727 |  | 4.9508 | 0.9889 | 3.9927 | 3.3651 | 3.3322 | 1.1064 | 0.3259 | 22.746 | 22.6019 | 22.3999 | 22.3808 | 22.295 | 22.2839 | 22.1646 | 22.9429 | 22.6649 | 22.7035 | 22.6961 | 22.682 | 23.0333 | 22.9335 | 22.9154 | 22.8008 | 22.6909 | 22.6199 | 22.4871 | 22.3906 | 22.3157 | 22.2656 | 22.9379 | 22.5709 | 22.5985 | 22.5924 | 22.5911 | 23.1736 | 22.6877 | 22.919 | 23.0584 | 22.9904 | 23.5097 | 22.8899 | 22.917 | 22.8939 | 22.8323 | 22.69 | 22.5843 | 22.4208 | 22.2644 | 23.268 | 22.6613 | 22.7505 | 22.9475 | 23.2794 | 23.3286 | 23.2754 | 23.2714 | 23.2128 | 23.1841 | 23.0619 | 23.0794 | 23.1202 | 23.0737 | 22.9964 | 22.9087 | 22.7814 | 22.6979 | 22.7152 | 22.8305 | 23.1428 | 23.1813 | 23.1516 | 23.0648 | 23.0084 | 23.8259 | 23.7254 | 23.7371 | 23.6676 | 23.6323 | 23.3063 | 23.3742 | 23.3952 | 23.3535 | 23.3546 | 23.3834 | 23.2508 | 22.9694 | 22.7817 | 23.3142 | 23.3683 | 23.3379 | 23.3064 | 23.2671 | 23.4552 | 23.5812 | 22.8243 | 22.9228 | 21.9693 | 21.9962 | 23.3206 | 22.9105 | 23.2579 | 22.9455 | 23.5123 | 22.7739 | 21.4689 | 21.6869 | 21.3255 | 21.2656 | 21.4663 | 21.6571 | 21.4244 | 21.581 | 21.3057 | 21.1828 | 22.6369 | 22.5211 | 25.2148 | 22.3235 | 22.2995 | 22.2354 | 22.1982 | 22.1141 | 22.2054 | 23.2081 | 22.5353 | 22.4658 | 22.5106 | 22.4911 | 22.7495 | 23.0097 | 22.9264 | 22.8634 | 22.7611 | 22.6686 | 22.6453 | 22.6077 | 22.5699 | 23.682 | 22.7601 | 22.7668 | 23.7934 | 22.7339 | 23.8129 | 22.9205 | 23.0698 | 23.027 | 23.9013 | 22.9489 | 22.9914 | 22.969 | 22.9287 | 22.7847 | 22.6903 | 22.6199 | 22.5405 | 23.6591 | 22.635 | 22.7515 | 23.0146 | 23.2339 | 23.8726 | 23.822 | 23.7389 | 23.6723 | 23.6172 | 23.8036 | 23.7755 | 23.684 | 23.6052 | 23.4891 | 23.3159 | 23.0438 | 22.9094 | 22.8358 | 22.9225 | 23.709 | 23.6285 | 23.5805 | 23.5207 | 23.48 | 24.1643 | 24.0772 | 23.9549 | 23.8685 | 23.7635 | 23.6452 | 23.8731 | 23.8033 | 23.7246 | 23.6695 | 23.6074 | 23.5919 | 23.0725 | 22.9819 | 24.1229 | 24.0411 | 24.0349 | 23.9804 | 23.9655 | 23.5272 | 24.4556 | 23.8672 | 23.8192 | 22.3194 | 22.5428 | 22.4776 | 23.4763 | 22.9733 | 23.424 |  | 21.5935 | 21.5285 | 21.9564 | 24.7104 | 23.443 | 23.456 | 22.5548 | 22.5266 | 21.6248 | 22.2557 | 10.8441 | 14.2627 | 14.897 | 11.1089 | -0.00017313 | -0.002617 | 0.0015203 | 0.0041263 | 0.001014 | -0.00069043 | 0.026986 | -0.013848 | -0.032698 | -360.1188 | 17.3946 | -360.4327 | 17.6492 | -360.8081 | 18.1933 | -360.7773 | 17.5486 | -352.5552 | 18.6943 | -352.6136 | 16.8094 | -2.5965 | 317.8269 | 22.048 | 14.5799 | 12.7392 | 22.0757
13:26 | 15 | 36.3487 |  | 8.5548 | 3.3072 | 1.0358 | 3.2946 | -1.5587 | 12.5452 | 5.6303 | 0.6321 | 0.6772 | 0.9818 | 0.7674 | -128.7472 | 4.9276 | 6.4848 | 1.8654 | -2.4065 | -0.8169 | 5.0649 |  | 4.9509 | 1.0134 | 3.9914 | 3.3662 | 3.3274 | 1.1082 | -0.6123 | 22.7519 | 22.6081 | 22.4012 | 22.3867 | 22.2953 | 22.2877 | 22.1642 | 22.9483 | 22.6645 | 22.7102 | 22.6972 | 22.6917 | 23.0374 | 22.9453 | 22.9054 | 22.7973 | 22.6875 | 22.6154 | 22.4854 | 22.3891 | 22.3192 | 22.2643 | 22.9361 | 22.567 | 22.5984 | 22.5907 | 22.5877 | 23.1719 | 22.6846 | 22.9175 | 23.0557 | 22.9773 | 23.5015 | 22.8825 | 22.916 | 22.8927 | 22.822 | 22.6847 | 22.5732 | 22.4195 | 22.2609 | 23.2648 | 22.651 | 22.75 | 22.9419 | 23.2746 | 23.3259 | 23.2705 | 23.2745 | 23.2106 | 23.1867 | 23.0618 | 23.0745 | 23.1176 | 23.0732 | 22.9979 | 22.9086 | 22.7783 | 22.6998 | 22.7168 | 22.833 | 23.1434 | 23.1814 | 23.1541 | 23.0683 | 23.0086 | 23.8295 | 23.7244 | 23.7432 | 23.672 | 23.6309 | 23.3052 | 23.3802 | 23.3911 | 23.35 | 23.361 | 23.3857 | 23.2562 | 22.971 | 22.7824 | 23.3142 | 23.37 | 23.3343 | 23.3041 | 23.2677 | 23.4669 | 23.6124 | 22.8187 | 22.9298 | 21.9713 | 22.0045 | 23.3281 | 22.9216 | 23.2629 | 22.9559 | 23.7058 | 22.9424 | 21.474 | 21.8703 | 21.4133 | 21.2939 | 21.6878 | 21.7107 | 21.4311 | 21.5912 | 21.3089 | 21.189 | 22.6373 | 22.5223 | 25.2136 | 22.3231 | 22.2972 | 22.2354 | 22.1919 | 22.1192 | 22.2033 | 23.2087 | 22.5288 | 22.4593 | 22.5105 | 22.4913 | 22.7497 | 23.0035 | 22.9163 | 22.8519 | 22.7623 | 22.6622 | 22.6308 | 22.608 | 22.5611 | 23.6718 | 22.7528 | 22.7564 | 23.778 | 22.7232 | 23.8074 | 22.9124 | 23.0666 | 23.0201 | 23.8976 | 22.9503 | 22.9868 | 22.9638 | 22.9212 | 22.7815 | 22.6901 | 22.6189 | 22.5396 | 23.6531 | 22.6297 | 22.7429 | 23.0078 | 23.233 | 23.872 | 23.8229 | 23.7401 | 23.6722 | 23.6181 | 23.8033 | 23.7747 | 23.6849 | 23.6093 | 23.4858 | 23.3341 | 23.0179 | 22.9105 | 22.8165 | 22.9216 | 23.6995 | 23.6232 | 23.5738 | 23.517 | 23.4788 | 24.1572 | 24.0679 | 23.9495 | 23.8616 | 23.766 | 23.641 | 23.8676 | 23.8005 | 23.7204 | 23.6585 | 23.6037 | 23.5951 | 23.07 | 22.9818 | 24.1247 | 24.0422 | 24.0349 | 23.9793 | 23.9647 | 23.6055 | 26.9375 | 23.8726 | 23.8223 | 22.3368 | 22.5538 | 22.5047 | 23.4996 | 22.9926 | 23.4406 |  | 21.6019 | 21.5411 | 21.9816 | 24.707 | 23.4492 | 23.4615 | 22.5603 | 22.5224 | 21.6234 | 22.2599 | 10.8072 | 14.2759 | 14.9134 | 11.1132 | 0.00058657 | -0.0029251 | 0.0020911 | 0.0042502 | 0.0015032 | -0.00016313 | 0.01523 | -0.002084 | -0.014224 | -360.1927 | 17.4069 | -360.365 | 17.6204 | -360.7804 | 18.1851 | -360.8481 | 17.5835 | -352.5921 | 18.6943 | -352.5983 | 16.7868 | 5.1774 | 333.8597 | 22.062 | 14.5946 | 12.7441 | 22.0729
13:26 | 16 | 36.2215 |  | 8.5278 | 3.3007 | 1.0604 | 3.2163 | -1.5407 | 12.6536 | 5.7056 | 0.6334 | 0.6788 | 0.98 | 0.766 | -128.7382 | 4.9516 | 6.5504 | 1.8429 | -2.3599 | -0.7863 | 5.1255 |  | 4.9295 | 0.9586 | 3.9907 | 3.3656 | 3.3299 | 1.1057 | -0.7227 | 22.7463 | 22.601 | 22.3956 | 22.3782 | 22.2865 | 22.2752 | 22.1555 | 22.943 | 22.6565 | 22.7052 | 22.6833 | 22.686 | 23.0258 | 22.9423 | 22.8995 | 22.7921 | 22.6798 | 22.613 | 22.4828 | 22.3871 | 22.3107 | 22.2572 | 22.9279 | 22.559 | 22.597 | 22.5791 | 22.5819 | 23.1669 | 22.6835 | 22.9209 | 23.0547 | 22.9739 | 23.4991 | 22.8756 | 22.9158 | 22.8939 | 22.8193 | 22.6788 | 22.5802 | 22.4156 | 22.2585 | 23.2628 | 22.6515 | 22.7526 | 22.9428 | 23.2667 | 23.3189 | 23.2676 | 23.2719 | 23.2098 | 23.1885 | 23.0579 | 23.0722 | 23.1124 | 23.0744 | 22.994 | 22.9028 | 22.7715 | 22.7031 | 22.7111 | 22.8253 | 23.1485 | 23.1747 | 23.1557 | 23.0703 | 23.0105 | 23.8282 | 23.7274 | 23.7417 | 23.6698 | 23.6292 | 23.3066 | 23.3766 | 23.3938 | 23.352 | 23.3622 | 23.3848 | 23.2525 | 22.9691 | 22.7802 | 23.312 | 23.3688 | 23.3298 | 23.3038 | 23.2687 | 23.4831 | 23.6387 | 22.8166 | 22.932 | 21.9758 | 22.0095 | 23.3428 | 22.9348 | 23.2653 | 22.9615 | 23.8489 | 23.0533 | 21.5786 | 22.056 | 21.615 | 21.3481 | 21.8399 | 21.7529 | 21.4403 | 21.5966 | 21.3165 | 21.1882 | 22.6348 | 22.5201 | 25.2128 | 22.3234 | 22.2996 | 22.2328 | 22.1889 | 22.1198 | 22.1997 | 23.2081 | 22.5271 | 22.4481 | 22.507 | 22.4857 | 22.7498 | 22.9992 | 22.9094 | 22.8472 | 22.786 | 22.6621 | 22.6297 | 22.6255 | 22.5626 | 23.6703 | 22.7561 | 22.7527 | 23.7798 | 22.7245 | 23.8092 | 22.9093 | 23.0678 | 23.0239 | 23.9021 | 22.9556 | 22.9927 | 22.9688 | 22.925 | 22.7801 | 22.7008 | 22.6247 | 22.5454 | 23.6536 | 22.6373 | 22.7448 | 23.0133 | 23.2429 | 23.8783 | 23.8304 | 23.7412 | 23.6769 | 23.628 | 23.813 | 23.7779 | 23.6856 | 23.6149 | 23.4943 | 23.3527 | 23.0014 | 22.916 | 22.8045 | 22.9238 | 23.6971 | 23.613 | 23.5621 | 23.5099 | 23.4727 | 24.1527 | 24.068 | 23.9417 | 23.8578 | 23.7635 | 23.6358 | 23.8563 | 23.7947 | 23.7159 | 23.6582 | 23.5951 | 23.5992 | 23.0689 | 22.9827 | 24.1257 | 24.0384 | 24.0297 | 23.9768 | 23.9656 | 23.7907 | 29.4233 | 23.8826 | 23.8362 | 22.3479 | 22.5652 | 22.5669 | 23.5619 | 23.0718 | 23.4687 |  | 21.6142 | 21.5454 | 22.0192 | 24.7021 | 23.446 | 23.4571 | 22.5629 | 22.5199 | 21.6283 | 22.2521 | 10.8298 | 14.3124 | 14.8996 | 11.1221 | 0.00040306 | -0.003082 | 0.0019079 | 0.0044197 | 0.0014871 | -0.00039437 | 0.022153 | -0.018076 | -0.023806 | -360.1711 | 17.4336 | -360.4789 | 17.6738 | -360.8481 | 18.1974 | -360.8174 | 17.5691 | -352.6198 | 18.7292 | -352.6783 | 16.832 | -1.9172 | 341.4806 | 22.0805 | 14.606 | 12.7902 | 22.0741
13:26 | 17 | 36.2576 |  | 8.448 | 3.2761 | 1.0097 | 3.1902 | -1.5546 | 12.6514 | 5.6584 | 0.6324 | 0.6763 | 0.9794 | 0.767 | -128.7 | 4.9549 | 6.5808 | 1.8627 | -2.4307 | -0.7563 | 5.1311 |  | 4.9193 | 0.929 | 3.991 | 3.3678 | 3.3298 | 1.1057 | 1.194 | 22.7354 | 22.598 | 22.3888 | 22.371 | 22.2804 | 22.267 | 22.148 | 22.9348 | 22.6511 | 22.6961 | 22.6741 | 22.6807 | 23.0188 | 22.9335 | 22.9051 | 22.7989 | 22.6863 | 22.6147 | 22.4894 | 22.39 | 22.3116 | 22.2585 | 22.9321 | 22.561 | 22.5995 | 22.5828 | 22.5861 | 23.1649 | 22.6909 | 22.9286 | 23.0467 | 22.9744 | 23.4979 | 22.8735 | 22.9132 | 22.8887 | 22.8158 | 22.6729 | 22.5829 | 22.4099 | 22.2538 | 23.2579 | 22.6495 | 22.753 | 22.9465 | 23.2685 | 23.317 | 23.2671 | 23.2729 | 23.2095 | 23.1869 | 23.0556 | 23.072 | 23.1093 | 23.0779 | 22.9909 | 22.9005 | 22.7721 | 22.7037 | 22.7141 | 22.8279 | 23.1482 | 23.1721 | 23.1489 | 23.0687 | 23.0105 | 23.8302 | 23.7268 | 23.7358 | 23.6677 | 23.6309 | 23.3015 | 23.3721 | 23.3973 | 23.3576 | 23.3594 | 23.3854 | 23.2493 | 22.9685 | 22.7826 | 23.3107 | 23.3678 | 23.332 | 23.3028 | 23.2689 | 23.4889 | 23.6835 | 22.8153 | 22.9395 | 21.9774 | 22.0067 | 23.349 | 22.9409 | 23.2607 | 22.9623 | 23.9293 | 23.1336 | 21.8174 | 22.1802 | 21.8835 | 21.461 | 21.8588 | 21.7598 | 21.442 | 21.5966 | 21.3229 | 21.1868 | 22.6323 | 22.5225 | 25.2249 | 22.3234 | 22.3011 | 22.2274 | 22.195 | 22.1207 | 22.1993 | 23.2102 | 22.5325 | 22.4465 | 22.5141 | 22.4887 | 22.7492 | 23.0021 | 22.9182 | 22.8539 | 22.7876 | 22.6692 | 22.639 | 22.6336 | 22.5712 | 23.6832 | 22.7683 | 22.7597 | 23.7895 | 22.7329 | 23.8124 | 22.917 | 23.0674 | 23.0319 | 23.9024 | 22.9544 | 22.9936 | 22.9711 | 22.9339 | 22.7824 | 22.7058 | 22.6261 | 22.5377 | 23.6559 | 22.6347 | 22.7544 | 23.0163 | 23.2398 | 23.8768 | 23.8281 | 23.7418 | 23.6789 | 23.6224 | 23.8116 | 23.772 | 23.6871 | 23.6137 | 23.4924 | 23.3564 | 23.0014 | 22.9136 | 22.8082 | 22.9233 | 23.7081 | 23.624 | 23.571 | 23.5142 | 23.4801 | 24.1602 | 24.0721 | 23.9534 | 23.8698 | 23.7741 | 23.6412 | 23.8663 | 23.8043 | 23.7237 | 23.673 | 23.5978 | 23.6031 | 23.0711 | 22.9842 | 24.1267 | 24.04 | 24.0319 | 23.9807 | 23.9712 | 24.0362 | 30.9842 | 23.9259 | 23.9028 | 22.3724 | 22.587 | 22.6814 | 23.7162 | 23.2985 | 23.5758 |  | 21.6218 | 21.5501 | 22.0977 | 24.6987 | 23.4416 | 23.4524 | 22.5596 | 22.5248 | 21.6238 | 22.2562 | 10.8144 | 14.2683 | 14.8954 | 11.1076 | 0.00014538 | -0.0026739 | 0.0021889 | 0.0046567 | 0.0013084 | -0.00032539 | 0.015089 | -0.0020252 | -0.025512 | -360.1927 | 17.3946 | -360.3865 | 17.6122 | -360.7712 | 18.2015 | -360.8635 | 17.5773 | -352.5921 | 18.6881 | -352.5583 | 16.7704 | -4.9854 | 352.659 | 22.1118 | 14.5818 | 12.7003 | 22.0743
13:26 | 18 | 36.1704 |  | 8.4643 | 3.335 | 0.965 | 3.2435 | -1.4528 | 12.5949 | 5.6537 | 0.6333 | 0.676 | 0.9781 | 0.7672 | -128.6478 | 4.935 | 6.5667 | 1.8022 | -2.4348 | -0.8457 | 5.0994 |  | 4.989 | 0.8719 | 3.991 | 3.367 | 3.3318 | 1.1078 | -1.0744 | 22.7378 | 22.602 | 22.3899 | 22.3721 | 22.2857 | 22.2706 | 22.1532 | 22.9287 | 22.6584 | 22.7005 | 22.6827 | 22.6853 | 23.0253 | 22.9428 | 22.9007 | 22.7901 | 22.6893 | 22.6105 | 22.4881 | 22.3817 | 22.3106 | 22.2561 | 22.9337 | 22.5646 | 22.5935 | 22.58 | 22.5856 | 23.1649 | 22.6924 | 22.9298 | 23.0475 | 22.9754 | 23.4969 | 22.8733 | 22.9128 | 22.8848 | 22.8146 | 22.6723 | 22.5791 | 22.4108 | 22.2524 | 23.2549 | 22.6487 | 22.7554 | 22.9456 | 23.27 | 23.3147 | 23.2647 | 23.27 | 23.2065 | 23.1834 | 23.0508 | 23.067 | 23.1121 | 23.0779 | 22.9922 | 22.901 | 22.7748 | 22.7036 | 22.7178 | 22.8307 | 23.1408 | 23.178 | 23.1474 | 23.0655 | 23.0091 | 23.8282 | 23.723 | 23.7361 | 23.6676 | 23.6299 | 23.2972 | 23.3739 | 23.3957 | 23.3547 | 23.3542 | 23.386 | 23.2505 | 22.9724 | 22.7809 | 23.3088 | 23.3656 | 23.3333 | 23.299 | 23.2686 | 23.4891 | 25.1834 | 22.8164 | 22.9429 | 21.9841 | 22.0153 | 23.3596 | 22.9551 | 23.2638 | 22.9728 | 23.931 | 23.1766 | 22.1797 | 22.2227 | 22.1895 | 21.6924 | 21.8316 | 21.7344 | 21.4411 | 21.596 | 21.3276 | 21.1876 | 22.6319 | 22.5237 | 25.2312 | 22.3243 | 22.2954 | 22.2247 | 22.1909 | 22.1248 | 22.204 | 23.2109 | 22.5355 | 22.4512 | 22.5235 | 22.493 | 22.7499 | 23.0065 | 22.9222 | 22.8601 | 22.7789 | 22.6732 | 22.6443 | 22.6388 | 22.5754 | 23.6943 | 22.7682 | 22.7665 | 23.7954 | 22.7334 | 23.8184 | 22.922 | 23.0645 | 23.0326 | 23.9017 | 22.9498 | 22.9872 | 22.962 | 22.9308 | 22.7811 | 22.7005 | 22.6189 | 22.5288 | 23.6537 | 22.6301 | 22.7533 | 23.0074 | 23.2345 | 23.8743 | 23.8234 | 23.743 | 23.6804 | 23.6238 | 23.8118 | 23.7728 | 23.6888 | 23.6181 | 23.4893 | 23.3487 | 23.0089 | 22.9128 | 22.8165 | 22.9286 | 23.7069 | 23.6288 | 23.578 | 23.5179 | 23.4922 | 24.1613 | 24.0707 | 23.96 | 23.8748 | 23.7834 | 23.6452 | 23.8693 | 23.8117 | 23.7286 | 23.6743 | 23.6017 | 23.6005 | 23.0744 | 22.9788 | 24.1269 | 24.0444 | 24.0397 | 23.9815 | 23.9724 | 24.3068 | 31.9048 | 24.0949 | 24.0143 | 22.4226 | 22.6112 | 22.8278 | 23.9458 | 23.6276 | 23.7829 |  | 21.6283 | 21.559 | 22.2146 | 24.6945 | 23.44 | 23.4545 | 22.5597 | 22.5203 | 21.6263 | 22.2645 | 10.8391 | 14.2578 | 14.9066 | 11.1461 | -0.00036881 | -0.0028136 | 0.0011147 | 0.0043067 | 0.0013097 | -0.0010971 | 0.02287 | -0.010759 | -0.040066 | -360.1188 | 17.4254 | -360.4542 | 17.6492 | -360.7866 | 18.1728 | -360.7527 | 17.5342 | -352.549 | 18.721 | -352.669 | 16.8094 | 7.4648 | 347.9538 | 22.1579 | 14.5822 | 12.6857 | 22.0733
13:26 | 19 | 36.1515 |  | 8.4551 | 3.3054 | 1.0666 | 3.2337 | -1.4612 | 12.6559 | 5.6508 | 0.634 | 0.6733 | 0.9788 | 0.7674 | -128.6802 | 4.9468 | 6.4562 | 1.8701 | -2.4765 | -0.8874 | 5.0299 |  | 4.9789 | 1.0017 | 3.9904 | 3.3637 | 3.3296 | 1.1065 | -0.1404 | 22.7422 | 22.5989 | 22.3959 | 22.3705 | 22.2897 | 22.2779 | 22.1545 | 22.9323 | 22.6594 | 22.6999 | 22.69 | 22.6843 | 23.0287 | 22.945 | 22.8961 | 22.7852 | 22.6834 | 22.6109 | 22.485 | 22.3798 | 22.311 | 22.2579 | 22.9315 | 22.5604 | 22.5944 | 22.5749 | 22.5847 | 23.1694 | 22.6906 | 22.9276 | 23.0451 | 22.9733 | 23.4965 | 22.8725 | 22.9128 | 22.8829 | 22.8093 | 22.6774 | 22.5804 | 22.4148 | 22.2523 | 23.2549 | 22.6485 | 22.7517 | 22.947 | 23.2685 | 23.3116 | 23.2622 | 23.2661 | 23.2061 | 23.1836 | 23.0516 | 23.0677 | 23.1112 | 23.0709 | 22.9924 | 22.8976 | 22.7749 | 22.7035 | 22.7169 | 22.8295 | 23.1386 | 23.1719 | 23.1457 | 23.0646 | 23.0076 | 23.8206 | 23.7187 | 23.7399 | 23.6642 | 23.6223 | 23.2965 | 23.374 | 23.3911 | 23.3483 | 23.3546 | 23.3865 | 23.2548 | 22.9756 | 22.775 | 23.3096 | 23.3674 | 23.3373 | 23.3036 | 23.2731 | 23.6102 | 28.0419 | 22.8188 | 22.9485 | 21.9893 | 22.0238 | 23.3645 | 22.9688 | 23.2701 | 22.9869 | 23.8396 | 23.155 | 22.5832 | 22.1806 | 22.5192 | 22.0198 | 21.7623 | 21.7095 | 21.4415 | 21.602 | 21.3344 | 21.1924 | 22.6298 | 22.5183 | 25.2348 | 22.3265 | 22.2978 | 22.2258 | 22.1856 | 22.1233 | 22.2089 | 23.2143 | 22.5309 | 22.4565 | 22.533 | 22.4886 | 22.7498 | 23.0069 | 22.9155 | 22.8585 | 22.7811 | 22.6675 | 22.6422 | 22.6358 | 22.5732 | 23.6902 | 22.7619 | 22.7659 | 23.792 | 22.7347 | 23.8198 | 22.9183 | 23.0677 | 23.0421 | 23.9026 | 22.9492 | 22.994 | 22.9664 | 22.928 | 22.7851 | 22.7007 | 22.6197 | 22.5378 | 23.6555 | 22.6335 | 22.751 | 23.0046 | 23.2384 | 23.8805 | 23.8287 | 23.7421 | 23.6806 | 23.6346 | 23.8134 | 23.7754 | 23.6861 | 23.6158 | 23.4946 | 23.3479 | 23.0116 | 22.9136 | 22.8163 | 22.9326 | 23.7038 | 23.6256 | 23.5716 | 23.5133 | 23.5 | 24.1633 | 24.0704 | 23.9592 | 23.8751 | 23.796 | 23.6447 | 23.8657 | 23.8075 | 23.7293 | 23.6653 | 23.6019 | 23.5963 | 23.0733 | 22.9756 | 24.1195 | 24.0374 | 24.0404 | 23.9787 | 23.9632 | 24.5229 | 32.2412 | 24.4039 | 24.1236 | 22.4888 | 22.6284 | 22.9912 | 24.1969 | 23.9606 | 24.0369 |  | 21.6445 | 21.5713 | 22.3606 | 24.6991 | 23.4401 | 23.4553 | 22.5694 | 22.5272 | 21.6322 | 22.2581 | 10.839 | 14.2792 | 14.8867 | 11.1175 | 0.00022488 | -0.0027408 | 0.0013319 | 0.0047122 | 0.0010312 | -0.00047921 | 0.025986 | -0.012801 | -0.024499 | -360.2142 | 17.4254 | -360.4081 | 17.6328 | -360.7712 | 18.2056 | -360.8727 | 17.6122 | -352.6752 | 18.723 | -352.5829 | 16.7868 | 7.2121 | 357.5975 | 22.2122 | 14.583 | 12.7269 | 22.0797
13:26 | 20 | 36.1914 |  | 8.5367 | 3.3046 | 1.03 | 3.2488 | -1.5383 | 12.6272 | 5.6726 | 0.633 | 0.6764 | 0.9801 | 0.7673 | -128.6921 | 4.9844 | 6.5558 | 1.8259 | -2.4219 | -0.8433 | 5.0247 |  | 4.9201 | 0.9038 | 3.9905 | 3.3681 | 3.3306 | 1.1085 | 0.4801 | 22.7354 | 22.5961 | 22.3948 | 22.3684 | 22.2862 | 22.272 | 22.1465 | 22.9369 | 22.6494 | 22.6947 | 22.6877 | 22.6799 | 23.0242 | 22.9374 | 22.8988 | 22.7891 | 22.6854 | 22.617 | 22.4883 | 22.3869 | 22.3193 | 22.2651 | 22.9334 | 22.5639 | 22.5971 | 22.5829 | 22.5854 | 23.1713 | 22.6908 | 22.9305 | 23.0383 | 22.9704 | 23.493 | 22.8693 | 22.9095 | 22.8812 | 22.8047 | 22.6762 | 22.5783 | 22.4099 | 22.2501 | 23.2523 | 22.6432 | 22.7459 | 22.9502 | 23.2633 | 23.3113 | 23.263 | 23.2679 | 23.2039 | 23.1763 | 23.0562 | 23.0657 | 23.109 | 23.0711 | 22.9958 | 22.8963 | 22.7756 | 22.6994 | 22.7206 | 22.8256 | 23.1361 | 23.1641 | 23.144 | 23.0655 | 23.0075 | 23.8213 | 23.7197 | 23.7368 | 23.6677 | 23.6211 | 23.3007 | 23.3715 | 23.3893 | 23.3474 | 23.3595 | 23.387 | 23.2555 | 22.9748 | 22.7771 | 23.3109 | 23.3685 | 23.3344 | 23.3028 | 23.277 | 23.8566 | 30.2887 | 22.821 | 22.9972 | 21.9989 | 22.0314 | 23.3748 | 23.0041 | 23.276 | 23.0071 | 23.6609 | 23.0633 | 22.9012 | 22.0904 | 22.8481 | 22.3393 | 21.6995 | 21.6872 | 21.4493 | 21.6109 | 21.3433 | 21.1971 | 22.6328 | 22.5194 | 25.2379 | 22.3223 | 22.303 | 22.2242 | 22.1895 | 22.1184 | 22.2033 | 23.2111 | 22.5317 | 22.4576 | 22.5416 | 22.482 | 22.7398 | 23.0123 | 22.9137 | 22.8535 | 22.7779 | 22.6654 | 22.6453 | 22.63 | 22.5762 | 23.6854 | 22.7615 | 22.7642 | 23.7911 | 22.7387 | 23.8174 | 22.9198 | 23.0748 | 23.0592 | 23.9075 | 22.957 | 23.0049 | 22.9744 | 22.9362 | 22.7959 | 22.7074 | 22.6316 | 22.553 | 23.6601 | 22.6428 | 22.7517 | 23.0133 | 23.2405 | 23.8781 | 23.8318 | 23.7409 | 23.6739 | 23.6294 | 23.8118 | 23.7726 | 23.6833 | 23.6146 | 23.4945 | 23.3476 | 23.017 | 22.9111 | 22.8228 | 22.9261 | 23.7007 | 23.6256 | 23.5678 | 23.5112 | 23.5002 | 24.1677 | 24.0722 | 23.9556 | 23.867 | 23.8115 | 23.6429 | 23.8673 | 23.7978 | 23.7232 | 23.6603 | 23.6017 | 23.5899 | 23.0654 | 22.9709 | 24.1173 | 24.029 | 24.0298 | 23.9747 | 23.9584 | 24.7009 | 32.4996 | 24.6856 | 24.225 | 22.5747 | 22.6519 | 23.1758 | 24.4464 | 24.2738 | 24.2959 |  | 21.6605 | 21.569 | 22.5453 | 24.6939 | 23.434 | 23.4523 | 22.5712 | 22.5315 | 21.6283 | 22.2531 | 10.8348 | 14.2819 | 14.8958 | 11.1276 | 5.0038e-06 | -0.0035923 | 0.0012999 | 0.0040691 | 0.0014932 | -0.00084053 | 0.0090358 | -0.0035998 | -0.010623 | -360.1435 | 17.4192 | -360.4604 | 17.6779 | -360.8574 | 18.1912 | -360.7897 | 17.5301 | -352.5521 | 18.6984 | -352.6352 | 16.8258 | 2.8527 | 347.7679 | 22.2759 | 14.5889 | 12.6873 | 22.0799
13:26 | 21 | 36.0475 |  | 8.5014 | 3.3004 | 1.0199 | 3.2418 | -1.5 | 12.6528 | 5.6693 | 0.6337 | 0.6741 | 0.9799 | 0.7669 | -128.7062 | 4.8926 | 6.4612 | 1.8267 | -2.4029 | -0.8473 | 4.9984 |  | 4.8881 | 1.0398 | 3.991 | 3.3661 | 3.3297 | 1.1051 | 0.6658 | 22.73 | 22.5946 | 22.3878 | 22.3684 | 22.2836 | 22.2661 | 22.1424 | 22.9344 | 22.6527 | 22.696 | 22.6857 | 22.6765 | 23.0244 | 22.9398 | 22.9 | 22.7834 | 22.688 | 22.6143 | 22.4863 | 22.3767 | 22.3114 | 22.2619 | 22.9244 | 22.5609 | 22.5919 | 22.5858 | 22.5836 | 23.1646 | 22.6861 | 22.9301 | 23.0431 | 22.975 | 23.4989 | 22.8716 | 22.9132 | 22.8836 | 22.8161 | 22.6776 | 22.5856 | 22.4151 | 22.26 | 23.2556 | 22.6474 | 22.7457 | 22.9523 | 23.2667 | 23.3111 | 23.2672 | 23.2674 | 23.2068 | 23.1745 | 23.0581 | 23.0677 | 23.115 | 23.0748 | 23.0004 | 22.9043 | 22.768 | 22.7034 | 22.7444 | 22.8276 | 23.135 | 23.1633 | 23.1479 | 23.0664 | 23.0106 | 23.824 | 23.7262 | 23.7361 | 23.6678 | 23.6281 | 23.3043 | 23.3741 | 23.3927 | 23.3489 | 23.3616 | 23.3873 | 23.2502 | 22.9705 | 22.7811 | 23.3066 | 23.3674 | 23.3315 | 23.3037 | 23.2736 | 24.1021 | 31.753 | 22.825 | 23.1401 | 22.009 | 22.0434 | 23.402 | 23.1205 | 23.2887 | 23.0536 | 23.5123 | 22.9592 | 23.0461 | 22 | 23.1592 | 22.4995 | 21.6479 | 21.6698 | 21.4625 | 21.62 | 21.3545 | 21.2138 | 22.6366 | 22.5202 | 25.2158 | 22.3166 | 22.3 | 22.2183 | 22.1905 | 22.1172 | 22.2004 | 23.2056 | 22.5333 | 22.4531 | 22.5533 | 22.4761 | 22.7332 | 23.0105 | 22.9143 | 22.8537 | 22.7758 | 22.6716 | 22.6463 | 22.6337 | 22.5825 | 23.6863 | 22.7654 | 22.768 | 23.7927 | 22.7431 | 23.8139 | 22.9248 | 23.0745 | 23.0628 | 23.9006 | 22.9569 | 22.9995 | 22.9698 | 22.9362 | 22.7923 | 22.7006 | 22.6339 | 22.5486 | 23.653 | 22.6385 | 22.7507 | 23.0104 | 23.2488 | 23.8791 | 23.8325 | 23.7448 | 23.6761 | 23.6326 | 23.8149 | 23.7761 | 23.6843 | 23.6199 | 23.4964 | 23.348 | 23.0168 | 22.9144 | 22.8301 | 22.9268 | 23.6901 | 23.6158 | 23.5618 | 23.5066 | 23.4951 | 24.158 | 24.0634 | 23.9407 | 23.8502 | 23.824 | 23.6331 | 23.858 | 23.789 | 23.7077 | 23.651 | 23.5964 | 23.5921 | 23.0694 | 22.9767 | 24.1248 | 24.0298 | 24.026 | 23.9763 | 23.9623 | 24.8903 | 32.2832 | 24.8823 | 24.324 | 22.6834 | 22.6939 | 23.3697 | 24.6997 | 24.5961 | 24.565 |  | 21.6945 | 21.577 | 22.7491 | 24.6934 | 23.4355 | 23.4524 | 22.5812 | 22.5288 | 21.6262 | 22.2538 | 10.8313 | 14.2712 | 14.9199 | 11.1313 | 0.00019008 | -0.0029124 | 0.0011328 | 0.0041604 | 0.0011877 | -0.00058566 | 0.034257 | 0.005134 | -0.024421 | -360.1619 | 17.4233 | -360.4081 | 17.6143 | -360.7466 | 18.1604 | -360.8204 | 17.5753 | -352.626 | 18.7189 | -352.6013 | 16.7848 | 10.9302 | 354.2121 | 22.3525 | 14.5955 | 12.7165 | 22.0775
13:26 | 22 | 35.9715 |  | 8.5223 | 3.3742 | 1.1036 | 3.3516 | -1.459 | 12.6771 | 5.6832 | 0.6337 | 0.6752 | 0.9774 | 0.767 | -128.6919 | 4.7772 | 6.4025 | 1.9848 | -2.3663 | -0.8408 | 5.0979 |  | 4.9335 | 1.0058 | 3.9901 | 3.365 | 3.3275 | 1.1048 | -0.206 | 22.7307 | 22.5954 | 22.3827 | 22.365 | 22.2798 | 22.2766 | 22.1455 | 22.9366 | 22.6587 | 22.6936 | 22.6898 | 22.6816 | 23.028 | 22.9427 | 22.8997 | 22.7829 | 22.6903 | 22.6122 | 22.4896 | 22.3794 | 22.3087 | 22.2623 | 22.9252 | 22.5637 | 22.596 | 22.5858 | 22.5894 | 23.1676 | 22.6887 | 22.928 | 23.0443 | 22.9783 | 23.4992 | 22.8725 | 22.9172 | 22.8861 | 22.8197 | 22.6817 | 22.5793 | 22.4168 | 22.2591 | 23.2587 | 22.6518 | 22.7488 | 22.9538 | 23.2638 | 23.3112 | 23.2607 | 23.2619 | 23.2074 | 23.1773 | 23.0558 | 23.067 | 23.1072 | 23.0712 | 22.995 | 22.8991 | 22.7587 | 22.699 | 22.7611 | 22.8283 | 23.1376 | 23.168 | 23.1451 | 23.0668 | 23.0128 | 23.8188 | 23.7289 | 23.7392 | 23.6704 | 23.6331 | 23.3051 | 23.3716 | 23.397 | 23.3477 | 23.3619 | 23.3892 | 23.2518 | 22.9685 | 22.7839 | 23.3156 | 23.3724 | 23.3375 | 23.3087 | 23.2716 | 24.3183 | 32.5168 | 22.8478 | 23.3103 | 22.0127 | 22.0543 | 23.4448 | 23.3165 | 23.3293 | 23.1835 | 23.423 | 22.8759 | 22.9994 | 21.9007 | 23.3878 | 22.5302 | 21.598 | 21.6378 | 21.4643 | 21.6201 | 21.364 | 21.2201 | 22.6406 | 22.5236 | 25.2021 | 22.3221 | 22.3009 | 22.2199 | 22.1953 | 22.1169 | 22.2015 | 23.2059 | 22.533 | 22.4492 | 22.5745 | 22.4792 | 22.7406 | 23.0059 | 22.9128 | 22.8565 | 22.7748 | 22.6768 | 22.6491 | 22.6302 | 22.58 | 23.6871 | 22.7643 | 22.7733 | 23.7923 | 22.7525 | 23.8161 | 22.9254 | 23.0743 | 23.064 | 23.8986 | 22.9525 | 22.9996 | 22.9724 | 22.9325 | 22.7895 | 22.6989 | 22.6322 | 22.5441 | 23.6521 | 22.6326 | 22.7483 | 23.009 | 23.2556 | 23.8828 | 23.8313 | 23.745 | 23.6806 | 23.6382 | 23.8111 | 23.7737 | 23.6881 | 23.6182 | 23.4958 | 23.3531 | 23.0156 | 22.9158 | 22.8341 | 22.9275 | 23.6924 | 23.614 | 23.5625 | 23.5099 | 23.5022 | 24.1522 | 24.0578 | 23.9385 | 23.8519 | 23.852 | 23.6349 | 23.8602 | 23.7927 | 23.7075 | 23.6532 | 23.5962 | 23.6006 | 23.073 | 22.982 | 24.129 | 24.0389 | 24.0361 | 23.9824 | 23.9663 | 25.1018 | 32.1287 | 25.0643 | 24.4128 | 22.8109 | 22.7538 | 23.5878 | 24.961 | 24.9285 | 24.8484 |  | 21.752 | 21.5914 | 22.9444 | 24.6876 | 23.4349 | 23.4505 | 22.5914 | 22.5243 | 21.62 | 22.2584 | 10.8102 | 14.2642 | 14.9199 | 11.1102 | -0.00046814 | -0.0030298 | 0.0015544 | 0.0041839 | 0.0017729 | -0.00063264 | 0.026674 | -0.017313 | -0.024039 | -360.1004 | 17.3946 | -360.4696 | 17.6985 | -360.8666 | 18.2241 | -360.8512 | 17.5424 | -352.5798 | 18.6902 | -352.6598 | 16.8464 | 3.4952 | 356.846 | 22.4384 | 14.592 | 12.9204 | 22.0722
13:26 | 23 | 36.051 |  | 8.527 | 3.4781 | 1.1111 | 3.3292 | -1.4999 | 12.5782 | 5.6912 | 0.6334 | 0.6745 | 0.9827 | 0.7668 | -128.6578 | 4.9113 | 6.4917 | 2.0091 | -2.3877 | -0.8618 | 5.0648 |  | 4.9444 | 0.9267 | 3.9904 | 3.3654 | 3.3293 | 1.1056 | 1.5081 | 22.7304 | 22.5932 | 22.3842 | 22.3622 | 22.2749 | 22.2753 | 22.1466 | 22.9396 | 22.6547 | 22.6894 | 22.6879 | 22.6868 | 23.026 | 22.9391 | 22.8943 | 22.7819 | 22.6861 | 22.6097 | 22.4871 | 22.3854 | 22.3067 | 22.2644 | 22.9279 | 22.5583 | 22.5981 | 22.5808 | 22.586 | 23.1676 | 22.6862 | 22.9221 | 23.0482 | 22.9744 | 23.4921 | 22.8708 | 22.9073 | 22.8838 | 22.8137 | 22.6807 | 22.5745 | 22.4117 | 22.258 | 23.2626 | 22.6506 | 22.7488 | 22.9501 | 23.261 | 23.3164 | 23.2563 | 23.2651 | 23.2072 | 23.1851 | 23.0526 | 23.0652 | 23.1044 | 23.0695 | 22.9937 | 22.8973 | 22.7591 | 22.6948 | 22.7653 | 22.8291 | 23.1382 | 23.1748 | 23.1477 | 23.0661 | 23.0118 | 23.8204 | 23.7282 | 23.7447 | 23.6728 | 23.6345 | 23.3016 | 23.3671 | 23.3987 | 23.3486 | 23.3591 | 23.3888 | 23.2537 | 22.968 | 22.7825 | 23.3171 | 23.3706 | 23.337 | 23.3033 | 23.2693 | 24.5278 | 32.7922 | 22.8773 | 23.4501 | 22.0224 | 22.0649 | 23.4992 | 23.5631 | 23.4149 | 23.3844 | 23.3004 | 22.7895 | 22.9527 | 21.7776 | 23.4754 | 22.5574 | 21.5313 | 21.5921 | 21.4599 | 21.6103 | 21.3667 | 21.21 | 22.6447 | 22.5261 | 25.2218 | 22.3273 | 22.3033 | 22.2224 | 22.1973 | 22.1145 | 22.1997 | 23.206 | 22.5294 | 22.4454 | 22.5866 | 22.4789 | 22.7437 | 23.0108 | 22.9184 | 22.8596 | 22.7788 | 22.6757 | 22.6469 | 22.6225 | 22.5767 | 23.6889 | 22.7646 | 22.7724 | 23.7957 | 22.7632 | 23.8155 | 22.9252 | 23.0719 | 23.0709 | 23.9067 | 22.9537 | 23.0019 | 22.972 | 22.9297 | 22.7943 | 22.7011 | 22.6254 | 22.5515 | 23.6552 | 22.6308 | 22.7488 | 23.0121 | 23.257 | 23.8786 | 23.8257 | 23.7416 | 23.6756 | 23.6346 | 23.8134 | 23.7686 | 23.6887 | 23.6166 | 23.4864 | 23.3554 | 23.0121 | 22.9119 | 22.8315 | 22.921 | 23.7024 | 23.6227 | 23.5727 | 23.5218 | 23.5208 | 24.1582 | 24.071 | 23.9511 | 23.8658 | 23.8882 | 23.6468 | 23.8742 | 23.8009 | 23.7232 | 23.6647 | 23.6067 | 23.5996 | 23.0672 | 22.9743 | 24.1268 | 24.0384 | 24.0288 | 23.9802 | 23.9585 | 25.2917 | 32.3785 | 25.2482 | 24.4912 | 22.9524 | 22.8283 | 23.8435 | 25.2134 | 25.2629 | 25.1245 |  | 21.8268 | 21.5981 | 23.1636 | 24.6908 | 23.4279 | 23.4462 | 22.6084 | 22.5145 | 21.6172 | 22.2536 | 10.8038 | 14.2721 | 14.8726 | 11.0682 | 0.00017786 | -0.0026938 | 0.001285 | 0.003889 | 0.00079712 | -0.00040873 | 0.032092 | -0.017625 | -0.012566 | -360.2173 | 17.4521 | -360.4604 | 17.6451 | -360.7773 | 18.1687 | -360.8235 | 17.5835 | -352.6475 | 18.7333 | -352.6444 | 16.793 | 6.4723 | 356.802 | 22.5375 | 14.5724 | 12.8731 | 22.0659
13:26 | 24 | 35.9774 |  | 8.5025 | 3.3393 | 1.0064 | 3.3079 | -1.5677 | 12.5621 | 5.5249 | 0.6332 | 0.6735 | 0.9777 | 0.7665 | -128.704 | 4.8131 | 6.4887 | 1.9999 | -2.3471 | -0.7534 | 5.0899 |  | 4.9253 | 0.8134 | 3.9895 | 3.3671 | 3.327 | 1.1057 | -0.8249 | 22.7352 | 22.5937 | 22.3847 | 22.3625 | 22.2739 | 22.2718 | 22.1462 | 22.9378 | 22.6552 | 22.6928 | 22.684 | 22.6875 | 23.023 | 22.9382 | 22.888 | 22.7765 | 22.6811 | 22.6092 | 22.4769 | 22.3811 | 22.2957 | 22.2559 | 22.918 | 22.5529 | 22.5926 | 22.5712 | 22.5826 | 23.1612 | 22.6827 | 22.9188 | 23.0559 | 22.9757 | 23.495 | 22.8735 | 22.9057 | 22.8849 | 22.8184 | 22.6789 | 22.5823 | 22.4133 | 22.2602 | 23.265 | 22.6528 | 22.7465 | 22.9506 | 23.272 | 23.321 | 23.2667 | 23.2715 | 23.2061 | 23.193 | 23.0548 | 23.0725 | 23.1114 | 23.0736 | 22.9958 | 22.9104 | 22.7657 | 22.7049 | 22.7743 | 22.8324 | 23.14 | 23.1733 | 23.1466 | 23.0686 | 23.0117 | 23.8211 | 23.7275 | 23.7431 | 23.6693 | 23.632 | 23.2956 | 23.3698 | 23.3922 | 23.3446 | 23.3562 | 23.3895 | 23.2583 | 22.9689 | 22.7795 | 23.31 | 23.3649 | 23.3332 | 23.3016 | 23.2677 | 24.7473 | 33.3133 | 22.9073 | 23.589 | 22.0266 | 22.0736 | 23.5616 | 23.8386 | 23.5248 | 23.604 | 23.1473 | 22.7128 | 22.9356 | 21.6884 | 23.4134 | 22.5796 | 21.4707 | 21.5613 | 21.4687 | 21.6176 | 21.3787 | 21.2183 | 22.6455 | 22.5261 | 25.2378 | 22.3184 | 22.2968 | 22.2186 | 22.1915 | 22.113 | 22.1974 | 23.2056 | 22.5306 | 22.4425 | 22.5966 | 22.4795 | 22.7436 | 23.0094 | 22.9199 | 22.8583 | 22.7755 | 22.6748 | 22.6387 | 22.6191 | 22.5749 | 23.6904 | 22.7686 | 22.7669 | 23.7942 | 22.7693 | 23.8103 | 22.9239 | 23.0688 | 23.0815 | 23.9029 | 22.9588 | 22.9986 | 22.9732 | 22.9273 | 22.7956 | 22.695 | 22.6212 | 22.5522 | 23.652 | 22.6349 | 22.7484 | 23.0055 | 23.2621 | 23.8772 | 23.8236 | 23.7411 | 23.676 | 23.6336 | 23.8144 | 23.7691 | 23.6852 | 23.6164 | 23.4836 | 23.3488 | 23.0222 | 22.9104 | 22.8414 | 22.9224 | 23.7049 | 23.6266 | 23.5769 | 23.5209 | 23.5377 | 24.1591 | 24.0735 | 23.9562 | 23.8654 | 23.9185 | 23.6495 | 23.8743 | 23.8058 | 23.7284 | 23.6675 | 23.6114 | 23.5974 | 23.0694 | 22.9753 | 24.1285 | 24.0357 | 24.0258 | 23.9722 | 23.96 | 25.4399 | 32.3339 | 25.513 | 24.566 | 23.0909 | 22.9117 | 24.1175 | 25.4565 | 25.6114 | 25.3883 |  | 21.9099 | 21.6099 | 23.3995 | 24.691 | 23.4314 | 23.444 | 22.6301 | 22.5181 | 21.6206 | 22.2523 | 10.8509 | 14.2844 | 14.8939 | 11.1005 | 0.00057366 | -0.0030562 | 0.0017035 | 0.0041901 | 0.0016301 | -0.0009747 | 0.024507 | -0.0058841 | -0.018404 | -360.0573 | 17.3597 | -360.3558 | 17.6369 | -360.8174 | 18.2261 | -360.805 | 17.5424 | -352.5121 | 18.645 | -352.5706 | 16.8197 | -6.2421 | 356.9157 | 22.6425 | 14.5891 | 12.721 | 22.0694
13:26 | 25 | 35.9178 |  | 8.5535 | 3.3774 | 1.0416 | 3.2917 | -1.5738 | 12.5405 | 5.5292 | 0.6349 | 0.6761 | 0.98 | 0.7675 | -128.7197 | 4.8907 | 6.4504 | 2.0493 | -2.3386 | -0.8446 | 5.1106 |  | 4.8965 | 0.8937 | 3.9896 | 3.3648 | 3.3312 | 1.1058 | 1.9664 | 22.7392 | 22.5994 | 22.3892 | 22.3707 | 22.2896 | 22.2777 | 22.151 | 22.9441 | 22.6594 | 22.6937 | 22.6858 | 22.6929 | 23.0302 | 22.9478 | 22.8984 | 22.78 | 22.6832 | 22.6125 | 22.4819 | 22.3831 | 22.3056 | 22.2551 | 22.9272 | 22.5603 | 22.5947 | 22.5761 | 22.5862 | 23.1669 | 22.6855 | 22.9252 | 23.0623 | 22.9793 | 23.4996 | 22.8774 | 22.9159 | 22.8874 | 22.823 | 22.6782 | 22.5863 | 22.4154 | 22.2595 | 23.2604 | 22.6551 | 22.7484 | 22.9507 | 23.2809 | 23.3238 | 23.2768 | 23.2752 | 23.2119 | 23.1936 | 23.0621 | 23.0772 | 23.1171 | 23.0755 | 22.9995 | 22.9191 | 22.7703 | 22.7106 | 22.7781 | 22.8357 | 23.1336 | 23.1729 | 23.1471 | 23.072 | 23.0163 | 23.8192 | 23.7183 | 23.7364 | 23.6669 | 23.6343 | 23.3002 | 23.3708 | 23.3876 | 23.3424 | 23.3578 | 23.3844 | 23.2712 | 22.9747 | 22.7855 | 23.3166 | 23.3707 | 23.3389 | 23.3058 | 23.2737 | 25.1132 | 33.8072 | 22.944 | 23.7174 | 22.0318 | 22.0981 | 23.6348 | 24.1199 | 23.6524 | 23.8402 | 23.0349 | 22.6384 | 22.8927 | 21.6458 | 23.2533 | 22.5917 | 21.4318 | 21.5584 | 21.4836 | 21.6352 | 21.4088 | 21.2449 | 22.6458 | 22.5276 | 25.2433 | 22.3215 | 22.2999 | 22.2242 | 22.1911 | 22.1187 | 22.2029 | 23.2077 | 22.5349 | 22.4508 | 22.6151 | 22.4859 | 22.7465 | 23.0021 | 22.9174 | 22.8553 | 22.7699 | 22.6776 | 22.6377 | 22.6182 | 22.5785 | 23.6885 | 22.7676 | 22.7697 | 23.7896 | 22.7728 | 23.8133 | 22.9231 | 23.0725 | 23.0919 | 23.9004 | 22.9612 | 23.0028 | 22.9798 | 22.9319 | 22.7902 | 22.6962 | 22.6244 | 22.5563 | 23.6522 | 22.6384 | 22.7469 | 23.0044 | 23.2744 | 23.8768 | 23.8235 | 23.7405 | 23.6739 | 23.6373 | 23.8076 | 23.7721 | 23.6812 | 23.6153 | 23.4878 | 23.3353 | 23.0452 | 22.9098 | 22.8563 | 22.9297 | 23.7022 | 23.6212 | 23.5736 | 23.5149 | 23.5445 | 24.1533 | 24.0646 | 23.9544 | 23.863 | 23.9466 | 23.6441 | 23.8673 | 23.8003 | 23.7197 | 23.6655 | 23.6084 | 23.6055 | 23.0711 | 22.9774 | 24.1268 | 24.038 | 24.0341 | 23.9742 | 23.9706 | 25.5559 | 31.8969 | 25.748 | 24.6456 | 23.2211 | 22.9886 | 24.3943 | 25.6856 | 25.9575 | 25.6472 |  | 22.0005 | 21.626 | 23.637 | 24.6836 | 23.4258 | 23.4412 | 22.65 | 22.5198 | 21.6177 | 22.2512 | 10.8066 | 14.2962 | 14.8689 | 11.106 | 5.7995e-05 | -0.0028385 | 0.0017982 | 0.0045216 | 0.0011212 | -0.00010517 | 0.0062841 | 0.0070639 | -0.026653 | -360.1865 | 17.4397 | -360.4789 | 17.643 | -360.765 | 18.1666 | -360.802 | 17.5691 | -352.6444 | 18.7374 | -352.6413 | 16.8115 | -1.5645 | 356.3227 | 22.7497 | 14.5825 | 12.7581 | 22.0688
13:26 | 26 | 36.0038 |  | 8.4894 | 3.3653 | 1.0509 | 3.3444 | -1.5025 | 12.5695 | 5.6642 | 0.634 | 0.6764 | 0.9788 | 0.7659 | -128.7595 | 4.8134 | 6.4943 | 2.0291 | -2.3124 | -0.7095 | 5.1946 |  | 4.8758 | 0.9437 | 3.9888 | 3.3636 | 3.3267 | 1.1077 | 0.7978 | 22.7393 | 22.6039 | 22.3933 | 22.371 | 22.2972 | 22.2831 | 22.1563 | 22.9531 | 22.659 | 22.6999 | 22.688 | 22.6972 | 23.0345 | 22.9495 | 22.9034 | 22.7904 | 22.6862 | 22.6129 | 22.4961 | 22.3823 | 22.3155 | 22.2598 | 22.9372 | 22.5602 | 22.5994 | 22.5859 | 22.5862 | 23.173 | 22.6854 | 22.9291 | 23.06 | 22.9765 | 23.4968 | 22.8772 | 22.9166 | 22.8838 | 22.824 | 22.6804 | 22.5834 | 22.4182 | 22.261 | 23.2573 | 22.6488 | 22.7465 | 22.9457 | 23.2853 | 23.3258 | 23.2753 | 23.2786 | 23.2204 | 23.1961 | 23.0656 | 23.0778 | 23.1193 | 23.0743 | 23.0002 | 22.9207 | 22.7706 | 22.7094 | 22.7748 | 22.8371 | 23.1411 | 23.1765 | 23.1559 | 23.0758 | 23.026 | 23.8253 | 23.7208 | 23.7415 | 23.6707 | 23.6441 | 23.3092 | 23.3753 | 23.3962 | 23.3514 | 23.3626 | 23.3876 | 23.2725 | 22.9743 | 22.7865 | 23.3177 | 23.3705 | 23.3424 | 23.3064 | 23.274 | 25.4736 | 34.244 | 22.9836 | 23.8107 | 22.0472 | 22.1424 | 23.7008 | 24.3978 | 23.8046 | 24.1044 | 22.9568 | 22.5634 | 22.8931 | 21.6076 | 23.0538 | 22.6489 | 21.3938 | 21.5598 | 21.4987 | 21.6489 | 21.4512 | 21.2817 | 22.6407 | 22.5203 | 25.2252 | 22.3272 | 22.3045 | 22.2205 | 22.192 | 22.1172 | 22.2047 | 23.2073 | 22.5294 | 22.4546 | 22.6251 | 22.4844 | 22.7458 | 23.0049 | 22.9205 | 22.861 | 22.7765 | 22.6828 | 22.6465 | 22.6221 | 22.5832 | 23.6864 | 22.7693 | 22.7701 | 23.7893 | 22.7837 | 23.8198 | 22.9257 | 23.0678 | 23.0921 | 23.8962 | 22.9532 | 22.9943 | 22.9722 | 22.9283 | 22.7816 | 22.6922 | 22.6194 | 22.5517 | 23.6465 | 22.6272 | 22.7418 | 23.0031 | 23.2868 | 23.8764 | 23.8205 | 23.7426 | 23.669 | 23.6418 | 23.8092 | 23.7717 | 23.6837 | 23.6157 | 23.4923 | 23.3317 | 23.0598 | 22.9128 | 22.8636 | 22.9324 | 23.7023 | 23.6177 | 23.5716 | 23.5203 | 23.5577 | 24.1581 | 24.067 | 23.9564 | 23.8702 | 23.9799 | 23.6434 | 23.8733 | 23.8053 | 23.7254 | 23.6677 | 23.6148 | 23.6141 | 23.0725 | 22.9825 | 24.1249 | 24.0433 | 24.0342 | 23.9876 | 23.9759 | 25.6416 | 31.3661 | 25.9023 | 24.7248 | 23.3459 | 23.0616 | 24.6616 | 25.8969 | 26.2962 | 25.8971 |  | 22.1031 | 21.6503 | 23.8607 | 24.6846 | 23.4269 | 23.4441 | 22.6812 | 22.5292 | 21.6167 | 22.248 | 10.8214 | 14.3037 | 14.8967 | 11.1071 | -0.0002483 | -0.0025776 | 0.0013052 | 0.0041449 | 0.0016386 | -0.00050624 | 0.0062329 | -0.0050696 | -0.029562 | -360.1558 | 17.3905 | -360.3804 | 17.6533 | -360.8389 | 18.2426 | -360.882 | 17.5876 | -352.5798 | 18.684 | -352.5706 | 16.8197 | -9.7311 | 363.1305 | 22.8591 | 14.6002 | 12.9008 | 22.0729
13:26 | 27 | 36.2113 |  | 8.5343 | 3.3152 | 1.0194 | 3.3406 | -1.5343 | 12.5656 | 5.5288 | 0.6349 | 0.6744 | 0.9808 | 0.7659 | -128.7179 | 4.8315 | 6.4324 | 1.8973 | -2.2926 | -0.877 | 5.0729 |  | 4.9189 | 0.8943 | 3.9896 | 3.3659 | 3.3294 | 1.108 | 0.6315 | 22.7341 | 22.6078 | 22.3943 | 22.3678 | 22.2863 | 22.2816 | 22.1574 | 22.9504 | 22.6545 | 22.7028 | 22.69 | 22.7032 | 23.0301 | 22.943 | 22.8955 | 22.7881 | 22.6845 | 22.6122 | 22.4879 | 22.38 | 22.3119 | 22.2609 | 22.9327 | 22.5591 | 22.5926 | 22.5852 | 22.5847 | 23.1684 | 22.6808 | 22.9297 | 23.0593 | 22.9806 | 23.5014 | 22.8807 | 22.9176 | 22.8895 | 22.8307 | 22.6882 | 22.5852 | 22.4152 | 22.2613 | 23.2596 | 22.6513 | 22.751 | 22.9522 | 23.2823 | 23.3231 | 23.2672 | 23.2747 | 23.2184 | 23.2019 | 23.0627 | 23.0728 | 23.1176 | 23.0739 | 22.9976 | 22.9148 | 22.7687 | 22.7039 | 22.7748 | 22.8319 | 23.1479 | 23.1706 | 23.1564 | 23.0725 | 23.0329 | 23.8241 | 23.725 | 23.7417 | 23.6734 | 23.6445 | 23.3027 | 23.3753 | 23.3955 | 23.3514 | 23.3586 | 23.3935 | 23.2654 | 22.9697 | 22.7907 | 23.3147 | 23.3676 | 23.3386 | 23.3076 | 23.2711 | 25.7103 | 34.9356 | 23.0102 | 23.8712 | 22.0673 | 22.2012 | 23.7693 | 24.6801 | 23.966 | 24.3955 | 22.8636 | 22.4722 | 23.0109 | 21.6264 | 22.8496 | 22.8491 | 21.3519 | 21.5432 | 21.518 | 21.6607 | 21.4901 | 21.3181 | 22.6393 | 22.5247 | 25.2271 | 22.3255 | 22.303 | 22.2227 | 22.197 | 22.1161 | 22.2011 | 23.2071 | 22.5334 | 22.4549 | 22.6381 | 22.492 | 22.7501 | 23.0046 | 22.915 | 22.8624 | 22.7727 | 22.6779 | 22.6462 | 22.6215 | 22.5811 | 23.6879 | 22.7644 | 22.7637 | 23.7825 | 22.7895 | 23.8162 | 22.9231 | 23.0627 | 23.0932 | 23.8974 | 22.9537 | 22.9923 | 22.9677 | 22.93 | 22.7828 | 22.6911 | 22.617 | 22.5466 | 23.648 | 22.627 | 22.7386 | 23.0043 | 23.2977 | 23.8738 | 23.8205 | 23.7408 | 23.6681 | 23.6422 | 23.8104 | 23.7693 | 23.6836 | 23.615 | 23.4888 | 23.3261 | 23.0688 | 22.9072 | 22.8712 | 22.9268 | 23.6948 | 23.6163 | 23.5642 | 23.5171 | 23.5663 | 24.1599 | 24.0617 | 23.9528 | 23.8666 | 24.0048 | 23.6443 | 23.8726 | 23.8082 | 23.7174 | 23.6622 | 23.6156 | 23.6081 | 23.071 | 22.9757 | 24.1286 | 24.0421 | 24.0317 | 23.9825 | 23.9678 | 25.7058 | 30.8275 | 26.0408 | 24.7939 | 23.4748 | 23.1516 | 24.9189 | 26.0953 | 26.6297 | 26.1257 |  | 22.2114 | 21.6883 | 24.0781 | 24.6874 | 23.4321 | 23.4469 | 22.7127 | 22.5344 | 21.6208 | 22.2465 | 10.832 | 14.2649 | 14.9207 | 11.0757 | 0.00019538 | -0.0030954 | 0.0015363 | 0.0046125 | 0.00098194 | -0.00029836 | 0.016527 | -0.0075113 | -0.0095672 | -360.1711 | 17.4397 | -360.4604 | 17.641 | -360.7958 | 18.1563 | -360.7712 | 17.5568 | -352.5983 | 18.7189 | -352.6167 | 16.8012 | -3.837 | 357.8304 | 22.9739 | 14.5928 | 12.715 | 22.0776
13:26 | 28 | 36.2576 |  | 8.5855 | 3.3754 | 1.095 | 3.3701 | -1.5801 | 12.5789 | 5.6043 | 0.6345 | 0.6724 | 0.9798 | 0.7657 | -128.6845 | 4.8911 | 6.4341 | 1.8829 | -2.2734 | -0.7969 | 5.0939 |  | 4.8704 | 0.9087 | 3.99 | 3.3659 | 3.3334 | 1.1077 | 0.4177 | 22.7373 | 22.6086 | 22.4008 | 22.3715 | 22.2896 | 22.2802 | 22.1623 | 22.9498 | 22.6531 | 22.7008 | 22.6883 | 22.7112 | 23.0339 | 22.9419 | 22.905 | 22.789 | 22.6825 | 22.6138 | 22.485 | 22.3819 | 22.3144 | 22.2658 | 22.9349 | 22.5634 | 22.5904 | 22.5793 | 22.5863 | 23.1697 | 22.6866 | 22.9318 | 23.058 | 22.9899 | 23.5067 | 22.8773 | 22.9181 | 22.891 | 22.8297 | 22.686 | 22.5932 | 22.4113 | 22.2622 | 23.2558 | 22.656 | 22.7503 | 22.9515 | 23.2803 | 23.3199 | 23.266 | 23.2738 | 23.217 | 23.2093 | 23.0606 | 23.0735 | 23.1177 | 23.0778 | 22.9953 | 22.9141 | 22.7699 | 22.6983 | 22.7815 | 22.8263 | 23.1445 | 23.174 | 23.1496 | 23.0694 | 23.0359 | 23.8177 | 23.724 | 23.7388 | 23.6721 | 23.6434 | 23.3007 | 23.3687 | 23.3918 | 23.3493 | 23.3547 | 23.3874 | 23.2717 | 22.9825 | 22.8001 | 23.3205 | 23.3749 | 23.3402 | 23.3156 | 23.2788 | 25.8936 | 35.5305 | 23.0269 | 23.9468 | 22.0963 | 22.279 | 23.843 | 24.9838 | 24.1426 | 24.6939 | 22.7937 | 22.3822 | 23.2301 | 21.8143 | 22.654 | 23.096 | 21.3117 | 21.5372 | 21.5537 | 21.6747 | 21.5365 | 21.3536 | 22.6441 | 22.53 | 25.2547 | 22.3231 | 22.3052 | 22.2314 | 22.1989 | 22.1197 | 22.1993 | 23.2112 | 22.5389 | 22.4541 | 22.6548 | 22.4928 | 22.7527 | 22.9974 | 22.9085 | 22.85 | 22.761 | 22.671 | 22.6424 | 22.6058 | 22.574 | 23.6825 | 22.7543 | 22.7563 | 23.7761 | 22.7816 | 23.8029 | 22.9147 | 23.0639 | 23.0951 | 23.902 | 22.9564 | 22.9954 | 22.9703 | 22.9274 | 22.7914 | 22.6925 | 22.6238 | 22.5482 | 23.6523 | 22.6277 | 22.7425 | 23.0074 | 23.31 | 23.8728 | 23.8195 | 23.736 | 23.6661 | 23.6453 | 23.8111 | 23.7682 | 23.6803 | 23.6105 | 23.4834 | 23.3234 | 23.0729 | 22.9009 | 22.8711 | 22.9268 | 23.6918 | 23.6185 | 23.5632 | 23.5107 | 23.5705 | 24.1564 | 24.0595 | 23.948 | 23.8616 | 24.0323 | 23.6442 | 23.8687 | 23.8031 | 23.7127 | 23.6592 | 23.6092 | 23.6056 | 23.0704 | 22.9715 | 24.1296 | 24.0412 | 24.0313 | 23.9748 | 23.9692 | 25.7437 | 30.3462 | 26.126 | 24.8751 | 23.6031 | 23.2563 | 25.16 | 26.2787 | 26.9548 | 26.3364 |  | 22.3323 | 21.7368 | 24.2877 | 24.6997 | 23.4399 | 23.4536 | 22.7566 | 22.5432 | 21.6259 | 22.2583 | 10.8136 | 14.268 | 14.8971 | 11.1342 | 0.00064578 | -0.002721 | 0.0011189 | 0.0040511 | 0.0016362 | -0.00034011 | 0.030896 | 0.0006156 | -0.036487 | -360.1435 | 17.3761 | -360.3712 | 17.6245 | -360.7897 | 18.2077 | -360.8327 | 17.5794 | -352.5798 | 18.6758 | -352.5736 | 16.8032 | -2.6986 | 360.5578 | 23.0939 | 14.5825 | 12.8144 | 22.0846
13:26 | 29 | 36.2303 |  | 8.6482 | 3.4267 | 1.1111 | 3.3524 | -1.4976 | 12.6191 | 5.5925 | 0.6348 | 0.6762 | 0.978 | 0.7659 | -128.7695 | 4.8317 | 6.4418 | 1.8532 | -2.3038 | -0.8883 | 5.0703 |  | 4.9223 | 0.9336 | 3.9888 | 3.3672 | 3.3339 | 1.1079 | 1.3606 | 22.7351 | 22.6079 | 22.3993 | 22.3684 | 22.2863 | 22.2771 | 22.1611 | 22.9434 | 22.655 | 22.7004 | 22.6871 | 22.7234 | 23.0302 | 22.9382 | 22.9121 | 22.7936 | 22.6892 | 22.6194 | 22.4979 | 22.385 | 22.3152 | 22.2682 | 22.9359 | 22.571 | 22.5959 | 22.5801 | 22.5919 | 23.1763 | 22.697 | 22.9386 | 23.0538 | 22.9919 | 23.5021 | 22.87 | 22.9174 | 22.8897 | 22.8208 | 22.6822 | 22.5898 | 22.4128 | 22.2603 | 23.2537 | 22.6546 | 22.7503 | 22.9505 | 23.2804 | 23.3199 | 23.2722 | 23.2749 | 23.2183 | 23.2111 | 23.0617 | 23.0792 | 23.1179 | 23.0792 | 22.9964 | 22.9182 | 22.7725 | 22.7048 | 22.7843 | 22.8333 | 23.144 | 23.1815 | 23.1495 | 23.0694 | 23.0344 | 23.8168 | 23.7277 | 23.7355 | 23.67 | 23.6458 | 23.306 | 23.366 | 23.3913 | 23.3493 | 23.3557 | 23.3853 | 23.2745 | 22.9822 | 22.7921 | 23.3193 | 23.3718 | 23.3412 | 23.3117 | 23.2763 | 25.8982 | 35.9039 | 23.0495 | 24.036 | 22.1287 | 22.3618 | 23.9156 | 25.2975 | 24.3203 | 24.9934 | 22.8094 | 22.3564 | 23.4606 | 22.3013 | 22.4394 | 23.2962 | 21.2951 | 21.5474 | 21.5975 | 21.7022 | 21.592 | 21.3895 | 22.6436 | 22.5212 | 25.2482 | 22.3184 | 22.3031 | 22.2227 | 22.1929 | 22.1116 | 22.1931 | 23.209 | 22.5346 | 22.4512 | 22.664 | 22.4875 | 22.7482 | 22.9931 | 22.9072 | 22.8456 | 22.7535 | 22.6694 | 22.639 | 22.6017 | 22.5701 | 23.6747 | 22.7527 | 22.7552 | 23.7796 | 22.7793 | 23.7952 | 22.9131 | 23.0663 | 23.1027 | 23.8993 | 22.96 | 22.9942 | 22.9738 | 22.929 | 22.79 | 22.6941 | 22.6266 | 22.5529 | 23.6544 | 22.6324 | 22.7481 | 23.0058 | 23.3184 | 23.8703 | 23.8192 | 23.7325 | 23.6677 | 23.6514 | 23.8042 | 23.766 | 23.6787 | 23.6097 | 23.4833 | 23.3233 | 23.0735 | 22.9024 | 22.87 | 22.9299 | 23.6957 | 23.6195 | 23.5669 | 23.5127 | 23.5791 | 24.1582 | 24.0647 | 23.9482 | 23.8614 | 24.0588 | 23.6437 | 23.8703 | 23.8032 | 23.7216 | 23.6595 | 23.6073 | 23.6075 | 23.0735 | 22.9779 | 24.1277 | 24.0406 | 24.0315 | 23.9779 | 23.9794 | 25.7818 | 30.0099 | 26.16 | 24.9445 | 23.7297 | 23.3681 | 25.3639 | 26.4376 | 27.2496 | 26.5212 |  | 22.455 | 21.8032 | 24.4765 | 24.694 | 23.4362 | 23.4491 | 22.7856 | 22.5361 | 21.6265 | 22.2667 | 10.8187 | 14.2866 | 14.9132 | 11.1401 | 6.6489e-06 | -0.0032571 | 0.0010668 | 0.0039301 | 0.0011951 | -0.00058192 | -0.0012173 | -0.0082287 | 0.00040886 | -360.2204 | 17.4377 | -360.5127 | 17.6594 | -360.8512 | 18.1974 | -360.8297 | 17.5691 | -352.6075 | 18.7312 | -352.6567 | 16.8279 | -4.9037 | 358.4773 | 23.2109 | 14.5999 | 12.8519 | 22.0813
13:26 | 30 | 36.106 |  | 8.6013 | 3.3648 | 1.0531 | 3.346 | -1.496 | 12.6103 | 5.534 | 0.6337 | 0.6739 | 0.9764 | 0.7661 | -128.7515 | 4.7806 | 6.3259 | 1.9705 | -2.2737 | -0.6785 | 5.1264 |  | 4.9702 | 0.9102 | 3.9894 | 3.3668 | 3.3309 | 1.1081 | 0.8136 | 22.7322 | 22.6098 | 22.3953 | 22.3652 | 22.2797 | 22.2785 | 22.1511 | 22.9404 | 22.6506 | 22.6977 | 22.6826 | 22.7256 | 23.0221 | 22.9351 | 22.9091 | 22.7977 | 22.6935 | 22.6203 | 22.4903 | 22.387 | 22.3167 | 22.2674 | 22.9322 | 22.5691 | 22.6025 | 22.5856 | 22.5944 | 23.175 | 22.6992 | 22.9392 | 23.0517 | 22.9894 | 23.5052 | 22.8769 | 22.9158 | 22.8887 | 22.819 | 22.6842 | 22.587 | 22.4155 | 22.2595 | 23.2602 | 22.6569 | 22.7575 | 22.9449 | 23.293 | 23.3288 | 23.2779 | 23.2812 | 23.2191 | 23.2229 | 23.0694 | 23.0796 | 23.1237 | 23.0845 | 23.0022 | 22.9185 | 22.7823 | 22.7145 | 22.7875 | 22.8434 | 23.1438 | 23.1706 | 23.1558 | 23.0718 | 23.0374 | 23.8186 | 23.7223 | 23.7336 | 23.6678 | 23.6457 | 23.2999 | 23.3663 | 23.3903 | 23.347 | 23.3596 | 23.388 | 23.269 | 22.9786 | 22.7897 | 23.3129 | 23.3658 | 23.3406 | 23.3044 | 23.2723 | 25.8297 | 35.8488 | 23.0791 | 24.1185 | 22.1809 | 22.4449 | 23.9943 | 25.6086 | 24.4918 | 25.2949 | 22.9698 | 22.5268 | 23.5808 | 23.0188 | 22.3049 | 23.4947 | 21.2875 | 21.606 | 21.634 | 21.7291 | 21.6388 | 21.4222 | 22.6372 | 22.5155 | 25.2362 | 22.3135 | 22.2971 | 22.2125 | 22.1874 | 22.1068 | 22.1918 | 23.2047 | 22.5323 | 22.4487 | 22.6724 | 22.484 | 22.737 | 22.9919 | 22.9012 | 22.8453 | 22.7423 | 22.6624 | 22.6329 | 22.5915 | 22.57 | 23.663 | 22.7469 | 22.7507 | 23.7726 | 22.7866 | 23.7938 | 22.9055 | 23.0624 | 23.1127 | 23.8975 | 22.9554 | 22.9944 | 22.9731 | 22.9331 | 22.7855 | 22.6965 | 22.6247 | 22.5523 | 23.6578 | 22.6354 | 22.7463 | 22.9963 | 23.3215 | 23.8625 | 23.8123 | 23.7283 | 23.6646 | 23.6496 | 23.7945 | 23.762 | 23.6708 | 23.6033 | 23.4774 | 23.3153 | 23.0731 | 22.898 | 22.8677 | 22.9224 | 23.6877 | 23.6174 | 23.5606 | 23.505 | 23.5878 | 24.1581 | 24.0633 | 23.9454 | 23.8567 | 24.0785 | 23.6418 | 23.8651 | 23.7968 | 23.7181 | 23.6557 | 23.6062 | 23.6073 | 23.0681 | 22.9758 | 24.1232 | 24.0332 | 24.0221 | 23.974 | 23.9725 | 25.8144 | 29.758 | 26.158 | 24.9956 | 23.8683 | 23.4883 | 25.5503 | 26.5721 | 27.5227 | 26.6848 |  | 22.5857 | 21.868 | 24.662 | 24.6826 | 23.434 | 23.4476 | 22.8069 | 22.5435 | 21.6245 | 22.2585 | 10.8193 | 14.2736 | 14.8955 | 11.1258 | 4.7396e-05 | -0.0027309 | 0.0013894 | 0.0041112 | 0.0011581 | -0.00042141 | 0.011843 | -0.013305 | -0.030206 | -360.1681 | 17.4213 | -360.4204 | 17.641 | -360.805 | 18.2015 | -360.8512 | 17.5814 | -352.6044 | 18.7045 | -352.5983 | 16.7909 | -3.3592 | 356.8233 | 23.3311 | 14.5845 | 12.9116 | 22.084
13:26 | 31 | 36.1309 |  | 8.6376 | 3.3476 | 1.0492 | 3.3247 | -1.4857 | 12.5618 | 5.5987 | 0.635 | 0.6777 | 0.9813 | 0.768 | -128.9206 | 4.7041 | 6.2744 | 1.7769 | -2.336 | -0.7231 | 5.0307 |  | 4.9396 | 0.9835 | 3.9901 | 3.3683 | 3.3268 | 1.1066 | 0.9997 | 22.7369 | 22.6098 | 22.3971 | 22.3702 | 22.2843 | 22.2851 | 22.154 | 22.9451 | 22.6494 | 22.6984 | 22.6847 | 22.7233 | 23.0259 | 22.9361 | 22.9037 | 22.8008 | 22.69 | 22.6139 | 22.4892 | 22.3874 | 22.3185 | 22.2654 | 22.9306 | 22.5634 | 22.6014 | 22.5806 | 22.5917 | 23.1709 | 22.695 | 22.931 | 23.0455 | 22.9868 | 23.5013 | 22.8751 | 22.9102 | 22.8783 | 22.819 | 22.6814 | 22.5888 | 22.4189 | 22.2554 | 23.2567 | 22.6516 | 22.7528 | 22.9385 | 23.2949 | 23.3296 | 23.2724 | 23.2802 | 23.2119 | 23.2269 | 23.0677 | 23.0797 | 23.119 | 23.0827 | 22.9973 | 22.9092 | 22.7905 | 22.7068 | 22.7811 | 22.8376 | 23.1499 | 23.169 | 23.1591 | 23.0749 | 23.0497 | 23.8273 | 23.7214 | 23.7386 | 23.6749 | 23.6506 | 23.3027 | 23.372 | 23.3921 | 23.3505 | 23.3653 | 23.3928 | 23.2622 | 22.9816 | 22.7932 | 23.32 | 23.3658 | 23.3381 | 23.2987 | 23.2819 | 25.7782 | 35.5748 | 23.1108 | 24.1934 | 22.2458 | 22.5329 | 24.0655 | 25.9052 | 24.6523 | 25.592 | 23.2074 | 22.9121 | 23.5879 | 23.6251 | 22.4453 | 23.7697 | 21.2856 | 21.82 | 21.6723 | 21.7469 | 21.6841 | 21.4483 | 22.6331 | 22.5149 | 25.248 | 22.3098 | 22.2948 | 22.2091 | 22.1871 | 22.1079 | 22.1916 | 23.201 | 22.5331 | 22.446 | 22.6817 | 22.4792 | 22.7251 | 22.9967 | 22.9046 | 22.8448 | 22.7418 | 22.6643 | 22.6369 | 22.5846 | 22.5667 | 23.6595 | 22.7509 | 22.7469 | 23.7725 | 22.7968 | 23.7983 | 22.9056 | 23.062 | 23.1142 | 23.9008 | 22.9491 | 22.9926 | 22.9719 | 22.9282 | 22.789 | 22.6939 | 22.6253 | 22.5448 | 23.653 | 22.6308 | 22.7429 | 22.9952 | 23.3367 | 23.865 | 23.8134 | 23.7268 | 23.6644 | 23.6574 | 23.7951 | 23.76 | 23.6719 | 23.5971 | 23.4736 | 23.3167 | 23.0757 | 22.896 | 22.8721 | 22.9196 | 23.6842 | 23.6154 | 23.5602 | 23.5047 | 23.5993 | 24.1558 | 24.0611 | 23.9437 | 23.8581 | 24.1073 | 23.6409 | 23.8641 | 23.7939 | 23.7168 | 23.6576 | 23.6021 | 23.6032 | 23.0695 | 22.9717 | 24.1193 | 24.0288 | 24.0225 | 23.9729 | 23.9674 | 25.8369 | 29.5191 | 26.1627 | 25.044 | 24.007 | 23.6128 | 25.7227 | 26.6894 | 27.7813 | 26.8319 |  | 22.7271 | 21.9468 | 24.8495 | 24.6867 | 23.4339 | 23.4536 | 22.8648 | 22.5579 | 21.6315 | 22.2631 | 10.8389 | 14.2866 | 14.8752 | 11.1306 | 0.00042498 | -0.0026186 | 0.0019069 | 0.0043 | 0.0015747 | -0.00044155 | 0.00030612 | -0.0079538 | 0.00096201 | -360.1311 | 17.4151 | -360.4112 | 17.6328 | -360.7773 | 18.181 | -360.7958 | 17.5486 | -352.5552 | 18.6943 | -352.589 | 16.7991 | 0.4551 | 362.9591 | 23.4556 | 14.5809 | 12.8117 | 22.0947
13:26 | 32 | 36.1039 |  | 8.6126 | 3.3337 | 0.9587 | 3.2576 | -1.4401 | 12.6584 | 5.65 | 0.634 | 0.6739 | 0.9801 | 0.7675 | -128.8692 | 4.7917 | 6.3098 | 1.8942 | -2.3867 | -0.8034 | 5.0592 |  | 4.9826 | 1.0496 | 3.9917 | 3.3649 | 3.3343 | 1.1081 | 0.2553 | 22.7371 | 22.6107 | 22.3947 | 22.3747 | 22.29 | 22.2862 | 22.1599 | 22.9418 | 22.6574 | 22.6985 | 22.6881 | 22.7375 | 23.0265 | 22.9419 | 22.9043 | 22.8005 | 22.6931 | 22.616 | 22.4949 | 22.3872 | 22.3209 | 22.2659 | 22.9362 | 22.566 | 22.5971 | 22.581 | 22.5952 | 23.1723 | 22.6907 | 22.9347 | 23.0426 | 22.9867 | 23.4961 | 22.8701 | 22.9057 | 22.8737 | 22.8147 | 22.6732 | 22.5833 | 22.4139 | 22.2462 | 23.25 | 22.6429 | 22.743 | 22.9417 | 23.2929 | 23.3223 | 23.2707 | 23.2677 | 23.2141 | 23.2257 | 23.0634 | 23.0801 | 23.1105 | 23.0768 | 22.9956 | 22.9078 | 22.7909 | 22.7045 | 22.7717 | 22.8348 | 23.1489 | 23.1782 | 23.1563 | 23.0762 | 23.0614 | 23.8254 | 23.7266 | 23.7409 | 23.676 | 23.6612 | 23.3044 | 23.376 | 23.3932 | 23.3524 | 23.3648 | 23.392 | 23.2642 | 22.9752 | 22.7884 | 23.3225 | 23.3631 | 23.3391 | 23.2958 | 23.286 | 25.7431 | 35.3262 | 23.1594 | 24.2346 | 22.3031 | 22.6197 | 24.1302 | 26.1824 | 24.7941 | 25.8693 | 23.4137 | 23.3077 | 23.4958 | 23.7549 | 22.7396 | 23.9287 | 21.2927 | 22.1132 | 21.7106 | 21.7672 | 21.7274 | 21.4775 | 22.6363 | 22.5179 | 25.2598 | 22.3105 | 22.2897 | 22.2154 | 22.1894 | 22.1107 | 22.1934 | 23.1932 | 22.53 | 22.4446 | 22.6878 | 22.4793 | 22.7251 | 22.9992 | 22.9108 | 22.8498 | 22.7472 | 22.6723 | 22.6356 | 22.5916 | 22.5663 | 23.6676 | 22.7525 | 22.7508 | 23.7755 | 22.8042 | 23.7968 | 22.9135 | 23.0634 | 23.114 | 23.9001 | 22.9501 | 22.9897 | 22.9674 | 22.9235 | 22.7893 | 22.6918 | 22.6204 | 22.5454 | 23.6474 | 22.6329 | 22.7455 | 22.996 | 23.3521 | 23.8675 | 23.8173 | 23.7252 | 23.6641 | 23.6621 | 23.7957 | 23.7537 | 23.6808 | 23.5996 | 23.474 | 23.3197 | 23.0779 | 22.8958 | 22.873 | 22.9191 | 23.6898 | 23.6163 | 23.5693 | 23.5121 | 23.6016 | 24.1549 | 24.0625 | 23.9436 | 23.8669 | 24.1304 | 23.642 | 23.8685 | 23.7996 | 23.7203 | 23.6591 | 23.6005 | 23.6048 | 23.0724 | 22.973 | 24.122 | 24.0304 | 24.0289 | 23.9756 | 23.9682 | 25.8465 | 29.3277 | 26.1885 | 25.0886 | 24.1348 | 23.7394 | 25.8617 | 26.7889 | 28.0149 | 26.9481 |  | 22.8592 | 22.028 | 25.0155 | 24.6882 | 23.4365 | 23.4508 | 22.8987 | 22.5547 | 21.6242 | 22.2669 | 10.8137 | 14.2678 | 14.9029 | 11.1276 | 0.00035764 | -0.0031696 | 0.0016513 | 0.0044924 | 0.0012826 | -0.00032371 | 0.020148 | -0.0013551 | -0.019692 | -360.1773 | 17.4192 | -360.4512 | 17.6471 | -360.8174 | 18.2036 | -360.8266 | 17.5753 | -352.5952 | 18.7148 | -352.629 | 16.8094 | 10.8643 | 356.8066 | 23.5702 | 14.5853 | 12.8479 | 22.0894
13:26 | 33 | 36.0611 |  | 8.5289 | 3.309 | 1.0701 | 3.3656 | -1.4901 | 12.7164 | 5.6017 | 0.6332 | 0.6727 | 0.9806 | 0.7666 | -128.8282 | 4.676 | 6.3714 | 1.9026 | -2.3073 | -0.8174 | 5.0656 |  | 4.983 | 0.9215 | 3.9895 | 3.3693 | 3.3304 | 1.1066 | 0.2942 | 22.742 | 22.613 | 22.3974 | 22.374 | 22.2921 | 22.2848 | 22.161 | 22.938 | 22.6603 | 22.6973 | 22.6903 | 22.7467 | 23.0235 | 22.9487 | 22.906 | 22.797 | 22.6868 | 22.6143 | 22.4972 | 22.382 | 22.3226 | 22.2622 | 22.9323 | 22.5684 | 22.5969 | 22.5847 | 22.5948 | 23.1708 | 22.6888 | 22.9363 | 23.0492 | 22.9925 | 23.5036 | 22.8757 | 22.9111 | 22.8852 | 22.8158 | 22.6785 | 22.5886 | 22.4182 | 22.2536 | 23.2594 | 22.6497 | 22.7487 | 22.95 | 23.2995 | 23.3252 | 23.2761 | 23.2723 | 23.2199 | 23.2348 | 23.0595 | 23.0779 | 23.1125 | 23.077 | 22.9958 | 22.9106 | 22.7915 | 22.7068 | 22.7685 | 22.8339 | 23.1422 | 23.1766 | 23.1506 | 23.0771 | 23.0707 | 23.8213 | 23.7248 | 23.7413 | 23.6681 | 23.6651 | 23.2951 | 23.3749 | 23.3949 | 23.3535 | 23.3598 | 23.3887 | 23.2788 | 22.9839 | 22.7957 | 23.3203 | 23.3735 | 23.342 | 23.3053 | 23.2879 | 25.7403 | 34.8549 | 23.2266 | 24.2587 | 22.3718 | 22.7016 | 24.1915 | 26.4279 | 24.9231 | 26.1154 | 23.5049 | 23.6639 | 23.4258 | 23.4444 | 22.8433 | 23.9063 | 21.2994 | 22.3906 | 21.751 | 21.7951 | 21.7683 | 21.5116 | 22.6418 | 22.52 | 25.2799 | 22.3159 | 22.292 | 22.2202 | 22.1889 | 22.1106 | 22.1937 | 23.2031 | 22.5284 | 22.4473 | 22.7025 | 22.4815 | 22.7297 | 22.9997 | 22.9139 | 22.8555 | 22.75 | 22.6709 | 22.6368 | 22.5968 | 22.5696 | 23.6731 | 22.7488 | 22.7518 | 23.7722 | 22.8137 | 23.7938 | 22.9132 | 23.0558 | 23.1152 | 23.8932 | 22.9484 | 22.9886 | 22.9604 | 22.9176 | 22.7899 | 22.6925 | 22.6197 | 22.546 | 23.6476 | 22.6331 | 22.7459 | 22.9902 | 23.3596 | 23.866 | 23.8154 | 23.7262 | 23.6636 | 23.6592 | 23.7954 | 23.7558 | 23.6825 | 23.5986 | 23.4778 | 23.3144 | 23.0854 | 22.8977 | 22.8697 | 22.9237 | 23.6886 | 23.6153 | 23.5652 | 23.5088 | 23.604 | 24.1526 | 24.0616 | 23.9438 | 23.8633 | 24.1441 | 23.6363 | 23.8681 | 23.7954 | 23.7152 | 23.6509 | 23.5996 | 23.6068 | 23.0664 | 22.9753 | 24.1247 | 24.0314 | 24.0271 | 23.973 | 23.9689 | 25.8447 | 29.1902 | 26.212 | 25.1274 | 24.2564 | 23.8716 | 25.9785 | 26.8764 | 28.2347 | 27.0418 |  | 22.9939 | 22.1134 | 25.172 | 24.6905 | 23.4322 | 23.4531 | 22.9251 | 22.564 | 21.6323 | 22.2595 | 10.841 | 14.296 | 14.8931 | 11.1251 | 0.00065855 | -0.0026719 | 0.0020465 | 0.0050037 | 0.0017091 | -0.00039473 | -0.0045612 | -0.0046611 | -0.010217 | -360.165 | 17.4274 | -360.4419 | 17.6471 | -360.8297 | 18.2056 | -360.8143 | 17.5794 | -352.5952 | 18.7169 | -352.626 | 16.8115 | 3.6422 | 362.2933 | 23.6824 | 14.5946 | 12.8549 | 22.0982
13:26 | 34 | 36.1278 |  | 8.6442 | 3.4093 | 1.178 | 3.3554 | -1.5694 | 12.6822 | 5.6404 | 0.6338 | 0.6741 | 0.9806 | 0.7671 | -128.8633 | 4.6235 | 6.3565 | 1.8554 | -2.2472 | -0.7768 | 5.0487 |  | 4.933 | 0.9011 | 3.9903 | 3.3659 | 3.3347 | 1.1072 | 0.3787 | 22.7437 | 22.6086 | 22.3947 | 22.3691 | 22.2852 | 22.281 | 22.1562 | 22.9358 | 22.6578 | 22.6951 | 22.6877 | 22.7546 | 23.0207 | 22.9421 | 22.9036 | 22.7918 | 22.6793 | 22.6056 | 22.498 | 22.3773 | 22.3238 | 22.2592 | 22.9267 | 22.5591 | 22.5913 | 22.579 | 22.5893 | 23.1682 | 22.6849 | 22.9279 | 23.0615 | 23.0037 | 23.506 | 22.8772 | 22.9182 | 22.8906 | 22.8222 | 22.6899 | 22.5986 | 22.4282 | 22.2604 | 23.2684 | 22.6573 | 22.7632 | 22.9631 | 23.3016 | 23.3281 | 23.2761 | 23.2794 | 23.2145 | 23.2409 | 23.0569 | 23.0732 | 23.1149 | 23.0755 | 22.9977 | 22.9108 | 22.7941 | 22.7077 | 22.768 | 22.835 | 23.1424 | 23.1788 | 23.1492 | 23.077 | 23.0743 | 23.8228 | 23.7294 | 23.7421 | 23.6705 | 23.6683 | 23.2976 | 23.3766 | 23.396 | 23.3545 | 23.3601 | 23.3903 | 23.2809 | 22.9811 | 22.7952 | 23.3194 | 23.3816 | 23.3368 | 23.3051 | 23.2871 | 25.7118 | 34.1882 | 23.2478 | 24.2775 | 22.4491 | 22.7789 | 24.2503 | 26.6403 | 25.0291 | 26.3309 | 23.5614 | 24.0304 | 23.4972 | 22.9865 | 22.6802 | 23.8014 | 21.3111 | 22.7735 | 21.7889 | 21.8263 | 21.8123 | 21.5442 | 22.6433 | 22.5219 | 25.3161 | 22.3145 | 22.2949 | 22.2175 | 22.1827 | 22.1057 | 22.1857 | 23.2031 | 22.5263 | 22.4514 | 22.7169 | 22.481 | 22.7274 | 23.0004 | 22.9164 | 22.8606 | 22.7531 | 22.6711 | 22.6386 | 22.5965 | 22.5722 | 23.6649 | 22.7504 | 22.7521 | 23.7734 | 22.8185 | 23.7961 | 22.9038 | 23.0546 | 23.1178 | 23.8914 | 22.9469 | 22.982 | 22.9582 | 22.9164 | 22.7892 | 22.6854 | 22.6194 | 22.5379 | 23.6474 | 22.6237 | 22.7371 | 22.9827 | 23.374 | 23.8675 | 23.8158 | 23.7311 | 23.6624 | 23.6723 | 23.7969 | 23.7603 | 23.6819 | 23.5984 | 23.4825 | 23.3153 | 23.0856 | 22.8975 | 22.8717 | 22.9234 | 23.6976 | 23.6154 | 23.5622 | 23.51 | 23.6174 | 24.1547 | 24.0621 | 23.9527 | 23.8585 | 24.162 | 23.6353 | 23.867 | 23.7944 | 23.7184 | 23.6486 | 23.6039 | 23.6051 | 23.0627 | 22.9732 | 24.1167 | 24.0301 | 24.0218 | 23.9702 | 23.9739 | 25.8391 | 29.0588 | 26.1892 | 25.1561 | 24.3819 | 24.0035 | 26.0897 | 26.9611 | 28.4466 | 27.1293 |  | 23.1248 | 22.1897 | 25.3268 | 24.6845 | 23.4248 | 23.4474 | 22.9599 | 22.5684 | 21.6262 | 22.2583 | 10.823 | 14.2764 | 14.8874 | 11.0957 | -0.00027905 | -0.0027392 | 0.0011562 | 0.0043973 | 0.00068141 | -0.00075152 | 0.0043993 | -0.013727 | -0.0076118 | -360.1435 | 17.4069 | -360.4173 | 17.6245 | -360.7589 | 18.1789 | -360.7804 | 17.5629 | -352.5921 | 18.6984 | -352.6075 | 16.793 | 6.4615 | 357.0331 | 23.7931 | 14.5819 | 12.9163 | 22.0973
13:26 | 35 | 36.0528 |  | 8.6154 | 3.4852 | 1.2311 | 3.341 | -1.6252 | 12.6795 | 5.6113 | 0.6338 | 0.6757 | 0.9824 | 0.7677 | -128.846 | 4.6064 | 6.2999 | 1.6982 | -2.3334 | -0.8092 | 4.9996 |  | 5.0239 | 0.9096 | 3.9895 | 3.3682 | 3.33 | 1.1065 | 0.4574 | 22.7462 | 22.607 | 22.3906 | 22.3711 | 22.2823 | 22.2825 | 22.1571 | 22.9374 | 22.6562 | 22.6937 | 22.6863 | 22.7671 | 23.0226 | 22.9403 | 22.8998 | 22.7919 | 22.6818 | 22.6061 | 22.498 | 22.3818 | 22.3268 | 22.2588 | 22.9327 | 22.5573 | 22.592 | 22.5783 | 22.5904 | 23.1723 | 22.6873 | 22.9233 | 23.0492 | 23.0022 | 23.498 | 22.8674 | 22.9104 | 22.8778 | 22.8135 | 22.6781 | 22.5899 | 22.4184 | 22.2501 | 23.2589 | 22.6447 | 22.7511 | 22.9517 | 23.3047 | 23.3273 | 23.2747 | 23.277 | 23.2128 | 23.2488 | 23.0648 | 23.0752 | 23.1162 | 23.078 | 22.9991 | 22.9133 | 22.7904 | 22.7085 | 22.7658 | 22.8355 | 23.1461 | 23.1797 | 23.1541 | 23.0803 | 23.0798 | 23.826 | 23.7338 | 23.7424 | 23.6715 | 23.6713 | 23.3053 | 23.3798 | 23.3944 | 23.3507 | 23.366 | 23.394 | 23.2807 | 22.979 | 22.7909 | 23.3205 | 23.375 | 23.3409 | 23.3066 | 23.2877 | 25.6822 | 33.5239 | 23.267 | 24.3058 | 22.5377 | 22.851 | 24.3124 | 26.8268 | 25.1322 | 26.5154 | 23.6617 | 24.3982 | 23.6357 | 22.584 | 22.4259 | 23.6236 | 21.6064 | 23.2634 | 21.816 | 21.8437 | 21.8489 | 21.5795 | 22.6434 | 22.5223 | 25.3374 | 22.3174 | 22.2938 | 22.2191 | 22.1819 | 22.1088 | 22.1864 | 23.1963 | 22.528 | 22.4513 | 22.7268 | 22.4799 | 22.7361 | 23.0024 | 22.9147 | 22.8576 | 22.7499 | 22.6754 | 22.634 | 22.594 | 22.5674 | 23.6602 | 22.7466 | 22.7459 | 23.7733 | 22.8145 | 23.7898 | 22.8987 | 23.056 | 23.1214 | 23.8905 | 22.9416 | 22.9766 | 22.9548 | 22.9142 | 22.7869 | 22.6763 | 22.6126 | 22.5385 | 23.6439 | 22.6173 | 22.7344 | 22.9729 | 23.3839 | 23.8661 | 23.8164 | 23.7241 | 23.663 | 23.6757 | 23.7959 | 23.7594 | 23.6804 | 23.6015 | 23.4801 | 23.321 | 23.079 | 22.8965 | 22.8738 | 22.9184 | 23.6976 | 23.6163 | 23.563 | 23.5101 | 23.6214 | 24.1503 | 24.0615 | 23.9531 | 23.857 | 24.1813 | 23.638 | 23.8619 | 23.7978 | 23.7189 | 23.6494 | 23.6074 | 23.607 | 23.0651 | 22.9751 | 24.1127 | 24.0307 | 24.0198 | 23.9664 | 23.9744 | 25.8366 | 29.013 | 26.1484 | 25.1879 | 24.4915 | 24.1275 | 26.1863 | 27.0322 | 28.6396 | 27.2 |  | 23.2603 | 22.2704 | 25.4763 | 24.684 | 23.4337 | 23.4494 | 23.0025 | 22.5749 | 21.6267 | 22.2585 | 10.835 | 14.2745 | 14.8932 | 11.0933 | 0.00034564 | -0.0023525 | 0.0010296 | 0.0040814 | 0.0011138 | -0.0013479 | 0.0078618 | -0.013938 | -0.016749 | -360.1558 | 17.409 | -360.4142 | 17.6512 | -360.8297 | 18.2036 | -360.8358 | 17.5568 | -352.586 | 18.7025 | -352.6352 | 16.8299 | -8.7189 | 362.4345 | 23.9001 | 14.5838 | 12.8481 | 22.1008
13:26 | 36 | 36.0747 |  | 8.5559 | 3.4197 | 1.1232 | 3.2646 | -1.6463 | 12.621 | 5.6428 | 0.6335 | 0.6768 | 0.98 | 0.7676 | -128.7977 | 4.6465 | 6.4157 | 1.6696 | -2.2751 | -0.7768 | 5.0046 |  | 4.9798 | 0.9531 | 3.9885 | 3.3651 | 3.3333 | 1.1073 | -0.3266 | 22.7473 | 22.6078 | 22.3964 | 22.3772 | 22.2808 | 22.2817 | 22.1596 | 22.9392 | 22.6565 | 22.6941 | 22.6878 | 22.7732 | 23.0278 | 22.9397 | 22.8984 | 22.7921 | 22.6807 | 22.6069 | 22.4924 | 22.3804 | 22.3263 | 22.253 | 22.931 | 22.5622 | 22.5912 | 22.5787 | 22.5917 | 23.169 | 22.6861 | 22.9243 | 23.0397 | 23.0013 | 23.4985 | 22.8686 | 22.9093 | 22.8772 | 22.8165 | 22.6783 | 22.5904 | 22.4144 | 22.25 | 23.2592 | 22.6455 | 22.7457 | 22.9499 | 23.3091 | 23.3254 | 23.2774 | 23.2771 | 23.2206 | 23.2652 | 23.0743 | 23.0801 | 23.1232 | 23.0858 | 23.0031 | 22.9153 | 22.7925 | 22.7106 | 22.7686 | 22.8378 | 23.1443 | 23.1772 | 23.1585 | 23.081 | 23.0876 | 23.8322 | 23.7313 | 23.7399 | 23.6743 | 23.6736 | 23.3057 | 23.381 | 23.3954 | 23.3476 | 23.3638 | 23.3963 | 23.285 | 22.9902 | 22.7906 | 23.3169 | 23.3756 | 23.3438 | 23.3091 | 23.291 | 25.7088 | 33.1403 | 23.3124 | 24.3392 | 22.63 | 22.9259 | 24.3671 | 26.9876 | 25.2227 | 26.6737 | 24.146 | 25.0748 | 23.9432 | 22.965 | 22.2604 | 24.2472 | 22.8902 | 23.8224 | 21.8507 | 21.8668 | 21.8864 | 21.6167 | 22.6367 | 22.5179 | 25.3825 | 22.314 | 22.291 | 22.2176 | 22.1868 | 22.1126 | 22.1889 | 23.1997 | 22.5282 | 22.4504 | 22.7319 | 22.4762 | 22.7353 | 23.005 | 22.9185 | 22.8579 | 22.7564 | 22.6758 | 22.6389 | 22.5986 | 22.5681 | 23.6636 | 22.7444 | 22.7443 | 23.7703 | 22.8222 | 23.7868 | 22.8982 | 23.0543 | 23.1237 | 23.8874 | 22.9385 | 22.9736 | 22.9527 | 22.913 | 22.781 | 22.6801 | 22.6103 | 22.5418 | 23.641 | 22.6211 | 22.7362 | 22.9716 | 23.3883 | 23.8639 | 23.8123 | 23.7212 | 23.6614 | 23.6674 | 23.7882 | 23.7537 | 23.6746 | 23.5947 | 23.4722 | 23.3183 | 23.0753 | 22.8962 | 22.8697 | 22.9165 | 23.6907 | 23.612 | 23.5608 | 23.5045 | 23.6206 | 24.1449 | 24.0552 | 23.9477 | 23.8563 | 24.1955 | 23.6345 | 23.8542 | 23.7915 | 23.7109 | 23.645 | 23.5992 | 23.6132 | 23.0696 | 22.9743 | 24.1163 | 24.033 | 24.0218 | 23.9682 | 23.9687 | 25.8324 | 29.0681 | 26.1309 | 25.2368 | 24.589 | 24.2549 | 26.2741 | 27.1056 | 28.8257 | 27.2537 |  | 23.3897 | 22.3617 | 25.6111 | 24.692 | 23.4307 | 23.4513 | 23.0351 | 22.5835 | 21.6361 | 22.2645 | 10.8249 | 14.2582 | 14.8951 | 11.0888 | 0.00063058 | -0.0029263 | 0.0019005 | 0.004365 | 0.00079956 | -0.00056611 | 0.01341 | 0.0055049 | -0.016615 | -360.2419 | 17.448 | -360.4666 | 17.6451 | -360.802 | 18.1953 | -360.8327 | 17.5937 | -352.6444 | 18.7333 | -352.6321 | 16.7889 | -0.014706 | 357.6757 | 24.0045 | 14.5766 | 12.7608 | 22.1098
13:26 | 37 | 36.0794 |  | 8.6222 | 3.4334 | 1.1237 | 3.3608 | -1.6215 | 12.6832 | 5.6771 | 0.6338 | 0.6753 | 0.9804 | 0.7667 | -128.8033 | 4.6624 | 6.4164 | 1.7082 | -2.2761 | -0.7658 | 5.0736 |  | 4.958 | 0.9044 | 3.9891 | 3.3654 | 3.3291 | 1.108 | 0.9299 | 22.7438 | 22.6113 | 22.3984 | 22.3768 | 22.2784 | 22.2805 | 22.1564 | 22.9399 | 22.6564 | 22.697 | 22.6853 | 22.7789 | 23.0257 | 22.9351 | 22.8989 | 22.7897 | 22.6833 | 22.612 | 22.4877 | 22.3807 | 22.3217 | 22.2541 | 22.9268 | 22.5651 | 22.589 | 22.5793 | 22.6005 | 23.1661 | 22.6819 | 22.9262 | 23.049 | 23.0072 | 23.5005 | 22.8758 | 22.9133 | 22.878 | 22.8176 | 22.6831 | 22.5892 | 22.4144 | 22.2547 | 23.2644 | 22.6541 | 22.7514 | 22.9513 | 23.3127 | 23.3255 | 23.2811 | 23.2771 | 23.2256 | 23.2706 | 23.0743 | 23.0828 | 23.1208 | 23.0861 | 23.0034 | 22.9139 | 22.8025 | 22.7166 | 22.7703 | 22.8456 | 23.1415 | 23.1774 | 23.1557 | 23.0734 | 23.0906 | 23.8299 | 23.7259 | 23.7391 | 23.6789 | 23.6788 | 23.3019 | 23.3752 | 23.3932 | 23.3495 | 23.3576 | 23.3932 | 23.2767 | 22.9842 | 22.7854 | 23.3142 | 23.3716 | 23.3413 | 23.302 | 23.291 | 25.7271 | 33.0669 | 23.3485 | 24.3462 | 22.7228 | 23.0062 | 24.4191 | 27.1459 | 25.3015 | 26.8238 | 24.8924 | 25.7609 | 24.6323 | 23.498 | 22.5026 | 25.6521 | 24.2428 | 24.4876 | 21.8932 | 21.9064 | 21.9419 | 21.6594 | 22.6363 | 22.5155 | 25.3992 | 22.3114 | 22.2882 | 22.219 | 22.1879 | 22.1135 | 22.1874 | 23.2015 | 22.532 | 22.4512 | 22.7413 | 22.4792 | 22.7286 | 23.0007 | 22.9131 | 22.8537 | 22.7563 | 22.6712 | 22.6374 | 22.594 | 22.5687 | 23.6506 | 22.7363 | 22.7385 | 23.7642 | 22.8283 | 23.7815 | 22.8921 | 23.0588 | 23.1286 | 23.8926 | 22.9417 | 22.9762 | 22.9573 | 22.9184 | 22.7796 | 22.6872 | 22.6099 | 22.5384 | 23.6426 | 22.6262 | 22.7338 | 22.9723 | 23.4057 | 23.8638 | 23.8103 | 23.7297 | 23.6631 | 23.6745 | 23.7893 | 23.7554 | 23.6726 | 23.5868 | 23.474 | 23.3173 | 23.0774 | 22.8961 | 22.8645 | 22.9184 | 23.6985 | 23.6142 | 23.5643 | 23.5068 | 23.63 | 24.1509 | 24.0587 | 23.9492 | 23.8579 | 24.2081 | 23.6325 | 23.8553 | 23.7904 | 23.7127 | 23.6479 | 23.5982 | 23.6089 | 23.0715 | 22.9709 | 24.1187 | 24.028 | 24.0214 | 23.9741 | 23.9663 | 25.8279 | 29.0281 | 26.136 | 25.283 | 24.6952 | 24.3835 | 26.3677 | 27.1813 | 29.0052 | 27.3047 |  | 23.5183 | 22.4421 | 25.7472 | 24.6955 | 23.4297 | 23.4504 | 23.065 | 22.5928 | 21.6368 | 22.2682 | 10.8139 | 14.2743 | 14.906 | 11.1078 | 1.0607e-05 | -0.0031061 | 0.00085928 | 0.0038172 | 0.0016028 | -0.00055636 | 0.021341 | -0.0063577 | -0.034031 | -360.1065 | 17.4131 | -360.4142 | 17.6718 | -360.8604 | 18.1748 | -360.7866 | 17.5363 | -352.5244 | 18.6984 | -352.6075 | 16.8279 | 10.3618 | 359.7957 | 24.1104 | 14.5902 | 12.8644 | 22.1148
13:26 | 38 | 35.971 |  | 8.6421 | 3.4533 | 1.1998 | 3.3271 | -1.5754 | 12.6494 | 5.7218 | 0.6333 | 0.6762 | 0.9815 | 0.7674 | -128.7825 | 4.696 | 6.4591 | 1.7101 | -2.3085 | -0.7462 | 5.1102 |  | 4.9475 | 0.9156 | 3.9878 | 3.3668 | 3.3299 | 1.1069 | 1.0944 | 22.7455 | 22.6105 | 22.3931 | 22.3714 | 22.2828 | 22.2818 | 22.1578 | 22.9397 | 22.6545 | 22.7016 | 22.6868 | 22.7934 | 23.0247 | 22.9397 | 22.899 | 22.7888 | 22.684 | 22.6167 | 22.4952 | 22.3884 | 22.3241 | 22.2604 | 22.9292 | 22.5628 | 22.5949 | 22.5794 | 22.6069 | 23.1676 | 22.6823 | 22.9284 | 23.0504 | 23.0132 | 23.4978 | 22.8786 | 22.9158 | 22.8777 | 22.8122 | 22.6827 | 22.585 | 22.4175 | 22.2641 | 23.2653 | 22.6556 | 22.7483 | 22.9497 | 23.308 | 23.3229 | 23.2768 | 23.2736 | 23.2161 | 23.2677 | 23.0602 | 23.0738 | 23.116 | 23.0745 | 22.9908 | 22.9105 | 22.796 | 22.7079 | 22.7631 | 22.84 | 23.1506 | 23.1758 | 23.1575 | 23.0718 | 23.0984 | 23.8303 | 23.7255 | 23.7447 | 23.6797 | 23.6882 | 23.3051 | 23.3759 | 23.3928 | 23.3555 | 23.3673 | 23.3934 | 23.2695 | 22.9747 | 22.7871 | 23.3168 | 23.3644 | 23.3429 | 23.2983 | 23.2886 | 25.8794 | 34.108 | 23.3747 | 24.3394 | 22.8168 | 23.0773 | 24.4587 | 27.2924 | 25.3827 | 26.9507 | 25.556 | 25.8755 | 25.5358 | 23.4552 | 23.1857 | 26.9515 | 24.6628 | 25.3319 | 21.9387 | 21.9339 | 21.9923 | 21.6971 | 22.6394 | 22.5187 | 25.3604 | 22.3132 | 22.2931 | 22.2223 | 22.1856 | 22.1111 | 22.1914 | 23.2008 | 22.5367 | 22.4457 | 22.7512 | 22.4798 | 22.73 | 22.9991 | 22.9125 | 22.8489 | 22.7513 | 22.6677 | 22.6303 | 22.5916 | 22.5604 | 23.6507 | 22.737 | 22.7305 | 23.7648 | 22.8305 | 23.7725 | 22.8922 | 23.0581 | 23.1315 | 23.8915 | 22.9376 | 22.9753 | 22.9577 | 22.9178 | 22.7778 | 22.6846 | 22.6029 | 22.5388 | 23.6411 | 22.6276 | 22.7305 | 22.9746 | 23.4202 | 23.8654 | 23.8092 | 23.7353 | 23.6621 | 23.6805 | 23.7955 | 23.7584 | 23.6709 | 23.5949 | 23.4766 | 23.3156 | 23.072 | 22.895 | 22.8702 | 22.9195 | 23.6972 | 23.6129 | 23.5607 | 23.5061 | 23.6329 | 24.1464 | 24.0535 | 23.9378 | 23.8529 | 24.2137 | 23.6266 | 23.8509 | 23.7863 | 23.7069 | 23.648 | 23.5898 | 23.6042 | 23.0679 | 22.9661 | 24.11 | 24.0281 | 24.0173 | 23.9668 | 23.9647 | 25.8249 | 28.8918 | 26.8588 | 25.4871 | 24.7967 | 24.5156 | 26.4608 | 27.2498 | 29.1634 | 27.3468 |  | 23.645 | 22.5178 | 25.8568 | 24.6875 | 23.4235 | 23.4429 | 23.1002 | 22.5988 | 21.6299 | 22.27 | 10.8263 | 14.3019 | 14.8615 | 11.1113 | -0.00015825 | -0.002752 | 0.0016534 | 0.0041403 | 0.0012308 | -1.4891e-05 | 0.010474 | -0.011288 | 0.0047924 | -360.1804 | 17.4172 | -360.3835 | 17.6184 | -360.7589 | 18.1604 | -360.8204 | 17.5855 | -352.6321 | 18.7107 | -352.5921 | 16.7745 | 6.4652 | 358.8952 | 24.2109 | 14.5817 | 12.914 | 22.1144
13:27 | 39 | 35.9472 |  | 8.5397 | 3.4733 | 1.1356 | 3.2278 | -1.6047 | 12.6777 | 5.5911 | 0.6337 | 0.6769 | 0.9801 | 0.7695 | -128.8349 | 4.6689 | 6.413 | 1.816 | -2.3155 | -0.7936 | 5.1033 |  | 4.9847 | 0.9561 | 3.9886 | 3.3667 | 3.3332 | 1.1082 | 0.3305 | 22.744 | 22.6085 | 22.3898 | 22.3641 | 22.2853 | 22.2792 | 22.1543 | 22.9381 | 22.6523 | 22.7012 | 22.6826 | 22.8017 | 23.0225 | 22.9379 | 22.8961 | 22.7946 | 22.6854 | 22.617 | 22.4944 | 22.388 | 22.3278 | 22.2595 | 22.9336 | 22.5609 | 22.5956 | 22.5776 | 22.6057 | 23.1634 | 22.6833 | 22.9294 | 23.0529 | 23.0239 | 23.5008 | 22.8804 | 22.9176 | 22.8805 | 22.8207 | 22.6874 | 22.5953 | 22.4262 | 22.2652 | 23.2638 | 22.6609 | 22.754 | 22.9607 | 23.3041 | 23.3169 | 23.2683 | 23.2661 | 23.2102 | 23.2748 | 23.0541 | 23.0684 | 23.1143 | 23.0697 | 22.9909 | 22.9099 | 22.7924 | 22.7028 | 22.7671 | 22.832 | 23.153 | 23.1763 | 23.1568 | 23.0729 | 23.1074 | 23.8302 | 23.731 | 23.7461 | 23.6772 | 23.697 | 23.3104 | 23.3769 | 23.3962 | 23.3575 | 23.3699 | 23.3974 | 23.2656 | 22.981 | 22.7871 | 23.3147 | 23.3618 | 23.3394 | 23.3034 | 23.2903 | 26.4634 | 37.9481 | 23.3885 | 24.3396 | 22.9094 | 23.1543 | 24.5034 | 27.4287 | 25.4581 | 27.0656 | 26.3776 | 25.5295 | 26.5208 | 23.5152 | 23.852 | 28.1131 | 24.7863 | 26.0623 | 21.9813 | 21.9614 | 22.0398 | 21.7321 | 22.6375 | 22.5237 | 25.3557 | 22.3142 | 22.2976 | 22.2223 | 22.1805 | 22.1132 | 22.1975 | 23.1955 | 22.5292 | 22.4405 | 22.7499 | 22.4733 | 22.7243 | 23.0052 | 22.9202 | 22.8608 | 22.7572 | 22.67 | 22.6335 | 22.5962 | 22.5628 | 23.6578 | 22.7432 | 22.7345 | 23.7657 | 22.8362 | 23.7748 | 22.8902 | 23.0501 | 23.1336 | 23.8824 | 22.9322 | 22.9715 | 22.9508 | 22.9085 | 22.7768 | 22.6741 | 22.5991 | 22.5319 | 23.6298 | 22.6122 | 22.7253 | 22.9698 | 23.4204 | 23.8606 | 23.8062 | 23.7331 | 23.6554 | 23.6799 | 23.7916 | 23.7456 | 23.6669 | 23.6001 | 23.4711 | 23.3066 | 23.0665 | 22.8946 | 22.8696 | 22.9094 | 23.6883 | 23.6053 | 23.5591 | 23.4997 | 23.6325 | 24.1424 | 24.0468 | 23.9295 | 23.8525 | 24.2229 | 23.6212 | 23.8466 | 23.7772 | 23.7012 | 23.6447 | 23.5814 | 23.6109 | 23.067 | 22.9686 | 24.1059 | 24.0319 | 24.0177 | 23.9675 | 23.9716 | 25.822 | 28.7696 | 27.9698 | 25.8094 | 24.8864 | 24.6518 | 26.5448 | 27.3032 | 29.2963 | 27.3754 |  | 23.7854 | 22.6008 | 25.9781 | 24.6885 | 23.4285 | 23.4527 | 23.1364 | 22.6191 | 21.6464 | 22.2721 | 10.8023 | 14.2427 | 14.844 | 11.0805 | 0.00026729 | -0.0026778 | 0.0019601 | 0.0044721 | 0.0015857 | -0.00085886 | 0.017871 | -0.010328 | -0.02771 | -360.1034 | 17.4028 | -360.4512 | 17.6902 | -360.8758 | 18.22 | -360.845 | 17.5609 | -352.5644 | 18.6963 | -352.6321 | 16.8381 | 2.1997 | 358.4109 | 24.3139 | 14.5433 | 12.8375 | 22.1328
13:27 | 40 | 35.8937 |  | 8.4538 | 3.4532 | 1.0174 | 3.2232 | -1.6136 | 12.6922 | 5.5778 | 0.6346 | 0.6756 | 0.9807 | 0.7686 | -128.8106 | 4.6784 | 6.5203 | 1.8181 | -2.2665 | -0.8149 | 5.0975 |  | 4.9455 | 0.9575 | 3.9857 | 3.3664 | 3.3305 | 1.107 | 1.0657 | 22.7374 | 22.604 | 22.3841 | 22.3575 | 22.2747 | 22.2684 | 22.1446 | 22.9302 | 22.6451 | 22.6862 | 22.6745 | 22.798 | 23.0106 | 22.9285 | 22.8981 | 22.7995 | 22.6866 | 22.6178 | 22.494 | 22.385 | 22.3264 | 22.2579 | 22.9301 | 22.5589 | 22.5971 | 22.5774 | 22.6043 | 23.1678 | 22.6912 | 22.9348 | 23.0522 | 23.0233 | 23.5013 | 22.8773 | 22.9105 | 22.8798 | 22.8211 | 22.6868 | 22.5955 | 22.4237 | 22.2578 | 23.2613 | 22.6645 | 22.754 | 22.9575 | 23.3117 | 23.324 | 23.2693 | 23.2721 | 23.2192 | 23.2866 | 23.0632 | 23.0746 | 23.1109 | 23.0726 | 22.9961 | 22.9124 | 22.7994 | 22.7111 | 22.7805 | 22.8378 | 23.1397 | 23.1767 | 23.1505 | 23.0688 | 23.111 | 23.8193 | 23.7259 | 23.7364 | 23.6737 | 23.69 | 23.3042 | 23.3694 | 23.3941 | 23.3539 | 23.3613 | 23.3896 | 23.2655 | 22.9824 | 22.7868 | 23.3154 | 23.361 | 23.3369 | 23.3051 | 23.2941 | 27.1498 | 42.7176 | 23.4137 | 24.3571 | 23.0003 | 23.2429 | 24.5548 | 27.5661 | 25.5349 | 27.1899 | 27.2501 | 25.069 | 27.7177 | 23.9412 | 24.6669 | 28.93 | 24.8993 | 26.5391 | 22.0152 | 21.9938 | 22.0946 | 21.7721 | 22.6459 | 22.5251 | 25.3681 | 22.3118 | 22.3016 | 22.2251 | 22.1779 | 22.1132 | 22.2025 | 23.1935 | 22.5245 | 22.4459 | 22.7519 | 22.4756 | 22.7217 | 23.001 | 22.9155 | 22.8553 | 22.7513 | 22.669 | 22.6307 | 22.5856 | 22.557 | 23.6531 | 22.733 | 22.7305 | 23.7529 | 22.8377 | 23.7755 | 22.8838 | 23.0472 | 23.1378 | 23.8818 | 22.937 | 22.9768 | 22.9492 | 22.9103 | 22.7781 | 22.668 | 22.6018 | 22.5349 | 23.6305 | 22.6064 | 22.7276 | 22.966 | 23.4235 | 23.8508 | 23.8076 | 23.7236 | 23.6497 | 23.6857 | 23.7842 | 23.7436 | 23.6662 | 23.5901 | 23.47 | 23.3133 | 23.0443 | 22.894 | 22.8602 | 22.902 | 23.692 | 23.6151 | 23.5607 | 23.5028 | 23.646 | 24.1506 | 24.0608 | 23.9395 | 23.8613 | 24.2578 | 23.6272 | 23.8515 | 23.7826 | 23.7077 | 23.6462 | 23.5964 | 23.617 | 23.0768 | 22.9746 | 24.1113 | 24.0376 | 24.0229 | 23.9757 | 23.9847 | 25.8312 | 28.6834 | 28.4694 | 26.0682 | 24.9735 | 24.7934 | 26.6217 | 27.3464 | 29.4041 | 27.4206 |  | 23.9506 | 22.6802 | 26.0864 | 24.6895 | 23.4331 | 23.4584 | 23.1741 | 22.626 | 21.6414 | 22.2796 | 10.8137 | 14.2535 | 14.8945 | 11.1069 | 0.0005397 | -0.0031249 | 0.0014341 | 0.0042046 | 0.0012567 | 0.00030342 | 0.018893 | -0.011874 | -0.020845 | -360.2173 | 17.4397 | -360.405 | 17.6307 | -360.7835 | 18.1584 | -360.8235 | 17.5896 | -352.6537 | 18.7271 | -352.5983 | 16.7807 | 4.9524 | 362.3755 | 24.4186 | 14.574 | 12.7624 | 22.1337
13:27 | 41 | 35.8249 |  | 8.5055 | 3.3958 | 0.9653 | 3.2306 | -1.7134 | 12.6695 | 5.5379 | 0.6345 | 0.6763 | 0.9784 | 0.7682 | -128.8128 | 4.7766 | 6.4308 | 1.7781 | -2.3249 | -0.82 | 5.0525 |  | 4.9132 | 0.8914 | 3.9873 | 3.3674 | 3.3308 | 1.1059 | 0.3684 | 22.7368 | 22.5967 | 22.38 | 22.3587 | 22.2696 | 22.2693 | 22.1482 | 22.9278 | 22.6436 | 22.6812 | 22.6716 | 22.8031 | 23.0104 | 22.9298 | 22.897 | 22.7938 | 22.6843 | 22.6139 | 22.4936 | 22.3759 | 22.3233 | 22.2574 | 22.9221 | 22.5544 | 22.5881 | 22.5685 | 22.6036 | 23.1646 | 22.6916 | 22.9268 | 23.0492 | 23.0226 | 23.5009 | 22.8777 | 22.9098 | 22.8853 | 22.8216 | 22.6851 | 22.5962 | 22.4199 | 22.2605 | 23.2653 | 22.6636 | 22.7525 | 22.955 | 23.3214 | 23.325 | 23.2721 | 23.2791 | 23.222 | 23.2969 | 23.0687 | 23.0729 | 23.1126 | 23.0751 | 22.9977 | 22.9199 | 22.7891 | 22.7165 | 22.8026 | 22.8449 | 23.134 | 23.1763 | 23.1523 | 23.067 | 23.1144 | 23.8166 | 23.7185 | 23.7323 | 23.6735 | 23.6868 | 23.299 | 23.3696 | 23.395 | 23.3521 | 23.3595 | 23.388 | 23.278 | 22.9794 | 22.7904 | 23.3161 | 23.3669 | 23.3374 | 23.3078 | 23.3012 | 27.8576 | 45.7871 | 23.4569 | 24.4015 | 23.0883 | 23.3217 | 24.6084 | 27.7411 | 25.6283 | 27.3722 | 28.2349 | 25.6067 | 28.8211 | 25.8844 | 25.8877 | 29.2931 | 24.8328 | 26.9709 | 22.0503 | 22.0261 | 22.1447 | 21.8153 | 22.642 | 22.5204 | 25.3888 | 22.3048 | 22.2918 | 22.2204 | 22.1778 | 22.1103 | 22.1955 | 23.195 | 22.5269 | 22.4441 | 22.76 | 22.4743 | 22.72 | 22.9884 | 22.9103 | 22.8439 | 22.7388 | 22.6616 | 22.625 | 22.576 | 22.5479 | 23.6408 | 22.7291 | 22.7238 | 23.7431 | 22.8415 | 23.7685 | 22.8806 | 23.0509 | 23.1348 | 23.8841 | 22.9344 | 22.9735 | 22.946 | 22.9103 | 22.7756 | 22.6716 | 22.6018 | 22.5385 | 23.6356 | 22.6137 | 22.7279 | 22.9647 | 23.4304 | 23.8515 | 23.8043 | 23.7158 | 23.6477 | 23.6895 | 23.7818 | 23.7475 | 23.6644 | 23.5829 | 23.4643 | 23.3259 | 23.0187 | 22.8923 | 22.8543 | 22.8996 | 23.6962 | 23.618 | 23.5567 | 23.5017 | 23.656 | 24.1508 | 24.0611 | 23.9392 | 23.86 | 24.2842 | 23.6277 | 23.8503 | 23.7818 | 23.7052 | 23.6423 | 23.5973 | 23.621 | 23.075 | 22.9739 | 24.1119 | 24.0359 | 24.0224 | 23.9678 | 23.986 | 25.8696 | 28.6936 | 28.7399 | 26.3016 | 25.0625 | 24.9725 | 26.6948 | 27.4221 | 29.5342 | 27.555 |  | 24.1272 | 22.7421 | 26.1687 | 24.6816 | 23.4218 | 23.4471 | 23.1938 | 22.6329 | 21.636 | 22.2707 | 10.8228 | 14.2772 | 14.8926 | 11.1291 | 0.00026199 | -0.0032464 | 0.0017674 | 0.004749 | 0.0014169 | -0.00032388 | 0.01185 | -0.0026956 | -0.012493 | -360.0881 | 17.3699 | -360.3835 | 17.6389 | -360.805 | 18.1912 | -360.7897 | 17.5445 | -352.5367 | 18.6614 | -352.5613 | 16.8238 | 4.6102 | 357.0478 | 24.5222 | 14.5849 | 12.6244 | 22.1345
13:27 | 42 | 35.7853 |  | 8.4464 | 3.4101 | 0.9534 | 3.2259 | -1.7336 | 12.6532 | 5.5188 | 0.6337 | 0.6759 | 0.9808 | 0.7683 | -128.7921 | 4.7491 | 6.4093 | 1.6738 | -2.3687 | -0.8134 | 4.9781 |  | 4.8879 | 0.9435 | 3.9881 | 3.3667 | 3.3287 | 1.1077 | 0.9185 | 22.7402 | 22.6016 | 22.3846 | 22.3597 | 22.2758 | 22.2734 | 22.1546 | 22.9338 | 22.6479 | 22.6852 | 22.6778 | 22.8158 | 23.0178 | 22.9357 | 22.8872 | 22.7829 | 22.6783 | 22.6071 | 22.4853 | 22.3677 | 22.3162 | 22.2541 | 22.9213 | 22.5527 | 22.58 | 22.5632 | 22.6069 | 23.1516 | 22.6835 | 22.9154 | 23.0397 | 23.0217 | 23.4978 | 22.8747 | 22.908 | 22.877 | 22.8134 | 22.6722 | 22.592 | 22.4135 | 22.2549 | 23.2619 | 22.6555 | 22.7514 | 22.9568 | 23.3233 | 23.3173 | 23.271 | 23.2749 | 23.2154 | 23.3048 | 23.0645 | 23.0702 | 23.1132 | 23.0757 | 22.9969 | 22.9218 | 22.7769 | 22.7152 | 22.8247 | 22.8429 | 23.138 | 23.1755 | 23.1538 | 23.0664 | 23.1212 | 23.8266 | 23.7228 | 23.7407 | 23.6734 | 23.696 | 23.2979 | 23.3742 | 23.398 | 23.3527 | 23.3578 | 23.3896 | 23.2806 | 22.9804 | 22.7854 | 23.3123 | 23.3704 | 23.3314 | 23.3078 | 23.3062 | 28.6415 | 47.7695 | 23.4927 | 24.501 | 23.1777 | 23.4015 | 24.6775 | 27.9799 | 25.7849 | 27.6661 | 29.5107 | 27.7616 | 29.9095 | 29.2035 | 27.9512 | 29.1905 | 25.853 | 27.1335 | 22.093 | 22.0551 | 22.1905 | 21.8549 | 22.6343 | 22.5139 | 25.4017 | 22.3073 | 22.2809 | 22.2133 | 22.1782 | 22.1102 | 22.1876 | 23.1925 | 22.525 | 22.4412 | 22.7691 | 22.4731 | 22.7177 | 22.9859 | 22.9075 | 22.8424 | 22.7297 | 22.6513 | 22.6246 | 22.5738 | 22.5516 | 23.6377 | 22.7281 | 22.7208 | 23.7439 | 22.8417 | 23.7652 | 22.8773 | 23.0472 | 23.1334 | 23.8792 | 22.9273 | 22.9688 | 22.9401 | 22.9006 | 22.7744 | 22.6765 | 22.6016 | 22.5311 | 23.6331 | 22.6062 | 22.7247 | 22.96 | 23.4413 | 23.8521 | 23.7965 | 23.7133 | 23.652 | 23.6864 | 23.7785 | 23.7475 | 23.6627 | 23.5818 | 23.4563 | 23.3224 | 23.0226 | 22.8885 | 22.8481 | 22.9001 | 23.6916 | 23.6115 | 23.5549 | 23.5002 | 23.6543 | 24.1385 | 24.0506 | 23.935 | 23.8504 | 24.3055 | 23.6197 | 23.8458 | 23.7747 | 23.6943 | 23.6345 | 23.5903 | 23.6196 | 23.0714 | 22.9725 | 24.1136 | 24.0273 | 24.0243 | 23.9661 | 23.9872 | 25.913 | 28.8586 | 29.0347 | 26.5453 | 25.1416 | 25.1825 | 26.7654 | 27.5315 | 29.7231 | 27.7672 |  | 24.3416 | 22.8232 | 26.2583 | 24.6868 | 23.4196 | 23.4465 | 23.2182 | 22.6456 | 21.6447 | 22.2754 | 10.8018 | 14.2625 | 14.8746 | 11.0812 | -0.00022609 | -0.0028777 | 0.0010924 | 0.0042618 | 0.0011754 | -0.00020423 | 0.027494 | -0.013524 | -0.034375 | -360.2327 | 17.45 | -360.4296 | 17.6286 | -360.7681 | 18.1543 | -360.8481 | 17.6102 | -352.6967 | 18.7395 | -352.6229 | 16.7807 | 5.3151 | 363.6855 | 24.6365 | 14.5686 | 12.5326 | 22.1452
13:27 | 43 | 35.6151 |  | 8.5945 | 3.4336 | 0.9854 | 3.2866 | -1.585 | 12.6908 | 5.6064 | 0.6334 | 0.6705 | 0.9803 | 0.768 | -128.8545 | 4.7807 | 6.4543 | 1.6369 | -2.3802 | -0.8548 | 4.9414 |  | 4.8581 | 1.0353 | 3.9869 | 3.3653 | 3.3287 | 1.1058 | -0.176 | 22.7398 | 22.6023 | 22.3878 | 22.3577 | 22.2747 | 22.2719 | 22.1475 | 22.9334 | 22.6497 | 22.6847 | 22.6807 | 22.8292 | 23.0218 | 22.9384 | 22.8932 | 22.7785 | 22.6793 | 22.6047 | 22.4902 | 22.3763 | 22.323 | 22.2507 | 22.9293 | 22.5501 | 22.5876 | 22.5709 | 22.6136 | 23.1539 | 22.6839 | 22.9226 | 23.0372 | 23.0191 | 23.494 | 22.8729 | 22.9058 | 22.8694 | 22.808 | 22.6716 | 22.5894 | 22.4147 | 22.2529 | 23.2616 | 22.6553 | 22.7492 | 22.9562 | 23.3259 | 23.3166 | 23.2679 | 23.2662 | 23.2078 | 23.3076 | 23.0573 | 23.0682 | 23.1093 | 23.0766 | 22.9906 | 22.9195 | 22.775 | 22.7043 | 22.8308 | 22.8418 | 23.1376 | 23.173 | 23.1461 | 23.0672 | 23.125 | 23.8216 | 23.7246 | 23.7402 | 23.6734 | 23.7072 | 23.2969 | 23.37 | 23.394 | 23.353 | 23.3577 | 23.385 | 23.2767 | 22.9758 | 22.7782 | 23.308 | 23.3653 | 23.3271 | 23.299 | 23.3048 | 28.9021 | 49.3247 | 23.5337 | 24.6514 | 23.2623 | 23.4961 | 24.7629 | 28.274 | 26.0093 | 28.0294 | 31.0237 | 30.6601 | 30.6788 | 32.2555 | 30.7712 | 28.5947 | 28.9045 | 27.2399 | 22.1296 | 22.0815 | 22.2328 | 21.8887 | 22.6375 | 22.5131 | 25.408 | 22.3071 | 22.2861 | 22.2099 | 22.1846 | 22.108 | 22.189 | 23.1923 | 22.5244 | 22.4455 | 22.7781 | 22.4755 | 22.7154 | 22.9923 | 22.9038 | 22.8418 | 22.7324 | 22.6503 | 22.6259 | 22.5739 | 22.5531 | 23.6406 | 22.723 | 22.7157 | 23.7461 | 22.8403 | 23.7646 | 22.8744 | 23.0394 | 23.1325 | 23.8698 | 22.9219 | 22.9615 | 22.9357 | 22.8996 | 22.7709 | 22.6694 | 22.5969 | 22.527 | 23.6283 | 22.6002 | 22.7183 | 22.9541 | 23.4515 | 23.8454 | 23.8006 | 23.712 | 23.6497 | 23.6832 | 23.7779 | 23.7477 | 23.6617 | 23.5831 | 23.4535 | 23.3261 | 23.0262 | 22.8843 | 22.8445 | 22.9012 | 23.6927 | 23.6075 | 23.5519 | 23.4942 | 23.6562 | 24.1413 | 24.0484 | 23.9299 | 23.8426 | 24.3407 | 23.622 | 23.8466 | 23.7741 | 23.6927 | 23.6311 | 23.5873 | 23.6133 | 23.0674 | 22.9672 | 24.1074 | 24.0179 | 24.0155 | 23.9637 | 23.9833 | 25.9381 | 29.1255 | 29.2561 | 26.799 | 25.2173 | 25.408 | 26.8513 | 27.6759 | 29.9692 | 28.0029 |  | 24.5785 | 22.9032 | 26.3524 | 24.6942 | 23.4265 | 23.455 | 23.2548 | 22.6671 | 21.6576 | 22.285 | 10.835 | 14.2674 | 14.9003 | 11.0933 | -5.394e-05 | -0.0028455 | 0.00088904 | 0.0039639 | 0.00097333 | -0.00064323 | 0.0056683 | 0.0044461 | -0.018992 | -360.1127 | 17.4069 | -360.4266 | 17.6738 | -360.8666 | 18.2159 | -360.8574 | 17.5917 | -352.5921 | 18.6861 | -352.629 | 16.832 | 7.8144 | 357.9182 | 24.7586 | 14.5839 | 12.6747 | 22.1623
13:27 | 44 | 35.7594 |  | 8.514 | 3.4155 | 0.9637 | 3.3006 | -1.6587 | 12.6697 | 5.6303 | 0.6344 | 0.6751 | 0.9815 | 0.7665 | -128.8065 | 4.7025 | 6.4627 | 1.6442 | -2.4049 | -0.802 | 4.9766 |  | 4.8941 | 0.896 | 3.9883 | 3.367 | 3.3297 | 1.1076 | -0.0299 | 22.7337 | 22.5946 | 22.3876 | 22.3579 | 22.27 | 22.2694 | 22.1478 | 22.9331 | 22.646 | 22.6802 | 22.6737 | 22.8391 | 23.0217 | 22.9371 | 22.8971 | 22.7812 | 22.6816 | 22.6051 | 22.4977 | 22.3802 | 22.3264 | 22.248 | 22.9258 | 22.5507 | 22.5911 | 22.5648 | 22.6161 | 23.1572 | 22.6825 | 22.9305 | 23.04 | 23.0181 | 23.489 | 22.8683 | 22.9039 | 22.8688 | 22.8074 | 22.675 | 22.5863 | 22.4081 | 22.247 | 23.2535 | 22.6548 | 22.7464 | 22.9526 | 23.3268 | 23.3136 | 23.2643 | 23.264 | 23.2059 | 23.3141 | 23.0546 | 23.0691 | 23.1106 | 23.0742 | 22.9862 | 22.9186 | 22.7782 | 22.7002 | 22.8254 | 22.844 | 23.1359 | 23.169 | 23.1467 | 23.0632 | 23.1307 | 23.8173 | 23.7247 | 23.7335 | 23.6684 | 23.7121 | 23.2984 | 23.3692 | 23.3856 | 23.3515 | 23.3604 | 23.3885 | 23.2789 | 22.9786 | 22.7907 | 23.3148 | 23.366 | 23.3359 | 23.3066 | 23.317 | 29.0306 | 50.9143 | 23.5985 | 24.8354 | 23.3464 | 23.5881 | 24.8656 | 28.6123 | 26.2619 | 28.4052 | 32.1004 | 31.8361 | 31.2108 | 34.6553 | 33.5799 | 28.8055 | 31.6399 | 28.3211 | 22.1583 | 22.1125 | 22.2823 | 21.9252 | 22.6384 | 22.5095 | 25.4354 | 22.3029 | 22.2886 | 22.2131 | 22.1856 | 22.1028 | 22.1903 | 23.1952 | 22.5271 | 22.4459 | 22.7864 | 22.4745 | 22.716 | 22.9963 | 22.902 | 22.8449 | 22.7451 | 22.6546 | 22.6264 | 22.5791 | 22.5456 | 23.6333 | 22.7184 | 22.7141 | 23.7471 | 22.8424 | 23.7649 | 22.8711 | 23.0423 | 23.1359 | 23.8723 | 22.9261 | 22.9594 | 22.9355 | 22.9044 | 22.7746 | 22.67 | 22.5949 | 22.5253 | 23.6329 | 22.6077 | 22.7202 | 22.9497 | 23.4615 | 23.8481 | 23.8078 | 23.713 | 23.6487 | 23.6968 | 23.7837 | 23.7485 | 23.6597 | 23.5892 | 23.4522 | 23.3346 | 23.0203 | 22.8876 | 22.8483 | 22.9051 | 23.694 | 23.604 | 23.5503 | 23.4901 | 23.6675 | 24.1419 | 24.0452 | 23.924 | 23.8426 | 24.3754 | 23.6248 | 23.8382 | 23.775 | 23.6915 | 23.6336 | 23.5883 | 23.6044 | 23.0594 | 22.9616 | 24.1002 | 24.0092 | 24.004 | 23.9558 | 23.974 | 25.9669 | 29.4142 | 29.444 | 27.0273 | 25.2933 | 25.6392 | 26.9442 | 27.8522 | 30.2699 | 28.2305 |  | 24.8069 | 22.9795 | 26.4311 | 24.6875 | 23.429 | 23.448 | 23.2757 | 22.6779 | 21.6495 | 22.2782 | 10.8384 | 14.2712 | 14.8846 | 11.1243 | 0.0005192 | -0.0033116 | 0.0011328 | 0.0038781 | 0.0010706 | -0.0010085 | 0.0065962 | -0.010817 | -0.023562 | -360.2142 | 17.448 | -360.4512 | 17.6122 | -360.765 | 18.1358 | -360.7835 | 17.5896 | -352.626 | 18.7271 | -352.626 | 16.7766 | 6.1672 | 362.0236 | 24.8786 | 14.5779 | 12.6117 | 22.1637
13:27 | 45 | 35.6874 |  | 8.5586 | 3.4709 | 0.9523 | 3.256 | -1.531 | 12.6995 | 5.6181 | 0.635 | 0.6746 | 0.9801 | 0.7679 | -128.9022 | 4.6509 | 6.4507 | 1.6652 | -2.4366 | -0.8395 | 4.8978 |  | 4.9744 | 1.0262 | 3.9856 | 3.3658 | 3.3305 | 1.1082 | -0.2173 | 22.7315 | 22.598 | 22.3837 | 22.3608 | 22.2718 | 22.2651 | 22.1505 | 22.9286 | 22.6404 | 22.6779 | 22.6729 | 22.8483 | 23.0159 | 22.9378 | 22.8957 | 22.7819 | 22.6814 | 22.6061 | 22.498 | 22.3773 | 22.3174 | 22.2516 | 22.9224 | 22.5536 | 22.5887 | 22.5656 | 22.6209 | 23.1578 | 22.6815 | 22.9307 | 23.0334 | 23.0167 | 23.4834 | 22.86 | 22.9014 | 22.8708 | 22.8044 | 22.6699 | 22.583 | 22.4023 | 22.2404 | 23.2468 | 22.6489 | 22.7485 | 22.9549 | 23.3276 | 23.3076 | 23.2654 | 23.2694 | 23.2027 | 23.324 | 23.054 | 23.0642 | 23.11 | 23.0665 | 22.9873 | 22.9119 | 22.7896 | 22.7008 | 22.8167 | 22.8383 | 23.1311 | 23.1655 | 23.1416 | 23.0566 | 23.132 | 23.8194 | 23.7153 | 23.7273 | 23.6589 | 23.7149 | 23.2916 | 23.3668 | 23.3843 | 23.3478 | 23.3594 | 23.3829 | 23.2767 | 22.9799 | 22.7864 | 23.3165 | 23.3661 | 23.3395 | 23.3079 | 23.3215 | 29.9607 | 52.1101 | 23.6407 | 25.0181 | 23.4276 | 23.6849 | 24.968 | 28.9638 | 26.5208 | 28.7686 | 32.8052 | 32.3808 | 31.2756 | 36.5883 | 36.3039 | 29.925 | 32.993 | 28.784 | 22.1962 | 22.1481 | 22.3423 | 21.9676 | 22.6393 | 22.5096 | 25.4815 | 22.3067 | 22.2895 | 22.2211 | 22.1851 | 22.1014 | 22.1888 | 23.1982 | 22.5204 | 22.4491 | 22.7945 | 22.4747 | 22.7199 | 22.996 | 22.901 | 22.8425 | 22.75 | 22.6554 | 22.6225 | 22.5819 | 22.5417 | 23.6322 | 22.7195 | 22.7123 | 23.7473 | 22.8502 | 23.7638 | 22.8713 | 23.0412 | 23.1452 | 23.8779 | 22.9339 | 22.9643 | 22.9393 | 22.8975 | 22.7813 | 22.6739 | 22.6007 | 22.5248 | 23.633 | 22.6089 | 22.7217 | 22.9497 | 23.4596 | 23.8495 | 23.7937 | 23.7104 | 23.645 | 23.7016 | 23.7776 | 23.7346 | 23.6506 | 23.5831 | 23.4526 | 23.3224 | 23.0202 | 22.8817 | 22.8544 | 22.9014 | 23.6919 | 23.6069 | 23.5563 | 23.4964 | 23.6799 | 24.1386 | 24.0479 | 23.9282 | 23.8495 | 24.4155 | 23.6212 | 23.8342 | 23.7799 | 23.6942 | 23.6383 | 23.5971 | 23.6115 | 23.0636 | 22.9622 | 24.1037 | 24.0188 | 24.0099 | 23.9605 | 23.9814 | 26.0047 | 29.7339 | 29.5203 | 27.2544 | 25.3738 | 25.8885 | 27.0416 | 28.039 | 30.6168 | 28.4336 |  | 25.0567 | 23.0717 | 26.5103 | 24.6843 | 23.4261 | 23.4515 | 23.3001 | 22.6954 | 21.656 | 22.2905 | 10.8074 | 14.2824 | 14.8813 | 11.1287 | 0.00023941 | -0.003167 | 0.0011818 | 0.0038336 | 0.00051257 | -0.00072473 | 0.012132 | -0.0040309 | -0.004799 | -360.085 | 17.3843 | -360.365 | 17.643 | -360.8174 | 18.1892 | -360.8297 | 17.5691 | -352.5429 | 18.6676 | -352.5736 | 16.8135 | 11.0297 | 360.4211 | 25.0069 | 14.5818 | 12.6936 | 22.1757
13:27 | 46 | 35.6284 |  | 8.5087 | 3.4933 | 1.0724 | 3.2885 | -1.678 | 12.5601 | 5.5639 | 0.6349 | 0.6747 | 0.9809 | 0.7676 | -128.9026 | 4.7835 | 6.4917 | 1.8496 | -2.4262 | -0.9187 | 5.0323 |  | 4.8903 | 0.9145 | 3.9863 | 3.3667 | 3.3305 | 1.1087 | -0.3329 | 22.7379 | 22.6054 | 22.3924 | 22.3667 | 22.2781 | 22.274 | 22.1506 | 22.9269 | 22.6475 | 22.6869 | 22.6817 | 22.8629 | 23.0187 | 22.9447 | 22.8901 | 22.7801 | 22.6752 | 22.602 | 22.4966 | 22.3728 | 22.3153 | 22.2494 | 22.9225 | 22.5502 | 22.5802 | 22.574 | 22.6246 | 23.1584 | 22.6822 | 22.9237 | 23.0391 | 23.031 | 23.4923 | 22.8639 | 22.9119 | 22.8793 | 22.8091 | 22.679 | 22.591 | 22.4145 | 22.2532 | 23.2599 | 22.6571 | 22.7601 | 22.9614 | 23.3384 | 23.3136 | 23.2708 | 23.2707 | 23.207 | 23.3348 | 23.0508 | 23.061 | 23.1102 | 23.0733 | 22.9912 | 22.917 | 22.8011 | 22.7032 | 22.8245 | 22.8381 | 23.1296 | 23.1702 | 23.1462 | 23.0624 | 23.1457 | 23.8228 | 23.7177 | 23.7321 | 23.6641 | 23.7306 | 23.2964 | 23.368 | 23.3927 | 23.3532 | 23.3643 | 23.3872 | 23.2793 | 22.9799 | 22.7793 | 23.3117 | 23.3667 | 23.3373 | 23.3047 | 23.3219 | 30.5208 | 52.5616 | 23.6712 | 25.1871 | 23.5193 | 23.815 | 25.075 | 29.3452 | 26.775 | 29.1215 | 33.6818 | 33.7198 | 30.7737 | 37.7319 | 38.723 | 30.4096 | 33.7182 | 28.5045 | 22.242 | 22.1863 | 22.4139 | 22.0252 | 22.6414 | 22.5177 | 25.5455 | 22.3138 | 22.2935 | 22.2216 | 22.1904 | 22.1079 | 22.1903 | 23.1991 | 22.5208 | 22.4483 | 22.8033 | 22.4781 | 22.722 | 22.9999 | 22.8996 | 22.8426 | 22.7532 | 22.6565 | 22.6204 | 22.5826 | 22.5417 | 23.6379 | 22.7235 | 22.7108 | 23.7436 | 22.8588 | 23.7611 | 22.8749 | 23.0453 | 23.1531 | 23.8767 | 22.9334 | 22.9676 | 22.9381 | 22.8925 | 22.7837 | 22.673 | 22.6032 | 22.5262 | 23.6274 | 22.6039 | 22.7218 | 22.9485 | 23.4612 | 23.8466 | 23.7903 | 23.7065 | 23.6429 | 23.6986 | 23.7758 | 23.7312 | 23.652 | 23.5807 | 23.454 | 23.3125 | 23.0303 | 22.8752 | 22.8507 | 22.8969 | 23.6881 | 23.6057 | 23.5544 | 23.4905 | 23.6874 | 24.1415 | 24.0461 | 23.9279 | 23.8496 | 24.448 | 23.6193 | 23.8359 | 23.7765 | 23.6952 | 23.635 | 23.5908 | 23.6201 | 23.0622 | 22.9636 | 24.1034 | 24.0228 | 24.0113 | 23.9603 | 23.9908 | 26.0444 | 30.0099 | 29.7104 | 27.5045 | 25.4556 | 26.1771 | 27.1612 | 28.2257 | 30.9788 | 28.6186 |  | 25.3426 | 23.1787 | 26.6064 | 24.6886 | 23.4333 | 23.4467 | 23.3271 | 22.7017 | 21.658 | 22.2911 | 10.7996 | 14.2748 | 14.8958 | 11.1276 | -0.00046518 | -0.003287 | 0.0014639 | 0.0043043 | 0.0015167 | -0.0010755 | 0.023773 | -0.016973 | -0.023415 | -360.2296 | 17.4664 | -360.4881 | 17.643 | -360.7743 | 18.144 | -360.802 | 17.6143 | -352.6813 | 18.7538 | -352.6629 | 16.8074 | 6.105 | 358.1549 | 25.157 | 14.5853 | 12.6452 | 22.1798
13:27 | 47 | 35.7317 |  | 8.4353 | 3.3956 | 0.9094 | 3.2758 | -1.5877 | 12.5884 | 5.6694 | 0.633 | 0.6743 | 0.9784 | 0.7664 | -128.8629 | 4.7602 | 6.4486 | 1.9338 | -2.4406 | -0.8309 | 4.9842 |  | 4.8778 | 0.9257 | 3.9866 | 3.3678 | 3.3284 | 1.1081 | 0.0571 | 22.7407 | 22.6011 | 22.3946 | 22.3618 | 22.2762 | 22.2776 | 22.1484 | 22.9278 | 22.6482 | 22.6859 | 22.6817 | 22.875 | 23.0214 | 22.9457 | 22.8855 | 22.7804 | 22.6754 | 22.6011 | 22.4977 | 22.3716 | 22.3199 | 22.2512 | 22.9208 | 22.5487 | 22.5767 | 22.5756 | 22.6254 | 23.1603 | 22.6798 | 22.9307 | 23.0405 | 23.0446 | 23.4975 | 22.8628 | 22.9147 | 22.8783 | 22.8136 | 22.6796 | 22.5933 | 22.4211 | 22.2617 | 23.266 | 22.6583 | 22.7685 | 22.966 | 23.3498 | 23.3185 | 23.2691 | 23.2709 | 23.2119 | 23.3408 | 23.0527 | 23.0662 | 23.1161 | 23.0812 | 22.9929 | 22.9232 | 22.8022 | 22.7133 | 22.8357 | 22.8439 | 23.1333 | 23.172 | 23.154 | 23.0664 | 23.1674 | 23.8235 | 23.729 | 23.74 | 23.6735 | 23.7425 | 23.3045 | 23.3758 | 23.3959 | 23.355 | 23.3703 | 23.3972 | 23.2769 | 22.9796 | 22.788 | 23.3078 | 23.3675 | 23.3357 | 23.3008 | 23.3262 | 30.4727 | 52.7863 | 23.7357 | 25.3524 | 23.6157 | 23.959 | 25.1885 | 29.7479 | 27.0324 | 29.4544 | 33.3454 | 33.6535 | 30.1571 | 38.6278 | 40.6146 | 30.5265 | 33.9931 | 28.4639 | 22.2888 | 22.2232 | 22.4899 | 22.0937 | 22.6332 | 22.5185 | 25.6012 | 22.3085 | 22.2847 | 22.2181 | 22.188 | 22.105 | 22.1883 | 23.1919 | 22.5236 | 22.439 | 22.8064 | 22.4723 | 22.7177 | 22.999 | 22.9082 | 22.8432 | 22.7538 | 22.6591 | 22.6241 | 22.5852 | 22.5448 | 23.6441 | 22.7245 | 22.7175 | 23.7444 | 22.8624 | 23.7673 | 22.8763 | 23.0525 | 23.1563 | 23.877 | 22.9309 | 22.9681 | 22.9357 | 22.8973 | 22.779 | 22.671 | 22.6042 | 22.5244 | 23.6268 | 22.6067 | 22.721 | 22.949 | 23.4744 | 23.8475 | 23.7997 | 23.7151 | 23.6479 | 23.7067 | 23.7793 | 23.7387 | 23.6567 | 23.5862 | 23.4545 | 23.3225 | 23.036 | 22.8783 | 22.8553 | 22.899 | 23.6884 | 23.605 | 23.5525 | 23.4939 | 23.7016 | 24.1394 | 24.041 | 23.9266 | 23.8472 | 24.4841 | 23.6211 | 23.8349 | 23.7728 | 23.6958 | 23.6332 | 23.5907 | 23.6193 | 23.0593 | 22.9652 | 24.1039 | 24.0208 | 24.0088 | 23.9628 | 23.996 | 26.1082 | 30.1794 | 29.847 | 27.7527 | 25.5548 | 26.4845 | 27.2962 | 28.4102 | 31.3395 | 28.7805 |  | 25.6435 | 23.3018 | 26.7223 | 24.7007 | 23.4332 | 23.4576 | 23.3628 | 22.7215 | 21.6673 | 22.3016 | 10.8298 | 14.3126 | 14.8939 | 11.1005 | 3.2841e-05 | -0.0026099 | 0.0018675 | 0.0047547 | 0.00097453 | -0.00012881 | 0.010339 | -0.0078427 | -0.0058009 | -360.1465 | 17.409 | -360.4327 | 17.6779 | -360.8727 | 18.2056 | -360.8204 | 17.5999 | -352.6106 | 18.6902 | -352.6044 | 16.8279 | 7.0283 | 362.111 | 25.3222 | 14.6032 | 12.6409 | 22.1944
13:27 | 48 | 35.7184 |  | 8.4506 | 3.5001 | 1.1751 | 3.2343 | -1.6828 | 12.5778 | 5.5935 | 0.6331 | 0.6744 | 0.9803 | 0.7685 | -128.7981 | 4.8373 | 6.46 | 1.9087 | -2.3869 | -0.8914 | 4.9514 |  | 4.9365 | 0.8917 | 3.9871 | 3.366 | 3.3314 | 1.1078 | 0.6075 | 22.7343 | 22.5926 | 22.3831 | 22.3544 | 22.2657 | 22.2665 | 22.1402 | 22.9215 | 22.6414 | 22.6759 | 22.6757 | 22.8801 | 23.0153 | 22.9396 | 22.8896 | 22.7863 | 22.6868 | 22.6062 | 22.5027 | 22.3795 | 22.325 | 22.2605 | 22.9255 | 22.5545 | 22.5903 | 22.5743 | 22.6347 | 23.1631 | 22.6869 | 22.9402 | 23.0385 | 23.046 | 23.4908 | 22.865 | 22.9094 | 22.8748 | 22.814 | 22.6742 | 22.5936 | 22.4244 | 22.2573 | 23.2669 | 22.6526 | 22.7659 | 22.9659 | 23.3545 | 23.314 | 23.2623 | 23.2698 | 23.2125 | 23.3476 | 23.054 | 23.0635 | 23.118 | 23.0784 | 22.9967 | 22.9175 | 22.8008 | 22.7127 | 22.8317 | 22.8432 | 23.1276 | 23.1626 | 23.145 | 23.0583 | 23.17 | 23.8188 | 23.7235 | 23.737 | 23.6697 | 23.7469 | 23.2987 | 23.3728 | 23.3897 | 23.3475 | 23.3628 | 23.3953 | 23.2757 | 22.9752 | 22.7803 | 23.3062 | 23.3631 | 23.3316 | 23.2974 | 23.3285 | 30.5647 | 52.5889 | 23.7611 | 25.5056 | 23.714 | 24.1054 | 25.3056 | 30.155 | 27.2938 | 29.785 | 32.5325 | 32.6371 | 29.3425 | 40.3211 | 41.9328 | 30.8244 | 34.8521 | 28.7813 | 22.3401 | 22.2621 | 22.5655 | 22.1624 | 22.637 | 22.5201 | 25.6288 | 22.3024 | 22.2795 | 22.2111 | 22.1788 | 22.1002 | 22.1835 | 23.1916 | 22.5196 | 22.4376 | 22.8061 | 22.4621 | 22.7058 | 22.9958 | 22.908 | 22.8384 | 22.7377 | 22.6589 | 22.625 | 22.5856 | 22.5443 | 23.6418 | 22.7252 | 22.7206 | 23.7456 | 22.8701 | 23.7693 | 22.8765 | 23.0445 | 23.1554 | 23.8719 | 22.9281 | 22.9662 | 22.9377 | 22.8997 | 22.7709 | 22.667 | 22.5988 | 22.5159 | 23.6212 | 22.6046 | 22.7125 | 22.9455 | 23.4787 | 23.8465 | 23.7982 | 23.718 | 23.6478 | 23.7037 | 23.776 | 23.7359 | 23.6531 | 23.582 | 23.4496 | 23.3291 | 23.0269 | 22.8826 | 22.8579 | 22.899 | 23.6919 | 23.6024 | 23.5528 | 23.4977 | 23.7122 | 24.1391 | 24.0457 | 23.9208 | 23.8448 | 24.5296 | 23.6173 | 23.8347 | 23.7721 | 23.6963 | 23.6332 | 23.5962 | 23.6218 | 23.0596 | 22.9676 | 24.1045 | 24.0186 | 24.0091 | 23.9649 | 24.0019 | 26.1765 | 30.3094 | 29.7497 | 27.9406 | 25.6711 | 26.7985 | 27.4349 | 28.5874 | 31.682 | 28.9366 |  | 25.9555 | 23.4326 | 26.8394 | 24.6925 | 23.4225 | 23.4543 | 23.3727 | 22.734 | 21.6644 | 22.3003 | 10.8108 | 14.2723 | 14.881 | 11.1029 | 0.00053653 | -0.0030202 | 0.0014319 | 0.0046708 | 0.0015722 | 4.4772e-05 | 0.00043522 | 0.0017313 | -0.033227 | -360.2142 | 17.4397 | -360.445 | 17.6328 | -360.7497 | 18.1194 | -360.7681 | 17.5978 | -352.6136 | 18.7189 | -352.6167 | 16.7766 | -0.49247 | 360.7443 | 25.4939 | 14.5766 | 12.6776 | 22.1992
13:27 | 49 | 35.5845 |  | 8.5057 | 3.4376 | 1.0974 | 3.2489 | -1.7059 | 12.5572 | 5.5631 | 0.6331 | 0.6774 | 0.9789 | 0.7679 | -128.8115 | 4.7646 | 6.4027 | 1.9346 | -2.404 | -0.8635 | 4.9801 |  | 4.9368 | 0.8561 | 3.987 | 3.3662 | 3.3284 | 1.1066 | 1.0424 | 22.7329 | 22.594 | 22.3821 | 22.3563 | 22.2654 | 22.2671 | 22.1406 | 22.9239 | 22.6475 | 22.6779 | 22.6759 | 22.897 | 23.0165 | 22.941 | 22.8895 | 22.7855 | 22.6814 | 22.605 | 22.5006 | 22.3818 | 22.3246 | 22.2586 | 22.9229 | 22.551 | 22.5901 | 22.5686 | 22.6458 | 23.1652 | 22.6945 | 22.9396 | 23.0396 | 23.0484 | 23.4895 | 22.8679 | 22.9056 | 22.8702 | 22.8086 | 22.6786 | 22.5948 | 22.4246 | 22.256 | 23.2641 | 22.6564 | 22.7595 | 22.9665 | 23.3587 | 23.3153 | 23.2641 | 23.2693 | 23.2201 | 23.3648 | 23.0595 | 23.067 | 23.1188 | 23.0804 | 23.0026 | 22.9265 | 22.8052 | 22.7136 | 22.8498 | 22.8519 | 23.119 | 23.1612 | 23.1406 | 23.0559 | 23.1773 | 23.8172 | 23.7197 | 23.7381 | 23.6667 | 23.7523 | 23.298 | 23.3711 | 23.386 | 23.3459 | 23.3586 | 23.3925 | 23.2764 | 22.9768 | 22.7777 | 23.3108 | 23.3648 | 23.3341 | 23.3023 | 23.339 | 30.5911 | 52.7393 | 23.7513 | 25.6417 | 23.8316 | 24.281 | 25.4285 | 30.5732 | 27.5639 | 30.1504 | 35.7206 | 33.1788 | 29.0834 | 43.1073 | 42.2213 | 31.2465 | 37.0606 | 32.2206 | 22.4064 | 22.3063 | 22.6534 | 22.2276 | 22.6489 | 22.5216 | 25.6779 | 22.3059 | 22.289 | 22.2079 | 22.1739 | 22.1045 | 22.1846 | 23.1927 | 22.52 | 22.4435 | 22.8145 | 22.4635 | 22.7071 | 22.9941 | 22.9015 | 22.8335 | 22.7335 | 22.654 | 22.6212 | 22.5856 | 22.5427 | 23.6406 | 22.7222 | 22.7168 | 23.746 | 22.8781 | 23.7662 | 22.8713 | 23.0421 | 23.1579 | 23.8697 | 22.9231 | 22.9634 | 22.9439 | 22.9034 | 22.7748 | 22.6681 | 22.5949 | 22.5173 | 23.6162 | 22.6004 | 22.7124 | 22.9396 | 23.4889 | 23.8534 | 23.7984 | 23.713 | 23.6435 | 23.7023 | 23.7754 | 23.7305 | 23.6494 | 23.5762 | 23.4462 | 23.3203 | 23.0292 | 22.8742 | 22.8604 | 22.8991 | 23.6842 | 23.5925 | 23.547 | 23.4915 | 23.7121 | 24.131 | 24.043 | 23.9121 | 23.8382 | 24.5696 | 23.6127 | 23.826 | 23.7676 | 23.6836 | 23.6296 | 23.5873 | 23.6218 | 23.0583 | 22.9674 | 24.1006 | 24.0176 | 24.0066 | 23.9561 | 24.0067 | 26.2325 | 30.4268 | 29.7288 | 28.1426 | 25.7949 | 27.1292 | 27.5867 | 28.7544 | 31.9945 | 29.1251 |  | 26.283 | 23.5984 | 26.9684 | 24.6915 | 23.425 | 23.4565 | 23.396 | 22.7511 | 21.6666 | 22.311 | 10.8158 | 14.27 | 14.8913 | 11.0944 | 0.00051461 | -0.0032722 | 0.0019015 | 0.0046964 | 0.0010164 | -0.0002605 | 0.014697 | -0.020284 | -0.029016 | -360.0911 | 17.3782 | -360.4081 | 17.6718 | -360.8235 | 18.1748 | -360.8204 | 17.5691 | -352.549 | 18.6758 | -352.6106 | 16.8258 | 15.243 | 365.2452 | 25.6841 | 14.5806 | 12.6432 | 22.2089
13:27 | 50 | 35.4847 |  | 8.5003 | 3.462 | 1.0615 | 3.2558 | -1.5167 | 12.5823 | 5.5938 | 0.6334 | 0.6758 | 0.9816 | 0.7671 | -128.8824 | 4.78 | 6.4362 | 1.8522 | -2.4113 | -0.8841 | 5.0083 |  | 4.9818 | 0.9507 | 3.9889 | 3.3645 | 3.3296 | 1.0968 | 1.3928 | 22.735 | 22.5942 | 22.3801 | 22.3529 | 22.2673 | 22.268 | 22.1409 | 22.9245 | 22.642 | 22.6836 | 22.6743 | 22.9138 | 23.0163 | 22.9384 | 22.8858 | 22.7803 | 22.6752 | 22.6019 | 22.5004 | 22.3731 | 22.3239 | 22.2548 | 22.9196 | 22.5458 | 22.5805 | 22.5642 | 22.6475 | 23.1625 | 22.6851 | 22.9399 | 23.0323 | 23.0445 | 23.4847 | 22.8608 | 22.8954 | 22.8606 | 22.8012 | 22.6743 | 22.5904 | 22.4135 | 22.2533 | 23.259 | 22.6507 | 22.7581 | 22.9656 | 23.3602 | 23.3098 | 23.2578 | 23.2595 | 23.2125 | 23.3682 | 23.0554 | 23.0671 | 23.1108 | 23.0732 | 22.9957 | 22.9261 | 22.8009 | 22.7151 | 22.8634 | 22.8496 | 23.1172 | 23.1624 | 23.1378 | 23.0595 | 23.1883 | 23.8145 | 23.7176 | 23.7362 | 23.6675 | 23.7601 | 23.2982 | 23.3708 | 23.3863 | 23.3485 | 23.3568 | 23.3857 | 23.2781 | 22.9731 | 22.7772 | 23.3084 | 23.3626 | 23.3341 | 23.2982 | 23.3456 | 30.6409 | 53.296 | 23.7542 | 25.7319 | 23.962 | 24.4653 | 25.5433 | 30.9661 | 27.8274 | 30.5371 | 41.9867 | 35.9843 | 30.0601 | 46.7424 | 43.5099 | 32.5755 | 39.2717 | 37.2145 | 22.4855 | 22.3665 | 22.747 | 22.2932 | 22.6437 | 22.5245 | 25.7201 | 22.313 | 22.2925 | 22.2093 | 22.1819 | 22.1088 | 22.1853 | 23.1915 | 22.5195 | 22.443 | 22.8326 | 22.4727 | 22.7142 | 22.9933 | 22.9035 | 22.8347 | 22.7375 | 22.6537 | 22.6243 | 22.5896 | 22.5477 | 23.6392 | 22.722 | 22.7154 | 23.7445 | 22.8815 | 23.7694 | 22.8708 | 23.0469 | 23.163 | 23.8705 | 22.9198 | 22.9615 | 22.9443 | 22.9019 | 22.7777 | 22.6715 | 22.5964 | 22.5209 | 23.6176 | 22.5971 | 22.7123 | 22.9437 | 23.5018 | 23.8618 | 23.7972 | 23.7143 | 23.6483 | 23.714 | 23.7566 | 23.7312 | 23.6509 | 23.5777 | 23.4494 | 23.3086 | 23.0445 | 22.8632 | 22.8746 | 22.8988 | 23.6838 | 23.5929 | 23.5448 | 23.4935 | 23.7229 | 24.1302 | 24.0418 | 23.9164 | 23.8405 | 24.6207 | 23.6184 | 23.8282 | 23.7669 | 23.6838 | 23.6241 | 23.5866 | 23.6227 | 23.0658 | 22.9653 | 24.104 | 24.0224 | 24.0097 | 23.9584 | 24.0213 | 26.3099 | 30.4649 | 29.9576 | 28.361 | 25.9466 | 27.477 | 27.7422 | 28.9083 | 32.2931 | 29.3621 |  | 26.5997 | 23.7668 | 27.1138 | 24.6873 | 23.4271 | 23.451 | 23.4248 | 22.7647 | 21.665 | 22.3172 | 10.827 | 14.2815 | 14.8905 | 11.126 | 0.00059947 | -0.0024418 | 0.001893 | 0.0044513 | 0.0016572 | -0.00043241 | 0.012155 | -0.0043985 | -0.018923 | -360.2727 | 17.4603 | -360.4727 | 17.6574 | -360.8112 | 18.1563 | -360.7866 | 17.6122 | -352.6506 | 18.7312 | -352.6598 | 16.8094 | 8.6594 | 359.454 | 25.8842 | 14.586 | 12.731 | 22.2148
13:27 | 51 | 35.5185 |  | 8.4827 | 3.4513 | 1.0441 | 3.2319 | -1.607 | 12.5964 | 5.4663 | 0.6335 | 0.6743 | 0.9776 | 0.7683 | -128.9525 | 4.7849 | 6.4048 | 1.9116 | -2.4112 | -0.9188 | 5.0395 |  | 4.9097 | 0.8946 | 3.9872 | 3.3632 | 3.3291 | 1.0975 | 0.7389 | 22.738 | 22.5938 | 22.3778 | 22.353 | 22.2649 | 22.268 | 22.1428 | 22.9229 | 22.6412 | 22.6837 | 22.6748 | 22.9292 | 23.0182 | 22.9394 | 22.8843 | 22.7795 | 22.6716 | 22.5988 | 22.4998 | 22.3661 | 22.3312 | 22.2515 | 22.9218 | 22.5446 | 22.5792 | 22.5628 | 22.6477 | 23.1579 | 22.6797 | 22.9366 | 23.0262 | 23.0433 | 23.4781 | 22.8562 | 22.886 | 22.8574 | 22.7956 | 22.6684 | 22.5882 | 22.4094 | 22.2527 | 23.2601 | 22.6436 | 22.7535 | 22.9615 | 23.3622 | 23.3041 | 23.2536 | 23.2561 | 23.2048 | 23.3777 | 23.0489 | 23.0598 | 23.1056 | 23.0686 | 22.9921 | 22.9204 | 22.798 | 22.713 | 22.8649 | 22.8413 | 23.1191 | 23.1544 | 23.1399 | 23.0583 | 23.1998 | 23.8172 | 23.7197 | 23.7306 | 23.6719 | 23.7742 | 23.2991 | 23.3732 | 23.3902 | 23.3515 | 23.3575 | 23.385 | 23.2831 | 22.966 | 22.7735 | 23.302 | 23.3561 | 23.3266 | 23.2945 | 23.3426 | 30.9202 | 53.3546 | 23.781 | 25.792 | 24.093 | 24.6375 | 25.6574 | 31.3263 | 28.0675 | 30.9269 | 46.9799 | 38.9128 | 31.9126 | 50.0739 | 46.7188 | 34.8168 | 40.2757 | 40.9904 | 22.5651 | 22.4346 | 22.8361 | 22.3622 | 22.6338 | 22.5185 | 25.8031 | 22.3065 | 22.2819 | 22.1979 | 22.1799 | 22.1041 | 22.1799 | 23.1881 | 22.5152 | 22.4363 | 22.8423 | 22.4667 | 22.7065 | 22.9956 | 22.9027 | 22.8392 | 22.743 | 22.6531 | 22.6242 | 22.5973 | 22.5516 | 23.634 | 22.7288 | 22.7167 | 23.7472 | 22.892 | 23.7742 | 22.8739 | 23.0494 | 23.1701 | 23.8699 | 22.9281 | 22.9668 | 22.9388 | 22.8952 | 22.7808 | 22.6714 | 22.5997 | 22.5265 | 23.6201 | 22.5955 | 22.7135 | 22.9444 | 23.5092 | 23.8596 | 23.7913 | 23.715 | 23.6519 | 23.7174 | 23.7461 | 23.7331 | 23.6466 | 23.5753 | 23.4477 | 23.3044 | 23.0404 | 22.8668 | 22.8662 | 22.9041 | 23.69 | 23.6029 | 23.5472 | 23.5001 | 23.7432 | 24.1373 | 24.0458 | 23.9265 | 23.8434 | 24.6795 | 23.6176 | 23.8399 | 23.7664 | 23.6901 | 23.6291 | 23.5941 | 23.6238 | 23.0617 | 22.9595 | 24.1039 | 24.0171 | 24.0091 | 23.9604 | 24.0328 | 26.4091 | 30.5043 | 30.5506 | 28.5839 | 26.111 | 27.8165 | 27.8899 | 29.0421 | 32.5709 | 29.6018 |  | 26.9039 | 23.9296 | 27.268 | 24.6779 | 23.42 | 23.4498 | 23.438 | 22.7754 | 21.6607 | 22.3161 | 10.8223 | 14.2336 | 14.8879 | 11.1157 | -0.00011386 | -0.0026713 | 0.0011105 | 0.0039509 | 0.00077254 | -0.00056196 | 0.031775 | -0.0089508 | -0.0077565 | -360.0788 | 17.3864 | -360.4419 | 17.6697 | -360.8574 | 18.1871 | -360.8266 | 17.565 | -352.5059 | 18.6614 | -352.6075 | 16.8279 | 6.6316 | 366.2715 | 26.0812 | 14.5607 | 12.6273 | 22.2181
13:27 | 52 | 35.4202 |  | 8.4396 | 3.5273 | 1.0045 | 3.2838 | -1.517 | 12.5675 | 5.601 | 0.6338 | 0.6744 | 0.9804 | 0.7675 | -128.9948 | 4.7608 | 6.4536 | 1.7425 | -2.44 | -0.9759 | 5.0093 |  | 4.9857 | 0.9376 | 3.9869 | 3.3637 | 3.3238 | 1.0967 | 2.1413 | 22.7408 | 22.5964 | 22.3782 | 22.356 | 22.265 | 22.2733 | 22.1488 | 22.9217 | 22.6442 | 22.6833 | 22.6767 | 22.9514 | 23.0224 | 22.9441 | 22.8851 | 22.7773 | 22.6733 | 22.5989 | 22.5059 | 22.3714 | 22.336 | 22.2553 | 22.9261 | 22.5445 | 22.5796 | 22.5658 | 22.6532 | 23.1615 | 22.6838 | 22.9347 | 23.0307 | 23.0627 | 23.4832 | 22.8571 | 22.891 | 22.867 | 22.801 | 22.6749 | 22.598 | 22.422 | 22.2538 | 23.264 | 22.6524 | 22.7588 | 22.9676 | 23.3752 | 23.3052 | 23.2582 | 23.2595 | 23.2059 | 23.3964 | 23.0583 | 23.0614 | 23.1063 | 23.0748 | 22.9948 | 22.9277 | 22.799 | 22.7118 | 22.8721 | 22.8444 | 23.1241 | 23.1533 | 23.1434 | 23.0588 | 23.2166 | 23.8224 | 23.7226 | 23.7317 | 23.6683 | 23.7896 | 23.3006 | 23.3747 | 23.3948 | 23.3512 | 23.363 | 23.3941 | 23.2854 | 22.9736 | 22.7778 | 23.302 | 23.3554 | 23.3288 | 23.2954 | 23.3482 | 31.5149 | 53.3957 | 23.8188 | 25.877 | 24.2187 | 24.8024 | 25.7778 | 31.6717 | 28.3068 | 31.3258 | 50.4329 | 42.0444 | 34.089 | 52.3826 | 49.8199 | 37.0965 | 40.6842 | 44.8329 | 22.6404 | 22.4964 | 22.9161 | 22.428 | 22.6321 | 22.5111 | 25.893 | 22.3001 | 22.2741 | 22.1958 | 22.1694 | 22.0989 | 22.174 | 23.183 | 22.5133 | 22.4321 | 22.8449 | 22.4529 | 22.7028 | 22.9957 | 22.904 | 22.8372 | 22.7497 | 22.6504 | 22.6173 | 22.5951 | 22.5543 | 23.6381 | 22.7263 | 22.7228 | 23.7496 | 22.9055 | 23.7739 | 22.8734 | 23.0519 | 23.1762 | 23.8742 | 22.9334 | 22.971 | 22.9408 | 22.9002 | 22.785 | 22.6752 | 22.6017 | 22.5272 | 23.6225 | 22.6025 | 22.7189 | 22.9434 | 23.5151 | 23.8587 | 23.7931 | 23.7158 | 23.6528 | 23.723 | 23.7704 | 23.7365 | 23.6454 | 23.5698 | 23.4479 | 23.3093 | 23.0342 | 22.872 | 22.8551 | 22.9053 | 23.6871 | 23.6065 | 23.5499 | 23.503 | 23.7548 | 24.1353 | 24.0452 | 23.9336 | 23.8457 | 24.7422 | 23.6141 | 23.84 | 23.7701 | 23.69 | 23.6338 | 23.5982 | 23.6261 | 23.0566 | 22.9604 | 24.1023 | 24.0174 | 24.0054 | 23.9583 | 24.0397 | 26.5235 | 30.5933 | 31.1153 | 28.8228 | 26.2823 | 28.1332 | 28.0421 | 29.1651 | 32.8304 | 29.8059 |  | 27.2262 | 24.1081 | 27.4376 | 24.6945 | 23.4236 | 23.454 | 23.4655 | 22.7841 | 21.6743 | 22.3269 | 10.8319 | 14.2582 | 14.9163 | 11.1381 | 0.00065409 | -0.0026445 | 0.0016428 | 0.0041298 | 0.0017829 | -0.00082455 | 0.020756 | -0.0047173 | -0.040483 | -360.1988 | 17.4233 | -360.4112 | 17.6245 | -360.7312 | 18.1399 | -360.8081 | 17.5917 | -352.6352 | 18.7087 | -352.5952 | 16.793 | 3.76 | 357.9644 | 26.2813 | 14.5872 | 12.6498 | 22.2292
13:27 | 53 | 35.5696 |  | 8.4243 | 3.4263 | 0.931 | 3.2798 | -1.5661 | 12.5822 | 5.6394 | 0.6355 | 0.6717 | 0.9801 | 0.7658 | -128.9782 | 4.7743 | 6.5419 | 1.7516 | -2.4663 | -0.8787 | 5.0507 |  | 4.9592 | 0.8083 | 3.9862 | 3.365 | 3.3286 | 1.0966 | 1.001 | 22.7356 | 22.5952 | 22.377 | 22.3521 | 22.2625 | 22.2727 | 22.1472 | 22.92 | 22.6375 | 22.6828 | 22.6755 | 22.9642 | 23.0186 | 22.9413 | 22.8856 | 22.7801 | 22.6785 | 22.6039 | 22.51 | 22.3774 | 22.3395 | 22.2606 | 22.9304 | 22.5573 | 22.5836 | 22.574 | 22.6645 | 23.1649 | 22.6911 | 22.9384 | 23.0374 | 23.0761 | 23.4893 | 22.8641 | 22.9046 | 22.8706 | 22.812 | 22.6814 | 22.6073 | 22.4243 | 22.2539 | 23.2661 | 22.6552 | 22.7628 | 22.9655 | 23.3827 | 23.3089 | 23.2598 | 23.2609 | 23.2062 | 23.4078 | 23.0611 | 23.0665 | 23.1097 | 23.077 | 22.9954 | 22.9246 | 22.8024 | 22.7144 | 22.8684 | 22.8462 | 23.1214 | 23.1547 | 23.1362 | 23.0547 | 23.227 | 23.8178 | 23.7157 | 23.7297 | 23.6612 | 23.7982 | 23.2948 | 23.372 | 23.3912 | 23.3519 | 23.361 | 23.3934 | 23.2879 | 22.975 | 22.7787 | 23.3053 | 23.3561 | 23.3291 | 23.2964 | 23.3589 | 31.8353 | 53.5105 | 23.8609 | 25.9732 | 24.3432 | 24.9542 | 25.8939 | 32.027 | 28.5557 | 31.7405 | 53.427 | 44.8016 | 36.9457 | 53.9867 | 51.9634 | 39.0458 | 41.894 | 48.6227 | 22.7129 | 22.5591 | 22.9963 | 22.4926 | 22.6426 | 22.5177 | 25.9409 | 22.3084 | 22.2796 | 22.2058 | 22.1708 | 22.0996 | 22.1785 | 23.1876 | 22.5183 | 22.4386 | 22.8642 | 22.454 | 22.7065 | 22.9963 | 22.8998 | 22.834 | 22.7498 | 22.6543 | 22.6189 | 22.5906 | 22.5528 | 23.643 | 22.7202 | 22.7286 | 23.7475 | 22.9079 | 23.7719 | 22.8741 | 23.0534 | 23.177 | 23.8737 | 22.9253 | 22.968 | 22.9398 | 22.8997 | 22.7803 | 22.6727 | 22.5993 | 22.523 | 23.6217 | 22.6038 | 22.7137 | 22.9395 | 23.5276 | 23.8638 | 23.7982 | 23.7159 | 23.6545 | 23.7291 | 23.7862 | 23.7392 | 23.654 | 23.5763 | 23.4519 | 23.3126 | 23.0354 | 22.868 | 22.8624 | 22.9031 | 23.6841 | 23.6042 | 23.5487 | 23.4969 | 23.7622 | 24.131 | 24.0441 | 23.9308 | 23.8438 | 24.8106 | 23.6122 | 23.8343 | 23.771 | 23.6922 | 23.626 | 23.5975 | 23.6286 | 23.0588 | 22.9671 | 24.108 | 24.0181 | 24.0085 | 23.9577 | 24.053 | 26.6596 | 30.6295 | 31.94 | 29.1119 | 26.4603 | 28.4322 | 28.2005 | 29.2937 | 33.093 | 29.9933 |  | 27.5285 | 24.3003 | 27.6122 | 24.6883 | 23.4425 | 23.4624 | 23.4951 | 22.8179 | 21.6893 | 22.3393 | 10.8179 | 14.2651 | 14.8656 | 11.0822 | 0.00022488 | -0.0031165 | 0.0018003 | 0.0042888 | 0.0012653 | -9.3415e-06 | 0.013681 | 0.009122 | -0.023496 | -360.1219 | 17.4048 | -360.4419 | 17.6861 | -360.882 | 18.1974 | -360.8604 | 17.5937 | -352.586 | 18.6902 | -352.629 | 16.8299 | -1.103 | 367.5958 | 26.4789 | 14.5653 | 12.5825 | 22.2536
13:27 | 54 | 35.6358 |  | 8.4469 | 3.5765 | 1.0639 | 3.3115 | -1.5573 | 12.6469 | 5.6727 | 0.6342 | 0.6757 | 0.9791 | 0.7671 | -129.0395 | 4.7837 | 6.4518 | 1.8019 | -2.3382 | -0.8873 | 5.0701 |  | 4.9733 | 0.9578 | 3.9866 | 3.365 | 3.3269 | 1.0964 | 1.14 | 22.7373 | 22.5952 | 22.3825 | 22.3536 | 22.2654 | 22.2794 | 22.1479 | 22.9235 | 22.6414 | 22.6852 | 22.682 | 22.9789 | 23.0198 | 22.9445 | 22.8894 | 22.7838 | 22.6795 | 22.6046 | 22.5067 | 22.3816 | 22.3469 | 22.263 | 22.9314 | 22.5656 | 22.5845 | 22.5766 | 22.678 | 23.1651 | 22.6958 | 22.9453 | 23.0412 | 23.0829 | 23.4946 | 22.8707 | 22.9112 | 22.8712 | 22.8152 | 22.683 | 22.6092 | 22.4267 | 22.261 | 23.2685 | 22.6572 | 22.7604 | 22.9641 | 23.3806 | 23.3038 | 23.257 | 23.2613 | 23.2054 | 23.4218 | 23.0538 | 23.0651 | 23.1077 | 23.0718 | 22.9929 | 22.9181 | 22.8081 | 22.7143 | 22.8693 | 22.8506 | 23.123 | 23.1551 | 23.1359 | 23.0546 | 23.2346 | 23.814 | 23.711 | 23.7303 | 23.6653 | 23.8088 | 23.3006 | 23.3709 | 23.3876 | 23.355 | 23.3608 | 23.3911 | 23.2911 | 22.9696 | 22.779 | 23.308 | 23.3588 | 23.3296 | 23.2991 | 23.3657 | 32.3465 | 53.6366 | 23.9098 | 26.047 | 24.4708 | 25.1143 | 26.0024 | 32.3937 | 28.8037 | 32.1545 | 55.8446 | 46.595 | 40.1693 | 54.946 | 52.6224 | 41.6632 | 44.4681 | 51.1579 | 22.7789 | 22.6145 | 23.0725 | 22.5473 | 22.6399 | 22.5172 | 26.0223 | 22.3044 | 22.2788 | 22.2016 | 22.1689 | 22.0964 | 22.1792 | 23.1871 | 22.5168 | 22.4393 | 22.881 | 22.4539 | 22.7041 | 22.9979 | 22.8972 | 22.8389 | 22.7479 | 22.6641 | 22.6216 | 22.595 | 22.5545 | 23.6443 | 22.7222 | 22.7312 | 23.7505 | 22.9127 | 23.7707 | 22.8766 | 23.0525 | 23.1832 | 23.877 | 22.9249 | 22.969 | 22.9405 | 22.8979 | 22.7837 | 22.6692 | 22.5996 | 22.5332 | 23.6106 | 22.6008 | 22.706 | 22.9373 | 23.5358 | 23.8589 | 23.7993 | 23.7086 | 23.6543 | 23.7251 | 23.7752 | 23.7309 | 23.6482 | 23.5727 | 23.4467 | 23.3043 | 23.0396 | 22.8672 | 22.8687 | 22.8968 | 23.6775 | 23.6013 | 23.5465 | 23.4927 | 23.7708 | 24.129 | 24.0391 | 23.9214 | 23.8376 | 24.8774 | 23.6072 | 23.834 | 23.768 | 23.6863 | 23.6222 | 23.5941 | 23.6302 | 23.0649 | 22.9701 | 24.1098 | 24.0168 | 24.0139 | 23.958 | 24.0646 | 26.8272 | 30.6358 | 32.7929 | 29.4138 | 26.6494 | 28.7129 | 28.3723 | 29.4273 | 33.3619 | 30.1853 |  | 27.8217 | 24.4717 | 27.7938 | 24.6795 | 23.4243 | 23.4571 | 23.5199 | 22.8372 | 21.6919 | 22.3422 | 10.8158 | 14.27 | 14.8983 | 11.1155 | 0.00018547 | -0.0023798 | 0.0014799 | 0.0046258 | 0.00096962 | -0.00091829 | 0.029721 | -0.01183 | -0.021618 | -360.1927 | 17.4377 | -360.4389 | 17.6348 | -360.7712 | 18.1543 | -360.802 | 17.5978 | -352.6229 | 18.7066 | -352.626 | 16.793 | -0.20292 | 358.5748 | 26.6759 | 14.5841 | 12.8216 | 22.2645
13:27 | 55 | 35.5493 |  | 8.4402 | 3.4477 | 1.0807 | 3.2863 | -1.6275 | 12.6105 | 5.6118 | 0.6326 | 0.6722 | 0.9807 | 0.7674 | -128.9536 | 4.7406 | 6.4105 | 1.8247 | -2.3179 | -0.7631 | 5.0587 |  | 4.9413 | 0.916 | 3.9866 | 3.3653 | 3.3261 | 1.0966 | 0.6968 | 22.7432 | 22.5963 | 22.3867 | 22.3633 | 22.2714 | 22.2843 | 22.1479 | 22.9306 | 22.6449 | 22.6873 | 22.6868 | 23.0031 | 23.0244 | 22.9522 | 22.8902 | 22.7751 | 22.6769 | 22.6024 | 22.5095 | 22.3842 | 22.3479 | 22.2648 | 22.9258 | 22.5615 | 22.5853 | 22.5709 | 22.6821 | 23.1643 | 22.696 | 22.9463 | 23.0424 | 23.0873 | 23.4985 | 22.8689 | 22.9108 | 22.8706 | 22.8141 | 22.6786 | 22.6093 | 22.4315 | 22.2649 | 23.2664 | 22.6563 | 22.755 | 22.9683 | 23.3967 | 23.3056 | 23.262 | 23.2656 | 23.2124 | 23.4438 | 23.0505 | 23.0699 | 23.1136 | 23.0733 | 22.9965 | 22.9287 | 22.8165 | 22.7163 | 22.8772 | 22.8528 | 23.1296 | 23.1588 | 23.1463 | 23.0607 | 23.25 | 23.8135 | 23.7204 | 23.7363 | 23.6715 | 23.8285 | 23.3101 | 23.3679 | 23.3923 | 23.3546 | 23.3703 | 23.3991 | 23.2909 | 22.9737 | 22.7767 | 23.3044 | 23.3606 | 23.3281 | 23.2939 | 23.3724 | 32.5802 | 53.8233 | 23.9476 | 26.1331 | 24.6006 | 25.2847 | 26.1218 | 32.7544 | 29.054 | 32.5475 | 56.674 | 48.0165 | 43.4829 | 55.5562 | 52.866 | 44.8762 | 47.0359 | 53.2049 | 22.8398 | 22.6603 | 23.1469 | 22.5974 | 22.635 | 22.518 | 26.0872 | 22.299 | 22.2742 | 22.1964 | 22.1695 | 22.0955 | 22.179 | 23.1837 | 22.5155 | 22.435 | 22.8865 | 22.4555 | 22.7061 | 22.9972 | 22.8957 | 22.8359 | 22.7376 | 22.6604 | 22.6193 | 22.5873 | 22.557 | 23.6431 | 22.7205 | 22.7221 | 23.7428 | 22.9194 | 23.766 | 22.8728 | 23.0491 | 23.1929 | 23.8758 | 22.9302 | 22.9714 | 22.9445 | 22.9006 | 22.7865 | 22.6762 | 22.6015 | 22.5351 | 23.6134 | 22.5954 | 22.7055 | 22.9408 | 23.5471 | 23.8617 | 23.8007 | 23.714 | 23.6571 | 23.7364 | 23.7646 | 23.7372 | 23.6471 | 23.5728 | 23.4495 | 23.3116 | 23.0444 | 22.8789 | 22.8783 | 22.8984 | 23.6814 | 23.6026 | 23.5492 | 23.493 | 23.7812 | 24.1233 | 24.0384 | 23.9242 | 23.8379 | 24.9577 | 23.6038 | 23.8351 | 23.7679 | 23.6807 | 23.627 | 23.5933 | 23.6277 | 23.0696 | 22.9681 | 24.1142 | 24.0182 | 24.0118 | 23.9611 | 24.0754 | 26.979 | 30.8163 | 33.6439 | 29.6801 | 26.8557 | 28.9863 | 28.5642 | 29.5528 | 33.6236 | 30.3998 |  | 28.1079 | 24.6401 | 27.9797 | 24.6872 | 23.4195 | 23.4493 | 23.548 | 22.8421 | 21.6924 | 22.3407 | 10.853 | 14.2866 | 14.8823 | 11.1236 | -0.00013938 | -0.002736 | 0.0018835 | 0.0045353 | 0.0013639 | -0.00030056 | 0.0047904 | 0.010677 | -0.0072972 | -360.085 | 17.3699 | -360.3989 | 17.6451 | -360.7958 | 18.1728 | -360.8174 | 17.5691 | -352.5398 | 18.6532 | -352.5706 | 16.8074 | 5.8891 | 363.98 | 26.8774 | 14.5844 | 12.7528 | 22.2673
13:27 | 56 | 35.5227 |  | 8.3987 | 3.4493 | 1.0304 | 3.3702 | -1.6809 | 12.5357 | 5.5468 | 0.6349 | 0.6731 | 0.9771 | 0.7675 | -128.9726 | 4.7502 | 6.3699 | 1.783 | -2.3857 | -0.8882 | 5.0229 |  | 4.8965 | 0.8516 | 3.9869 | 3.3674 | 3.3278 | 1.0983 | 0.2273 | 22.7438 | 22.5953 | 22.3788 | 22.3612 | 22.2731 | 22.282 | 22.1448 | 22.9336 | 22.6433 | 22.6837 | 22.6801 | 23.0239 | 23.0227 | 22.95 | 22.8823 | 22.7714 | 22.671 | 22.603 | 22.5066 | 22.3801 | 22.3469 | 22.2671 | 22.9205 | 22.5526 | 22.5873 | 22.5657 | 22.6874 | 23.1666 | 22.6923 | 22.9361 | 23.0423 | 23.0934 | 23.4967 | 22.8655 | 22.9093 | 22.8745 | 22.8195 | 22.6791 | 22.6093 | 22.4278 | 22.2654 | 23.2638 | 22.6504 | 22.7497 | 22.9672 | 23.4188 | 23.3107 | 23.266 | 23.2694 | 23.2181 | 23.463 | 23.0522 | 23.0725 | 23.1186 | 23.0804 | 22.9993 | 22.9409 | 22.8225 | 22.7182 | 22.8758 | 22.8539 | 23.1233 | 23.1596 | 23.1417 | 23.0615 | 23.2649 | 23.8131 | 23.719 | 23.7322 | 23.6701 | 23.8391 | 23.3082 | 23.3683 | 23.3876 | 23.345 | 23.3675 | 23.3945 | 23.2953 | 22.9828 | 22.7822 | 23.3059 | 23.3603 | 23.3284 | 23.2941 | 23.3791 | 32.4527 | 54.607 | 23.9877 | 26.2326 | 24.7392 | 25.4564 | 26.243 | 33.1204 | 29.309 | 32.9367 | 56.7108 | 49.3775 | 45.8043 | 56.2636 | 53.6684 | 47.3265 | 48.216 | 55.1683 | 22.9016 | 22.7081 | 23.222 | 22.6611 | 22.6395 | 22.5236 | 26.1511 | 22.3043 | 22.2765 | 22.2025 | 22.172 | 22.0981 | 22.1781 | 23.1826 | 22.52 | 22.4335 | 22.8964 | 22.4634 | 22.701 | 22.9944 | 22.8967 | 22.835 | 22.7409 | 22.6549 | 22.6197 | 22.5831 | 22.5528 | 23.6394 | 22.7208 | 22.714 | 23.7372 | 22.9256 | 23.7675 | 22.8743 | 23.0545 | 23.1994 | 23.8749 | 22.9359 | 22.9708 | 22.9446 | 22.905 | 22.7869 | 22.6819 | 22.6061 | 22.5353 | 23.6246 | 22.5976 | 22.7104 | 22.939 | 23.5662 | 23.8643 | 23.8015 | 23.7193 | 23.6581 | 23.7498 | 23.7654 | 23.7461 | 23.6521 | 23.5838 | 23.4568 | 23.3262 | 23.0422 | 22.8847 | 22.891 | 22.91 | 23.6884 | 23.6027 | 23.5569 | 23.4939 | 23.7926 | 24.1223 | 24.0453 | 23.9286 | 23.8395 | 25.0457 | 23.6064 | 23.8333 | 23.7741 | 23.6829 | 23.6313 | 23.5994 | 23.6207 | 23.0631 | 22.9613 | 24.1136 | 24.0133 | 24.0055 | 23.9564 | 24.0826 | 27.0786 | 31.3287 | 34.268 | 29.9076 | 27.067 | 29.2593 | 28.7933 | 29.6824 | 33.8673 | 30.6431 |  | 28.4054 | 24.8077 | 28.1809 | 24.6876 | 23.4207 | 23.4472 | 23.5729 | 22.859 | 21.6987 | 22.3457 | 10.8102 | 14.236 | 14.8846 | 11.0961 | 0.00040166 | -0.0030064 | 0.001531 | 0.0041368 | 0.0013515 | -0.00032726 | 0.028105 | -0.0019343 | -0.027905 | -360.2235 | 17.4418 | -360.4481 | 17.6594 | -360.7989 | 18.1604 | -360.8389 | 17.6266 | -352.6352 | 18.7128 | -352.6506 | 16.8135 | 7.5337 | 363.174 | 27.0887 | 14.5603 | 12.5791 | 22.2788
13:27 | 57 | 35.536 |  | 8.449 | 3.4777 | 1.0107 | 3.3005 | -1.5841 | 12.684 | 5.6271 | 0.6343 | 0.6752 | 0.9813 | 0.7687 | -128.9153 | 4.7431 | 6.4853 | 1.729 | -2.3157 | -0.8452 | 5.041 |  | 4.785 | 0.7913 | 3.9876 | 3.367 | 3.3304 | 1.0971 | 1.6223 | 22.749 | 22.6009 | 22.3798 | 22.3541 | 22.2748 | 22.2841 | 22.151 | 22.934 | 22.6502 | 22.688 | 22.6807 | 23.0499 | 23.0219 | 22.9439 | 22.8857 | 22.7791 | 22.6715 | 22.6076 | 22.511 | 22.3807 | 22.3499 | 22.2684 | 22.9262 | 22.5533 | 22.5911 | 22.5644 | 22.6978 | 23.1728 | 22.6891 | 22.9359 | 23.0398 | 23.1045 | 23.4962 | 22.8664 | 22.905 | 22.8731 | 22.8187 | 22.6843 | 22.608 | 22.4239 | 22.2624 | 23.2705 | 22.6467 | 22.7507 | 22.962 | 23.4281 | 23.3086 | 23.2609 | 23.2646 | 23.2167 | 23.4728 | 23.0498 | 23.0671 | 23.1116 | 23.0741 | 22.9911 | 22.9342 | 22.8213 | 22.713 | 22.8684 | 22.8482 | 23.1318 | 23.1641 | 23.1435 | 23.0707 | 23.2849 | 23.8183 | 23.7216 | 23.7304 | 23.6741 | 23.8615 | 23.3107 | 23.3743 | 23.3902 | 23.3468 | 23.3668 | 23.3973 | 23.3003 | 22.9893 | 22.7919 | 23.3095 | 23.363 | 23.3374 | 23.3048 | 23.3913 | 32.8174 | 55.4892 | 24.0224 | 26.3082 | 24.8886 | 25.6309 | 26.3566 | 33.4813 | 29.5628 | 33.3207 | 56.8992 | 51.7861 | 46.7523 | 56.9039 | 54.9049 | 49.3546 | 48.5274 | 56.83 | 22.9641 | 22.7538 | 23.295 | 22.7247 | 22.649 | 22.5306 | 26.2298 | 22.3134 | 22.2864 | 22.2095 | 22.1735 | 22.0999 | 22.1776 | 23.1834 | 22.5239 | 22.4351 | 22.916 | 22.4632 | 22.6943 | 22.9903 | 22.8999 | 22.8386 | 22.7532 | 22.6618 | 22.6189 | 22.5903 | 22.5473 | 23.6344 | 22.7224 | 22.7138 | 23.7428 | 22.9338 | 23.7705 | 22.8739 | 23.0505 | 23.2069 | 23.8784 | 22.9286 | 22.9697 | 22.9393 | 22.9007 | 22.7867 | 22.6771 | 22.6096 | 22.542 | 23.6254 | 22.6012 | 22.7096 | 22.9386 | 23.5733 | 23.8533 | 23.8007 | 23.7128 | 23.6563 | 23.7523 | 23.7598 | 23.7447 | 23.6522 | 23.5805 | 23.4556 | 23.3243 | 23.0424 | 22.8819 | 22.8949 | 22.9117 | 23.6831 | 23.6034 | 23.5561 | 23.4933 | 23.7977 | 24.1306 | 24.0456 | 23.9265 | 23.8384 | 25.1251 | 23.6164 | 23.8293 | 23.7781 | 23.6878 | 23.6263 | 23.6036 | 23.6279 | 23.0572 | 22.9597 | 24.1091 | 24.0138 | 24.0068 | 23.9574 | 24.0924 | 27.1459 | 31.6755 | 34.6446 | 30.096 | 27.2834 | 29.5226 | 29.061 | 29.801 | 34.1039 | 30.8693 |  | 28.6929 | 24.9806 | 28.4144 | 24.6955 | 23.4298 | 23.4572 | 23.6075 | 22.8859 | 21.7118 | 22.3604 | 10.8193 | 14.2595 | 14.8884 | 11.1188 | 0.0009173 | -0.0025195 | 0.0016002 | 0.0043464 | 0.00092402 | -0.00098525 | 0.0021602 | 0.0015971 | -0.0092035 | -360.1373 | 17.4048 | -360.405 | 17.6492 | -360.8358 | 18.1707 | -360.8143 | 17.5855 | -352.5367 | 18.6676 | -352.5644 | 16.8032 | -1.7494 | 361.5928 | 27.3093 | 14.5739 | 12.6451 | 22.2989
13:27 | 58 | 35.5164 |  | 8.4362 | 3.4553 | 1.0376 | 3.3215 | -1.5675 | 12.6169 | 5.6579 | 0.6335 | 0.6736 | 0.9813 | 0.7697 | -129.0676 | 4.7002 | 6.3992 | 1.5826 | -2.3444 | -0.9147 | 4.989 |  | 4.8601 | 0.9745 | 3.9874 | 3.3674 | 3.3267 | 1.0979 | 1.5041 | 22.7495 | 22.6089 | 22.3877 | 22.3596 | 22.2771 | 22.2858 | 22.1561 | 22.9342 | 22.6437 | 22.6902 | 22.6824 | 23.0651 | 23.0237 | 22.9432 | 22.8936 | 22.7838 | 22.6815 | 22.6125 | 22.5167 | 22.3878 | 22.3506 | 22.2685 | 22.9307 | 22.5653 | 22.5948 | 22.5717 | 22.7026 | 23.1777 | 22.6966 | 22.9447 | 23.0367 | 23.1134 | 23.4992 | 22.8634 | 22.9084 | 22.8672 | 22.8144 | 22.6878 | 22.6141 | 22.4255 | 22.262 | 23.2731 | 22.6499 | 22.7571 | 22.9663 | 23.437 | 23.3104 | 23.2642 | 23.2667 | 23.2186 | 23.4878 | 23.0551 | 23.0724 | 23.1136 | 23.0704 | 22.992 | 22.93 | 22.8223 | 22.7179 | 22.8765 | 22.8449 | 23.1326 | 23.1634 | 23.1466 | 23.0677 | 23.2999 | 23.8179 | 23.7222 | 23.7297 | 23.6711 | 23.8786 | 23.3033 | 23.3709 | 23.393 | 23.3509 | 23.3679 | 23.3941 | 23.3076 | 22.9881 | 22.788 | 23.3061 | 23.3607 | 23.3384 | 23.3062 | 23.3959 | 33.3116 | 56.1484 | 24.0355 | 26.3638 | 25.0326 | 25.8067 | 26.4607 | 33.8415 | 29.816 | 33.676 | 58.1142 | 54.901 | 47.4646 | 57.5856 | 56.3664 | 50.8491 | 48.7212 | 58.4068 | 23.0292 | 22.7996 | 23.3638 | 22.7847 | 22.6579 | 22.5339 | 26.31 | 22.3193 | 22.2947 | 22.2097 | 22.1779 | 22.1098 | 22.1867 | 23.1923 | 22.5236 | 22.4407 | 22.9405 | 22.4586 | 22.6995 | 22.9892 | 22.8938 | 22.8349 | 22.7654 | 22.6638 | 22.6193 | 22.6011 | 22.5484 | 23.6339 | 22.7247 | 22.7208 | 23.7445 | 22.9446 | 23.7691 | 22.8725 | 23.0458 | 23.2118 | 23.8799 | 22.9208 | 22.9677 | 22.94 | 22.8943 | 22.7883 | 22.6721 | 22.6081 | 22.5386 | 23.6206 | 22.5993 | 22.705 | 22.9376 | 23.5832 | 23.8528 | 23.8006 | 23.7146 | 23.6544 | 23.7554 | 23.752 | 23.742 | 23.6518 | 23.5789 | 23.4503 | 23.3203 | 23.0372 | 22.8771 | 22.8902 | 22.9055 | 23.6826 | 23.6041 | 23.5499 | 23.4901 | 23.8098 | 24.1313 | 24.0413 | 23.9291 | 23.8424 | 25.2049 | 23.6209 | 23.8357 | 23.7761 | 23.6916 | 23.6219 | 23.6017 | 23.6446 | 23.0612 | 22.9685 | 24.1147 | 24.021 | 24.0159 | 23.962 | 24.1155 | 27.2019 | 31.6672 | 34.8769 | 30.2594 | 27.5098 | 29.7923 | 29.3361 | 29.9051 | 34.356 | 31.0558 |  | 28.9652 | 25.1499 | 28.6817 | 24.6954 | 23.437 | 23.4614 | 23.6481 | 22.9066 | 21.7219 | 22.3758 | 10.8158 | 14.3052 | 14.8842 | 11.1155 | -0.00014367 | -0.0028025 | 0.0017609 | 0.0045552 | 0.0010633 | -0.00049543 | 0.0091166 | -0.0033765 | -0.01021 | -360.1711 | 17.4131 | -360.4327 | 17.6328 | -360.7158 | 18.144 | -360.7897 | 17.5773 | -352.5921 | 18.6984 | -352.6167 | 16.8032 | 6.9857 | 365.8346 | 27.5343 | 14.5947 | 12.6315 | 22.3143
13:27 | 59 | 35.4133 |  | 8.4455 | 3.49 | 1.0323 | 3.347 | -1.6717 | 12.7422 | 5.6511 | 0.6341 | 0.6757 | 0.9845 | 0.7688 | -129.1006 | 4.6495 | 6.3932 | 1.5432 | -2.3019 | -0.7971 | 4.9876 |  | 4.919 | 0.9622 | 3.9871 | 3.3683 | 3.3309 | 1.1 | -1.0758 | 22.7505 | 22.6154 | 22.3885 | 22.3679 | 22.2787 | 22.2891 | 22.1542 | 22.9316 | 22.6416 | 22.6889 | 22.6864 | 23.0753 | 23.0294 | 22.9453 | 22.8978 | 22.7907 | 22.6895 | 22.6105 | 22.5225 | 22.3918 | 22.3577 | 22.2781 | 22.9333 | 22.5705 | 22.6012 | 22.5841 | 22.7154 | 23.1854 | 22.7001 | 22.9473 | 23.0455 | 23.1264 | 23.5075 | 22.8699 | 22.921 | 22.8788 | 22.8192 | 22.6924 | 22.6272 | 22.4354 | 22.2667 | 23.2742 | 22.661 | 22.762 | 22.971 | 23.4544 | 23.3162 | 23.2758 | 23.2764 | 23.2247 | 23.506 | 23.0627 | 23.0785 | 23.1244 | 23.0776 | 23.0034 | 22.9365 | 22.8336 | 22.7249 | 22.8991 | 22.8593 | 23.1333 | 23.1664 | 23.1482 | 23.0686 | 23.3161 | 23.8246 | 23.7242 | 23.7352 | 23.6723 | 23.8931 | 23.303 | 23.3729 | 23.3951 | 23.356 | 23.364 | 23.3876 | 23.3069 | 22.9834 | 22.7875 | 23.3075 | 23.3589 | 23.3353 | 23.3019 | 23.3993 | 33.5215 | 56.7999 | 24.04 | 26.4384 | 25.1828 | 25.986 | 26.5686 | 34.2238 | 30.0521 | 34.0444 | 61.3723 | 58.1873 | 48.2489 | 58.1537 | 57.588 | 51.618 | 48.0696 | 59.8379 | 23.0968 | 22.8511 | 23.4387 | 22.8424 | 22.6499 | 22.5298 | 26.3795 | 22.313 | 22.2841 | 22.2088 | 22.1709 | 22.1098 | 22.1867 | 23.1894 | 22.5175 | 22.4317 | 22.9512 | 22.4509 | 22.6998 | 22.9981 | 22.9043 | 22.8372 | 22.7716 | 22.6689 | 22.6244 | 22.6132 | 22.5549 | 23.637 | 22.7267 | 22.7279 | 23.7482 | 22.9591 | 23.7772 | 22.8816 | 23.0547 | 23.2189 | 23.8798 | 22.9272 | 22.9671 | 22.9482 | 22.9014 | 22.7953 | 22.6778 | 22.611 | 22.5378 | 23.6223 | 22.6036 | 22.7062 | 22.9367 | 23.599 | 23.8598 | 23.8088 | 23.7218 | 23.6557 | 23.7666 | 23.7601 | 23.7449 | 23.6474 | 23.5814 | 23.4487 | 23.3206 | 23.0439 | 22.8858 | 22.8941 | 22.9068 | 23.6856 | 23.6042 | 23.5531 | 23.4937 | 23.8264 | 24.1311 | 24.0389 | 23.932 | 23.8499 | 25.276 | 23.6208 | 23.843 | 23.7725 | 23.6899 | 23.6207 | 23.5984 | 23.6359 | 23.0669 | 22.9698 | 24.1079 | 24.0165 | 24.016 | 23.9514 | 24.125 | 27.266 | 31.5667 | 34.7924 | 30.3731 | 27.7554 | 30.0825 | 29.6153 | 30.0353 | 34.6243 | 31.2079 |  | 29.234 | 25.3232 | 28.9672 | 24.6938 | 23.433 | 23.4609 | 23.6848 | 22.9353 | 21.7264 | 22.383 | 10.8019 | 14.2694 | 14.9015 | 11.0957 | -0.00037306 | -0.0027627 | 0.00050056 | 0.0031981 | 0.0014303 | -0.00084546 | 0.02352 | -0.018454 | -0.01267 | -360.1681 | 17.4131 | -360.445 | 17.6677 | -360.8112 | 18.1871 | -360.8543 | 17.6102 | -352.5829 | 18.682 | -352.6106 | 16.8197 | 3.4148 | 358.1257 | 27.7683 | 14.5854 | 12.7048 | 22.3309
13:27 | 60 | 35.3926 |  | 8.4443 | 3.4677 | 1.0314 | 3.2896 | -1.5717 | 12.7012 | 5.7238 | 0.6339 | 0.6741 | 0.9797 | 0.7681 | -128.9946 | 4.6617 | 6.4931 | 1.6052 | -2.3958 | -0.8396 | 5.0569 |  | 4.9233 | 0.9107 | 3.9875 | 3.3688 | 3.3276 | 1.0998 | 1.7831 | 22.7586 | 22.6159 | 22.3974 | 22.369 | 22.2791 | 22.294 | 22.1563 | 22.9372 | 22.6527 | 22.6982 | 22.6903 | 23.0976 | 23.0336 | 22.9517 | 22.9014 | 22.7907 | 22.6878 | 22.6123 | 22.5263 | 22.3945 | 22.3662 | 22.2856 | 22.9383 | 22.57 | 22.6025 | 22.5895 | 22.7306 | 23.1881 | 22.7013 | 22.9492 | 23.0521 | 23.1341 | 23.5101 | 22.8795 | 22.9199 | 22.8839 | 22.8217 | 22.6982 | 22.6351 | 22.4389 | 22.2675 | 23.2795 | 22.6653 | 22.7572 | 22.9718 | 23.4605 | 23.3198 | 23.2661 | 23.2743 | 23.2229 | 23.5172 | 23.0591 | 23.0739 | 23.1264 | 23.0703 | 23.0005 | 22.9406 | 22.8302 | 22.7182 | 22.9076 | 22.8586 | 23.1381 | 23.1756 | 23.1564 | 23.0777 | 23.3404 | 23.8299 | 23.7336 | 23.7413 | 23.6806 | 23.9186 | 23.3098 | 23.3802 | 23.3998 | 23.3605 | 23.3711 | 23.3976 | 23.3057 | 22.9874 | 22.794 | 23.3118 | 23.3664 | 23.3377 | 23.3083 | 23.4115 | 33.6768 | 57.1798 | 24.1021 | 26.553 | 25.3465 | 26.1728 | 26.6995 | 34.6243 | 30.2816 | 34.4532 | 64.7385 | 60.0662 | 48.1066 | 58.4215 | 58.6337 | 52.6493 | 47.4866 | 61.2535 | 23.1718 | 22.9063 | 23.5308 | 22.9058 | 22.6547 | 22.5369 | 26.4518 | 22.3153 | 22.2828 | 22.211 | 22.1748 | 22.1004 | 22.1894 | 23.1836 | 22.5221 | 22.4282 | 22.9711 | 22.4454 | 22.6977 | 23.0018 | 22.9146 | 22.8442 | 22.7701 | 22.672 | 22.6288 | 22.6135 | 22.5636 | 23.6457 | 22.7317 | 22.7292 | 23.7582 | 22.9668 | 23.7834 | 22.8807 | 23.0517 | 23.2296 | 23.8743 | 22.9267 | 22.968 | 22.9436 | 22.9051 | 22.7997 | 22.6784 | 22.6119 | 22.5396 | 23.6221 | 22.6037 | 22.7056 | 22.9344 | 23.6151 | 23.864 | 23.8164 | 23.7281 | 23.6694 | 23.7819 | 23.7762 | 23.7493 | 23.6514 | 23.5848 | 23.4576 | 23.3328 | 23.0597 | 22.9002 | 22.8978 | 22.9139 | 23.684 | 23.602 | 23.5566 | 23.4974 | 23.8412 | 24.1366 | 24.0371 | 23.9294 | 23.8491 | 25.3412 | 23.6193 | 23.8377 | 23.7737 | 23.688 | 23.6237 | 23.5988 | 23.6276 | 23.0652 | 22.9655 | 24.1065 | 24.0141 | 24.0057 | 23.9491 | 24.1339 | 27.34 | 31.4714 | 34.8681 | 30.4828 | 28.0185 | 30.3768 | 29.9043 | 30.1813 | 34.8856 | 31.3499 |  | 29.4939 | 25.487 | 29.2614 | 24.6898 | 23.43 | 23.4584 | 23.7166 | 22.9477 | 21.7295 | 22.3865 | 10.8215 | 14.2613 | 14.9024 | 11.1076 | 0.000545 | -0.0027913 | 0.0015799 | 0.0042569 | 0.0010275 | -0.00023143 | 0.03178 | -0.015254 | -0.0041308 | -360.1835 | 17.4418 | -360.4481 | 17.6512 | -360.8112 | 18.1543 | -360.8143 | 17.5917 | -352.6075 | 18.7045 | -352.6136 | 16.8094 | 4.2685 | 367.7883 | 28.0077 | 14.5818 | 12.7041 | 22.3386
13:27 | 61 | 35.3972 |  | 8.4162 | 3.4035 | 1.0393 | 3.2446 | -1.6543 | 12.7149 | 5.6957 | 0.6358 | 0.6717 | 0.9842 | 0.7664 | -129.027 | 4.6447 | 6.4721 | 1.6135 | -2.5109 | -0.8931 | 5.0308 |  | 4.898 | 0.9501 | 3.9858 | 3.3669 | 3.3259 | 1.0997 | 1.2634 | 22.7655 | 22.6103 | 22.396 | 22.3655 | 22.2781 | 22.2938 | 22.1588 | 22.9426 | 22.6495 | 22.7037 | 22.6895 | 23.1149 | 23.0317 | 22.9514 | 22.8939 | 22.7853 | 22.6847 | 22.6098 | 22.5191 | 22.3867 | 22.3631 | 22.281 | 22.9339 | 22.5671 | 22.5977 | 22.582 | 22.7302 | 23.1811 | 22.6985 | 22.9482 | 23.0515 | 23.1397 | 23.5087 | 22.8809 | 22.913 | 22.881 | 22.8178 | 22.6992 | 22.632 | 22.431 | 22.267 | 23.2753 | 22.6625 | 22.7547 | 22.9714 | 23.4701 | 23.3188 | 23.2638 | 23.2694 | 23.2211 | 23.5371 | 23.0642 | 23.0683 | 23.1249 | 23.0662 | 22.9961 | 22.9465 | 22.8256 | 22.7188 | 22.9107 | 22.8527 | 23.1359 | 23.1754 | 23.1591 | 23.0796 | 23.3531 | 23.8273 | 23.73 | 23.7369 | 23.6781 | 23.9313 | 23.308 | 23.382 | 23.3999 | 23.357 | 23.3699 | 23.3975 | 23.3191 | 22.9978 | 22.7983 | 23.3149 | 23.3679 | 23.3468 | 23.3146 | 23.4196 | 33.7739 | 58.1524 | 24.1577 | 26.6877 | 25.508 | 26.3644 | 26.8389 | 35.0548 | 30.5218 | 34.8739 | 67.0556 | 60.6881 | 46.931 | 58.5998 | 59.8732 | 53.8016 | 47.2251 | 62.5334 | 23.2585 | 22.96 | 23.6279 | 22.9791 | 22.6609 | 22.5441 | 26.6766 | 22.3187 | 22.2894 | 22.2104 | 22.1774 | 22.1079 | 22.1847 | 23.1842 | 22.5235 | 22.4335 | 22.9939 | 22.4452 | 22.6887 | 22.9983 | 22.906 | 22.844 | 22.7701 | 22.6648 | 22.626 | 22.6081 | 22.5673 | 23.6532 | 22.7314 | 22.7295 | 23.7573 | 22.9719 | 23.7819 | 22.8793 | 23.0521 | 23.2409 | 23.8735 | 22.9242 | 22.9715 | 22.938 | 22.9006 | 22.7996 | 22.6784 | 22.613 | 22.5383 | 23.6186 | 22.6005 | 22.7046 | 22.931 | 23.6292 | 23.8629 | 23.811 | 23.7293 | 23.6775 | 23.7871 | 23.7823 | 23.7471 | 23.6536 | 23.5804 | 23.4609 | 23.3391 | 23.0536 | 22.9005 | 22.8951 | 22.9152 | 23.6868 | 23.6056 | 23.5584 | 23.4986 | 23.8648 | 24.1432 | 24.0502 | 23.9312 | 23.8503 | 25.4146 | 23.6236 | 23.8364 | 23.7764 | 23.6899 | 23.6331 | 23.6041 | 23.6413 | 23.068 | 22.971 | 24.1147 | 24.0265 | 24.0109 | 23.9608 | 24.1552 | 27.4274 | 31.4447 | 34.9529 | 30.6292 | 28.282 | 30.6844 | 30.2104 | 30.3484 | 35.1384 | 31.5014 |  | 29.7741 | 25.6561 | 29.5714 | 24.6934 | 23.429 | 23.4556 | 23.7446 | 22.965 | 21.7251 | 22.3954 | 10.8228 | 14.27 | 14.8913 | 11.1084 | 0.00020898 | -0.0031078 | 0.0015735 | 0.0039673 | 0.0012974 | -0.00073035 | 0.017797 | 0.0022117 | -0.017418 | -360.1096 | 17.3987 | -360.3896 | 17.6266 | -360.7466 | 18.1666 | -360.7773 | 17.5896 | -352.5521 | 18.6553 | -352.5767 | 16.8074 | 4.6149 | 359.3058 | 28.2564 | 14.5806 | 12.5845 | 22.3451
13:27 | 62 | 35.4548 |  | 8.4473 | 3.3877 | 0.9842 | 3.2652 | -1.6589 | 12.613 | 5.5866 | 0.6353 | 0.6726 | 0.9842 | 0.769 | -129.0766 | 4.5931 | 6.2813 | 1.6276 | -2.4381 | -0.9 | 5.0405 |  | 4.9638 | 0.9352 | 3.9864 | 3.3669 | 3.3291 | 1.0982 | 0.7001 | 22.766 | 22.6154 | 22.3895 | 22.3696 | 22.2818 | 22.2963 | 22.1592 | 22.9428 | 22.6487 | 22.7001 | 22.6912 | 23.1285 | 23.0325 | 22.9507 | 22.8935 | 22.7882 | 22.6857 | 22.6088 | 22.522 | 22.383 | 22.357 | 22.2745 | 22.9316 | 22.5679 | 22.6015 | 22.5783 | 22.7392 | 23.1793 | 22.6956 | 22.9466 | 23.0581 | 23.1507 | 23.5157 | 22.89 | 22.9187 | 22.8838 | 22.8211 | 22.6972 | 22.632 | 22.4325 | 22.2686 | 23.2744 | 22.6596 | 22.7579 | 22.9685 | 23.4906 | 23.3178 | 23.2792 | 23.2711 | 23.225 | 23.5574 | 23.0669 | 23.0695 | 23.1177 | 23.0731 | 22.9988 | 22.9429 | 22.839 | 22.7273 | 22.9193 | 22.8532 | 23.1373 | 23.1723 | 23.1611 | 23.0786 | 23.3615 | 23.8249 | 23.7282 | 23.7377 | 23.6768 | 23.9437 | 23.3093 | 23.3811 | 23.402 | 23.361 | 23.3659 | 23.3948 | 23.3204 | 22.9986 | 22.8009 | 23.3121 | 23.3711 | 23.3434 | 23.3071 | 23.4274 | 33.7703 | 59.5355 | 24.1797 | 26.8133 | 25.6649 | 26.5548 | 26.9665 | 35.5078 | 30.7819 | 35.2981 | 68.723 | 62.1666 | 46.4986 | 58.5645 | 61.3072 | 54.3894 | 47.782 | 61.4723 | 23.3521 | 23.0185 | 23.7327 | 23.0551 | 22.6488 | 22.5424 | 27.0072 | 22.3156 | 22.2898 | 22.2097 | 22.1728 | 22.1129 | 22.1862 | 23.186 | 22.5207 | 22.4347 | 23.0131 | 22.4491 | 22.6871 | 22.9996 | 22.9005 | 22.8406 | 22.7583 | 22.6636 | 22.6247 | 22.5918 | 22.5688 | 23.6534 | 22.7276 | 22.7289 | 23.7521 | 22.9846 | 23.7797 | 22.8826 | 23.0599 | 23.2511 | 23.8757 | 22.9296 | 22.9749 | 22.9413 | 22.8945 | 22.804 | 22.6813 | 22.6213 | 22.5396 | 23.6191 | 22.5967 | 22.7059 | 22.9331 | 23.6392 | 23.8615 | 23.8087 | 23.7254 | 23.6679 | 23.7823 | 23.7788 | 23.7427 | 23.6512 | 23.5777 | 23.4568 | 23.3335 | 23.0449 | 22.8924 | 22.9032 | 22.916 | 23.6883 | 23.6134 | 23.5632 | 23.4977 | 23.8757 | 24.1426 | 24.0529 | 23.9318 | 23.8503 | 25.482 | 23.6251 | 23.836 | 23.7749 | 23.6912 | 23.6307 | 23.6076 | 23.654 | 23.0717 | 22.9741 | 24.1122 | 24.0319 | 24.0164 | 23.9643 | 24.1784 | 27.536 | 31.4404 | 35.0475 | 30.7814 | 28.5497 | 30.9915 | 30.5439 | 30.542 | 35.4061 | 31.687 |  | 30.0418 | 25.8397 | 29.8879 | 24.687 | 23.4327 | 23.4571 | 23.7791 | 22.9904 | 21.7418 | 22.402 | 10.8348 | 14.2891 | 14.883 | 11.1342 | 0.00024609 | -0.0025801 | 0.0015171 | 0.0046627 | 0.00091047 | -0.00045758 | 8.3381e-05 | -0.0049251 | -0.029661 | -360.165 | 17.4356 | -360.4389 | 17.6594 | -360.8297 | 18.1645 | -360.8204 | 17.5999 | -352.6167 | 18.684 | -352.6198 | 16.8279 | 2.8126 | 365.9418 | 28.5093 | 14.5861 | 12.5562 | 22.3661
13:27 | 63 | 35.404 |  | 8.4413 | 3.3885 | 1.0412 | 3.3071 | -1.6676 | 12.6111 | 5.6644 | 0.6357 | 0.6752 | 0.9821 | 0.7688 | -129.1042 | 4.5914 | 6.3036 | 1.6422 | -2.4377 | -0.9077 | 4.9954 |  | 4.9423 | 0.9395 | 3.9848 | 3.3659 | 3.3287 | 1.0988 | 1.5978 | 22.7642 | 22.6265 | 22.4018 | 22.3725 | 22.2932 | 22.3036 | 22.1641 | 22.9438 | 22.6556 | 22.6988 | 22.6929 | 23.1478 | 23.0377 | 22.9563 | 22.9027 | 22.7965 | 22.6912 | 22.6178 | 22.528 | 22.3923 | 22.3558 | 22.2762 | 22.9361 | 22.5675 | 22.6042 | 22.5868 | 22.7578 | 23.1839 | 22.7033 | 22.948 | 23.0584 | 23.1577 | 23.5167 | 22.8851 | 22.9238 | 22.8815 | 22.8202 | 22.698 | 22.6386 | 22.4388 | 22.2719 | 23.2753 | 22.6627 | 22.7579 | 22.9719 | 23.5037 | 23.3204 | 23.2746 | 23.2689 | 23.2206 | 23.5699 | 23.0612 | 23.0733 | 23.1093 | 23.0757 | 22.9979 | 22.9352 | 22.8415 | 22.724 | 22.9138 | 22.8479 | 23.1454 | 23.1746 | 23.1578 | 23.0753 | 23.3808 | 23.8232 | 23.7291 | 23.7426 | 23.6798 | 23.961 | 23.3143 | 23.3822 | 23.4015 | 23.3623 | 23.3716 | 23.4019 | 23.3245 | 23.001 | 22.8064 | 23.3134 | 23.3752 | 23.3397 | 23.3084 | 23.4451 | 33.9761 | 59.8418 | 24.229 | 26.9511 | 25.8327 | 26.7369 | 27.0951 | 35.9762 | 31.0585 | 35.7347 | 70.1755 | 64.9203 | 46.6326 | 58.5378 | 62.6406 | 55.2046 | 47.9987 | 60.5479 | 23.4436 | 23.076 | 23.8393 | 23.1325 | 22.6514 | 22.5424 | 27.1467 | 22.3153 | 22.2959 | 22.2136 | 22.1794 | 22.1167 | 22.1987 | 23.1899 | 22.5227 | 22.4372 | 23.0435 | 22.4569 | 22.6982 | 22.9992 | 22.8981 | 22.8366 | 22.7427 | 22.6681 | 22.625 | 22.5848 | 22.5669 | 23.643 | 22.7274 | 22.7257 | 23.7461 | 22.9942 | 23.7782 | 22.8791 | 23.063 | 23.2591 | 23.8812 | 22.9334 | 22.9745 | 22.9466 | 22.9007 | 22.8076 | 22.6837 | 22.6237 | 22.5432 | 23.6168 | 22.5998 | 22.7076 | 22.9316 | 23.6519 | 23.8596 | 23.809 | 23.7201 | 23.6585 | 23.7833 | 23.7826 | 23.7437 | 23.6552 | 23.5852 | 23.4558 | 23.3273 | 23.0478 | 22.8924 | 22.9103 | 22.9143 | 23.6839 | 23.6069 | 23.554 | 23.4946 | 23.8714 | 24.1297 | 24.0444 | 23.9236 | 23.8443 | 25.5395 | 23.6207 | 23.8327 | 23.7743 | 23.6899 | 23.6216 | 23.6078 | 23.6566 | 23.0763 | 22.9786 | 24.1148 | 24.0308 | 24.0172 | 23.9576 | 24.2014 | 27.6791 | 31.4881 | 35.2814 | 30.8952 | 28.8206 | 31.2875 | 30.8918 | 30.7175 | 35.7015 | 31.9057 |  | 30.3067 | 26.0271 | 30.2032 | 24.6903 | 23.4371 | 23.4506 | 23.8159 | 22.999 | 21.7486 | 22.4045 | 10.7925 | 14.275 | 14.8689 | 11.113 | -0.00031819 | -0.0030498 | 0.0018451 | 0.0045451 | 0.0018937 | -0.00034011 | 0.0034222 | 9.0188e-05 | -0.012524 | -360.1773 | 17.4315 | -360.4481 | 17.6615 | -360.8112 | 18.1789 | -360.8758 | 17.6163 | -352.5921 | 18.6943 | -352.6044 | 16.8135 | -10.8958 | 360.7239 | 28.7633 | 14.572 | 12.588 | 22.3738
13:27 | 64 | 35.3973 |  | 8.496 | 3.4723 | 0.9445 | 3.2654 | -1.5987 | 12.6194 | 5.6449 | 0.6363 | 0.6749 | 0.986 | 0.7692 | -129.1442 | 4.6377 | 6.2944 | 1.675 | -2.5012 | -0.8055 | 5.0765 |  | 4.9346 | 1.0033 | 3.9855 | 3.3673 | 3.3282 | 1.1008 | 1.38 | 22.7693 | 22.6241 | 22.4002 | 22.3638 | 22.2829 | 22.2965 | 22.1621 | 22.9383 | 22.6549 | 22.6956 | 22.6914 | 23.1666 | 23.0353 | 22.9546 | 22.9102 | 22.8033 | 22.6934 | 22.6214 | 22.534 | 22.3973 | 22.3621 | 22.2791 | 22.9391 | 22.5682 | 22.6106 | 22.5964 | 22.7674 | 23.1907 | 22.7058 | 22.9527 | 23.057 | 23.1671 | 23.5151 | 22.8829 | 22.9235 | 22.8791 | 22.8169 | 22.7017 | 22.6432 | 22.4384 | 22.2723 | 23.2777 | 22.663 | 22.7602 | 22.9728 | 23.514 | 23.3232 | 23.27 | 23.2707 | 23.2175 | 23.5906 | 23.0674 | 23.0756 | 23.1113 | 23.081 | 23.0002 | 22.941 | 22.8399 | 22.7222 | 22.9134 | 22.8516 | 23.1542 | 23.1736 | 23.1544 | 23.0776 | 23.4022 | 23.8263 | 23.7295 | 23.7409 | 23.6827 | 23.9807 | 23.3129 | 23.3806 | 23.402 | 23.354 | 23.3746 | 23.4048 | 23.3371 | 23.0049 | 22.8113 | 23.3201 | 23.3746 | 23.3463 | 23.3138 | 23.4598 | 34.1398 | 59.5021 | 24.2891 | 27.1122 | 26.0051 | 26.922 | 27.2339 | 36.4462 | 31.3343 | 36.1604 | 72.0637 | 67.9173 | 46.3487 | 58.1526 | 63.7354 | 56.4841 | 48.6073 | 62.4921 | 23.5543 | 23.1379 | 23.9526 | 23.223 | 22.6587 | 22.5412 | 27.3017 | 22.3203 | 22.2948 | 22.2177 | 22.183 | 22.1194 | 22.1933 | 23.1889 | 22.5224 | 22.4382 | 23.0698 | 22.4613 | 22.7005 | 22.9903 | 22.8907 | 22.8309 | 22.7443 | 22.664 | 22.6165 | 22.5982 | 22.5605 | 23.6369 | 22.7236 | 22.7221 | 23.7418 | 22.9974 | 23.7729 | 22.8758 | 23.0639 | 23.2756 | 23.8819 | 22.9304 | 22.9721 | 22.9466 | 22.9077 | 22.8071 | 22.6846 | 22.6183 | 22.5461 | 23.6201 | 22.6027 | 22.7067 | 22.9295 | 23.672 | 23.8589 | 23.8044 | 23.7215 | 23.654 | 23.7983 | 23.7843 | 23.7507 | 23.6573 | 23.5878 | 23.4564 | 23.3301 | 23.0544 | 22.8995 | 22.9197 | 22.9214 | 23.6907 | 23.6016 | 23.5449 | 23.4955 | 23.8841 | 24.1281 | 24.0456 | 23.9237 | 23.8424 | 25.5949 | 23.6234 | 23.8364 | 23.7741 | 23.695 | 23.6249 | 23.6049 | 23.6497 | 23.0761 | 22.9818 | 24.1107 | 24.0247 | 24.0183 | 23.9538 | 24.2098 | 27.8284 | 31.5588 | 35.588 | 31.0537 | 29.0941 | 31.5989 | 31.2548 | 30.8686 | 36.0292 | 32.1314 |  | 30.5712 | 26.2335 | 30.5286 | 24.6999 | 23.4313 | 23.4546 | 23.8625 | 23.0391 | 21.7614 | 22.4206 | 10.8249 | 14.2862 | 14.9008 | 11.1104 | 0.00062456 | -0.0031165 | 0.0015895 | 0.0043123 | 0.0012653 | -3.2835e-05 | 0.00089816 | -0.010795 | -0.030847 | -360.1342 | 17.411 | -360.4081 | 17.6348 | -360.7558 | 18.1625 | -360.7897 | 17.5876 | -352.5429 | 18.6737 | -352.5767 | 16.8094 | 4.8598 | 363.7616 | 29.026 | 14.5935 | 12.6679 | 22.4002
13:27 | 65 | 35.3007 |  | 8.5376 | 3.4941 | 0.9892 | 3.1542 | -1.6508 | 12.5291 | 5.6394 | 0.6346 | 0.675 | 0.9824 | 0.7693 | -129.131 | 4.591 | 6.2675 | 1.6413 | -2.4632 | -0.8622 | 5.0246 |  | 4.9251 | 1.0138 | 3.9854 | 3.3667 | 3.33 | 1.0997 | 0.7005 | 22.7764 | 22.6204 | 22.3919 | 22.3614 | 22.2718 | 22.2933 | 22.1623 | 22.9409 | 22.6508 | 22.6928 | 22.6852 | 23.1896 | 23.0318 | 22.951 | 22.9085 | 22.798 | 22.6911 | 22.6117 | 22.5281 | 22.3908 | 22.3644 | 22.2752 | 22.9327 | 22.5652 | 22.609 | 22.5882 | 22.7684 | 23.1871 | 22.7002 | 22.9496 | 23.0555 | 23.179 | 23.5199 | 22.8825 | 22.9209 | 22.882 | 22.8217 | 22.6989 | 22.6418 | 22.4407 | 22.2699 | 23.2848 | 22.6606 | 22.763 | 22.9709 | 23.5205 | 23.3249 | 23.2727 | 23.2786 | 23.2208 | 23.6067 | 23.0685 | 23.0787 | 23.111 | 23.0802 | 22.9978 | 22.9447 | 22.8405 | 22.7247 | 22.9201 | 22.8592 | 23.1486 | 23.1718 | 23.1554 | 23.0803 | 23.4116 | 23.826 | 23.7281 | 23.7383 | 23.6788 | 23.997 | 23.3077 | 23.3765 | 23.396 | 23.3524 | 23.3691 | 23.3993 | 23.3448 | 23.0045 | 22.8093 | 23.3232 | 23.3787 | 23.3456 | 23.3143 | 23.4672 | 34.5591 | 59.6733 | 24.3359 | 27.2677 | 26.1868 | 27.1309 | 27.3757 | 36.9202 | 31.6094 | 36.5848 | 73.9691 | 70.3045 | 46.5715 | 57.9556 | 64.3242 | 58.1257 | 52.957 | 64.9417 | 23.665 | 23.2115 | 24.0801 | 23.3285 | 22.6591 | 22.5478 | 27.8803 | 22.3241 | 22.2933 | 22.2213 | 22.184 | 22.1173 | 22.1978 | 23.1915 | 22.5266 | 22.4468 | 23.0931 | 22.465 | 22.7069 | 22.9946 | 22.8946 | 22.8316 | 22.7635 | 22.6595 | 22.6213 | 22.6055 | 22.5702 | 23.6499 | 22.7267 | 22.7279 | 23.7504 | 23.0163 | 23.7733 | 22.8787 | 23.0613 | 23.2882 | 23.877 | 22.9269 | 22.9682 | 22.9459 | 22.9038 | 22.8059 | 22.6786 | 22.6161 | 22.5467 | 23.619 | 22.5963 | 22.7027 | 22.9318 | 23.6942 | 23.8591 | 23.8033 | 23.7241 | 23.6505 | 23.8062 | 23.7759 | 23.7517 | 23.6574 | 23.5863 | 23.4561 | 23.3382 | 23.0504 | 22.9043 | 22.9203 | 22.9299 | 23.701 | 23.6092 | 23.5487 | 23.498 | 23.9076 | 24.1441 | 24.0532 | 23.9312 | 23.8487 | 25.6515 | 23.6292 | 23.8483 | 23.7772 | 23.7019 | 23.6349 | 23.6136 | 23.6526 | 23.0713 | 22.9748 | 24.1048 | 24.0205 | 24.0174 | 23.9515 | 24.2211 | 27.9678 | 31.6396 | 35.816 | 31.2665 | 29.3705 | 31.9187 | 31.6292 | 31.0253 | 36.3679 | 32.3864 |  | 30.8353 | 26.4391 | 30.8629 | 24.6946 | 23.4193 | 23.4505 | 23.8961 | 23.0614 | 21.7568 | 22.4304 | 10.8179 | 14.2649 | 14.8784 | 11.1249 | 0.0010182 | -0.0034476 | 0.0015363 | 0.0043067 | 0.0015437 | -0.00062723 | 0.02163 | -0.017732 | -0.027084 | -360.1896 | 17.4172 | -360.4266 | 17.6512 | -360.7743 | 18.1604 | -360.8512 | 17.6102 | -352.5675 | 18.682 | -352.6229 | 16.8135 | 11.1276 | 363.1515 | 29.2967 | 14.5716 | 12.5917 | 22.4091
13:27 | 66 | 35.3143 |  | 8.4941 | 3.4596 | 0.9899 | 3.132 | -1.6245 | 12.5285 | 5.6062 | 0.6337 | 0.6748 | 0.9818 | 0.7703 | -129.1237 | 4.6213 | 6.3179 | 1.6935 | -2.4766 | -0.99 | 4.9831 |  | 4.9466 | 1.0212 | 3.985 | 3.3653 | 3.3284 | 1.0994 | 2.0425 | 22.7816 | 22.6263 | 22.3979 | 22.3693 | 22.2827 | 22.2993 | 22.1677 | 22.9473 | 22.6523 | 22.6957 | 22.6875 | 23.2199 | 23.0323 | 22.9507 | 22.9083 | 22.7948 | 22.6902 | 22.607 | 22.5226 | 22.3894 | 22.3664 | 22.2776 | 22.9255 | 22.5569 | 22.604 | 22.5815 | 22.7745 | 23.1872 | 22.7029 | 22.9506 | 23.0581 | 23.1878 | 23.525 | 22.8791 | 22.9271 | 22.8865 | 22.8262 | 22.706 | 22.6457 | 22.4506 | 22.2744 | 23.2875 | 22.6661 | 22.7631 | 22.9725 | 23.5375 | 23.3246 | 23.2728 | 23.2869 | 23.2274 | 23.6299 | 23.0724 | 23.0832 | 23.1169 | 23.0791 | 23.0006 | 22.9465 | 22.8466 | 22.7282 | 22.9267 | 22.8568 | 23.1432 | 23.1731 | 23.1567 | 23.0801 | 23.4253 | 23.8273 | 23.7279 | 23.7414 | 23.6762 | 24.0156 | 23.3124 | 23.3791 | 23.3944 | 23.355 | 23.3667 | 23.4016 | 23.3485 | 23.0058 | 22.8072 | 23.3279 | 23.3773 | 23.3405 | 23.31 | 23.4781 | 35.1891 | 60.0203 | 24.3495 | 27.4216 | 26.3827 | 27.3447 | 27.5196 | 37.3929 | 31.876 | 37.0281 | 75.4416 | 72.0463 | 49.5555 | 57.6384 | 62.8686 | 59.5934 | 56.9734 | 67.3978 | 23.7627 | 23.2898 | 24.2201 | 23.4348 | 22.6573 | 22.551 | 28.2661 | 22.3195 | 22.2923 | 22.2159 | 22.1775 | 22.1175 | 22.1976 | 23.1916 | 22.5276 | 22.4434 | 23.121 | 22.467 | 22.7143 | 22.9996 | 22.8993 | 22.8333 | 22.7746 | 22.6646 | 22.6263 | 22.6025 | 22.5749 | 23.651 | 22.7347 | 22.7277 | 23.7528 | 23.0369 | 23.7745 | 22.8795 | 23.0583 | 23.2968 | 23.8776 | 22.9248 | 22.9708 | 22.9479 | 22.9054 | 22.8055 | 22.6823 | 22.6227 | 22.5515 | 23.6152 | 22.5959 | 22.7014 | 22.9295 | 23.7158 | 23.8553 | 23.8056 | 23.7243 | 23.6502 | 23.8075 | 23.7733 | 23.7501 | 23.6577 | 23.5896 | 23.4582 | 23.3394 | 23.0496 | 22.9044 | 22.917 | 22.927 | 23.7009 | 23.6147 | 23.5514 | 23.4986 | 23.9201 | 24.155 | 24.0595 | 23.9355 | 23.8544 | 25.7111 | 23.6332 | 23.8476 | 23.7831 | 23.7027 | 23.6365 | 23.6265 | 23.6645 | 23.0758 | 22.9732 | 24.1146 | 24.0233 | 24.0204 | 23.9552 | 24.2519 | 28.1048 | 31.7314 | 35.8873 | 31.5211 | 29.6541 | 32.236 | 32.0119 | 31.1789 | 36.704 | 32.6988 |  | 31.1107 | 26.6584 | 31.2195 | 24.6937 | 23.4299 | 23.4527 | 23.9422 | 23.08 | 21.7671 | 22.4432 | 10.8158 | 14.284 | 14.9054 | 11.1296 | 0.00032653 | -0.0028495 | 0.0018781 | 0.0046258 | 0.0011335 | -0.00037796 | 0.017606 | -0.0038063 | -0.022573 | -360.165 | 17.4295 | -360.4481 | 17.6677 | -360.8174 | 18.1748 | -360.842 | 17.6061 | -352.5921 | 18.7045 | -352.6167 | 16.832 | 6.6595 | 361.5379 | 29.5772 | 14.5947 | 12.5291 | 22.4235
13:27 | 67 | 35.2471 |  | 8.491 | 3.5125 | 1.0875 | 3.0962 | -1.71 | 12.5348 | 5.5453 | 0.6352 | 0.6747 | 0.9794 | 0.7686 | -129.1787 | 4.5683 | 6.3776 | 1.6359 | -2.4681 | -0.8757 | 5.0878 |  | 4.9385 | 1.0401 | 3.9842 | 3.3637 | 3.3278 | 1.0989 | 1.6987 | 22.7842 | 22.6259 | 22.4026 | 22.3686 | 22.2807 | 22.2942 | 22.1648 | 22.94 | 22.6517 | 22.6944 | 22.6884 | 23.2366 | 23.0269 | 22.948 | 22.9133 | 22.7984 | 22.6937 | 22.6132 | 22.5368 | 22.3991 | 22.3771 | 22.288 | 22.9363 | 22.564 | 22.6064 | 22.5883 | 22.7888 | 23.1904 | 22.7071 | 22.9531 | 23.0645 | 23.2007 | 23.528 | 22.8833 | 22.9296 | 22.8883 | 22.8305 | 22.7167 | 22.653 | 22.4557 | 22.2816 | 23.2844 | 22.6735 | 22.7641 | 22.9755 | 23.5582 | 23.3248 | 23.277 | 23.2934 | 23.236 | 23.6555 | 23.0786 | 23.0882 | 23.1255 | 23.0849 | 23.011 | 22.9577 | 22.8605 | 22.73 | 22.9419 | 22.8562 | 23.1481 | 23.1853 | 23.1625 | 23.0811 | 23.4492 | 23.8343 | 23.7343 | 23.7473 | 23.6835 | 24.0397 | 23.3193 | 23.385 | 23.4027 | 23.3588 | 23.3712 | 23.4085 | 23.354 | 23.0075 | 22.8099 | 23.3312 | 23.3724 | 23.3418 | 23.3082 | 23.4864 | 35.473 | 60.1207 | 24.389 | 27.5829 | 26.5738 | 27.5463 | 27.6562 | 37.8497 | 32.1467 | 37.4694 | 76.8109 | 73.4498 | 53.3952 | 57.3287 | 59.4659 | 58.9508 | 60.405 | 69.8479 | 23.8685 | 23.3696 | 24.3621 | 23.5365 | 22.6592 | 22.5576 | 28.9411 | 22.3212 | 22.2959 | 22.2194 | 22.1838 | 22.125 | 22.1959 | 23.1963 | 22.5311 | 22.4458 | 23.1552 | 22.4725 | 22.7173 | 22.9941 | 22.8982 | 22.8303 | 22.771 | 22.6683 | 22.6291 | 22.5969 | 22.5724 | 23.6456 | 22.7343 | 22.7281 | 23.7498 | 23.0495 | 23.7738 | 22.8814 | 23.064 | 23.3062 | 23.8849 | 22.9267 | 22.967 | 22.9493 | 22.906 | 22.8093 | 22.6877 | 22.6255 | 22.5499 | 23.6177 | 22.59 | 22.7051 | 22.925 | 23.7289 | 23.8499 | 23.8036 | 23.7191 | 23.647 | 23.8114 | 23.7765 | 23.7466 | 23.6576 | 23.5863 | 23.4564 | 23.3373 | 23.0589 | 22.9008 | 22.9289 | 22.9211 | 23.7001 | 23.611 | 23.5536 | 23.4979 | 23.931 | 24.1504 | 24.0517 | 23.9399 | 23.856 | 25.7726 | 23.6286 | 23.8429 | 23.7867 | 23.7002 | 23.6348 | 23.6255 | 23.6699 | 23.0774 | 22.9794 | 24.1176 | 24.0292 | 24.0149 | 23.9612 | 24.2741 | 28.2233 | 31.9863 | 35.7456 | 31.7334 | 29.9457 | 32.5786 | 32.4088 | 31.3225 | 37.0371 | 33.0432 |  | 31.4038 | 26.887 | 31.5752 | 24.6889 | 23.429 | 23.4592 | 23.9884 | 23.1021 | 21.7676 | 22.4542 | 10.8223 | 14.2475 | 14.8866 | 11.0951 | -0.00035485 | -0.0033545 | 0.00077625 | 0.0033575 | 0.0013318 | -0.00054555 | 0.021315 | 0.0061262 | -0.041025 | -360.1927 | 17.4069 | -360.4142 | 17.6307 | -360.7681 | 18.1502 | -360.8112 | 17.5917 | -352.5706 | 18.6758 | -352.5767 | 16.7971 | 3.0833 | 365.9967 | 29.8649 | 14.567 | 12.5747 | 22.4349
13:27 | 68 | 35.276 |  | 8.4183 | 3.4972 | 0.9762 | 3.0135 | -1.685 | 12.5669 | 5.6815 | 0.6339 | 0.6754 | 0.9808 | 0.7689 | -129.2102 | 4.5735 | 6.3174 | 1.6765 | -2.4886 | -0.8697 | 5.0953 |  | 4.9939 | 1.0373 | 3.9842 | 3.3639 | 3.3259 | 1.1 | 1.13 | 22.7845 | 22.6261 | 22.403 | 22.3673 | 22.2794 | 22.2995 | 22.1674 | 22.9403 | 22.6525 | 22.6956 | 22.691 | 23.2565 | 23.0291 | 22.9517 | 22.9114 | 22.8016 | 22.6971 | 22.6177 | 22.5385 | 22.4016 | 22.3793 | 22.2873 | 22.9445 | 22.5713 | 22.6013 | 22.5893 | 22.7955 | 23.1829 | 22.7049 | 22.9505 | 23.0626 | 23.2071 | 23.5229 | 22.8815 | 22.9249 | 22.8854 | 22.8275 | 22.709 | 22.6557 | 22.4517 | 22.281 | 23.2769 | 22.6735 | 22.7621 | 22.9663 | 23.5693 | 23.3329 | 23.2834 | 23.2908 | 23.2364 | 23.6733 | 23.0768 | 23.0864 | 23.1247 | 23.0832 | 23.0101 | 22.9554 | 22.8644 | 22.7312 | 22.9494 | 22.8652 | 23.1569 | 23.195 | 23.1695 | 23.0845 | 23.4706 | 23.835 | 23.7403 | 23.7515 | 23.6888 | 24.0617 | 23.3272 | 23.3889 | 23.4086 | 23.365 | 23.3758 | 23.4097 | 23.3667 | 23.0198 | 22.816 | 23.3307 | 23.377 | 23.3487 | 23.3164 | 23.4992 | 35.8625 | 59.7304 | 24.4729 | 27.7412 | 26.7632 | 27.7419 | 27.7902 | 38.3079 | 32.4448 | 37.9325 | 78.3572 | 74.1831 | 54.3401 | 59.2775 | 57.7074 | 59.2363 | 64.3721 | 71.8697 | 23.9715 | 23.4481 | 24.493 | 23.6351 | 22.6631 | 22.5666 | 30.3697 | 22.3239 | 22.2995 | 22.2211 | 22.1988 | 22.1301 | 22.2008 | 23.2017 | 22.5356 | 22.4552 | 23.1876 | 22.4797 | 22.7226 | 22.9958 | 22.8967 | 22.8323 | 22.7748 | 22.6685 | 22.6348 | 22.595 | 22.5747 | 23.6479 | 22.7301 | 22.7306 | 23.7525 | 23.0676 | 23.7749 | 22.8824 | 23.072 | 23.3143 | 23.8888 | 22.9312 | 22.9667 | 22.9492 | 22.9043 | 22.8128 | 22.6886 | 22.6284 | 22.5542 | 23.6182 | 22.5864 | 22.7115 | 22.9317 | 23.7446 | 23.8525 | 23.8038 | 23.7171 | 23.6446 | 23.817 | 23.7838 | 23.7448 | 23.6572 | 23.5813 | 23.4523 | 23.3465 | 23.0515 | 22.9015 | 22.9292 | 22.9221 | 23.6952 | 23.6029 | 23.5458 | 23.4954 | 23.94 | 24.1427 | 24.0446 | 23.9331 | 23.8512 | 25.8316 | 23.6246 | 23.842 | 23.7801 | 23.6928 | 23.6351 | 23.626 | 23.6708 | 23.0776 | 22.9859 | 24.1184 | 24.0257 | 24.0139 | 23.9623 | 24.2965 | 28.2983 | 32.7922 | 36.0603 | 31.8569 | 30.2247 | 32.9274 | 32.8134 | 31.4491 | 37.3581 | 33.3617 |  | 31.6958 | 27.1306 | 31.9444 | 24.6843 | 23.4255 | 23.4531 | 24.0344 | 23.129 | 21.7761 | 22.4629 | 10.8369 | 14.2701 | 14.9067 | 11.1221 | 0.00037955 | -0.0030115 | 0.0016502 | 0.0047726 | 0.0010657 | -0.00053534 | 0.015571 | -0.0076633 | -0.019701 | -360.0942 | 17.4131 | -360.4112 | 17.6492 | -360.7804 | 18.1625 | -360.8235 | 17.5896 | -352.6013 | 18.6861 | -352.586 | 16.8279 | 9.3064 | 357.8398 | 30.1552 | 14.5884 | 12.574 | 22.4525
13:27 | 69 | 35.203 |  | 8.4243 | 3.4408 | 0.9026 | 3.0354 | -1.6759 | 12.5019 | 5.6373 | 0.6335 | 0.6763 | 0.9799 | 0.7697 | -129.2293 | 4.4887 | 6.3837 | 1.7726 | -2.4266 | -0.9315 | 5.0933 |  | 4.9553 | 0.9637 | 3.9847 | 3.3661 | 3.3264 | 1.0995 | 2.7029 | 22.7848 | 22.6308 | 22.4034 | 22.3701 | 22.2868 | 22.303 | 22.165 | 22.9407 | 22.6552 | 22.6994 | 22.6938 | 23.2823 | 23.0331 | 22.9537 | 22.9084 | 22.8025 | 22.6935 | 22.6229 | 22.5353 | 22.3963 | 22.3766 | 22.2866 | 22.9359 | 22.5697 | 22.5978 | 22.5897 | 22.8048 | 23.1789 | 22.7037 | 22.9502 | 23.0622 | 23.2125 | 23.5156 | 22.8827 | 22.925 | 22.8826 | 22.8216 | 22.699 | 22.6544 | 22.4491 | 22.2814 | 23.2776 | 22.6718 | 22.7615 | 22.965 | 23.5807 | 23.3321 | 23.2812 | 23.2849 | 23.2342 | 23.6981 | 23.0692 | 23.0814 | 23.1197 | 23.0782 | 23.0032 | 22.951 | 22.8646 | 22.7316 | 22.9404 | 22.8691 | 23.1619 | 23.1899 | 23.1732 | 23.0854 | 23.4849 | 23.8368 | 23.7409 | 23.7553 | 23.6911 | 24.0842 | 23.3293 | 23.3905 | 23.411 | 23.3661 | 23.3812 | 23.4024 | 23.3742 | 23.0226 | 22.8167 | 23.3309 | 23.3755 | 23.3467 | 23.3218 | 23.5101 | 36.261 | 59.3262 | 24.5294 | 27.8537 | 26.9598 | 27.9508 | 27.9167 | 38.7453 | 32.7671 | 38.4222 | 79.6964 | 74.9382 | 55.526 | 62.8456 | 57.6 | 61.9424 | 65.2644 | 73.135 | 24.0787 | 23.5319 | 24.625 | 23.7395 | 22.6631 | 22.5638 |  | 22.3279 | 22.3031 | 22.2196 | 22.1962 | 22.1265 | 22.2046 | 23.1964 | 22.5379 | 22.4513 | 23.2136 | 22.4813 | 22.7296 | 22.9977 | 22.8929 | 22.8373 | 22.7675 | 22.6762 | 22.6314 | 22.5947 | 22.5781 | 23.6455 | 22.7339 | 22.7288 | 23.7553 | 23.0897 | 23.7708 | 22.881 | 23.0677 | 23.3354 | 23.8869 | 22.9333 | 22.973 | 22.9452 | 22.9056 | 22.8116 | 22.6853 | 22.6285 | 22.5626 | 23.6179 | 22.5956 | 22.7113 | 22.94 | 23.7629 | 23.8548 | 23.8032 | 23.7205 | 23.6458 | 23.8201 | 23.785 | 23.7415 | 23.653 | 23.5834 | 23.4545 | 23.3539 | 23.0398 | 22.905 | 22.9218 | 22.9237 | 23.6977 | 23.6033 | 23.5422 | 23.4976 | 23.9475 | 24.1408 | 24.0435 | 23.9273 | 23.8521 | 25.8936 | 23.6259 | 23.8423 | 23.7804 | 23.6907 | 23.6307 | 23.6291 | 23.6723 | 23.0789 | 22.9881 | 24.1235 | 24.0206 | 24.0191 | 23.9624 | 24.3205 | 28.3764 | 33.7323 | 36.4866 | 32.0109 | 30.5097 | 33.2762 | 33.2417 | 31.562 | 37.7021 | 33.6481 |  | 32.0005 | 27.3605 | 32.3467 | 24.6944 | 23.4363 | 23.4654 | 24.0975 | 23.1653 | 21.7993 | 22.4941 | 10.8404 | 14.2665 | 14.8743 | 11.1329 | 0.0004941 | -0.0028953 | 0.0012488 | 0.0043229 | 0.0013454 | -0.00075032 | 0.0117 | -0.0097708 | -0.016411 | -360.165 | 17.4397 | -360.4512 | 17.6512 | -360.8174 | 18.183 | -360.8666 | 17.6163 | -352.6136 | 18.6963 | -352.6383 | 16.8115 | 8.7748 | 368.5964 | 30.4557 | 14.5704 | 12.508 | 22.4823
13:27 | 70 | 35.1341 |  | 8.4871 | 3.3573 | 0.9744 | 3.0659 | -1.6239 | 12.527 | 5.5528 | 0.6345 | 0.6761 | 0.9821 | 0.7695 | -129.2625 | 4.5846 | 6.3502 | 1.7174 | -2.4914 | -0.955 | 5.0789 |  | 4.946 | 0.9133 | 3.9845 | 3.3645 | 3.3252 | 1.0982 | 1.5553 | 22.7922 | 22.6352 | 22.4075 | 22.3761 | 22.2894 | 22.3075 | 22.1665 | 22.9395 | 22.6576 | 22.7013 | 22.6948 | 23.3052 | 23.0339 | 22.9494 | 22.9085 | 22.803 | 22.6927 | 22.621 | 22.5324 | 22.3916 | 22.3731 | 22.2865 | 22.9345 | 22.567 | 22.5977 | 22.5887 | 22.8168 | 23.1814 | 22.7006 | 22.9486 | 23.0647 | 23.2213 | 23.5171 | 22.8831 | 22.9241 | 22.8834 | 22.8194 | 22.6968 | 22.6562 | 22.4501 | 22.2779 | 23.2797 | 22.6693 | 22.7602 | 22.9689 | 23.5969 | 23.3255 | 23.2798 | 23.2887 | 23.2407 | 23.7167 | 23.0578 | 23.0836 | 23.1214 | 23.0797 | 23.0054 | 22.9575 | 22.8682 | 22.7313 | 22.9428 | 22.8717 | 23.1572 | 23.1873 | 23.1724 | 23.0878 | 23.4991 | 23.833 | 23.7379 | 23.757 | 23.6907 | 24.1021 | 23.3255 | 23.3925 | 23.4096 | 23.3653 | 23.3816 | 23.4012 | 23.3746 | 23.0169 | 22.8121 | 23.3279 | 23.3716 | 23.3405 | 23.3162 | 23.5158 | 36.4527 | 59.4071 | 24.5646 | 27.9286 | 27.164 | 28.1738 | 28.034 | 39.1428 | 33.0822 | 38.8698 | 80.4396 | 76.4386 | 57.849 | 66.2998 | 56.7092 | 64.6164 | 63.368 | 74.1189 | 24.1771 | 23.6088 | 24.7534 | 23.8296 | 22.6686 | 22.5567 |  | 22.3234 | 22.3029 | 22.226 | 22.1858 | 22.1266 | 22.2069 | 23.1982 | 22.536 | 22.4515 | 23.2306 | 22.4771 | 22.7294 | 22.9999 | 22.8967 | 22.8394 | 22.7633 | 22.6794 | 22.6373 | 22.6042 | 22.5845 | 23.6517 | 22.7392 | 22.7336 | 23.758 | 23.1123 | 23.776 | 22.8851 | 23.0638 | 23.3471 | 23.8847 | 22.933 | 22.9704 | 22.9416 | 22.9057 | 22.8081 | 22.6803 | 22.6276 | 22.5555 | 23.6192 | 22.5956 | 22.7019 | 22.9377 | 23.7806 | 23.8541 | 23.7983 | 23.7205 | 23.6429 | 23.8247 | 23.7792 | 23.7364 | 23.6493 | 23.5802 | 23.4552 | 23.3401 | 23.0609 | 22.9028 | 22.9341 | 22.9237 | 23.6996 | 23.6064 | 23.5478 | 23.4981 | 23.9583 | 24.1377 | 24.0453 | 23.9307 | 23.8533 | 25.9625 | 23.6283 | 23.8401 | 23.7811 | 23.6947 | 23.6258 | 23.6279 | 23.6735 | 23.081 | 22.985 | 24.1204 | 24.0211 | 24.0212 | 23.9664 | 24.3366 | 28.5069 | 33.9643 | 36.6798 | 32.1998 | 30.8102 | 33.6474 | 33.7069 | 31.7087 | 38.0774 | 33.9198 |  | 32.2863 | 27.5901 | 32.7355 | 24.6876 | 23.4271 | 23.4571 | 24.1325 | 23.1863 | 21.798 | 22.4914 | 10.8348 | 14.2678 | 14.8747 | 11.1065 | 5.0038e-06 | -0.0028408 | 0.0016747 | 0.0043278 | 0.001423 | -0.00051164 | 0.0081296 | -0.010764 | -0.02351 | -360.1435 | 17.4131 | -360.4142 | 17.6328 | -360.7866 | 18.1604 | -360.8174 | 17.5753 | -352.5583 | 18.6696 | -352.5798 | 16.8156 | 9.556 | 358.991 | 30.7643 | 14.5712 | 12.4649 | 22.4921
13:27 | 71 | 35.0295 |  | 8.4007 | 3.4282 | 0.942 | 3.0259 | -1.6096 | 12.5258 | 5.5492 | 0.6334 | 0.6738 | 0.9813 | 0.769 | -129.2029 | 4.5064 | 6.3018 | 1.7102 | -2.4391 | -0.9755 | 5.0609 |  | 4.8316 | 0.7786 | 3.9816 | 3.3673 | 3.3248 | 1.1002 | 1.4049 | 22.7911 | 22.6354 | 22.4065 | 22.3753 | 22.2893 | 22.3101 | 22.1733 | 22.9395 | 22.6556 | 22.7024 | 22.698 | 23.3274 | 23.0331 | 22.9482 | 22.9136 | 22.8039 | 22.6962 | 22.6163 | 22.5296 | 22.3914 | 22.3743 | 22.2852 | 22.9414 | 22.5635 | 22.5941 | 22.5845 | 22.8185 | 23.1832 | 22.6993 | 22.9513 | 23.0658 | 23.2367 | 23.5207 | 22.8812 | 22.9195 | 22.8861 | 22.8225 | 22.7015 | 22.6631 | 22.4512 | 22.2775 | 23.2757 | 22.6693 | 22.7519 | 22.9685 | 23.61 | 23.3255 | 23.28 | 23.2926 | 23.2423 | 23.7323 | 23.0569 | 23.0878 | 23.1243 | 23.0835 | 23.0084 | 22.9636 | 22.8707 | 22.733 | 22.9596 | 22.8717 | 23.1585 | 23.1826 | 23.1739 | 23.0901 | 23.513 | 23.8298 | 23.7376 | 23.7593 | 23.6877 | 24.1223 | 23.3206 | 23.3884 | 23.4093 | 23.3629 | 23.3772 | 23.4037 | 23.3835 | 23.0264 | 22.819 | 23.3332 | 23.3795 | 23.3447 | 23.317 | 23.5383 | 36.7214 | 59.833 | 24.6201 | 28.0059 | 27.3715 | 28.4017 | 28.151 | 39.5063 | 33.365 | 39.3036 | 81.5329 | 78.3522 | 59.9732 | 68.7614 | 54.9917 | 66.976 | 63.1548 | 76.3799 | 24.2667 | 23.6758 | 24.8741 | 23.911 | 22.6731 | 22.555 |  | 22.3193 | 22.297 | 22.2271 | 22.1855 | 22.1308 | 22.2058 | 23.1981 | 22.5289 | 22.4521 | 23.2523 | 22.473 | 22.722 | 22.9938 | 22.9009 | 22.8351 | 22.7582 | 22.6691 | 22.6346 | 22.5957 | 22.5838 | 23.6541 | 22.7347 | 22.7299 | 23.7523 | 23.1247 | 23.7759 | 22.8846 | 23.0706 | 23.3548 | 23.8832 | 22.9336 | 22.9714 | 22.9466 | 22.9057 | 22.8157 | 22.6884 | 22.6308 | 22.5556 | 23.6244 | 22.5984 | 22.7075 | 22.9397 | 23.8071 | 23.8524 | 23.7963 | 23.7204 | 23.6475 | 23.8361 | 23.7834 | 23.7337 | 23.653 | 23.5828 | 23.4561 | 23.3445 | 23.0616 | 22.9049 | 22.9436 | 22.9302 | 23.6938 | 23.6069 | 23.5453 | 23.4933 | 23.9714 | 24.14 | 24.0466 | 23.9276 | 23.8533 | 26.0238 | 23.626 | 23.8324 | 23.7758 | 23.6917 | 23.6305 | 23.6319 | 23.6754 | 23.0873 | 22.9847 | 24.1148 | 24.0195 | 24.0212 | 23.969 | 24.3601 | 28.5975 | 33.8593 | 37.0454 | 32.3391 | 31.0961 | 34.002 | 34.1581 | 31.8744 | 38.4195 | 34.1612 |  | 32.576 | 27.8319 | 33.1177 | 24.6783 | 23.4208 | 23.4463 | 24.1726 | 23.1999 | 21.7998 | 22.4921 | 10.8354 | 14.2759 | 14.8569 | 11.1062 | 6.9269e-05 | -0.0024554 | 0.0018568 | 0.0046501 | 0.0011754 | -0.00070355 | 0.0096489 | 0.0049381 | -0.02 | -360.1927 | 17.4233 | -360.4235 | 17.6389 | -360.7773 | 18.1604 | -360.8143 | 17.5917 | -352.6013 | 18.6922 | -352.6229 | 16.8176 | 11.4992 | 365.6215 | 31.0694 | 14.5664 | 12.3687 | 22.4998
13:27 | 72 | 34.9181 |  | 8.4217 | 3.4347 | 0.9525 | 3.0947 | -1.6287 | 12.4524 | 5.5644 | 0.6339 | 0.675 | 0.98 | 0.7709 | -129.2744 | 4.3879 | 6.2848 | 1.7335 | -2.3969 | -0.9146 | 5.116 |  | 4.9319 | 0.8232 | 3.9825 | 3.3646 | 3.3311 | 1.1002 | 1.0557 | 22.7893 | 22.6308 | 22.4054 | 22.3702 | 22.2833 | 22.3059 | 22.1706 | 22.9398 | 22.6557 | 22.6981 | 22.6908 | 23.3499 | 23.0271 | 22.9462 | 22.9189 | 22.8061 | 22.6932 | 22.6135 | 22.5391 | 22.3953 | 22.3849 | 22.2871 | 22.9432 | 22.5633 | 22.5951 | 22.5837 | 22.8271 | 23.1879 | 22.6979 | 22.951 | 23.0694 | 23.2552 | 23.5249 | 22.8882 | 22.922 | 22.8867 | 22.8261 | 22.7038 | 22.6706 | 22.4536 | 22.2824 | 23.2752 | 22.6696 | 22.7539 | 22.9707 | 23.6211 | 23.3234 | 23.2761 | 23.2861 | 23.2356 | 23.7523 | 23.0544 | 23.0868 | 23.1218 | 23.0808 | 23.0007 | 22.9619 | 22.8707 | 22.7313 | 22.9641 | 22.8635 | 23.163 | 23.1894 | 23.1739 | 23.0905 | 23.5316 | 23.8367 | 23.7401 | 23.7569 | 23.6906 | 24.1492 | 23.3206 | 23.3873 | 23.4082 | 23.3649 | 23.3761 | 23.4032 | 23.3914 | 23.0329 | 22.828 | 23.3381 | 23.3828 | 23.3545 | 23.3249 | 23.5568 | 37.2355 | 59.9607 | 24.7378 | 28.0726 | 27.5954 | 28.6463 | 28.2711 | 39.8488 | 33.6304 | 39.7621 | 83.126 | 80.294 | 62.881 | 70.6892 | 55.4633 | 68.311 | 65.4386 | 79.2659 | 24.3634 | 23.7454 | 24.9852 | 23.996 | 22.6666 | 22.5532 |  | 22.3223 | 22.2938 | 22.2265 | 22.1885 | 22.1345 | 22.2034 | 23.1914 | 22.5265 | 22.4528 | 23.2748 | 22.4671 | 22.715 | 22.9927 | 22.9009 | 22.8336 | 22.7407 | 22.671 | 22.6324 | 22.5731 | 22.5848 | 23.6469 | 22.7286 | 22.7252 | 23.7448 | 23.1374 | 23.7701 | 22.8806 | 23.0667 | 23.3722 | 23.8844 | 22.9353 | 22.9758 | 22.9517 | 22.9047 | 22.8287 | 22.6913 | 22.6296 | 22.5635 | 23.6253 | 22.6055 | 22.7186 | 22.9405 | 23.8319 | 23.8562 | 23.7975 | 23.7212 | 23.6555 | 23.8457 | 23.7874 | 23.7351 | 23.6512 | 23.5875 | 23.4572 | 23.3551 | 23.034 | 22.9157 | 22.9401 | 22.9339 | 23.692 | 23.6063 | 23.5461 | 23.4964 | 23.9907 | 24.144 | 24.044 | 23.9282 | 23.853 | 26.0797 | 23.6222 | 23.8296 | 23.7747 | 23.6855 | 23.6294 | 23.6344 | 23.6747 | 23.0819 | 22.9811 | 24.1056 | 24.0178 | 24.0152 | 23.9646 | 24.376 | 28.624 | 34.0089 | 37.2216 | 32.4317 | 31.3798 | 34.357 | 34.5964 | 32.0435 | 38.7474 | 34.3727 |  | 32.8751 | 28.0744 | 33.5132 | 24.6907 | 23.4293 | 23.4516 | 24.2356 | 23.2462 | 21.812 | 22.5128 | 10.8384 | 14.2501 | 14.8634 | 11.1102 | 0.00035464 | -0.002889 | 0.0013436 | 0.0038546 | 0.0017729 | -0.00065613 | 0.022954 | -0.0086205 | -0.020651 | -360.1742 | 17.4274 | -360.4512 | 17.6738 | -360.8358 | 18.1789 | -360.842 | 17.5978 | -352.6075 | 18.6963 | -352.6352 | 16.8299 | 10.7164 | 361.3659 | 31.3797 | 14.5568 | 12.4754 | 22.5291
13:27 | 73 | 34.9464 |  | 8.3959 | 3.3628 | 0.8745 | 3.0633 | -1.6369 | 12.4386 | 5.6242 | 0.6344 | 0.6732 | 0.9798 | 0.7686 | -129.3915 | 4.382 | 6.34 | 1.6783 | -2.4571 | -0.9616 | 5.122 |  | 4.9373 | 0.8321 | 3.9829 | 3.3666 | 3.3274 | 1.1012 | 0.421 | 22.7969 | 22.6333 | 22.4071 | 22.371 | 22.2786 | 22.308 | 22.1664 | 22.9397 | 22.6564 | 22.6949 | 22.6905 | 23.3695 | 23.027 | 22.9427 | 22.919 | 22.8075 | 22.6922 | 22.6136 | 22.5434 | 22.3959 | 22.3821 | 22.2839 | 22.9361 | 22.5585 | 22.6006 | 22.5812 | 22.8412 | 23.1913 | 22.6971 | 22.9436 | 23.0716 | 23.262 | 23.5298 | 22.8921 | 22.93 | 22.8831 | 22.826 | 22.709 | 22.6759 | 22.4589 | 22.278 | 23.28 | 22.6696 | 22.7598 | 22.969 | 23.6374 | 23.3225 | 23.2781 | 23.2876 | 23.236 | 23.7736 | 23.059 | 23.081 | 23.1247 | 23.0746 | 22.998 | 22.9581 | 22.8683 | 22.7244 | 22.9615 | 22.8646 | 23.1672 | 23.1928 | 23.1783 | 23.0993 | 23.5517 | 23.8351 | 23.7432 | 23.7556 | 23.6899 | 24.1738 | 23.3277 | 23.3898 | 23.4107 | 23.3754 | 23.3813 | 23.4113 | 23.3937 | 23.0377 | 22.8293 | 23.3332 | 23.3811 | 23.3534 | 23.3225 | 23.5619 | 37.5033 | 60.519 | 24.8959 | 28.1329 | 27.8334 | 28.8895 | 28.3842 | 40.1647 | 33.8777 | 40.2043 | 84.5567 | 82.2969 | 66.3045 | 72.3514 | 58.1754 | 69.3971 | 67.6408 | 80.7555 | 24.4687 | 23.814 | 25.0977 | 24.0918 | 22.6658 | 22.5522 |  | 22.321 | 22.2946 | 22.2234 | 22.1845 | 22.132 | 22.2045 | 23.1915 | 22.5259 | 22.4504 | 23.2987 | 22.465 | 22.7155 | 23.0011 | 22.901 | 22.8459 | 22.7352 | 22.6807 | 22.642 | 22.5757 | 22.5936 | 23.6539 | 22.7349 | 22.7358 | 23.7522 | 23.1673 | 23.7832 | 22.8863 | 23.0637 | 23.3905 | 23.8843 | 22.9407 | 22.9765 | 22.9483 | 22.906 | 22.8295 | 22.6872 | 22.6318 | 22.5643 | 23.6237 | 22.6015 | 22.7141 | 22.9353 | 23.8588 | 23.8593 | 23.801 | 23.7202 | 23.6471 | 23.852 | 23.7754 | 23.7381 | 23.6478 | 23.5839 | 23.4515 | 23.3496 | 23.0392 | 22.9169 | 22.9367 | 22.9357 | 23.6944 | 23.6078 | 23.5542 | 23.5025 | 24.0155 | 24.1436 | 24.048 | 23.9357 | 23.8531 | 26.1457 | 23.6289 | 23.8329 | 23.7803 | 23.6938 | 23.6273 | 23.6387 | 23.6849 | 23.0813 | 22.9863 | 24.1105 | 24.0245 | 24.016 | 23.9713 | 24.4013 | 28.6959 | 34.3728 | 37.1058 | 32.5099 | 31.6749 | 34.7302 | 35.0723 | 32.2275 | 39.1 | 34.6088 |  | 33.1729 | 28.3125 | 33.8834 | 24.6832 | 23.4287 | 23.4502 | 24.288 | 23.2752 | 21.8208 | 22.5193 | 10.8242 | 14.2644 | 14.8647 | 11.0957 | 0.00031362 | -0.0028396 | 0.0013968 | 0.0040719 | 0.0013072 | 3.2234e-05 | 0.017628 | -0.0021609 | -0.020547 | -360.1465 | 17.4213 | -360.405 | 17.6348 | -360.765 | 18.1481 | -360.8081 | 17.5835 | -352.5736 | 18.6881 | -352.6044 | 16.8053 | 20.837 | 362.9376 | 31.6961 | 14.5645 | 12.382 | 22.548
13:27 | 74 | 34.9818 |  | 8.4546 | 3.4008 | 1.0148 | 3.1663 | -1.6716 | 12.4806 | 5.6222 | 0.634 | 0.6726 | 0.9817 | 0.7671 | -129.3928 | 4.4585 | 6.2513 | 1.6755 | -2.3795 | -0.8146 | 5.1337 |  | 5.0076 | 0.8547 | 3.9823 | 3.3667 | 3.3294 | 1.101 | 1.9472 | 22.8 | 22.6409 | 22.4061 | 22.3688 | 22.282 | 22.3116 | 22.1696 | 22.9394 | 22.6554 | 22.6994 | 22.6939 | 23.3846 | 23.0308 | 22.9476 | 22.9167 | 22.8003 | 22.6929 | 22.6152 | 22.535 | 22.3862 | 22.3725 | 22.2811 | 22.9256 | 22.554 | 22.5934 | 22.5777 | 22.8484 | 23.1818 | 22.6964 | 22.9367 | 23.0627 | 23.2672 | 23.5313 | 22.8828 | 22.9246 | 22.8847 | 22.8278 | 22.7067 | 22.6731 | 22.4551 | 22.2748 | 23.2862 | 22.6689 | 22.76 | 22.972 | 23.6571 | 23.3318 | 23.2811 | 23.2972 | 23.2446 | 23.8008 | 23.068 | 23.0833 | 23.1294 | 23.0781 | 23.0111 | 22.9712 | 22.8735 | 22.7311 | 22.9659 | 22.8729 | 23.1729 | 23.187 | 23.1775 | 23.1024 | 23.5666 | 23.8252 | 23.7455 | 23.7556 | 23.694 | 24.1921 | 23.3265 | 23.3919 | 23.4177 | 23.3753 | 23.3835 | 23.4152 | 23.4044 | 23.047 | 22.8344 | 23.3418 | 23.3845 | 23.3534 | 23.3295 | 23.5828 | 38.0447 | 61.8067 | 24.9843 | 28.2004 | 28.0768 | 29.1159 | 28.5004 | 40.4699 | 34.123 | 40.6414 | 85.7636 | 84.4737 | 69.995 | 73.2976 | 60.5782 | 70.6527 | 69.1173 | 82.1158 | 24.5799 | 23.8846 | 25.2155 | 24.205 | 22.6656 | 22.5547 |  | 22.3256 | 22.2981 | 22.2201 | 22.177 | 22.1243 | 22.2034 | 23.1941 | 22.5232 | 22.4508 | 23.3306 | 22.4679 | 22.7181 | 23.0054 | 22.9093 | 22.8517 | 22.7376 | 22.6809 | 22.6449 | 22.5946 | 22.5951 | 23.6634 | 22.7416 | 22.7436 | 23.7597 | 23.203 | 23.7929 | 22.8876 | 23.0708 | 23.404 | 23.8829 | 22.9453 | 22.9747 | 22.9476 | 22.9074 | 22.8306 | 22.6877 | 22.6385 | 22.5658 | 23.6252 | 22.599 | 22.7127 | 22.9339 | 23.8798 | 23.8589 | 23.8009 | 23.7211 | 23.6413 | 23.8579 | 23.7552 | 23.738 | 23.6458 | 23.5775 | 23.4454 | 23.3495 | 23.0372 | 22.9083 | 22.9227 | 22.9399 | 23.701 | 23.6133 | 23.5593 | 23.5077 | 24.0336 | 24.148 | 24.0598 | 23.9373 | 23.8596 | 26.21 | 23.6364 | 23.8447 | 23.7884 | 23.7045 | 23.6334 | 23.6435 | 23.6945 | 23.0889 | 22.9923 | 24.1167 | 24.0284 | 24.0224 | 23.9736 | 24.4265 | 28.8095 | 34.6631 | 37.3259 | 32.5707 | 31.9705 | 35.1041 | 35.5715 | 32.4259 | 39.457 | 34.869 |  | 33.4644 | 28.5582 | 34.2401 | 24.6868 | 23.4161 | 23.4448 | 24.3426 | 23.3118 | 21.8297 | 22.5341 | 10.8466 | 14.2593 | 14.8915 | 11.1097 | 0.00062442 | -0.0025173 | 0.0019655 | 0.0045932 | 0.0019334 | -0.00031155 | 0.021657 | 0.0053027 | -0.03287 | -360.1435 | 17.411 | -360.405 | 17.643 | -360.8081 | 18.1645 | -360.8081 | 17.5855 | -352.5675 | 18.6799 | -352.586 | 16.8299 | 8.964 | 364.6938 | 32.0127 | 14.5754 | 12.5835 | 22.5708
13:27 | 75 | 34.9233 |  | 8.4436 | 3.2835 | 0.9219 | 3.0779 | -1.6439 | 12.4715 | 5.6071 | 0.6349 | 0.6782 | 0.9859 | 0.769 | -129.2882 | 4.4658 | 6.3732 | 1.6515 | -2.3649 | -0.8547 | 5.1702 |  | 4.9616 | 0.8563 | 3.9824 | 3.3659 | 3.3258 | 1.1008 | 1.3579 | 22.798 | 22.6393 | 22.409 | 22.3683 | 22.2867 | 22.3111 | 22.1741 | 22.9391 | 22.6518 | 22.6929 | 22.6866 | 23.4114 | 23.029 | 22.9464 | 22.915 | 22.8026 | 22.6926 | 22.618 | 22.5355 | 22.3877 | 22.3792 | 22.2833 | 22.9263 | 22.5624 | 22.5901 | 22.5822 | 22.859 | 23.1767 | 22.693 | 22.9402 | 23.0665 | 23.2834 | 23.5378 | 22.8848 | 22.9188 | 22.888 | 22.8286 | 22.7108 | 22.6776 | 22.4489 | 22.2758 | 23.2923 | 22.664 | 22.764 | 22.9751 | 23.6731 | 23.3372 | 23.2871 | 23.3024 | 23.2495 | 23.8282 | 23.0747 | 23.0883 | 23.1266 | 23.0849 | 23.013 | 22.9766 | 22.8836 | 22.7383 | 22.9796 | 22.8755 | 23.1666 | 23.1833 | 23.167 | 23.0918 | 23.5808 | 23.8292 | 23.7457 | 23.7554 | 23.694 | 24.205 | 23.3203 | 23.3908 | 23.4125 | 23.367 | 23.3736 | 23.4069 | 23.4128 | 23.049 | 22.8372 | 23.3457 | 23.3861 | 23.3594 | 23.3322 | 23.5983 | 38.5417 | 62.5894 | 25.0078 | 28.2629 | 28.3321 | 29.3499 | 28.641 | 40.7806 | 34.39 | 41.1002 | 86.8424 | 86.1948 | 73.0836 | 74.0974 | 64.1876 | 72.1736 | 71.7118 | 83.3737 | 24.6978 | 23.9571 | 25.3302 | 24.3116 | 22.6632 | 22.5545 |  | 22.3271 | 22.292 | 22.2191 | 22.1788 | 22.1218 | 22.206 | 23.1996 | 22.5287 | 22.4532 | 23.3611 | 22.4687 | 22.7135 | 23.0063 | 22.914 | 22.8504 | 22.7499 | 22.6832 | 22.6463 | 22.6008 | 22.5891 | 23.6541 | 22.7401 | 22.7391 | 23.7604 | 23.2319 | 23.7894 | 22.8865 | 23.0686 | 23.4169 | 23.8853 | 22.9434 | 22.9737 | 22.9504 | 22.9091 | 22.8332 | 22.6925 | 22.6376 | 22.569 | 23.6226 | 22.6009 | 22.7148 | 22.9414 | 23.907 | 23.8648 | 23.8053 | 23.724 | 23.6521 | 23.8679 | 23.7648 | 23.7433 | 23.654 | 23.5838 | 23.4545 | 23.3625 | 23.0326 | 22.9117 | 22.93 | 22.947 | 23.6948 | 23.613 | 23.5585 | 23.5044 | 24.0407 | 24.1502 | 24.0557 | 23.9314 | 23.8597 | 26.2652 | 23.6284 | 23.8434 | 23.7777 | 23.7002 | 23.6321 | 23.6406 | 23.6972 | 23.0917 | 22.9892 | 24.1147 | 24.0231 | 24.0198 | 23.965 | 24.4477 | 28.9473 | 34.7767 | 37.7998 | 32.6623 | 32.2735 | 35.4981 | 36.1147 | 32.65 | 39.8257 | 35.1348 |  | 33.7573 | 28.8157 | 34.5972 | 24.6753 | 23.4205 | 23.447 | 24.3948 | 23.3353 | 21.8385 | 22.5422 | 10.832 | 14.2862 | 14.8938 | 11.1386 | -0.00010427 | -0.0025294 | 0.0017769 | 0.004571 | 0.0009844 | -0.00010331 | 0.033904 | -0.0061145 | -0.007506 | -360.2019 | 17.4521 | -360.4604 | 17.6594 | -360.8112 | 18.1645 | -360.8143 | 17.6143 | -352.6475 | 18.7107 | -352.669 | 16.8176 | 27.4194 | 360.7356 | 32.3423 | 14.59 | 12.4745 | 22.5869
13:27 | 76 | 34.8961 |  | 8.483 | 3.3347 | 0.9015 | 3.2072 | -1.6224 | 12.4702 | 5.5139 | 0.6353 | 0.6743 | 0.9821 | 0.7692 | -129.2962 | 4.4054 | 6.3005 | 1.7934 | -2.2485 | -0.7377 | 5.2982 |  | 4.9838 | 0.8516 | 3.9823 | 3.3672 | 3.3282 | 1.1006 | 1.7081 | 22.799 | 22.6369 | 22.4108 | 22.3705 | 22.287 | 22.3109 | 22.1745 | 22.9352 | 22.6512 | 22.6897 | 22.6866 | 23.4369 | 23.0322 | 22.9463 | 22.908 | 22.8009 | 22.6905 | 22.6105 | 22.5385 | 22.385 | 22.3795 | 22.2818 | 22.9244 | 22.5658 | 22.5896 | 22.5791 | 22.8659 | 23.1716 | 22.6899 | 22.942 | 23.077 | 23.2976 | 23.5377 | 22.8908 | 22.9206 | 22.8834 | 22.826 | 22.7189 | 22.6828 | 22.467 | 22.2755 | 23.285 | 22.667 | 22.7629 | 22.9703 | 23.6848 | 23.3323 | 23.2942 | 23.3023 | 23.251 | 23.852 | 23.0728 | 23.0827 | 23.1296 | 23.0867 | 23.0066 | 22.972 | 22.8855 | 22.731 | 22.9806 | 22.8688 | 23.1621 | 23.1772 | 23.1694 | 23.0915 | 23.5951 | 23.8377 | 23.7447 | 23.759 | 23.6892 | 24.2278 | 23.3246 | 23.3894 | 23.4043 | 23.3667 | 23.3723 | 23.4021 | 23.4105 | 23.0404 | 22.8262 | 23.3319 | 23.3806 | 23.3585 | 23.3144 | 23.6024 | 38.4756 | 62.6244 | 25.0821 | 28.3307 | 28.5967 | 29.6 | 28.8008 | 41.0904 | 34.6607 | 41.5748 | 88.0684 | 87.76 | 75.1607 | 75.188 | 68.7395 | 73.7822 | 71.364 | 82.4135 | 24.8091 | 24.0242 | 25.4529 | 24.4054 | 22.6654 | 22.5552 |  | 22.3242 | 22.2944 | 22.2267 | 22.1833 | 22.1288 | 22.209 | 23.1989 | 22.5339 | 22.4531 | 23.3866 | 22.4662 | 22.7082 | 23.0111 | 22.9163 | 22.8547 | 22.7521 | 22.6949 | 22.6468 | 22.5966 | 22.5979 | 23.6489 | 22.7416 | 22.7405 | 23.7608 | 23.2577 | 23.7958 | 22.897 | 23.0712 | 23.4385 | 23.8915 | 22.9447 | 22.9793 | 22.959 | 22.9192 | 22.8402 | 22.7028 | 22.6424 | 22.5788 | 23.6271 | 22.607 | 22.7156 | 22.95 | 23.9402 | 23.8689 | 23.8108 | 23.7243 | 23.6577 | 23.8764 | 23.7822 | 23.7488 | 23.6612 | 23.5872 | 23.4665 | 23.3739 | 23.05 | 22.9196 | 22.9563 | 22.9521 | 23.6931 | 23.6111 | 23.5526 | 23.4943 | 24.0558 | 24.146 | 24.0468 | 23.9314 | 23.8559 | 26.3185 | 23.6183 | 23.8428 | 23.7714 | 23.698 | 23.6293 | 23.6412 | 23.6967 | 23.0885 | 22.9902 | 24.1146 | 24.021 | 24.0163 | 23.9637 | 24.4776 | 29.1788 | 34.8215 | 37.9788 | 32.844 | 32.5972 | 35.9041 | 36.7021 | 32.8868 | 40.2218 | 35.3992 |  | 34.05 | 29.0801 | 34.9492 | 24.6766 | 23.4205 | 23.4517 | 24.4568 | 23.3689 | 21.8479 | 22.5508 | 10.8277 | 14.275 | 14.8689 | 11.099 | 0.00055173 | -0.0023688 | 0.0012594 | 0.0042158 | 0.0015426 | -0.00080999 | 0.039911 | -0.0076 | -0.0069869 | -360.1158 | 17.4028 | -360.4204 | 17.6574 | -360.8174 | 18.1645 | -360.8112 | 17.5671 | -352.5244 | 18.6779 | -352.5952 | 16.8258 | 10.5053 | 366.3814 | 32.6849 | 14.572 | 12.6687 | 22.6084
13:27 | 77 | 34.7878 |  | 8.3888 | 3.2677 | 0.8702 | 3.0185 | -1.6446 | 12.5031 | 5.5748 | 0.6343 | 0.6744 | 0.982 | 0.7668 | -129.2435 | 4.3927 | 6.4028 | 1.8187 | -2.2933 | -0.869 | 5.1674 |  | 4.9938 | 0.9307 | 3.9815 | 3.366 | 3.3276 | 1.1011 | 1.115 | 22.7942 | 22.6308 | 22.4033 | 22.3675 | 22.2837 | 22.3073 | 22.1718 | 22.9352 | 22.6537 | 22.695 | 22.6877 | 23.4499 | 23.0276 | 22.9515 | 22.9071 | 22.7994 | 22.6888 | 22.6113 | 22.5327 | 22.3796 | 22.3814 | 22.282 | 22.9244 | 22.5618 | 22.5904 | 22.5744 | 22.8807 | 23.1747 | 22.6939 | 22.944 | 23.0709 | 23.3075 | 23.5267 | 22.8858 | 22.923 | 22.8819 | 22.824 | 22.7217 | 22.6844 | 22.4998 | 22.274 | 23.2829 | 22.6652 | 22.7612 | 22.969 | 23.696 | 23.3283 | 23.2929 | 23.2991 | 23.2501 | 23.8762 | 23.0668 | 23.081 | 23.1307 | 23.0859 | 23.0109 | 22.9705 | 22.8807 | 22.7313 | 22.9913 | 22.8736 | 23.1639 | 23.1759 | 23.1725 | 23.0918 | 23.6112 | 23.8396 | 23.7444 | 23.756 | 23.6924 | 24.2497 | 23.3284 | 23.3923 | 23.4068 | 23.3683 | 23.3792 | 23.4043 | 23.4124 | 23.04 | 22.8217 | 23.3253 | 23.3809 | 23.3568 | 23.3141 | 23.6134 | 38.7936 | 63.825 | 25.145 | 28.3956 | 28.8747 | 29.865 | 28.9744 | 41.4199 | 34.9631 | 42.0492 | 89.8657 | 89.5006 | 77.4661 | 75.8801 | 72.4617 | 75.6551 | 66.6594 | 81.1597 | 24.9126 | 24.0889 | 25.5748 | 24.5079 | 22.6685 | 22.563 |  | 22.3262 | 22.2984 | 22.2287 | 22.1857 | 22.1364 | 22.2053 | 23.1936 | 22.5334 | 22.4564 | 23.4142 | 22.4671 | 22.7163 | 23.0149 | 22.9151 | 22.8529 | 22.7531 | 22.6948 | 22.6525 | 22.5939 | 22.608 | 23.6577 | 22.7408 | 22.7438 | 23.7644 | 23.2858 | 23.7953 | 22.9037 | 23.0731 | 23.4484 | 23.8923 | 22.9419 | 22.983 | 22.957 | 22.9169 | 22.8453 | 22.6991 | 22.648 | 22.582 | 23.6272 | 22.6034 | 22.7173 | 22.944 | 23.9609 | 23.8577 | 23.8043 | 23.7181 | 23.6507 | 23.8828 | 23.7785 | 23.7467 | 23.6559 | 23.5791 | 23.4598 | 23.3744 | 23.0501 | 22.9175 | 22.965 | 22.9476 | 23.6984 | 23.6123 | 23.5558 | 23.499 | 24.0714 | 24.1414 | 24.0499 | 23.9357 | 23.8598 | 26.3794 | 23.6258 | 23.8509 | 23.7799 | 23.7012 | 23.6309 | 23.6449 | 23.6958 | 23.0905 | 22.9858 | 24.116 | 24.0226 | 24.0246 | 23.9678 | 24.4967 | 29.4322 | 34.884 | 38.267 | 33.0922 | 32.9221 | 36.3016 | 37.2779 | 33.1055 | 40.6192 | 35.6631 |  | 34.357 | 29.3466 | 35.3128 | 24.6809 | 23.4229 | 23.4518 | 24.5207 | 23.4038 | 21.8571 | 22.5677 | 10.8136 | 14.2609 | 14.9042 | 11.1483 | 0.00059875 | -0.0030263 | 0.0014 | 0.0045451 | 0.00091047 | -0.000763 | 0.027653 | -0.0086508 | -0.01534 | -360.1865 | 17.4213 | -360.3958 | 17.6307 | -360.7435 | 18.144 | -360.802 | 17.5855 | -352.6075 | 18.6881 | -352.6075 | 16.793 | -3.0262 | 358.6779 | 33.0322 | 14.5826 | 12.518 | 22.6304
13:27 | 78 | 34.8323 |  | 8.4009 | 3.2917 | 0.9735 | 3.0581 | -1.6649 | 12.4219 | 5.5656 | 0.6354 | 0.6729 | 0.9809 | 0.7678 | -129.3071 | 4.3548 | 6.4432 | 1.7979 | -2.2655 | -0.8273 | 5.2497 |  | 4.9505 | 0.8319 | 3.9809 | 3.3603 | 3.3283 | 1.1 | 1.9034 | 22.7965 | 22.6313 | 22.3969 | 22.3688 | 22.278 | 22.3015 | 22.169 | 22.9367 | 22.6509 | 22.6907 | 22.6869 | 23.4686 | 23.0216 | 22.9511 | 22.9113 | 22.7976 | 22.6845 | 22.6167 | 22.5316 | 22.3824 | 22.3881 | 22.2872 | 22.9275 | 22.5592 | 22.5938 | 22.5779 | 22.8931 | 23.1783 | 22.6954 | 22.9461 | 23.0675 | 23.3227 | 23.5248 | 22.8877 | 22.9223 | 22.8773 | 22.8222 | 22.7344 | 22.6943 | 22.4974 | 22.2768 | 23.2956 | 22.6653 | 22.7635 | 22.9776 | 23.7048 | 23.3263 | 23.2791 | 23.2896 | 23.2468 | 23.8911 | 23.0633 | 23.0849 | 23.1235 | 23.081 | 23.002 | 22.9703 | 22.8786 | 22.7365 | 23.0016 | 22.8755 | 23.1617 | 23.1827 | 23.1655 | 23.0831 | 23.6247 | 23.8378 | 23.7435 | 23.7513 | 23.6932 | 24.2654 | 23.3242 | 23.3889 | 23.4045 | 23.3684 | 23.3748 | 23.4049 | 23.418 | 23.0453 | 22.8295 | 23.3316 | 23.3817 | 23.3546 | 23.3241 | 23.6262 | 39.286 | 65.4113 | 25.1523 | 28.4571 | 29.1574 | 30.1336 | 29.1542 | 41.7393 | 35.2972 | 42.5221 | 92.0913 | 90.1697 | 80.1787 | 76.3685 | 74.3565 | 77.5114 | 64.4016 | 80.4832 | 25.0237 | 24.1659 | 25.7019 | 24.6269 | 22.6628 | 22.5617 |  | 22.3184 | 22.2883 | 22.2205 | 22.1817 | 22.1299 | 22.1999 | 23.188 | 22.5286 | 22.4477 | 23.4352 | 22.4625 | 22.7145 | 23.0116 | 22.9106 | 22.8497 | 22.7622 | 22.6889 | 22.6574 | 22.596 | 22.6054 | 23.663 | 22.7412 | 22.7414 | 23.7662 | 23.3128 | 23.7836 | 22.8964 | 23.0725 | 23.4547 | 23.8904 | 22.9404 | 22.9755 | 22.9496 | 22.906 | 22.8427 | 22.6942 | 22.6469 | 22.5831 | 23.6252 | 22.5994 | 22.7157 | 22.9411 | 23.9958 | 23.8517 | 23.8051 | 23.7174 | 23.6493 | 23.8953 | 23.7777 | 23.7462 | 23.6583 | 23.5819 | 23.4576 | 23.3762 | 23.0661 | 22.9209 | 22.9716 | 22.9515 | 23.7057 | 23.6151 | 23.5557 | 23.5081 | 24.0866 | 24.1422 | 24.0509 | 23.9374 | 23.8634 | 26.4404 | 23.6284 | 23.8513 | 23.7857 | 23.7007 | 23.6333 | 23.6512 | 23.7029 | 23.0981 | 22.9878 | 24.1224 | 24.0269 | 24.0267 | 23.9676 | 24.52 | 29.6475 | 35.0512 | 38.6311 | 33.3131 | 33.2407 | 36.6938 | 37.8524 | 33.2986 | 40.995 | 35.9642 |  | 34.6678 | 29.6185 | 35.6989 | 24.6855 | 23.4251 | 23.4503 | 24.5894 | 23.4438 | 21.8696 | 22.5907 | 10.8137 | 14.2746 | 14.8522 | 11.0858 | 0.00037515 | -0.0025379 | 0.0015043 | 0.0044162 | 0.0012567 | -0.00089456 | 0.031387 | -0.0092949 | -0.017218 | -360.1619 | 17.4233 | -360.4666 | 17.6861 | -360.8574 | 18.1912 | -360.8143 | 17.5691 | -352.5798 | 18.682 | -352.6629 | 16.8566 | 9.7549 | 367.8796 | 33.3829 | 14.5634 | 12.5352 | 22.6567
13:27 | 79 | 34.7382 |  | 8.3753 | 3.2287 | 0.8631 | 2.9946 | -1.7099 | 12.4896 | 5.5269 | 0.6353 | 0.6726 | 0.9814 | 0.7659 | -129.3701 | 4.244 | 6.3817 | 1.5831 | -2.2789 | -0.7987 | 5.0681 |  | 4.8795 | 0.7797 | 3.982 | 3.3648 | 3.3287 | 1.1007 | 0.9003 | 22.8127 | 22.6393 | 22.3999 | 22.3717 | 22.2796 | 22.3076 | 22.1702 | 22.9339 | 22.6518 | 22.6891 | 22.6917 | 23.4943 | 23.0313 | 22.9485 | 22.9103 | 22.7965 | 22.6862 | 22.6124 | 22.536 | 22.3854 | 22.3924 | 22.2844 | 22.9281 | 22.554 | 22.5921 | 22.5748 | 22.9014 | 23.1737 | 22.6949 | 22.9429 | 23.0729 | 23.3433 | 23.5338 | 22.8991 | 22.9245 | 22.8795 | 22.8262 | 22.7387 | 22.6981 | 22.4902 | 22.2832 | 23.3009 | 22.6773 | 22.7687 | 22.9857 | 23.718 | 23.3163 | 23.2734 | 23.2853 | 23.2443 | 23.907 | 23.0498 | 23.0806 | 23.1184 | 23.0786 | 22.9959 | 22.9751 | 22.8809 | 22.7298 | 23.0101 | 22.8666 | 23.1542 | 23.1832 | 23.1574 | 23.0786 | 23.6381 | 23.8338 | 23.7376 | 23.7479 | 23.6864 | 24.2833 | 23.3186 | 23.3862 | 23.3998 | 23.3642 | 23.3721 | 23.4064 | 23.4106 | 23.0507 | 22.8316 | 23.3351 | 23.3791 | 23.3528 | 23.3204 | 23.6382 | 39.4098 | 66.6289 | 25.185 | 28.5295 | 29.4473 | 30.4182 | 29.3324 | 42.0393 | 35.6151 | 42.9947 | 94.0786 | 90.2136 | 82.3888 | 75.9244 | 73.5895 | 78.3956 | 62.4108 | 79.784 | 25.1372 | 24.2459 | 25.8438 | 24.7465 | 22.6613 | 22.558 |  | 22.3162 | 22.2913 | 22.2165 | 22.1797 | 22.1328 | 22.2016 | 23.1872 | 22.522 | 22.4475 | 23.4554 | 22.4609 | 22.7092 | 23.0074 | 22.9093 | 22.8493 | 22.7519 | 22.6854 | 22.6474 | 22.5937 | 22.6043 | 23.6669 | 22.743 | 22.7416 | 23.7596 | 23.3318 | 23.7858 | 22.8891 | 23.0763 | 23.4732 | 23.8871 | 22.9407 | 22.9769 | 22.949 | 22.9051 | 22.8482 | 22.6999 | 22.6523 | 22.5863 | 23.6312 | 22.6015 | 22.7173 | 22.9478 | 24.0312 | 23.8647 | 23.805 | 23.7249 | 23.655 | 23.9068 | 23.7816 | 23.7505 | 23.6642 | 23.5896 | 23.4638 | 23.3786 | 23.0847 | 22.9256 | 22.9871 | 22.9577 | 23.704 | 23.6168 | 23.5496 | 23.5055 | 24.1052 | 24.1469 | 24.0485 | 23.94 | 23.8637 | 26.4913 | 23.6224 | 23.8451 | 23.7881 | 23.6981 | 23.6323 | 23.6527 | 23.7035 | 23.0963 | 22.9875 | 24.1189 | 24.0257 | 24.0149 | 23.9641 | 24.5416 | 29.8861 | 35.2132 | 38.6962 | 33.4773 | 33.5547 | 37.0732 | 38.4316 | 33.4669 | 41.3959 | 36.2768 |  | 34.9889 | 29.8955 | 36.0607 | 24.6871 | 23.4238 | 23.4418 | 24.6539 | 23.4807 | 21.8768 | 22.5997 | 10.8193 | 14.2736 | 14.8955 | 11.1117 | -4.6647e-05 | -0.0027309 | 0.0014362 | 0.0040171 | 0.0011347 | -0.0004449 | 0.016517 | 0.004033 | -0.02233 | -360.1742 | 17.4233 | -360.405 | 17.6122 | -360.7773 | 18.1666 | -360.8327 | 17.6122 | -352.6352 | 18.6717 | -352.5706 | 16.795 | 14.7218 | 360.0562 | 33.7338 | 14.5845 | 12.3003 | 22.6788
13:27 | 80 | 34.6904 |  | 8.3632 | 3.2258 | 0.9443 | 2.9655 | -1.6694 | 12.4788 | 5.6394 | 0.636 | 0.6727 | 0.9836 | 0.7677 | -129.4727 | 4.2793 | 6.3471 | 1.5498 | -2.3027 | -0.9342 | 5.0655 |  | 5.0206 | 0.9377 | 3.9813 | 3.3693 | 3.3283 | 1.1011 | 2.2462 | 22.8175 | 22.6435 | 22.4055 | 22.3679 | 22.279 | 22.3108 | 22.1739 | 22.9333 | 22.656 | 22.6903 | 22.6931 | 23.5164 | 23.0316 | 22.9478 | 22.9134 | 22.8001 | 22.6905 | 22.6111 | 22.5388 | 22.3866 | 22.3936 | 22.2818 | 22.9291 | 22.5506 | 22.5904 | 22.5753 | 22.9122 | 23.1729 | 22.6941 | 22.9395 | 23.0622 | 23.35 | 23.5254 | 22.8875 | 22.92 | 22.8836 | 22.8198 | 22.7283 | 22.6967 | 22.4762 | 22.286 | 23.2858 | 22.6715 | 22.7663 | 22.9763 | 23.7356 | 23.3139 | 23.2821 | 23.2888 | 23.241 | 23.9319 | 23.0463 | 23.0758 | 23.1182 | 23.083 | 23.0053 | 22.9789 | 22.8869 | 22.7261 | 23.035 | 22.8744 | 23.1488 | 23.1741 | 23.1609 | 23.0816 | 23.6526 | 23.8294 | 23.7327 | 23.7479 | 23.68 | 24.3061 | 23.3175 | 23.3883 | 23.4054 | 23.363 | 23.3729 | 23.4129 | 23.4085 | 23.0528 | 22.8324 | 23.3343 | 23.376 | 23.3452 | 23.3189 | 23.6576 | 39.4421 | 67.1365 | 25.2107 | 28.6146 | 29.7506 | 30.7168 | 29.504 | 42.3521 | 35.932 | 43.4889 | 95.5624 | 91.313 | 83.8733 | 74.7588 | 69.5859 | 79.3037 | 58.495 | 79.3147 | 25.253 | 24.3209 | 25.9889 | 24.8652 | 22.6701 | 22.5669 |  | 22.3217 | 22.2961 | 22.2199 | 22.1817 | 22.1382 | 22.2121 | 23.1916 | 22.5249 | 22.4515 | 23.4821 | 22.467 | 22.7114 | 23.0001 | 22.9064 | 22.8438 | 22.7421 | 22.6829 | 22.6449 | 22.5925 | 22.6056 | 23.6589 | 22.7408 | 22.7355 | 23.7579 | 23.3507 | 23.7888 | 22.8909 | 23.0712 | 23.4845 | 23.8823 | 22.9366 | 22.976 | 22.9441 | 22.9047 | 22.8484 | 22.6958 | 22.6515 | 22.5807 | 23.6239 | 22.5958 | 22.7109 | 22.9418 | 24.0504 | 23.8674 | 23.799 | 23.7198 | 23.6522 | 23.9123 | 23.7807 | 23.7417 | 23.6616 | 23.5855 | 23.4635 | 23.3771 | 23.0862 | 22.9235 | 22.9959 | 22.9548 | 23.6984 | 23.611 | 23.551 | 23.5037 | 24.1238 | 24.1464 | 24.048 | 23.9417 | 23.8677 | 26.5461 | 23.625 | 23.8421 | 23.7888 | 23.6963 | 23.6327 | 23.6518 | 23.703 | 23.0993 | 22.986 | 24.114 | 24.0231 | 24.0135 | 23.9621 | 24.5661 | 30.163 | 35.8566 | 39.1979 | 33.6616 | 33.8638 | 37.4433 | 39.0089 | 33.6315 | 41.8267 | 36.5858 |  | 35.3374 | 30.177 | 36.4156 | 24.6784 | 23.4219 | 23.4412 | 24.7237 | 23.525 | 21.8877 | 22.6139 | 10.8117 | 14.2866 | 14.8991 | 11.0909 | 0.00010067 | -0.002811 | 0.0014415 | 0.0038831 | 0.0011249 | -0.00065238 | 0.024868 | -0.013338 | -0.011904 | -360.1188 | 17.4007 | -360.3989 | 17.6615 | -360.8297 | 18.1728 | -360.7958 | 17.5671 | -352.5583 | 18.6573 | -352.6044 | 16.8484 | 2.6191 | 365.0726 | 34.0892 | 14.5928 | 12.3853 | 22.7064
13:27 | 81 | 34.7383 |  | 8.3772 | 3.2102 | 0.8506 | 2.9731 | -1.6401 | 12.4488 | 5.6335 | 0.6357 | 0.6741 | 0.9806 | 0.7673 | -129.3944 | 4.236 | 6.4104 | 1.5811 | -2.3213 | -0.9307 | 5.0347 |  | 4.9424 | 0.8335 | 3.9797 | 3.367 | 3.329 | 1.1017 | 2.2728 | 22.8138 | 22.6451 | 22.405 | 22.3658 | 22.2772 | 22.3136 | 22.1748 | 22.9367 | 22.6528 | 22.6929 | 22.6899 | 23.5391 | 23.0317 | 22.9533 | 22.9142 | 22.7945 | 22.6869 | 22.6156 | 22.5332 | 22.3872 | 22.3958 | 22.2859 | 22.9277 | 22.5495 | 22.5861 | 22.5789 | 22.9208 | 23.171 | 22.692 | 22.9383 | 23.0544 | 23.3558 | 23.5056 | 22.8762 | 22.9154 | 22.8801 | 22.8121 | 22.7101 | 22.7022 | 22.4468 | 22.2842 | 23.2693 | 22.6643 | 22.7658 | 22.9646 | 23.7548 | 23.3234 | 23.2811 | 23.2883 | 23.2429 | 23.9559 | 23.0672 | 23.0808 | 23.1219 | 23.08 | 23.0056 | 22.9843 | 22.8969 | 22.7349 | 23.0369 | 22.8779 | 23.1495 | 23.1722 | 23.1622 | 23.0822 | 23.6655 | 23.8252 | 23.7322 | 23.7477 | 23.6823 | 24.3314 | 23.3179 | 23.3871 | 23.4031 | 23.3582 | 23.3708 | 23.413 | 23.4162 | 23.0511 | 22.8351 | 23.335 | 23.3823 | 23.3409 | 23.3219 | 23.675 | 39.8698 | 66.4514 | 25.2399 | 28.707 | 30.0596 | 31.0109 | 29.666 | 42.6759 | 36.2696 | 43.9992 | 96.3135 | 93.2568 | 84.2042 | 74.7455 | 64.5855 | 80.6489 | 59.9706 | 80.1343 | 25.3784 | 24.404 | 26.1302 | 24.9872 | 22.6778 | 22.5742 |  | 22.3247 | 22.2936 | 22.2249 | 22.1829 | 22.1331 | 22.2109 | 23.1945 | 22.5213 | 22.4488 | 23.5018 | 22.4682 | 22.709 | 22.9979 | 22.9012 | 22.8442 | 22.7521 | 22.689 | 22.6488 | 22.6037 | 22.6031 | 23.654 | 22.7415 | 22.7325 | 23.7655 | 23.3735 | 23.7866 | 22.8922 | 23.0688 | 23.497 | 23.8877 | 22.9387 | 22.9763 | 22.9487 | 22.9072 | 22.8546 | 22.7007 | 22.654 | 22.5809 | 23.6252 | 22.5961 | 22.7104 | 22.9413 | 24.0783 | 23.8726 | 23.8045 | 23.7171 | 23.6537 | 23.9229 | 23.7826 | 23.7425 | 23.6635 | 23.588 | 23.4635 | 23.3816 | 23.0991 | 22.9305 | 23.0034 | 22.9586 | 23.7049 | 23.609 | 23.551 | 23.5043 | 24.1394 | 24.1463 | 24.0517 | 23.9387 | 23.8656 | 26.6065 | 23.6299 | 23.8491 | 23.7862 | 23.6957 | 23.6343 | 23.6599 | 23.705 | 23.0992 | 22.9856 | 24.1086 | 24.0168 | 24.0149 | 23.9585 | 24.5936 | 30.3735 | 36.6158 | 39.5563 | 33.8293 | 34.1675 | 37.808 | 39.5892 | 33.8087 | 42.2423 | 36.9107 |  | 35.6939 | 30.4815 | 36.7475 | 24.6847 | 23.4207 | 23.441 | 24.7983 | 23.5553 | 21.9046 | 22.6163 | 10.8144 | 14.2826 | 14.8826 | 11.1282 | 0.00040996 | -0.0031881 | 0.0014224 | 0.0040508 | 0.0014514 | 3.4082e-05 | 0.025692 | -0.0063114 | -0.013906 | -360.2388 | 17.4439 | -360.4481 | 17.6204 | -360.762 | 18.1687 | -360.8358 | 17.6328 | -352.6967 | 18.7066 | -352.629 | 16.7991 | -2.2255 | 362.4566 | 34.4448 | 14.5826 | 12.2979 | 22.7299
13:27 | 82 | 34.7813 |  | 8.3829 | 3.1915 | 0.6631 | 3.0381 | -1.5231 | 12.5225 | 5.6157 | 0.6357 | 0.6734 | 0.979 | 0.7683 | -129.3627 | 4.2393 | 6.4198 | 1.5463 | -2.3061 | -1.0342 | 5.0255 |  | 4.9662 | 0.8327 | 3.9809 | 3.3685 | 3.3256 | 1.1018 | 2.152 | 22.81 | 22.6471 | 22.4029 | 22.3704 | 22.2822 | 22.3182 | 22.1732 | 22.9373 | 22.6545 | 22.6976 | 22.6868 | 23.5695 | 23.0366 | 22.9545 | 22.9075 | 22.794 | 22.6823 | 22.6175 | 22.5359 | 22.3857 | 22.3976 | 22.2887 | 22.9264 | 22.5511 | 22.5842 | 22.5743 | 22.9302 | 23.1777 | 22.6918 | 22.9379 | 23.0541 | 23.3689 | 23.5145 | 22.8804 | 22.9178 | 22.8821 | 22.812 | 22.6966 | 22.707 | 22.4499 | 22.2809 | 23.2731 | 22.6598 | 22.7671 | 22.9686 | 23.7768 | 23.3327 | 23.2759 | 23.2886 | 23.2505 | 23.9743 | 23.0806 | 23.0872 | 23.1261 | 23.0736 | 23.0088 | 22.9849 | 22.9104 | 22.7421 | 23.0421 | 22.88 | 23.1542 | 23.1759 | 23.1609 | 23.0836 | 23.6821 | 23.8266 | 23.7346 | 23.7517 | 23.687 | 24.357 | 23.3218 | 23.384 | 23.4015 | 23.3565 | 23.3729 | 23.4128 | 23.4202 | 23.0525 | 22.8373 | 23.3321 | 23.3935 | 23.3461 | 23.3221 | 23.6878 | 39.9939 | 66.3145 | 25.3131 | 28.8205 | 30.3748 | 31.3014 | 29.8226 | 42.9971 | 36.6111 | 44.5106 | 96.6423 | 95.1213 | 83.0221 | 76.1069 | 61.8587 | 83.0298 | 64.845 | 82.6906 | 25.5032 | 24.4852 | 26.277 | 25.1023 | 22.6816 | 22.577 |  | 22.3251 | 22.2937 | 22.2222 | 22.182 | 22.1375 | 22.2037 | 23.1938 | 22.5167 | 22.4493 | 23.5231 | 22.4606 | 22.7085 | 23.0025 | 22.9007 | 22.8459 | 22.7524 | 22.6901 | 22.6506 | 22.6026 | 22.6028 | 23.6603 | 22.7414 | 22.7339 | 23.7636 | 23.403 | 23.7905 | 22.8914 | 23.0723 | 23.5152 | 23.8913 | 22.9403 | 22.9823 | 22.9556 | 22.9093 | 22.8644 | 22.7028 | 22.6541 | 22.5854 | 23.6291 | 22.5977 | 22.7187 | 22.9446 | 24.1161 | 23.8692 | 23.8063 | 23.7187 | 23.6552 | 23.9346 | 23.7874 | 23.752 | 23.6652 | 23.5913 | 23.4674 | 23.3879 | 23.0893 | 22.9344 | 23.0075 | 22.9578 | 23.7024 | 23.6102 | 23.5561 | 23.5085 | 24.1537 | 24.1495 | 24.0537 | 23.9365 | 23.8612 | 26.6657 | 23.6259 | 23.8526 | 23.778 | 23.6976 | 23.6345 | 23.6584 | 23.7099 | 23.0973 | 22.9849 | 24.1138 | 24.0189 | 24.0109 | 23.9586 | 24.6229 | 30.5449 | 36.8157 | 39.492 | 33.9378 | 34.478 | 38.1976 | 40.1957 | 33.9948 | 42.6515 | 37.2325 |  | 36.0452 | 30.7893 | 37.08 | 24.6729 | 23.4209 | 23.4419 | 24.8781 | 23.5957 | 21.9092 | 22.6321 | 10.8426 | 14.2756 | 14.8826 | 11.1353 | -3.6716e-05 | -0.0030942 | 0.0013521 | 0.0037451 | 0.0013109 | -0.00074116 | 0.014102 | 0.002811 | -0.026459 | -360.1188 | 17.4028 | -360.4204 | 17.6451 | -360.8297 | 18.183 | -360.8327 | 17.5712 | -352.5336 | 18.6553 | -352.589 | 16.8217 | 3.5564 | 363.0614 | 34.8077 | 14.5791 | 12.2763 | 22.7524
13:27 | 83 | 34.6314 |  | 8.4456 | 3.2107 | 0.7513 | 2.9323 | -1.6483 | 12.4461 | 5.5585 | 0.6354 | 0.6751 | 0.9826 | 0.7698 | -129.4094 | 4.3073 | 6.3459 | 1.637 | -2.4368 | -1.0846 | 5.0502 |  | 4.9892 | 0.8482 | 3.9813 | 3.3685 | 3.329 | 1.1019 | 0.9434 | 22.8068 | 22.6431 | 22.4047 | 22.373 | 22.2826 | 22.3163 | 22.1729 | 22.9338 | 22.6563 | 22.6986 | 22.688 | 23.5966 | 23.0336 | 22.9482 | 22.9067 | 22.7977 | 22.6899 | 22.6201 | 22.5475 | 22.3887 | 22.396 | 22.29 | 22.9263 | 22.5529 | 22.5867 | 22.5732 | 22.9388 | 23.1821 | 22.6926 | 22.9401 | 23.0469 | 23.3767 | 23.5218 | 22.8746 | 22.9148 | 22.879 | 22.8056 | 22.7042 | 22.7096 | 22.4562 | 22.2724 | 23.274 | 22.6577 | 22.7596 | 22.9683 | 23.7858 | 23.3263 | 23.2741 | 23.2846 | 23.249 | 23.9897 | 23.0708 | 23.0747 | 23.1206 | 23.0733 | 23.0067 | 22.9767 | 22.9072 | 22.7424 | 23.0643 | 22.8822 | 23.1565 | 23.1774 | 23.1658 | 23.0816 | 23.7045 | 23.8302 | 23.7334 | 23.7536 | 23.6916 | 24.3832 | 23.3244 | 23.3869 | 23.4092 | 23.367 | 23.3785 | 23.4205 | 23.4247 | 23.054 | 22.8374 | 23.3364 | 23.3871 | 23.3443 | 23.3186 | 23.706 | 39.9336 | 66.8509 | 25.3949 | 28.97 | 30.7002 | 31.6034 | 29.9815 | 43.3284 | 36.9535 | 45.0708 | 95.9247 | 96.7178 | 78.7888 | 76.5597 | 64.6057 | 85.8027 | 69.1387 | 84.8429 | 25.6378 | 24.5664 | 26.4332 | 25.2199 | 22.6763 | 22.573 |  | 22.321 | 22.2944 | 22.2239 | 22.1745 | 22.1409 | 22.2058 | 23.1923 | 22.5182 | 22.4449 | 23.5514 | 22.4566 | 22.7052 | 23.0072 | 22.9074 | 22.8474 | 22.7506 | 22.6885 | 22.6556 | 22.6006 | 22.6131 | 23.6632 | 22.7432 | 22.7393 | 23.7702 | 23.4403 | 23.7894 | 22.8924 | 23.0728 | 23.5277 | 23.8848 | 22.9392 | 22.9741 | 22.9583 | 22.9093 | 22.8599 | 22.6964 | 22.6497 | 22.5874 | 23.6185 | 22.5949 | 22.7086 | 22.938 | 24.156 | 23.863 | 23.8059 | 23.7221 | 23.6524 | 23.9395 | 23.7957 | 23.7504 | 23.6672 | 23.588 | 23.4673 | 23.3861 | 23.0843 | 22.9352 | 23.0159 | 22.9593 | 23.7007 | 23.6136 | 23.5557 | 23.5064 | 24.1734 | 24.1438 | 24.0523 | 23.9388 | 23.8625 | 26.7266 | 23.627 | 23.8526 | 23.7796 | 23.7018 | 23.6376 | 23.6592 | 23.7065 | 23.0994 | 22.9833 | 24.1134 | 24.019 | 24.0127 | 23.9566 | 24.6493 | 30.7422 | 36.8745 | 39.6964 | 34.0497 | 34.8012 | 38.623 | 40.8296 | 34.1788 | 43.0565 | 37.5666 |  | 36.4122 | 31.117 | 37.4116 | 24.6766 | 23.4171 | 23.4385 | 24.96 | 23.6387 | 21.9212 | 22.6557 | 10.832 | 14.2367 | 14.8643 | 11.0897 | -1.619e-05 | -0.0024379 | 0.0015597 | 0.0045184 | 0.0014501 | -0.00032185 | 0.032218 | -0.0031175 | 0.0060876 | -360.1773 | 17.45 | -360.4142 | 17.602 | -360.7312 | 18.1276 | -360.7866 | 17.6061 | -352.626 | 18.7025 | -352.6136 | 16.793 | 14.1921 | 365.147 | 35.1873 | 14.5505 | 12.2098 | 22.7799
13:27 | 84 | 34.5477 |  | 8.4262 | 3.1658 | 0.8408 | 2.9577 | -1.6431 | 12.4409 | 5.5208 | 0.6353 | 0.6726 | 0.9821 | 0.7675 | -129.3912 | 4.2046 | 6.3924 | 1.7589 | -2.3654 | -1.0082 | 5.0516 |  | 4.9442 | 0.8799 | 3.9818 | 3.3677 | 3.327 | 1.1008 | 1.2654 | 22.8079 | 22.6349 | 22.4002 | 22.3645 | 22.2759 | 22.3118 | 22.1667 | 22.9314 | 22.6481 | 22.6956 | 22.687 | 23.6171 | 23.0221 | 22.9411 | 22.9035 | 22.7957 | 22.6892 | 22.6238 | 22.5458 | 22.3886 | 22.397 | 22.2886 | 22.9253 | 22.5538 | 22.5856 | 22.5736 | 22.9512 | 23.1768 | 22.6888 | 22.9371 | 23.0508 | 23.3956 | 23.517 | 22.8758 | 22.9135 | 22.8798 | 22.808 | 22.7104 | 22.7188 | 22.4632 | 22.2787 | 23.283 | 22.6672 | 22.7665 | 22.9733 | 23.7942 | 23.3179 | 23.2722 | 23.2827 | 23.2421 | 24.0125 | 23.0635 | 23.0642 | 23.1115 | 23.0689 | 23.007 | 22.9762 | 22.91 | 22.7509 | 23.063 | 22.8769 | 23.1543 | 23.1757 | 23.1606 | 23.0757 | 23.7264 | 23.8343 | 23.7322 | 23.7472 | 23.6906 | 24.4039 | 23.317 | 23.3858 | 23.4079 | 23.3673 | 23.3773 | 23.4232 | 23.4259 | 23.0552 | 22.8326 | 23.3324 | 23.3796 | 23.3423 | 23.3168 | 23.7198 | 40.0891 | 67.5845 | 25.4318 | 29.0997 | 31.0321 | 31.9201 | 30.1459 | 43.6882 | 37.3419 | 45.6554 | 96.0173 | 97.8939 | 74.5023 | 77.8044 | 71.2209 | 87.8769 | 74.065 | 86.3246 | 25.7889 | 24.6529 | 26.5888 | 25.3506 | 22.6792 | 22.5721 |  | 22.3201 | 22.297 | 22.2264 | 22.1805 | 22.1417 | 22.2124 | 23.1919 | 22.5247 | 22.4471 | 23.5855 | 22.4638 | 22.7091 | 23.0077 | 22.9094 | 22.8522 | 22.7692 | 22.6859 | 22.6566 | 22.6113 | 22.6207 | 23.6647 | 22.7473 | 22.7431 | 23.7724 | 23.4633 | 23.7885 | 22.8893 | 23.0752 | 23.5473 | 23.8919 | 22.941 | 22.9814 | 22.9662 | 22.9162 | 22.8664 | 22.7064 | 22.6636 | 22.5919 | 23.6265 | 22.6031 | 22.7157 | 22.9458 | 24.1923 | 23.8676 | 23.8104 | 23.7258 | 23.6539 | 23.9463 | 23.801 | 23.7529 | 23.6767 | 23.5891 | 23.4638 | 23.393 | 23.1042 | 22.942 | 23.0356 | 22.967 | 23.7096 | 23.6195 | 23.554 | 23.5048 | 24.1946 | 24.1402 | 24.0543 | 23.9406 | 23.866 | 26.7797 | 23.6306 | 23.8525 | 23.7864 | 23.7017 | 23.6395 | 23.6638 | 23.7003 | 23.0967 | 22.9775 | 24.1078 | 24.0162 | 24.017 | 23.9582 | 24.6666 | 30.9039 | 36.8912 | 39.9471 | 34.2152 | 35.1189 | 39.0758 | 41.4636 | 34.3422 | 43.4295 | 37.9243 |  | 36.7845 | 31.4597 | 37.7429 | 24.676 | 23.421 | 23.4438 | 25.0405 | 23.6811 | 21.9295 | 22.6778 | 10.7911 | 14.2663 | 14.8801 | 11.1051 | 0.00018248 | -0.0029211 | 0.0012893 | 0.004623 | 0.0010854 | -0.00052246 | 0.026231 | -0.0021885 | -0.022195 | -360.1311 | 17.4151 | -360.4235 | 17.6553 | -360.8697 | 18.2118 | -360.8389 | 17.5896 | -352.5921 | 18.682 | -352.6413 | 16.8443 | 15.4632 | 359.5697 | 35.5747 | 14.5732 | 12.291 | 22.8053
13:27 | 85 | 34.5784 |  | 8.3917 | 3.1236 | 0.9413 | 2.9557 | -1.6101 | 12.5259 | 5.6217 | 0.635 | 0.6787 | 0.9816 | 0.7701 | -129.4687 | 4.201 | 6.3906 | 1.6298 | -2.3935 | -0.8945 | 5.0339 |  | 4.9658 | 0.8921 | 3.981 | 3.3674 | 3.329 | 1.1012 | 2.1496 | 22.8116 | 22.6329 | 22.3973 | 22.3611 | 22.2705 | 22.3146 | 22.1656 | 22.9354 | 22.6517 | 22.6937 | 22.6849 | 23.6475 | 23.0206 | 22.9458 | 22.904 | 22.8035 | 22.6842 | 22.6191 | 22.5415 | 22.388 | 22.3976 | 22.2909 | 22.9291 | 22.5597 | 22.5924 | 22.5724 | 22.9682 | 23.1775 | 22.6891 | 22.9437 | 23.0551 | 23.4125 | 23.5144 | 22.8767 | 22.9125 | 22.8856 | 22.8119 | 22.7036 | 22.7293 | 22.4667 | 22.2847 | 23.2859 | 22.667 | 22.7716 | 22.9806 | 23.8132 | 23.32 | 23.2694 | 23.2832 | 23.2444 | 24.0389 | 23.0643 | 23.0738 | 23.1143 | 23.0632 | 23.0091 | 22.9858 | 22.9227 | 22.7545 | 23.0573 | 22.8723 | 23.1446 | 23.1782 | 23.1585 | 23.0761 | 23.7471 | 23.8269 | 23.7317 | 23.7445 | 23.6856 | 24.424 | 23.3193 | 23.3829 | 23.4047 | 23.3609 | 23.374 | 23.4211 | 23.4307 | 23.0566 | 22.8317 | 23.3179 | 23.3787 | 23.3446 | 23.317 | 23.7266 | 40.6105 | 67.9709 | 25.4717 | 29.1726 | 31.3699 | 32.2565 | 30.3182 | 44.0689 | 37.7732 | 46.2316 | 98.1791 | 98.4497 | 75.934 | 80.8271 | 76.5711 | 89.6709 | 77.7443 | 88.1213 | 25.9371 | 24.7341 | 26.7344 | 25.476 | 22.684 | 22.5742 |  | 22.3233 | 22.2924 | 22.2261 | 22.19 | 22.1427 | 22.2124 | 23.1906 | 22.5263 | 22.4506 | 23.6136 | 22.4644 | 22.7056 | 23.0034 | 22.905 | 22.8488 | 22.7555 | 22.6879 | 22.6542 | 22.6101 | 22.619 | 23.6613 | 22.7418 | 22.7389 | 23.7617 | 23.4842 | 23.7887 | 22.8875 | 23.0821 | 23.5669 | 23.9036 | 22.9464 | 22.9926 | 22.9654 | 22.925 | 22.8804 | 22.7173 | 22.6748 | 22.6 | 23.638 | 22.6067 | 22.7289 | 22.9554 | 24.2251 | 23.868 | 23.8092 | 23.7221 | 23.6563 | 23.959 | 23.7897 | 23.7505 | 23.6669 | 23.5893 | 23.4619 | 23.3889 | 23.1138 | 22.944 | 23.0399 | 22.9737 | 23.7066 | 23.6154 | 23.551 | 23.5028 | 24.2133 | 24.1351 | 24.0506 | 23.9384 | 23.8644 | 26.8365 | 23.6326 | 23.847 | 23.7812 | 23.696 | 23.6362 | 23.662 | 23.7123 | 23.109 | 22.9877 | 24.1251 | 24.0212 | 24.0235 | 23.9666 | 24.6975 | 31.1151 | 36.858 | 39.9616 | 34.4401 | 35.4377 | 39.555 | 42.104 | 34.4956 | 43.7756 | 38.2777 |  | 37.166 | 31.8089 | 38.0653 | 24.6779 | 23.4217 | 23.4423 | 25.12 | 23.7263 | 21.9393 | 22.6967 | 10.8207 | 14.2821 | 14.876 | 11.1342 | 0.00045769 | -0.0029089 | 0.0012829 | 0.0042393 | 0.0018001 | -0.00057505 | 0.019163 | -0.0040654 | -0.010949 | -360.1681 | 17.4521 | -360.4666 | 17.6163 | -360.7589 | 18.1337 | -360.7835 | 17.5917 | -352.6321 | 18.7107 | -352.6413 | 16.8012 | 11.4558 | 368.5588 | 35.9704 | 14.579 | 12.355 | 22.8328
13:27 | 86 | 34.4637 |  | 8.4754 | 3.1958 | 0.9509 | 3.046 | -1.6341 | 12.5049 | 5.4655 | 0.6345 | 0.6748 | 0.9846 | 0.7688 | -129.5284 | 4.1804 | 6.5095 | 1.6228 | -2.436 | -1.085 | 4.923 |  | 4.928 | 0.9685 | 3.9796 | 3.3654 | 3.326 | 1.1009 | 1.7438 | 22.8112 | 22.6311 | 22.4018 | 22.3638 | 22.2705 | 22.3204 | 22.1669 | 22.9304 | 22.6531 | 22.6938 | 22.6863 | 23.6758 | 23.0249 | 22.9471 | 22.9022 | 22.8001 | 22.6858 | 22.6108 | 22.5491 | 22.3876 | 22.4045 | 22.2909 | 22.9223 | 22.5536 | 22.5928 | 22.5693 | 22.977 | 23.1733 | 22.6925 | 22.9463 | 23.0573 | 23.4222 | 23.5056 | 22.8754 | 22.9141 | 22.8885 | 22.813 | 22.7068 | 22.7333 | 22.4633 | 22.2831 | 23.276 | 22.6673 | 22.7672 | 22.9806 | 23.8357 | 23.3194 | 23.2674 | 23.2831 | 23.2519 | 24.0607 | 23.0729 | 23.0828 | 23.123 | 23.0747 | 23.0024 | 22.9883 | 22.9224 | 22.7508 | 23.0695 | 22.8777 | 23.1406 | 23.184 | 23.1604 | 23.0789 | 23.7736 | 23.8263 | 23.7344 | 23.7478 | 23.6885 | 24.4527 | 23.3227 | 23.3868 | 23.4029 | 23.3674 | 23.3797 | 23.4262 | 23.431 | 23.0604 | 22.8353 | 23.3173 | 23.3745 | 23.3464 | 23.3146 | 23.7455 | 40.929 | 68.5039 | 25.5201 | 29.2086 | 31.7119 | 32.6027 | 30.5001 | 44.4573 | 38.2084 | 46.8038 | 99.7988 | 99.017 | 80.8191 | 82.8035 | 80.7973 | 90.3699 | 81.655 | 90.5286 | 26.0761 | 24.8165 | 26.8779 | 25.5958 | 22.6785 | 22.5813 |  | 22.32 | 22.2874 | 22.2232 | 22.1876 | 22.1458 | 22.2101 | 23.1893 | 22.5214 | 22.4472 | 23.6342 | 22.4654 | 22.7057 | 23.0008 | 22.9017 | 22.8436 | 22.7457 | 22.69 | 22.6533 | 22.619 | 22.6216 | 23.6608 | 22.745 | 22.742 | 23.7654 | 23.5142 | 23.7857 | 22.8915 | 23.0755 | 23.5728 | 23.9002 | 22.9452 | 22.9845 | 22.9552 | 22.9183 | 22.8745 | 22.7122 | 22.6679 | 22.5965 | 23.6285 | 22.5993 | 22.7155 | 22.952 | 24.2607 | 23.8647 | 23.8062 | 23.7269 | 23.6612 | 23.9736 | 23.7894 | 23.7479 | 23.6589 | 23.5907 | 23.4615 | 23.3837 | 23.1062 | 22.9465 | 23.0319 | 22.9798 | 23.6977 | 23.6128 | 23.55 | 23.501 | 24.2327 | 24.1381 | 24.046 | 23.9369 | 23.86 | 26.8956 | 23.6321 | 23.8451 | 23.7734 | 23.6942 | 23.6322 | 23.6674 | 23.7281 | 23.124 | 23.0004 | 24.1316 | 24.0254 | 24.0259 | 23.967 | 24.7295 | 31.312 | 36.8043 | 39.8032 | 34.684 | 35.7575 | 40.0332 | 42.7501 | 34.647 | 44.1163 | 38.6321 |  | 37.5422 | 32.173 | 38.3698 | 24.6818 | 23.4193 | 23.4413 | 25.1964 | 23.7767 | 21.9535 | 22.7121 | 10.834 | 14.2745 | 14.9117 | 11.0838 | 0.00038785 | -0.0029585 | 0.0015416 | 0.0043337 | 0.0010953 | -0.00019745 | 0.010915 | -0.00033811 | -0.0098527 | -360.1004 | 17.3905 | -360.3804 | 17.643 | -360.8389 | 18.1933 | -360.842 | 17.565 | -352.5644 | 18.6512 | -352.6229 | 16.8299 | 18.2081 | 364.1365 | 36.3676 | 14.5931 | 12.2777 | 22.8651
13:27 | 87 | 34.4407 |  | 8.4091 | 3.1462 | 0.8115 | 2.9414 | -1.5899 | 12.507 | 5.5377 | 0.6356 | 0.679 | 0.9791 | 0.7689 | -129.5176 | 4.1739 | 6.4157 | 1.7445 | -2.4882 | -1.1023 | 4.9346 |  | 4.9246 | 0.9714 | 3.9808 | 3.3691 | 3.3275 | 1.1018 | 1.3112 | 22.8178 | 22.6445 | 22.4097 | 22.3697 | 22.2765 | 22.3306 | 22.1714 | 22.9349 | 22.656 | 22.705 | 22.6932 | 23.7108 | 23.032 | 22.9532 | 22.9005 | 22.7902 | 22.6853 | 22.6085 | 22.5543 | 22.3883 | 22.4144 | 22.2928 | 22.9213 | 22.5478 | 22.5874 | 22.5693 | 22.9861 | 23.1741 | 22.6915 | 22.9456 | 23.0561 | 23.4342 | 23.5037 | 22.8794 | 22.9156 | 22.8851 | 22.8123 | 22.7053 | 22.7344 | 22.4618 | 22.2816 | 23.2771 | 22.6678 | 22.768 | 22.9867 | 23.8593 | 23.3219 | 23.2688 | 23.2845 | 23.2523 | 24.0799 | 23.0719 | 23.0777 | 23.1239 | 23.0808 | 23.0024 | 22.9832 | 22.9402 | 22.7506 | 23.0662 | 22.8833 | 23.1419 | 23.1828 | 23.1584 | 23.075 | 23.7967 | 23.8299 | 23.7356 | 23.7504 | 23.6936 | 24.4741 | 23.3206 | 23.3862 | 23.4031 | 23.3722 | 23.3813 | 23.4291 | 23.4323 | 23.0628 | 22.8357 | 23.3229 | 23.3761 | 23.3446 | 23.3138 | 23.7684 | 41.1791 | 69.9564 | 25.5773 | 29.2683 | 32.0709 | 32.9544 | 30.6726 | 44.8289 | 38.6277 | 47.341 | 100.1864 | 100.7661 | 84.9321 | 84.5825 | 84.2275 | 89.7547 | 86.3091 | 93.422 | 26.2315 | 24.9062 | 27.0246 | 25.7213 | 22.6769 | 22.5875 |  | 22.3196 | 22.2885 | 22.2153 | 22.1806 | 22.1472 | 22.2084 | 23.1906 | 22.5249 | 22.447 | 23.6565 | 22.4691 | 22.707 | 22.9975 | 22.903 | 22.8417 | 22.7488 | 22.6838 | 22.6503 | 22.6213 | 22.6283 | 23.6582 | 22.7525 | 22.7461 | 23.762 | 23.5398 | 23.7859 | 22.8945 | 23.0677 | 23.5769 | 23.8954 | 22.9371 | 22.9771 | 22.9543 | 22.9104 | 22.8721 | 22.7079 | 22.6667 | 22.5951 | 23.6262 | 22.5946 | 22.7109 | 22.9475 | 24.297 | 23.8611 | 23.8056 | 23.7259 | 23.6603 | 23.9816 | 23.7897 | 23.7484 | 23.6628 | 23.5875 | 23.4606 | 23.3887 | 23.1018 | 22.9453 | 23.0437 | 22.9798 | 23.6957 | 23.615 | 23.5544 | 23.5115 | 24.258 | 24.1528 | 24.0531 | 23.9429 | 23.8641 | 26.9519 | 23.6285 | 23.8506 | 23.7787 | 23.702 | 23.6352 | 23.6688 | 23.7351 | 23.1264 | 23.0044 | 24.1271 | 24.0292 | 24.0227 | 23.9686 | 24.763 | 31.4064 | 36.7237 | 39.7661 | 34.8737 | 36.0807 | 40.4932 | 43.4063 | 34.8135 | 44.477 | 38.9819 |  | 37.9308 | 32.5348 | 38.6866 | 24.6807 | 23.4152 | 23.4427 | 25.2721 | 23.8199 | 21.9673 | 22.7343 | 10.8258 | 14.2936 | 14.892 | 11.119 | -0.00046348 | -0.0029519 | 0.0011605 | 0.0040007 | 0.0012653 | -0.0010282 | 0.021721 | -0.0053156 | -0.0019296 | -360.1988 | 17.4644 | -360.5035 | 17.6451 | -360.7958 | 18.1502 | -360.7989 | 17.604 | -352.6444 | 18.7189 | -352.6813 | 16.8299 | 21.3692 | 368.053 | 36.7697 | 14.5928 | 12.2243 | 22.8936
13:27 | 88 | 34.4173 |  | 8.4476 | 3.2556 | 1.0009 | 2.9988 | -1.6677 | 12.4681 | 5.3909 | 0.6359 | 0.6763 | 0.9827 | 0.7695 | -129.5287 | 4.0485 | 6.3607 | 1.7725 | -2.4884 | -0.9568 | 4.9705 |  | 4.9275 | 1.0178 | 3.9795 | 3.3682 | 3.3321 | 1.1019 | 1.1972 | 22.823 | 22.6491 | 22.4066 | 22.3721 | 22.2781 | 22.3314 | 22.1714 | 22.9384 | 22.6611 | 22.7047 | 22.6969 | 23.7496 | 23.0386 | 22.9612 | 22.9065 | 22.7968 | 22.6903 | 22.6148 | 22.5507 | 22.3923 | 22.4164 | 22.2957 | 22.9275 | 22.5513 | 22.5922 | 22.5748 | 23.01 | 23.1788 | 22.6948 | 22.9503 | 23.0469 | 23.4444 | 23.5049 | 22.8739 | 22.9085 | 22.8728 | 22.8055 | 22.6955 | 22.7377 | 22.4548 | 22.2782 | 23.2772 | 22.6597 | 22.766 | 22.982 | 23.8823 | 23.3248 | 23.2735 | 23.2878 | 23.2498 | 24.1066 | 23.0734 | 23.0785 | 23.1151 | 23.0777 | 23.0019 | 22.9852 | 22.9542 | 22.7468 | 23.0633 | 22.8837 | 23.1434 | 23.1807 | 23.1602 | 23.0812 | 23.8216 | 23.8271 | 23.7313 | 23.7509 | 23.6942 | 24.4944 | 23.3235 | 23.3869 | 23.4078 | 23.3743 | 23.3799 | 23.4316 | 23.4386 | 23.066 | 22.8381 | 23.3325 | 23.3787 | 23.3437 | 23.3206 | 23.7868 | 41.6154 | 70.9961 | 25.643 | 29.3531 | 32.4343 | 33.3198 | 30.8307 | 45.1849 | 39.0186 | 47.8419 | 101.027 | 102.9089 | 88.136 | 86.0421 | 87.0267 | 89.1342 | 89.3648 | 96.2459 | 26.3928 | 24.9947 | 27.1768 | 25.8452 | 22.6768 | 22.5795 |  | 22.3184 | 22.2845 | 22.2149 | 22.1757 | 22.1461 | 22.2025 | 23.1866 | 22.5249 | 22.4463 | 23.6822 | 22.4663 | 22.7024 | 22.9974 | 22.9012 | 22.8407 | 22.7361 | 22.6871 | 22.6531 | 22.6015 | 22.6291 | 23.6575 | 22.7509 | 22.7457 | 23.7639 | 23.5695 | 23.7884 | 22.895 | 23.0692 | 23.5898 | 23.8943 | 22.934 | 22.9792 | 22.9544 | 22.9071 | 22.8746 | 22.707 | 22.6729 | 22.6042 | 23.6269 | 22.5904 | 22.7112 | 22.9418 | 24.3364 | 23.8712 | 23.811 | 23.7254 | 23.6664 | 23.9894 | 23.7851 | 23.7517 | 23.6655 | 23.5906 | 23.4655 | 23.3971 | 23.1206 | 22.9493 | 23.0591 | 22.9837 | 23.6948 | 23.6162 | 23.5544 | 23.5152 | 24.2757 | 24.146 | 24.06 | 23.9451 | 23.8686 | 27.01 | 23.6325 | 23.8524 | 23.7826 | 23.7036 | 23.636 | 23.6746 | 23.7368 | 23.1256 | 23.0057 | 24.1235 | 24.0244 | 24.0176 | 23.9677 | 24.7917 | 31.532 | 36.6814 | 39.7311 | 35.0304 | 36.4041 | 40.9549 | 44.047 | 35.0008 | 44.8576 | 39.2981 |  | 38.3256 | 32.9082 | 38.9881 | 24.6775 | 23.4242 | 23.4455 | 25.3639 | 23.8617 | 21.9781 | 22.7548 | 10.8495 | 14.283 | 14.9134 | 11.1203 | 0.00032792 | -0.0028546 | 0.0016694 | 0.0043443 | 0.00098809 | -0.00025712 | 0.012463 | -0.017561 | -0.0039599 | -360.0788 | 17.3966 | -360.3927 | 17.643 | -360.842 | 18.1851 | -360.842 | 17.5753 | -352.546 | 18.6409 | -352.5675 | 16.832 | 10.2376 | 360.5196 | 37.1728 | 14.5982 | 12.3412 | 22.9199
13:27 | 89 | 34.3313 |  | 8.3773 | 3.1466 | 0.8741 | 2.9991 | -1.6895 | 12.4902 | 5.4816 | 0.6353 | 0.6727 | 0.9804 | 0.7692 | -129.5216 | 4.0483 | 6.4584 | 1.6256 | -2.4848 | -1.0456 | 4.9238 |  | 4.941 | 0.989 | 3.9799 | 3.3675 | 3.3294 | 1.102 | 2.0768 | 22.8157 | 22.6385 | 22.3958 | 22.3636 | 22.2705 | 22.3216 | 22.165 | 22.9294 | 22.6533 | 22.6898 | 22.6867 | 23.7719 | 23.0325 | 22.9558 | 22.8994 | 22.7977 | 22.686 | 22.6115 | 22.5443 | 22.3821 | 22.4081 | 22.2938 | 22.9181 | 22.5514 | 22.5863 | 22.571 | 23.0242 | 23.1706 | 22.6916 | 22.9437 | 23.0443 | 23.4563 | 23.5059 | 22.865 | 22.9049 | 22.8694 | 22.8009 | 22.6981 | 22.7515 | 22.4711 | 22.2772 | 23.2775 | 22.6642 | 22.7648 | 22.9742 | 23.8985 | 23.3255 | 23.2795 | 23.2869 | 23.2496 | 24.1297 | 23.0688 | 23.0848 | 23.1151 | 23.0769 | 23.0034 | 22.9907 | 22.9534 | 22.7518 | 23.0692 | 22.8887 | 23.1438 | 23.1776 | 23.1645 | 23.0854 | 23.8347 | 23.8296 | 23.7346 | 23.7484 | 23.6898 | 24.521 | 23.3195 | 23.3919 | 23.4049 | 23.3717 | 23.3808 | 23.4342 | 23.439 | 23.0706 | 22.8434 | 23.3283 | 23.3787 | 23.3445 | 23.3178 | 23.8023 | 41.9996 | 70.677 | 25.7207 | 29.4472 | 32.7904 | 33.6736 | 30.9829 | 45.5659 | 39.3627 | 48.3036 | 103.4585 | 104.5299 | 90.9607 | 87.6 | 89.0792 | 88.8186 | 90.9954 | 98.6622 | 26.5507 | 25.0881 | 27.341 | 25.9699 | 22.68 | 22.5856 |  | 22.3177 | 22.2933 | 22.2258 | 22.1856 | 22.1533 | 22.207 | 23.1908 | 22.5262 | 22.4513 | 23.721 | 22.4709 | 22.7155 | 22.9991 | 22.9004 | 22.8434 | 22.7577 | 22.6969 | 22.6581 | 22.6095 | 22.6322 | 23.6631 | 22.7512 | 22.7499 | 23.773 | 23.5992 | 23.7896 | 22.8935 | 23.0761 | 23.6128 | 23.9011 | 22.9461 | 22.9896 | 22.9617 | 22.9145 | 22.8859 | 22.7172 | 22.6824 | 22.616 | 23.6296 | 22.6021 | 22.7132 | 22.9488 | 24.3764 | 23.8746 | 23.8168 | 23.7329 | 23.6724 | 24.0001 | 23.7781 | 23.7526 | 23.6638 | 23.597 | 23.4682 | 23.4056 | 23.1224 | 22.9596 | 23.0541 | 22.9847 | 23.6929 | 23.6135 | 23.5543 | 23.5098 | 24.2904 | 24.1397 | 24.0527 | 23.9387 | 23.863 | 27.0695 | 23.635 | 23.8479 | 23.7822 | 23.6947 | 23.6294 | 23.6749 | 23.7411 | 23.1251 | 23.0042 | 24.1196 | 24.0184 | 24.0128 | 23.9622 | 24.8135 | 31.7574 | 36.6845 | 39.8245 | 35.2239 | 36.7213 | 41.4359 | 44.6601 | 35.1947 | 45.2727 | 39.5903 |  | 38.7376 | 33.2849 | 39.3014 | 24.6808 | 23.4275 | 23.4462 | 25.4536 | 23.9125 | 21.9988 | 22.7859 | 10.8158 | 14.2698 | 14.8829 | 11.0737 | 0.00020299 | -0.0032276 | 0.00145 | 0.0039852 | 0.0011778 | -0.00078439 | 0.023314 | 0.00033652 | -0.030694 | -360.1711 | 17.448 | -360.4327 | 17.6102 | -360.7804 | 18.1255 | -360.7681 | 17.5917 | -352.5798 | 18.7004 | -352.6229 | 16.8094 | 9.9534 | 365.9535 | 37.5757 | 14.5763 | 12.1885 | 22.9556
13:27 | 90 | 34.2405 |  | 8.3181 | 3.2132 | 0.9124 | 2.9606 | -1.7263 | 12.4521 | 5.4848 | 0.635 | 0.6724 | 0.9803 | 0.7701 | -129.6017 | 3.9928 | 6.2893 | 1.7376 | -2.5322 | -0.9444 | 5.024 |  | 4.961 | 0.9673 | 3.9805 | 3.366 | 3.3279 | 1.1003 | 1.1483 | 22.8109 | 22.6377 | 22.3984 | 22.3584 | 22.2682 | 22.3215 | 22.1662 | 22.9285 | 22.653 | 22.6882 | 22.6843 | 23.7938 | 23.0332 | 22.9509 | 22.8908 | 22.7953 | 22.6822 | 22.6073 | 22.5479 | 22.3801 | 22.4075 | 22.2941 | 22.9177 | 22.5489 | 22.5753 | 22.5703 | 23.0344 | 23.1743 | 22.6892 | 22.9393 | 23.0426 | 23.47 | 23.509 | 22.8647 | 22.9059 | 22.8739 | 22.8064 | 22.7096 | 22.7571 | 22.4782 | 22.2715 | 23.2809 | 22.6665 | 22.766 | 22.9775 | 23.912 | 23.3209 | 23.2792 | 23.2799 | 23.2493 | 24.1501 | 23.0551 | 23.0785 | 23.1176 | 23.0797 | 23.0064 | 22.9963 | 22.9484 | 22.753 | 23.0763 | 22.8873 | 23.1391 | 23.1602 | 23.159 | 23.0687 | 23.8408 | 23.8331 | 23.7343 | 23.7426 | 23.686 | 24.5436 | 23.3164 | 23.3864 | 23.4012 | 23.3613 | 23.3768 | 23.429 | 23.4471 | 23.0715 | 22.849 | 23.3148 | 23.3757 | 23.3432 | 23.3126 | 23.8153 | 42.354 | 71.3027 | 25.8832 | 29.5858 | 33.1682 | 34.0312 | 31.1482 | 45.983 | 39.6666 | 48.7494 | 105.9386 | 106.269 | 92.4669 | 89.0697 | 90.8572 | 88.9061 | 92.9025 | 101.0373 | 26.7103 | 25.1833 | 27.5003 | 26.1 | 22.6794 | 22.5883 |  | 22.3185 | 22.2972 | 22.2294 | 22.1827 | 22.1483 | 22.2081 | 23.1898 | 22.5209 | 22.4532 | 23.7523 | 22.4682 | 22.7162 | 22.997 | 22.9064 | 22.8483 | 22.771 | 22.7036 | 22.6574 | 22.6239 | 22.6366 | 23.6637 | 22.7513 | 22.7568 | 23.7687 | 23.6262 | 23.7907 | 22.8951 | 23.0856 | 23.6284 | 23.9006 | 22.9498 | 22.989 | 22.9638 | 22.9153 | 22.8969 | 22.7223 | 22.6853 | 22.6196 | 23.6321 | 22.6082 | 22.7142 | 22.9539 | 24.4158 | 23.8685 | 23.8095 | 23.7286 | 23.6659 | 24.0087 | 23.7764 | 23.746 | 23.6576 | 23.5902 | 23.4639 | 23.4089 | 23.1117 | 22.9561 | 23.0478 | 22.9811 | 23.6942 | 23.6106 | 23.5514 | 23.5086 | 24.3073 | 24.1432 | 24.0456 | 23.9307 | 23.8624 | 27.1323 | 23.6271 | 23.8475 | 23.7825 | 23.6923 | 23.6251 | 23.6693 | 23.7508 | 23.1288 | 23.0038 | 24.1228 | 24.0166 | 24.0123 | 23.9614 | 24.8437 | 32.0245 | 36.7161 | 40.1448 | 35.4625 | 37.0552 | 41.9142 | 45.2898 | 35.4039 | 45.7462 | 39.8691 |  | 39.1663 | 33.6713 | 39.6266 | 24.6665 | 23.425 | 23.4382 | 25.5348 | 23.9587 | 22.0135 | 22.809 | 10.8209 | 14.2604 | 14.9003 | 11.1285 | 0.00025162 | -0.0030099 | 0.0014745 | 0.0046928 | 0.0011372 | -0.00029092 | 0.012964 | -0.011599 | -0.020471 | -360.1558 | 17.409 | -360.4081 | 17.6451 | -360.8727 | 18.2056 | -360.8635 | 17.6102 | -352.5952 | 18.6573 | -352.586 | 16.8361 | 32.8383 | 368.2934 | 37.9903 | 14.5803 | 12.2485 | 22.9861
13:27 | 91 | 34.2564 |  | 8.3545 | 3.2762 | 0.9712 | 3.001 | -1.6905 | 12.4655 | 5.4949 | 0.6362 | 0.6746 | 0.9816 | 0.769 | -129.7075 | 3.8691 | 6.2426 | 1.553 | -2.5274 | -0.9664 | 5.0317 |  | 4.8931 | 0.9092 | 3.9802 | 3.3692 | 3.3288 | 1.0997 | 2.011 | 22.8176 | 22.6382 | 22.3946 | 22.3587 | 22.2683 | 22.3212 | 22.1651 | 22.9292 | 22.652 | 22.6931 | 22.6913 | 23.8237 | 23.0319 | 22.9518 | 22.8883 | 22.7866 | 22.68 | 22.6044 | 22.5469 | 22.3767 | 22.4079 | 22.2863 | 22.92 | 22.5416 | 22.5705 | 22.5697 | 23.039 | 23.1724 | 22.6868 | 22.9393 | 23.0479 | 23.4889 | 23.5099 | 22.8642 | 22.9076 | 22.8782 | 22.8134 | 22.7082 | 22.7599 | 22.4691 | 22.2762 | 23.2883 | 22.6669 | 22.7723 | 22.9855 | 23.934 | 23.3138 | 23.2716 | 23.2815 | 23.249 | 24.1756 | 23.0554 | 23.0767 | 23.1202 | 23.0823 | 23.0042 | 23.0004 | 22.9473 | 22.748 | 23.0888 | 22.887 | 23.1377 | 23.1562 | 23.1558 | 23.0676 | 23.8686 | 23.8347 | 23.7305 | 23.7414 | 23.6872 | 24.5732 | 23.316 | 23.3849 | 23.409 | 23.3642 | 23.3752 | 23.4326 | 23.4526 | 23.0714 | 22.8491 | 23.3139 | 23.3734 | 23.3401 | 23.3148 | 23.8349 | 42.3259 | 73.4144 | 25.9832 | 29.7416 | 33.5483 | 34.3909 | 31.3069 | 46.4046 | 39.9361 | 49.2166 | 107.3172 | 106.163 | 92.0113 | 90.0391 | 92.985 | 89.294 | 95.4363 | 102.38 | 26.8691 | 25.2812 | 27.6647 | 26.2412 | 22.6727 | 22.5769 |  | 22.31 | 22.2841 | 22.2201 | 22.172 | 22.1435 | 22.2072 | 23.1776 | 22.5158 | 22.4476 | 23.7702 | 22.4602 | 22.708 | 22.9937 | 22.9062 | 22.8487 | 22.7718 | 22.7091 | 22.6581 | 22.6325 | 22.6352 | 23.6589 | 22.7465 | 22.7521 | 23.7612 | 23.654 | 23.7886 | 22.8956 | 23.0807 | 23.6336 | 23.8891 | 22.9378 | 22.9812 | 22.9556 | 22.9064 | 22.8934 | 22.7178 | 22.6771 | 22.6098 | 23.6266 | 22.6037 | 22.7047 | 22.9483 | 24.4427 | 23.8654 | 23.8031 | 23.722 | 23.6548 | 24.0139 | 23.7837 | 23.7449 | 23.6591 | 23.5828 | 23.4627 | 23.4103 | 23.1195 | 22.951 | 23.0564 | 22.9856 | 23.6962 | 23.6062 | 23.5486 | 23.5067 | 24.3266 | 24.1378 | 24.0478 | 23.9256 | 23.8619 | 27.1863 | 23.6234 | 23.8452 | 23.7776 | 23.6915 | 23.631 | 23.6745 | 23.7568 | 23.1301 | 23.0068 | 24.1245 | 24.0229 | 24.0157 | 23.9619 | 24.8771 | 32.285 | 36.7871 | 40.3896 | 35.7264 | 37.4147 | 42.3909 | 45.9418 | 35.6162 | 46.24 | 40.1655 |  | 39.5974 | 34.0587 | 39.9454 | 24.6626 | 23.4135 | 23.4341 | 25.6206 | 24.0076 | 22.0218 | 22.8257 | 10.8298 | 14.2915 | 14.9009 | 11.1286 | 0.0002915 | -0.0021636 | 0.0012818 | 0.00459 | 0.0013257 | -0.00081022 | 0.013678 | -0.005072 | -0.021316 | -360.1435 | 17.4356 | -360.4481 | 17.6081 | -360.7589 | 18.1276 | -360.7804 | 17.5917 | -352.6383 | 18.6902 | -352.629 | 16.8074 | 26.8781 | 363.6061 | 38.411 | 14.5962 | 12.2298 | 23.0147
13:27 | 92 | 34.2624 |  | 8.3755 | 3.3003 | 1.024 | 3.0667 | -1.6809 | 12.3815 | 5.482 | 0.6359 | 0.6723 | 0.9795 | 0.7689 | -129.7835 | 3.825 | 6.2423 | 1.5602 | -2.4051 | -0.948 | 5.0288 |  | 4.8723 | 1.0373 | 3.9807 | 3.3679 | 3.3264 | 1.1014 | 2.6277 | 22.8197 | 22.6423 | 22.3888 | 22.3593 | 22.2675 | 22.3206 | 22.1642 | 22.9289 | 22.6451 | 22.6946 | 22.6885 | 23.8628 | 23.0311 | 22.9564 | 22.8936 | 22.7881 | 22.679 | 22.6066 | 22.5487 | 22.3742 | 22.4109 | 22.2947 | 22.9237 | 22.5406 | 22.5763 | 22.5709 | 23.0513 | 23.1626 | 22.6917 | 22.9425 | 23.0534 | 23.5075 | 23.5062 | 22.8627 | 22.9063 | 22.8747 | 22.812 | 22.7049 | 22.7699 | 22.4668 | 22.2852 | 23.2864 | 22.6721 | 22.7752 | 22.9905 | 23.9555 | 23.3147 | 23.2622 | 23.2805 | 23.2463 | 24.1989 | 23.0599 | 23.0763 | 23.1188 | 23.0733 | 22.9975 | 23.0049 | 22.9624 | 22.7558 | 23.0941 | 22.8857 | 23.1408 | 23.1726 | 23.1573 | 23.0755 | 23.8935 | 23.8333 | 23.7349 | 23.743 | 23.6925 | 24.6014 | 23.3172 | 23.3938 | 23.4157 | 23.3665 | 23.3798 | 23.4387 | 23.4538 | 23.0685 | 22.8397 | 23.311 | 23.3723 | 23.3356 | 23.3129 | 23.854 | 42.4205 | 75.0055 | 25.9999 | 29.8964 | 33.9315 | 34.7719 | 31.4611 | 46.8523 | 40.2048 | 49.6988 | 108.4996 | 105.8125 | 90.7298 | 91.467 | 94.8664 | 91.0322 | 97.7251 | 102.1336 | 27.0349 | 25.3804 | 27.8345 | 26.3878 | 22.6713 | 22.5837 |  | 22.3121 | 22.2831 | 22.2213 | 22.1755 | 22.155 | 22.2147 | 23.1841 | 22.5201 | 22.4466 | 23.8018 | 22.4658 | 22.7124 | 22.9953 | 22.9068 | 22.8499 | 22.7638 | 22.7112 | 22.6651 | 22.6284 | 22.6366 | 23.6605 | 22.749 | 22.7477 | 23.7662 | 23.6809 | 23.7887 | 22.8943 | 23.0736 | 23.6465 | 23.8889 | 22.9397 | 22.9818 | 22.9525 | 22.9096 | 22.897 | 22.7219 | 22.6803 | 22.6087 | 23.6267 | 22.6044 | 22.7013 | 22.9463 | 24.4736 | 23.8609 | 23.8036 | 23.7185 | 23.6532 | 24.0212 | 23.7861 | 23.7455 | 23.6578 | 23.5855 | 23.4596 | 23.411 | 23.1211 | 22.95 | 23.0654 | 22.9924 | 23.6972 | 23.6043 | 23.5469 | 23.5044 | 24.3481 | 24.1343 | 24.0455 | 23.9286 | 23.8629 | 27.2413 | 23.6305 | 23.8403 | 23.7742 | 23.6897 | 23.6307 | 23.6756 | 23.762 | 23.1371 | 23.0083 | 24.1239 | 24.0281 | 24.0205 | 23.9683 | 24.9076 | 32.5605 | 36.8877 | 40.3042 | 35.9641 | 37.7724 | 42.8618 | 46.614 | 35.8195 | 46.7238 | 40.5062 |  | 40.0598 | 34.4454 | 40.2656 | 24.6704 | 23.4084 | 23.4367 | 25.6958 | 24.0562 | 22.0342 | 22.855 | 10.837 | 14.2627 | 14.8829 | 11.13 | 0.00025001 | -0.0025936 | 0.0010987 | 0.0045967 | 0.0012481 | -0.00043203 | 0.012536 | 0.00038428 | -0.022055 | -360.1004 | 17.3905 | -360.4019 | 17.6245 | -360.8266 | 18.1687 | -360.8358 | 17.5876 | -352.5952 | 18.6594 | -352.589 | 16.8299 | 30.8485 | 368.4012 | 38.8403 | 14.5728 | 12.3284 | 23.0452
13:27 | 93 | 34.2038 |  | 8.3664 | 3.2752 | 0.9476 | 2.9916 | -1.6969 | 12.3706 | 5.4612 | 0.6362 | 0.6744 | 0.9843 | 0.7695 | -129.7596 | 3.9148 | 6.2912 | 1.5588 | -2.3314 | -1.0022 | 5.0324 |  | 4.792 | 1.0163 | 3.9799 | 3.3666 | 3.3287 | 1.1003 | 2.229 | 22.8156 | 22.644 | 22.3922 | 22.3604 | 22.2685 | 22.3217 | 22.166 | 22.9264 | 22.6435 | 22.6878 | 22.6826 | 23.8962 | 23.0343 | 22.9532 | 22.8976 | 22.7958 | 22.684 | 22.6165 | 22.5601 | 22.3854 | 22.4261 | 22.3095 | 22.9324 | 22.5473 | 22.5833 | 22.5774 | 23.0846 | 23.1798 | 22.7008 | 22.9501 | 23.0444 | 23.5205 | 23.4985 | 22.8651 | 22.9041 | 22.8746 | 22.8093 | 22.707 | 22.7787 | 22.463 | 22.2873 | 23.2887 | 22.6678 | 22.7765 | 22.9915 | 23.9739 | 23.3169 | 23.264 | 23.2747 | 23.2403 | 24.2253 | 23.0664 | 23.0783 | 23.1131 | 23.072 | 23.0013 | 23.0087 | 22.9809 | 22.7638 | 23.0865 | 22.8867 | 23.1418 | 23.1742 | 23.1487 | 23.0717 | 23.9141 | 23.8276 | 23.7333 | 23.7395 | 23.6911 | 24.6273 | 23.3185 | 23.3923 | 23.4089 | 23.3652 | 23.3821 | 23.4378 | 23.4575 | 23.0692 | 22.8318 | 23.3079 | 23.364 | 23.3353 | 23.3081 | 23.8692 | 42.3457 | 76.5398 | 26.0254 | 30.0691 | 34.3284 | 35.1851 | 31.6292 | 47.3125 | 40.5177 | 50.1804 | 109.706 | 107.0334 | 90.234 | 92.3736 | 96.582 | 94.0994 | 98.861 | 102.9087 | 27.2071 | 25.4807 | 28.0147 | 26.5259 | 22.6695 | 22.5838 |  | 22.3095 | 22.2822 | 22.2194 | 22.1748 | 22.1582 | 22.2108 | 23.1863 | 22.5231 | 22.4436 | 23.8311 | 22.4671 | 22.713 | 22.9922 | 22.8999 | 22.8465 | 22.7511 | 22.7009 | 22.6627 | 22.6173 | 22.634 | 23.6644 | 22.7477 | 22.7411 | 23.7653 | 23.7 | 23.7812 | 22.8905 | 23.0771 | 23.6645 | 23.8971 | 22.9462 | 22.986 | 22.9535 | 22.9123 | 22.9062 | 22.7231 | 22.686 | 22.6161 | 23.6271 | 22.5982 | 22.7091 | 22.9503 | 24.5179 | 23.8646 | 23.807 | 23.7237 | 23.6602 | 24.039 | 23.7926 | 23.7496 | 23.6558 | 23.588 | 23.4602 | 23.4202 | 23.1178 | 22.9514 | 23.0819 | 22.999 | 23.6961 | 23.6121 | 23.551 | 23.5087 | 24.3755 | 24.1403 | 24.0448 | 23.931 | 23.8701 | 27.3045 | 23.632 | 23.84 | 23.7701 | 23.6891 | 23.625 | 23.6796 | 23.7663 | 23.1417 | 23.0128 | 24.1175 | 24.021 | 24.0181 | 23.9716 | 24.9313 | 32.8141 | 36.9845 | 40.1239 | 36.1219 | 38.1289 | 43.3145 | 47.3148 | 36.0234 | 47.1982 | 40.9 |  | 40.5686 | 34.8326 | 40.6043 | 24.6754 | 23.4237 | 23.4487 | 25.7976 | 24.1159 | 22.0558 | 22.8899 | 10.8178 | 14.2936 | 14.8893 | 11.1095 | 0.00068364 | -0.0027125 | 0.0012743 | 0.0044176 | 0.0019025 | -0.00044155 | 0.013854 | -0.001218 | -0.041957 | -360.2081 | 17.4562 | -360.4727 | 17.6266 | -360.7589 | 18.1461 | -360.8358 | 17.6102 | -352.6629 | 18.7066 | -352.6413 | 16.8156 | 35.9013 | 363.5186 | 39.2846 | 14.5915 | 12.2345 | 23.0859
13:27 | 94 | 34.1915 |  | 8.4688 | 3.2106 | 0.9682 | 2.9751 | -1.6641 | 12.4043 | 5.4169 | 0.6359 | 0.6748 | 0.9796 | 0.7708 | -129.7308 | 3.9062 | 6.2706 | 1.6038 | -2.379 | -0.9934 | 5.0483 |  | 4.9309 | 0.9874 | 3.978 | 3.3665 | 3.3271 | 1.1004 | 1.6624 | 22.8204 | 22.6337 | 22.3918 | 22.3586 | 22.2672 | 22.3168 | 22.1642 | 22.9223 | 22.6401 | 22.683 | 22.6766 | 23.9258 | 23.0339 | 22.9506 | 22.8944 | 22.7901 | 22.6881 | 22.6144 | 22.5536 | 22.3878 | 22.4349 | 22.3046 | 22.9258 | 22.5496 | 22.5823 | 22.5745 | 23.1011 | 23.1831 | 22.6976 | 22.9566 | 23.039 | 23.5377 | 23.495 | 22.8676 | 22.9029 | 22.8763 | 22.8065 | 22.7078 | 22.7911 | 22.4645 | 22.2843 | 23.285 | 22.6647 | 22.7795 | 22.9935 | 23.9993 | 23.3149 | 23.2663 | 23.2773 | 23.2458 | 24.2561 | 23.0732 | 23.0861 | 23.113 | 23.0794 | 23.0062 | 23.0153 | 22.9943 | 22.7649 | 23.0856 | 22.8894 | 23.1344 | 23.1686 | 23.1455 | 23.0699 | 23.9356 | 23.8215 | 23.7306 | 23.7341 | 23.6893 | 24.6539 | 23.3151 | 23.3844 | 23.4051 | 23.3697 | 23.3781 | 23.4355 | 23.4683 | 23.0747 | 22.8375 | 23.3145 | 23.3648 | 23.3356 | 23.3078 | 23.8858 | 41.9341 | 78.1813 | 26.1464 | 30.2649 | 34.7267 | 35.6008 | 31.8024 | 47.8084 | 40.8359 | 50.6593 | 109.7887 | 108.2967 | 89.3084 | 92.9387 | 97.8567 | 96.2436 | 100.4286 | 104.6609 | 27.3877 | 25.594 | 28.2124 | 26.6632 | 22.6671 | 22.5778 |  | 22.3043 | 22.2804 | 22.2097 | 22.1698 | 22.1592 | 22.2054 | 23.1831 | 22.5207 | 22.4466 | 23.8498 | 22.4668 | 22.7101 | 22.9939 | 22.8978 | 22.8422 | 22.7709 | 22.7048 | 22.6628 | 22.6204 | 22.6361 | 23.6631 | 22.7456 | 22.7408 | 23.7614 | 23.7248 | 23.7772 | 22.8919 | 23.0767 | 23.6787 | 23.8966 | 22.9385 | 22.9784 | 22.9487 | 22.9053 | 22.906 | 22.7192 | 22.6902 | 22.6146 | 23.6261 | 22.5944 | 22.7132 | 22.9525 | 24.5538 | 23.8709 | 23.8102 | 23.7275 | 23.6626 | 24.0587 | 23.7941 | 23.7511 | 23.659 | 23.5873 | 23.4646 | 23.4198 | 23.1318 | 22.962 | 23.1011 | 23.007 | 23.6937 | 23.6114 | 23.5556 | 23.5067 | 24.3994 | 24.1399 | 24.0405 | 23.9315 | 23.8632 | 27.3676 | 23.6282 | 23.8393 | 23.7683 | 23.6857 | 23.6227 | 23.6799 | 23.7699 | 23.1369 | 23.0148 | 24.1083 | 24.0142 | 24.0162 | 23.9684 | 24.9549 | 33.0613 | 37.1092 | 40.4781 | 36.2765 | 38.488 | 43.762 | 48.0227 | 36.2624 | 47.6867 | 41.3268 |  | 41.0819 | 35.2157 | 40.916 | 24.6732 | 23.4231 | 23.4419 | 25.8885 | 24.1674 | 22.0727 | 22.9042 | 10.8235 | 14.292 | 14.9075 | 11.1438 | 0.00038485 | -0.0029831 | 0.0013042 | 0.0038605 | 0.0012111 | -0.00027149 | 0.027173 | -0.0083214 | -0.025944 | -360.0911 | 17.3925 | -360.3773 | 17.6225 | -360.7835 | 18.1502 | -360.8174 | 17.5691 | -352.5613 | 18.6655 | -352.5829 | 16.8238 | 44.8643 | 370.079 | 39.7267 | 14.5998 | 12.2933 | 23.12
13:27 | 95 | 34.2334 |  | 8.4898 | 3.2739 | 0.9741 | 2.9945 | -1.7015 | 12.3857 | 5.3892 | 0.6357 | 0.6718 | 0.9844 | 0.77 | -129.7029 | 3.9249 | 6.3045 | 1.7405 | -2.4897 | -1.0152 | 5.0191 |  | 4.8394 | 1.0301 | 3.9803 | 3.3671 | 3.3296 | 1.0998 | 3.2526 | 22.8267 | 22.6317 | 22.3909 | 22.3561 | 22.2632 | 22.323 | 22.165 | 22.9228 | 22.6414 | 22.6848 | 22.6747 | 23.9571 | 23.0299 | 22.9473 | 22.8987 | 22.7864 | 22.685 | 22.6122 | 22.5492 | 22.3812 | 22.4348 | 22.3036 | 22.9191 | 22.552 | 22.5798 | 22.5763 | 23.1123 | 23.1681 | 22.6963 | 22.9573 | 23.0414 | 23.556 | 23.4923 | 22.873 | 22.9007 | 22.8764 | 22.8038 | 22.7127 | 22.7995 | 22.468 | 22.2858 | 23.2777 | 22.6648 | 22.7749 | 22.9984 | 24.0201 | 23.3145 | 23.2673 | 23.2797 | 23.2504 | 24.2744 | 23.0816 | 23.0829 | 23.113 | 23.0787 | 23.0016 | 23.0099 | 22.9904 | 22.7703 | 23.1057 | 22.8875 | 23.1267 | 23.1692 | 23.1519 | 23.0742 | 23.9528 | 23.822 | 23.7325 | 23.7382 | 23.6918 | 24.6845 | 23.3119 | 23.3817 | 23.4046 | 23.3686 | 23.3774 | 23.445 | 23.4738 | 23.0749 | 22.8495 | 23.3126 | 23.3685 | 23.3336 | 23.3142 | 23.9025 | 42.2106 | 78.5872 | 26.3131 | 30.4335 | 35.1165 | 36.0111 | 31.9692 | 48.3489 | 41.1331 | 51.1404 | 108.8065 | 109.0057 | 88.6465 | 94.2114 | 98.3896 | 97.0065 | 102.7171 | 105.3903 | 27.5659 | 25.7103 | 28.4161 | 26.8143 | 22.6717 | 22.5839 |  | 22.3089 | 22.2824 | 22.2148 | 22.1649 | 22.1618 | 22.2042 | 23.1845 | 22.5169 | 22.4479 | 23.8752 | 22.471 | 22.7091 | 22.9961 | 22.904 | 22.8472 | 22.788 | 22.715 | 22.6703 | 22.627 | 22.6418 | 23.657 | 22.7479 | 22.7445 | 23.7648 | 23.757 | 23.7829 | 22.894 | 23.0709 | 23.6944 | 23.8927 | 22.9312 | 22.9744 | 22.9408 | 22.9041 | 22.9112 | 22.7202 | 22.6962 | 22.6142 | 23.6235 | 22.5962 | 22.714 | 22.9495 | 24.5834 | 23.8605 | 23.8042 | 23.7148 | 23.6581 | 24.0652 | 23.7829 | 23.743 | 23.6549 | 23.5838 | 23.4621 | 23.4039 | 23.1411 | 22.9664 | 23.0996 | 23.0069 | 23.6924 | 23.6111 | 23.5568 | 23.5086 | 24.4306 | 24.1412 | 24.0403 | 23.935 | 23.8632 | 27.4347 | 23.6263 | 23.843 | 23.7748 | 23.6877 | 23.6264 | 23.6819 | 23.7807 | 23.1495 | 23.0114 | 24.1105 | 24.0216 | 24.0209 | 23.9748 | 24.9933 | 33.2711 | 37.2759 | 41.0539 | 36.4838 | 38.8275 | 44.1803 | 48.7312 | 36.5432 | 48.1972 | 41.7201 |  | 41.6364 | 35.6039 | 41.2266 | 24.6728 | 23.4291 | 23.4485 | 25.9762 | 24.2347 | 22.0958 | 22.9411 | 10.8334 | 14.2663 | 14.8801 | 11.084 | 0.00011195 | -0.0022401 | 0.0014532 | 0.0040115 | 0.0013195 | -0.00028754 | 0.026994 | -0.023633 | -0.0039144 | -360.2173 | 17.448 | -360.4604 | 17.6245 | -360.7866 | 18.1502 | -360.8358 | 17.6143 | -352.6413 | 18.7087 | -352.6444 | 16.8258 | 38.1149 | 359.175 | 40.1667 | 14.5732 | 12.279 | 23.1653
13:27 | 96 | 34.1056 |  | 8.3314 | 3.1521 | 0.8761 | 2.9713 | -1.757 | 12.3067 | 5.375 | 0.635 | 0.6763 | 0.98 | 0.7709 | -129.7797 | 3.893 | 6.2335 | 1.6583 | -2.425 | -0.9574 | 4.9873 |  | 4.8092 | 0.9889 | 3.9791 | 3.3653 | 3.3289 | 1.1003 | 0.0059 | 22.8241 | 22.6396 | 22.384 | 22.3566 | 22.263 | 22.33 | 22.1697 | 22.9254 | 22.6463 | 22.6841 | 22.6811 | 23.9913 | 23.0252 | 22.9512 | 22.8972 | 22.7878 | 22.686 | 22.6152 | 22.5571 | 22.3817 | 22.4313 | 22.3107 | 22.927 | 22.5542 | 22.5803 | 22.5816 | 23.1314 | 23.1694 | 22.7 | 22.9593 | 23.036 | 23.57 | 23.4837 | 22.869 | 22.8987 | 22.8756 | 22.8006 | 22.7085 | 22.7996 | 22.4662 | 22.2874 | 23.2741 | 22.6655 | 22.7747 | 22.9989 | 24.0383 | 23.3097 | 23.2731 | 23.2763 | 23.2475 | 24.2897 | 23.0831 | 23.0706 | 23.1162 | 23.0743 | 22.997 | 23.0074 | 22.9826 | 22.7712 | 23.1146 | 22.8885 | 23.1263 | 23.1705 | 23.1566 | 23.0786 | 23.9781 | 23.8219 | 23.7336 | 23.7453 | 23.6957 | 24.7176 | 23.3134 | 23.3845 | 23.4077 | 23.3692 | 23.3835 | 23.455 | 23.4681 | 23.0749 | 22.8483 | 23.3124 | 23.3706 | 23.3332 | 23.3136 | 23.9185 | 43.1265 | 78.4353 | 26.3952 | 30.5893 | 35.4939 | 36.3977 | 32.1419 | 48.882 | 41.4403 | 51.6081 | 108.8935 | 108.0449 | 88.7289 | 95.4387 | 98.5458 | 96.882 | 104.5256 | 105.8702 | 27.7517 | 25.8232 | 28.6212 | 26.9714 | 22.6799 | 22.5958 |  | 22.3177 | 22.2898 | 22.2263 | 22.1787 | 22.1697 | 22.2143 | 23.1939 | 22.528 | 22.4537 | 23.9158 | 22.4787 | 22.7155 | 22.9963 | 22.9065 | 22.8544 | 22.7801 | 22.714 | 22.6708 | 22.6233 | 22.6472 | 23.658 | 22.7473 | 22.7459 | 23.7686 | 23.7888 | 23.7851 | 22.8922 | 23.0736 | 23.7131 | 23.8972 | 22.9337 | 22.9779 | 22.9449 | 22.9122 | 22.9201 | 22.7189 | 22.6973 | 22.6223 | 23.6261 | 22.5994 | 22.7172 | 22.9499 | 24.6172 | 23.8603 | 23.8035 | 23.7126 | 23.6579 | 24.0668 | 23.7878 | 23.7415 | 23.6556 | 23.5856 | 23.4621 | 23.4029 | 23.1445 | 22.9662 | 23.1072 | 23.0088 | 23.6926 | 23.6124 | 23.5603 | 23.5127 | 24.4641 | 24.1472 | 24.0499 | 23.9338 | 23.8742 | 27.5066 | 23.631 | 23.8449 | 23.779 | 23.6922 | 23.6344 | 23.688 | 23.7911 | 23.1647 | 23.0176 | 24.1128 | 24.0323 | 24.0191 | 23.9774 | 25.0371 | 33.4103 | 37.4949 | 41.2442 | 36.6752 | 39.1741 | 44.5775 | 49.4462 | 36.8698 | 48.7205 | 42.1003 |  | 42.2025 | 35.9775 | 41.5209 | 24.6689 | 23.4259 | 23.4522 | 26.073 | 24.2867 | 22.1112 | 22.9714 | 10.8474 | 14.288 | 14.8628 | 11.1319 | 0.00024746 | -0.0025382 | 0.0021987 | 0.0043341 | 0.0015845 | -3.1266e-05 | 0.03439 | 0.010556 | -0.017302 | -360.1619 | 17.4336 | -360.4419 | 17.6512 | -360.8327 | 18.1625 | -360.8543 | 17.604 | -352.5706 | 18.6779 | -352.6198 | 16.8299 | 48.1067 | 368.6897 | 40.5988 | 14.5754 | 12.0951 | 23.1989
13:27 | 97 | 34.0926 |  | 8.304 | 3.2286 | 0.9013 | 2.9746 | -1.659 | 12.3852 | 5.3612 | 0.6361 | 0.6744 | 0.9814 | 0.7701 | -129.8227 | 3.781 | 6.2572 | 1.7883 | -2.3844 | -0.8936 | 5.0179 |  | 4.8971 | 1.0107 | 3.9796 | 3.3684 | 3.3291 | 1.1007 | 2.7162 | 22.8201 | 22.6386 | 22.3801 | 22.3549 | 22.2618 | 22.3266 | 22.1715 | 22.9238 | 22.6483 | 22.6836 | 22.6864 | 24.0279 | 23.0254 | 22.9603 | 22.8919 | 22.79 | 22.6869 | 22.6139 | 22.5573 | 22.3871 | 22.4267 | 22.3131 | 22.9303 | 22.5561 | 22.5863 | 22.5771 | 23.1479 | 23.1644 | 22.7047 | 22.9595 | 23.0318 | 23.5883 | 23.4833 | 22.8633 | 22.8994 | 22.8755 | 22.803 | 22.7101 | 22.8067 | 22.4732 | 22.2893 | 23.2674 | 22.6737 | 22.7874 | 23.0021 | 24.0655 | 23.3111 | 23.2739 | 23.2763 | 23.249 | 24.3232 | 23.0838 | 23.0775 | 23.1217 | 23.0768 | 23.002 | 23.0246 | 22.9995 | 22.7751 | 23.1093 | 22.8969 | 23.1284 | 23.1665 | 23.1494 | 23.0748 | 23.999 | 23.8168 | 23.7316 | 23.7438 | 23.6941 | 24.7438 | 23.3157 | 23.3853 | 23.4121 | 23.37 | 23.3865 | 23.4557 | 23.4725 | 23.0814 | 22.8476 | 23.3186 | 23.3725 | 23.3405 | 23.3099 | 23.9467 | 43.8217 | 77.8552 | 26.4577 | 30.751 | 35.8629 | 36.7658 | 32.3175 | 49.399 | 41.7462 | 52.0446 | 110.1923 | 106.1137 | 90.5183 | 96.3382 | 99.0853 | 97.5132 | 104.1373 | 105.5287 | 27.9438 | 25.941 | 28.8247 | 27.1319 | 22.6729 | 22.5923 |  | 22.3134 | 22.2855 | 22.2201 | 22.177 | 22.1673 | 22.2151 | 23.1878 | 22.5223 | 22.4514 | 23.938 | 22.4689 | 22.7157 | 22.9951 | 22.9023 | 22.847 | 22.7581 | 22.7083 | 22.6675 | 22.6139 | 22.6483 | 23.6542 | 22.7438 | 22.743 | 23.7597 | 23.8132 | 23.7812 | 22.8871 | 23.0755 | 23.7285 | 23.8939 | 22.9408 | 22.9792 | 22.9469 | 22.9098 | 22.925 | 22.7249 | 22.697 | 22.6297 | 23.6249 | 22.6024 | 22.7145 | 22.9514 | 24.6554 | 23.8646 | 23.8007 | 23.7128 | 23.6629 | 24.076 | 23.792 | 23.7438 | 23.6561 | 23.587 | 23.4561 | 23.4143 | 23.1504 | 22.9668 | 23.1183 | 23.0097 | 23.6929 | 23.6057 | 23.5575 | 23.5126 | 24.4864 | 24.1467 | 24.0521 | 23.933 | 23.8762 | 27.5677 | 23.6305 | 23.8419 | 23.775 | 23.6939 | 23.6328 | 23.6886 | 23.7921 | 23.1635 | 23.0185 | 24.11 | 24.0325 | 24.0208 | 23.9712 | 25.0635 | 33.5817 | 37.7845 | 41.5869 | 36.8186 | 39.5322 | 45.0042 | 50.1581 | 37.2414 | 49.2529 | 42.4869 |  | 42.7632 | 36.3492 | 41.8031 | 24.6695 | 23.4186 | 23.4448 | 26.1606 | 24.3293 | 22.1118 | 22.9922 | 10.8207 | 14.275 | 14.9183 | 11.1201 | 0.0006928 | -0.002815 | 0.0015171 | 0.0042393 | 0.0010275 | -0.00066903 | 0.014774 | -0.0010084 | -0.0045525 | -360.1311 | 17.4172 | -360.4019 | 17.6204 | -360.7712 | 18.1296 | -360.7835 | 17.5835 | -352.5644 | 18.6779 | -352.5983 | 16.8135 | 56.7354 | 362.4018 | 41.0298 | 14.5967 | 12.2796 | 23.2205
13:27 | 98 | 33.9662 |  | 8.3399 | 3.2182 | 0.8803 | 2.9394 | -1.6551 | 12.3237 | 5.4529 | 0.6348 | 0.6739 | 0.9797 | 0.7684 | -129.8189 | 3.8029 | 6.2237 | 1.7811 | -2.3529 | -0.9468 | 5.097 |  | 4.8562 | 0.9267 | 3.9793 | 3.3679 | 3.3254 | 1.1003 | 2.6817 | 22.8256 | 22.6369 | 22.384 | 22.3551 | 22.2674 | 22.3328 | 22.1772 | 22.9291 | 22.6539 | 22.6862 | 22.685 | 24.0709 | 23.0313 | 22.9588 | 22.8938 | 22.7872 | 22.6815 | 22.6087 | 22.5575 | 22.3888 | 22.4285 | 22.3183 | 22.9288 | 22.5585 | 22.5909 | 22.5698 | 23.1632 | 23.1574 | 22.7044 | 22.9574 | 23.0388 | 23.6116 | 23.4914 | 22.8671 | 22.8988 | 22.88 | 22.8075 | 22.7188 | 22.8233 | 22.4824 | 22.295 | 23.2742 | 22.6777 | 22.7902 | 23.0079 | 24.0948 | 23.3188 | 23.2721 | 23.2772 | 23.2557 | 24.3556 | 23.091 | 23.0856 | 23.1253 | 23.085 | 23.008 | 23.0325 | 23.0088 | 22.7823 | 23.1414 | 22.9016 | 23.1278 | 23.1593 | 23.1441 | 23.0691 | 24.0151 | 23.8161 | 23.7265 | 23.7393 | 23.691 | 24.7732 | 23.3101 | 23.3817 | 23.4071 | 23.37 | 23.3804 | 23.4572 | 23.481 | 23.0916 | 22.8493 | 23.3179 | 23.3648 | 23.3388 | 23.3087 | 23.9709 | 44.0543 | 77.665 | 26.5428 | 30.8545 | 36.236 | 37.1425 | 32.485 | 49.8946 | 42.0427 | 52.5141 | 111.4243 | 105.1928 | 93.6106 | 97.1741 | 99.6511 | 97.4516 | 102.6257 | 104.7279 | 28.1413 | 26.069 | 29.0299 | 27.3031 | 22.67 | 22.5903 |  | 22.3099 | 22.2827 | 22.2166 | 22.1715 | 22.1783 | 22.2144 | 23.1767 | 22.516 | 22.4502 | 23.9572 | 22.4697 | 22.7136 | 22.9859 | 22.8976 | 22.8404 | 22.7458 | 22.705 | 22.6607 | 22.6039 | 22.6484 | 23.6487 | 22.7409 | 22.7355 | 23.7535 | 23.8316 | 23.7762 | 22.8835 | 23.0774 | 23.7441 | 23.895 | 22.9462 | 22.9826 | 22.949 | 22.9092 | 22.9356 | 22.7375 | 22.7004 | 22.6301 | 23.6254 | 22.607 | 22.7153 | 22.9559 | 24.6914 | 23.8536 | 23.7922 | 23.7033 | 23.6604 | 24.0779 | 23.7669 | 23.738 | 23.6495 | 23.5801 | 23.4499 | 23.4172 | 23.1383 | 22.9675 | 23.1177 | 23.0067 | 23.6926 | 23.6062 | 23.5525 | 23.5109 | 24.5117 | 24.145 | 24.0484 | 23.9347 | 23.8717 | 27.6246 | 23.6262 | 23.8428 | 23.7714 | 23.695 | 23.6338 | 23.6931 | 23.7922 | 23.1557 | 23.0186 | 24.1084 | 24.0251 | 24.0188 | 23.967 | 25.0888 | 33.8085 | 38.0611 | 41.7866 | 37.0057 | 39.8869 | 45.4738 | 50.8633 | 37.6007 | 49.7876 | 42.825 |  | 43.3285 | 36.7331 | 42.0935 | 24.6731 | 23.417 | 23.4427 | 26.2492 | 24.3866 | 22.1252 | 23.0282 | 10.7997 | 14.2251 | 14.8721 | 11.1074 | 0.0001576 | -0.0032681 | 0.0014745 | 0.0045752 | 0.00099674 | -0.00038487 | 0.017542 | -0.010071 | -0.01107 | -360.1681 | 17.4172 | -360.4235 | 17.6369 | -360.7989 | 18.1604 | -360.8389 | 17.5958 | -352.5706 | 18.6902 | -352.6106 | 16.834 | 66.1188 | 365.3128 | 41.4697 | 14.5486 | 12.2582 | 23.2559
13:28 | 99 | 33.8911 |  | 8.2138 | 3.2453 | 0.8301 | 2.903 | -1.6239 | 12.2283 | 5.4 | 0.6363 | 0.6772 | 0.9799 | 0.7699 | -129.8689 | 3.7826 | 6.2243 | 1.7353 | -2.3856 | -0.877 | 5.0946 |  | 4.8905 | 0.9146 | 3.9785 | 3.3671 | 3.3269 | 1.0998 | 1.4765 | 22.8261 | 22.6333 | 22.384 | 22.3524 | 22.2684 | 22.3371 | 22.1759 | 22.9246 | 22.648 | 22.6919 | 22.6816 | 24.1062 | 23.0375 | 22.9565 | 22.8981 | 22.79 | 22.6814 | 22.6153 | 22.5663 | 22.3844 | 22.4394 | 22.3303 | 22.9256 | 22.5573 | 22.5915 | 22.5752 | 23.1826 | 23.164 | 22.7078 | 22.9626 | 23.0393 | 23.6301 | 23.4897 | 22.8661 | 22.8984 | 22.8758 | 22.8059 | 22.7183 | 22.8329 | 22.4953 | 22.2944 | 23.27 | 22.6716 | 22.7821 | 23.0089 | 24.1237 | 23.318 | 23.2701 | 23.2765 | 23.2539 | 24.382 | 23.0876 | 23.0827 | 23.1215 | 23.0852 | 23.0094 | 23.0342 | 23.0106 | 22.7832 | 23.1711 | 22.9056 | 23.1261 | 23.1646 | 23.1426 | 23.0745 | 24.0371 | 23.8235 | 23.7318 | 23.7466 | 23.6976 | 24.8065 | 23.3152 | 23.387 | 23.4078 | 23.3763 | 23.3805 | 23.4648 | 23.4869 | 23.0931 | 22.8477 | 23.3143 | 23.3617 | 23.3315 | 23.3076 | 23.9847 | 43.8824 | 79.0133 | 26.5866 | 30.9464 | 36.6055 | 37.5244 | 32.6603 | 50.3634 | 42.3838 | 53.0356 | 111.8895 | 104.2711 | 93.303 | 97.6997 | 100.1462 | 97.2377 | 100.4621 | 103.7182 | 28.3352 | 26.196 | 29.2368 | 27.4641 | 22.6685 | 22.591 |  | 22.3091 | 22.2844 | 22.2178 | 22.1763 | 22.1839 | 22.2168 | 23.1739 | 22.5182 | 22.4567 | 23.9865 | 22.4741 | 22.7154 | 22.9912 | 22.9043 | 22.8482 | 22.745 | 22.7142 | 22.6694 | 22.6036 | 22.6575 | 23.66 | 22.7513 | 22.7399 | 23.7631 | 23.8643 | 23.7878 | 22.8897 | 23.0786 | 23.7577 | 23.8927 | 22.9463 | 22.9802 | 22.9495 | 22.9098 | 22.9343 | 22.7386 | 22.7086 | 22.6345 | 23.6257 | 22.604 | 22.7187 | 22.9553 | 24.7341 | 23.8664 | 23.7911 | 23.712 | 23.6602 | 24.0907 | 23.7514 | 23.737 | 23.6557 | 23.5788 | 23.4567 | 23.427 | 23.1232 | 22.975 | 23.1111 | 23.0127 | 23.6872 | 23.6123 | 23.5581 | 23.5059 | 24.5409 | 24.1438 | 24.046 | 23.9316 | 23.8752 | 27.69 | 23.626 | 23.844 | 23.7701 | 23.6936 | 23.6334 | 23.6994 | 23.7962 | 23.1551 | 23.026 | 24.1069 | 24.0203 | 24.0106 | 23.9671 | 25.12 | 34.0032 | 38.3202 | 41.6893 | 37.2136 | 40.2505 | 45.9793 | 51.579 | 37.9359 | 50.3278 | 43.1319 |  | 43.8895 | 37.1353 | 42.3881 | 24.6766 | 23.4253 | 23.4526 | 26.3545 | 24.4531 | 22.1507 | 23.076 | 10.8193 | 14.2663 | 14.9224 | 11.1051 | -0.00021717 | -0.0027568 | 0.001219 | 0.0042467 | 0.0011323 | -0.00031103 | 0.017837 | 0.0017278 | -0.021526 | -360.1804 | 17.4418 | -360.4512 | 17.6471 | -360.805 | 18.1563 | -360.8204 | 17.6122 | -352.586 | 18.6984 | -352.6537 | 16.8238 | 52.3586 | 367.9076 | 41.919 | 14.5944 | 12.1707 | 23.3019
13:28 | 100 | 33.8004 |  | 8.263 | 3.3395 | 0.943 | 2.9766 | -1.6526 | 12.2776 | 5.4757 | 0.6357 | 0.6738 | 0.9839 | 0.7699 | -129.8983 | 3.7378 | 6.2658 | 1.7945 | -2.3624 | -0.8809 | 5.1288 |  | 4.8911 | 0.9203 | 3.9781 | 3.3683 | 3.3286 | 1.1011 | 1.9468 | 22.8242 | 22.6314 | 22.3858 | 22.3538 | 22.2662 | 22.3362 | 22.1709 | 22.9238 | 22.6386 | 22.6922 | 22.6818 | 24.1417 | 23.035 | 22.9611 | 22.8926 | 22.7862 | 22.6799 | 22.6199 | 22.5667 | 22.3832 | 22.441 | 22.3289 | 22.9214 | 22.5598 | 22.5871 | 22.578 | 23.2044 | 23.1735 | 22.7037 | 22.9639 | 23.0356 | 23.6473 | 23.4833 | 22.8609 | 22.9016 | 22.8702 | 22.8057 | 22.7091 | 22.8415 | 22.5067 | 22.2906 | 23.273 | 22.6732 | 22.7822 | 23.0099 | 24.1486 | 23.3126 | 23.2641 | 23.2768 | 23.2471 | 24.4115 | 23.0714 | 23.0852 | 23.1166 | 23.0815 | 23.0116 | 23.0333 | 23.0188 | 22.7842 | 23.1583 | 22.9069 | 23.1228 | 23.1667 | 23.1394 | 23.0769 | 24.0507 | 23.8242 | 23.733 | 23.7503 | 23.698 | 24.8346 | 23.3213 | 23.389 | 23.4077 | 23.3743 | 23.3877 | 23.4704 | 23.5002 | 23.0912 | 22.8561 | 23.3161 | 23.3613 | 23.3331 | 23.3107 | 24.002 | 43.6263 | 80.8275 | 26.5895 | 31.051 | 36.9658 | 37.9096 | 32.8162 | 50.7924 | 42.7557 | 53.5931 | 112.2546 | 104.6216 | 92.8005 | 98.3578 | 100.3568 | 98.4454 | 98.7882 | 103.8451 | 28.5207 | 26.3212 | 29.4425 | 27.6105 | 22.6702 | 22.5926 |  | 22.306 | 22.2857 | 22.2185 | 22.1761 | 22.1772 | 22.2156 | 23.1729 | 22.5166 | 22.4574 | 24.011 | 22.4701 | 22.7117 | 22.9946 | 22.9042 | 22.8447 | 22.7419 | 22.7129 | 22.6739 | 22.6024 | 22.6562 | 23.6596 | 22.7483 | 22.7359 | 23.7641 | 23.8911 | 23.7884 | 22.8946 | 23.0766 | 23.7663 | 23.8853 | 22.9345 | 22.9792 | 22.9454 | 22.9083 | 22.9361 | 22.7361 | 22.71 | 22.6368 | 23.6199 | 22.5969 | 22.7164 | 22.9496 | 24.7793 | 23.8768 | 23.7938 | 23.716 | 23.6579 | 24.1058 | 23.7576 | 23.738 | 23.6582 | 23.5783 | 23.4552 | 23.4358 | 23.1257 | 22.9787 | 23.1105 | 23.0171 | 23.6867 | 23.614 | 23.5626 | 23.5104 | 24.5709 | 24.1413 | 24.0467 | 23.933 | 23.8806 | 27.7608 | 23.6303 | 23.8412 | 23.776 | 23.6965 | 23.6326 | 23.7066 | 23.8045 | 23.1682 | 23.0327 | 24.112 | 24.0208 | 24.0172 | 23.9717 | 25.1499 | 34.1806 | 38.5566 | 41.667 | 37.417 | 40.6129 | 46.5043 | 52.3022 | 38.2466 | 50.8621 | 43.4291 |  | 44.4297 | 37.5395 | 42.689 | 24.6838 | 23.4293 | 23.4511 | 26.4522 | 24.5136 | 22.1758 | 23.0995 | 10.83 | 14.2696 | 14.8464 | 11.1023 | 0.00043206 | -0.0022907 | 0.0010455 | 0.0040737 | 0.0010115 | -0.00060353 | 0.024633 | -0.014479 | -0.02631 | -360.1281 | 17.409 | -360.3896 | 17.6081 | -360.7589 | 18.1461 | -360.8174 | 17.5896 | -352.5644 | 18.6635 | -352.5829 | 16.795 | 62.5846 | 363.6927 | 42.3691 | 14.558 | 12.3343 | 23.3447
13:28 | 101 | 33.7066 |  | 8.2605 | 3.2203 | 1.0438 | 2.941 | -1.6753 | 12.2623 | 5.352 | 0.6364 | 0.6747 | 0.9804 | 0.7704 | -129.8736 | 3.7889 | 6.2531 | 1.7832 | -2.3775 | -0.9769 | 5.065 |  | 4.9352 | 0.9119 | 3.9773 | 3.3678 | 3.3275 | 1.101 | 1.4266 | 22.8266 | 22.6316 | 22.3837 | 22.3606 | 22.2677 | 22.3382 | 22.1746 | 22.9267 | 22.6377 | 22.6902 | 22.6856 | 24.1863 | 23.0354 | 22.9642 | 22.8864 | 22.778 | 22.6828 | 22.6092 | 22.5652 | 22.384 | 22.4376 | 22.3252 | 22.9166 | 22.5558 | 22.5824 | 22.5721 | 23.2189 | 23.1706 | 22.704 | 22.9532 | 23.0363 | 23.6667 | 23.4866 | 22.8623 | 22.9035 | 22.8723 | 22.8079 | 22.7157 | 22.8461 | 22.5038 | 22.2889 | 23.2824 | 22.6759 | 22.7854 | 23.0073 | 24.1731 | 23.309 | 23.2614 | 23.2755 | 23.2549 | 24.439 | 23.0599 | 23.0842 | 23.1214 | 23.0821 | 23.0077 | 23.0372 | 23.0242 | 22.7799 | 23.1468 | 22.9075 | 23.1215 | 23.161 | 23.1431 | 23.0735 | 24.0719 | 23.8267 | 23.7301 | 23.7455 | 23.6985 | 24.8656 | 23.3237 | 23.3903 | 23.409 | 23.3743 | 23.3958 | 23.4726 | 23.5088 | 23.0938 | 22.8559 | 23.3154 | 23.3558 | 23.3342 | 23.3111 | 24.0187 | 43.6706 | 82.5512 | 26.6702 | 31.1536 | 37.3271 | 38.3073 | 32.9559 | 51.2067 | 43.0832 | 54.1668 | 113.2058 | 107.0214 | 92.6804 | 99.6451 | 99.0347 | 99.4754 | 100.9515 | 106.3116 | 28.7041 | 26.4444 | 29.6374 | 27.7583 | 22.6709 | 22.5959 |  | 22.3082 | 22.2862 | 22.2161 | 22.1777 | 22.1786 | 22.2188 | 23.1715 | 22.5093 | 22.4549 | 24.0334 | 22.4742 | 22.7069 | 22.9844 | 22.8994 | 22.8347 | 22.756 | 22.7099 | 22.6644 | 22.6103 | 22.6515 | 23.6523 | 22.7398 | 22.7317 | 23.7609 | 23.9106 | 23.775 | 22.8934 | 23.0837 | 23.7848 | 23.8912 | 22.9354 | 22.9828 | 22.9566 | 22.9078 | 22.9449 | 22.7347 | 22.7129 | 22.64 | 23.6231 | 22.6051 | 22.7139 | 22.9552 | 24.8261 | 23.8638 | 23.7969 | 23.7098 | 23.6533 | 24.1155 | 23.768 | 23.7381 | 23.6605 | 23.5771 | 23.458 | 23.4368 | 23.1496 | 22.9847 | 23.1298 | 23.0212 | 23.687 | 23.6058 | 23.5532 | 23.5047 | 24.5871 | 24.1409 | 24.0462 | 23.931 | 23.8738 | 27.8211 | 23.6285 | 23.8302 | 23.7832 | 23.6987 | 23.6309 | 23.7049 | 23.8154 | 23.172 | 23.0342 | 24.113 | 24.0206 | 24.0188 | 23.968 | 25.1794 | 34.3985 | 38.7284 | 41.6603 | 37.6156 | 40.9577 | 47.0085 | 53.0164 | 38.5225 | 51.3726 | 43.7367 |  | 44.9712 | 37.9376 | 42.9926 | 24.6858 | 23.4264 | 23.4542 | 26.5536 | 24.5629 | 22.1883 | 23.1297 | 10.8066 | 14.2889 | 14.8676 | 11.1135 | 0.00056922 | -0.0030287 | 0.0014639 | 0.0042807 | 0.0010719 | -0.00053514 | -0.0013137 | -0.002358 | -0.034775 | -360.1465 | 17.4315 | -360.4604 | 17.6369 | -360.8235 | 18.1399 | -360.7897 | 17.5814 | -352.5798 | 18.6943 | -352.6444 | 16.8299 | 63.2329 | 367.1779 | 42.8148 | 14.5783 | 12.2236 | 23.3756
13:28 | 102 | 33.5437 |  | 8.2864 | 3.2429 | 0.8771 | 2.927 | -1.6371 | 12.3135 | 5.5111 | 0.6369 | 0.6777 | 0.9788 | 0.768 | -129.9814 | 3.6576 | 6.2301 | 1.7932 | -2.4186 | -0.9746 | 5.1435 |  | 4.9248 | 0.9144 | 3.9778 | 3.3689 | 3.3308 | 1.1007 | 2.1893 | 22.8288 | 22.6361 | 22.3836 | 22.3537 | 22.2674 | 22.3435 | 22.1723 | 22.921 | 22.6431 | 22.6907 | 22.6861 | 24.2219 | 23.0333 | 22.9664 | 22.8901 | 22.7779 | 22.6814 | 22.6114 | 22.5699 | 22.3876 | 22.4491 | 22.3308 | 22.9232 | 22.558 | 22.5862 | 22.5751 | 23.2366 | 23.1709 | 22.713 | 22.9594 | 23.0349 | 23.6902 | 23.4862 | 22.8699 | 22.8996 | 22.8663 | 22.8071 | 22.7259 | 22.8502 | 22.5026 | 22.2894 | 23.2763 | 22.6694 | 22.781 | 23.0003 | 24.1965 | 23.3076 | 23.2659 | 23.2716 | 23.2592 | 24.4604 | 23.0665 | 23.0812 | 23.1216 | 23.0849 | 23.0071 | 23.0394 | 23.0331 | 22.7841 | 23.1378 | 22.9196 | 23.1209 | 23.159 | 23.1457 | 23.0724 | 24.0914 | 23.8275 | 23.7306 | 23.7406 | 23.6989 | 24.8954 | 23.3208 | 23.3927 | 23.4109 | 23.3756 | 23.3936 | 23.4747 | 23.5063 | 23.0943 | 22.8488 | 23.307 | 23.3563 | 23.3358 | 23.3109 | 24.035 | 43.699 | 83.8562 | 26.7585 | 31.3182 | 37.7003 | 38.7293 | 33.1111 | 51.6814 | 43.366 | 54.6932 | 114.4363 | 108.9791 | 92.9927 | 100.7374 | 97.591 | 100.9431 | 105.0487 | 108.2368 | 28.8742 | 26.563 | 29.8215 | 27.91 | 22.6685 | 22.5953 |  | 22.3056 | 22.2841 | 22.2119 | 22.1766 | 22.1829 | 22.2151 | 23.1736 | 22.5041 | 22.4497 | 24.0559 | 22.4727 | 22.7106 | 22.9799 | 22.8964 | 22.8325 | 22.7773 | 22.7067 | 22.6679 | 22.6194 | 22.6495 | 23.651 | 22.7401 | 22.7335 | 23.7557 | 23.9365 | 23.7759 | 22.8902 | 23.0783 | 23.8013 | 23.8926 | 22.9404 | 22.9796 | 22.9539 | 22.9019 | 22.9497 | 22.7364 | 22.7153 | 22.644 | 23.6262 | 22.606 | 22.7159 | 22.9579 | 24.8713 | 23.8564 | 23.7981 | 23.7081 | 23.656 | 24.1285 | 23.7797 | 23.7388 | 23.6582 | 23.5813 | 23.4618 | 23.4405 | 23.1677 | 22.9956 | 23.1359 | 23.0219 | 23.6844 | 23.6012 | 23.5453 | 23.4943 | 24.604 | 24.1407 | 24.0436 | 23.9239 | 23.8739 | 27.8878 | 23.6248 | 23.8294 | 23.7773 | 23.6986 | 23.6352 | 23.7015 | 23.8195 | 23.1696 | 23.0349 | 24.1107 | 24.0204 | 24.0205 | 23.9669 | 25.209 | 34.5791 | 38.9034 | 41.9135 | 37.7761 | 41.2959 | 47.4646 | 53.7513 | 38.8049 | 51.8688 | 44.1086 |  | 45.5417 | 38.3296 | 43.3116 | 24.6877 | 23.4271 | 23.4517 | 26.6601 | 24.6116 | 22.198 | 23.1724 | 10.7996 | 14.2678 | 14.8958 | 11.1065 | 0.00045168 | -0.003287 | 0.0014639 | 0.003928 | 0.0014464 | -0.0012164 | 0.023678 | -0.0097132 | -0.010814 | -360.1865 | 17.4315 | -360.4142 | 17.6348 | -360.805 | 18.1728 | -360.8789 | 17.6286 | -352.629 | 18.6779 | -352.5983 | 16.8217 | 65.2928 | 358.9249 | 43.2655 | 14.5818 | 12.2711 | 23.4048
13:28 | 103 | 33.4444 |  | 8.3258 | 3.1934 | 0.8253 | 2.8682 | -1.6967 | 12.3289 | 5.3891 | 0.6348 | 0.6732 | 0.9844 | 0.7694 | -130.0161 | 3.5979 | 6.2157 | 1.7207 | -2.5288 | -1.0137 | 5.1118 |  | 4.9399 | 0.9391 | 3.9782 | 3.3676 | 3.3294 | 1.1022 | 2.8101 | 22.8245 | 22.6396 | 22.3902 | 22.349 | 22.2664 | 22.346 | 22.1698 | 22.9225 | 22.6445 | 22.6852 | 22.6848 | 24.2571 | 23.0286 | 22.9674 | 22.8826 | 22.7764 | 22.6726 | 22.613 | 22.5696 | 22.3816 | 22.4518 | 22.3336 | 22.9237 | 22.5574 | 22.5878 | 22.5737 | 23.2543 | 23.1731 | 22.703 | 22.9583 | 23.0356 | 23.7153 | 23.4911 | 22.8746 | 22.8965 | 22.8628 | 22.8099 | 22.7235 | 22.857 | 22.5237 | 22.2893 | 23.2832 | 22.6719 | 22.7829 | 23.002 | 24.2293 | 23.305 | 23.2666 | 23.2727 | 23.2624 | 24.4885 | 23.0682 | 23.0839 | 23.1171 | 23.0906 | 23.0125 | 23.0288 | 23.0455 | 22.788 | 23.1206 | 22.9262 | 23.1278 | 23.1606 | 23.148 | 23.0763 | 24.1101 | 23.8277 | 23.7264 | 23.7366 | 23.6985 | 24.9255 | 23.3204 | 23.3891 | 23.408 | 23.3682 | 23.3928 | 23.4764 | 23.5113 | 23.1026 | 22.8569 | 23.3099 | 23.3626 | 23.3368 | 23.3137 | 24.055 | 43.6745 | 84.1006 | 26.9368 | 31.5576 | 38.0807 | 39.1585 | 33.2885 | 52.2453 | 43.6401 | 55.1283 | 116.0817 | 110.2847 | 96.1403 | 99.8071 | 94.1513 | 103.0091 | 106.9117 | 109.8658 | 29.0327 | 26.6876 | 30.0105 | 28.0682 | 22.6734 | 22.6015 |  | 22.3057 | 22.2866 | 22.2131 | 22.1822 | 22.1862 | 22.2115 | 23.1786 | 22.5138 | 22.4518 | 24.0877 | 22.4723 | 22.717 | 22.9837 | 22.8938 | 22.836 | 22.7742 | 22.7004 | 22.6733 | 22.6047 | 22.6524 | 23.6491 | 22.7379 | 22.7319 | 23.7534 | 23.9618 | 23.7782 | 22.8851 | 23.0749 | 23.8134 | 23.8918 | 22.9388 | 22.9797 | 22.9434 | 22.9038 | 22.956 | 22.7394 | 22.7182 | 22.6484 | 23.6268 | 22.6024 | 22.72 | 22.9578 | 24.9103 | 23.8572 | 23.7977 | 23.7097 | 23.6557 | 24.1374 | 23.781 | 23.7364 | 23.6494 | 23.5856 | 23.4548 | 23.4476 | 23.1601 | 22.9936 | 23.1329 | 23.0271 | 23.6869 | 23.6067 | 23.5526 | 23.5033 | 24.6378 | 24.1432 | 24.0425 | 23.9285 | 23.8804 | 27.9582 | 23.626 | 23.8393 | 23.7694 | 23.6955 | 23.6405 | 23.7094 | 23.823 | 23.1725 | 23.0348 | 24.1102 | 24.0192 | 24.016 | 23.9755 | 25.2404 | 34.7591 | 39.1251 | 42.245 | 37.9077 | 41.6475 | 47.9061 | 54.4936 | 39.1204 | 52.3921 | 44.5368 |  | 46.1434 | 38.7067 | 43.6311 | 24.6768 | 23.417 | 23.4455 | 26.7567 | 24.6661 | 22.2134 | 23.2039 | 10.8279 | 14.2676 | 14.8804 | 11.0788 | -0.0001185 | -0.0026788 | 0.0014809 | 0.0039694 | 0.0009992 | -0.00023684 | 0.0052536 | -0.0022747 | -0.022373 | -360.1619 | 17.4295 | -360.4481 | 17.6348 | -360.7989 | 18.1214 | -360.7897 | 17.5753 | -352.5613 | 18.6799 | -352.6229 | 16.8156 | 73.904 | 369.0658 | 43.721 | 14.574 | 12.1209 | 23.4398
13:28 | 104 | 33.3968 |  | 8.2989 | 3.2428 | 0.8058 | 2.9136 | -1.7771 | 12.2909 | 5.3966 | 0.6362 | 0.6761 | 0.9771 | 0.77 | -129.9731 | 3.6263 | 6.2933 | 1.6773 | -2.6361 | -1.0024 | 5.0469 |  | 4.9728 | 0.9439 | 3.9776 | 3.3706 | 3.3293 | 1.1014 | 2.1276 | 22.8315 | 22.6419 | 22.3919 | 22.3581 | 22.2652 | 22.3497 | 22.17 | 22.9266 | 22.6459 | 22.6894 | 22.6916 | 24.296 | 23.0311 | 22.9639 | 22.8824 | 22.784 | 22.6786 | 22.6138 | 22.5759 | 22.383 | 22.452 | 22.3442 | 22.9255 | 22.5554 | 22.5947 | 22.5796 | 23.2794 | 23.1807 | 22.7095 | 22.9599 | 23.0395 | 23.7336 | 23.5017 | 22.8722 | 22.8989 | 22.8707 | 22.8122 | 22.7464 | 22.8751 | 22.5461 | 22.2896 | 23.2876 | 22.6737 | 22.7856 | 23.0092 | 24.2631 | 23.2998 | 23.2644 | 23.2749 | 23.2626 | 24.5176 | 23.0709 | 23.0856 | 23.1166 | 23.0872 | 23.0127 | 23.0247 | 23.0536 | 22.7845 | 23.1233 | 22.9251 | 23.1347 | 23.1619 | 23.1479 | 23.0813 | 24.1417 | 23.8314 | 23.728 | 23.7417 | 23.6998 | 24.9626 | 23.3226 | 23.3885 | 23.4103 | 23.3693 | 23.3956 | 23.4819 | 23.5229 | 23.1148 | 22.8636 | 23.3125 | 23.3629 | 23.3389 | 23.313 | 24.076 | 44.1148 | 83.2424 | 27.3174 | 31.8008 | 38.4568 | 39.5615 | 33.4814 | 52.8386 | 43.894 | 55.5058 | 117.2573 | 111.9491 | 97.1228 | 97.8372 | 92.6044 | 105.4364 | 106.6976 | 109.5408 | 29.1947 | 26.8069 | 30.2132 | 28.2215 | 22.6695 | 22.5952 |  | 22.3083 | 22.2807 | 22.2122 | 22.1802 | 22.1841 | 22.2113 | 23.1788 | 22.5133 | 22.4508 | 24.1148 | 22.4679 | 22.7139 | 22.9937 | 22.8996 | 22.8426 | 22.7725 | 22.7065 | 22.676 | 22.6115 | 22.6653 | 23.6592 | 22.7399 | 22.7392 | 23.7578 | 23.9997 | 23.7818 | 22.8883 | 23.0793 | 23.8284 | 23.8921 | 22.9388 | 22.9844 | 22.9491 | 22.9083 | 22.9624 | 22.7455 | 22.7231 | 22.6539 | 23.6288 | 22.6046 | 22.7179 | 22.9622 | 24.9542 | 23.8671 | 23.8043 | 23.7137 | 23.6552 | 24.1514 | 23.7792 | 23.7375 | 23.6524 | 23.5808 | 23.4532 | 23.4472 | 23.1604 | 22.9909 | 23.1544 | 23.0346 | 23.6848 | 23.6103 | 23.5576 | 23.5168 | 24.6682 | 24.1401 | 24.0443 | 23.935 | 23.8816 | 28.0193 | 23.6303 | 23.8394 | 23.7774 | 23.6986 | 23.6397 | 23.7141 | 23.8285 | 23.1727 | 23.036 | 24.1092 | 24.0175 | 24.0104 | 23.9713 | 25.2691 | 34.9962 | 39.2665 | 42.3771 | 38.0566 | 41.9996 | 48.3488 | 55.2224 | 39.4504 | 52.9143 | 44.9989 |  | 46.7548 | 39.099 | 43.9656 | 24.6741 | 23.4213 | 23.4492 | 26.8579 | 24.7333 | 22.2296 | 23.2377 | 10.8403 | 14.288 | 14.9263 | 11.1038 | -0.00024635 | -0.0027966 | 0.001941 | 0.0044517 | 0.0021933 | -0.00038373 | 0.0088673 | -0.011611 | -0.023222 | -360.1404 | 17.3925 | -360.3712 | 17.6143 | -360.7989 | 18.1645 | -360.8481 | 17.6081 | -352.5644 | 18.6388 | -352.5952 | 16.8115 | 75.8948 | 365.3947 | 44.1761 | 14.6072 | 12.0522 | 23.4814
13:28 | 105 | 33.4459 |  | 8.279 | 3.1918 | 0.7863 | 2.9137 | -1.6451 | 12.4027 | 5.4816 | 0.6343 | 0.6731 | 0.9796 | 0.7685 | -129.9849 | 3.5706 | 6.2937 | 1.6284 | -2.6303 | -1.0148 | 5.0114 |  | 4.908 | 0.9159 | 3.9785 | 3.3711 | 3.3318 | 1.1017 | 2.394 | 22.8397 | 22.6436 | 22.3883 | 22.3579 | 22.2673 | 22.3595 | 22.1689 | 22.9294 | 22.6493 | 22.6949 | 22.6961 | 24.3297 | 23.0332 | 22.965 | 22.8885 | 22.7869 | 22.683 | 22.6197 | 22.5746 | 22.3878 | 22.4575 | 22.3557 | 22.9287 | 22.5631 | 22.5986 | 22.5872 | 23.3053 | 23.1853 | 22.7146 | 22.9698 | 23.0467 | 23.7635 | 23.502 | 22.8744 | 22.9077 | 22.8739 | 22.8136 | 22.76 | 22.8898 | 22.5282 | 22.2975 | 23.2829 | 22.6758 | 22.7809 | 23.0111 | 24.2906 | 23.2994 | 23.2711 | 23.2716 | 23.265 | 24.5468 | 23.0778 | 23.0785 | 23.1202 | 23.0883 | 23.0122 | 23.0278 | 23.0356 | 22.7929 | 23.1591 | 22.9277 | 23.1327 | 23.1616 | 23.1438 | 23.0769 | 24.1658 | 23.8216 | 23.7303 | 23.7475 | 23.6969 | 24.9961 | 23.3179 | 23.3836 | 23.41 | 23.3712 | 23.3893 | 23.481 | 23.5287 | 23.1165 | 22.8629 | 23.3153 | 23.3605 | 23.3352 | 23.3089 | 24.0954 | 44.6243 | 82.1179 | 27.7404 | 31.9901 | 38.8419 | 39.9457 | 33.675 | 53.4108 | 44.1458 | 55.9335 | 117.4399 | 113.4654 | 96.1644 | 97.1207 | 95.945 | 107.4133 | 107.5987 | 108.7005 | 29.3728 | 26.9302 | 30.4291 | 28.3787 | 22.6711 | 22.5989 |  | 22.3131 | 22.2799 | 22.2186 | 22.1758 | 22.1929 | 22.2208 | 23.1817 | 22.5151 | 22.4525 | 24.1453 | 22.4714 | 22.7154 | 23.004 | 22.9138 | 22.8475 | 22.7892 | 22.72 | 22.6853 | 22.6321 | 22.6814 | 23.6737 | 22.7508 | 22.7534 | 23.7683 | 24.0431 | 23.7904 | 22.9013 | 23.0798 | 23.8447 | 23.8945 | 22.9413 | 22.9842 | 22.9548 | 22.9053 | 22.9717 | 22.7484 | 22.727 | 22.6562 | 23.6295 | 22.6048 | 22.7125 | 22.9619 | 24.9923 | 23.8705 | 23.8032 | 23.7123 | 23.6529 | 24.1588 | 23.7725 | 23.737 | 23.6516 | 23.5774 | 23.4528 | 23.4378 | 23.1781 | 22.9929 | 23.1773 | 23.0313 | 23.6817 | 23.6069 | 23.5523 | 23.5136 | 24.6885 | 24.1294 | 24.0419 | 23.9316 | 23.8797 | 28.0774 | 23.6315 | 23.8374 | 23.7809 | 23.6986 | 23.6375 | 23.7097 | 23.8382 | 23.179 | 23.0422 | 24.1077 | 24.0157 | 24.0195 | 23.9652 | 25.297 | 35.2493 | 39.3344 | 42.4945 | 38.2809 | 42.3533 | 48.8013 | 55.9427 | 39.7692 | 53.4344 | 45.4838 |  | 47.3729 | 39.5018 | 44.306 | 24.6743 | 23.4283 | 23.4479 | 26.9594 | 24.7831 | 22.2485 | 23.2664 | 10.8264 | 14.2522 | 14.8871 | 11.1122 | 0.0005116 | -0.0029446 | 0.0016875 | 0.0043408 | 0.001062 | -0.00028754 | 0.012305 | -0.0071078 | -0.017231 | -360.1896 | 17.4582 | -360.4881 | 17.6369 | -360.845 | 18.144 | -360.8174 | 17.6061 | -352.6321 | 18.7128 | -352.6567 | 16.8299 | 79.4158 | 367.1863 | 44.6332 | 14.5697 | 12.0686 | 23.5158
13:28 | 106 | 33.2707 |  | 8.3042 | 3.2391 | 0.7891 | 2.8921 | -1.644 | 12.3287 | 5.3927 | 0.6346 | 0.6734 | 0.9816 | 0.769 | -130.0176 | 3.5201 | 6.2838 | 1.6781 | -2.5629 | -0.9979 | 5.0297 |  | 4.8463 | 0.8464 | 3.9788 | 3.3694 | 3.333 | 1.1011 | 1.6411 | 22.841 | 22.6476 | 22.393 | 22.3616 | 22.2727 | 22.368 | 22.1759 | 22.9332 | 22.654 | 22.6973 | 22.6978 | 24.3668 | 23.0407 | 22.9668 | 22.8925 | 22.7835 | 22.6807 | 22.6161 | 22.5626 | 22.3866 | 22.4619 | 22.3627 | 22.9268 | 22.5668 | 22.5942 | 22.5815 | 23.3234 | 23.18 | 22.7055 | 22.9619 | 23.0506 | 23.7925 | 23.5085 | 22.8703 | 22.9133 | 22.8745 | 22.8239 | 22.7441 | 22.8968 | 22.5352 | 22.3086 | 23.2838 | 22.6814 | 22.7823 | 23.0124 | 24.3167 | 23.3041 | 23.2699 | 23.2735 | 23.271 | 24.5794 | 23.0682 | 23.0719 | 23.1215 | 23.0861 | 23.0084 | 23.0346 | 23.0367 | 22.7912 | 23.1736 | 22.9302 | 23.138 | 23.1612 | 23.1455 | 23.071 | 24.1849 | 23.8248 | 23.7235 | 23.75 | 23.7008 | 25.0286 | 23.3201 | 23.3825 | 23.409 | 23.373 | 23.3875 | 23.4803 | 23.5354 | 23.1087 | 22.8633 | 23.313 | 23.3556 | 23.3248 | 23.3055 | 24.1128 | 44.9346 | 81.4029 | 27.9402 | 32.1016 | 39.2353 | 40.3317 | 33.8655 | 53.9287 | 44.4189 | 56.3954 | 116.3008 | 113.4548 | 97.9402 | 97.0788 | 99.169 | 109.3429 | 108.1012 | 110.2589 | 29.5544 | 27.0566 | 30.66 | 28.5482 | 22.6675 | 22.6097 |  | 22.3167 | 22.2826 | 22.2189 | 22.182 | 22.1982 | 22.2241 | 23.1841 | 22.517 | 22.4559 | 24.1727 | 22.4788 | 22.715 | 22.998 | 22.914 | 22.8475 | 22.782 | 22.7223 | 22.6862 | 22.6358 | 22.6796 | 23.6706 | 22.7474 | 22.7513 | 23.7733 | 24.0681 | 23.7927 | 22.9 | 23.0784 | 23.8584 | 23.8933 | 22.9425 | 22.9854 | 22.9518 | 22.9044 | 22.9771 | 22.7411 | 22.7305 | 22.6571 | 23.6242 | 22.6003 | 22.7089 | 22.9584 | 25.0325 | 23.8639 | 23.7998 | 23.7169 | 23.6539 | 24.1622 | 23.772 | 23.7376 | 23.6522 | 23.5762 | 23.4569 | 23.4424 | 23.1827 | 22.9924 | 23.1759 | 23.031 | 23.6845 | 23.6023 | 23.5521 | 23.5027 | 24.7167 | 24.1322 | 24.0392 | 23.9256 | 23.8803 | 28.1378 | 23.6265 | 23.8349 | 23.7778 | 23.6881 | 23.6316 | 23.7081 | 23.8425 | 23.1857 | 23.043 | 24.1057 | 24.0173 | 24.013 | 23.9649 | 25.3219 | 35.4728 | 39.4006 | 42.8982 | 38.5128 | 42.6994 | 49.2471 | 56.6528 | 40.0677 | 53.9793 | 45.9676 |  | 47.9818 | 39.9345 | 44.6539 | 24.6723 | 23.4274 | 23.4513 | 27.0677 | 24.8422 | 22.2592 | 23.3059 | 10.83 | 14.2907 | 14.9098 | 11.1305 | 0.0001735 | -0.0032299 | 0.0016778 | 0.0047086 | 0.0014328 | -0.00060353 | 0.0029831 | -0.0047855 | -0.015811 | -360.1465 | 17.3946 | -360.3835 | 17.6061 | -360.765 | 18.1687 | -360.882 | 17.604 | -352.5952 | 18.6491 | -352.5521 | 16.7889 | 86.6709 | 366.4429 | 45.0921 | 14.6003 | 12.0425 | 23.5507
13:28 | 107 | 33.1817 |  | 8.3575 | 3.1808 | 0.8001 | 2.9175 | -1.7533 | 12.2322 | 5.3865 | 0.6345 | 0.6738 | 0.9795 | 0.7689 | -130.0679 | 3.3781 | 6.2084 | 1.7036 | -2.5582 | -0.9614 | 5.0629 |  | 4.7954 | 0.8725 | 3.9783 | 3.3719 | 3.333 | 1.0996 | 3.4453 | 22.8483 | 22.6547 | 22.4016 | 22.3685 | 22.2804 | 22.3757 | 22.1859 | 22.9367 | 22.6615 | 22.7014 | 22.6999 | 24.4055 | 23.0424 | 22.9675 | 22.8956 | 22.7895 | 22.6838 | 22.6176 | 22.5745 | 22.3987 | 22.4698 | 22.3736 | 22.9324 | 22.5698 | 22.5964 | 22.5874 | 23.35 | 23.1847 | 22.7155 | 22.9635 | 23.0498 | 23.8117 | 23.506 | 22.8706 | 22.9154 | 22.8825 | 22.8261 | 22.7603 | 22.9287 | 22.5683 | 22.3178 | 23.2856 | 22.6799 | 22.7817 | 23.0179 | 24.3538 | 23.3129 | 23.2592 | 23.2792 | 23.276 | 24.61 | 23.0751 | 23.0797 | 23.1179 | 23.081 | 23.0083 | 23.0397 | 23.0569 | 22.7912 | 23.1757 | 22.9298 | 23.1385 | 23.1628 | 23.1505 | 23.0721 | 24.2042 | 23.8302 | 23.7246 | 23.742 | 23.7003 | 25.0602 | 23.3184 | 23.3851 | 23.4027 | 23.3742 | 23.3842 | 23.4816 | 23.5594 | 23.1215 | 22.8734 | 23.306 | 23.3601 | 23.3327 | 23.3103 | 24.1346 | 45.3718 | 81.0187 | 28.0598 | 32.1945 | 39.6292 | 40.7261 | 34.0839 | 54.3856 | 44.7049 | 56.8515 | 115.2616 | 112.7681 | 99.9622 | 98.1299 | 101.9095 | 111.7501 | 108.1768 | 111.9653 | 29.7467 | 27.1784 | 30.9025 | 28.7118 | 22.6683 | 22.6095 |  | 22.3207 | 22.2849 | 22.2182 | 22.1794 | 22.1959 | 22.2228 | 23.1839 | 22.5105 | 22.4535 | 24.193 | 22.4729 | 22.7061 | 22.9897 | 22.9029 | 22.8407 | 22.7576 | 22.7121 | 22.6824 | 22.614 | 22.6694 | 23.6611 | 22.7338 | 22.7425 | 23.7678 | 24.0865 | 23.7839 | 22.8898 | 23.0834 | 23.8769 | 23.8887 | 22.9436 | 22.9887 | 22.9484 | 22.907 | 22.989 | 22.7416 | 22.7352 | 22.6621 | 23.6293 | 22.5961 | 22.715 | 22.9663 | 25.0831 | 23.864 | 23.8022 | 23.723 | 23.6632 | 24.1798 | 23.7652 | 23.745 | 23.6574 | 23.5833 | 23.4661 | 23.4466 | 23.1888 | 22.9976 | 23.1878 | 23.0415 | 23.6906 | 23.6032 | 23.5584 | 23.5054 | 24.7451 | 24.14 | 24.0467 | 23.9277 | 23.8793 | 28.2079 | 23.6266 | 23.8335 | 23.7833 | 23.6893 | 23.6337 | 23.7178 | 23.8454 | 23.1855 | 23.0407 | 24.1087 | 24.0141 | 24.0054 | 23.9642 | 25.3544 | 35.6481 | 39.4637 | 43.3811 | 38.7442 | 43.038 | 49.7152 | 57.3565 | 40.3604 | 54.5322 | 46.4704 |  | 48.5632 | 40.3734 | 45.0178 | 24.6745 | 23.423 | 23.4502 | 27.1732 | 24.9049 | 22.2725 | 23.3398 | 10.8305 | 14.2851 | 14.9088 | 11.1011 | 0.00020274 | -0.0026989 | 0.001498 | 0.0041248 | 0.0014243 | -0.00047586 | 0.0081554 | -0.00037969 | -0.013095 | -360.1558 | 17.448 | -360.4481 | 17.6245 | -360.7927 | 18.1173 | -360.7558 | 17.5855 | -352.6198 | 18.6943 | -352.6537 | 16.8299 | 107.3855 | 365.218 | 45.5524 | 14.597 | 12.0108 | 23.5887
13:28 | 108 | 33.2437 |  | 8.2999 | 3.0786 | 0.7223 | 2.9356 | -1.6699 | 12.3083 | 5.4344 | 0.6351 | 0.6747 | 0.9768 | 0.7701 | -130.0924 | 3.4193 | 6.1869 | 1.7314 | -2.6291 | -1.0992 | 5.0982 |  | 4.8334 | 0.9503 | 3.9776 | 3.3707 | 3.3296 | 1.0995 | 3.3898 | 22.8481 | 22.656 | 22.3996 | 22.3631 | 22.281 | 22.3797 | 22.1847 | 22.9289 | 22.6548 | 22.6974 | 22.6983 | 24.4388 | 23.0358 | 22.9669 | 22.8953 | 22.7905 | 22.6908 | 22.6216 | 22.5901 | 22.4048 | 22.4764 | 22.3803 | 22.9317 | 22.5689 | 22.6028 | 22.5966 | 23.3738 | 23.1885 | 22.726 | 22.9687 | 23.0525 | 23.8395 | 23.4914 | 22.8817 | 22.9174 | 22.8822 | 22.8184 | 22.7864 | 22.9476 | 22.5808 | 22.3144 | 23.2811 | 22.6755 | 22.7792 | 23.0115 | 24.3905 | 23.3119 | 23.2597 | 23.281 | 23.2816 | 24.643 | 23.0831 | 23.0844 | 23.1218 | 23.082 | 23.0161 | 23.0369 | 23.0602 | 22.7911 | 23.1843 | 22.9271 | 23.1365 | 23.1682 | 23.1525 | 23.0783 | 24.2272 | 23.8282 | 23.7337 | 23.7376 | 23.7001 | 25.0995 | 23.3169 | 23.3862 | 23.4036 | 23.3735 | 23.3876 | 23.4856 | 23.5763 | 23.1356 | 22.8838 | 23.3154 | 23.3661 | 23.3349 | 23.3176 | 24.1572 | 45.9898 | 81.4063 | 28.2465 | 32.2848 | 40.0247 | 41.1261 | 34.3446 | 54.8088 | 44.9829 | 57.319 | 116.3741 | 113.321 | 102.4079 | 100.4024 | 104.6103 | 113.7979 | 109.3499 | 113.4608 | 29.9486 | 27.3137 | 31.142 | 28.8717 | 22.6869 | 22.623 |  | 22.3284 | 22.299 | 22.2324 | 22.1805 | 22.1974 | 22.2271 | 23.1835 | 22.5089 | 22.4551 | 24.2242 | 22.478 | 22.7041 | 22.997 | 22.9048 | 22.8364 | 22.7641 | 22.7151 | 22.6834 | 22.6107 | 22.6753 | 23.6577 | 22.7399 | 22.743 | 23.7638 | 24.1175 | 23.7812 | 22.8952 | 23.0888 | 23.8935 | 23.8884 | 22.9431 | 22.9826 | 22.9503 | 22.9065 | 23.0002 | 22.7472 | 22.7438 | 22.6707 | 23.6278 | 22.6002 | 22.7194 | 22.97 | 25.1276 | 23.8668 | 23.8009 | 23.7225 | 23.6693 | 24.1984 | 23.7553 | 23.7465 | 23.6514 | 23.5858 | 23.4646 | 23.4381 | 23.2051 | 23.0041 | 23.2086 | 23.0519 | 23.6908 | 23.6129 | 23.5602 | 23.51 | 24.7777 | 24.1421 | 24.0452 | 23.9345 | 23.8784 | 28.2847 | 23.6298 | 23.839 | 23.7838 | 23.695 | 23.6361 | 23.7338 | 23.8604 | 23.192 | 23.0491 | 24.1108 | 24.0108 | 24.0128 | 23.9688 | 25.3918 | 35.8202 | 39.5543 | 43.6439 | 39.0184 | 43.3792 | 50.2288 | 58.0501 | 40.6492 | 55.0935 | 46.9601 |  | 49.1183 | 40.8098 | 45.3877 | 24.676 | 23.4285 | 23.4548 | 27.2712 | 24.9598 | 22.2903 | 23.3798 | 10.8314 | 14.264 | 14.9045 | 11.1036 | -0.00035654 | -0.0029148 | 0.0010327 | 0.0038726 | 0.0012788 | -0.00047528 | 0.024607 | -0.0034747 | -0.034832 | -360.2111 | 17.4192 | -360.3927 | 17.6122 | -360.802 | 18.1748 | -360.9158 | 17.641 | -352.629 | 18.6799 | -352.6075 | 16.8176 | 106.8221 | 369.5538 | 46.0156 | 14.5842 | 11.9983 | 23.6251
13:28 | 109 | 33.1086 |  | 8.3522 | 3.1987 | 0.701 | 2.8829 | -1.6404 | 12.3405 | 5.4022 | 0.6349 | 0.6739 | 0.9787 | 0.7702 | -130.1655 | 3.3989 | 6.1544 | 1.6402 | -2.614 | -1.0431 | 5.0621 |  | 4.8979 | 0.8618 | 3.9769 | 3.3704 | 3.3316 | 1.0994 | 2.6195 | 22.854 | 22.6616 | 22.401 | 22.3642 | 22.2869 | 22.3881 | 22.1854 | 22.9297 | 22.6561 | 22.6998 | 22.7028 | 24.4797 | 23.0388 | 22.9685 | 22.8965 | 22.789 | 22.6944 | 22.6208 | 22.5982 | 22.4092 | 22.4814 | 22.3862 | 22.9317 | 22.5682 | 22.6111 | 22.5978 | 23.3952 | 23.1863 | 22.7284 | 22.9693 | 23.0537 | 23.8599 | 23.4886 | 22.8833 | 22.9208 | 22.8714 | 22.8179 | 22.7811 | 22.9467 | 22.5696 | 22.3115 | 23.273 | 22.6714 | 22.7794 | 23 | 24.4169 | 23.3101 | 23.2645 | 23.2838 | 23.2794 | 24.6752 | 23.0811 | 23.0843 | 23.1308 | 23.0875 | 23.0185 | 23.0455 | 23.0738 | 22.7959 | 23.1946 | 22.9185 | 23.1409 | 23.171 | 23.1529 | 23.0841 | 24.2508 | 23.8267 | 23.7318 | 23.7406 | 23.7031 | 25.1336 | 23.3188 | 23.3864 | 23.4103 | 23.3718 | 23.3934 | 23.4933 | 23.5859 | 23.1432 | 22.886 | 23.319 | 23.3699 | 23.3368 | 23.3207 | 24.1808 | 46.5174 | 81.2478 | 28.3512 | 32.3312 | 40.4139 | 41.5291 | 34.636 | 55.1949 | 45.2571 | 57.761 | 117.9183 | 115.3586 | 105.9841 | 103.4894 | 107.0605 | 114.6348 | 109.6067 | 114.0453 | 30.1533 | 27.4538 | 31.3761 | 29.0289 | 22.6897 | 22.6296 |  | 22.3271 | 22.3032 | 22.2349 | 22.184 | 22.2048 | 22.2299 | 23.1839 | 22.5105 | 22.4548 | 24.251 | 22.4789 | 22.7057 | 22.9996 | 22.9116 | 22.8472 | 22.7748 | 22.7226 | 22.6898 | 22.6193 | 22.6882 | 23.6624 | 22.7507 | 22.7465 | 23.7695 | 24.1502 | 23.788 | 22.9014 | 23.0825 | 23.9047 | 23.8886 | 22.9374 | 22.9774 | 22.9503 | 22.9064 | 23.0016 | 22.7523 | 22.7449 | 22.6736 | 23.6214 | 22.5982 | 22.7147 | 22.9656 | 25.1689 | 23.8619 | 23.8008 | 23.7195 | 23.6677 | 24.2093 | 23.7603 | 23.7402 | 23.6499 | 23.5815 | 23.4575 | 23.4406 | 23.2085 | 23.0069 | 23.2107 | 23.0526 | 23.6852 | 23.6136 | 23.5592 | 23.5146 | 24.812 | 24.1392 | 24.0388 | 23.9352 | 23.8817 | 28.3666 | 23.6293 | 23.8436 | 23.7792 | 23.6936 | 23.6329 | 23.7385 | 23.8742 | 23.2066 | 23.0597 | 24.1112 | 24.0141 | 24.016 | 23.9751 | 25.4271 | 35.9945 | 39.6969 | 43.7427 | 39.2446 | 43.7281 | 50.7693 | 58.7464 | 40.9504 | 55.6661 | 47.405 |  | 49.6306 | 41.2573 | 45.7518 | 24.6745 | 23.429 | 23.4537 | 27.3725 | 25.0141 | 22.3065 | 23.4124 | 10.8102 | 14.2642 | 14.8987 | 11.1102 | 0.00037815 | -0.0031473 | 0.0014138 | 0.0043015 | 0.0011175 | -0.00030376 | 0.015467 | 0.00078794 | -0.019839 | -360.1219 | 17.4459 | -360.4758 | 17.6553 | -360.8389 | 18.1194 | -360.7466 | 17.5609 | -352.5583 | 18.6984 | -352.6752 | 16.8505 | 110.7429 | 364.9084 | 46.4783 | 14.5814 | 12.0126 | 23.6603
13:28 | 110 | 33.0577 |  | 8.3989 | 3.1941 | 0.7049 | 2.9169 | -1.6414 | 12.3342 | 5.3569 | 0.6353 | 0.6715 | 0.9811 | 0.7714 | -130.1202 | 3.2749 | 6.2681 | 1.6646 | -2.6506 | -1.1039 | 5.0486 |  | 4.888 | 0.8899 | 3.977 | 3.3696 | 3.329 | 1.101 | 3.1757 | 22.8545 | 22.6622 | 22.3991 | 22.3612 | 22.2851 | 22.3907 | 22.1943 | 22.9353 | 22.6567 | 22.6983 | 22.7057 | 24.5142 | 23.0404 | 22.9691 | 22.8971 | 22.7941 | 22.6913 | 22.6249 | 22.5931 | 22.4121 | 22.4881 | 22.3917 | 22.9353 | 22.5715 | 22.6165 | 22.6017 | 23.4225 | 23.1956 | 22.7256 | 22.9711 | 23.0536 | 23.8779 | 23.491 | 22.8794 | 22.9231 | 22.8728 | 22.8204 | 22.7792 | 22.967 | 22.5708 | 22.3111 | 23.2735 | 22.6714 | 22.777 | 22.9958 | 24.4489 | 23.3133 | 23.2618 | 23.2755 | 23.274 | 24.6992 | 23.0817 | 23.0825 | 23.1314 | 23.0897 | 23.0072 | 23.0561 | 23.075 | 22.7994 | 23.2053 | 22.9089 | 23.138 | 23.1767 | 23.153 | 23.0779 | 24.2729 | 23.8191 | 23.7236 | 23.7408 | 23.7016 | 25.1629 | 23.3175 | 23.3847 | 23.4074 | 23.3699 | 23.3904 | 23.4912 | 23.5915 | 23.1506 | 22.8833 | 23.32 | 23.3685 | 23.3349 | 23.3189 | 24.2054 | 46.4538 | 81.0993 | 28.3549 | 32.3622 | 40.7994 | 41.9398 | 34.9466 | 55.552 | 45.5716 | 58.2218 | 118.6753 | 116.9406 | 108.6093 | 106.5121 | 108.5641 | 113.587 | 108.1305 | 113.8933 | 30.3718 | 27.5813 | 31.5988 | 29.1997 | 22.6788 | 22.6173 |  | 22.321 | 22.2977 | 22.2262 | 22.1787 | 22.2078 | 22.2269 | 23.1817 | 22.5112 | 22.451 | 24.2744 | 22.4676 | 22.7035 | 22.997 | 22.9118 | 22.8546 | 22.7706 | 22.7203 | 22.6898 | 22.6096 | 22.6941 | 23.6651 | 22.7514 | 22.7447 | 23.7713 | 24.1774 | 23.79 | 22.8988 | 23.0794 | 23.9232 | 23.8881 | 22.9376 | 22.9791 | 22.9545 | 22.9047 | 23.005 | 22.7548 | 22.7507 | 22.6757 | 23.6225 | 22.5997 | 22.7162 | 22.9639 | 25.2082 | 23.8617 | 23.8021 | 23.7175 | 23.6604 | 24.2159 | 23.7611 | 23.7406 | 23.6577 | 23.5833 | 23.4581 | 23.4481 | 23.2037 | 23.0127 | 23.2124 | 23.056 | 23.686 | 23.6069 | 23.5532 | 23.5144 | 24.8373 | 24.1389 | 24.0433 | 23.931 | 23.8872 | 28.4442 | 23.6267 | 23.839 | 23.7772 | 23.69 | 23.6348 | 23.7327 | 23.884 | 23.2131 | 23.0581 | 24.1091 | 24.0139 | 24.01 | 23.9727 | 25.4549 | 36.1279 | 39.8883 | 43.8414 | 39.3858 | 44.082 | 51.3126 | 59.4448 | 41.2613 | 56.2136 | 47.818 |  | 50.124 | 41.7078 | 46.114 | 24.6772 | 23.4278 | 23.4472 | 27.4777 | 25.0688 | 22.3202 | 23.4445 | 10.8249 | 14.251 | 14.8656 | 11.0893 | 0.00024839 | -0.0034688 | 0.0021049 | 0.0040536 | 0.0012887 | -0.00059667 | 0.024651 | 0.0045845 | -0.010561 | -360.1711 | 17.3987 | -360.3773 | 17.5876 | -360.7743 | 18.1481 | -360.8543 | 17.6163 | -352.6198 | 18.6553 | -352.5829 | 16.7991 | 110.0845 | 368.6478 | 46.9406 | 14.5583 | 12.0003 | 23.6945
13:28 | 111 | 33.1597 |  | 8.3443 | 3.1628 | 0.7358 | 2.9372 | -1.6815 | 12.3261 | 5.3345 | 0.6361 | 0.675 | 0.9782 | 0.7707 | -130.1338 | 3.3078 | 6.2815 | 1.5535 | -2.6313 | -1.1689 | 5.0301 |  | 4.8527 | 0.8049 | 3.9778 | 3.3683 | 3.3294 | 1.1002 | 1.9159 | 22.8619 | 22.6652 | 22.3975 | 22.3644 | 22.2813 | 22.3942 | 22.1933 | 22.9353 | 22.6567 | 22.7007 | 22.7086 | 24.5553 | 23.0383 | 22.9719 | 22.8998 | 22.7944 | 22.6902 | 22.6283 | 22.5872 | 22.4136 | 22.5006 | 22.3986 | 22.9362 | 22.5724 | 22.6125 | 22.6037 | 23.4504 | 23.2048 | 22.7264 | 22.975 | 23.0609 | 23.9089 | 23.4995 | 22.8803 | 22.9242 | 22.8842 | 22.8289 | 22.801 | 22.9851 | 22.5827 | 22.316 | 23.2796 | 22.6748 | 22.7818 | 23.0025 | 24.4803 | 23.3121 | 23.2653 | 23.2662 | 23.2702 | 24.727 | 23.0843 | 23.0766 | 23.127 | 23.0804 | 23.0008 | 23.0625 | 23.0772 | 22.7901 | 23.201 | 22.906 | 23.1392 | 23.1784 | 23.1513 | 23.0767 | 24.2971 | 23.8202 | 23.7294 | 23.739 | 23.704 | 25.2081 | 23.3199 | 23.3874 | 23.407 | 23.3724 | 23.3881 | 23.493 | 23.5921 | 23.1483 | 22.8856 | 23.3199 | 23.3593 | 23.3263 | 23.317 | 24.2267 | 46.1744 | 81.8304 | 28.3391 | 32.4041 | 41.1857 | 42.3589 | 35.2429 | 55.897 | 45.9097 | 58.722 | 119.584 | 117.8901 | 110.6487 | 108.1886 | 110.2655 | 112.3363 | 108.6919 | 115.145 | 30.5871 | 27.7057 | 31.8163 | 29.3775 | 22.6762 | 22.6142 |  | 22.3207 | 22.2956 | 22.2237 | 22.1792 | 22.212 | 22.2238 | 23.1832 | 22.5142 | 22.4502 | 24.3015 | 22.4648 | 22.6985 | 22.9958 | 22.9058 | 22.8437 | 22.7605 | 22.7158 | 22.6844 | 22.5966 | 22.686 | 23.6638 | 22.7437 | 22.7389 | 23.7631 | 24.2099 | 23.7847 | 22.8908 | 23.0811 | 23.9424 | 23.8903 | 22.9403 | 22.9798 | 22.9546 | 22.904 | 23.0152 | 22.7595 | 22.7612 | 22.6834 | 23.6257 | 22.6095 | 22.7183 | 22.9664 | 25.252 | 23.8651 | 23.8025 | 23.7201 | 23.6568 | 24.2234 | 23.7732 | 23.7429 | 23.658 | 23.5824 | 23.4582 | 23.4486 | 23.2087 | 23.0252 | 23.2271 | 23.0647 | 23.6886 | 23.605 | 23.5498 | 23.5141 | 24.8622 | 24.1413 | 24.0459 | 23.927 | 23.892 | 28.5242 | 23.6265 | 23.8375 | 23.7869 | 23.6934 | 23.6387 | 23.7335 | 23.8979 | 23.2188 | 23.0603 | 24.1163 | 24.0195 | 24.0103 | 23.9711 | 25.4856 | 36.245 | 40.0777 | 43.9617 | 39.517 | 44.4453 | 51.8254 | 60.1423 | 41.5838 | 56.7192 | 48.2231 |  | 50.6086 | 42.1527 | 46.4896 | 24.6764 | 23.4285 | 23.4529 | 27.5775 | 25.1243 | 22.3313 | 23.4884 | 10.8249 | 14.2862 | 14.8867 | 11.1175 | 0.00010733 | -0.0026468 | 0.0018472 | 0.0046416 | 0.0016633 | -0.0005027 | 0.017544 | -0.0097922 | -0.024976 | -360.1158 | 17.448 | -360.5066 | 17.6718 | -360.9066 | 18.1461 | -360.7897 | 17.5855 | -352.5644 | 18.6963 | -352.6906 | 16.8731 | 126.4823 | 363.006 | 47.4011 | 14.5865 | 11.8801 | 23.7278
13:28 | 112 | 33.1337 |  | 8.3686 | 3.1726 | 0.8203 | 2.975 | -1.556 | 12.3266 | 5.35 | 0.6365 | 0.673 | 0.9812 | 0.7709 | -130.2555 | 3.3965 | 6.1989 | 1.4857 | -2.6254 | -1.1347 | 4.9976 |  | 4.9476 | 0.7967 | 3.9793 | 3.3681 | 3.3275 | 1.0984 | 2.8784 | 22.8766 | 22.6686 | 22.4027 | 22.3743 | 22.2922 | 22.4034 | 22.1925 | 22.9423 | 22.6648 | 22.7054 | 22.7109 | 24.5913 | 23.0443 | 22.9743 | 22.8976 | 22.7934 | 22.6875 | 22.6286 | 22.5972 | 22.4129 | 22.5041 | 22.4007 | 22.9359 | 22.5673 | 22.6145 | 22.5998 | 23.471 | 23.1989 | 22.7245 | 22.9758 | 23.0643 | 23.9439 | 23.5029 | 22.8867 | 22.9263 | 22.8877 | 22.8335 | 22.7955 | 22.9825 | 22.5706 | 22.3277 | 23.2793 | 22.6753 | 22.7889 | 23.0113 | 24.5167 | 23.3139 | 23.2686 | 23.2776 | 23.2767 | 24.767 | 23.0904 | 23.0834 | 23.1306 | 23.0844 | 23.0097 | 23.0683 | 23.0941 | 22.8036 | 23.1957 | 22.9159 | 23.1492 | 23.1851 | 23.1569 | 23.092 | 24.3216 | 23.8294 | 23.7437 | 23.7451 | 23.7126 | 25.246 | 23.3235 | 23.3922 | 23.4146 | 23.3729 | 23.3915 | 23.4979 | 23.6034 | 23.1513 | 22.8915 | 23.3117 | 23.3628 | 23.3306 | 23.3151 | 24.2451 | 46.0866 | 82.5702 | 28.3139 | 32.4389 | 41.5627 | 42.77 | 35.5015 | 56.234 | 46.2315 | 59.1732 | 121.2395 | 119.2435 | 112.4772 | 109.5725 | 112.1188 | 112.5413 | 108.2456 | 117.7862 | 30.7837 | 27.8373 | 32.0387 | 29.5683 | 22.677 | 22.6183 |  | 22.3206 | 22.2891 | 22.2204 | 22.1806 | 22.2174 | 22.2304 | 23.1859 | 22.5179 | 22.4527 | 24.333 | 22.4701 | 22.6987 | 23.0033 | 22.903 | 22.8426 | 22.7574 | 22.7184 | 22.6849 | 22.6042 | 22.6844 | 23.6653 | 22.7455 | 22.7397 | 23.7634 | 24.2456 | 23.7865 | 22.888 | 23.0847 | 23.9593 | 23.8914 | 22.9408 | 22.9839 | 22.9513 | 22.9112 | 23.0292 | 22.7705 | 22.7639 | 22.6926 | 23.6313 | 22.6089 | 22.7193 | 22.9734 | 25.2953 | 23.8622 | 23.7974 | 23.719 | 23.6653 | 24.2384 | 23.7708 | 23.7397 | 23.6503 | 23.5809 | 23.4559 | 23.4454 | 23.2215 | 23.0341 | 23.2443 | 23.0767 | 23.6841 | 23.6086 | 23.5544 | 23.5213 | 24.8923 | 24.1419 | 24.0449 | 23.9348 | 23.8961 | 28.6101 | 23.6262 | 23.8417 | 23.786 | 23.7011 | 23.6375 | 23.7419 | 23.9032 | 23.2252 | 23.066 | 24.1168 | 24.0231 | 24.0186 | 23.9745 | 25.5162 | 36.3619 | 40.2428 | 44.0717 | 39.633 | 44.8246 | 52.33 | 60.8193 | 41.9181 | 57.2123 | 48.6531 |  | 51.1056 | 42.609 | 46.8491 | 24.6776 | 23.4315 | 23.4547 | 27.6896 | 25.1788 | 22.3509 | 23.5231 | 10.8094 | 14.2568 | 14.9005 | 11.1227 | 0.00036134 | -0.0024899 | 0.0018664 | 0.0048954 | 0.0011409 | -0.00057692 | 0.013483 | -0.0028282 | -0.034393 | -360.1681 | 17.4048 | -360.3773 | 17.5794 | -360.7435 | 18.1604 | -360.8266 | 17.5855 | -352.6352 | 18.6573 | -352.5675 | 16.793 | 124.7113 | 369.5007 | 47.8588 | 14.5786 | 11.9774 | 23.7648
13:28 | 113 | 32.9811 |  | 8.2893 | 3.1291 | 0.7496 | 2.8825 | -1.6546 | 12.3101 | 5.3067 | 0.6351 | 0.6768 | 0.9809 | 0.7706 | -130.284 | 3.2406 | 6.2842 | 1.4993 | -2.6207 | -1.1812 | 4.9686 |  | 4.8646 | 0.8285 | 3.9803 | 3.3709 | 3.329 | 1.0995 | 2.4313 | 22.8776 | 22.6745 | 22.4081 | 22.3814 | 22.3008 | 22.4112 | 22.2034 | 22.9506 | 22.6685 | 22.708 | 22.7075 | 24.6252 | 23.0482 | 22.9731 | 22.8967 | 22.7927 | 22.6876 | 22.6267 | 22.5956 | 22.4144 | 22.5029 | 22.3995 | 22.9352 | 22.5706 | 22.6157 | 22.5982 | 23.4944 | 23.1919 | 22.7181 | 22.9725 | 23.0575 | 23.9654 | 23.4997 | 22.8753 | 22.9114 | 22.8769 | 22.826 | 22.7878 | 22.9894 | 22.5729 | 22.3256 | 23.2747 | 22.673 | 22.7837 | 23.0052 | 24.554 | 23.3187 | 23.2686 | 23.2811 | 23.2836 | 24.806 | 23.0894 | 23.0826 | 23.1295 | 23.0879 | 23.0125 | 23.0652 | 23.0962 | 22.8159 | 23.1909 | 22.9246 | 23.1488 | 23.1923 | 23.1573 | 23.0973 | 24.3451 | 23.8316 | 23.742 | 23.7555 | 23.7123 | 25.2786 | 23.325 | 23.3928 | 23.4155 | 23.3711 | 23.3905 | 23.4938 | 23.6215 | 23.165 | 22.9001 | 23.3131 | 23.3704 | 23.3376 | 23.3224 | 24.2685 | 46.2041 | 83.2266 | 28.3514 | 32.5138 | 41.9355 | 43.1845 | 35.7403 | 56.6095 | 46.5392 | 59.5931 | 123.0767 | 120.8722 | 114.1502 | 110.9523 | 113.0817 | 112.9304 | 105.0157 | 119.9508 | 30.976 | 27.9679 | 32.2546 | 29.7705 | 22.6711 | 22.6227 |  | 22.3181 | 22.2835 | 22.2199 | 22.1839 | 22.2192 | 22.2289 | 23.1879 | 22.52 | 22.4526 | 24.3613 | 22.4732 | 22.6987 | 23.0082 | 22.9062 | 22.8507 | 22.7662 | 22.7184 | 22.6799 | 22.6176 | 22.6927 | 23.6616 | 22.749 | 22.7366 | 23.7653 | 24.2725 | 23.7904 | 22.8909 | 23.0865 | 23.9703 | 23.8857 | 22.934 | 22.9834 | 22.9463 | 22.9132 | 23.0283 | 22.7691 | 22.7589 | 22.6902 | 23.6233 | 22.5983 | 22.7174 | 22.973 | 25.3411 | 23.8647 | 23.8003 | 23.7172 | 23.6705 | 24.2528 | 23.7694 | 23.7393 | 23.6474 | 23.5815 | 23.4546 | 23.452 | 23.2194 | 23.0368 | 23.2482 | 23.078 | 23.6881 | 23.6123 | 23.5582 | 23.5161 | 24.9186 | 24.1418 | 24.048 | 23.9395 | 23.8995 | 28.6828 | 23.6292 | 23.8435 | 23.7806 | 23.7005 | 23.6358 | 23.7465 | 23.9028 | 23.233 | 23.0698 | 24.1078 | 24.022 | 24.0209 | 23.9796 | 25.5448 | 36.5147 | 40.3906 | 44.4661 | 39.7804 | 45.2019 | 52.8347 | 61.4661 | 42.2252 | 57.6839 | 49.0489 |  | 51.607 | 43.0661 | 47.2022 | 24.6805 | 23.4235 | 23.4545 | 27.7955 | 25.2458 | 22.3574 | 23.5627 | 10.832 | 14.2649 | 14.8572 | 11.1109 | 0.00035994 | -0.0028605 | 0.0014426 | 0.0043538 | 0.0013331 | -0.00076818 | 0.030262 | -0.009756 | -0.011429 | -360.0634 | 17.3905 | -360.4235 | 17.641 | -360.8697 | 18.1769 | -360.7712 | 17.5424 | -352.5398 | 18.6594 | -352.6352 | 16.8607 | 123.5223 | 365.9972 | 48.3122 | 14.5611 | 11.8115 | 23.8016
13:28 | 114 | 33.0813 |  | 8.3636 | 3.0992 | 0.7615 | 3.025 | -1.6901 | 12.3721 | 5.2812 | 0.6373 | 0.676 | 0.9803 | 0.7699 | -130.403 | 3.2323 | 6.3158 | 1.4867 | -2.575 | -1.1283 | 5.0357 |  | 4.8661 | 0.8524 | 3.9788 | 3.3685 | 3.3254 | 1.0979 | 2.9042 | 22.881 | 22.6841 | 22.4151 | 22.3832 | 22.3 | 22.4155 | 22.2088 | 22.9518 | 22.6707 | 22.7146 | 22.7144 | 24.6717 | 23.0461 | 22.9749 | 22.8993 | 22.7913 | 22.6908 | 22.6297 | 22.5968 | 22.4179 | 22.5041 | 22.4109 | 22.9373 | 22.5788 | 22.615 | 22.6017 | 23.5255 | 23.1928 | 22.7229 | 22.9755 | 23.0582 | 23.9858 | 23.5059 | 22.8718 | 22.9074 | 22.8754 | 22.8249 | 22.793 | 22.9999 | 22.5759 | 22.318 | 23.281 | 22.6749 | 22.7829 | 23.0033 | 24.5849 | 23.3184 | 23.2714 | 23.2801 | 23.2932 | 24.8382 | 23.0853 | 23.0779 | 23.1258 | 23.0855 | 23.0105 | 23.0653 | 23.099 | 22.8118 | 23.1933 | 22.9208 | 23.1448 | 23.1787 | 23.1531 | 23.0912 | 24.3604 | 23.8251 | 23.7316 | 23.747 | 23.7078 | 25.3121 | 23.3173 | 23.3879 | 23.4105 | 23.3676 | 23.3861 | 23.4952 | 23.646 | 23.1824 | 22.9114 | 23.3269 | 23.3705 | 23.3479 | 23.3324 | 24.3008 | 47.2753 | 83.2726 | 28.4568 | 32.6732 | 42.3239 | 43.6424 | 35.9715 | 57.0647 | 46.8383 | 60.062 | 123.9026 | 122.1709 | 114.5234 | 112.2129 | 110.4306 | 112.7221 | 102.6991 | 121.8273 | 31.1725 | 28.094 | 32.4795 | 29.9657 | 22.6769 | 22.6348 |  | 22.3238 | 22.288 | 22.2291 | 22.1926 | 22.2283 | 22.2351 | 23.1947 | 22.527 | 22.4533 | 24.3952 | 22.4757 | 22.7022 | 23.0014 | 22.9054 | 22.8463 | 22.7522 | 22.7186 | 22.6766 | 22.6039 | 22.6928 | 23.6602 | 22.7435 | 22.7329 | 23.7611 | 24.2955 | 23.7833 | 22.8888 | 23.0882 | 23.9841 | 23.8871 | 22.936 | 22.9778 | 22.9424 | 22.9064 | 23.0301 | 22.767 | 22.7631 | 22.6943 | 23.6222 | 22.5919 | 22.7161 | 22.9703 | 25.3895 | 23.8691 | 23.8096 | 23.7215 | 23.6641 | 24.2628 | 23.7628 | 23.7474 | 23.6532 | 23.5863 | 23.4601 | 23.4603 | 23.2221 | 23.045 | 23.2592 | 23.077 | 23.6971 | 23.6146 | 23.5577 | 23.5107 | 24.9448 | 24.1487 | 24.0507 | 23.94 | 23.9017 | 28.7508 | 23.6335 | 23.8423 | 23.7806 | 23.6995 | 23.6322 | 23.7456 | 23.9126 | 23.2412 | 23.0784 | 24.1076 | 24.023 | 24.0211 | 23.9801 | 25.5816 | 36.6874 | 40.4853 | 44.8107 | 40.0025 | 45.5761 | 53.3455 | 62.1137 | 42.5206 | 58.1585 | 49.3862 |  | 52.1136 | 43.518 | 47.5434 | 24.6777 | 23.419 | 23.4466 | 27.8994 | 25.2923 | 22.3824 | 23.6047 | 10.8349 | 14.2746 | 14.8875 | 11.114 | 0.00044567 | -0.0029606 | 0.0008017 | 0.0038518 | 0.00064809 | -0.00054221 | -0.0042843 | 0.0031218 | -0.022516 | -360.2388 | 17.4356 | -360.4081 | 17.6061 | -360.7681 | 18.183 | -360.8666 | 17.6122 | -352.6967 | 18.6861 | -352.5736 | 16.8074 | 134.68 | 367.0902 | 48.7721 | 14.5811 | 11.925 | 23.8374
13:28 | 115 | 32.9166 |  | 8.2685 | 3.0835 | 0.8539 | 3.0037 | -1.7395 | 12.3391 | 5.3014 | 0.6368 | 0.6718 | 0.9836 | 0.768 | -130.3466 | 3.3273 | 6.3885 | 1.4415 | -2.6026 | -1.1601 | 5 |  | 4.8563 | 0.7915 | 3.9787 | 3.371 | 3.3263 | 1.0994 | 4.134 | 22.8811 | 22.6845 | 22.4173 | 22.3774 | 22.2943 | 22.4143 | 22.2076 | 22.9465 | 22.6684 | 22.7091 | 22.7209 | 24.7084 | 23.0444 | 22.9717 | 22.8982 | 22.7981 | 22.6929 | 22.6405 | 22.6085 | 22.4204 | 22.5121 | 22.4256 | 22.9482 | 22.5814 | 22.6195 | 22.6081 | 23.5528 | 23.204 | 22.7251 | 22.977 | 23.0589 | 24.015 | 23.5079 | 22.879 | 22.9162 | 22.8838 | 22.8253 | 22.7763 | 23.0119 | 22.5663 | 22.3173 | 23.2847 | 22.6755 | 22.7773 | 23.0062 | 24.6226 | 23.3173 | 23.2702 | 23.2804 | 23.297 | 24.8708 | 23.0894 | 23.0884 | 23.1285 | 23.0885 | 23.0145 | 23.0719 | 23.1066 | 22.8111 | 23.2086 | 22.9296 | 23.1435 | 23.1728 | 23.1558 | 23.0924 | 24.3744 | 23.8214 | 23.7291 | 23.734 | 23.7091 | 25.345 | 23.3098 | 23.3865 | 23.4105 | 23.3677 | 23.3841 | 23.4937 | 23.6565 | 23.1856 | 22.9115 | 23.3294 | 23.3673 | 23.3469 | 23.3309 | 24.3266 | 48.4187 | 83.142 | 28.5044 | 32.8497 | 42.7302 | 44.1362 | 36.1903 | 57.5705 | 47.132 | 60.5684 | 124.1263 | 123.2965 | 114.6084 | 113.6091 | 106.1361 | 111.1459 | 99.7633 | 122.8874 | 31.3664 | 28.222 | 32.7117 | 30.1576 | 22.6837 | 22.635 |  | 22.3279 | 22.2912 | 22.2328 | 22.1916 | 22.2294 | 22.2421 | 23.1877 | 22.5249 | 22.4531 | 24.4265 | 22.4787 | 22.7038 | 23.0075 | 22.9086 | 22.8453 | 22.7519 | 22.7285 | 22.6859 | 22.6045 | 22.6992 | 23.662 | 22.7405 | 22.74 | 23.7607 | 24.3307 | 23.784 | 22.8945 | 23.0896 | 24.0005 | 23.8954 | 22.9417 | 22.9745 | 22.9463 | 22.9078 | 23.041 | 22.7713 | 22.7726 | 22.7047 | 23.6257 | 22.5986 | 22.7147 | 22.97 | 25.4334 | 23.8705 | 23.8153 | 23.7284 | 23.6714 | 24.2742 | 23.7644 | 23.7513 | 23.6579 | 23.5876 | 23.4661 | 23.4626 | 23.2468 | 23.054 | 23.2696 | 23.0899 | 23.6951 | 23.6164 | 23.5608 | 23.5139 | 24.9801 | 24.1453 | 24.0508 | 23.9443 | 23.9022 | 28.824 | 23.6363 | 23.8414 | 23.7765 | 23.7013 | 23.6339 | 23.7489 | 23.9285 | 23.2437 | 23.0841 | 24.108 | 24.0232 | 24.018 | 23.9817 | 25.6165 | 36.7994 | 40.5572 | 44.8695 | 40.1924 | 45.9581 | 53.8767 | 62.7756 | 42.8232 | 58.6609 | 49.6773 |  | 52.6259 | 43.9665 | 47.8739 | 24.6729 | 23.4235 | 23.4454 | 27.9983 | 25.3503 | 22.3916 | 23.6407 | 10.8229 | 14.2909 | 14.9041 | 11.13 | 0.0002265 | -0.0025701 | 0.0010284 | 0.0043144 | 0.00085012 | -0.0012072 | 0.03185 | -0.015806 | -0.029071 | -360.1034 | 17.3946 | -360.4142 | 17.6307 | -360.845 | 18.1728 | -360.7989 | 17.5506 | -352.5152 | 18.6347 | -352.589 | 16.8423 | 141.8097 | 367.8864 | 49.2429 | 14.5975 | 11.8312 | 23.871
13:28 | 116 | 32.9601 |  | 8.2263 | 3.0752 | 0.7918 | 2.9622 | -1.7176 | 12.3816 | 5.4278 | 0.637 | 0.6756 | 0.9829 | 0.7688 | -130.3368 | 3.161 | 6.2646 | 1.3846 | -2.6438 | -1.1141 | 5.0019 |  | 4.768 | 0.7975 | 3.9797 | 3.3701 | 3.3279 | 1.0982 | 3.7156 | 22.8814 | 22.6899 | 22.4211 | 22.3861 | 22.2955 | 22.426 | 22.2117 | 22.9498 | 22.6687 | 22.7085 | 22.7178 | 24.7557 | 23.0484 | 22.9729 | 22.9009 | 22.7993 | 22.6944 | 22.6404 | 22.6162 | 22.4234 | 22.5281 | 22.4271 | 22.9509 | 22.5827 | 22.6187 | 22.6086 | 23.576 | 23.2043 | 22.7218 | 22.9699 | 23.0597 | 24.042 | 23.5127 | 22.878 | 22.927 | 22.8935 | 22.8223 | 22.7821 | 23.0303 | 22.578 | 22.3218 | 23.2808 | 22.6769 | 22.7751 | 23.0085 | 24.6618 | 23.3157 | 23.2709 | 23.281 | 23.2968 | 24.9098 | 23.0908 | 23.0931 | 23.1333 | 23.0904 | 23.0193 | 23.0713 | 23.1084 | 22.8165 | 23.2383 | 22.9371 | 23.1479 | 23.1823 | 23.1601 | 23.099 | 24.3963 | 23.8273 | 23.7328 | 23.7386 | 23.7126 | 25.3799 | 23.3174 | 23.3923 | 23.4089 | 23.3743 | 23.3846 | 23.4958 | 23.6693 | 23.1902 | 22.9174 | 23.3219 | 23.3727 | 23.343 | 23.3263 | 24.3449 | 48.6232 | 82.89 | 28.6344 | 32.9859 | 43.1349 | 44.6481 | 36.3923 | 58.0804 | 47.4392 | 61.0856 | 124.28 | 124.2638 | 114.4851 | 114.5661 | 106.6242 | 110.7759 | 99.3706 | 123.0901 | 31.5579 | 28.3493 | 32.9345 | 30.3484 | 22.6842 | 22.6337 |  | 22.3309 | 22.294 | 22.2326 | 22.189 | 22.233 | 22.2391 | 23.1826 | 22.5235 | 22.4542 | 24.4521 | 22.4761 | 22.7018 | 23.0074 | 22.9107 | 22.8484 | 22.7567 | 22.7301 | 22.6911 | 22.6083 | 22.7058 | 23.6576 | 22.7358 | 22.7437 | 23.7592 | 24.3595 | 23.7846 | 22.8933 | 23.093 | 24.0192 | 23.8992 | 22.9399 | 22.9791 | 22.9502 | 22.9146 | 23.0511 | 22.7823 | 22.7786 | 22.7094 | 23.6265 | 22.6033 | 22.7182 | 22.9704 | 25.4803 | 23.8682 | 23.8125 | 23.7266 | 23.6685 | 24.2858 | 23.7771 | 23.7453 | 23.6565 | 23.5875 | 23.4645 | 23.465 | 23.2486 | 23.0564 | 23.2771 | 23.0948 | 23.6901 | 23.6156 | 23.5557 | 23.5129 | 25.0041 | 24.136 | 24.0466 | 23.9379 | 23.8993 | 28.888 | 23.6305 | 23.8411 | 23.7736 | 23.6935 | 23.6362 | 23.7554 | 23.9394 | 23.2511 | 23.0796 | 24.1095 | 24.0213 | 24.0112 | 23.9817 | 25.6447 | 36.9017 | 40.6927 | 45.0718 | 40.3213 | 46.3367 | 54.4565 | 63.4267 | 43.1086 | 59.1733 | 49.9334 |  | 53.1312 | 44.415 | 48.2043 | 24.6824 | 23.4289 | 23.4561 | 28.1159 | 25.4168 | 22.4085 | 23.69 | 10.8223 | 14.2618 | 14.8808 | 11.1017 | -4.3345e-05 | -0.0028592 | 0.0009231 | 0.0036922 | 0.00084275 | -0.00011569 | 0.026768 | 0.00074307 | -0.033431 | -360.1958 | 17.4336 | -360.4081 | 17.5814 | -360.7589 | 18.1584 | -360.8358 | 17.6102 | -352.6598 | 18.684 | -352.6167 | 16.7991 | 159.3863 | 364.7122 | 49.7192 | 14.5713 | 11.8024 | 23.9126
13:28 | 117 | 32.928 |  | 8.2123 | 3.0871 | 0.7158 | 2.9787 | -1.6265 | 12.3765 | 5.3294 | 0.6376 | 0.6725 | 0.9806 | 0.7686 | -130.4287 | 3.083 | 6.2852 | 1.5129 | -2.5785 | -1.068 | 5.0762 |  | 4.8153 | 0.806 | 3.9793 | 3.371 | 3.3295 | 1.0989 | 2.9476 | 22.8921 | 22.6912 | 22.4216 | 22.3912 | 22.3017 | 22.435 | 22.2142 | 22.9565 | 22.6709 | 22.7139 | 22.7137 | 24.8029 | 23.0523 | 22.9759 | 22.9061 | 22.7992 | 22.698 | 22.6405 | 22.626 | 22.4256 | 22.5343 | 22.431 | 22.9472 | 22.5838 | 22.6187 | 22.6093 | 23.6045 | 23.2001 | 22.7251 | 22.969 | 23.066 | 24.0696 | 23.5176 | 22.8808 | 22.9376 | 22.8973 | 22.8295 | 22.7935 | 23.0477 | 22.5947 | 22.3282 | 23.2815 | 22.6804 | 22.7852 | 23.0158 | 24.6907 | 23.3083 | 23.2688 | 23.283 | 23.3023 | 24.9421 | 23.0836 | 23.0884 | 23.1342 | 23.0907 | 23.0157 | 23.0797 | 23.1093 | 22.821 | 23.2705 | 22.9267 | 23.1454 | 23.1798 | 23.1594 | 23.0978 | 24.4118 | 23.8305 | 23.7297 | 23.7403 | 23.7128 | 25.4116 | 23.3172 | 23.39 | 23.4036 | 23.3711 | 23.3831 | 23.4964 | 23.6899 | 23.1992 | 22.921 | 23.3257 | 23.3734 | 23.3418 | 23.3253 | 24.3667 | 48.4256 | 82.7976 | 28.7225 | 33.0824 | 43.5387 | 45.1805 | 36.5907 | 58.5876 | 47.7658 | 61.6236 | 123.4542 | 125.1835 | 114.526 | 114.9589 | 108.6082 | 112.6744 | 103.9729 | 123.4317 | 31.7445 | 28.4796 | 33.155 | 30.5296 | 22.6827 | 22.6403 |  | 22.3327 | 22.2985 | 22.2355 | 22.1895 | 22.2422 | 22.2435 | 23.1869 | 22.5247 | 22.4661 | 24.485 | 22.4696 | 22.6988 | 23.0037 | 22.906 | 22.846 | 22.7588 | 22.7242 | 22.6884 | 22.6123 | 22.7064 | 23.6598 | 22.7375 | 22.7391 | 23.7594 | 24.3872 | 23.7824 | 22.8898 | 23.0964 | 24.0369 | 23.8974 | 22.941 | 22.9799 | 22.9526 | 22.915 | 23.0639 | 22.7873 | 22.7864 | 22.7155 | 23.63 | 22.6034 | 22.7222 | 22.9762 | 25.5292 | 23.8728 | 23.8122 | 23.7256 | 23.6682 | 24.2993 | 23.7711 | 23.7453 | 23.6602 | 23.5888 | 23.4651 | 23.4792 | 23.2362 | 23.0592 | 23.2829 | 23.1017 | 23.6914 | 23.6184 | 23.5573 | 23.5181 | 25.0333 | 24.1447 | 24.046 | 23.9393 | 23.9013 | 28.9538 | 23.631 | 23.8457 | 23.7804 | 23.6987 | 23.6401 | 23.7608 | 23.9581 | 23.2599 | 23.0821 | 24.1114 | 24.0283 | 24.0148 | 23.9805 | 25.6763 | 37.0351 | 40.8879 | 45.1749 | 40.4752 | 46.7158 | 55.0789 | 64.0687 | 43.4018 | 59.6758 | 50.2176 |  | 53.62 | 44.8469 | 48.5172 | 24.6932 | 23.4351 | 23.4596 | 28.2328 | 25.4775 | 22.4403 | 23.7414 | 10.8129 | 14.2533 | 14.8764 | 11.126 | 0.00057596 | -0.0027941 | 0.0019399 | 0.004616 | 0.0015401 | -0.00085533 | 0.018165 | -0.00038588 | -0.02026 | -360.1034 | 17.4048 | -360.4327 | 17.6574 | -360.8512 | 18.2036 | -360.8512 | 17.5629 | -352.5798 | 18.6635 | -352.6229 | 16.8628 | 150.8343 | 369.7087 | 50.1958 | 14.5649 | 11.8912 | 23.9589
13:28 | 118 | 32.7552 |  | 8.1872 | 3.0069 | 0.6043 | 2.9414 | -1.7187 | 12.2249 | 5.3146 | 0.6363 | 0.6737 | 0.9796 | 0.7692 | -130.5071 | 3.0641 | 6.2328 | 1.5375 | -2.7019 | -1.1408 | 4.9905 |  | 4.779 | 0.7893 | 3.9789 | 3.3685 | 3.3273 | 1.0986 | 3.634 | 22.8975 | 22.6861 | 22.421 | 22.3817 | 22.3006 | 22.434 | 22.2143 | 22.9537 | 22.6684 | 22.7145 | 22.7174 | 24.8415 | 23.0483 | 22.9745 | 22.9035 | 22.8051 | 22.6989 | 22.6421 | 22.6219 | 22.4218 | 22.5345 | 22.4348 | 22.945 | 22.5786 | 22.616 | 22.6106 | 23.6346 | 23.2022 | 22.7272 | 22.9731 | 23.0719 | 24.0982 | 23.518 | 22.8841 | 22.9359 | 22.8978 | 22.835 | 22.8139 | 23.0674 | 22.6139 | 22.3364 | 23.2901 | 22.6889 | 22.7854 | 23.0236 | 24.7276 | 23.3169 | 23.272 | 23.2891 | 23.3137 | 24.9713 | 23.0853 | 23.0906 | 23.1346 | 23.0883 | 23.0153 | 23.1008 | 23.1156 | 22.8267 | 23.2932 | 22.9316 | 23.1464 | 23.1825 | 23.1582 | 23.0948 | 24.4308 | 23.8314 | 23.73 | 23.738 | 23.7103 | 25.4468 | 23.3134 | 23.3918 | 23.4069 | 23.3705 | 23.3822 | 23.489 | 23.6984 | 23.2068 | 22.9211 | 23.3239 | 23.3735 | 23.3412 | 23.3275 | 24.3859 | 48.159 | 82.909 | 28.7436 | 33.1507 | 43.9374 | 45.7169 | 36.7788 | 59.0684 | 48.1024 | 62.1789 | 123.4338 | 126.2298 | 115.2863 | 115.2429 | 109.3335 | 115.0067 | 107.2161 | 123.1444 | 31.9237 | 28.6078 | 33.3644 | 30.6946 | 22.6845 | 22.6476 |  | 22.3345 | 22.303 | 22.2389 | 22.1944 | 22.2495 | 22.2501 | 23.1874 | 22.5257 | 22.469 | 24.5187 | 22.4742 | 22.7008 | 23.0064 | 22.9075 | 22.8481 | 22.7706 | 22.7269 | 22.6873 | 22.6185 | 22.715 | 23.6633 | 22.7411 | 22.7351 | 23.7574 | 24.4232 | 23.7858 | 22.8917 | 23.0927 | 24.0525 | 23.8918 | 22.9406 | 22.9739 | 22.9499 | 22.9132 | 23.0687 | 22.7901 | 22.7886 | 22.7183 | 23.6281 | 22.5975 | 22.7171 | 22.982 | 25.5784 | 23.8753 | 23.8091 | 23.7237 | 23.675 | 24.311 | 23.7767 | 23.7478 | 23.6579 | 23.5846 | 23.465 | 23.4871 | 23.2397 | 23.0632 | 23.2807 | 23.1067 | 23.692 | 23.6136 | 23.5653 | 23.5207 | 25.0668 | 24.1434 | 24.0467 | 23.9365 | 23.9011 | 29.0231 | 23.6318 | 23.8444 | 23.7803 | 23.693 | 23.6305 | 23.7648 | 23.9703 | 23.265 | 23.0891 | 24.1154 | 24.0275 | 24.0195 | 23.9806 | 25.7157 | 37.2297 | 41.0858 | 45.333 | 40.6758 | 47.1128 | 55.7045 | 64.6999 | 43.712 | 60.1701 | 50.5468 |  | 54.0746 | 45.2523 | 48.8361 | 24.6843 | 23.4369 | 23.4539 | 28.3326 | 25.5264 | 22.4501 | 23.7832 | 10.8192 | 14.2667 | 14.9038 | 11.1113 | 0.00068822 | -0.0031513 | 0.0023094 | 0.0044931 | 0.00090306 | -0.00022635 | 0.0046548 | -0.0052691 | -0.0095767 | -360.1988 | 17.4315 | -360.3958 | 17.5958 | -360.7281 | 18.1235 | -360.7835 | 17.5855 | -352.6167 | 18.6963 | -352.586 | 16.7889 | 162.4978 | 363.042 | 50.6668 | 14.5853 | 11.6443 | 23.9883
13:28 | 119 | 32.7086 |  | 8.2284 | 3.0039 | 0.5799 | 2.9386 | -1.6826 | 12.2143 | 5.3105 | 0.6366 | 0.6778 | 0.9839 | 0.7702 | -130.4501 | 3.0422 | 6.2118 | 1.5929 | -2.6324 | -1.1044 | 5.0232 |  | 4.8379 | 0.7824 | 3.9795 | 3.3692 | 3.3275 | 1.0986 | 3.3338 | 22.893 | 22.6824 | 22.4191 | 22.3759 | 22.2942 | 22.4371 | 22.2105 | 22.953 | 22.6636 | 22.7116 | 22.7138 | 24.8861 | 23.043 | 22.9646 | 22.9033 | 22.8028 | 22.6943 | 22.6424 | 22.6199 | 22.423 | 22.5315 | 22.4372 | 22.9452 | 22.5775 | 22.6142 | 22.6147 | 23.6607 | 23.1984 | 22.728 | 22.9758 | 23.0688 | 24.1223 | 23.5118 | 22.8908 | 22.9306 | 22.8905 | 22.8266 | 22.8168 | 23.0678 | 22.6141 | 22.3296 | 23.2858 | 22.6836 | 22.7789 | 23.014 | 24.7667 | 23.3321 | 23.2783 | 23.291 | 23.3188 | 25.002 | 23.0929 | 23.0933 | 23.1387 | 23.0937 | 23.0164 | 23.106 | 23.131 | 22.829 | 23.2885 | 22.943 | 23.1548 | 23.1968 | 23.1621 | 23.0997 | 24.4548 | 23.8308 | 23.7331 | 23.7452 | 23.7179 | 25.4841 | 23.3212 | 23.3988 | 23.4146 | 23.3741 | 23.3898 | 23.4977 | 23.711 | 23.2164 | 22.9295 | 23.3219 | 23.3788 | 23.3393 | 23.3336 | 24.4062 | 48.2908 | 82.7326 | 28.8366 | 33.2257 | 44.3365 | 46.2401 | 36.95 | 59.5182 | 48.4408 | 62.7268 | 124.692 | 127.0585 | 113.0572 | 115.7502 | 111.156 | 117.7025 | 110.4422 | 121.8148 | 32.0994 | 28.74 | 33.571 | 30.8595 | 22.6862 | 22.6503 |  | 22.3333 | 22.2994 | 22.2368 | 22.198 | 22.2534 | 22.2481 | 23.1896 | 22.5296 | 22.4588 | 24.5523 | 22.4802 | 22.7022 | 23.0065 | 22.9103 | 22.8506 | 22.7683 | 22.7266 | 22.69 | 22.6173 | 22.7275 | 23.6608 | 22.7429 | 22.7368 | 23.7604 | 24.4587 | 23.7872 | 22.891 | 23.093 | 24.0717 | 23.8865 | 22.9423 | 22.9775 | 22.9492 | 22.9098 | 23.0751 | 22.7914 | 22.7939 | 22.722 | 23.6271 | 22.5941 | 22.7145 | 22.9835 | 25.6257 | 23.866 | 23.8061 | 23.7204 | 23.6722 | 24.3221 | 23.7804 | 23.7494 | 23.6526 | 23.5829 | 23.4665 | 23.4765 | 23.2538 | 23.0691 | 23.2938 | 23.1058 | 23.6954 | 23.6152 | 23.5607 | 23.5207 | 25.0966 | 24.1425 | 24.0504 | 23.9349 | 23.9035 | 29.1039 | 23.63 | 23.8456 | 23.7802 | 23.6875 | 23.6281 | 23.7737 | 23.9726 | 23.2701 | 23.0914 | 24.1164 | 24.0225 | 24.0164 | 23.977 | 25.7466 | 37.4281 | 41.2096 | 45.6855 | 40.8739 | 47.5068 | 56.2936 | 65.2999 | 43.9995 | 60.6463 | 50.9429 |  | 54.5262 | 45.6737 | 49.1676 | 24.6734 | 23.4271 | 23.4542 | 28.4346 | 25.5904 | 22.4643 | 23.8301 | 10.8431 | 14.2909 | 14.9155 | 11.1064 | 0.00048032 | -0.0025655 | 0.0022435 | 0.0041669 | 0.0019087 | -0.00078507 | 0.015447 | -0.012333 | -0.041992 | -360.1034 | 17.3946 | -360.405 | 17.6286 | -360.8235 | 18.1974 | -360.845 | 17.5691 | -352.5644 | 18.6532 | -352.6013 | 16.8464 | 172.7688 | 369.3972 | 51.1305 | 14.6032 | 11.7278 | 24.0273
13:28 | 120 | 32.7732 |  | 8.212 | 3.0034 | 0.589 | 2.9086 | -1.746 | 12.2359 | 5.3261 | 0.6353 | 0.6768 | 0.9814 | 0.7678 | -130.407 | 3.0608 | 6.2706 | 1.6247 | -2.6075 | -1.0945 | 5.0203 |  | 4.711 | 0.6096 | 3.9792 | 3.3709 | 3.3296 | 1.0992 | 1.3512 | 22.8948 | 22.688 | 22.4196 | 22.3824 | 22.3002 | 22.4478 | 22.2113 | 22.9582 | 22.668 | 22.7135 | 22.7162 | 24.9273 | 23.0424 | 22.9671 | 22.9035 | 22.7986 | 22.6951 | 22.6454 | 22.6154 | 22.4306 | 22.5266 | 22.4431 | 22.9434 | 22.5807 | 22.6119 | 22.6139 | 23.6859 | 23.1969 | 22.7258 | 22.9761 | 23.073 | 24.152 | 23.5018 | 22.8921 | 22.9331 | 22.8838 | 22.8252 | 22.7963 | 23.0713 | 22.6058 | 22.3253 | 23.2851 | 22.6798 | 22.779 | 23.0068 | 24.8036 | 23.3371 | 23.2755 | 23.2868 | 23.3139 | 25.0376 | 23.088 | 23.0912 | 23.1303 | 23.1 | 23.021 | 23.0914 | 23.1387 | 22.8341 | 23.2731 | 22.9452 | 23.151 | 23.1933 | 23.162 | 23.1019 | 24.4776 | 23.8242 | 23.7352 | 23.745 | 23.723 | 25.5205 | 23.3245 | 23.3909 | 23.4103 | 23.3752 | 23.3906 | 23.504 | 23.7286 | 23.2294 | 22.9404 | 23.3253 | 23.3814 | 23.34 | 23.3357 | 24.4344 | 48.3624 | 81.7766 | 29.0037 | 33.3105 | 44.7407 | 46.732 | 37.1062 | 59.9352 | 48.7544 | 63.238 | 125.4525 | 127.8229 | 112.751 | 115.9642 | 113.4315 | 119.5296 | 115.7112 | 120.4827 | 32.2928 | 28.8784 | 33.786 | 31.0274 | 22.6828 | 22.6545 |  | 22.3303 | 22.3004 | 22.2414 | 22.1993 | 22.2574 | 22.2518 | 23.194 | 22.5282 | 22.4638 | 24.5849 | 22.4835 | 22.7015 | 23.0058 | 22.9135 | 22.8458 | 22.7794 | 22.7293 | 22.694 | 22.6162 | 22.7319 | 23.6652 | 22.7444 | 22.7412 | 23.7703 | 24.4954 | 23.79 | 22.8979 | 23.0937 | 24.0863 | 23.8885 | 22.9455 | 22.9763 | 22.9513 | 22.911 | 23.086 | 22.7906 | 22.7988 | 22.7302 | 23.6267 | 22.6006 | 22.7166 | 22.9858 | 25.6737 | 23.8753 | 23.8117 | 23.7312 | 23.6848 | 24.3402 | 23.7773 | 23.7507 | 23.6578 | 23.5858 | 23.4665 | 23.4709 | 23.2702 | 23.0788 | 23.3165 | 23.1164 | 23.6972 | 23.6167 | 23.5656 | 23.5284 | 25.127 | 24.1489 | 24.0499 | 23.9376 | 23.9057 | 29.1899 | 23.6302 | 23.8491 | 23.7816 | 23.6944 | 23.6357 | 23.7776 | 23.988 | 23.2814 | 23.0991 | 24.1193 | 24.0269 | 24.0175 | 23.9863 | 25.7825 | 37.5685 | 41.3118 | 46.0396 | 41.0252 | 47.9001 | 56.8276 | 65.873 | 44.2427 | 61.0916 | 51.4045 |  | 54.9794 | 46.1068 | 49.4963 | 24.6779 | 23.4273 | 23.4495 | 28.5339 | 25.6479 | 22.4763 | 23.8659 | 10.8235 | 14.285 | 14.8722 | 11.1227 | -3.8367e-05 | -0.0025369 | 0.0019835 | 0.0048954 | 0.0011409 | -0.00024799 | 0.028079 | 0.0024739 | -0.004988 | -360.2512 | 17.45 | -360.4696 | 17.6328 | -360.7743 | 18.1604 | -360.8174 | 17.5937 | -352.6413 | 18.7004 | -352.6352 | 16.8258 | 153.2117 | 364.325 | 51.582 | 14.5786 | 11.6378 | 24.0621
13:28 | 121 | 32.6907 |  | 8.1753 | 2.9702 | 0.6604 | 2.8919 | -1.7152 | 12.1698 | 5.363 | 0.6356 | 0.6751 | 0.9828 | 0.7677 | -130.4026 | 2.8855 | 6.1989 | 1.5851 | -2.6185 | -1.1192 | 4.9964 |  | 4.7197 | 0.6676 | 3.9784 | 3.3711 | 3.3253 | 1.0983 | 1.8769 | 22.8976 | 22.6928 | 22.4224 | 22.3871 | 22.3 | 22.4488 | 22.2135 | 22.9547 | 22.6622 | 22.7106 | 22.7244 | 24.9656 | 23.0391 | 22.9683 | 22.9073 | 22.8036 | 22.6985 | 22.6452 | 22.6106 | 22.4288 | 22.5296 | 22.4458 | 22.9444 | 22.5765 | 22.6188 | 22.6072 | 23.7097 | 23.2015 | 22.7204 | 22.9719 | 23.0808 | 24.1825 | 23.5199 | 22.8907 | 22.9291 | 22.8881 | 22.8279 | 22.7849 | 23.0866 | 22.5998 | 22.3296 | 23.2893 | 22.6841 | 22.7864 | 23.0082 | 24.8484 | 23.3343 | 23.2749 | 23.2956 | 23.3249 | 25.0794 | 23.083 | 23.0974 | 23.1318 | 23.1018 | 23.0215 | 23.0961 | 23.1445 | 22.8386 | 23.2718 | 22.9509 | 23.1522 | 23.1891 | 23.1694 | 23.104 | 24.5013 | 23.8205 | 23.7369 | 23.7465 | 23.7222 | 25.5604 | 23.3244 | 23.3891 | 23.4077 | 23.376 | 23.3886 | 23.5072 | 23.7439 | 23.2418 | 22.9495 | 23.33 | 23.3844 | 23.345 | 23.336 | 24.4639 | 48.0951 | 80.5054 | 29.1401 | 33.3728 | 45.1427 | 47.1911 | 37.255 | 60.3361 | 49.0745 | 63.719 | 125.942 | 128.5089 | 116.4251 | 116.6678 | 114.5242 | 120.0902 | 117.419 | 120.7393 | 32.513 | 29.0191 | 34.0121 | 31.2023 | 22.6843 | 22.6564 |  | 22.3351 | 22.3083 | 22.246 | 22.1987 | 22.2693 | 22.2582 | 23.1982 | 22.5308 | 22.4689 | 24.614 | 22.487 | 22.7113 | 23.0015 | 22.9116 | 22.8445 | 22.7947 | 22.7363 | 22.6954 | 22.6212 | 22.726 | 23.6667 | 22.742 | 22.7376 | 23.7678 | 24.5251 | 23.7921 | 22.8997 | 23.0893 | 24.1033 | 23.8929 | 22.9438 | 22.9762 | 22.9545 | 22.9111 | 23.0982 | 22.7965 | 22.8029 | 22.7366 | 23.6275 | 22.6005 | 22.7153 | 22.9823 | 25.7224 | 23.8868 | 23.8183 | 23.7389 | 23.7022 | 24.3594 | 23.7776 | 23.7539 | 23.658 | 23.5896 | 23.4638 | 23.4746 | 23.2801 | 23.0857 | 23.331 | 23.1287 | 23.691 | 23.6113 | 23.5695 | 23.5286 | 25.1556 | 24.1458 | 24.0454 | 23.929 | 23.9015 | 29.2724 | 23.627 | 23.8417 | 23.778 | 23.6943 | 23.6301 | 23.7725 | 24.0004 | 23.2955 | 23.1034 | 24.1211 | 24.026 | 24.022 | 23.9942 | 25.8198 | 37.6601 | 41.4027 | 46.4529 | 41.2011 | 48.2966 | 57.3219 | 66.4352 | 44.4551 | 61.5359 | 51.8544 |  | 55.4391 | 46.5581 | 49.8494 | 24.683 | 23.4318 | 23.4531 | 28.6406 | 25.7123 | 22.4937 | 23.9095 | 10.8228 | 14.3052 | 14.8913 | 11.1225 | 0.000256 | -0.0026147 | 0.0014096 | 0.0042495 | 0.001508 | -0.00049543 | 0.016366 | -0.012881 | -0.0027165 | -360.1158 | 17.3864 | -360.3865 | 17.6225 | -360.8204 | 18.1645 | -360.802 | 17.5609 | -352.5306 | 18.6553 | -352.5829 | 16.8299 | 163.0059 | 369.2036 | 52.0293 | 14.5982 | 11.624 | 24.103
13:28 | 122 | 32.4711 |  | 8.2356 | 3.0098 | 0.6006 | 2.8379 | -1.6753 | 12.1641 | 5.3459 | 0.6376 | 0.6767 | 0.9798 | 0.7676 | -130.5198 | 2.8488 | 6.3416 | 1.5236 | -2.6343 | -1.1305 | 4.967 |  | 4.7559 | 0.7025 | 3.9777 | 3.3729 | 3.3243 | 1.0992 | 1.6552 | 22.8973 | 22.6917 | 22.4194 | 22.3798 | 22.2944 | 22.4463 | 22.2124 | 22.9486 | 22.6568 | 22.7044 | 22.7148 | 25.003 | 23.0418 | 22.9588 | 22.9114 | 22.8066 | 22.7014 | 22.6423 | 22.6233 | 22.4317 | 22.5345 | 22.4453 | 22.9504 | 22.5733 | 22.6226 | 22.6098 | 23.736 | 23.2046 | 22.7184 | 22.9652 | 23.0805 | 24.207 | 23.5323 | 22.8852 | 22.9203 | 22.8914 | 22.8256 | 22.7777 | 23.1109 | 22.6011 | 22.3441 | 23.29 | 22.6805 | 22.7875 | 23.0062 | 24.881 | 23.3283 | 23.2806 | 23.2981 | 23.3304 | 25.106 | 23.0782 | 23.0958 | 23.1358 | 23.0995 | 23.0166 | 23.1031 | 23.1665 | 22.8342 | 23.2663 | 22.9503 | 23.157 | 23.1923 | 23.1758 | 23.1065 | 24.5241 | 23.8244 | 23.7409 | 23.753 | 23.7242 | 25.6044 | 23.3272 | 23.4007 | 23.4116 | 23.3777 | 23.3949 | 23.521 | 23.7582 | 23.249 | 22.9504 | 23.3307 | 23.3851 | 23.3515 | 23.3411 | 24.4918 | 48.017 | 80.1275 | 29.2869 | 33.4272 | 45.5479 | 47.6203 | 37.4012 | 60.7203 | 49.3939 | 64.1723 | 126.7298 | 129.4151 | 119.308 | 118.2603 | 114.8094 | 120.1613 | 114.2767 | 121.7515 | 32.7457 | 29.1642 | 34.2524 | 31.3884 | 22.6919 | 22.6645 |  | 22.3391 | 22.3099 | 22.2426 | 22.1975 | 22.2759 | 22.2644 | 23.1959 | 22.5317 | 22.467 | 24.6425 | 22.4871 | 22.7167 | 23.003 | 22.9094 | 22.844 | 22.8018 | 22.7386 | 22.697 | 22.6368 | 22.7327 | 23.662 | 22.7399 | 22.7377 | 23.7613 | 24.5594 | 23.7895 | 22.8949 | 23.0924 | 24.1223 | 23.8972 | 22.9418 | 22.9831 | 22.9581 | 22.9091 | 23.1064 | 22.7996 | 22.8063 | 22.7408 | 23.6332 | 22.6039 | 22.7145 | 22.9828 | 25.7767 | 23.8839 | 23.8239 | 23.7422 | 23.7003 | 24.3744 | 23.7897 | 23.7591 | 23.6622 | 23.5973 | 23.4666 | 23.4876 | 23.2847 | 23.0962 | 23.3505 | 23.1356 | 23.6915 | 23.6113 | 23.5653 | 23.5247 | 25.1803 | 24.1448 | 24.0518 | 23.9293 | 23.9055 | 29.3601 | 23.6325 | 23.842 | 23.7822 | 23.6963 | 23.636 | 23.7803 | 24.0144 | 23.3091 | 23.1117 | 24.1198 | 24.0303 | 24.0245 | 23.9979 | 25.8541 | 37.7558 | 41.4561 | 46.6544 | 41.4225 | 48.6899 | 57.7674 | 67.0062 | 44.6635 | 61.9686 | 52.2513 |  | 55.8914 | 47.0076 | 50.2318 | 24.6847 | 23.4341 | 23.4604 | 28.749 | 25.7743 | 22.5172 | 23.9616 | 10.8279 | 14.2606 | 14.9016 | 11.114 | 0.00039866 | -0.0029606 | 0.0010828 | 0.0041576 | 0.0014205 | -0.00044825 | 0.015984 | -0.010155 | -0.027766 | -360.1835 | 17.4356 | -360.4358 | 17.6307 | -360.7773 | 18.1502 | -360.8174 | 17.5937 | -352.6106 | 18.684 | -352.6413 | 16.8381 | 169.4297 | 366.0575 | 52.4703 | 14.5811 | 11.6108 | 24.1457
13:28 | 123 | 32.3 |  | 8.2139 | 3.0731 | 0.6361 | 2.8566 | -1.6598 | 12.1933 | 5.2729 | 0.6372 | 0.6753 | 0.9825 | 0.7691 | -130.5827 | 2.7033 | 6.2509 | 1.5981 | -2.6418 | -1.2677 | 4.9653 |  | 4.7262 | 0.7138 | 3.9769 | 3.3701 | 3.3281 | 1.0983 | 3.5391 | 22.9043 | 22.6954 | 22.421 | 22.3793 | 22.2953 | 22.4506 | 22.2152 | 22.9453 | 22.6673 | 22.7071 | 22.7045 | 25.0447 | 23.0484 | 22.9621 | 22.9162 | 22.8032 | 22.7056 | 22.6385 | 22.6274 | 22.436 | 22.5377 | 22.4478 | 22.9519 | 22.5729 | 22.6171 | 22.6094 | 23.7647 | 23.2076 | 22.7224 | 22.97 | 23.0825 | 24.2369 | 23.5228 | 22.8854 | 22.9277 | 22.8907 | 22.8267 | 22.7989 | 23.1308 | 22.6298 | 22.3571 | 23.2922 | 22.6797 | 22.785 | 23.0069 | 24.9168 | 23.3241 | 23.2792 | 23.2967 | 23.3292 | 25.1367 | 23.0794 | 23.0948 | 23.1329 | 23.0963 | 23.02 | 23.1049 | 23.1778 | 22.8401 | 23.261 | 22.9467 | 23.162 | 23.1936 | 23.1763 | 23.1106 | 24.5441 | 23.83 | 23.7425 | 23.7544 | 23.7259 | 25.6453 | 23.3261 | 23.4028 | 23.417 | 23.377 | 23.3949 | 23.5219 | 23.7753 | 23.2591 | 22.9509 | 23.3273 | 23.3834 | 23.3539 | 23.3402 | 24.5084 | 48.3456 | 81.0854 | 29.4952 | 33.4898 | 45.952 | 48.0436 | 37.5458 | 61.0679 | 49.6707 | 64.5699 | 127.5349 | 130.601 | 120.9584 | 118.9728 | 116.3017 | 120.2781 | 109.7265 | 123.7285 | 33.0049 | 29.3154 | 34.5018 | 31.5884 | 22.7059 | 22.6757 |  | 22.3407 | 22.3156 | 22.2453 | 22.2002 | 22.2815 | 22.2715 | 23.1955 | 22.5297 | 22.471 | 24.6716 | 22.4888 | 22.7129 | 23.0035 | 22.9097 | 22.8461 | 22.7967 | 22.7365 | 22.6939 | 22.6343 | 22.7441 | 23.663 | 22.7411 | 22.7441 | 23.7633 | 24.5958 | 23.7907 | 22.8931 | 23.0995 | 24.1358 | 23.8975 | 22.9415 | 22.9852 | 22.9584 | 22.9133 | 23.1074 | 22.8075 | 22.8124 | 22.7419 | 23.6363 | 22.6052 | 22.7162 | 22.9882 | 25.8254 | 23.8794 | 23.8228 | 23.7401 | 23.69 | 24.3795 | 23.8092 | 23.7589 | 23.6664 | 23.599 | 23.4719 | 23.4986 | 23.2836 | 23.1057 | 23.361 | 23.1342 | 23.6955 | 23.612 | 23.5693 | 23.5289 | 25.206 | 24.149 | 24.0524 | 23.932 | 23.9052 | 29.4535 | 23.6334 | 23.8412 | 23.7769 | 23.6916 | 23.6394 | 23.7855 | 24.0265 | 23.3086 | 23.1178 | 24.12 | 24.0288 | 24.0229 | 23.9955 | 25.8866 | 37.857 | 41.5168 | 46.4483 | 41.6261 | 49.0731 | 58.1849 | 67.5825 | 44.8612 | 62.3691 | 52.591 |  | 56.3348 | 47.4629 | 50.6195 | 24.6865 | 23.4321 | 23.4616 | 28.8483 | 25.8396 | 22.5286 | 24.0044 | 10.8336 | 14.2801 | 14.8916 | 11.1131 | -0.00025257 | -0.0029728 | 0.0013468 | 0.0037887 | 0.0012443 | -0.00063056 | 0.0023084 | 0.010728 | -0.031372 | -360.1435 | 17.411 | -360.4358 | 17.6348 | -360.8266 | 18.181 | -360.8204 | 17.5814 | -352.5613 | 18.6655 | -352.6136 | 16.8402 | 180.0745 | 365.9512 | 52.9067 | 14.5858 | 11.604 | 24.1841
13:28 | 124 | 32.2393 |  | 8.2916 | 3.0577 | 0.5971 | 2.9147 | -1.6824 | 12.1969 | 5.2698 | 0.6377 | 0.6747 | 0.9837 | 0.7696 | -130.6506 | 2.6103 | 6.1724 | 1.5786 | -2.7595 | -1.1341 | 4.9525 |  | 4.7442 | 0.6522 | 3.9771 | 3.3687 | 3.326 | 1.0974 | 2.8972 | 22.9168 | 22.7013 | 22.4275 | 22.3868 | 22.3012 | 22.4569 | 22.2234 | 22.9478 | 22.6723 | 22.7178 | 22.7112 | 25.0958 | 23.046 | 22.9662 | 22.9184 | 22.8055 | 22.703 | 22.6427 | 22.6266 | 22.4356 | 22.5484 | 22.4557 | 22.951 | 22.5725 | 22.6161 | 22.605 | 23.7906 | 23.2035 | 22.719 | 22.9713 | 23.0849 | 24.2668 | 23.5209 | 22.9016 | 22.9265 | 22.883 | 22.8184 | 22.8159 | 23.1348 | 22.6432 | 22.3478 | 23.2858 | 22.6786 | 22.7836 | 23.0003 | 24.9619 | 23.3278 | 23.2827 | 23.3059 | 23.3374 | 25.18 | 23.0915 | 23.1014 | 23.1392 | 23.0999 | 23.025 | 23.1141 | 23.1836 | 22.8529 | 23.2657 | 22.9501 | 23.1684 | 23.1985 | 23.1752 | 23.1126 | 24.5608 | 23.832 | 23.7351 | 23.7536 | 23.7273 | 25.6781 | 23.3227 | 23.3911 | 23.4184 | 23.3746 | 23.3928 | 23.5172 | 23.7888 | 23.2677 | 22.9609 | 23.331 | 23.3829 | 23.3506 | 23.3388 | 24.5326 | 48.5901 | 82.2585 | 29.7232 | 33.5439 | 46.3662 | 48.4874 | 37.6867 | 61.3984 | 49.9382 | 64.9502 | 127.3092 | 131.1771 | 122.032 | 119.079 | 118.6035 | 119.0346 | 106.7047 | 127.3011 | 33.2643 | 29.4633 | 34.7483 | 31.792 | 22.7147 | 22.6776 |  | 22.3433 | 22.316 | 22.2487 | 22.2024 | 22.2862 | 22.2726 | 23.1953 | 22.534 | 22.4771 | 24.702 | 22.4922 | 22.7143 | 23.0027 | 22.9109 | 22.8555 | 22.7865 | 22.7377 | 22.6995 | 22.6329 | 22.7525 | 23.6645 | 22.743 | 22.7484 | 23.7655 | 24.6256 | 23.7972 | 22.8964 | 23.1049 | 24.1551 | 23.8977 | 22.9478 | 22.9922 | 22.9612 | 22.9166 | 23.1224 | 22.8165 | 22.8232 | 22.75 | 23.6347 | 22.6042 | 22.7158 | 22.9872 | 25.8689 | 23.8758 | 23.8241 | 23.7328 | 23.6818 | 24.3925 | 23.8192 | 23.7527 | 23.6731 | 23.5978 | 23.4752 | 23.5139 | 23.2938 | 23.1116 | 23.364 | 23.1417 | 23.6923 | 23.6143 | 23.5669 | 23.5299 | 25.2324 | 24.1559 | 24.0541 | 23.9351 | 23.907 | 29.5355 | 23.6291 | 23.8383 | 23.7732 | 23.6873 | 23.6387 | 23.7911 | 24.0346 | 23.3101 | 23.1167 | 24.12 | 24.0235 | 24.0205 | 23.991 | 25.9217 | 37.9225 | 41.5779 | 46.1712 | 41.8034 | 49.4708 | 58.6044 | 68.189 | 45.0615 | 62.7919 | 52.9083 |  | 56.77 | 47.914 | 51.0076 | 24.6851 | 23.4211 | 23.4554 | 28.9397 | 25.8986 | 22.5369 | 24.0472 | 10.8314 | 14.271 | 14.8904 | 11.0966 | -0.00026251 | -0.0025626 | 0.0010796 | 0.0042018 | 0.00097456 | -0.00056924 | 0.018456 | -0.0063877 | -0.024524 | -360.1373 | 17.4151 | -360.4081 | 17.602 | -360.7435 | 18.1461 | -360.762 | 17.5629 | -352.546 | 18.6573 | -352.6167 | 16.8279 | 196.4448 | 362.7124 | 53.3512 | 14.5807 | 11.6038 | 24.2177
13:28 | 125 | 32.0699 |  | 8.2668 | 3.1281 | 0.5694 | 2.9181 | -1.7022 | 12.1813 | 5.305 | 0.6366 | 0.6757 | 0.9872 | 0.7701 | -130.6388 | 2.577 | 6.1126 | 1.6005 | -2.6635 | -1.1415 | 5.0026 |  | 4.6315 | 0.581 | 3.9795 | 3.3698 | 3.3257 | 1.0991 | 4.3226 | 22.9219 | 22.7056 | 22.4251 | 22.3834 | 22.304 | 22.4671 | 22.224 | 22.9503 | 22.6662 | 22.7137 | 22.7151 | 25.1434 | 23.0372 | 22.9653 | 22.9156 | 22.8082 | 22.7002 | 22.6448 | 22.6273 | 22.431 | 22.559 | 22.4617 | 22.9519 | 22.5781 | 22.6193 | 22.6104 | 23.8225 | 23.1948 | 22.7171 | 22.9632 | 23.0834 | 24.2963 | 23.5167 | 22.8994 | 22.9149 | 22.8838 | 22.8181 | 22.8119 | 23.1515 | 22.6304 | 22.3426 | 23.2789 | 22.6788 | 22.778 | 22.9996 | 25.0041 | 23.3302 | 23.2867 | 23.304 | 23.3419 | 25.2133 | 23.0974 | 23.1015 | 23.142 | 23.1011 | 23.0167 | 23.1064 | 23.183 | 22.8566 | 23.2855 | 22.953 | 23.1701 | 23.2044 | 23.1727 | 23.1084 | 24.5896 | 23.834 | 23.7371 | 23.7531 | 23.7318 | 25.7161 | 23.3255 | 23.3887 | 23.4151 | 23.3747 | 23.3898 | 23.5211 | 23.8039 | 23.2766 | 22.9729 | 23.3334 | 23.3848 | 23.3566 | 23.3402 | 24.5655 | 48.5653 | 82.5208 | 29.9437 | 33.6062 | 46.7777 | 48.9421 | 37.8276 | 61.7215 | 50.2213 | 65.3727 | 126.8041 | 131.4099 | 123.5757 | 118.7744 | 120.3455 | 118.2458 | 108.2283 | 129.8382 | 33.4966 | 29.6064 | 34.9786 | 31.9916 | 22.7102 | 22.6793 |  | 22.3426 | 22.3065 | 22.2436 | 22.2023 | 22.2914 | 22.2704 | 23.1926 | 22.5266 | 22.4783 | 24.7382 | 22.4983 | 22.7148 | 23.0043 | 22.9115 | 22.8539 | 22.7833 | 22.745 | 22.7063 | 22.6412 | 22.7549 | 23.6651 | 22.7471 | 22.7429 | 23.7677 | 24.66 | 23.7963 | 22.9006 | 23.1031 | 24.1694 | 23.8917 | 22.9442 | 22.9899 | 22.9591 | 22.9102 | 23.1346 | 22.8179 | 22.8273 | 22.7596 | 23.6318 | 22.6041 | 22.7158 | 22.9843 | 25.909 | 23.8754 | 23.8206 | 23.7255 | 23.6698 | 24.4054 | 23.8061 | 23.7461 | 23.6695 | 23.5925 | 23.4694 | 23.516 | 23.2911 | 23.1171 | 23.3621 | 23.1463 | 23.6925 | 23.6134 | 23.5498 | 23.5239 | 25.2543 | 24.1482 | 24.0534 | 23.9352 | 23.9095 | 29.6012 | 23.6229 | 23.8357 | 23.7707 | 23.689 | 23.6338 | 23.7948 | 24.0447 | 23.3221 | 23.1232 | 24.1234 | 24.0263 | 24.0201 | 23.9916 | 25.9571 | 38.0125 | 41.7055 | 45.854 | 41.9933 | 49.8888 | 59.0237 | 68.8442 | 45.2814 | 63.2526 | 53.2294 |  | 57.2312 | 48.3696 | 51.3957 | 24.6944 | 23.4325 | 23.4618 | 29.0487 | 25.9585 | 22.5644 | 24.1031 | 10.8299 | 14.2981 | 14.8701 | 11.0873 | 0.00020898 | -0.0032722 | 0.0018546 | 0.0041084 | 0.0010164 | -0.00065987 | 0.0081627 | -0.0010839 | -0.024386 | -360.1558 | 17.4048 | -360.4296 | 17.6225 | -360.7989 | 18.1892 | -360.845 | 17.5814 | -352.5706 | 18.6717 | -352.6136 | 16.8423 | 198.9215 | 362.5706 | 53.8091 | 14.5841 | 11.6031 | 24.2614
13:28 | 126 | 32.0709 |  | 8.2507 | 3.1471 | 0.6897 | 2.9466 | -1.7681 | 12.1687 | 5.3497 | 0.6352 | 0.6767 | 0.9822 | 0.7683 | -130.62 | 2.4435 | 6.2111 | 1.5646 | -2.7565 | -1.2073 | 4.9743 |  | 4.6765 | 0.7039 | 3.9787 | 3.3683 | 3.328 | 1.0984 | 3.0023 | 22.9157 | 22.6989 | 22.4166 | 22.3794 | 22.295 | 22.4693 | 22.219 | 22.947 | 22.6585 | 22.7011 | 22.7069 | 25.1782 | 23.0332 | 22.9594 | 22.9192 | 22.8098 | 22.7024 | 22.6412 | 22.6252 | 22.4283 | 22.5598 | 22.4678 | 22.9542 | 22.5798 | 22.6206 | 22.6169 | 23.8536 | 23.1962 | 22.7256 | 22.9669 | 23.0837 | 24.3231 | 23.5071 | 22.8816 | 22.917 | 22.8915 | 22.8254 | 22.8 | 23.1618 | 22.6149 | 22.3486 | 23.2787 | 22.6789 | 22.7699 | 23.0012 | 25.0434 | 23.33 | 23.2863 | 23.2968 | 23.3455 | 25.2429 | 23.089 | 23.0987 | 23.1337 | 23.0962 | 23.0133 | 23.1154 | 23.1859 | 22.8514 | 23.3028 | 22.9566 | 23.1746 | 23.2008 | 23.1755 | 23.1086 | 24.6254 | 23.835 | 23.7447 | 23.7507 | 23.7328 | 25.7516 | 23.3283 | 23.3923 | 23.4161 | 23.3762 | 23.3852 | 23.5237 | 23.8137 | 23.2861 | 22.9808 | 23.3365 | 23.3824 | 23.357 | 23.3444 | 24.5861 | 48.652 | 82.5039 | 29.9952 | 33.6819 | 47.1835 | 49.4086 | 37.9873 | 62.0549 | 50.522 | 65.8329 | 126.4663 | 132.2146 | 124.7106 | 117.6549 | 121.48 | 119.5834 | 113.7387 | 129.3808 | 33.7286 | 29.7538 | 35.2022 | 32.1915 | 22.6969 | 22.678 |  | 22.3333 | 22.2942 | 22.2316 | 22.1954 | 22.2873 | 22.2636 | 23.1872 | 22.5159 | 22.477 | 24.7668 | 22.4922 | 22.7087 | 23.0106 | 22.912 | 22.8454 | 22.7867 | 22.7433 | 22.7052 | 22.6455 | 22.7626 | 23.6673 | 22.7486 | 22.7403 | 23.7699 | 24.6945 | 23.7916 | 22.8981 | 23.1029 | 24.1813 | 23.8852 | 22.9446 | 22.9817 | 22.9565 | 22.9085 | 23.1383 | 22.818 | 22.8314 | 22.7603 | 23.6246 | 22.6044 | 22.7132 | 22.9873 | 25.9435 | 23.8723 | 23.8124 | 23.7244 | 23.6706 | 24.4122 | 23.7813 | 23.7418 | 23.6569 | 23.5872 | 23.4645 | 23.5101 | 23.2857 | 23.1176 | 23.366 | 23.145 | 23.7016 | 23.6148 | 23.5525 | 23.5257 | 25.2875 | 24.1507 | 24.0527 | 23.9372 | 23.9142 | 29.678 | 23.6288 | 23.8451 | 23.7785 | 23.6966 | 23.6354 | 23.8006 | 24.0607 | 23.3367 | 23.1354 | 24.1316 | 24.0332 | 24.0242 | 23.9938 | 25.9964 | 38.1937 | 41.9043 | 45.6407 | 42.2523 | 50.3107 | 59.4391 | 69.5092 | 45.5321 | 63.742 | 53.545 |  | 57.6909 | 48.8256 | 51.7703 | 24.6841 | 23.4247 | 23.4603 | 29.143 | 26.0243 | 22.58 | 24.1433 | 10.8073 | 14.2757 | 14.8768 | 11.1207 | 0.00043948 | -0.0031858 | 0.0017801 | 0.0045033 | 0.0013368 | -0.00099254 | 0.0085847 | -0.0027649 | -0.032658 | -360.1958 | 17.4254 | -360.4358 | 17.6163 | -360.802 | 18.183 | -360.8112 | 17.5917 | -352.5644 | 18.6717 | -352.6229 | 16.832 | 193.8294 | 366.7564 | 54.2672 | 14.5763 | 11.622 | 24.3022
13:28 | 127 | 32.1016 |  | 8.2388 | 3.0418 | 0.5441 | 2.9226 | -1.7993 | 12.133 | 5.1397 | 0.6364 | 0.6761 | 0.9824 | 0.7716 | -130.637 | 2.4815 | 6.2256 | 1.5318 | -2.7696 | -1.1948 | 5.0677 |  | 4.6463 | 0.6342 | 3.9768 | 3.3708 | 3.3273 | 1.0974 | 4.4093 | 22.9225 | 22.6955 | 22.4193 | 22.3804 | 22.2976 | 22.4694 | 22.2215 | 22.9459 | 22.66 | 22.7073 | 22.709 | 25.2168 | 23.0411 | 22.9575 | 22.9215 | 22.8094 | 22.7043 | 22.6438 | 22.617 | 22.4305 | 22.562 | 22.4735 | 22.9496 | 22.5755 | 22.6156 | 22.6161 | 23.8783 | 23.196 | 22.7231 | 22.9682 | 23.0882 | 24.3451 | 23.5121 | 22.8768 | 22.9169 | 22.8908 | 22.8228 | 22.8011 | 23.1753 | 22.6238 | 22.3441 | 23.279 | 22.6726 | 22.7668 | 22.9972 | 25.0802 | 23.3305 | 23.2821 | 23.2947 | 23.3482 | 25.2721 | 23.0827 | 23.1 | 23.1324 | 23.0992 | 23.0225 | 23.1295 | 23.1961 | 22.8582 | 23.3078 | 22.9576 | 23.1752 | 23.1923 | 23.1759 | 23.1117 | 24.6569 | 23.838 | 23.7443 | 23.7506 | 23.7329 | 25.7793 | 23.327 | 23.3924 | 23.4149 | 23.3776 | 23.3917 | 23.5271 | 23.8281 | 23.2895 | 22.9843 | 23.3423 | 23.3771 | 23.349 | 23.3434 | 24.6107 | 49.1623 | 83.256 | 29.9921 | 33.7536 | 47.5965 | 49.9044 | 38.138 | 62.4052 | 50.8534 | 66.2967 | 126.5374 | 133.426 | 125.5557 | 117.4221 | 122.353 | 121.3383 | 113.9067 | 127.3425 | 33.96 | 29.8907 | 35.4233 | 32.3895 | 22.6966 | 22.6801 |  | 22.3293 | 22.3012 | 22.2324 | 22.1976 | 22.2886 | 22.2702 | 23.1859 | 22.5215 | 22.4815 | 24.7992 | 22.4904 | 22.7127 | 23.0164 | 22.9197 | 22.8467 | 22.7911 | 22.7422 | 22.7069 | 22.6504 | 22.7777 | 23.67 | 22.7513 | 22.7485 | 23.7685 | 24.7286 | 23.7954 | 22.9041 | 23.1105 | 24.2004 | 23.8925 | 22.9455 | 22.987 | 22.957 | 22.9124 | 23.1519 | 22.8265 | 22.8393 | 22.7691 | 23.6204 | 22.604 | 22.7159 | 22.9972 | 25.9846 | 23.8685 | 23.8114 | 23.7274 | 23.6774 | 24.4243 | 23.781 | 23.7443 | 23.6592 | 23.5965 | 23.4654 | 23.5203 | 23.3004 | 23.122 | 23.3861 | 23.1509 | 23.7077 | 23.6189 | 23.5619 | 23.5277 | 25.3186 | 24.159 | 24.0532 | 23.9404 | 23.9205 | 29.7546 | 23.6383 | 23.8582 | 23.7822 | 23.6964 | 23.6396 | 23.8078 | 24.0791 | 23.3469 | 23.1441 | 24.1318 | 24.0343 | 24.0295 | 23.9987 | 26.0382 | 38.3731 | 42.0557 | 45.8138 | 42.5179 | 50.7406 | 59.8547 | 70.1467 | 45.8194 | 64.2542 | 53.8622 |  | 58.1716 | 49.2885 | 52.1373 | 24.6937 | 23.4243 | 23.4584 | 29.2394 | 26.0909 | 22.5976 | 24.2019 | 10.8235 | 14.2779 | 14.9005 | 11.1086 | 0.00017324 | -0.0030066 | 0.0017493 | 0.0044721 | 0.0010472 | -0.00041245 | 0.013483 | -0.0026371 | -0.014249 | -360.1004 | 17.3946 | -360.3865 | 17.6061 | -360.7681 | 18.1502 | -360.7866 | 17.565 | -352.5521 | 18.6347 | -352.5706 | 16.8238 | 209.1704 | 360.0968 | 54.73 | 14.5892 | 11.4409 | 24.3442
13:28 | 128 | 32.057 |  | 8.2114 | 3.0265 | 0.6391 | 2.8842 | -1.8182 | 12.1317 | 5.145 | 0.6358 | 0.6732 | 0.9833 | 0.7681 | -130.6583 | 2.3622 | 6.186 | 1.4918 | -2.8278 | -1.2324 | 4.9292 |  | 4.6809 | 0.6314 | 3.9789 | 3.3704 | 3.326 | 1.0965 | 2.9064 | 22.9285 | 22.701 | 22.4242 | 22.3819 | 22.3019 | 22.4793 | 22.2224 | 22.9443 | 22.6625 | 22.7096 | 22.713 | 25.265 | 23.0414 | 22.9607 | 22.9219 | 22.8102 | 22.7098 | 22.651 | 22.6282 | 22.4345 | 22.5716 | 22.4887 | 22.9506 | 22.5846 | 22.6228 | 22.6155 | 23.9129 | 23.2033 | 22.7243 | 22.9721 | 23.0915 | 24.3795 | 23.5194 | 22.8864 | 22.9238 | 22.8874 | 22.8208 | 22.8151 | 23.1811 | 22.6402 | 22.341 | 23.2801 | 22.6674 | 22.7723 | 23.0004 | 25.1168 | 23.335 | 23.2765 | 23.2933 | 23.3444 | 25.3031 | 23.0896 | 23.1034 | 23.1388 | 23.0997 | 23.0198 | 23.1267 | 23.2004 | 22.8675 | 23.3126 | 22.951 | 23.1741 | 23.1986 | 23.178 | 23.1139 | 24.6836 | 23.8359 | 23.7365 | 23.749 | 23.7365 | 25.8138 | 23.3277 | 23.3951 | 23.4153 | 23.3776 | 23.3944 | 23.5323 | 23.847 | 23.2977 | 22.9881 | 23.3365 | 23.3871 | 23.3506 | 23.3437 | 24.641 | 49.4454 | 83.7166 | 30.0617 | 33.8106 | 48.0063 | 50.4191 | 38.2662 | 62.7714 | 51.2253 | 66.7507 | 128.16 | 134.5181 | 126.3919 | 118.1492 | 121.4873 | 122.8996 | 110.8099 | 126.9073 | 34.1897 | 30.0309 | 35.6567 | 32.5877 | 22.7099 | 22.687 |  | 22.3327 | 22.3097 | 22.2424 | 22.2035 | 22.3044 | 22.2853 | 23.1952 | 22.5247 | 22.4861 | 24.835 | 22.4992 | 22.7226 | 23.0166 | 22.9198 | 22.8517 | 22.7847 | 22.7507 | 22.7098 | 22.6435 | 22.7855 | 23.6737 | 22.7594 | 22.7578 | 23.7737 | 24.7658 | 23.8021 | 22.9132 | 23.1181 | 24.2182 | 23.8951 | 22.9478 | 22.9928 | 22.9604 | 22.9149 | 23.1688 | 22.8353 | 22.8531 | 22.7805 | 23.6305 | 22.6059 | 22.7262 | 23.0054 | 26.0407 | 23.8712 | 23.8135 | 23.7271 | 23.6798 | 24.4358 | 23.7999 | 23.7504 | 23.6662 | 23.5998 | 23.4645 | 23.5319 | 23.3091 | 23.1375 | 23.4063 | 23.1616 | 23.7018 | 23.6178 | 23.56 | 23.5281 | 25.3442 | 24.1522 | 24.0518 | 23.9361 | 23.917 | 29.8242 | 23.6398 | 23.8505 | 23.7818 | 23.6938 | 23.637 | 23.8135 | 24.0898 | 23.3506 | 23.154 | 24.1262 | 24.0338 | 24.0306 | 24.0057 | 26.0704 | 38.5262 | 42.1586 | 45.9642 | 42.7114 | 51.1648 | 60.2938 | 70.7515 | 46.1017 | 64.7549 | 54.1551 |  | 58.6563 | 49.7625 | 52.4991 | 24.6973 | 23.4287 | 23.462 | 29.3441 | 26.1602 | 22.6135 | 24.2546 | 10.8157 | 14.2985 | 14.915 | 11.1075 | 9.3275e-06 | -0.002469 | 0.0017972 | 0.005037 | 0.0014896 | -0.00062225 | 0.023553 | -0.019117 | -0.023465 | -360.1527 | 17.4172 | -360.4358 | 17.6533 | -360.8081 | 18.1728 | -360.8112 | 17.5753 | -352.6013 | 18.6758 | -352.629 | 16.8525 | 208.9785 | 369.7294 | 55.1942 | 14.6068 | 11.3678 | 24.3868
13:28 | 129 | 31.9767 |  | 8.0636 | 3.0381 | 0.5842 | 2.8239 | -1.7696 | 12.1614 | 5.1707 | 0.6368 | 0.6754 | 0.9842 | 0.7697 | -130.6901 | 2.2764 | 6.1585 | 1.4578 | -2.7956 | -1.2524 | 4.8999 |  | 4.6471 | 0.6537 | 3.9791 | 3.3717 | 3.329 | 1.0977 | 3.5334 | 22.9309 | 22.7079 | 22.4289 | 22.3898 | 22.3039 | 22.4831 | 22.2218 | 22.9472 | 22.6682 | 22.7093 | 22.7177 | 25.3177 | 23.0379 | 22.9606 | 22.9197 | 22.8165 | 22.7078 | 22.656 | 22.649 | 22.4374 | 22.5798 | 22.4944 | 22.9597 | 22.5936 | 22.6329 | 22.6163 | 23.9462 | 23.2112 | 22.7299 | 22.9785 | 23.0966 | 24.4169 | 23.5237 | 22.8888 | 22.9319 | 22.8922 | 22.8214 | 22.8225 | 23.1941 | 22.664 | 22.3493 | 23.2843 | 22.6744 | 22.7785 | 23.0013 | 25.1509 | 23.3377 | 23.2777 | 23.2921 | 23.3449 | 25.3333 | 23.0858 | 23.0965 | 23.1426 | 23.0994 | 23.0176 | 23.1193 | 23.2011 | 22.8595 | 23.3233 | 22.9487 | 23.1769 | 23.2074 | 23.1787 | 23.1202 | 24.7061 | 23.8391 | 23.7386 | 23.7494 | 23.7385 | 25.8559 | 23.3261 | 23.3922 | 23.4193 | 23.3806 | 23.3938 | 23.5352 | 23.8579 | 23.3075 | 22.9939 | 23.3355 | 23.3911 | 23.3537 | 23.3488 | 24.6644 | 50.2162 | 84.3357 | 30.1192 | 33.8843 | 48.4172 | 50.9532 | 38.4047 | 63.1629 | 51.6216 | 67.1979 | 130.5531 | 135.6163 | 127.364 | 118.4467 | 120.2181 | 123.9674 | 112.2993 | 128.2248 | 34.4136 | 30.1776 | 35.9022 | 32.7808 | 22.708 | 22.688 |  | 22.3395 | 22.3109 | 22.2439 | 22.2113 | 22.3108 | 22.2851 | 23.2024 | 22.528 | 22.4909 | 24.8635 | 22.5035 | 22.7248 | 23.0184 | 22.9143 | 22.8538 | 22.777 | 22.7561 | 22.7116 | 22.6368 | 22.7918 | 23.6776 | 22.7578 | 22.7594 | 23.7806 | 24.7999 | 23.8033 | 22.9102 | 23.1188 | 24.2409 | 23.897 | 22.9571 | 22.9931 | 22.9617 | 22.9207 | 23.1798 | 22.8376 | 22.8614 | 22.7889 | 23.6331 | 22.6102 | 22.725 | 23.0067 | 26.0955 | 23.8749 | 23.8127 | 23.7298 | 23.6798 | 24.4509 | 23.8077 | 23.7579 | 23.6661 | 23.5982 | 23.4698 | 23.5366 | 23.3179 | 23.1484 | 23.415 | 23.1722 | 23.7025 | 23.62 | 23.556 | 23.5324 | 25.3747 | 24.1529 | 24.0525 | 23.9431 | 23.9236 | 29.9029 | 23.6443 | 23.8482 | 23.7838 | 23.6961 | 23.6401 | 23.8244 | 24.0963 | 23.3569 | 23.1544 | 24.1223 | 24.0295 | 24.0251 | 24.0064 | 26.1041 | 38.7025 | 42.3169 | 45.8643 | 42.8753 | 51.5897 | 60.7822 | 71.3512 | 46.3825 | 65.2438 | 54.4046 |  | 59.1381 | 50.2272 | 52.8645 | 24.6958 | 23.4283 | 23.4632 | 29.4454 | 26.2188 | 22.6278 | 24.3068 | 10.7925 | 14.2678 | 14.8888 | 11.0994 | 0.00019308 | -0.0027469 | 0.00092515 | 0.0042102 | 0.0010485 | -0.00020625 | 0.0008325 | -0.0028834 | -0.013774 | -360.165 | 17.4213 | -360.4019 | 17.6369 | -360.765 | 18.1728 | -360.8389 | 17.5835 | -352.5798 | 18.6737 | -352.5983 | 16.8258 | 204.4387 | 363.9711 | 55.6654 | 14.5783 | 11.3048 | 24.4233