| # Last updated September 2003 | # Surge Protection Anthology # Citations – Part 5 ## Monitoring instruments, ## Laboratory measurements, and Test methods | # Surges Happen ! |
| --- | --- | --- |

See website for links to documents in blue.

ALLEN, G.W., “Design of Power-Line Monitoring Equipment,” IEEE Transactions, PAS-90, May 1971.

‒   Description of the instrumentation used by Allen and Segall in [53].

‒   5 references

BULL, J.H., “Impedance of the Supply Mains at Radio Frequencies,” Proceedings, 2nd Symposium on Electromagnetic Compatibility, Montreux, 1975.

‒   Reports measurements and 50 Ω/50 μH equivalent circuit.

‒   6 references

BUSCHKE, H.A., “A Practical Approach to Testing Electronic Equipment for Susceptibility to AC Line Transients,” IEEE Transactions on Reliability, vol. 37, No. 4, Oct. 1988.

‒   Describes test methods and test circuits developed independently from standard approaches.

‒   3 references

CUMMINS, K.L., KRIDER, E.P., and MALONE, M.D., “The U.S. National Lightning Detection Network ™ and Applications of Cloud-to-Ground Lightning Data by Electric Power Utilities,” IEEE Transactions EM-40 No.4, November 1998.

‒   Discusses the principle of lightning detection.

‒   Provides guidelines on the uncertainties of lightning parameters that are acceptable in the industry.

‒   75 references

CROUCH, K.E. and MARTZLOFF, F.D., “Lightning Protection of Residential AC Wiring,” Declassified GE Memo Report MOR-78-095, 1978.

Accessible as  Propagation 1978

‒  Effect of large currents flowing in the neutral/grounding conductor of the service drop to a building.

‒  A unidirectional 8/20 s current flowing only in the grounding conductors induces oscillatory transients in the differential mode. (Test results contributed to the data base of IEEE Std C62.41.)

‒  5 references

FISHER, F.A. and MARTZLOFF, F.D., “Transient Control Level Philosophy and Implementation, Part II: Techniques and Equipment for Making TCL Tests,” Proceedings, 2nd Symposium on Electromagnetic Compatibility, Montreux, 1977.

Accessible as  TCL testing

‒  Second part of a paper proposing a test protocol based on concepts derived from high-voltage BIL testing.

‒  General discussion of circuits for surge generators.

FOUST, C.M., “Instruments for lightning measurements,” General Electric Review, Vol 34, No.4, April 1931

Accessible as  Foust 1931

‒  This rare archival paper is included as an annex to this part of the SPD Anthology to illustrate the progress made in instrumentation since the earliest cathode-ray oscillograph.

‒  The “Surge Voltage Recorder” based on Lichtenberg Figures is also described in this article – a photograph of the only known survivor in existence (70 years later) of these instruments appears in the 2002 article “PQ Monitoring: Where do we go from here?” -- Accessible as  PQ Monitoring ).

GAUPER, H.A. and MARTZLOFF, F.D., Discussion of Allen & Segall  paper  “Monitoring of Computer Installations for Power Line Disturbances,” IEEE Conference Paper C 74-199-6, IEEE PES Winter Meeting, New York, 1974.

Accessible as  Discuss A&S

‒   The original conference paper is no longer available as it was not published in the Transactions – nor was the discussion.  The file included in the Anthology was scanned from archival files.

‒   The discussion offers some comments on instrumentation limitations and the importance of sensitivity settings threshold selection

HASSE, P. and BIRKL, J., “EMV-Testverfahren zur Ableiterkoordination” [EMC Test Procedures for Coordination of Surge Protective Devices], EMC Kompendium 1998, pp 112-115.

‒   Proposes to define a “steepness factor” to characterize the initial rate of rise of current.

HOWELL, E.K. and MARTZLOFF, F.D., “High-Voltage Impulse Testers,” Unclassified GE TIS Report 75 CRD039, March 1975

Accessible as Impulse testers

‒   Describes three possible approaches toward obtaining an oscillatory transient of the tuype that became the IEEE “Ring Wave”

‒   4 references

KEY, T.S. and MARTZLOFF, F.D. “Surging the Upside-Down House: Looking into Upsetting Reference Voltages,” Proceedings, EPRI-PQA’94 Conference, Amsterdam, October 1994.

Accessible as  Upsdwn surging

‒   Describes a test bed for the propagation and mitigation of surges.

‒   Illustrates the differences of voltage references developed across multiple ports of appliances.

‒   8 references

KEY, T.S., MANSOOR, A. and MARTZLOFF, F.D., “No Joules for Surges: Relevant and Realistic Assessment of Surge Stress Threats,” Proceedings, IEEE International Conference on Harmonics and Power Quality, Las Vegas NV, Oct. 1996.

Accessible as  No joules

‒   Challenges the erroneous concept of characterizing “energy in the surge” from a simple voltage measurement.

‒   Lists surge parameters leading to failure of specific equipment.

‒   15 references

KREISS, D.G., The Dranetz Field Handbook for Power Quality Analysis, Dranetz Technologies, Inc., Edison NJ.

‒   One chapter on planning and performing a power quality survey includes the topic of ‘impulses’.

‒   One chapter on waveforms shows examples of recorded surges.

LINDES, G., MANSOOR, A., MARTZLOFF, F.D., and VANNOY, D., “Surge Recordings That Make Sense: Joules Deposition: Yes! - ‘Joule Content’: Never!,” Proceedings, PQA’97 USA, 1997

Accessible as  Joules Yes-No

‒   Challenges the erroneous concept of “energy in the surge” based on a simple voltage measurement.

‒   Lists surge parameters leading to failure of specific equipment.

‒   Proposes the approach for using existing power quality monitors to record available surge currents.

‒   24 references

MANSOOR, A., MARTZLOFF, F.D., and PHIPPS, K. “The Fallacy of Monitoring Surge Voltages: SPDs and PCs Galore!,” Proceedings, EPRI PQA’99 Conference, May 1999.

Accessible as  Galore

‒   Experimental measurements of effective mitigation by multiple SPDs.

‒   Numerical simulation of the effect of proliferating SPDs and PCs.

‒   Calls for an industry-wide reassessment of surge monitoring parameters.

‒   18 references

MARKEL, L.C., MELHORN, C.J., WILLIAMS, S.R., and MEHTA, H., “Design of a Measurement Program to Characterize Distribution System Power Quality,” CIRED 12th International Conference on Electricity Distribution, 1993.

‒   Simplification of a system-wide survey through stratified random sampling.

MARTZLOFF, F.D., “Surge Suppression in a Typical Home Wiring System,” Declassified GE TIS Report 63GL97, 1963.

Accessible as  Typical home

‒   Injection of surges and their mitigation in a residential power system.

‒   Examples of suppression achieved by selenium cells before the advent of metal-oxide varistors.

‒   2 references

MARTZLOFF, F.D., “Effect of Rate of Voltage Rise on Reverse Breakdown of Silicon Diodes.” Declassified GE TIS Report 63GL132, 1963.

Accessible as  Rate of rise

‒   Steep front surges tend to increase the level at which 1960's diodes failed under surge conditions.

‒   Higher peak inverse voltage (PIV) do not result in higher levels for the surges that cause failure.

MARTZLOFF, F.D., “Low Cost Surge Counter,” Declassified GE TIS Report 64GL166, 1964.

Accessible as  Surge counter

‒   Design of the surge counters used for the surge monitoring reported in Martzloff & Hahn, 1970.

MARTZLOFF, F.D., “Semiconductor Performance under Reverse Transient Over-voltages,” Declassified GE TIS Report 67C-066, 1966.

Accessible as  Reverse semicon

‒   For semiconductors of the late sixties vintage, there is no correlation between their peak inverse voltage rating (PIV) and the surge level at which failure occurs – most likely by edge flashover.

‒   Ageing by storage at elevated temperature changed the PIV but not the surge failure level.

‒   8 references

MARTZLOFF, F.D., “High Speed Transient Recording System,” Declassified GE TIS Report 68-C-019, January 1968.

Accessible as  Hi-speed recorder

‒   Description of a now-obsolete system for recording transients with nanosecond rise time and kilovolts peaks, with effective protection against spurious signals

‒   5 references

MARTZLOFF, F.D., “Transient Control Level Test Generators.” Unclassified GE TIS Report 77CRD241, 1977.

Accessible as  TCL generator

‒   Development of a home-made Ring Wave generator used in the seventies and eighties.

‒   Two examples of circuits with identical open-circuit voltage waveforms, but different short-circuit current waveforms.

‒   8 references

MARTZLOFF, F.D. and FISHER, F.A., “Transient Control Level Philosophy and Implementation, Part 1: The Reasoning Behind the Philosophy,” Proceedings, 2nd Symposium on Electromagnetic Compatibility, Montreux, 1977.

Accessible as  TCL Philosophy

‒   Techniques and equipment for making TCL tests.

‒   10 references

MARTZLOFF, F.D., Discussion of IEEE paper by Aspnes, J.D., Evans, B.W., and Merritt, R.P., "Rural Alaska Power Quality,” IEEE Transactions PAS-104, No. 4, March 1985.

Accessible as  Discuss A&E&M

‒   Signals the fallacy of surge recordings from a monitoring instrument that included an internal SPD to protect its own power supply, inadvertently mitigating surges on the receptacle also used as power source to be monitored.

MARTZLOFF, F.D., “Surge Testing: Don’t Kid Yourself, Don’t Kill Yourself !” EMC Technology and Interference Control News, August 1988.

Accessible as  Don’t kid-kill

‒   Overview of the just-then-published IEEE Guide on Surge Testing, C62.45-1987.

MARTZLOFF, F.D. and GRUZS, T.M., “Power Quality Site Surveys: Facts, Fiction and Fallacies.”  IEEE Transactions IA-24, No.6, November/December 1988.

Accessible as  PQ surveys FFF

‒   Review of surveys conducted in the 1960-1990 period and discussion of limitations

‒   Introduces the new term of “swell” to designate temporary overvoltages as opposed to surges

‒   33 references

MARTZLOFF, F.D. and GRUZS, T.M., “Monitoring Power Quality,”  Powertechnics Magazine, February 1990.

Accessible as  Monitoring PQ

‒   First part of a two-part trade magazine article based on the IEEE paper “Power Quality Site Surveys: Facts, Fiction and Fallacies.”

‒   11 references

MARTZLOFF, F.D. and PELLEGRINI, G., “Real, Realistic Ring Waves for Surge Testing,” Proceedings, 9th International Zürich Symposium on Electromagnetic Compatibility, 1991.

Accessible as  Real waves

‒   Reports measurements on the propagation of oscillatory waves in typical low-voltage circuits, as opposed to the unidirectional waves initially defines for high-voltage power systems.

‒   Shows how impinging unidirectional surges can produce oscillatory waves responses.

‒   17 references

MARTZLOFF, F.D., “Keeping up with the Reality of Today’s Surge Environment,” Proceedings, Power Quality ‘95 Conference, 1995.

Accessible as  Keeping up

‒   Explains that monitoring voltage surges no longer makes sense because of the proliferation of SPDs.

‒   Rebuts the misconception of characterizing surges by their “energy content.”

‒   Proposes an IEEE-sponsored sharing of field failure data as an assessment of the surge environment.

‒   15 references

MARTZLOFF, F.D., “Surge Recordings That Make Sense: Shifting Focus from Voltage to Current measurements,” Proceedings, EMC ROMA 96 Symposium, 1996.

Accessible as  Make sense

‒   Makes the case that the proliferation of SPDs makes monitoring surge voltages debatable.

‒   Proposes an approach for using existing power quality monitors to record available surge currents.

‒   18 references

MARTZLOFF, F.D., MANSOOR, A., PHIPPS, K.O., and GRADY, W.W., “Surging the Upside-Down House: Measurement and Modeling Techniques,”  Proceedings, PQA’95 Conference, New York, NY, 1995.

Accessible as Upsdown measure

‒   Describes a test bed for studying the propagation of surges in low-voltage installations.

‒   Test and computer modeling on appliances connected to different systems show reference voltage shifts.

‒   4 references

MARTZLOFF, F.D. and PHIPPS, K.O., “A novel transducer for monitoring surge currents in AC mains,”  Proceedings, EMC Europe 2000 Symposium, Bruges, 2000.

Accessible as  Novel transducer

‒   Proliferation of SPDs makes monitoring surge voltage debatable, hence a need for an easy-to-deploy current transducer

‒   Reports an a breadboard trial and limitations of the approach.

‒   12 references

MARTZLOFF, F.D., “A New IEC Standard on the Measurement of Power Quality Parameters,” Proceedings, EMC Europe 2000 Symposium, Bruges, 2000.

Accessible as  PQ IEC Standard

‒   Progress report on the development of IEC 61000-4-30 “Electromagnetic Compatibility (EMC) – Part 4-30: Testing and measurement techniques – Power quality measurement methods.”

‒   Provides some historical perspective on the chartering of this activity in IEC SC77A.

‒   15 references

MARTZLOFF, F.D. and PHIPPS, K., Lingering Lead Length Legacies.’  IEEE paper TPWRD-00331-2002  (Scheduled for Transactions PWRD Jan 2004)

Accessible as  Lingering legacies

‒   Presents corrections to some misconceptions about the significance of lead length and proposed designs alleged to overcome the problem

‒   Provides, by laboratory measurements, quantitative information on the magnitude of lead length effects

‒   16 references

McEACHERN, A., Handbook of Power Signatures, Basic Measuring Instruments, Foster City CA, 1989.

‒   Reports generic types of disturbances with non-standard terminology.

‒   Calls a surge as defined by IEEE an ‘impulse’. Calls a swell as defined by IEEE a ‘surge’.

‒   Describes procedures on conducting a site survey.

‒   267 pages

MILLANTA, L.M. and FORTI, M.M., “A Notch-Filter Network for Wide-Band Measurements of Transient Voltages on the Power Line,” IEEE Transactions on EMC, Aug. 1988.

‒   Describes the design and characteristics of a probe that filters out the power-frequency component.

‒   20 references

MILLANTA, L.M., FORTI, M.M., and MACI, S.S., “A Broad-Band Network for Power-Line Disturbance Voltage Measurements,” IEEE Transactions EMC-30, No.3, Aug. 1988.

‒   Filter network removing the power-frequency voltage from the record.

‒   5 references

MILLANTA, L.M. and FORTI, M.M., “A Classification of the Power-Line Voltage Disturbances for an Exhaustive Description and Measurement,” Proceedings, IEEE EMC Symposium, 1989.

‒   Proposal for systematic classification of disturbances.

‒   17 references

NAVE, M.J., “A Novel Differential Mode Rejection Network for Conducted Emissions Diagnostics,” Proceedings, IEEE EMC Symposium, 1989.

‒   Discussion of common mode and differential mode from the point of view of frequency domain measurements.

‒   5 references

RICHMAN, P., “Precision Coil Impulse Testing with 0.3 A, Micro-Breakdown Sensitivity,” Power Conversion International, vol. 8, No. 5, May 1982.

‒   General review of surge generator technology.

‒   Detection of breakdown by monitoring both voltage and current waveforms in EUT.

‒   11 references

RICHMAN, P., “Single-Output, Voltage and Current Generation for Testing Electronic Systems,” Proceedings, IEEE 1983 EMC Symposium, 1983.

‒   Presents the case for the Combination Wave rather than separate 1.2/50 μs and 8/20 μs impulses.

‒   4 references

RICHMAN, P., “Changes to Classic Surge-Test Waves Required by Back-Filters Used for Testing Powered Equipment,” Proceedings, 6th Symposium on Electromagnetic Compatibility Zürich, 1985.

‒   Undershoot effects on unidirectional waves, the case for oscillatory waves.

‒   5 references

SENKO, G., “Probes and Techniques for Measuring Surge Voltage Waves with Fronts from 10 ns to 1.2 μs and Peaks to 10 kV,” Proceedings, 7th International Zürich Symposium on Electromagnetic Compatibility, 1987.

‒   Describes a differential probe with 10 kΩ input impedance, 2 ns rise time, 10 kV rating.

‒   5 references

SHAKARJIAN, D.R .and STANDLER, R.B., “AC Power Disturbance Detector Circuit,” IEEE Transactions PWRD-6, No.2, April 1991.

‒   Design, construction, and performance of a circuit that detects transients on low-voltage AC mains.

‒   The disturbance detector circuit can be used to trigger a digital waveform recorder or to operate a counter circuit to simply record the occurrence of a disturbance.

‒   7 references

STANDLER, R.B., “An Experiment to Monitor Disturbances on the Mains,” Proceedings, IEEE IAS Annual Meeting, Oct. 1987.

‒   Experiment to collect waveforms of mains disturbances and determine energy deposited in MOVs.

‒   16 references

STANDLER, R.B., “An Experiment to Monitor Disturbances on the Mains,” Conference Record of the 1987 IEEE Industry Applications Society Annual Meeting, 1987.

‒   Describes the design of an experiment to characterize disturbances on the mains, including the trigger criteria for waveform recorders.

‒   Definitions of some disturbances are provided.

‒   16 references

STANDLER, R.B., “Equations for Some Transient Overvoltage Test Waveforms,” IEEE Transactions EMC-30, No.1, February 1988.

‒   Simple equations are provided that satisfy the definitions of five of the most common transient overvoltage test waveforms: the Ring Wave specified in ANSI C62.41-1980, the fast transient specified in IEC 801, and the 8/20-μs 1.2/50-μs, and 10/1000-μs waveforms.

‒   7 references

STANDLER, R.B., “Standard Waveforms for Surge Testing: Experimental Evaluation and Proposed New Criteria for Tolerances,” Proceedings, 8th International Zürich Symposium on Electromagnetic Compatibility, 1989.

‒   Evaluates several commercial surge generators and proposes using equations to define nominal waveforms and tolerances of unipolar waves.

‒   11 references

STANDLER, R.B., “Calculation of Energy in Transient Overvoltages,” Proceedings, IEEE EMC Symposium, 1989.

‒   Shows that using the integral of V2/50Ω.dt to compute energy in a surge is invalid.

‒   An artificial AC line network simulates a long branch circuit to give line impedance vs. frequency.

‒   18 references

STANDLER, R.B., “American Surge Test Methods for Equipment Connected to the Low-voltage AC Supply Mains,” Proceedings, Lightning Protection 92 - Buildings, Structures and Electronic Equipment Conference 1992.

‒   Describes how electronic equipment and surge protective devices are surge tested in the USA, with emphasis on differences between the American and European practices.

‒   11 references

UMAN, M.A., RAKOV, V.A., RAMBO, K.J., VAUGHT, T.W., FERNANDEZ, M.I., BERNSTEIN, R., and GOLDEN, C., “Triggered-lightning Facility for Studying Lightning Effects on Power Systems,” Proceedings, 23th International Conference on Lightning Protection, Florence, Italy, 1996.

‒   Description of rocket-triggered lightning at Camp Blanding, with examples of recordings.

‒   6 references

WIESINGER, J., “Hybrid-Generator für die Isolationskoordination,” (Hybrid Generators for the Coordination of Insulation) ETZ-104, No. 21, 1983.

‒   Endorses the concept of the Combination Wave in the European context.