| # Last updated December 2002 | # Surge Protection Anthology # Part 8 – Annex A – Citations ## Coordination of cascaded surge-protective devices (See also file Bibliography 1992 for additional citations. See website for links to documents in blue.) | # Surges Happen! |
| --- | --- | --- |

GOEDDE, G.L., MARZ, M.B., and HENRY, D.C., “Coordinating Lightning Stroke Protection From the Utility System to Load Devices,”   Proceedings, Second International Power Quality/ESD Conference, October 1990.

- Describes secondary surge phenomena and the importance of transformer secondary circuit protection coordination to both utilities and end users.

- An effective MOV protection coordination scheme is described and recommended.

- Multiple grounds at different potentials, especially under lightning surge conditions, prevent distribution transformer primary arresters from protecting secondary circuits.

- 13 references

HASSE, P., ZAHLMANN, P., WIESINGER, J., and ZISCHANK, W., “Principle for an Advanced Coordination of Surge-protective Devices in Low-voltage Systems,” Proceedings, 22nd International Conference on Lightning Protection, Budapest, 1994.

- Proposes a scheme where the performance of SPDs for any waveform is converted to an equivalent configuration referred to the performance under the Combination Wave.

- 7 references

HOSTFET, O.T., HERVLAND, T., NANSEN, B., and HUSE, J., “Coordination of Surge Protective Devices in Power Supply Systems: Needs for Secondary Protection,”   Proceedings, 21th International Conference on Lightning Protection, Berlin, September 1992.

- On the basis of observed failures on secondary surge protection devices, theoretical and experimental investigations are performed in order to clarify the need for such protection including the sharing of energy stresses in relation to the primary surge protection system.

- The higher energy stresses will generally occur on the device with the lowest limiting voltage.  Therefore, the protection level for the secondary protection should be selected higher than for the primary protection.

- 5 references

LAI, J.S., “Performance Criteria for Cascading Surge-Protective Devices,” Proceedings, Open Forum on Surge Protection Application, NISTIR-4654, August 1991.

- Voltage limiting level of cascaded devices, their separation distance, and surge waveform are used as parameters to compute the energy deposited in the devices.

- Experimental verification shows reasonable agreement between simulation and experiment.

- Contains details of the data base used for the Lai & Martzloff IEEE Transactions IA-24 1993 paper [291].

- 10 references

LAI, J.S. and MARTZLOFF, F.D., “Coordinating Cascaded Surge-Protection Devices: High-Low versus Low- High,”  IEEE Transactions IA-24, No.4, July/August 1993.  (First publication, Conference Record, IEEE IAS Annual Meeting, September 1991.)

- Accessible as  Coordination 1993 Computations and experiments showing the effect of line length and impinging surge waveform on sharing energy between service entrance arrester and SPD inside building.

- While the 8/20 μs waveform can still result in a contribution from both devices to sharing the energy, the 10/1000 μs waveform does not produce any inductive separation of the devices past the rise time, so that energy is equally shared between devices of equal rating.

- 11 references

MANSOOR, A., MARTZLOFF, F.D., and PHIPPS, K., “Gapped Arresters Revisited: A Solution to Cascade Coordination,”  IEEE Transactions PWRD-13, No.4, December 1998.

Accessible as  Gapped arresters

- Demonstrates the principle of a coordination scheme compatible with downstream SPDs having lower limiting voltage than the SPD at the service entrance.

- 23 references

MARTZLOFF, F.D., “Surge Voltage Suppression in Residential Power Circuits,” Unclassified GE TIS Report 76CRD092, 1976.

Accessible as  Coordination 1976

- Performance of mid-seventies vintage of service entrance SPD and simple MOV plug-in SPD.

- Introduction of the concept of cascade coordination achieved by the inductance of wiring.

- 4 references

MARTZLOFF, F.D. and CROUCH, K.E., “Coordination of overvoltage protection in low-voltage residential systems,” Translated from Conference record, Canadian Conference on Communications and Power, 1978.

- Accessible as  Coordination 1978

- Summary tutorial aimed at the French-speaking Canadian community to solicit comments for IEEE Std 587.

- Tests by injecting a simulated lightning flash current into the grounding system of a simulated house.

- The unidirectional current induces oscillatory transients in the house wiring system.

- 4 references

- MARTZLOFF, F.D., “Coordination of SPDs in Low-Voltage AC Power Circuits,” IEEE Transactions PAS-99, No. 1, Jan/Feb 1980.

- Accessible as  Coordination 1980

- Coordination between voltage-switching and voltage-limiting SPDs.

- Coupling between equipment grounding conductor and phase wires.

- Where an unidirectional current is injected into the ground system only, the response of the system is an oscillating voltage involving the phase conductors.

- Without substantial connected loads in the system, the open-circuit surges appearing at the service entrance propagate along the branch circuits with very little attenuation.

- 7 references

MARTZLOFF, F.D. “The coordination of transient protection for solid-state power conversion equipment,” Conference Record, IEEE/IAS International Semiconductor Power Converter Conference, May 1982.

- Accessible as  Coordination 1982

- Tutorial aimed at semiconductor-oriented audience for an overview of overvoltages and IEEE and IEC work.

- Emphasizes that protection of sensitive equipment is possible if proper coordination is implemented

- Provides some examples

- 17 references

- MARTZLOFF, F.D. and LAI, J.S., “Cascading Surge-Protective Devices: Coordination versus the IEC 664 Staircase,” Proceedings, PQA ‘91 Conference.

- Accessible as  Coordination 1991

- Coordination of cascaded devices can be achieved under various combinations of parameters, but some combinations might leave the smaller device subjected to the highest stress.

- Significant parameters in achieving successful coordination involve three factors, over which the occupant of the premises has no control: the relative limiting voltages of the two devices, their separation distance, and the prevailing waveforms for impinging surges.

- 13 references

- MARTZLOFF, F.D. and LAI, J.S., “Cascading Surge-Protective Devices: Options for Effective Implementation,” Proceedings, PQA ‘92 Conference, September 1992.

- Accessible as  Coordination 1992

- Implications of the situation resulting from the present uncoordinated application of devices with low limiting voltage at the end of branch circuits and devices with higher limiting voltage at the service entrance.

- The reality of having many millions of 130-V rated varistors installed on 120-V systems makes the ideal scenario of a well-coordinated cascade difficult or perhaps unattainable in the near future.

- As a compromise, a cascade with equal voltage ratings for the arrester and the suppressor can offer successful coordination, if the impinging surges are presumed to be relatively short.

- Tolerances on device characteristics might make the compromise ineffective.

- Bibliography with 32 citations

MARTZLOFF, F.D., “Annotated Bibliography – Application of surge-protective devices and coordination of cascades,” Unpublished working document submitted to IEEE and IEC working groups in support of a task force intended to develop standards on the subject of cascade coordination.

- Accessible as  Bibliography 1992

- Compilation of titles, abstracts, conclusions, and, for some of the citations, comments by the reviewer.

- 47 citations

- MARTZLOFF, F.D. and MANSOOR, A., “The role and stress of surge-protective devices in sharing lightning current,” Proceedings, EMC Europe 2002 Symposium, 2002.

- Accessible as  Role of SPDs

- Numerical simulation of the dispersion of lightning current for a direct flash to the building.

- Not only the service entrance SPD gets involved in the exit current, but also SPDs downstream in the building.

- Comparison of actual failure rates of these downstream SPDs with model prediction yields inferences on assumptions made for the lightning flash.

- 23 references

- MARZ, M.B. and MENDIS, S.R., “Protecting Load Devices from the Effects of Low-Side Surges,”   Proceedings, IEEE/ICPS Conference, May 1992.

- Utilities are becoming aware of the low-side surge phenomenon and are applying secondary arresters to protect their distribution transformers.  This practice can increase the voltage stress at the customer service entrance.

- If any ground paths exist on the customer side of the service entrance, these surges can penetrate further into the customer's system.

- Damage caused by low-side surges can be avoided if properly coordinated arresters are installed at the transformer secondary, service entrance, and load device.

- 15 references

- STANDLER, R.B., “Coordination of Surge Arresters and Suppressors for Use on Low-Voltage Mains,”  Proceedings, 9th International Zürich Symposium on Electromagnetic Compatibility, 1991.

- Results of both a theoretical analysis and laboratory experiments are reported on sharing of current between an arrester at the service entrance and a suppressor at receptacles during surges.

- Shows that it is better to design the arrester with a smaller conduction voltage than the suppressor, in order to obtain better coordination, better electromagnetic compatibility, and lower cost.

- Computations were made with only resistance of wire between cascaded devices, no inductance.

- 9 references

- STRINGFELLOW, M.F. and STONELY, B.T., “Coordination of Surge Suppressors in Low-Voltage AC Power Circuits,”  Proceedings, Forum on Surge Protection Application, NISTIR-4657, August 1991.

- Experiments showing the effect of line length and impinging surge waveform on sharing energy between service entrance arrester and surge suppressor inside building.

- Metal-oxide varistors were applied at three points on the system.  These were at the service entrance, at the distribution panel and at the load.

- Removal of protection at either load or distribution panel resulted in unacceptably large oscillatory voltages.  Best load protection was achieved with MOVs in all three locations.

- 4 references

-o-o-o-o-o-o-o-o-o-o-