## sHeaderMod
time
ahu_dp | Differential pressure measurement in the secondary loop by the AHU coils
ahu1_cc_out_rtd | Temperature of the propylene glycol leaving the cooling coil in AHU1
ahu1_cc_rtd | Temperature of the air just after the cooling coil in AHU1
ahu1_f_cc | Flow rate of PG through the cooling coil in AHU1
ahu1_f_ra | Return airflow rate in AHU1
ahu1_f_sa | Supply airflow rate in AHU1
ahu1_fan_power | Power consumption of the AHU1 supply fan
ahu1_heat_c | Control signal for the electric heater in AHU1
ahu1_heat_power | Power consumption of the electric heater in AHU1
ahu1_heat_rtd | Temperature downstream of the electric heater in AHU1
ahu1_in_rtd | Temperature at the inlet of AHU1, after the return and supply air are mixed
ahu1_on | On/off control signal for the AHU1 supply fan
ahu1_out_rtd | Temperature downstream of AHU1
ahu1_p_down | Duct static pressure downstream of AHU1
ahu1_p_up | Static pressure upstream of the supply fan in AHU1
ahu1_rh_down | Relative humidity downstream of AHU1
ahu1_rh_ra | Relative humidity of the return air in AHU1
ahu1_rh_sa | Relative humidity of the supply air in AHU1
ahu1_rh_up | Relative humidity upstream of the supply fan in AHU1, after the return and supply air are mixed
ahu1_t_ra | Temperature of the return air in AHU1
ahu1_t_sa | Temperature of the supply air in AHU1
ahu1_tdb_ra | Dry bulb temperature of the return air in AHU1; same probe as ahu1_rh_ra
ahu1_tdb_sa | Dry bulb temperature of the supply air in AHU1; same probe as ahu1_rh_sa
ahu1_vfd | Speed of the AHU1 supply fan
ahu2_cc_out_rtd | Temperature of the propylene glycol leaving the cooling coil in AHU2
ahu2_cc_rtd | Temperature of the air just after the cooling coil in AHU2
ahu2_f_cc | Flow rate of PG through the cooling coil in AHU2
ahu2_f_ra | Return airflow rate in AHU2
ahu2_f_sa | Supply airflow rate in AHU2
ahu2_fan_power | Power consumption of the AHU2 supply fan
ahu2_heat_c | Control signal for the electric heater in AHU2
ahu2_heat_power | Power consumption of the electric heater in AHU2
ahu2_heat_rtd | Temperature downstream of the electric heater in AHU2
ahu2_in_rtd | Temperature at the inlet of AHU2, after the return and supply air are mixed
ahu2_on | On/off control signal for the AHU2 supply fan
ahu2_out_rtd | Temperature downstream of AHU2
ahu2_p_down | Duct static pressure downstream of AHU2
ahu2_p_up | Static pressure upstream of the supply fan in AHU2
ahu2_rh_down | Relative humidity downstream of AHU2
ahu2_rh_ra | Relative humidity of the return air in AHU2
ahu2_rh_up | Relative humidity upstream of the supply fan in AHU2, after the return and supply air are mixed
ahu2_t_ra | Temperature of the return air in AHU2
ahu2_t_sa | Temperature of the supply air in AHU2
ahu2_tdb_ra | Dry bulb temperature of the return air in AHU2; same probe as ahu2_rh_ra
ahu2_vfd | Speed of the AHU2 supply fan
ch1_c_out_rtd | Temperature of the water leaving the condenser in Chiller1
ch1_e_in_rtd | Temperature of the PG returning to both Chiller1 and Chiller2
ch1_e_out_rtd | Temperature of the PG leaving the evaporator in Chiller1
ch1_f_c | Flow rate of the water through the condenser in Chiller1
ch1_f_e | Flow rate of the PG through the evaporator in Chiller1
ch1_on | On/off control signal for Chiller1
ch1_power | Power consumption of Chiller1
ch1_t_reset | Control to enable remote temperature setpoint for Chiller1
ch1_t_sp | Remote temperature setpoint for Chiller1
ch2_c_out_rtd | Temperature of the water leaving the condenser in Chiller2
ch2_e_out_rtd | Temperature of the PG leaving the evaporator in Chiller2
ch2_f_c | Flow rate of the water through the condenser in Chiller2
ch2_f_e | Flow rate of the PG through the evaporator in Chiller2
ch2_on | On/off control signal for Chiller2
ch2_power | Power consumption of Chiller2
ch2_t_reset | Control to enable remote temperature setpoint for Chiller2
ch2_t_sp | Remote temperature setpoint for Chiller2
cl_f | Flow rate of water in the condensing loop
cw_in_rtd | Temperature of the chilled water entering the condensing loop
d10_pos_c | Control signal for the position of Damper10
d10_pos_fb | Feedback signal for the position of Damper10
d11_pos_c | Control signal for the position of Damper11
d11_pos_fb | Feedback signal for the position of Damper11
d15_pos_c | Control signal for the position of Damper15
d15_pos_fb | Feedback signal for the position of Damper15
d16_pos_c | Control signal for the position of Damper16
d16_pos_fb | Feedback signal for the position of Damper16
d17_pos_c | Control signal for the position of Damper17
d17_pos_fb | Feedback signal for the position of Damper17
d18_pos_c | Control signal for the position of Damper18
d18_pos_fb | Feedback signal for the position of Damper18
d2_pos_c | Control signal for the position of Damper2
d2_pos_fb | Feedback signal for the position of Damper2
d3_pos_c | Control signal for the position of Damper3
d3_pos_fb | Feedback signal for the position of Damper3
d4_pos_c | Control signal for the position of Damper4
d4_pos_fb | Feedback signal for the position of Damper4
d5_pos_c | Control signal for the position of Damper5
d5_pos_fb | Feedback signal for the position of Damper5
d6_pos_c | Control signal for the position of Damper6
d6_pos_fb | Feedback signal for the position of Damper6
d7_pos_c | Control signal for the position of Damper7
d7_pos_fb | Feedback signal for the position of Damper7
d8_pos_c | Control signal for the position of Damper8
d8_pos_fb | Feedback signal for the position of Damper8
dx_c1 | On/off signal for Compressor1 in the DX system
dx_c1_power | Partial measurement of power consumption of Compressor1 in the DX system
dx_c1_tsc1 | First temperature measurement used to estimate subcool in Compressor1 in the DX system
dx_c1_tsc2 | Second temperature measurement used to estimate subcool in Compressor1 in the DX system
dx_c1_tsh1 | First temperature measurement used to estimate superheat in Compressor1 in the DX system
dx_c1_tsh2 | Second temperature measurement used to estimate superheat in Compressor1 in the DX system
dx_c2 | On/off signal for Compressor2 in the DX system
dx_c2_power | Partial measurement of power consumption of Compressor2 in the DX system
dx_c2_tsc1 | First temperature measurement used to estimate subcool in Compressor2 in the DX system
dx_c2_tsc2 | Second temperature measurement used to estimate subcool in Compressor2 in the DX system
dx_c2_tsh1 | First temperature measurement used to estimate superheat in Compressor2 in the DX system
dx_c2_tsh2 | Second temperature measurement used to estimate superheat in Compressor2 in the DX system
dx_ds_c | Control signal for Compressor1 in the DX system
dx_m_cs | No longer used
dx_m_sclk | No longer used
dx_sp_cs | No longer used
dx_sp_din | No longer used
dx_sp_sclk | No longer used
dx_sp_spi | No longer used
dx_z_cs | No longer used
dx_z_din | No longer used
dx_z_sclk | No longer used
dx_z_spi | No longer used
exf1_f | Airflow rate at ExhaustFan1
exf1_on | On/off control for ExhaustFan1
exf1_p_down | Pressure downstream of ExhaustFan1
exf1_p_up | Pressure upstream of ExhaustFan1
exf1_power | Power consumption of ExhaustFan1
exf1_t_in | Temperature upstream of ExhaustFan1
exf1_vfd | Speed of ExhaustFan1
exf2_f | Airflow rate at ExhaustFan2
exf2_on | On/off control for ExhaustFan2
exf2_p_down | Pressure downstream of ExhaustFan2
exf2_p_up | Pressure upstream of ExhaustFan2
exf2_power | Power consumption of ExhaustFan2
exf2_t_in | Temperature upstream of ExhaustFan2
exf2_vfd | Speed of ExhaustFan2
hw_rtd | Temperature of the hot water entering the lab
hx1_f_hw | Flow rate of the hot water in HeatExchanger1
hx1_f_pg | Flow rate of the PG in HeatExchanger1
hx1_hw_rtd | Temperature of the hot water at the outlet of HeatExchanger1
hx1_pg_rtd | Tempeature of the PG at the outlet of HeatExchanger1
hx2_cw_rtd | Temperature of the chilled water at the outlet of HeatExchanger2
hx2_hw_rtd | Temperature of the hot water at the outlet of HeatExchanger2
hx3_cw_rtd | Temperature of the chilled water at the outlet of HeatExchanger3
hx3_f_cw | Flow rate of the chilled water through HeatExchanger3
hx3_f_pg | Flow rate of the PG through HeatExchanger3
hx3_pg_rtd | Temperature of the PG at the outlet of HeatExchanger3
indoor_p | Measurement of pressure in the IBAL
indoor_rh | Measurement of the relative humidity in the IBAL
indoor_rtd | Measurement of the temperature in the IBAL
mcc_run | On/off signal for the harmonic filter in the MCC
mcc_run_fb | Feedback for the on/off signal for the harmonic filter in the MCC
oau_cc_rtd | Air temperature downstream of the DX cooling coil in the OAU
oau_f_out | Airflow rate exhausting to the outdoors from the OAU
oau_fan_power | Power consumption of the OAU fan
oau_fz_in | Return signal from freezestat
oau_fz_out | Voltage signal to freezestat
oau_heat_c | Control signal for the electric heater in the OAU
oau_heat_power | Partial measurement of power consumption of the electric heater in the OAU
oau_hs_rtd | Temperature of the air just downstream of the electric heater in the OAU
oau_in_rtd | Temperatutre of the air at the inlet of the OAU, after the return and supply air mix
oau_on | On/off control signal for the OAU fan
oau_out_rtd | Temperature at the outlet of the OAU
oau_p_down | Static pressure downstream of the OAU fan
oau_p_up | Static pressure upstream of the OAU fan
oau_rh | Relative humidity at the outlet of the OAU
oau_t_out | Temperature of the air exhausting to the outdoors from the OAU
oau_vfd | Speed of the OAU fan
outdoor_rh | Relative humidity of the outdoor air
outdoor_rtd | Temperature of the outdoor air
pl_f | Flow rate in the primary loop
pl_ftemp | No longer used
pl_in_rtd | Temperautre of the PG entering (returning to) the primary loop
pl_out_rtd | Temperature of the PG leaving the primary loop
pump1_on | On/off control signal for Pump1
pump1_p_down | Pressure downstream of Pump1
pump1_p_up | Pressure upstream of Pump1
pump1_power | Power consumption of Pump1
pump1_vfd | Speed of Pump1
pump2_on | On/off control signal for Pump2
pump2_p_down | Pressure downstream of Pump2
pump2_p_up | Pressure upstream of Pump2
pump2_power | Power consumption of Pump2
pump2_vfd | Speed of Pump2
pump3_dp | Differential pressure across the secondary loop
pump3_on | On/off control signal for Pump3
pump3_out_rtd | Temperature downstream of Pump3
pump3_p_down | Pressure downstream of Pump3
pump3_p_up | Pressure upstream of Pump3
pump3_power | Power consumption of Pump3
pump3_vfd | Speed of Pump3
pump4_on | On/off control signal for Pump4
pump4_out_rtd | Temperature downstream of Pump4
pump4_p_down | Pressure downstream of Pump4
pump4_p_up | Pressure upstream of Pump4
pump4_power | Power consumption of Pump4
pump4_vfd | Speed of Pump4
pump5_on | On/off control signal for Pump5
pump5_p_down | Pressure downstream of Pump5
pump5_p_up | Pressure upstream of Pump5
pump5_power | Power consumption of Pump5
pump5_vfd | Speed of Pump5
sl_f | Flow rate in the secondary loop
sl_ftemp | No longer used
sl_out_rtd | Temperature at the outlet of the secondary loop
timer | No longer used
tmc1_in_rtd | Temperature of the water entering the Thermal Mass Coil 1
tmc1_out_rtd | Temperature of the water leaving Thermal Mass Coil 1
tmc1_pos_c | Position of the throttling valve in Thermal Mass Coil 1
tmc1_pump_on | On/off control signal for the pump in Thermal Mass Coil 1
tmc2_in_rtd | Temperature of the water entering the Thermal Mass Coil 2
tmc2_out_rtd | Temperature of the water leaving Thermal Mass Coil 2
tmc2_pos_c | Position of the throttling valve in Thermal Mass Coil 2
tmc2_pump_on | On/off control signal for the pump in Thermal Mass Coil 2
tmc3_in_rtd | Temperature of the water entering the Thermal Mass Coil 3
tmc3_out_rtd | Temperature of the water leaving Thermal Mass Coil 3
tmc3_pos_c | Position of the throttling valve in Thermal Mass Coil 3
tmc3_pump_on | On/off control signal for the pump in Thermal Mass Coil 3
tmc4_in_rtd | Temperature of the water entering the Thermal Mass Coil 4
tmc4_out_rtd | Temperature of the water leaving Thermal Mass Coil 4
tmc4_pos_c | Position of the throttling valve in Thermal Mass Coil 4
tmc4_pump_on | On/off control signal for the pump in Thermal Mass Coil 4
ts_f | Flow rate through the thermal storage tank
ts_in_rtd | Temperature of the PG entering the thermal storage tank
ts_meter | Ice meter reading of the inventory in the thermal storage tank
ts_out_rtd | Temperature of the PG leaving the thermal storage tank
v1_pos_c | Control signal for the position of Valve1
v1_pos_fb | Feedback signal for the position of Valve1
v10_pos_c | Control signal for the position of Valve10
v10_pos_fb | Feedback signal for the position of Valve10
v11_pos_c | Control signal for the position of Valve11
v11_pos_fb | Feedback signal for the position of Valve11
v12_pos_c | Control signal for the position of Valve12
v12_pos_fb | Feedback signal for the position of Valve12
v13_pos_c | Control signal for the position of Valve13
v13_pos_fb | Feedback signal for the position of Valve13
v14_pos_c | Control signal for the position of Valve14
v14_pos_fb | Feedback signal for the position of Valve14
v15_pos_c | Control signal for the position of Valve15
v15_pos_fb | Feedback signal for the position of Valve15
v16_pos_c | Control signal for the position of Valve16
v16_pos_fb | Feedback signal for the position of Valve16
v17_pos_c | Control signal for the position of Valve17
v17_pos_fb | Feedback signal for the position of Valve17
v18_pos_c | Control signal for the position of Valve18
v18_pos_fb | Feedback signal for the position of Valve18
v19_pos_c | Control signal for the position of Valve19
v19_pos_fb | Feedback signal for the position of Valve19
v2_pos_c | Control signal for the position of Valve2
v2_pos_fb | Feedback signal for the position of Valve2
v20_pos_c | Control signal for the position of Valve20
v20_pos_fb | Feedback signal for the position of Valve20
v3_pos_c | Control signal for the position of Valve3
v3_pos_fb | Feedback signal for the position of Valve3
v4_pos_c | Control signal for the position of Valve4
v4_pos_fb | Feedback signal for the position of Valve4
v5_pos_c | Control signal for the position of Valve5
v5_pos_fb | Feedback signal for the position of Valve5
v6_pos_c | Control signal for the position of Valve6
v6_pos_fb | Feedback signal for the position of Valve6
v7_pos_c | Control signal for the position of Valve7
v7_pos_fb | Feedback signal for the position of Valve7
v8_pos_c | Control signal for the position of Valve8
v8_pos_fb | Feedback signal for the position of Valve8
v9_pos_c | Control signal for the position of Valve9
v9_pos_fb | Feedback signal for the position of Valve9
vav1_f | Airflow rate through VAV1
vav1_heat_c | Control signal for the electric reheat in VAV1
vav1_heat_power | Power consumption of the electric reheat in VAV1
vav1_out_rtd | Temperature of the air downstream of VAV1
vav1_t_in | Temperature of the air upstream of VAV1
vav2_f | Airflow rate through VAV2
vav2_heat_c | Control signal for the electric reheat in VAV2
vav2_heat_power | Power consumption of the electric reheat in VAV2
vav2_out_rtd | Temperature of the air downstream of VAV2
vav2_t_in | Temperature of the air upstream of VAV2
vav3_f | Airflow rate through VAV3
vav3_heat_c | Control signal for the electric reheat in VAV3
vav3_heat_power | Power consumption of the electric reheat in VAV3
vav3_out_rtd | Temperature of the air downstream of VAV3
vav3_t_in | Temperature of the air upstream of VAV3
vav4_f | Airflow rate through VAV4
vav4_heat_c | Control signal for the electric reheat in VAV4
vav4_heat_power | Power consumption of the electric reheat in VAV4
vav4_out_rtd | Temperature of the air downstream of VAV4
vav4_t_in | Temperature of the air upstream of VAV4
vch1_pos_fb | No longer used
vch2_pos_fb | No longer used
vsh_in | Return signal for the shutoff valves for the chilled and hot water
vsh_out | Control signal for the shutoff valves for the chilled and hot water
zs1_heat_c | Control signal for the electric heater in ZS1
zs1_heat_power | Power consumption of the electric heater in ZS1
zs1_heat_rtd | Temperature of the air downstream of the electric heater in ZS1
zs1_out_rtd | Temperature of the air downstream of ZS1 (zone temperature)
zs1_rh | Relative humidity of the air downstream of ZS1 (zone relative humidity)
zs2_heat_c | Control signal for the electric heater in ZS2
zs2_heat_power | Power consumption of the electric heater in ZS2
zs2_heat_rtd | Temperature of the air downstream of the electric heater in ZS2
zs2_out_rtd | Temperature of the air downstream of ZS2 (zone temperature)
zs2_rh | Relative humidity of the air downstream of ZS2 (zone relative humidity)
zs3_heat_c | Control signal for the electric heater in ZS3
zs3_heat_power | Power consumption of the electric heater in ZS3
zs3_heat_rtd | Temperature of the air downstream of the electric heater in ZS3
zs3_out_rtd | Temperature of the air downstream of ZS3 (zone temperature)
zs3_rh | Relative humidity of the air downstream of ZS3 (zone relative humidity)
zs4_heat_c | Control signal for the electric heater in ZS4
zs4_heat_power | Power consumption of the electric heater in ZS4
zs4_heat_rtd | Temperature of the air downstream of the electric heater in ZS4
zs4_out_rtd | Temperature of the air downstream of ZS4 (zone temperature)
zs4_rh | Relative humidity of the air downstream of ZS4 (zone relative humidity)