| # Last updated April 2004 | # Surge Protection Anthology Part 6 -- Tutorials, Textbooks, and Reviews Text of “Protective Devices” files | # Surges Happen! |
| --- | --- | --- |

FOREWORD

This file contains the text part from seven papers on the following subjects:

- Metal oxide varistor: A new way to suppress transients (1979)

- Transient overvoltage protection: The implications of new techniques (1981)

- Lightning and NEMP transient protection with metal oxide varistors (1982)

- Surge suppressors and clamps (1988)

- A glimpse at long-term effects of momentary overvoltages on ZnO varistors (1989)

- What are the lights on your surge protector telling you ? (1998)

- Lingering lead length legacies (2004)

This file is formatted as MS Word, allowing you to do a search for keywords, but it does not support graphics as it was derived from an OCR scan of hard-copy archives.  However, should you wish to examine the complete original format, each page in this file has an identifying header and footer that contain a hyperlink to the pdf file for the document being displayed on that page, regardless of the font size that you select for optimum viewing.  These headers and footers and hyperlinks become accessible when you select the “Print Layout” in the “View” mode.

Best wishes and good browsing !

Metal-oxide varistor:

a new way to suppress transients

by J.D. Harnden and F.D. Martzloff, Corporate Research and Development, General Electric Co.

and W.G. Morris and F.B. Golden,  Semiconductor Products Department, General Electric Co.

Although it belongs to the established family of reliable varistor protection devices, the recently introduced metal-oxide type of varistor is adding a new dimension to the technology of protecting circuits and components.  Trademarked as the GE-MOV and MOV varistor by General Electric Co., the metal-oxide-type varistor offers the advantages of nanosecond switching speeds and small size, while being able to handle current surges on the order of hundreds of amperes.

Like other varistor transient suppressors, the new varistor has a nonlinear voltage-current characteristic that makes it useful in voltage-regulation applications.  And because its nonlinear V-I curve is very steep-steeper than that of most other varistors-it can pass widely varying currents over a narrow voltage range.  In some applications, using the device allows a circuit to be redesigned with fewer components.

At low applied voltages, the metal-oxide-type varistor looks like an open circuit because its unique two-phase material assumes the properties of an insulator.  When applied voltage exceeds rated clamping voltage, the device effectively becomes a short circuit, protecting the component that it shunts.

The unit, moreover, requires very little standby power, making it useful for guarding semiconductors.  Steady-state power dissipation is typically a fraction of a milliwatt, as compared to the hundreds of watts dissipated by some other varistor devices.

At present, operating voltage ratings for MOV-brand series VP varistors range from 140 to 1,400 volts peak, watt-second ratings from 10 to 160 joules, and continuous power ratings range from 0.5 watt to 1.3 watt. Units are priced from less than $1 to $14 in 1,000-unit lots.

# An Inside look

The metal-oxide-type varistor (Fig. 1) has an encapsulated polycrystalline ceramic body, with metal contacts and wire leads.  Zinc oxide and bismuth oxide, the essential ingredients, are mixed with proprietary powdered additives, and then pressed into disks and sintered at a temperature greater than 1,200oC.

Because the bismuth oxide is molten above 825oC, it assists in the formation of a dense polycrystalline ceramic through liquid-phase sintering.  During cooling, the liquid phase forms a rigid amorphous coating around each zinc oxide grain, yielding a microstructure of zinc oxide grains that are isolated from each other by a thin continuous intergranular phase. It is this complex two-phase microstructure that is responsible for the nonlinear characteristics.

The voltage across a metal-oxide-type varistor and the current through it are related by the power law, I=kVn, where k is a constant. Exponent n, which is also referred to as alpha (), typically has a value between 25 and 50 or more, leading to the idealized V-I curve of Fig. 1. Over a wide current range, the voltage remains within a narrow band that is commonly called the varistor voltage.

Many properties of the varistor can be directly related to the microstructure and the properties of the two phases.  As shown in Fig. 1, the unit's idealized V-I curve consists of two linear segments for extremely low and extremely high currents, and a nonlinear segment in the varistor voltage range.

At low applied voltages, the device's linear characteristic can be attributed primarily to leakage current through the intergranular phase.  Device behavior is roughly that of an insulator, indicating that low applied voltages cause a high electric field across the intergranular phase and a low field within the zinc oxide grains.

In the varistor voltage range, the intergranular phase becomes nonlinear, and current through it increases rapidly as the voltage is raised slowly.  The conduction mechanism that affects the nonlinear characteristic is now under investigation and is thought to be space-charge-limiting or tunneling phenomena.  For extremely high currents, the resistance of the intergranular layer becomes less than that of the zinc oxide grains, causing the V-I curve to tend towards linearity again.

# Comparing transient suppressors

A comparison of the volt-ampere characteristic of the metal-oxide-type varistor to that of other voltage suppressors yields the graph shown in Fig. 2. A number of varistor devices are represented, including silicon, selenium, silicon-carbide, and metal-oxide types.  A point-of-reference curve for a linear ohmic resistor is also shown.  The higher a device's alpha is, the better is its voltage suppression capability.

The parameters of some of the most widely used transient voltage suppressors are summarized in the table of Fig. 2. (The commercial voltage ratings reflect peak values; they must be divided by 1.41 to obtain root-mean-square values.) It should be noted that selenium suppressors are normally supplied as a single package of several series-connected plates, so that the selenium voltage rating is not that of a single plate.  The other varistor data, however, reflects single-unit ratings.

Metal-oxide-type varistors can also be connected in series to increase clamping-voltage rating.  Moreover, they can serve in a structural mode as well as an electrical one, for instance, by replacing the spacer between switch contacts to allow approaching arcless switching commutation, especially in dc applications.

One of the most important considerations when choosing a protection device is its steady-state power dissipation.  In the case of varistors, the higher the alpha or exponent, the lower will be the standby loss.  For example, if a varistor is shunted across a load, protecting it at a 300-V level in the presence of a 2,000-V transient with a surge impedance of 10 ohms, a steady-state power dissipation is required of the varistor, since it is connected continuously to the 117-V rms line.  For the silicon-carbide varistor, which has a typical alpha of 3, the necessary steady-state dissipation will be 660 watts. On the other hand, a metal-oxide-type varistor with an exponent of 30 will dissipate only 0.1 milliwatt.

Suppressor comparison

V-I curves of various varistor transient suppressors and linear ohmic resistor show that characteristic for metal-oxide-type varistor is nearly horizontal because of its high alpha () value. (All varistors obey power law, I = kV) Table compares some key specifications for several popular surge protectors.  Shortly, clamping-voltage range will be broader for 9 MOV varistors.

# Examining device behavior

Fig. 3a shows the simplified equivalent circuit for the metal-oxide-type varistor, as well as its schematic symbol; representative capacitance and resistance values are used.  The low-current-level resistance, R-off, is due primarily to the resistivity of the intergranular phase.  Capacitance C can be attributed to the very thin dielectric of the intergranular phase; it becomes a fairly significant factor for the varistor's dynamic characteristic.  The high-current-level resistance, R-on, is due to the intrinsic resistivity of the zinc oxide grains; it represents the unit's limiting resistance.  The component values in the figure are for a typical MOV-brand series VP device.

As indicated in Fig. 3b, the device's V-I curve ordinarily exhibits a slightly negative voltage temperature coefficient, in the order of 0.0 1 % /oC to 0.05 % /oC for the series VP varistors.  At very low current levels, this coefficient is substantially larger but does not affect the normal operating range.  Maximum steady-state power dissipation for a disk with 3 square centimeters of total surface area is usually 1 watt in a 70oC free-convection ambient environment.

Typical capacitance curves are depicted in Fig. 3c for units with differing diameters.  Device capacitance influences high-frequency impedance properties, as shown by the plots of Fig. 3d for two production units--one with a 130-V rms rating, and the other with a 1,000-V rms rating.  A point-of-reference curve for a fixed 0.005-microfarad capacitor is also included.

When a fast-rising surge is applied to a metal-oxide-type varistor, its capacitance immediately makes it appear as a low impedance.  After the capacitance becomes fully charged, the unit simply operates at the point predicted by its V-I characteristic.

# Tracing the origin of transients

Transient surges originate from a variety of sources.  Regardless of whether electrical circuits operate from ac or dc sources, they are often plagued by voltage transients that are either generated within the circuit itself or transmitted into the circuit from external sources.

One of the most common sources of transients in power distribution systems is the L(di/dt) voltage caused by transformer magnetizing currents as the transformers are switched within either a feeder utility system or an industrial plant's own distribution system.  Residual lightning surges are another source of concern.  These surges can be thought of as an overflow on the main lightning arrestors with which most consumer, commercial, and industrial distribution systems are protected at the interface between the utility and the user's distribution systems.  Still other sources can be found in homes themselves, resulting from equipment that is connected to the utility system.

Even a small synchronous line clock in the home can be subjected to a number of surges within just a 24-hour period.  In fact, with the introduction of more automatic switching functions and complex electrical equipment into the home, line surges are becoming more frequent.  And oddly, the better and newer the wiring and installation, the less inherent protection is provided by spill-over occurring in poorly wired outlets, switches, and fixtures, and the greater the resulting impressed voltage level on connected equipment.

# Using metal-oxide-type varistors

When a step-down transformer is switched on, it can impress severe transients on any components connected to its secondary winding due to its interwinding capacitance.  Installing a metal-oxide-type varistor, as shown in Fig. 4a, can eliminate this startup transient.

Another source of component failure, which is sometimes overlooked, can occur in the conventional transistor series-pass voltage regulator (Fig. 4b).  When the circuit is turned on, the capacitor appears to be a short circuit, and the transistor is exposed to the full unregulated bus voltage.  Placing a metal-oxide-type varistor across the transistor allows a soft current rise to pass through the regulator without the usual voltage surge.

Semiconductors can be protected with the new varistor, resulting in a design with fewer components, because the device can improve the electrical properties of the circuit in which it is installed.  As an example, consider the output stage of small fine-operated radio (Fig. 4c) that requires high-voltage transistors and an associated RC network to withstand the voltage spikes generated by distortion during overload.

The oscilloscope traces of transistor stress show the voltage transient that occurs with normal RC suppression but is dramatically reduced with varistor suppression.  Because of this significant transient reduction, the circuit can be redesigned with fewer parts. (The third scope trace displays varistor current.)

# Choosing the right varistor

Selecting the correct metal-oxide-type varistor is a simple, logical procedure.  First, find the device with a peak operating voltage rating that is close to, yet higher than, the normal peak ac-line voltage.  Next, determine or estimate the energy level of the transient to be suppressed.  This energy level is usually determined by the energy term, LI2/2, where I is the peak magnetizing current flowing in inductance L, which stores the transient energy in its field.  In the case of transformers, I may be considered the peak exciting current.

The expected transient current level must be found next. (Peak feeder transformer magnetizing current, reflected to the secondary, is often used to estimate the peak transient current.) Then, the varistor unit can be selected that has the proper ratings for recurrent voltage, clamping voltage, and energy level.

In the case of dc applications, varistor steady-state power dissipation should be checked.  Be sure to derate the device's energy rating if power dissipation demands will elevate the varistor case temperature above 85 oC.  For applications where repetitive transients may be encountered, calculate the expected watt-seconds per pulse and multiply this figure by the pulse repetition rate to determine the additional steady-state power dissipation required.  And finally, make certain that the unit can comply with such ambient environmental factors as operating and storage temperatures.

# Looking ahead

The next major developments for MOV-brand varistors will revolve around package changes to enhance applications versatility and improve heat transfer.  Future packages will be available in a variety of mounting schemes-for example, a bolt-down version with or one without heat-transfer capability that could be directly fastened to chassis, brackets, bus bars, and heat exchangers.  Low-inductance pill-shaped packages that are compatible with pressure-mounted thyristors are also being considered.  Another possibility is a finned package for direct air convection and forced cooling.

Since metal-oxide-type varistors can be made rather thick, they should be available in the near future with kilovolt ratings.  MOV-brand series VP units are currently being developed to cover the clamping voltage range of  30 V to 10 kV.

# BIBLIOGRAPHY

R. A. Delaney and H. D. Kaiser, Journal of Electrochemical Society, Solid State Sciences, Vol. 114, pp. 883-842,1967.

M. Matsuoka, T. Masyama, and Y. Iida, Supplementary Journal of Japanese Society of Applied Physics, Vol. 39, 94-101, 1970.

M. Matsuoka, Japanese Journal of Applied Physics, Vol. 10, 736-746, 1971.

W. G. Morris, “The Electrical Properties of ZnO-Bi2O3 Ceramics,” General Electric Co., Corporate Research and Development Report 72CRD069.

F. B. Golden, R. W. Fox, “GE-MOV Varistor Voltage Transient Suppressors,” General Electric Co., Semiconductor Products Dept., Application Note 200.60.

F. B. Golden, “A New Voltage Transient Suppressor,” IEEE International Semiconductor Power Converter Conference Record, Publication 72CHO 602-3-1 A, pp. 2-6-1 to 2-6-9.

Transient Overvoltage Protection:

The Implications of New Techniques

François D. Martzloff

Corporate Research and Development

General Electric Company

# Summary

Reliability problems can occur from the use of modern electronic devices without applying appropriate protection techniques or using incorrect installation procedures.  Although surge arresters are effective in limiting overvoltages, a metal oxide varistor can provide a much lower clamping voltage if installation procedures are taken into consideration.  Sparkover voltage measurements, with a specified time rise, measured arrester performance.  The response of the arresters to a current impulse was investigated and lead effects were identified.  Tests indicated that the metal oxide varistor, installed with short leads, provides low clamping voltage.

# Introduction

Incorrect protection for modern electronic devices from lightning strokes can cause reliability problems which could arise from various sources:

·	Sensitivity of modern electronic equipment

·	Improper procedures of installation

·	Complete lack of protective devices.

This paper examines new applications of old concepts which are required by the constantly increasing use of electronic equipment; the particular increased sensitivity of these devices; and intense, competitive pressures.  We shall consider first the design and environment of surge arresters for low-voltage systems and then examine their performance as a function of installation.

# Surge arrester design for low voltage systems

In the past, typical surge arresters (diverters) for service entrance duty have been limited to a gap-varistor design.  This design involves gap sparkover voltage with a result of a relatively high clamping voltage for the arresters.  The new, commercial availability of metal oxide varistors, with current ratings suitable for service entrance duty, provides a low clamping voltage at the service entrance.

Surge arresters, which have sufficient current discharge capacity, consist of a gap in series with a non-linear resistor, usually a silicon carbide block (Figures 1, 2, and 3).  These arresters are effective in limiting overvoltages to levels compatible with solid insulation.    In recognition of this compatibility, the IEC Report 664 [1] proposes voltage levels of 2500 V for a 120 V circuit and 4000 V for a 220 V circuit (Table 1).  However, these voltages are not consistent with the inherent withstand characteristics of electronic appliances.  A much lower level (indicated by Category I or II of the 664 report) is required, i.e., 800 or 1500 V for 120 V circuits and 1500 or 2500 V for 220 V circuits.  These voltages can be achieved with a 32 mm metal oxide varistor for which the rated clamping voltage is 550 V and 900 V for disks suitable for 120 V and 220 V circuits, respectively.

However, the capability for low clamping voltage might not be attained if installation procedures do not take the connecting lead effects into consideration.  Furthermore the proposed IEC practice of several cascaded surge protective devices requires careful coordination of the devices and the intermediate impedance [2], a goal which may not be easy to achieve in routine installation practices.

Table I

Preferred series of values of impulse withstand voltages

for rated voltages based on a controlled voltage situation

## Test procedures and standards

The  evaluation  of  surge  arrester  performance   is accomplished by the  application  of  standardized  tests which are presumably specific to the operational environment of the arrester.

Performance tests for a low-voltage arrester include sparkover voltage measurement with a specified rise time and also the use of one or more current impulses to demonstrate the capability of discharging a surge either without damage or without the production of excessive discharge voltage during the surge.  Figure 4 shows the relationship between these parameters of a gap-varistor design.  Because damage to semiconductors is likely to occur during the initial front of the surge before sparkover, the concern over the following discharge voltage is less significant.

Figure 5, however, shows how the gapless varistor can clamp at lower voltages.  But, there is a risk of an inductive drop which would add a substantial voltage to the intrinsic clamping voltage due to the long connecting leads required under some proposed regulations [3].

# Sparkover voltage

Figure 6 shows the sparkover voltage of typical arresters in USA circuits at 120 V line-to-ground and, also, in European circuits at 220 or 440 V between terminals.  These sparkover voltages were recorded for a 10 kV/s rate of rise (Figure 6a).  It is apparent that the gap-type arrester oscillograms exhibit an anomaly at approximately 150 /uus before the gap sparks over (Figure 6b, c, d).*

In contrast, the clamping voltage of the varistor (Figures 7a and b) is not only lower, but it is also free from any interference.  In Figure 7c, the absence of a significant overshoot in varistor clamping is shown:

·	The fast front is the open circuit voltage without the varistor

·	The trace to the right illustrates the clamping action of the varistor.

## Impulse current

The selection of the current waveform is not obvious.  The use of an 8/20 s waveform to represent surge currents associated with lightning strokes is well established.  Indeed, most standards [4,5] call for an 8/20 s waveform.  Levels may be in the range of 3 to 10 kA crest at the service entrance (Table 2) [4].

The selection of an 8/20 s wave reflects our present day knowledge of typical lightning currents [6,71.  In addition, the 8/20 s wave discharges an appropriate amount of energy in the arrester under test.

The question, then, of the likelihood of a 8 s front propagating along a low voltage system can be raised.  Figure 8 depicts a possible distribution of the surge current from a stroke to an overhead system.  Taking 50 kA [8] as the median level of lightning stroke, the resultant 5 kA crest is expected, and, with short distances along the service drop, a rise time of 8 s can be maintained.

The explanation of this peculiarity is actually quite simple.  In real time, the gap fires 150 s before the display records the event, but the oscilloscope used for these tests has a 150 s delay line.  Therefore, the anomaly is the interference created in the oscilloscope by the gap. (Even an EMI option for the oscilloscope is not enough!) This occurrence exemplifies the objectionable effects that a gap can have upon electronic devices.

Table 2

Surge voltages and currents deemed to represent the indoor and outdoor environment

and recommended for use in designing protective systems

Within these parameters, an 8/20 s waveform for both the conventional arresters and the candidate metal oxide varistors in service entrance duty appears reasonable.  In addition, it is likely to be demanded in the performance of test procedures for arresters - either by customers or by regulatory agencies.

### Installation of arresters in panels

Two panels, typical of USA and European hardware (Figures 9 and 10), were wired in the laboratory and subjected to impinging surges of 5 kA crest, 8/20 s (Figure 1la), that were applied between one phase line and the panel ground.  Voltages appearing at the out-going branch circuits were recorded with oscilloscope probes by using a differential connection after preliminary checking on signal/noise performance of the system.  Figure 1lb shows the response of the 120 V arrester to this impinging surge.  This response will be discussed in detail with the test results.

On the USA-type panel, the 120 V arrester was installed externally to the panel, and the 45 cm long leads were connected to the main entrance lugs of the panel (as implied by the specifications of the National Electrical Code and the proposed UL Document [31).  The 220 V arrester is designed for installation in the panel, and the point-to-point wiring allows short leads for the connection across line and ground (or neutral) inside the panel.  The 440 V arrester, as indicated by the manufacturer's suggested installation (Figure 12), is intended to be connected outside at the service entrance rather than at the panel.  Consequently, in the laboratory simulation, it was connected 3 m before the panel.

The 150 V and 250 V varistors (Figure 13) were installed either outside or inside the panel.  The installation will be discussed with the test results.

## Test results on discharge voltage

All discharge voltage measurements were made with the surge generator set for the standard 5 kA crest, 8/20 s current impulse shown in Figure 11a.  The clamping voltage of each device and the impedance of its connections may reduce the current to some extent (the charging voltage of the generator was 12 kV), but the same effect would take place under the assumption of a current division resulting from the ratio of the impedances offered to the impinging stroke of 50 kA.

Figure 11b shows the discharge voltage of the 120 V arrester which reflects the applied current wave of Figure 11.  In view of the expectation raised by the low-clamping voltage of the metal oxide varistors, the discharge voltage of the 150 V varistor recorded in Figure 14a seems disappointing.  This can be explained easily.  The clamping voltage of the varistor is degraded by the addition of the voltage due to the 45 cm leads (Figure 14b).  Setting aside the proposed installation requirements and seeking optimum performance, the short connections of Figure 15 produce the remarkably low discharge voltage shown in Figure 16a.  For the 220/380 V panel (Figure 10), the layout of components and the absence of conflicting specifications, that is, the promoting of short leads in the standards [9,10], makes possible the equally remarkable low-clamping voltage of the 250 V varistor shown in Figure 16b.

In contrast, the discharge voltages of conventional arresters are higher and contain some high frequency oscillations which may be troublesome.  Granted that the voltages are clamped to levels which eliminate the hazards of flashover in the wiring.  That is an accomplishment already.  But these still relatively high discharge voltages may not be low enough to ensure the survival of electronics connected directly to the mains protected by these arresters.

Figure 17 shows the response of the integral arrester in the 220/380 V panel.  The short connections made possible by this arrangement eliminate the problem of added voltage drop.  The initial response (17a) of the gap sparkover is well balanced with the discharge voltage during the full impulse (17b).  There is, however, the  problem of unavoidable collapse of voltage following sparkover, with a possible result of producing interference in connected electronics as well as direct radiation. (See footnote under Sparkover voltage.)

Figure 18 shows the response of the arrester installed at the service entrance.  The initial response (Figure 18a) indicates that the additional leads inductance and capacitance can produce peculiar resonances.  Nevertheless, the complete impulse discharge (18b) is well balanced with the initial response although the initial collapse reaches the full amplitude during sparkover.

# Conclusion

Present technology offers two choices for the protection  of low-voltage circuits against atmospheric overvoltages:

·	 Conventional arresters

·	 Metal oxide varistors.

Although conventional arresters provide protection against the hazards of wiring flashover, they can still allow voltages damaging or disturbing sensitive electronics.  Metal oxide varistors, although not yet packaged in a manner convenient for panel installation, not only produce low clamping voltages but they also produce no high frequency disturbances.  These benefits, however, will be obtainable only if proper installation procedures are followed.

# Acknowledgments

The assistance of Eric Carroll (GETSCO, Paris) and Louis Regez (Landis & Gyr, Zug) in identifying practices and procuring components, and of Alma Bongarten, Editor, is gratefully acknowledged.

# References

1.	 Insulation coordination within low-voltage systems including clearances and creepage distances for equip-ent.  International Electrotechnical Commission Report 6640.  Geneva, Switzerland 1980

2.	Martzloff, F.D.: "Coordination of surge protectors in low-voltage ac power circuits." IEEE Transactions on Power Apparatus and Systems.  Vol.  PAS-99 No. 1, January/February 1980.

3.	Proposed UL Standard 1449 for low-voltage transient suppressors

4.	Guide for application of valve-type lightning arresters .for alternative-current systems.  ANSI         Standard C62.2

5.	Guide on surge voltages in low voltage ac power circuits.  IEEE Standard to be published in 1981

6.	Cianos N. and Pierce E.T.: A ground lightning environment for engineering usage.  Stanford Research Institute Technical Report.  August 1972

7.	Golde, R.H., ed: Lightning, 2 vols., Academic Press.  London and New York 1977

8.	Johnson, I.B.: Surge protection in power  systems.  IEEE Tutorial Course.  IEEE Power Engineering Society. 79EHO144-6-PWR, 1978

9.	Installations électriques à basse tension.  French Standard NF C15-100

10.	Leitsaetze fur den Schutz elektrischer Anlagen gegen Überspannungen.  German Standard VDE 0675

LIGHTNING AND NEMP TRANSIENT PROTECTION

WITH METAL OXIDE VARISTORS

François D. Martzloff

General Electric Company

# FUNDAMENTALS ON VARISTORS

The term varistor is derived from its function as a variable resistor.   It is also called a voltage-dependent resistor, but that description misleadingly implies that the voltage is the independent parameter in surge protection.  Two very different devices have been successfully developed as varistors: silicon carbide discs have been used for years in the surge arrester industry, and, more recently, metal oxide varistor technology has come of age.

## Structure and Packaging

Composition of the varistor consists primarily of zinc oxide with small additions of selected metal oxides.  These materials are sintered at high temperature to produce a polycrystalline ceramic body.  The structure of the body is a matrix of conductive zinc oxide grains separated by a highly resistive intergranular boundary (Figure 1).

Figure 1. Photomicrograph of a polished and etched section of a metal oxide varistor.

Since electrical conduction occurs between zinc oxide grains distributed throughout the bulk of the device, a varistor is inherently more rugged than its single junction counterparts, such as zener diodes.  In the varistor, energy is absorbed throughout the body of the device with the resultant heat spread evenly through its volume.  Electrical properties are controlled mainly by the physical dimensions of the varistor body, which is generally sintered in the shape of a disc.  Energy rating is determined by volume, voltage rating by thickness, and current capability by area.

In conventional applications, a varistor device consists of a disc of the material, with electrodes applied by silk screen, metal spray, etc., to opposite, parallel faces.  A connection is made to the electrodes for feeding current in and out of the varistor by attachment of the device leads to the disc, and thence to the circuit.  The attachment can take many forms (Figure 2),(1) but all involve the insertion of some lead length, a potential problem that will be discussed later.

## Electrical Parameters

Varistor V-I Characteristics

Varistor electrical characteristics are conveniently displayed using a log-log format in order to show the wide range of the V-I curve.  The log format is also clearer than a linear representation which tends to exaggerate the nonlinearity in proportion to the current scale chosen.  A typical V-I characteristic curve is shown in Figure 3. In order to illustrate three distinct regions of electrical operation, this plot shows a wider range of current than is normally provided on varistor data sheets.

In the leakage region (Figure 3), the predominant parameter is the R_off resistance (Figure 4), shown as the 109 ohm line in the figure.  As the current density increases, normal varistor operation occurs, with R_x being the predominant parameter.  Finally, in the upturn region, where R_x has become very small compared to R_on, the latter dominates.  Two other parameters, the capacitance C (reflecting a high effective dielectric constant of the material) and the lead inductance at high frequencies.

The leakage region is of little interest to the user; in the normal operating region, the flatness of the characteristic is a criterion of clamping effectiveness.  Departure from this flat characteristic in the upturn region could be viewed as undesirable, however, this upturn is useful in providing current sharing across the section of the device at high currents.

The capacitance may be objectionable at high frequencies.  Adding a low capacitance avalanche diode in series is a method of reducing the effective capacitance.  The unconventional examples described in the next section also show means of reducing capacitive effects.

The lead inductance, already mentioned, will be discussed at greater length in the following subsections.

The V-I characteristic, then, is the basic application design tool for selecting a device to perform a protective function.  For a successful application, however, other factors, which are discussed in detail in the information available from manufacturers, must also be taken into consideration.  Some of these factors are:

·	Selection of the appropriate nominal voltage for the line voltage of the application

·	Selection of energy-handling capability (including source impedance of the transient, waveshape, and number of occurrences)

·	Heat dissipation

·	Proper installation in the circuit (configuration, lead length)

"Overshoot" - A Lead Effect

Enough instances of poor installation practices have been observed, and enough questions have been raised on alleged "overshoot," that a brief discussion of lead effects is in order.(2) To illustrate the effect of lead length on the overshoot, two measurement arrangements were used.  As shown in Figures 5a and 5b, respectively, 0.5 cm2 and 22 cm2  of area were enclosed by the leads of the varistor and of the voltage probe.

The corresponding voltage measurements are shown in the oscillograms of Figures 6a and 6b.  With a slow current front of 8 s, there is little difference in the voltages occurring with a small or large loop area, even with a peak current of 2.7 kA.

With the steep front of 0.5 s, the peak voltage recorded with the large loop is nearly twice the voltage of the small loop.  Note (Figure 6b) that at the current peak, L di/dt = 0, and the two voltage readings are equal; before the peak, L di/dt is positive, and after, it is negative.

Hence, when one is making measurements as well as when one is designing a circuit for a protection scheme, it is essential to be alert to the effects of lead length (or, more accurately, of loop area) for connecting the varistors.  This warning is especially important when the currents are in excess of a few amperes with rise times of less than one microsecond.

## Speed of Response

The varistor action depends upon a conduction mechanism similar to that of other semiconductor devices.  For this reason, conduction occurs very rapidly, with no time lag apparent, even into the nanosecond range.  Figure 7 shows a composite photograph of two voltage traces with and without a varistor inserted in a very low inductance impulse generator.(3) The second trace (which is not synchronized with the first, but merely superimposed on the oscilloscope screen) shows that the voltage clamping effect of the varistor occurs in less than one nanosecond.

In the conventional lead-mounted devices, the inductance of the leads would completely mask the fast action of the varistor.  Therefore, the test circuit for Figure 7 required insertion of a small piece of varistor material in a coaxial line to demonstrate the intrinsic varistor response.

Tests made on lead-mounted devices, even with careful attention to minimizing lead length, show that the voltages induced in the loop formed by the leads contribute a substantial part of the voltage appearing across the terminals of a varistor at high current and fast current rise.  In typical power applications where the threat is lightning or switching surges, the impressed current rise time is seldom short enough for this effect to become significant.   Competitive technology will make claims that an "overshoot" occurs, but that has been shown to be primarily a lead effect as discussed in the preceding subsection.

Voltage rate-of-rise is not the best term to use when discussing the response of a varistor to a fast impulse, unlike spark gaps where a finite time is involved in switching from a non-conducting to a conducting state.  The response of the varistor to the transient current delivered by a circuit is the appropriate characteristic to consider.

Applications involving NEMP protection will be fast-rising voltages and current surges, so that the packaging will become very significant, and a departure will be required from the conventional packages currently found in commercial devices.  In the next section, these unconventional applications will be briefly presented.

## Failure Modes

An electrical component is subject to failure either because its capability was exceeded by the applied stress or because some latent defect in the component went by unnoticed in the quality control processes.  While this situation is well recognized for ordinary components, a surge protective device, which is no exception to these limitations, tends to be expected to perform miracles, or to at least fail graciously in a  "fail-safe"  mode.  The  term  "fail to different  users  and,  therefore,  should  not  be used.  To some users, fail-safe  means  that  the  protected hardware must never  be  exposed  to  an  over-voltage, so that failure of the protective device must be in the fail-short mode, even if it puts the system out of operation.  To other users, fail-safe means that the function must be maintained, even if the hardware is left temporarily unprotected, so that failure of the protective device must be in the open-circuit mode.  It is more accurate and less misleading to describe failure modes as "fail-short" or "fail-open," as the case may be.(4)

Metal oxide varistors, when subjected to excessive energy (high surge current), will fail in the "fail-short" mode.  If the varistor is connected to a power system with large short-circuit capability, the fault current may produce melting of a soldered safe,"  however,  may  mean  different  failure  modes connection or shattering of the ceramic, ultimately producing a "fail-open" condition.

UNCONVENTIONAL APPLICATIONS

For the protection of fast rise transients occurring with NEMP, it is apparent that lead-mounted devices are likely to be unsatisfactory.  To still benefit from the inherent advantages of metal oxide varistors, novel packaging is required.  In this section, several examples are given: bulkhead connectors and coaxial connectors, each with conventional sintered blocks or with reconstituted material.  Both have been shown to be feasible, although the complete details have not yet been fully developed.

Two further applications are also described, which are still in the conceptual stage, but show promise of useful application in the integrated protection of circuits: as thick film layers between conductor runs, and as substrates.

## Bulkhead Connectors

The inductance of the leads whose effects have been discussed can be essentially eliminated by construction in a coaxial configuration.  This type of packaging would be especially effective and convenient in conjunction with connectors for cable entry into shielded boxes.  (5)

Figure 8 shows a configuration for a single wire, and Figure 9 for multiple wires or pairs.  In both figures, a varistor bead is inserted between the conductor(s) and an opening of the bulkhead plate, which is part of the grounded shell.  In this manner, any impinging surge current flowing  in the conductor is diverted to the grounded chassis  of the enclosure, with minimum inductance inserted.

In principle, this construction is quite simple.  The details of the bonding between conductors and varistor will require development, which should be within the skills of connector manufacturing.

A possible objection to this construction would be-that the whole volume of the varistor bead acts as the dielectric of a capacitor inserted between the conductor and its sheath.  With an effective dielectric constant of 1000, and the small radial distance required for low-voltage clamping, the resulting capacitance might be excessive for high-frequency applications.  We note, however, that some advanced varistor materials have been fabricated with lower dielectric constants.

An alternate construction is shown in Figure 10, where the varistor disc has two concentric electrodes that are silk-screened on the side of the disc, rather than on the inside and outside surfaces, as in Figures 8 and 9. In this manner, the disc can have a substantial distance between the inside and out side surfaces, reducing the resulting capacitance.  The clamping voltage is then determined by the distance between the edges of the two electrodes This arrangement offers the advantages of lower capacitance and greater accuracy in the distance between electrodes, albeit at the cost of reducing the energy handling capability since only a thin surface layer of the varistor disc will conduct the surge current.

Coaxial Mounting

A varistor can also be inserted in a shielded cable by a coaxial "Tee" configuration.  In fact, that configuration is required for making valid measurements of the varistor performance in the submicrosecond time range.  (3)

Here again, the capacitance of the varistor might be objectionable at high frequencies.  A possible remedy to this situation is shown in the configuration of Figure 11, where the capacitance of the varistor is series-tuned to the inductance of the clamping spring.  This achieves high impedance to the UHF signal frequency, thus low loading, but offers a lower impedance and good suppression at the lower frequencies associated with lightning surge currents. (6) This would not, of course, be suitable for NEMP protection.

# Reconstituted Material

In the two preceding examples, the description of the varistor simply stated "varistor disc," with the assumption that the material had been prepared in the conventional sequence of pressing a powder into shape and sintering the piece in its final form.  There is another method of producing varistor components, especially attractive for parts shaped in a form different than conventional mass-produced discs.

In this method, the varistor material, obtained by the usual sintering, is ground into particles of controlled dimension, mixed with a suitable binder in proper proportions, and molded into the finished part.  By this method, it is possible to embed electrodes and conductors directly into the varistor material, as well as to fill a cavity such as a conductor shell.  (7)

Figure 12 shows the structure of a portion of a device using reconstituted material (tracing of a photomicrograph), where the three constituents interface: electrode, particle of varistor material, and plastic binder.  Here, the particle of varistor material is formed of several grains of ZnO with the varistor boundary layer between the individual ZnO grains.  If the particles of varistor material were smaller than the ZnO grains, there would not be any barrier layer left and the varistor action would be lost.  Thus, there is a need to optimize the grain size, the particle size, and the proportion of binder, depending on the specific application.

Figure 13 shows a photograph of a connector made by molding the reconstituted varistor material inside the shell of a connector provided with two pins.  The resulting varistor characteristic is shown in Figure 15 for pin-to-pin and pin-to-case.  With a shell that would be especially made for this application (the sample shown here was a standard shell), the pin-to-case characteristic would be controlled for lower voltage.

Another shape demonstrated is the plug of Figure 14, where a flat-headed stud is embedded in a metal cup, illustrating how electrodes can be molded directly into the reconstituted material.  The resulting characteristic is shown in Figure 16.

## Thick Film

The reconstituted material just described might also be useful for producing varistor layers with thick-film technology.  Currently, the reconstituted material is obtained by pressing the particles of varistor material in a cavity.  Producing a paint-like film would require some development in order to maintain the particle/binder proportion leading to the behavior as a varistor.  Should the particles become isolated from one another by an excess of binder, the varistor action would be lost.

With a suitable paint-like compound, it would be possible to silk screen varistor layers directly between conductor runs.  The clamping voltage would be controlled by the distance between the runs, while the current density would be controlled by the combined thickness of the layer and length along the run.

As an alternate to painting layers of reconstituted varistor material between runs, a more advanced concept would include the sintering of varistor layers on a suitable substrate, on which runs and other components could be added in sub-sequent processing.  This concept has not been reduced to practice, but illustrates the wide range of options that may be available beyond the commercial packaging of discs.

## Substrates

Another approach to the integration of varistor protection to circuits would be the use of substrate slabs of sintered varistor material, on which the circuit runs could be metallized.  Two possible concepts are proposed.  In Figure 17, the substrate acts only along a thin layer between two runs located on the same side of the substrate.  Because of the highly nonlinear property of the material, there is little fringing of current into the depth of the substrate.

In Figure 18, the substrate acts as an insulating barrier between the runs on one side and the ground plane on the other side.  Under normal operating voltages, the substrate layer offers a very large resistance and, thus, is nearly an insulator.  Upon development of a high voltage between any part of the circuit and ground, the surge is immediately diverted to the ground plane without any additional lead length.

In the latter approach, development of optimum compositions would allow producing a substrate with sufficient mechanical strength and a voltage which is still low enough.  Here we are dealing with the suppression of transients of moderate energy at the point where they may be induced (presumably as the circuit would be illuminated by an EM field).

## Varistor Materials Technology

Many of the unconventional varistor applications listed above required tailoring the varistor materials properties for optimum implementation of the system requirements under consideration.  Using technology available or under development, we can modify the varistor material in a variety of ways.  For example, we may:

1.	Increase the varistor breakdown field, thereby decreasing the space necessary for a given breakdown voltage.

2.	Decrease (or increase) the varistor dielectric constant.

3.	Fabricate screen-printable thin film varistors.

4.	Fabricate large (up to about 103 g weight and 30 cm diameter) devices for extremely large energy or current carrying capacities.

5.	Directly press varistors in special shapes (e.g., rings or slabs) to fit specific connector systems.

6.	Fabricate low-voltage varistors with breakdown voltages as low as 15 to 20 volts.

7.	Vary the degree of varistor nonlinearity.

In general, optimization of a particular varistor material parameter will involve a trade-off with other material properties.  The proper component design will involve the synergistic combination of materials technology and circuit design expertise.

## CONCLUSIONS

Varistor materials have been shown suitable for applications other than the conventional lead mounted device used in electronic circuit boards or the large blocks used in power system surge arresters.  The feasibility of some approaches has been shown, with details of implementation to be developed.  For other approaches, the development is still at the conceptual stage.

# ACKNOWLEDGMENTS

The concepts and technologies discussed in this report represent the contributions of many others, associated with metal oxide varistor technologies, some since their early introduction into the United States by General Electric.  The authors listed in the references contributed to the concepts discussed in the present report and should be acknowledged as implicit co-authors of this report.

REFERENCES

1.	Transient Voltage Suppression Manual, 2nd Edition, edited by J.C. Hey and W.P. Kram, General Electric Company, Auburn, NY, 1978.

2.	F.A. Fisher, "'Overshoot' - A Lead Effect in Varistor Characteristics," General Electric TIS Report 78CRD201, Schenectady, NY.

3.	H.R. Philipp and L.M. Levinson, "ZnO Varistors for Protection Against Nuclear Electromagnetic Pulses," J. Appl.  Phys. 52(2), 1981, pp. 1083-1090.

4.	IEEE Standard C62.33-1981, "Test Specifications for Varistor Surge Protective Devices."

5.	D.M. Tasca, J.D. Harnden, Jr., and F.D. Martzloff, U.S. Patent 3,711,794 (1973).

6.	F.D. Martzloff, U.S. Patent 3,863,111 (1975).

7.	J.F. Burgess, R.T. Girard, F.D. Martzloff, C.A. Neugebauer, U.S. Patent 4,103,274 (1978).

SURGE SUPPRESSORS AND CLAMPS

François D. Martzloff

National Bureau of Standards

Gaithersburg MD 20899

# INTRODUCTION

Various devices have been developed for the protection of electrical and electronic equipment against transient overvoltages.  They are often called "transient suppressors" although, for accuracy, they should be called "transient limiters," "clamps," or "diverters" because they cannot really suppress the transients; rather, they limit the transients to acceptable levels or make them harmless by diverting them to ground.  The IEEE dictionary has selected the more generic but lengthy term of “surge protective device.”

There are two categories of transient suppressors: those that block transients, preventing their propagation toward sensitive circuits, and those that divert transients, limiting residual voltages.     Since many of these transients originate from a current source, blocking them may not always be possible because the current forced into the high-impedance blocking path would only result in higher voltages and breakdown.  Therefore, diverting of the transient is more likely to find general application.  A combination of diverting and blocking can be a very effective approach.  This approach generally takes the form of a multistage circuit, where a first device diverts the transient current to ground; a second device offers a restricted path for transient propagation but an acceptable path for the signal or power, and a third device  clamps the residual transient (Figure 1).  Thus, we are primarily interested in diverting devices.

The diverting device can be of two kinds: voltage-clamping or short-circuiting devices (the latter called "crowbars").  Both of them involve some nonlinearity, either frequency nonlinearity (as in filters) or, more usually, voltage nonlinearity.  This voltage nonlinearity is the result of two different mechanisms -- a continuous change in the device conductivity as the current increases, or an abrupt switching action as the voltage increases.

Because the technical and trade literature contains many articles on these devices, we shall limit the discussions of the details but make some comparisons to point out the significant differences in the performance . Understanding the relative merits and the limitations of each technology will allow informed choice and recognition that there is room for each approach in the wide range of needs and applications.

# CROWBAR DEVICES

The principle of crowbar devices is quite simple: upon occurrence of an overvoltage, the device changes from a high-impedance state to a low-impedance state, offering a low-impedance path to divert the surge to ground.   This switching can be inherent to the device, as in the case of spark gaps involving the breakdown of a gas or be the recently introduced combination of multijunction solid state devices.

The major advantage of the crowbar device is that its low impedance allows the flow of substantial surge currents without the development of high energies within the device itself; the energy has to be spent elsewhere in the circuit.  This "reflection" of the impinging surge  can also be a disadvantage in some circuits if the transient disturbance associated with the gap firing is being considered.  Where there is no power-follow (discussed below), such as in some communication circuits, the spark gap has the advantage of very simple construction with potentially low cost.

The crowbar device, however, has three limitations. one is the volt-time sensitivity of the breakdown process in air gaps or gas tubes.  As the voltage increases across a gap, significant conduction of current – therefore voltage limitation for the surge – cannot occur until the transition to the arc mode of conduction, by avalanche breakdown of the gas between the two electrodes.  The load is unprotected during the initial rise because of this delay time (typically in microseconds) .   Large variations exist in sparkover voltage attained in successive operations since the process is statistical in nature.  This sparkover voltage can also be substantially higher after a long period of rest than after successive discharges.  Because of the physics of the process, it is difficult to produce consistent sparkover voltage for low voltage ratings.  This difficultly is increased by the effect of manufacturing tolerances on very small gap distances, but can be alleviated by filling the tube with a gas having lower breakdown voltage than air.  The technology developed by manufacturers of gas tubes has minimized these effects.  One advantage of the solid state crowbars over the gas breakdown tubes is the absence of any practical time delay in firing.

The second limitation is associated with the speed of the sparkover, which produces fast current rise in the circuits and, thus objectionable noise.  An example is found in hybrid protective systems.  Figure 2 shows the circuit of such a commercially available device.  The gap does a very nice job of diverting impinging high energy surges, but the magnetic field associated with the high di/dt induces a voltage in the loop adjacent to the second suppressor, adding a substantial spike to what was expected to be a low clamping voltage.  Some product literature advocates locating solid-state crowbars on the very circuit board where components to be protected are mounted – a perfect recipe for injecting interference right into the circuits!

A third limitation occurs if power current from the steady-state voltage source can follow the surge discharge (hence the term "power-follow").  In ac circuits, this power follow current may or may not be cleared at a natural current zero.  Additional means, therefore, must be provided to open the power circuit if the crowbar device is not designed to provide self-clearing action within specified limits of surge energy, system voltage, and power-follow current.  This combination of a gap with a current-limiting, nonlinear varistor has been very successful in the utility industry as high voltage surge arresters.

# VOLTAGE-CLAMPING DEVICES

Voltage-clamping devices have variable impedance, depending on the current flowing through the device or the voltage across its terminal.  Impedance variation is monotonic and does not contain discontinuities, in contrast to crowbar devices, which show a turn-on action.  As far as their volt-ampere characteristics are concerned, these devices are time-dependent to a certain degree.  However, unlike the sparkover of a gap or the triggering of a thyristor, time delay is not involved.

When a voltage clamping device is applied, the circuit remains essentially unaffected by the device before and after the transient for any steady-state voltage below clamping level.  Increased current drawn through the device as the surge voltage attempts to increase results in voltage-clamping action.  Nonlinear impedance is the result if this current rise is greater than the voltage increase.  The increased voltage drop in the source impedance (Zs in Figure 3) due to higher current results in the apparent clamping of the voltage.  It must be emphasized that the device depends' on the source impedance to produce this clamping.  The circuit behaves as a voltage divider where the source impedance (high side of the divider) is constant but the clamping device impedance (low side of the divider) is changing.  If the impedance of the source is very low, the ratio is low, and eventually the suppressor could not work at all with a zero source impedance.  In contrast, a crowbar-type device effectively short circuits the transient toward ground, but, once established, this short-circuit will remain until the current (the surge current as well as any power-follow current supplied by the power system) is brought to a low level.

The action of voltage clamping can be performed by any device exhibiting a nonlinear impedance.  Two categories of such devices, having the same effect but operating quite different physical processes, have found an acceptance in the industry: polycrystalline varistors and single-junction avalanche diodes.  Another technology, using selenium rectifiers, has been practically eliminated because of the improved characteristics of modern varistors.

#### Avalanche diodes

Avalanche diodes were initially applied as voltage clamps in the form of zener diodes, a natural outgrowth of their application as voltage regulators.  Improved construction, specifically aimed at surge absorption, has made them very effective suppressors.  Large diameter junction and low thermal impedance connections are used to deal with the problem of dissipating the heat of the surge, inherent in a thin single-layer junction.

The advantage of the avalanche diode is the possibility of obtaining quite low clamping voltages and nearly flat volt-ampere characteristics over its useful power range.  Therefore, these diodes are widely used in low-voltage electronic circuits to protect 5 V or 15 V logic circuits, as an example.  At higher voltages, the problem of the heat generation associated with single junctions can be overcome by stacking several lower voltage junctions.

Characteristics of Avalanche Diodes – Silicon avalanche diodes are available with characteristics especially tailored to providing transient suppression.  These special diodes must not be confused with regulator-type Zener diodes although many engineers tend to use the generic term "Zener diode." May Zeus help them if they were to misapply a regulator-type Zener, expecting effective protection!

Figure 4 shows a typical family of the V-I characteristics for one product.  The parameter I is the peak of a specified current waveform, generally the 10/1000 s double-exponential test waveform preferred by communication engineers, rather than a 8/20 s waveform preferred by power engineers.  The V-I curves are remarkably flat from 1 to 20 amperes, with clamping voltages low enough to protect sensitive electronics.

Manufacturers of avalanche diodes generally rate their devices in terms of maximum peak power for a specified pulse duration.  Even though the rated power will decrease with increasing pulse duration, it is not a case of constant total energy (see Figure 5).  A two-decade increase in pulse duration will reduce the power by only, about one decade, primarily because of increasing heat transfer for longer pulses.

Since the junction is very thin, the capacitance of an avalanche diode is appreciable.  This capacitance can be a concern in high-frequency circuits where it would produce an undesirable insertion loss.  It is possible to minimize this effect by using a combination with a low-capacitance ordinary diode in series with the avalanche diode.  Properly packaged and installed avalanche diodes exhibit a quick response to steep-front pulses, and have been used for NEMP

However, this quick response protection can be completely obliterated by improper wiring.  The  effect  of  lead length, discussed in detail in the next section, is applicable to any transient suppressor.

#### Varistors

The term varistor is derived from its function as a variable resistor.  It is also called a voltage-dependent resistor, but that description implies that the voltage is the independent parameter in surge protection, an incorrect perception.  Two very different devices have been successfully developed as varistors: 1) silicon carbide disks have been used for years in the surge arrester industry and 2) metal oxide varistors are now widely used.

In silicon carbide varistors, as well as in metal oxide varistors, the relationship between the current flowing in the device and the voltage appearing across its terminals can be represented approximately by a power function I = kVa.   In this equation, the exponent a, can be considered as a figure of merit: the higher the value of a, the more effective the clamping.   Hence, there has been a race between manufacturers and specification writers for higher and higher values of a. We will see, however, that there are practical limits to this race and that better performance can be obtained at higher current densities by departing somewhat from large values of the exponent.

In silicon carbide varistors, the physical process of nonlinear conduction is not completely understood, and the manufacturing of the material, successful as it is, has remained an art.  It appears that the process takes place at the tips of the grains of silicon carbide which are held together by a binder.  The story is told that this device's action was found accidentally by having a grinding wheel, on a disorderly work bench, inadvertently connected to an experimental circuit; for many years the silicon carbide varistors indeed looked like grinding wheels, each complete with a hole in the center.

Metal oxide varistors depend on the conduction process occurring at the boundaries between the grains of oxide (typically zinc oxide) grown during a carefully controlled sintering process.  The physics of the non-linear conduction have been described in the literature [1-4]; in these application notes, we will be more concerned with the behavior of the varistors as two-terminal electrical components.

Electrical Characteristics of Varistors – Because the prime function of a varistor is to provide the nonlinear effect, the other parameters are generally the result of a tradeoff in design and inherent characteristics.  Electrical behavior of a varistor can be understood through the equivalent circuit of Figure 6.  The major element is the varistor proper, Rv, whose V-I characteristic is assumed to be the perfect power law I = kVa.  In parallel with this varistor, there is a capacitor, C, and a leakage resistance R.    In series with this three-component group, there is the bulk resistance of the zinc oxide grains, RS$ and the inductance of the leads, L.

Under dc conditions (at low current densities, because obviously no varistor could stand a high energy produced by dc currents of high density), only the varistor element and the leakage resistance are significant.  Under pulse conditions at high current densities, all but the leakage resistance are significant: the varistor provides low impedance to the current flow, but eventually the series resistance produces an upturn in the V-I characteristic; the lead inductance can produce spurious overshoot problems if it is not dealt with properly; the capacitance can offer either a welcome additional path for fast transients or an objectionable loading for high-frequency signals, depending on the application.

V-I Characteristics --- When the V-I characteristics are plotted on a log-log graph, the curve of Figure 7 is obtained.  It has three regions as shown, resulting from the dominance of Rp, Rv, Rs as the current in the device goes from nanoamperes to kiloamperes.

The V-I characteristic is the basic application design tool for selecting a device in order to perform a protective function.  For successful application, however, other factors, which are discussed in detail in information available from manufacturers, must also be taken into consideration.

Some of these factors are:

*	Selection of the appropriate nominal voltage for the line voltage (Avoid unnecessarily low clamping.)

*	Selection of energy-handling capability (Consideration of the source impedance, waveshape, and number of occurrences of the transient [5].)

*	Heat dissipation  (Ambient temperature, steady state and transient energy.)

* 	Proper installation in the circuit (Lead length).

In fact, enough instances of poor "installation practices have been observed that a brief discussion of lead effects is quite in order.

When making voltage measurements across a clamping device for evaluating its performance, one must recognize possible instrumentation artifacts which require special precautions to avoid errors:

1.  Use two probes in a differential mode to make a measurement directly at device terminals, and not a single-ended system.

2.  Avoid contaminating the true device voltage by the additional voltage caused by magnetic coupling into the probes loop.

Commercial oscilloscope preamplifiers offer a wide choice of differential mode operation, either through an [add + invert) mode of two-channel preamplifiers, or through a differential amplifier built specifically for high common-mode rejection (sometimes at the expense of bandwidth).  Thus, careful attention must be given to these two aspects of measurements.

The voltage measured by the two probes (or the voltage that would be applied to a protected load downstream from the device) is the sum of the actual clamping voltage at the device terminals and a spurious voltage caused by magnetic coupling.  This spurious voltage is induced into the loop formed by the clamping device leads and the probes (or the downstream wiring in the case of an actual protective scheme) by the changing magnetic field of the surge current flowing in the device.

To illustrate this situation, the measurement circuit shown in Figure 8 was set up in the output circuit of a generator producing a 8/20 s impulse.  The "device" was a hollow conductor, with a hole at the center through which a twisted pair was fed, one wire of the pair branching out to each end of the conductor, separated by 10 cm.  At the same 10-cm separation, but outside of the hollow conductor, two thin wires were also soldered, brought to the midpoint of the hollow conductor and in close contact with the conductor; from the midpoint outward, they were twisted in the same manner as the inside pair.  A third pair of wires was soldered at the end points of the hollow conductor, and arranged to form a rectangle, the hollow conductor being one side of that rectangle. various widths were set up for the rectangle, and each time the measured voltage was recorded.  Figure 9 shows measured voltage vs. radial distance of the opposite side of the rectangle.  The effect is present even for close proximity, and reaches a saturation beyond 10 cm.

This example shows that one must not only connect the probes as close as possible to the clamping devices terminals, but also strive to minimize the area established by the probes close to the devices.

In this case of a low-voltage suppressor, it would be better to solder short leads to the device terminals, bring them together while hugging the device, then twist them into a pair and connect the oscilloscope probes some distance away from the device.  The same conclusion is applicable to the wiring layout in actual hardware: Creating a loop near the protective device is an invitation to induce additional voltages in the output of the protective device, thus losing effectiveness (Figure 3).

Hence, when one is making measurements as well as when one is designing a circuit for a protection scheme, it is essential to be alert to the effects of lead length (more accurately of loop area) for connecting the protective devices.  This warning is especially important when the currents are in excess of a few amperes with rise times of less than 1 s.

# COMPARISONS OF PROTECTIVE DEVICES

#### Linear Versus Nonlinear Devices

When a protection scheme is designed for an electronic system operating in an environment which is not completely defined, it is often necessary to make an assumption about the parameters of the transient expected to occur.   In particular, if an error is made in assuming the source impedance of this transient, the consequences are dramatically different between a linear device for which the protective level will be affected in proportion to the error, and a nonlinear device where the protective level will be affected approximately in inverse ratio to the exponent of the V-I characteristic.

#### Spark Gap Versus Varistor

The choice between these two devices will be influenced by the inherent  characteristics of the application.  Where power-follow may be a problem, there is little opportunity to apply a simple gap.  Where very steep-front transients occur, the  gap alone may let an excessive voltage go by the "protected" circuit until the voltage is limited by sparkover.  Where the capacitance of a varistor is objectionable, the low inherent capacitance of a gap will seem attractive.  If very high energy levels can be deposited in a varistor (the power dissipated remains as heat energy trapped in the bulk material) , compared to the lower levels inherent to the crowbar action of a gap, then a surge arrester of any type with high capacity connected at the service entrance may be combined with a varistor of lower clamping voltage installed further in the circuit.  This combined protection, however, requires proper coordination between the two suppressors [6].

## Avalanche Diode versus varistor

The basic performance characteristics of these two devices are similar, and therefore the choice may be dictated by clamping voltage requirements (avalanche diodes are available at lower clamping voltages), by energy-handling capabilities (avalanche diodes are generally lower in capability per unit of cost), or by packaging requirements (varistor material is more flexible and does not require hermetic packaging).

# FAILURE MODES

Failure of electrical components can occur because their capability was exceeded by the applied stress or because some latent defect in the component went by unnoticed in the quality control processes.  This situation is well recognized for ordinary components but a surge protective device, which is no exception to these limitations, tends to be expected to perform miracles or at least to fail graciously in a "fail-safe" mode.

The term "fail-safe," however, means different failure modes to different users, therefore it should not be used.  To some users, fail-safe means that the protected hardware must never be exposed to an overvoltage, so that failure of the protective device must be in the fail-short mode, even if it puts the system out of operation.  To other users, fail-safe means that the function must be maintained, even if the hardware is left temporarily unprotected, so that failure of the protective device must be in the open-circuit mode.  It is more accurate and less misleading to describe a failure mode "fail-short" or "fail-open," as the case may be.

When the diverting path is a crowbar-type device, little energy is dissipated in the crowbar, as noted earlier.  In a voltage-clamping device, because more energy is deposited in the device, the energy handling capability of a candidate protective device is an important parameter to consider in the design of a protection scheme.  With nonlinear devices, an error made in the assumed value of the current surge produces little error on the voltage developed across the protective device and applied to the protected circuit (the error, however, affects directly the amount of energy which the protective device has to absorb.  At worst, when surge currents in excess of  the protective device capability are imposed by the environment, such as an error made in the assumptions, a human error in the use of the device, or because nature tends to support Murphy's law, the circuit in need of protection can generally be protected at the price of failure in the short-circuit mode of the protective device.  However, if substantial power-frequency currents can be supplied by the power system, a fail-short protective device generally terminates as fail-open when the power system fault in the failed device is not quickly cleared by a series overcurrent protective device (a fuse or a breaker).

When there is a need to eliminate a failed protector at the specific equipment level, insertion of the fuse in the line provides protection of the equipment (Figure 10a), while insertion of the fuse in series with the shunt-connected protector provides protection of the function, albeit with loss of overvoltage protection (Figure 10b).  A fuse must be selected with suitable i2t to withstand the effect of repetitive surges expected to flow in the application.

## CONCLUSIONS

1.	Surge protective devices are available for protecting low-voltage electronics.  Two basic types offer different advantages:

*	Crowbar devices have a high current capability but they would produce a power-follow, if applied in a power system; their fast switching action can be a cause of problems if it is not recognized.

*	Voltage clamping devices, either the avalanche junctions or the varistors, are free from the problems of power-follow and interference caused by a fast switching, but the energy which is deposited in these must be recognized for long-term reliability.

2.	Avalanche diodes offer low clamping voltage, which makes them most suitable for low-voltage, low-power electronics.

3.	Metal-oxide varistors are now available in a wide range of forms, clamping voltages and energy-handling capacities.

4.	Each of these devices has its own best field of application for better reliability of the circuits in the not-quite-defined electromagnetic environment of power and communication systems.

## REFERENCES

1. Matsuoka, M., Masa Yama, T. and Lida.,Y. "Nonlinear Electrical Properties of Zinc Oxide Ceramics," Proc.  First Conf.  Solid State Devices, Tokyo, 1969, J. Japan Soc. Appl.  Phys., 39 1970, Suppl. p.94.

2. Harnden, J.D., Martzloff, F.D., Morris, W.G. and Golden, F.B., "The GE-MOV varistor -- The Super Alpha Varistor," Electronics, 45, no.21, 1972, p.91.

3. Sakshaug, E.C., Kresge, J.S. and Miske, S.A., "A New Concept in Station Arrester Design," IEEE PAS-96 No.2, March-April 1977, p.647.

4. Mahan, G.D., Levinson, L.M., and Philipp, H.R., "Theory of Conduction in ZnO Varistors," Report 78CRD205, General Electric Company, Schenectady, NY, 1978.

5. Martzloff, F.D., "Matching Surge Protective Devices to Their Environment," IEEE IA-21 No.1, Jan/Feb 1985, p.99.

6. Martzloff, F.D., "Coordination of Surge Protectors in Low-Voltage Power Circuits," IEEE PAS-99 No.1, Jan/Feb 1980, p.129.

A GLIMPSE AT LONG-TERM EFFECTS OF MOMENTARY OVERVOLTAGES

ON ZINC OXIDE VARISTORS

François D. Martzloff and Thomas F. Leedy

National Institute of Standards and Technology

Gaithersburg, Maryland 20899

ABSTRACT

Because the prime function of varistors is the diversion of high energy surges, most of the attention is directed toward selecting the appropriate device rating to ensure long life under surge conditions.  Some attention is also given to matching steady-state rating of the device to the power system voltage.  However, during abnormal (and not well defined) power system conditions, the line voltage can reach values that will cause substantial current in the varistor.  Until the effects of these momentary overvoltages are better identified and understood, there will be a risk of near-term failure at worst and accelerated aging at best.

SELECTION OF VARISTOR RATINGS

Selection of a varistor rating is essentially a process of matching the capabilities of the device to the power system environment, while obtaining the desired low clamping voltage during surge events.  Low clamping voltage of a varistor may be obtained in one of two ways, or both: low current density at the surge current, which means a relatively large area, or low intrinsic voltage, which means a relatively thin disc.  Increasing the area of a disc increases the device cost so that the natural tendency of designers will be to seek the thinner disc rather that the larger diameter disc.  Therefore, this paper addresses the concerns raised by excessive reduction of disc thickness, that is, the use of varistors with rated line voltage lower than what prudent practice would indicate.

In matching a varistor to its environment, the two principal environment characteristics to be considered are: (1) the surges expected to occur on the system -- the primary reason for using the varistor -- and (2) the system rated voltage.  In the application of surge arresters to electric utility systems, considerable attention is given to abnormal power system conditions, as evident in the rating of these arresters which takes into consideration the maximum continuous operating voltage (MCOV) permissible for an arrester. [1]

In the case of low-voltage electronic circuits, equipment designers generally rely on the manufacturer's rating of a device for the stated nominal system voltage.  This system voltage is defined with some expected tolerance, such as 15%, on the maximum voltage that can occur.

Surge ratings - Specification sheets published by varistor manufacturers generally include a "Pulse Rating" family of curves showing the number of permissible surges (pulses) as a function of current amplitude and duration.  This pulse rating makes it possible to select a device of appropriate dimensions -- that is, current handling capability -- to ensure survival in the known or postulated surge environment [2].  Actually, survival means more than the non-occurrence of a catastrophic failure.  For varistors used in electronic equipment, the criterion for end of life, or total consumption of the Pulse Rating, is a change of more than 10% in the device nominal voltage.  The actual process leading to this change in device characteristic is not clearly described by the manufacturers literature, but is generally believed to involve microscopic damage to the structure.

Steady-state vs. momentary ratings - The steady-state rating is generally determined by the manufacturers, on the basis of in-house experience.  This process is reflected in the wording of an IEEE Standard on varistors defining "Rated RMS Voltage" as follows: There is no single test that can determine the voltage rating, but rather an evaluation process taking into consideration .... 7hese considerations are within the realm of the manufacturer's and user's application engineering functions. [3] In plain English, this means that there is no clear-cut guidance available; rather, designers are left on their own to make the bard choices.  The manufacturers, however, do publish an Arrhenius plot of mean life versus temperature, implying high activation energy levels in the processes leading to the end of life under steady-state line voltage.

Field experience has shown that the expectation of a + 15% maximum deviation of line voltage is optimistic.  The term "swell" has been proposed [4] to describe the occurrence of a momentary increase of the sinusoidal line voltage amplitude, lasting from a few cycles to a few seconds.  During such a swell, the normal standby current of the varistor will increase in accordance with the varistor power law.  For instance, a 20% increase in line voltage (a factor of 1.2) rather than the 15% often considered as the "high-line limit" by designers, with a varistor exponent of 32, produces an increase of the standby current of 1.2 elevated to the 32th power -- a 340-fold increase ! This current level can no longer be considered a benign "standby current."

Thus, the selection process of a varistor must also include proper attention to the long-term effects of repeated swells.  A search of the literature reveals that no work has been published on these effects.

Perhaps one of the reasons for this lack of information is that very little specific information has been collected on the severity of swells occurring in power systems.  The electric utilities and their customers have recently increased their awareness of the so-called Power Quality issue, as a result of concerns over the performance of increasingly sophisticated electronic equipment supplied by a disturbance-prone power system.  One of the effects of these concerns has been the development of disturbance monitors with graphics capability.  As more and more of these monitors are applied, the occurrence and characteristics of swells will become much better known.

Thus, between the well-defined bounds of short-time surges and the less defined steady-state voltage rating, neither the occurrence nor the effects of repeated swells are well defined.  Faced with this lack of information, the authors have initiated a joint project of experimental and theoretical evaluation of the effect of repeated swells on zinc oxide varistors.  The experimental work consists essentially in applying repeated swells of various amplitudes and durations, seeking to detect some change in the electrical characteristics of the varistor that would herald the onset of objectionable degradation.  The theoretical work consists in modeling the behavior of the varistor, essentially its temperature, in response to a variety of swells.  To fully understand the science involved, however, this work should be complemented by fundamental studies on the degradation mechanisms leading to any observed change in the electrical characteristics.  One of the purposes of this paper is to motivate ceramists toward looking into the effects of swells from the point of view of ceramic structural changes.  In the meantime, the experimental work, supported by modeling to identify the impact of various levels of swells, will draw the attention of equipment designers to the pitfalls of selecting excessively thin discs. [5]

MODELING THE EFFECT OF SWELLS

A circuit analysis model of a metal-oxide varistor was used to investigate the behavior of varistors when exposed to swells.  The model consists of two parts: The electrical part of the model predicts the current-voltage behavior of the varistor and the thermal part of the model predicts the temperature changes caused by the energy deposited in the varistor during the swell.  The electrical and thermal simulations were performed using a commercial software system which uses behavioral equations to mimic nearly any physical device or process.

The model computations were performed for a varistor rated at 130 V rms.  Such a varistor is the lowest rating offered by manufacturers for a 120 V circuit.  To represent a possible worst case, the varistor characteristics used for the model computations were set at the lower limit of the tolerance band.  To simplify the model, no allowance is made for heat loss by convection, the situation that can be expected in a tight packaging without any encapsulation.  Heat losses by radiation are negligible at the temperatures involved.  These postulates provide worst case results, a justifiable approach when considering reliability.

Figure 1 shows an example of the output plot of the model computations, for a 206 V peak line voltage (145 V rms, a 20 % swell).  The current exhibits the highly nonlinear response of a varistor, with 20 mA peaks.  The resulting temperature increase steps are also plotted for each successive pulse, occurring at the 120 pulse-per-second rate.  As the temperature increases, so will heat losses, until a thermal equilibrium is reached, unless thermal runaway would occur.

Figure 2 shows the temperature rise predicted for the application of swells at two voltage levels beyond the 20% swell of Figure 1, each with a duration of 200 s. This 200 s duration was selected because it approximates the time required to reach thermal equilibrium in this model, not because of an inference that power system swells last 200 s. The lower curve shows the temperature rise of approximately 130 oC expected from 156 V rms (a 30 % swell).  The upper curve shows a temperature rise of nearly 300 oC for 160 V rms (a 33 % swell). These curves illustrate that a relatively small change in the swell level, from 156 V to 160 V rms, produces a drastic increase in the power dissipation and the temperature rise  of  a  varistor.  The  300 oC  temperature  rise  means  assured destruction of the varistor, the 130 oC temperature could mean some accelerated aging, if repeated enough times.  Thus, the cumulative effect of repeated swells needs to be evaluated.  This evaluation is the subject of the experimental work.

EXPERIMENTS WITH REPEATED SWELLS

Several factors are known or suspected in the behavior of actual varistors exposed to repeated stress, complicating the apparent simplicity of varistor modeling.  Aging -- a change in the varistor characteristics in response to overstresses -- is only one of them.  Even when considering only aging, there is no universally recognized criterion of degradation.  Most varistor specifications refer to a 10% limit in changes of the nominal voltage of the varistor.  However, since this nominal voltage is defined arbitrarily for a 1 mA current regardless of the varistor cross section, the criterion varies with varistor sizes.  Another proposed criterion, power dissipation at some ac voltage, is complicated by the fact that the power dissipation changes with the duration of application of the steady-state as well as swell ac voltages.

This effect, which permanently changes the characteristics of the varistor, sometimes called "formation," was quite apparent when successive swells were applied.  During application of one swell, for instance, the increasing temperature of the varistor is reflected in the increased peak amplitude of the current, as shown in Figure 3A.  However, when comparing the pattern of current peaks within the first swell to the pattern of a later swell, after many additional swells (Figure 3B), the most obvious change is a reduction of the current peaks between the original swell and the later swell.  Thus, a systematic method to account for that "formation" effect must be developed to define a valid criterion of aging before conclusions can be drawn on quantifying the aging effect of swells.

CONCLUSIONS

Attempts at improving surge protection by selecting varistors with low voltage ratings increase the risk of premature aging, even early failure, of varistors exposed to repeated momentary overvoltages ("swells").

The effects of such repeated swells have not been documented by the manufacturers, although it is a subject of investigation that would provide useful results for greater reliability.  Additional theoretical and experimental work is necessary to develop guidance useful to prudent equipment designers.

While the occurrence of these swells has not been well characterized in the past, the increasing availability of power line disturbance monitors will improve this characterization in the future.  Combined with a better understanding of the effects of swells, this knowledge will enhance the reliable application of metal-oxide varistors.

REFERENCES

[11 Sakshaug, E.C., Burke, J.J., and Kresge, J.S., Metal Oxide Arresters on Distribution Systems - Fundamental Considerations, IEEE Winter Power Meeting Paper, 1989. (To be published in IEEE Transactions on Power Delivery.)

[21 Martzloff, F.D., Matching Surge Protective Devices to their Environment, IEEE-LAS Transactions, Vol.  IA-21, No.1, pp. 99-106,1986.

[3] IEEE Standard Test Specifications for Varistor Surge-Protective Devices, ANSI/IEEE C62.33-1982.

[4] Martzloff, F.D., and Gruzs, T.M., Power Quality Site Surveys: Facts, Fiction and Fallacies, IEEE-IAS Transactions, Vol. 24, No.6, pp.1005-1017,1988.

[5] Martzloff, F.D., and Leedy, T.F., Selecting Varistor Clamping Voltage: Lower is not Better! Proceedings, EMC Zurich Symposium, pp. 137-142, 1989.

Figure 1. Computed instantaneous temperature increase of a varistor during two cycles of a 20% swell

Figure 2. Computed integrated temperature increases during a 30% swell and a 33% swell

Figure 3. Samples of varistor current during a 16-second swell with peak voltage at 117%

What Are the Lights on Your Surge Protector Telling You?

François Martzloff

National Institute of Standards and Technology

Gaithersburg, Maryland

Especially in a free market, sensible standards and reasonable regulations have a role to play toward providing useful, reliable and safe consumer products, such as the now familiar transient voltage surge suppressors (TVSS). However, the definition of what is sensible and reasonable has not been stipulated in any TVSS standard. This article provides a historical perspective of the evolution of how TVSS standards address the issue of a disconnector, an emerging concept in TVSS design.

A sampling of how this concept has been implemented by the TVSS industry, including overcurrent protective devices (fuses) and thermal runaway protection (thermal cut-out), shows a variety of rather confusing approaches. To illustrate this point, let’s consider three familiar products: fruit cakes, automobiles, and TVSSs.

We will all agree that our military personnel serving in some desolate foreign country are entitled to a high-quality product when the traditional fruitcake is sent to them at holiday time. To ensure that this happens, as reported tongue-in-cheek by the media a few years ago, a lengthy specification had been developed for quality control in the procurement of fruitcakes.

Consider now the plight of the tired traveler, arriving at night in an unfamiliar airport and renting a car. The agent behind the counter gives the traveler the keys and the location of the car in the parking lot, and smiles with good wishes thrown into the deal. Arriving at the designated spot in the dark parking lot, everyone expects to find that the steering is located on the left, controlled by means of a wheel, the engine is started with an ignition key, generally near the steering column, and gas and brakes are controlled by the right foot. But what about finding the headlight control after you have closed the door (it’s cold and windy out)? Worse yet, two miles out of the airport, in heavy traffic, it suddenly starts to rain and the traveler fumbles to find the windshield wiper control? Now would it not be lovely if there were standards mandating the location of these controls?

No Common Meaning to Lights

Coming now to the point of TVSSs, consider the plight of the consumer who bought a TVSS, and discarded the bubble package or misplaced the instruction sheet. This consumer is now trying to find the meaning of the pilot light, or pilot lights, indicating the state of the device — specifically whether protection is in effect or protection is lost. The original 1985 version of UL Standard 1449 stipulated that a visible or other indication of the protection status must be provided when an overcurrent protection has operated. But that is no help to the computer user who has installed a plug-in suppressor sandwiched between the wall and the desk. Even if the TVSS were visible, there might be one. two or even three pilot lights, with or without clear and reliable indication of their meaning.

To place this undesirable situation in perspective, I visited three local electronics and do-it-yourself stores and bought 17 different brands of TVSSs. The question was, “How would the user be informed on the status of protection after a temporary overvoltage caused failure of the protective element in the TVSS package?” A temporary overvoltage was selected as the method of failure because there is growing evidence that they cause a large number of the failures that occur — perhaps the majority —rather than “large” surges. Although that statement could be the subject of one entire issue of this magazine, it is only mentioned here to describe how the failures were obtained.

The point of the inquiry was not to describe how the failure occurred (in particular whether there was a potential hazard, since the devices were manufactured before the 1996 Second Edition of UL 1449 became effective). The point of the inquiry is to find what information is clearly conveyed to the user after the TVSS has failed, and its disconnector has operated. Neither the new UL 1449, nor any IEEE or IEC standards address that practical question. In fact, the new 1996 version of UL 1449 no longer stipulates inclusion of a visible indication. As it turned out, several of the packages among the 17 specimens had very little information on the significance of the indicating light or how the indications should be interpreted. Furthermore, as mentioned earlier, once the bubble package is discarded, the information is lost, because it is unlikely the typical user will safeguard the back of the bubble package where the details — if any — might have appeared.

SPD Failure Modes

Surge-protective devices (SPDs) components — switching away from the jargon ‘TVSS’ to the official term of ‘SPD’ approved by the IEEE and IEC — like any electrical component, are subject to failure for a variety of causes including severe overstress beyond their rating, natural ageing, premature failure caused by misapplication, etc. The outcome of such failures ranges from an open circuit to a very low impedance, but rarely a zero-impedance short circuit. A final open circuit may be difficult to achieve in an environment of high available fault current. If achieved, it implies loss of protection against subsequent surges. A zero-impedance condition would mean no energy dissipation (no heating) in the failed SPD component and thus a relatively benign failure mode from the point of view of the SPD environment, but that would require interruption by an upstream overcurrent protection device.

In reality, the nature of the failure mechanism, in particular for metal-oxide varistors, (MOVs) is that the impedance of the failed SPD, which is resistive, is low, but not zero. Consequently, the power circuit will deliver to this medium-range resistance a current that involves significant energy, depending upon the actual resistance of the failed device and the upstream impedance of the power system.

If left unabated, this deposited energy will produce severe overheating with attendant risk of fire or other objectionable failure modes. It is to prevent such objectionable scenarios that the concept of an SPD disconnector emerged, as seen in this historical perspective.

The term “disconnector” is a recent addition to the vocabulary of the SPD industry, and the spell-checker of most word processors flags it as unknown (as if your processor had never disconnected on you?). Even the definition of the term has gone through several iterations in recent years.

According to emerging standards, the disconnector function is to “disconnect an SPD from the power system in case of SPD failure.” This clear and simple concept, however, has not been consistently implemented by industry, in particular by the low-voltage SPD industry. In particular, two different devices — a fuse or a thermal cut-off — can serve toward that end, each covering one type of SPD failure. In case of SPD failure resulting in a low impedance mode (a few ohms) an overcurrent occurs, with amplitudes in excess of the SPD rating, so that a fuse can clear the circuit. In case of a thermal runaway, the beginning of SPD failure, the current is still too low to operate the fuse, but the consequences of failure (overheating) can be prevented by the operation of a thermal cut-out in close proximity to the SPD experiencing the beginning of overheating.

This ambiguity in the type of disconnector design and the lack of consistency or consensus in the interpretation of the function is apparent in the wide variety of designs found on the market, while standard-writing bodies are still working on developing an acceptable consensus over a broad range of applications. One unresolved issue is whether the user expects protection after failure — through a complete disconnect of the load — or would rather take a chance by maintaining continuity of operation, but without protection.

Standards development generally lags the development of products in a competitive, fast-moving technology. Low-voltage SPDs are no exception. To illustrate this point, Table I presents a chronological tabulation of the evolution of the disconnector concept, from the introduction of metal-oxide varistors in the mid-seventies, to the latest amendment of the definition of a disconnector in the late nineties.

The tabulation shows the reference document and cites, verbatim or in summary, the implied need — and eventually the specification — for a suitable disconnector function. Inspection of the chronology shows a clear trend toward mandating a reliable disconnector function, but also some concessions to existing product practices. Nevertheless, the disconnector remains the ultimate protection against objectionable failure modes. As recognition of this essential role of a disconnector increases, one can expect that standards are more likely to mandate provision of a reliable and clearly defined disconnector function for all low-voltage SPDs. It may he easy for an outsider to make judgments on the apparent chaos of the marketplace and the present standards, but there are extenuating circumstances because the concept as well as the implementation of a satisfactory disconnector are not trivial. Some of the options, advantages and drawbacks are briefly enumerated below.

# Disconnector Provisions

## Integral disconnector

-  Disconnects only the shunt-connected SPD

      - Design challenge: requirement of not operating for the expected surges but of operating promptly upon failure of the SPD element.

      - User information: necessity to SPD disconnector, the details of the \operation and the interpretation of indications provided by all the different manufacturers do not offer a systematic. user-friendly and standardized situation.

To illustrate this point, Table 2 presents a summary of the visible indications on the 17 blind-purchase of TVSSs, after producing their failure by applying a temporary overvoltage. In this table, it is postulated that for the typical consumer, ensuring protection of expensive equipment is preferable, even if it means that power is cut off for the equipment; in other words, maintaining continuity is undesirable.

There may be some applications where maintaining continuity would be the first choice. In either case, a clear indication of which state prevails should be clearly stated. From this table, it is apparent that the two possibilities — maintained continuity, or maintained protection — are offered by different manufacturers. However, the implications of this choice were not clearly stated on the package, and in two instances, the indications were in fact misleading. Hopefully, industry and standards-writing bodies will remedy this situation.

Without invoking a bureaucratic system of regulations, it would seem that a clear consensus among the manufacturers would make the informed end-user much more appreciative of the industry offerings, and provide enhanced safety for the public.

Conclusions

- A survey of the low-voltage SPD (TVSS) products currently on the market shows not only a variety of disconnector responses after a failure, but in some cases, false indication of the protection status.

- Information provided by several manufacturers, on the product pack(ICC (soon to he discarded after purchase by the end-user) or on the product itself fails to give unambiguous information on the status of load protection after failure of the SPD component.

- Anecdotal information indicates that devices currently on the market might not be provided with disconnector that meets the undefined but expected safety in failure modes. The second edition of UL 1449 is a very constructive step toward a remedy, although it does not address the question of status indication.

- This uncoordinated — not to say chaotic — situation clearly points to the need for accelerating the development of an industry-wide consensus on the design, operation. and interpretation of the indications of low-voltage SPD disconnectors.  Hopefully, this article will help the process.

Lingering Lead Length Legacies

in Surge-Protective Devices Applications

François D. Martzloff, Life Fellow, IEEE, and Kermit Phipps, Member IEEE

Abstract—Two experiments are reported to show how some lingering inherited misconceptions about the applications of surge-protective devices (SPDs) can lead to erroneous or cost-ineffective attempts to address the issue of lead length. The first experiment demonstrates the fallacy of the “four-terminal SPD” configuration if taken at face value without additional precautions on lead dress. The second experiment provides quantitative information on the actual effect of lead length. With this information, designers and installers can place the issue in a realistic perspective and avoid unnecessary effort.

I. INTRODUCTION

Many references found (inherited) in the literature imply that lead length is a significant factor to consider for correct installation and characterization of surge-protective devices (SPDs). This perception has led to the design of “four-terminal” one-port SPDs where the incoming power must be routed through the device terminals, rather than using an SPD with simple shunt connection with a pair of leads of unspecified length. connected at some point of the system. However, both perception and design miss the point that the problem is actually one of mutual inductance as well as “lead length.” It is indeed important to recognize that to achieve an optimum surge protection, connecting leads of SPDs should be as short as possible. Yet not only long lead lengths, but also significant loop area formed by the connecting leads, will add an inductive voltage to the protective voltage of the SPDs, degrading their performance. The perception was further complicated by concerns about the “speed of response” issue. After a brief review of some old issues, this paper reports the results of two experiments aimed at placing the lead length issue in the proper perspective.

II. HISTORICAL PERSPECTIVE

Concerns about the undesirable performance degradation of improperly installed surge-protective devices are not new. In the high-voltage arena, the concepts of “separation effects” and “connecting lead wires” have been recognized for more than a half-century (Witzke and Bliss, 1950 [11); (IEEE Std.C62.2~19872 [2]), and the recent IEC 61 643-12 (2002) [31 is a comprehensive guide for low-voltage applications.~ In the low-voltage arena, the situation has been complicated by misguided attention to the issue of “speed of response” and concerns about “overshoot” in the application of SPDs, fueled by debates about relative merits of emerging technologies such as metal-oxide varistors (MOVs) and silicon avalanche diodes (SADs). The debates on this issue were quite active soon after introduction of MOVs and SADs in the seventies. At that time, so many papers were published that any attempt to recite them entails a severe risk of offending the authors who might be overlooked in a list of references, so that we will not take that risk here. The debates have now abated although lingering perceptions or misperceptions remain.

For MOVs, a typical application manual published in the seventies [41 addressed both the issues of “speed of response” and “lead length” as illustrated by Figs. 1 and 2 (overleaf) excerpted from this manual. Other documents, such as IEEE Std. C62.33-l982 [5] attempted to place speed of response and overshoot in perspective and de-emphasize the issues, but were not entirely successful, to wit the claims for nanosecond response that still appear on the wrapping of some commercial SPD packages. Some justification for the emphasis on speed of response can be found in historical context, when interest was arising about ensuring protection against the nuclear electromagnetic pulse, and might still be valid for some military applications. In more mundane modern surge protection for today’s industrial, commercial, and residential ac power circuits, the perspective is different. Reality checks and economic considerations suggest that these concerns might be an overkill in surge protection for circuits where the propagation of fast surges is limited [61 and typical wiring practices do not allow the sophistication of perfect connections in those applications.

Therefore, in this paper we will not go beyond a brief review of the old issues of speed of response and overshoot, but will concentrate on discussing the lead length that seems to be the lingering and misunderstood issue.

A.  Speed of Response

For instance, Fig. 1 shows an oscillogram recorded to document the response to fast-rising pulses by an MOV disc inserted in the coaxial test fixture necessary to observe this sub-microsecond pulse without test connection artifacts [7]. Indeed, the experiment confirmed the claim of fast speed of response of the intrinsic MOV material, but practical devices are generally not fitted in coaxial packages—just what the tutorial experiment reported later in this paper did require.

B.	  Overshoot

In Fig. 1, one might consider that the “TRACE 2” indeed display an overshoot that may be significant when concerned with nanosecond response of an MOV. However, for this context of surge mitigation in ac power circuits, very short picosecond pulses such as that shown in Fig. 1, or the EFT pulse. defined in IEC 61 000-4-4 [8] and IEEE C62.41-1991 [91 have to travel only a few meters away from their origin to have their rise time and duration stretched into tens of nanoseconds or more [101.

Fig. 2 shows the test fixture arrangements and resulting performance for two current impulses with rise times, respectively, 8 s and 0.5 s [11]. These two rise times were not arbitrarily selected—our readers will readily recognize what became the IEEE Std. 587-1980 waveforms [12]. However, creating and injecting the 2.5-kA, 0.5-s pulse into the test circuit required great care, to avoid spurious signals, illustrating again that such conditions rarely, if ever, do occur in real-world situations [13]. The original figure caption of the GE Transient Manual included in Fig. 2 mentions both lead length and overshoot, a regrettable mention—with hindsight—because it focuses attention on lead length, which is not the direct cause of that “overshoot.”

The perceptive reader at that time might have noticed that the test fixture sketches in the figure correctly emphasized the issue of loop area, but the caption provided in the original 1978 figure is perhaps responsible for launching lead length legacies by focusing on lead length. Small wonder then, that so many lengthy debates and test specifications have been concerned with lead length rather than the direct effect of electromagnetic coupling between the two loops involved in an installation—the injected surge current loop and the protected equipment loop. Nevertheless, there is some redeeming tutorial value in that figure, which we will now briefly discuss.

C.  Electromagnetic Coupling Between Loops

In Fig. 2, it should be noted that the traces were superimposed by multiple exposures and are not synchronous, so no attempt should be made to correlate exactly the timing of the voltage and current traces. Nevertheless, the inductive coupling mechanism is apparent in that the maximum voltage occurs at the beginning of the current pulse (maximum di/dt). Observe the large “overshoot” on the right-side oscillogram for the 22-cm2 area loop and the more modest voltage for the 0.5-cm2 area loop. As further evidence, the amount of “overshoot” for the two traces disappears at the point of current peak (di/dt = 0); at that point, the voltage trace indicates the “true” level of the voltage limiting action of the MOV disc, free from spurious inductive effects.

In principle, the coupling aspect is simple, as illustrated in Fig. 3, which shows how the changing magnetic flux created by the flow of surge current in the circuit at left (Loop “A”) induces a voltage in the circuit at right (Loop “B”). Thus, the load that was expected to be protected at the limiting level of the SPD actually sees that limiting voltage augmented by the induced voltage, as shown by the waveforms drawn in Fig. 3.

IEC 61 643-12 [3] also addresses this effect in Annex K. Figure K-6 of that annex, redrawn here as Fig. 4, is similar to our Fig. 3, but is relegated to a distant annex. In contrast, the Fig. 10 of the IEC document (redrawn here as Fig. 5), is found in the main body under the heading of “Influence of the connecting lead length” (italics ours) and, thus, appears to support the four-terminal approach by designating it as “preferred scheme”—but does not qualify it with a discussion of the possible electromagnetic coupling.

Note also that this connection arrangement still falls under the category of “one-port SPD” because there is no impedance between the “input” and “output” terminals, as would be the case for a “two-port SPD.”4 So, the idea of “lead length” as a prime and perhaps sole factor lingers on into the 21st century. This situation is what motivated us to conduct the experiments reported in this paper.

To quantify the effect of electromagnetic coupling between the two loops, we conducted a first experiment using a specially-constructed coaxial SPD to be inserted in a well-defined configuration of the two loops—the incoming surge loop “A” and load loop “B” as defined in the schematic circuit representation of Fig. 3.

III. NEW EXPERIMENTS

The first experiment addresses the issue of the inductive coupling between adjacent loops, and the misleading perception that a four-terminal arrangement, such as that shown in Fig. 5, automatically circumvents the lead length issue.

The second experiment deals with the real issue of lead length for shunt-connected (“one port”) SPDs, and provides some quantitative information on the magnitude of the effect as determined by surge current parameters and, indeed, lead length.

A.  Coupling Between Adjacent Loops

For this demonstration, a “coaxial MOV” unit was constructed as shown on Fig. 6, allowing measurement of the “true” limiting voltage of the MOV without any significant inductive coupling. A 40-mm-diameter MOV disc was drilled at its center to allow connecting the core conductor of a coaxial cable to the top electrode, with the shield of the cable connected to the bottom electrode. Fig. 6 is a cross-section view of the device, which has complete rotational symmetry. A cap (cross hatch) is soldered to the top electrode and a sleeve (cross hatch) is soldered to the bottom electrode. Connections could be made at any point of the cap and of the sleeve; for the purpose of showing the device in a cross-section, terminal connections are represented on the left and on the right, but are at the same potential. According to the principle of the “four-terminal SPD,” the incoming power supply (presumed to include a surge) would be connected at the left of the device, and surge-free (or at least mitigated) power for the protected load would be available at the right of the device. The “true” MOV voltage resulting from a surge can then be observed at the end of the coaxial cable. This structure was only aimed at the demonstration, not as a practical low-voltage SPD, but was inspired by old discussions on how to make a distribution arrester consisting of three parallel-connected stacks of MOV discs arranged at 120° with the power take-off at the center of the triangle [14].

Using this special coaxial MOV, measurements were performed on several simplified configurations of lead geometry, including the so-called “four-terminal SPD” suggested by some authors and offered in some commercial packages. Fig. 7 shows the test circuit and definition of the terms “span” and “w” (width). The test circuit consists of two well-defined rectangular loops of conductors with the dimensions shown, mounted on a common sheet of insulating material. On the left, a loop in which the applied surge current is driven into the coaxial MOV; on the right, a loop representing the path of the power supply toward the protected load—in this case, the voltage input of a digital signal analyzer (DSA). The surge current imposed on the MOV (maintained at the same level for all the tests by keeping the same setting on the surge generator) is monitored by a current-viewing transducer and fed to a second channel of the DSA. Bonding the conductors of the two loops at “A” and “B” allows obtaining a configuration equivalent to that of a conventional two-terminal, one-port, shunt-connected SPD.

Figs. 8 and 9 (overleaf) show the results obtained with two different standard surge waveforms—the Ring Wave and the Combination Wave of C62.41-1991 [91 for fixed dimensions (1 m) of the surge loop (left square in Fig. 7), and a constant width (w = 1 m) but decreasing span of the measurement loop (right square in Fig. 7). Maximum decrease of the span would of course be accomplished by twisting the leads that go to the DSA, immediately from the point of attachment to the MOV.  And the ultimate minimum span is the coaxial cable output from the MOV.

The oscillograms of Fig. 8 (for the relatively high di/dt of a Ring Wave) show, from left to right, how the inductive voltage can be reduced by decreasing the “span” of the loop that feeds power (and the mitigated surge) to the load. For the first of the oscillograms (at left), the two loops have a portion of the circuit in common by bonding the two corners of the squares above (“A”) and below (“B”) the MOV, clearly the worst possible case, with a relatively large span representing a very poor lead arrangement.

The next oscillogram toward the right shows the case of the “improved” four-terminal SPD configuration: the resulting protective voltage is only reduced from 624 to 618 V (the three-digit values being read from the numerical display of the DSA, not from the oscillograms). That is hardly an improvement, and it is perhaps below the variability of the repeated surges and digitizing noise.5 This negligible difference between the two configurations demonstrates the fallacy of the four-terminal configuration if not accompanied by attention to the lead dress and resultant electromagnetic coupling, as can be seen in the oscillograms following these first two. Going on toward the right, the span is progressively decreased with corresponding decrease (improvement) of the protective voltage, until the ultimate (but impractical in the field) idealized configuration of the coaxial MOV with voltage read from the coaxial cable connection (zero span and zero loop width, w = 0).

The oscillograms of Fig. 9 show, for a Combination Wave, and from left to right, the worst case of a large inductive coupling (made equivalent to the common lead configuration by bonding the corners “A” and “B” of the square loops), the four-terminal coaxial MOV arrangement with a span of 1 m, and the measurement taken at the output of the coaxial cable.

With that gentler rate of rise (a fifth of that of the Ring Wave for the current levels injected in this experiment), the effect of inductive coupling is negligible. (The waveforms are quite similar, only the DSA-generated peak values overwritten in the oscillograms show a difference). Of course, if the amplitude of the surge current were higher, the effect of the inductive coupling would be higher. Because this inductive effect is linear, in comparison with the nonlinear voltage-limiting response of the MOV, it will become increasingly noticeable for higher surge currents. However, there is a limit to the di/dt rate of change that can be imposed at the sending end of a branch circuit, because the voltage necessary at the sending end for driving such a steep current toward an SPD at the far end would cause a flashover of the wiring devices in the service panel [15]).

B.	Shunt-Connected SPD Installations

The second experiment demonstrates the effect of installing a separate shunt-type SPD with long connections to a service panel. For practical situations, it is often postulated that the connecting leads can be represented by an inductance in the order of I RH/in, while the resistance of these leads can be neglected. A connection involving 30 cm of leads, a typical length for a careful installation of a shunt-connected SPD, could add several hundred volts to the limiting voltage achieved by the SPD itself in cases of high rates of current changes in the incoming surge.

SPDs packaged as power strips or plug-in inherently provide a two-port configuration on which the user has no control, but hopefully include internal wiring configuration that minimizes the lead effect. Furthermore, SPDs designed for integrated installation, such as a meter-base SPD or a panel plug-in SPD, offer a minimum of lead length, if the grounding lead is kept as short as possible (twisting leads to reduce the loop area or cancel the coupling is not a possible option in this case). On the other hand, in the case of separate SPDs permanently connected in shunt but located some distance from the point of connection, the length of that connection becomes quite significant, as our second experiment will show (nothing new about that), but also quantify.

Again, IEC 61643-12 provides useful information on this subject, but its Fig. 10-c (redrawn here as Fig. 10) only states that twisting leads is an acceptable alternative when the preferred four-terminal configuration (Fig. 5) is not possible. In our second experiment that we are about to describe, the connection of the SPD was made with the closely-spaced but not twisted pair of conductors encased in their plastic jacket. We did not attempt to twist the leads, being unaware of a potential significant reduction of inductance by twisting the closely-spaced pair (unlike sensitivity to external electromagnetic fields which, indeed, can be decreased by twisting leads). Instead, we went to another possibly greater reduction of inductance by using a coaxial cable connection, as we will describe later.

The experiment was conducted with a circuit as shown in Fig. 11, using a 20-m-long line of typical residential cable (2 + G conductors, plastic jacket, 2.5 mm2 or #12 AWG). The coaxial varistor was connected at the far end (right), and a Ring Wave was applied at the near end (left). With a constant generator setting and an unchanged line length, the surge current could be maintained at a constant amplitude and waveform, thus allowing direct comparison of the measured voltages. These voltages were measured for several distances “d” between the varistor and the point of connection of the probes. In an actual installation, this point of connection would be the service panel, and the cable length “d” between that point and the varistor would be the infamous “lead length” associated with a real-world installation. Fig. 12 (overleaf) shows the voltage measured for an ideal (but impractical) coaxial MOV, serving as baseline reference of the “true” limiting voltage, and the voltages measured for increasing values of the lead length.

Fig. 12 shows, from left to right, the voltages at the point of connection of the MOY (Vp) for increasing distances between this point of connection and the shunt-connected SPD, the idealized coaxial MOV in our experiment (upper trace). The lower traces document the constant value of the peak of the impinging surge current injected into the circuit. From left to right, compared to the baseline (d = 0) for a measurement made at the coaxial cable output of the MOV, the Vp caption shows the increase in the effective limiting voltage (decreased performance) that will be seen by the “protected” load. That increase is already 240 V for just 1rn of connecting leads and that type of impinging surge.

Some proposals have been made to decrease this adverse effect by using a coaxial cable to make the connection of the SPD package to the service panel. For the last oscillogram to the right of Fig. 12, a readily available 3-rn length of an RG8 coaxial cable replaced the last 3 m of the plastic-jacket cable. Interpolating the readings on plain cable for d = 2 m and d = 4 m yields 1150 V (for a 3-rn length of plastic jacketed cable), compared to the 960 V obtained for the coaxial cable connection. While this might be seen as a significant improvement, it might not be large enough to justify the costs or the complication of a coaxial cable lead that would have to be installed by an electrician unfamiliar with methods of connecting such coaxial cables within conventional wiring.

The experiments reported here were conducted using real wiring but contrived configurations to illustrate the points being made. The applied surges were delivered by a generator producing “textbook” C62.41 waveshapes. Being injected in an inductive circuit, the actual surge current had a rise time of about 0.8 s rather than the C62.41 value of 0.5 s. Close examination of the original laboratory (larger) current traces of Fig. 12 revealed an actual maximum rate of rise of about 290 A/s for a peak value of 220 A (about half the 500 A peak value of the Category B of C62.41). Such a rate of rise, applied to a connection of 1 m, and rule of thumb of 1 H/m for the cable inductance, should produce a voltage drop of about 290 V. The difference in the observed voltages in Fig. 12 for d = 0 its and d = 1 in is 240 V, not quite the 290 V computed with the rule of thumb inductance value. Given the wide range of real-world rates of rise, this difference between the experimental observations and the rule-of-thumb computation does not affect the conclusions on the order of magnitude of the effect.

In the previously cited paper [15], the “gentle toe” concept was brought up: the theoretical waveforms, such as those used in numerical computations, can produce unrealistic values for the maximum rate of rise at the instant of the surge initiation. In the real world, surge currents do not have their maximum rate of rise at t = 0, but only some brief time after. Another difference between theory and reality is that most practical Combination Wave surge generators have an “undershoot”—a reversal of polarity in the surge current—after the theoretical unidirectional impulse. This polarity reversal is further enhanced by the inductance of practical circuits, as opposed to the dead short postulated in the definition of the short-circuit current of the Combination Wave. Consequently, for modeling purposes, many researchers use a damped sine wave instead of the standard unidirectional wave (Hasse et al. [16]). However, this damped sine wave has its maximum di/dt at t = 0 (the derivative of the sine is a cosine); hence, the “gentle toe” idea to reconcile theory and reality.

For instance, Table I, first compiled in the cited paper [15], shows the maximum values of di/dt for three different nominal rise times of a damped sine wave with a 5 kA peak. It is noteworthy that the relationships are not linear, and that the maximum di/dt is greater than the value that one would obtain by simply dividing the rise time into the peak value, a fact that is sometimes overlooked in oversimplified discussions. These more realistic values of di/dt can then be combined with the empirical 1 H/m value of the connecting leads to estimate the degradation resulting from an excessive lead length.

IV. CONCLUSIONS

These experiments have clearly demonstrated that focusing exclusively on the “lead length” for SPD installations can lead to misconceptions or unwarranted expectations, such as the “four-terminal SPD” configuration. On the other hand, a quantitative assessment of the effect of long connections of a shunt-type device will provide useful guidance on installation practices.

1)	While there is merit in the concept of a four-terminal shunt SPD, the benefits can be greatly degraded if proper attention is not given to the lead configuration. Just using a four-terminal device will not ensure optimum performance.

- Improper installation of a separate shunt-type SPD via a “long” connecting cable to the service panel will degrade the performance in case of high rates of current changes in the impinging surge (in particular those implied for some commercial packages that propose ratings of tens of thousands of amperes). In the case of more moderate reasonable rates of change, this effect might have been somewhat overemphasized in the literature.

- Attention should be given to the lead configuration as well as to lead length. For instance:

•	For a separately-mounted one-port SPD, twisting the leads or using a coaxial cable between their point of connection to the protected circuit and the SPD package will reduce the inductive coupling but not greatly reduce the inductance of the connection. Lead length remains a significant factor.

•	For one-port SPD packages that are mounted inside or on the side of a panel, an arrangement that provides a minimum of lead length, twisting leads (if possible) will help reduce inductive coupling.

REFERENCES

[1]  R. L. Witzke and T. J. Bliss, “Coordination of lightning arrester location with transformer insulation level,” AIEE Trans., vol. 69, pp. 964 – 975, 1950.

[2]  IEEE Guide for the Application of Gapped Silicon-Carbide Arresters for Alternating-Current Systems, IEEE Std, C62.2, 1987.

[3]  IEC 61643-12(2002) Surge protective devices connected to low-voltage power distribution systems—Selection and application principles, 2002.

[4]  Transient Voltage Suppression Manual, 2nd ed. Auburn, NY: General Electric Company, 1978.

[5)  IEEE Standard Test Specifications for Varistor Surge-Protective Devices, IEEE Std. C62.33, 1982.

[6]  F. D. Martzloff and T. F. Leedy, “Electrical fast transients: applications and limitations,” IEEE Trans. Ind. Applicat,, pp. 151 – 159. Jan/Feb. 1990.

[7]  L. M. Levinson and H. Philipp, Personal communication and acknowledgment, (General Electric Corporate R&D) performed in the seventies the experiment that produced the oscillogram of Fig. 1, which was incorporated in the GE Transient Suppression Manual [4].

[8]  IEC 61000-4-4 (1995) Electromagnetic Compatibility—Part 4: Testing and measurement techniques—Section 4: Electrical fast transient burst immunity tests, 1995.

[9]  IEEE Recommended Practice on Surge Voltages in AC Power Circuits, IEEE Std. C62.4l, 1991.

[10] F. D. Martzloff and P. F. Wilson, “Fast transient tests—trivial or terminal pursuit?,” in Proc. 7th lot. Zurich Symp. Electromagnetic Compatibility, 1987.

[11] F. A. Fisher, “Overshoot—A Lead Effect in Varistor Characteristics,” General Electric Company, Schenectady, NY, Rep. 78CRD, 1978.

[12]	IEEE Guide for Surges Voltages in Low-Voltage AC Power Circuits, IEEE Std. 587, 1980.

[13]  F. A. Fisher, Personal communication and acknowledgment, (General Electric Corporate R&D) designed the test generator and performed in the seventies the experiment that produced the oscillograms of Fig. 2, which were incorporated in the GE Transient Suppression Manual [4].

[14]  R. E. Koch, “Power Line High Energy Surge Arrester for Application on a 14.4/24.9kV System,”, General Electric Rep. CCR-84-04, 1984.

[15]  A. Mansoor and F. D. Martzloff, “Driving high surge currents into long cables: More begets less,” IEEE Trans. Power Delivers’, vol. 12, pp. 1176—1183, July 1997.

[16]  P. Hasse, L. Wiesinger, P. Zahlmann, and W. Zischank, “Principle for an advanced coordination of surge protective devices in low voltage systems,” in Proc. 22nd  Int. Conf Lightning Protection, 1994.

## François Martzloff

END OF FILE “Text Protective Devices”

## April 2004