| # Last updated April 2004 | # Surge Protection Anthology Part 6 – Tutorials, Textbooks, and Reviews Text of “Site Surveys” files | # Surges Happen! |
| --- | --- | --- |

FOREWORD

This file contains the text part of the nine papers listed below:

- Power quality site surveys: Facts, fiction and fallacies (1988)

- Power quality measurements: Bringing order out of chaos (1988)

- Monitoring power quality (1988)

- Systems and instruments in site surveys (1990)

- No joules for surges: Relevant and realistic assessment of surge stress threats (1986)

- Surge recordings that make sense:  Shifting focus from voltage to current measurements (1996)

- Surge recordings that make sense: Joule deposition: Yes.  “Joule content”: Never ! (1997)

- The fallacy of monitoring surge voltages: SPDs and PCs galore! (1999)

- Some enlightening case histories on lightning damage (2000)

This file is formatted as MS Word, allowing you to do a search for keywords, but it does not support graphics as it was derived from an OCR scan of hard-copy archives.  However, should you wish to examine the complete original format, each page in this file has an identifying header and footer that contain a hyperlink to the pdf file for the document being displayed on that page, regardless of the font size that you select for optimum viewing.  These headers and footers and hyperlinks become accessible when you select the “Print Layout” in the “View” mode.

Best wishes and good browsing !

Power Quality Site Surveys:  Facts, Fiction, and Fallacies

Francois D. Martzloff, Fellow, IEEE, and Thomas M. Gruzs, Member, IEEE

Abstract – The quality of the power supplied to sensitive electronic equipment is an important issue.  Monitoring disturbances of the power supply has been the objective of various site surveys, but results often appear to be instrument-dependent or site-dependent, making comparisons difficult.  After a review of the origins and types of disturbances, the types of monitoring instruments are described.  A summary of nine published surveys reported in the last 20 years is presented, and a close examination of underlying assumptions allows meaningful comparisons which can reconcile some of the differences.  Finally, the paper makes an appeal for improved definitions and applications in the use of monitoring instruments.

#### INTRODUCTION

Site surveys are generally initiated to evaluate the quality of the power available at a specific location with the aim of avoiding equipment disturbances in a planned installation or of explaining (and correcting) disturbances in an existing installation.  In either case, survey results constitute one of the inputs in the decision-making process of providing supplementary line conditioning equipment, either before or after disturbances have become a problem.  Depending on the reliability requirements of the load equipment, its susceptibility, and the severity of the disturbances, various line conditioning methods have been proposed: surge suppressor (with or without filter), isolating transformer, voltage regulator, magnetic synthesizer, motor-generator set, or uninterruptible power supply (UPS).

Because this additional line conditioning equipment may require significant capital investment, the choice of corrective measures is generally made by economic trade-off which is the prerogative and responsibility of the end user.  However, if technical inputs to this trade-off are incorrect because erroneous conclusions were drawn as a result of a faulty site survey, the whole process is worthless, or worse yet, misleading.

For this reason, a good understanding of the merits and limitations of site surveys is essential for reconciling expectation with reality before expensive line conditioning equipment is called for; one should deal, not with fiction or fallacies, but with facts.

Power disturbances that affect sensitive electronic loads have a variety of sources.  Lightning, utility switching, and utility outages are often-cited sources of power disturbances.  However, power disturbances are often caused by users themselves, through switching of loads, ground faults, or normal operation of equipment.  Computer systems, as one example of these so-called sensitive loads, are not only sensitive loads but also can generate some disturbances themselves.  Their nonlinear load characteristics can cause interactions with the power system such as unusual voltage drops, overloaded neutral conductors, or distortion of the line voltage.

Utility systems are designed to provide reliable bulk power.  However, it is not feasible for them to provide continuous power of the quality required for a completely undisturbed computer operation.  Because normal use of electricity generates disturbances and because unexpected power system failures will occur, every site will experience some power disturbances.  The nature of these power disturbances, their severity, and their incidence rates will vary from site to site.

To place the problem in perspective, however, one should keep in mind that poor-quality power is only one of the many causes of computer downtime.  Hardware problems, software problems, and operator errors also contribute to computer downtime.

Sometimes there is too great a tendency to attribute operational difficulties to power supply problems.  For example, studying power-related computer problems at U.S. Navy installations, Key [1] found that only 5 to 10 percent of the observed computer downtime was attributable to power problems.  Reviewing case histories, Martzloff [2] described a safety problem created by panic actions of the computer system operators who pulled out power cords of the remote terminals (including the safety grounding conductor) because they suspected power line surges when, in fact, the problem was incorrect grounding practices for the shields of the data lines.

Historically, transient overvoltage effects on novel semiconductor systems were the first concern; by now, the importance of undervoltages or loss of power has also been recognized.  In the nine surveys reviewed in this paper, four address all types of disturbances and five are concerned exclusively with the transient overvoltages.  While this review is mostly concerned with the reports of transient overvoltages, this limited discussion does not mean that other disturbances are less significant.

Power quality surveys have been performed, reported, and discussed by many authors, but their results or conclusions are not consistent [3]-[14].  Quotations from these surveys, out of context, have perhaps also contributed to the confusion.  In an attempt to clarify the issues, this paper presents a brief review of the origins and definitions of disturbances, and then it describes the development of monitoring instruments.  Comparisons are made among nine published surveys with attempts at reconciling results.  Finally, an appeal is made for improved measurement methods to provide more consistent reporting of recorded power disturbances.

#### DEFINITION DEFICIENCIES

As will become painfully apparent in the review of site surveys, the terms used by the workers reporting their measurements do not have common definitions.  An effort is being made within the IEEE to resolve this problem, as described later in this paper, but consensus has yet to be reached.  In this paper, terms describing disturbances are consistent with the IEEE Standard Dictionary of Electrical and Electronics Terms [15] and with established usage within the community of surge protective devices engineers.  Two examples of this lack of consensus are described here to make the point; resolving them is beyond the scope of this paper.

The generally accepted meaning of surge voltage, in the context of power systems, is a short-duration overvoltage, typically less than 1 ms or less than one half-cycle of the power frequency.  This meaning is not that which has been established by manufacturers and users of monitoring instruments and line conditioners.  This unfortunate second meaning is a momentary overvoltage at the fundamental frequency with a duration of typically a few cycles.  In this paper, this second meaning of the word "surge" (a momentary overvoltage) will be signaled by the use of quotation marks.  What the surge protective devices engineers call surge is called "impulse" or "spike" by the monitoring instrument community.  Fig.  1 shows by graphic descriptions the confusion created by the dual meaning of the word surge.  Acknowledging the desire of users for terse labels, we propose for consideration the word "swell" instead of "surge" for a momentary overvoltage.

## Figure 1 – Graphic definitions of disturbances

The term "outage" is another example of confusion created by unsettled definitions.  Most users agreed that it meant a complete loss of line voltage, but the duration of this outage was quite different when it was defined by computer users (as short as one half-cycle) or power engineers (seconds, perhaps minutes).  Now, the users and manufacturers of line conditioners do not make a clear distinction between complete loss of line voltage (zero voltage condition), severe undervoltages ("deep sags"), or the single-phasing of polyphase power systems.  For example, a momentary flicker of fluorescent lighting caused by a brief loss of voltage might be considered an outage; however, a brief sag to less than 80 percent of nominal voltage will produce the same visible effect.  Some UPS manufacturers consider input voltage sags that cause transfer to the battery backup operation as outages.  Part of the problem may be that the definition of "outage" has regulatory implications for evaluating the performance of public utility companies.  No such distinction has been made in this paper, because taking sides on that issue is not within its scope.

The term "sag" has not yet been defined in the IEEE Dictionary, but it is now generally accepted as meaning a momentary voltage reduction at the ac power frequency.  However, details (threshold, duration, etc.) of what characterizes a sag are not well defined.

#### MOTIVATION FOR SITE SURVEYS

Protection from power disturbances now essential because increasing dependency on computer-based systems for industry, commerce, and consumers makes disruptions less and less acceptable.  The most visible indication of power disturbances is the occurrence of operational problems such as hardware damage, system crashes, and processing errors.

Some users of computer systems may accept, albeit reluctantly, operational problems because they see them as unavoidable.  Other users may be unaware that otherwise invisible power disturbances could be the cause of operational problems.  A single power disturbance can cost more in downtime and hardware damage than the investment in power protection that would have prevented the disturbance; almost all sites could benefit from a reduction of operational problems by improving the quality of the power supplied to the computer systems [13].

Power line monitoring with sophisticated power disturbance recorders has often been advocated as a way to determine if any line conditioning is required.  While monitoring appears to be a logical first step, it has limitations.  For example, severe disturbances occur infrequently or on a seasonal basis.  Therefore, monitoring periods of less than a year might not produce an accurate power disturbance profile; most users are unwilling to wait at least 1 year.  Also, power line monitoring produces only past performance information, for changes within the site, at neighboring sites, or by the utility can drastically alter the power disturbance profile.

While exact prediction of the disturbances to be expected at a specific location is almost impossible and attempting it would be a fallacy, general guidelines can be formulated.  An attempt has been made by standards-writing groups to provide guidance [16] or specifications reflecting expected disturbances [17]-[19].  Users, however, generally seek specific data for their particular case; hence site surveys will still be necessary.

Another fallacy would be to attempt correction of power line disturbances revealed by monitoring and then to expect operational problems of equipment to disappear without having first determined the exact susceptibility of the equipment.

#### CAUSES OF POWER LINE DISTURBANCES

Transient overvoltages, historically among the first disturbances to be recorded by users, have two major causes: lightning and load switching.  Depending on local conditions one can be more important than the other, but both need to be recognized.

Lightning surges are the result of direct hits to the power system conductors as well as the result of indirect effects, where the lightning bolt strikes an object close to the conductors but not the conductors themselves.  A lightning strike to the power system may cause the operation of gap-type surge arresters, producing a severe reduction or a complete loss of the power system voltage for one half-cycle.  A flashover of line insulators can cause a breaker to trip, with reclosing delayed by several cycles, causing a power outage.  Thus lightning can be the obvious cause of overvoltages near its point of impact but also a less obvious cause of voltage loss or sag at a considerable distance from its point of impact.  This latter effect has been clearly observed in the Goldstein-Speranza [8] study.

Power system load switching is also a major cause of disturbances.  Switching large loads on or off can produce long-duration voltage changes beyond the immediate transient response of the circuit.  Whether the switching is done by the utility or by the user is immaterial from the technical point of view, although the responsibility may be the subject of a contractual dispute.  When power factor correction capacitors are switched, high-frequency (500 Hz-5 kHz) oscillations occur which can reach 120-percent overvoltages (2.2 pu) for milliseconds [20]. Fault clearing by current-limiting fuses can also create substantial overvoltages [21].

In a study of 100 computer system failures attributable to power supply disturbances, Key [1] considered power line monitoring, computer operation logs, data from the National Weather Service, and local utility data to determine the cause of the power disturbance (Fig. 2). Weather was cited as the major cause of disruptive sags and outages; sags were found to disrupt computer operations four times as often as outages, a finding that agrees with the results of the comparison between the Allen-Segall and Goldstein-Speranza studies discussed later.

## Figure 2 – Causes of computer failures as reported in the Key study

The type of power distribution system also has a strong influence on the incidence of disturbances.  In his study, Key compared the rates of incidence of sags and outages (Fig. 3).  A similar analysis was performed by Allen and Segall in another study [22], reaching essentially the same conclusions.  Both studies found that the rate of occurrence of disturbances is significantly lower for underground and network systems than for overhead and radial systems, respectively.

## Figure 3 – Effect of power distribution system configuration

on incidence of disturbances as reported in the Key study

#### TYPES OF DISTURBANCES

Power line disturbances can be classified into two categories: common mode disturbances and normal mode disturbances.  The two terms were first defined in the context of communication circuits; a recent IEEE Guide [23] has established an expanded definition which is used in this paper, as outlined in the following paragraphs.  The IEEE Dictionary [15] and the IEC Dictionary [24] define symmetrical and asymmetrical voltages akin to but not interchangeable with the definitions of normal mode and common mode, respectively.

#### Common Mode Disturbances

Common mode disturbances are defined as unwanted potential differences between any or all current-carrying conductors and the grounding conductor or earth.  In three-phase grounded-wye power supplies typical of large computer systems, common mode disturbances could also be defined as the potential difference between neutral and ground.

Two different types of common mode disturbances can affect a sensitive load.  The first type is a disturbance on the input power conductors relative to the input power grounding conductor.  Fig. 4 shows in 1 and 2 examples of origins for these disturbances.  This type of disturbance can be limited somewhat by a line conditioner, but it is also influenced by the location of the line conditioner and the wiring practices.

Figure 4 – Three examples of the origin of common mode disturbance on power input

Figure 5 – Three examples of the origin of normal mode disturbance on power input

The second type is a ground potential difference between elements of the computer or remote peripherals connected to the computer.  Fig. 4 shows in 3 an example of this type.  This type of disturbance is more difficult to limit because it is influenced by factors such as the system configuration and the impedance of the grounding system.  These two factors are generally beyond the direct control of the user except in the construction of a new facility.

Because of the broad frequency band involved, wiring resonances can make equalizing ground potentials difficult.  Proper computer system grounding, including a signal reference grid, has been found to be effective against most common mode disturbances [25].  However, when remote elements are connected to the computer systems by data cables, large ground potential differences are possible.  Proper surge protection of the power supply and proper grounding of data cables will help eliminate hardware damage but might not prevent data corruption.  When dealing with the situation of example 3 in Fig. 4, fiber optic links are very effective because they provide complete metallic separation of the various elements in the system, a separation that might not be sufficiently achieved by the discrete opto-isolation devices sometimes proposed for that function [2].

#### Normal Mode Disturbances

Normal mode disturbances are defined as unwanted potential differences between any two current-carrying circuit conductors.  Fig. 5 shows three examples of the origins of such disturbances.  Usually a sine wave of nominal voltage is desired for a computer power supply.  Any deviation from this sine wave is a normal mode disturbance.  Computer users and monitoring instruments designers characterize these disturbances by a variety of terms not always clearly defined such as sags, surges ("swells"), outages, impulses, ringing transients, waveform distortion, and high-frequency noise.  Unfortunately, there is no consensus at the present time on the exact meaning of these terms and their underlying quantitative definitions such as amplitude, duration, and thresholds, Later in this paper, a new effort to remedy this situation is described.

#### HISTORY OF THE DEVELOPMENT OF DISTURBANCE MONITORS

Historically, the first (unintended) disturbance monitors were the actual load equipment; only later, when confronted with unexplained failures or malfunctions, did the users start monitoring the quality of their power systems.  Monitoring power quality at the fundamental frequency had long been performed by utilities, but the precise characterization of microsecond-duration surges in the early 1960's required special oscilloscopes.  For the next 15 years, combinations of oscilloscopes or simple peak-detecting circuits were the basic instruments for monitoring transient overvoltages.  In the 1970's commercially-produced digitizers became available, and the technology has made continuing progress as experience has been accumulated and faster digitizing circuits have been developed.

Early site surveys were generally limited to voltage measurements in the normal mode.  This limited scope reflected concerns for damage to sensitive electronic components connected across the line.  The fact that the source impedance of the surge was not recognized as being important in these surveys led to the generation of some performance standards that do not specify the current-handling requirements for the surge protective devices [19].  With the introduction and widespread application of clamping protective devices (silicon avalanche diodes or metal oxide varistors), the surge current diverted through these devices became a very important factor for proper device selection.

Therefore, the need emerged for characterizing current as well as voltage surges, but few surveys to date have addressed this need.  This need offers a challenge to designers of monitoring instruments and to would-be surveyors.

This challenge has produced attempts to define an "energy" measurement with an instrument which is only a voltmeter.  By assigning a parametric value to the source impedance of the surges and integrating the product (volts)2-seconds of the surges, some knowledge on the energy involved would be obtained as suggested in [14].  However, the real question concerns the sharing of energy between the impedance of the source and the impedance of the load, in this case the nonlinear impedance of the protective device.  A lengthy discussion of the energy contained in the surge versus the energy delivered to the protective device is beyond the scope of this paper, but the difference needs to be recognized to prevent further confusion as future monitoring instruments include an "energy" parameter in their readouts.

With the present development of sophisticated multichannel digitizing instruments, it should be feasible in future surveys to monitor both voltage and current in the normal mode as well as in the common mode.  Note, however, that the current of interest is that which the surge source (of otherwise unknown impedance) would force through a proposed surge protective device.  This device would he shunt-connected at the point being monitored so that the current to be monitored is not the surge current in the direction of undefined downstream loads.  The amplitude as well as the waveform of the surges needs to be characterized for correct application of surge protective devices.  Peak-reading monitors provide useful information on surge activity at a given site, but assessment of the surge severity level for the proper sizing of protective devices requires waveform and source impedance information [20], [26].

Recent monitoring instruments offer the capability of recording potential differences between the neutral and the grounding conductor which constitutes one form of common mode disturbances.  To our knowledge, no instrument has been offered for explicit monitoring of potential differences within the grounding system itself such as 1 and 2 in Fig. 4. Some types of monitors include current probes and could record current in grounding conductors, but this parameter has not yet been reported in published surveys.

One difficulty encountered by users of monitoring instruments in this fast-paced technology is that manufacturers introduce improved features in response to specific wishes of the users or as a result of their own research; data collected by different instruments become equipment-dependent.  While this continuing progress is a welcome development, it makes comparison of survey results difficult without the details on the instrument characteristics and methods of measurement.

Occasionally, an instrument might have limitations or might introduce artifacts which are not immediately apparent so that the survey results suffer some loss of credibility when these possible limitations are discovered [11], [12].  Users may also have difficulty in interpreting complex instrument outputs, and excessive simplification of a complex data base can lead to some misunderstanding or misapplication of published documents; a tutorial effort is then necessary to avoid these pitfalls [27], [28].

#### TYPES OF MONITORS

The instruments used in the various surveys reflect technology progress as well as logistics constraints resulting in a diversity of approaches.  Nevertheless, all monitoring instruments used in past surveys were voltmeters (with one exception, combining voltage and current measurements) from which disturbance parameters were derived.  Some of the monitors recorded a single parameter such as the actual voltage peak or the fact that the voltage exceeded a preset threshold.  Other monitors combined time with voltage measurements describing voltage waveforms.  The recording functions of instruments used in the surveys may be classified in broad categories.

Threshold counters-The surge is applied to a calibrated voltage divider, triggering a counter each time a preset threshold is exceeded.  The early types were analog; more recent types are digital.

Digital peak recorders-The surge is converted to a digital value which is recorded in a buffer memory for later playback or printed out immediately after it occurs.  In the early types of recorders, only the peak was recorded; in later types, the duration of the surge was also recorded, opening the way to the more complex digital waveform recorders now available.

Oscilloscope with camera-The surge triggers a single sweep on the CRT of the oscilloscope which is recorded as it occurs by a shutterless camera with automatic film advance.  The oscilloscopes available at that time (the early 1960's) did not allow differential measurements.

Screen storage oscilloscope-The surge is displayed and stored on the cathode ray tube.  The writing-speed capability of these oscilloscopes was a limitation in the late 1960's.

Digital storage oscilloscope-The surge is digitized and stored in a shift register for subsequent playback and display whenever a preset threshold is exceeded.  An important feature is the capability of displaying events prior to the beginning of the surge.

Digital waveform recorder-The surge is digitized and stored in a manner similar to the digital storage oscilloscope, but additional data processing functions are incorporated in the instrument, allowing reports of many different parameters of the disturbance relating voltage to time.

Although some surveys might aim at great accuracy, the real world experiences such an infinite variety of disturbances that any attempt to describe them in fine detail only restricts general usefulness of the data.  Seeking such fine and definitive detail is another fallacy.  Some simple instruments can be considered useful (and inexpensive) indicators of frequent disturbances; other, more sophisticated (and more expensive) instruments can provide quite comprehensive data on disturbances (but only on past events from which future disturbances can be extrapolated only by assuming that the causes will remain unchanged).  Thus there is a practical limit to the amount of detail that a survey can yield, and unrealistic expectations of very precise information should be avoided.

Before attempting yet another broad survey of power quality, would-be surveyors need to consider not only improvements in instrumentation but also changes that have occurred in modern power systems, in particular the proliferation of surge protective devices.  These two differences between earlier surveys and the more recent surveys should be kept in mind when comparing results and when planning future surveys.

Prior to the proliferation of surge protective devices in low-voltage' systems, a limitation had already been recognized [17] for peak voltages: the flashover of clearances, typically between 2 and 8 kV for low-voltage wiring devices.  For that reason the expected maximum value cited in the IEEE Guide on Surge Voltages [16] reflects this possible truncation of the distribution around 6 kV.  Unfortunately, some readers of this Guide interpreted the upper practical limit of 6 kV as the basis for a withstand requirement, and they have included a 6-kV test requirement in their performance specifications.  A new version of this Guide, currently under preparation as a Recommended Practice, will attempt to avoid this misinterpretation.

The number of surge protective devices such as varistors used in the United States on low-voltage ac power circuits since their introduction in 1972 may be estimated at 500 million.  Therefore, a new limitation exists in the voltage surges that will be recorded.  A surge-recording instrument installed at a random location might be close to a varistor connected near the point being monitored.  Such a proximity of surge protective devices and recording instruments may impact present and future measurements in several ways, as contrasted to previous measurement campaigns.  Four are outlined below.

1)	Locations where voltage surges were previously identified-assuming no change in the source of the surges-are now likely to experience lower voltage surges, while current surges will occur in the newly installed protective devices.

2)	Not only will the peaks of the observed voltages be changed, but also their waveforms will be affected by the presence of nearby varistors as illustrated in Figs. 6, 7, and 8.

A)	If a varistor is located between the source of the surge and the recording instrument (Fig. 6), the instrument will record the clamping voltage of the varistor.  This voltage will have lower peaks but longer time to half-peak than the original surge.

## Figure 6 – Varistor upstream of monitor

## Figure 7 – Varistor downstream of recorder

## Figure 8 – Voltages measured at beginning and end of 75-m branch circuit

for surge applied in normal mode at service entrance

B)	If the instrument is located between the source of  the surge and a varistor, or if a parallel branch circuit contains a varistor (Fig. 7), the instrument will now record the clamping voltage of the varistor, preceded by a spike corresponding to the inductive drop in the line feeding the surge current to the varistor.

TABLE 1

DETAILS OF THE LOCALES AND INSTRUMENTATION

C)	If a varistor is connected between the line and neutral conductors, and the surge is impinging between line and neutral at the service entrance (normal mode), a new situation is created, as shown in Fig. 8. The line-to-neutral voltage is clamped as intended; however, the inductive drop in the neutral conductor returning the surge current to the service entrance produces a surge voltage between the neutral and the grounding conductors at the point of connection of the varistor and any downstream point supplied by the same neutral.  Because this surge has a short duration, it will be enhanced by the open-end transmission line effect between the neutral and grounding conductors [29].

3)	The surge voltage limitation function previously performed by flashover of clearances is now more likely to be assumed by the new surge protective devices that are constantly being added to the systems.

- These three situations will produce a significant reduction in the mean of voltage surge recordings from the total population of different locations as more and more varistors are installed.  However, the upper limit will remain the same for locations where no varistors have been installed.  Focusing on the mean of voltage surges recorded in power systems can create a false sense of security and an incorrect description of the environment.  Furthermore, the need for adequate surge current handling capability of a proposed suppressor with lower clamping voltage might be underestimated because some diversion is already being performed.

#### REVIEW OF PUBLISHED SURVEYS

This summary includes nine papers published in the United States and in Europe, with a brief description of instrumentation design, definition of parameters, and results.  Papers are listed in chronological order.

Table I shows details of the locale, system voltage, instrument type, and connection mode as described in the papers.  Other surveys may have been published, particularly in Europe, which did not come to the attention of the authors.  Suggestions for including additional published data in the revision process for the Guide on Surge Voltages [16] are invited.

Bull and Nethercot, in a 1964 article [3], report monitoring performed in the mid 1960's on 240-V systems in Great Britain with instruments of their design.  Their initial instrument used vacuum tubes, leading to the development of a solid-state circuit which may be considered the forerunner of modern monitors.  The instrument had several channels, each with a different threshold.  Eventually, the solid-state instrument was made available commercially, and several units were used in some of the monitoring performed in the United States and reported in the data base of [16].

The monitoring locations were selected to include a variety of conditions, with data being collected for several weeks at each location over a total period of 2 years.  The results do not mention transients above 600 V; it seems that no channels were provided above that level because the authors were only concerned with the range of 50-600 V.

Martzloff and Hahn, in a 1970 paper [5], report the highlights of measurements made in the 1963 to 1967 period on residential, commercial, and industrial circuits, mostly single-phase 120 V. Further details, originally held proprietary, were eventually released [30] for sharing information with other interested parties.  Waveform data were obtained with commercial, custom-modified oscilloscopes fitted with motor-driven cameras.  These oscilloscopes were installed at various locations where transient activity was suspected.  In addition, a peak counter circuit was developed, and 90 units with a 1200- or a 2000-V threshold were deployed at 300 locations where there was no prior suspicion of unusual transient activity.

The oscilloscope data gave one of the first indications that the traditional unidirectional impulse, long used for dielectric testing, might not be representative of surges occurring in low-voltage circuits.  The threshold data indicated locations where surges above 1200 V occur frequently (about 3 percent of the sample), while other locations appear far less exposed to surges.  The 100:1 reduction of an alarming failure rate of clock motors, achieved by increasing the surge withstand capability of the motors from 2000 to 6000 V, is documented in that paper.

Cannova, in a 1972 paper [6], reports the monitoring of surges on U.S. Navy shipboard 120- and 450-V power systems in the late 1960's.  Instrumentation used for the initial phase of the monitoring program consisted of oscilloscopes similar to those used by Martzloff.  Provision was also included for the option of measuring the transients alone (through filters) or superimposed on the ac line voltage; this option reflects the old dichotomy, still unsettled to this day, as to whether the transients should be measured as an absolute value or as a deviation from the instantaneous value of the ac sine wave (see the surge and impulse descriptions in Fig. 1, and the last column of Table 1).

The results are not reported separately for 120- and 450-V systems, it is not possible to express them in terms of per-unit or percentage of nominal system voltage.  The statistical treatment aims at fitting the recorded transients to a normal distribution and concludes that a log normal distribution is a better fit.  A brief statement is made on the durations of the recorded transients (without a statement on how those durations are defined), citing a majority of durations between 4 s and 6 s, with a few at 19 s.

From the data base, acknowledged to be a small total number of events, a voltage protection level of 2500 V was defined.  The specification of a 2500-V 1.2/50-s voltage withstand by DOD STD 1399 was derived from this survey.

Two aspects of the conclusions are especially worth noting: 1)  there was no information on the source impedance of the surges, and yet the data eventually served to specify requirements for surge protective devices; and 2) a large difference in frequency of occurrence was noted among ships of the same type and class, similar to the observations on land surveys.

Allen and Segall, in a 1974 paper [7], report the monitoring of several types of power disturbances at computer sites, performed with oscilloscopes, oscillographs, and digital instruments, in the 1969-1972 period.  Details of the instrumentation were described in a separate paper [31].  Disturbances are described as overvoltages and undervoltages, oscillatory decaying disturbances, voltage spike disturbances, and outages.  The terms sag and "surge" ("swell") had not yet made their appearance in the jargon.

The survey was conducted in two phases.  In a first phase, preliminary information was obtained on ranges of disturbances, leading to the development of a second generation of monitors deployed in the next phase.  The recorded disturbances are described by plots and histograms.  The highest surge recorded in the first phase is shown as 350 V. In the second phase, the monitors grouped all surges into three categories, the highest having a range of 100 percent (of line voltage) to infinity, so that no detailed information is provided to describe high peak values.  The survey does report in detail the occurrence of undervoltages and overvoltages, providing a basis for the comparisons with the Goldstein-Speranza study made later in the present paper.

Goldstein and Speranza, in a 1982 paper [8], report the monitoring of several types of disturbances at a variety of locations in the Bell System, with digital multiparameter instruments, in the 1977 and 1979 period.  The conditions of the survey are documented, including instrument locations and definitions of the parameters as well as the methods of data processing.

The findings are briefly reported with emphasis on predictions for disturbances expected at specific sites.  The prediction is obtained by using a statistical model derived for all sites and making adjustments reflecting specific site conditions determined by a limited survey at that site.  The authors are emphatic on the point that the lack of correlation between sites prevents blanket application of the overall findings to any specific site, but that useful predictions are possible by combining the overall data with limited knowledge on specific site data.  This concept is echoed in the Guide on Surge Voltages [I 6], where the frequency of occurrence is presented in graphic form with well-defined slopes but with a wide band of possible exposures, depending on the particulars of the site.

A Polya distribution is identified by Goldstein and Speranza as the best fit for this type of rare events data, in contrast to other surveys where their authors attempted to fit a normal distribution or a power or exponential law profile.

Wernstrom, Broms, and Boberg, in a 1984 report published in Sweden and circulated in the United States as an English draft translation [10], report monitoring of industrial 220/380-V systems by digital multi-threshold instruments, corroborated by waveform recording with digital storage oscilloscopes.  The parameters to be recorded and reported are defined in an introductory section; however, their description of "common mode" and "differential mode" in the English translation does not correspond exactly to symmetrical and asymmetrical voltages defined by the IEC.

In the section discussing transient sources and propagation, they make a significant comment that "common mode voltages are the most interesting and at the same time are the voltages most difficult to defend against."

The range of surges recorded extends from 200 to 2000 V. In a summary tabulation, rise times are shown as ranging from 20 to 200 ns and duration from 0.2 to 2.5 s.  An interesting additional measurement was made by simultaneous recordings at two distant points of the power system, showing some aspects of the propagation and attenuation of a surge.  The survey also shows a wide difference of surge activity among sites but a relatively constant slope of the rate of occurrence versus level.

Aspnes, Evans, and Merritt, in a 1985 paper [11], report a survey of the power quality of rural Alaska at isolated power generation facilities.  The monitoring instruments are identified as one of the contemporary commercial digitizing monitors.  A very comprehensive summary of the recordings is presented including frequency deviations (a unique situation in these isolated systems), sags and "surges" ("swells"), impulses (i.e., surges), and outages.

Because the sites were in isolated systems (their installed capacity or system impedance is not stated), one would expect differences from the typical survey of interconnected power systems.  In fact suspected differences were the motivation for conducting the survey.  Thus finding differences in the results would not be particularly meaningful from the point of view of this paper aiming at comparisons.  However, bringing up this survey serves the purpose of noting that some ambiguity surfaced in connection with the possibility that built-in surge protection in the monitors might have attenuated the surges being recorded.  Knowing the source impedance of the surges (not the impedance at power frequency) would have settled the issue.  This case history point out again the desirability of including surge current monitoring in future surveys as a method of characterizing the source impedance of the surges.

Odenberg and Braskich, in a 1985 paper [12], report the monitoring of computer and industrial environments with a digital instrument capable of the simultaneous recording of voltage surges and current surges.  This new capability for relating voltage and current shows a growing awareness of the need to monitor current surges-an improvement over previous surveys limited to the measurement of voltages.  However, the reported surge currents are those of a current toward undefined loads downstream from the instrument; they do not include any measurement of the current through a shunt-connected surge diverter, a measurement that would have provided new information on the source impedance of the surges.

The digital processing applied by the instrument yields two points of the surge: the peak value with the time to reach peak and the time elapsed until decay to 50 percent of the peak value.  From these two points, a "waveform" description is proposed without any other information on the actual waveform.  From a large number of recorded surges (over 250 000 events) a startling finding is cited: 90 percent of the recorded surges have their 50-percent point in a narrow window of 900-1100 s.  Attempts to reconcile this singular finding with the observations reported by other surveys have not been successful.

Goedbloed, in a 1987 paper [14], describes in detail a custom-built automated measurement system monitoring 220/ 380-V networks in Europe.  The automated measurement system reflects the progress made in digitizing techniques since the Bull-Nethercot days of vacuum tubes.  By combining two commercial recorders with a custom interface, the developers obtained detailed recordings with a 10-ns sampling interval and 20-uus window on the first recorder and a ]-[is sampling interval and 2-ms window for the second recorder.

The system included a provision for automated data reduction, yielding raw data as well as statistical information on amplitude, rate of rise, energy measure, spectral density, and conversions from time domain to frequency domain.  With a relatively low threshold of 100 V above the line voltage, the distribution of occurrences is weighted toward low amplitudes; nevertheless, occurrences are reported above 3000 V.

The paper also addresses indirectly the question of normal mode versus common mode surges by discussing symmetrical voltage and asymmetrical voltage as defined in the IEC Dictionary [24].  An indirect definition is proposed for a third type identified as the "so-called non-symmetrical voltage" which was the mode of monitoring used in this survey: line to grounding conductor (called "protective earth" or "protective conductor" in Europe).  This third type is currently incorporated in the more general definition of common mode proposed by the IEEE Guide on Surge Testing, which might leave some ambiguity on the definitions (see Fig. 5), or lead to considering "pure common mode" as opposed to some combined mode in which both normal and common (pure) modes are combined.  Looking for guidance in IEC definitions does not help much; the IEC definition addresses delta networks, but the Goedbloed paper states that nearly all networks monitored were of the TN type-that is, phase, neutral (implying a wye), and protective-earth conductors.  The paper clearly states the mode of connection so there is no ambiguity, but this instance serves again to illustrate the need to harmonize definitions. [Footnote: A related issue, now being addressed but not yet resolved, is the effect produced on the amplitudes of common mode surges by different practices for grounding the neutral (at the service entrance or at the remote substation).  Comments are invited on this aspect of characterizing the environment.]

#### COMPARISONS AMONG SURVEYS

Relative Occurrence of Different Types of Disturbances

Two of the surveys reviewed in this paper have been widely cited, one performed in the early 1970's by Allen and Segall (A-S for short) [7], and the other performed in the late 1970's by Goldstein and Speranza (G-S) [8].  However, the findings do not a first appear to be in agreement; a detailed comparison of these two surveys provides a good illustration of the pitfalls of superficial interpretation of survey results.

A cursory comparison of the results (Table 11) might lead one to conclude that a significant change in power disturbances at computer sites occurred between 1972 (end of the A-S study) and 1979 (end of the G-S study).

A-S reported 88.3 percent of observed disturbances as spikes, impulses, and transients, 11.2 percent as sags, and 0.47 percent as outages . G-S, on the other hand, reported 87 percent of the observed disturbances as sags, 7.4 percent as impulses, 0.7 percent as "surges" ("swells"), and 4.7 percent as outages (which they call power failures).

TABLE II

UNRECONCILED COMPARISONS BETWEEN THE GOLDSTEIN-SPERANZA

AND ALLEN-SEGALL RESULTS

TABLE III
MONITOR  THRESHOLDS

Taking a more careful look at the monitoring thresholds used in each study (Table 111) helps to explain why the number of impulses appear to have decreased and the number of sags appear to have increased.  Since G-S use a threshold of -4 percent for sags while A-S use -10 percent, one can expect the G-S study to indicate a higher percentage of sags, because the sags between -4 and -10 percent are not included in the A-S study.  Oscillatory decaying disturbances are not specifically identified in the G-S study but are included under the category of impulses.  The threshold for impulses used by G-S (200 V for 120-V lines, or 118 percent) is higher than that used by A-S (± 10 percent).  Because the rate of occurrence increases steeply for lower amplitude disturbances, one can expect a drastic reduction in the percentage of impulses reported by the G-S study as compared to the A-S study.

The increase in percentage of power outages reported by G-S may be explained by the shift in the number of disturbances observed due to other threshold changes.  Percentages can be a very misleading basis for comparison unless all conditions are equal.  For example, the incidence of power outages observed in both studies is very similar, even though the percentages are one order of magnitude apart; A-S report 0.6  occurrence per month while G-S report 0.4 occurrence per month.

Both studies present summaries and statistical analyses of their disturbance data in difference ways.  A-S use only the observed disturbances as a data base and present results as incidence rate graphs.  Incidence rates of sags and impulses at different thresholds are given by A-S, allowing a more direct comparison with the disturbance thresholds of the monitoring instruments used in the G-S study.

The G-S study presents a statistical model of the disturbance rates to predict the incidence rates at predefined disturbance levels, selected to correspond to those levels generally expected to cause computer systems problems: impulses greater than 200 V (118 percent of nominal peak voltage), sags greater than - 20 percent of the nominal voltage, and "surges" ("swells") greater than 10 percent of nominal.  The G-S model states the disturbance rates in terms of probability, such as 50 percent of the sites will have less that "x" disturbances per year or 90 percent of the sites will have less than "y" disturbances per year, but with a cautionary note that there is no firm correlation between sites, making specific predictions from overall results somewhat uncertain.

When the disturbance rates at the same thresholds are compared for the A-S data and the G-S model (for 75 percent probability), the results are surprisingly similar (Table IV).  The conclusions of these two studies are that deep sags contribute about 62 percent of the power system problems which are related to normal mode disturbances, severe impulses are responsible for 21 percent outages for 14 percent and "surges" ("swells") for 2 percent.

# Differences in Surge Amplitudes

The amplitudes of the surges reported in the surveys vary over a wide range, and comparisons are difficult because the data are not presented in a uniform format.  An attempt was made to get a quantitative comparison of the amplitudes reported in the surveys; however, the exercise was quickly found to be futile because of the following two main reasons.

1)	Looking at "maximum values," one finds that in some surveys the quoted maximum is actually a value in excess of the range of the instrumentation, while for others it is the measured value.  There are too few points and insufficient information to attempt a statistical treatment of this truncated data base (censored data in statistical terms).  Furthermore, the quoted value in some surveys is the total voltage (instantaneous value of ac sine wave plus surge), while in others the sine voltage has been filtered out.  When surges are in the range of several thousand volts (the concern being damages), the difference between the two definitions is not significant; however, when surges are in the range of a few hundred volts (the concern being malfunctions), the difference is significant.

2)	Because the lower threshold of the recorder varies among surveys, and the frequency of occurrences increases dramatically with lower threshold, the labels of average, median, most frequent, typical, etc., are not meaningful for comparing amplitudes.  The preceding discussion of A-S and G-S results has illustrated the profound effect of threshold selection on reported results when they are expressed in percentages.

For these two reasons, any comparison at the present stage of inconsistency in report formats can only be qualitative.  Conjecture or speculation, rather than hard facts, might explain differences, as illustrated in the following two examples.

TABLE  IV

#### RECONCILED COMPARISONS

The relatively small number of high-amplitude surges reported by Allen-Segall compared to other surveys [16] might be explained by a limitation of their instrument.  This explanation was submitted as a written discussion of the paper, but because of the "conference paper" status of the paper it was not published by the IEEE. [Editor’s 2003 Note:  That Conference paper, together with its discussion, is now accessible, with permission of the IEEE, in this Anthology Part 5.

Briefly stated, the storage oscilloscopes used by A-S had the limited writing speed of contemporary technology; furthermore, the small amplitude set for full scale was such that a high-amplitude transient would have its peak off screen and the steep rise would not be seen on the phosphor.  Fig. 9 shows a set of oscillograms recorded in the laboratory by Martzloff in 1974, with the same model of oscilloscope as used by A-S: an actual 2200-V transient overvoltage appears as a benign 400-V transient if the oscilloscope sensitivity is set in anticipation of relatively low-amplitude transients and relatively slow speed, as was the case in the A-S study [31].

Figure 9 – Appearance of recordings made with storage oscilloscope and high-speed oscilloscope

Another difference in observed amplitudes is found in the results of the Alaska power survey [11].  One possible explanation for the relatively low surge level observed was suggested in the discussion of that paper: the built-in surge protection of the power supply for the internal electronics of the monitor might have reduced the levels of the surges observed by the monitors which had their power cord and monitoring probe connected to the same duplex receptacle.

A general explanation of differences in amplitudes found in the various surveys might be the observation by some of their authors of the lack of correlation between sites.  Furthermore, some surveys include sites where equipment failures were experienced or expected, while other surveys were made at sites not singled out for particular problems.  Thus the differences in overall results of various surveys might simply be the result of the different surge exposure at the points of monitoring.  This explanation implies that surveys will still be needed where specific information is desired.

#### Differences in Waveform

From those surveys made with waveform recording capability, the "typical" forms suggested by each author have been collected in Fig. 10.  The finding of ringing waves, as opposed to the traditional unidirectional impulses, seems general in these low-voltage circuits. [Footnote: The data base of the Guide on Surge Voltages [16] shows oscillograms of ring waves recorded in the Bell System during a survey before the Goldstein/Speranza study, but not otherwise published.]

Martzloff and Hahn were among the first to report ring waves.  Their reported measurements were incorporated into the data that resulted in the eventual selection of a 100-kHz ring wave with a 250- or 500 ns rise time for the UL Standard Ground Fault Circuit Interrupters [32] and the 0.5-s 100kHz ring wave of the IEEE Guide on Surge Voltages [16].

While Cannova does not report detailed descriptions of the waveforms, the statements "4 to 6 s" and "up to 19 s" could be interpreted either as a time to half-value or as the time between the initial rise and the first zero crossing of a ringing wave.  Interestingly, that data base led to the specification of a unidirectional longer impulse, the classic 1.2/50-s voltage impulse, for conservative rating of candidate surge protection devices to be installed in the shipboard environment [19].

Wernstrom, Broms, and Boberg show three examples of recordings.  The first is indeed a ring wave with a frequency of about 500 kHz and a rise time of 200 ns.  The second example is a burst of nanosecond-duration transients, similar in shape to the proposed IEC/TC65 Electrical Fast Transients [33].  The third example is (of all things) a unidirectional (almost) impulse.

The data reported by Odenberg and Braskich are different from the others in that only two points of the waveform are reported: peak and 50 percent of peak amplitude.  As such, this description is not a complete waveform; furthermore, their report that 90 percent of their 250 000 recordings show the 50percent point occurring between 900 and 1100 s is unique among all the surveys.

The Goedbloed data presentation reflects concerns addressing interference rather than damage; hence, the emphasis was given to amplitude, rate of rise, and energy rather than waveform.  An oscillogram characterized as "typical" is presented in Fig. 10: it is a ring wave with a frequency of about 800 kHz.  In the data processing by conversion of the recorded events to a standardized trapezoidal pulse, the median of the time to half-value is found to be about 2 s, which is an indirect measure of the relatively short duration of the observed surges.

## Figure 10 – “Typical” waveforms reported in surveys

Agreement and Disagreement on Rate of Occurrence versus Levels

Several of the survey authors have attempted to fit a classic distribution or a simple relationship between the rate of occurrence and the amplitude of the surges.

In making such attempts, the frequency of occurrence is presented in different forms such as histograms, cumulative frequency, or number of occurrences in excess of a stated surge level.  Fig.  11 shows on a single chart the relative distributions of the findings, normalized for voltage level and frequency of occurrence for each survey result: the slope of the lines is what can be compared, not the absolute rate of occurrence.  It is remarkable that slopes are similar among the surveys if one keeps in mind that the absolute frequency of occurrence is site-dependent.

## Figure 11 – Comparison of slopes of frequency of occurrence versus level of surges among surveys

#### WORKING TOWARD MORE CONSISTENT SURVEYS

The ambiguities plaguing the field of site surveys have become apparent to many interested workers, resulting in the formation of a new Working Group Monitoring Electrical Quality sponsored by the Power Systems Instrumentation and Measurements Committee.  The scope of the document being developed by this Working Group is as follows.

This Recommended Practice covers monitoring the electrical quality of single-phase and polyphase ac power systems.

- To obtain consistent descriptions of disturbances in the electrical quality of power systems, this document presents definitions of nominal conditions and of deviations from these nominal conditions that may originate within the source of supply or from interactions between the source and the load.

- To identify which deviations may be of interest, a brief generic description is presented of the susceptibility of load equipment to deviations from nominal conditions.

- To obtain comparable results from monitoring surveys performed with different instruments by different operators, this document presents recommendations for measurement and application techniques, and interpretations of results.

- While there is no implied limitation on the voltage rating of the power system being monitored, signal inputs to the instruments are limited to 1000 V or less.  Fundamental frequencies of the ac power systems being monitored are in the range of 45 to 450 Hz.

- Although it is recognized that the instruments may also be used for monitoring de supply systems or data transmission systems, details of application to these cases are under consideration and are not included in the present scope.  It is also recognized that the instruments may perform monitoring functions for environmental conditions (temperature, humidity, high-frequency electromagnetic radiation).  However, the scope of this document is limited to the conducted electrical parameters derived from voltage or from current measurements, or both.

Contributions to the development of this document are invited and welcome, and further information may be obtained from the authors.

#### CONCLUSIONS

A review of power quality site surveys conducted over the last twenty years reveals interest facts, and close examination of the results can dispel some fictions and fallacies.

1)	Considerable progress has been made in recording capability of monitoring instruments, mostly as the result of progress in the hardware and software used in digitizing systems.  Improvements include multichannel synchronized recording of different parameters, fast data acquisition, automated data reduction, and improved resolution.

2)	With the steady progress and expanded capability of instruments, it becomes increasingly important to achieve greater consistency in definitions of the disturbance parameters and the methods of application of the monitoring instruments.

3)	Site-to-site variations in exposures preclude making precise predictions for a specific site from an overall data base, but useful predictions can be made by adjusting the overall data base only slightly by limited data collection at the site of interest.

4)	The steady increase in the number of surge protective devices being installed in low-voltage power circuits in the last several years can be expected to continue.  The result might be a lowering of the mean values of observed surges but not necessarily the extreme values of the distribution.

- Differences among results indicated by a cursory comparison can in many cases be resolved by a closer examination of the conditions under which the surveys were conducted.  However, some differences appear less likely to be explained if raw data have been processed and the initial parameter measurements are no longer available for consideration.  Providing greater detail in the published reports and sharing of experiences at technical meetings might help overcome this difficulty.

6)	A new IEEE Working Group on Monitoring Electrical Quality has been formed with a broad scope that encompasses this process of improving consistency in the definitions and interpretation of power disturbances.  In addition, the IEEE Working Group on Surge Characterization is also attempting to obtain a broader data base for the revision of the Guide on Surge Voltages.  These two groups are ready to provide counsel and forum to any would-be surveyor in planning and reporting the collection of new data on disturbances, thus avoiding later difficulties in incorporating the results in a shared data pool.  This paper is presented in support of this effort and to promote greater participation among interested workers and users.

#### ACKNOWLEDGMENTS

The contributions to this review by Arnold Perrey, Catherine Fisher, and Robert Palm, Jr., respectively, in the literature search, organization, and graphic presentation, are gratefully acknowledged.

#### REFERENCES

[1]   T. S. Key, "Diagnosing power quality-related computer problems," IEEE Trans.  Ind.  Appl., vol.  IA-15, no. 4, July/Aug. 1979.

[2]   F. D. Martzloff, “The protection of computer and electronic systems against power supply and data line disturbances," General Electric Company, Schenectady, NY, Report 85CRD084, 1985.

[3]   J. H. Bull and M. A. Nethercot, "The frequency of occurrence and magnitude of short duration transients in low-voltage supply mains," Radio Electronic Engineer, Sept. 1964.

[4]   Committee Report, "Bibliography on surge voltages in ac power circuits rated 600 V and less," IEEE Trans.  Power App.  Syst., vol.  PAS-89, no. 6, July/Aug. 1970.

[5]   F. D. Martzloff and G. J. Hahn, "Surge voltages in residential and industrial power circuits," IEEE Trans.  Power App.  Syst., vol.  PAS89, no. 6, July/Aug. 1970.

[6]   S. F. Cannova, "Short-time voltage transients in shipboard electrical systems," in IEEE IAS 1972 Annual Meeting Conference Record.

[7]   G. W. Allen and D. Segall, "Monitoring of computer installation for power line disturbances," presented at the IEEE PES Winter Meeting Conference, New York, Jan. 1974, Paper C74199-6.

[8]   M. Goldstein, and P. D. Speranza, "The quality of U.S. commercial ac power," in Proc.  INTELEC Conf., 1982.

[9]   O. B. Laug, and D. L. Hillhouse, Analysis of Requirements for Shipboard Voltage Spike Suppressors, NBSIR 84-2844, National Bureau of Standards, 1984.

[10]  H. Wernstrom, M. Broms, and S. Boberg, "Transient overvoltages on ac power supply systems in Swedish industry," Foorsvarets Forskningsanstalt, Huvudavdelning 3, Sweden, Report FOA E 30002E2, 1984.

[11]  J. D. Aspnes, B. W. Evans, and R. P. Merritt, "Rural Alaska electric power quality," IEEE Trans.  Power App.  Syst., vol.  PAS- 104, no. 3, Mar. 1985.

[12]  R. Odenberg and B. Braskich, "Measurements of voltage and current surges on the ac power line in computer and industrial environments," IEEE Trans. Power App. Syst., vol.  PAS- 104, no.  I0, Oct. 1985.

[13]  T. M. Gruzs, "Power disturbances and computer systems: A comparison of the Allen-Segall and the Goldstein-Speranza power line monitoring studies," in Proc. 1986 Electrical Overstress Exposition, Nelson Publishing Company, Nokomis, FL, Jan. 1986.

[14]  J. J. Goedbloed, "Transients in low-voltage supply networks," IEEE Trans.  Electromagn.  Compat., vol.  EMC-29, no. 2, May 1987.

[15]  IEEE Standard Dictionary of Electrical and Electronics Terms, ANSI/IEEE Std 100-1984.

[16]  Guide on Surge Voltages in Low-Voltage AC Power Circuits, ANSI/IEEE C62.41-1980.

[17]  Insulation Coordination within Low-Voltage Systems, Including Clearances and Creepage Distances for Equipment, IEC 664-1980.

[18]  Electromagnetic Emission and Susceptibility Requirements for the Control of Electromagnetic Interference, DOD-STD-46 I B.

[19]  Interface Standard for Shipboard Systems, DOD-STD- 1 399, Sec. 300, 1978.

[20]  F. D. Martzloff, "Varistor versus environment: Winning the rematch," IEEE Trans.  Power Del., vol.  PWRD- 1, no. 2, Apr. 1986.

[21]  W, Meissen, "Uberspannungen in Niederspannungsnetzen," (Overvoltages in Low-Voltage Networks), Elektrotechnische Zeitschrift, vol. 104, 1983.

[22]  G. W. Allen and D. Segall, "Impact of utility distribution systems on power line disturbances," presented at the IEEE PES Summer Meeting Conf., July 1976, Paper A763884.

[23]  IEEE Guide on Surge Testing for Equipment Connected to Low-Voltage AC Power Circuits, ANSI/IEEE C62.45-1987.

[24]  IEC Multilingual Dictionary of Electricity, published by IEEE and distributed in cooperation with Wiley-Interscience.

[25]  Guideline on Electrical Power for ADP Installations, FIPS Pub 94, National Bureau of Standards, 1983.

[26]  F. D. Martzloff, "Matching surge protective devices to their Environment," IEEE Trans.  Ind.  Appl., vol.  IA-21, no. 1, Jan./Feb. 1985.

[27]  T. S. Key and F. D. Martzloff, "A consensus on powering and grounding sensitive electronic equipment," in Conf.  Rec.  IEEE IAS Annual  Meeting, vol. 2, Sept. 1986, pp. 1054-1060.

[28]  Recommended Practice on Powering and Grounding Sensitive Electronic Equipment in Commercial and Industrial Power Systems, IEEE P1100.

[29]  F. D. Martzloff and H. A. Gauper, "Surge and high-frequency propagation in industrial power lines," IEEE Trans.  Ind.  Appl, vol.  IA-22, no. 4, July/Aug. 1986.

[30]  F. D. Martzloff, "Transient overvoltages in secondary systems," General Electric Company, Schenectady, NY, Report 81CRD121, 1981.

[31]  G. W. Allen, "Design of power-line monitoring equipment," IEEE Trans.  Power App.  Syst., vol.  PAS-90, no. 6, Nov./Dec. 1971.

[32]  UL Standard for Safety 943, Ground Fault Circuit Interrupters, Underwriters Laboratories, 1976.

[33]  Electrical Fast Transients-Burst Requirements, IEC Standard 80 1 4.

POWER QUALITY MEASUREMENTS:

BRINGING  ORDER OUT OF CHAOS

François D. Martzloff

National Bureau of Standards

ABSTRACT - The quality of the power supplied to sensitive electronic equipment is an important issue.      Quantifying this quality, however, is difficult under the present state of nonexistent or uncoordinated standards concerning two related questions: (1) what levels of power quality are required for what types of loads, and (2) what measurement techniques are required to determine reliably the level of disturbances that reduce quality.  Development of standards by the consensus process and voluntary compliance, although a slow process, is a mechanism for reaching technically sound and cost-effective solutions.   Several standards projects are in progress, but need an industry-wide support to become the generally accepted basis for valid and useful measurements of power quality.

# INTRODUCTION

The issue of Power Quality has gained increased recognition as the result of two unrelated but parallel developments: (1) an increase in the sophistication of electronic systems, sometimes resulting in an unintentional increase in their sensitivity to power supply disturbances. and (2) an increase in the number and  power rating or power conversion equipment, generally resulting in the distortion of the power system voltage.  Improvements in the situation described as .poor power quality' can  be achieved by reducing the sensitivity of equipment to power line disturbances, or by limiting the injection of disturbances -- or better yet, by reducing both in a coordinated approach.  While these remedies might seem obvious in principle, their implementation (enforcement) appears more difficult. Voluntary      standards provide a guide for such an implementation.  To  that end three types of standards are necessary.  The first concerns measurements, to obtain correct and universally acceptable data.  The second concerns equipment performance, to define both its tolerance to disturbances and its limits on emission of disturbances.  The third concerns acceptable disturbance levels on the utility supply,  to promote compatibility of equipment with the utility supply.  These standards are developed by reconciling purely technical objectives with economic reality.  For a standard to be  effective and acceptable, both aspects must have an accurate basis.  This paper gives emphasis to the technical aspects of the measurements, specifically field measurements of power quality.

THE GOAL: MATCHING EQUIPMENT CAPABILITY WITH POWER QUALITY

To achieve a satisfactory operational environment regarding power quality, a coordinated approach is needed to match the characteristics of equipment with those of the power supply.  The concept of matching is important: it implies actions on both sides of the issues, not unilateral demands for corrective action based on  a posture that the other party is the offender. Three approaches will read to this matching, separately or in combination:

1.	Increasing equipment tolerance for disturbances,

2.	Controlling the emission of disturbances by equipment, utility equipment

as well as end-user equipment)

3.	Providing interface devices when necessary.

Each of these three approaches requires accurate information on power supply disturbances for any action to be effective.  Action can be preventive, when a potential problem is identified before new equipment is  installed.  Action can be curative, when a problem arises after new equipment is installed. The problem can appear in two forms: (1) the new equipment is sensitive to disturbances already present in the system (the equipment is the victim); (2) the new equipment creates a disturbance that affects equipment already in service (the new equipment is the offender).

These two terms used to label the situation reveal the adversarial postures that can exist.  In an ideal world, one would consider total system goals to optimize economical and technical solutions, rather than point fingers.  In the real world, cooperation can lead to a mutually satisfactory solution between the source and the receiver of disturbances (note the neutral words) in contrast with the other labels.

The first step towards recognizing the need for improving the power quality situation is to determine the level of disturbances occurring in the system. The parameters characterizing a power supply are: frequency, voltage amplitude,  waveform, and symmetry. Therefore, the nature of disturbances may be classified by their effect y of disturbances is associated d the probability of occurring at a given site over a time period.

The level of disturbances is determined by measurements conducted   at the site of an existing installation or at a future installation  of  potentially  sensitive  equipment.  These measurements are described as 'site surveys.'  If the tolerance of the equipment for disturbances is defined (a need that is not always recognized) and the level of disturbances determined by the site survey is excessive, then the three matching actions mentioned above come into play.  Any one of the three, or a combination, can be the most effective solution.  Knowledge of the situation will point toward a solution, rather than reliance on a common misconception that providing a simple interface (line conditioning) will solve all problems.        This misconception is nurtured by frequent observations that many problems have in fact been solved by simply inserting a line conditioner.  However, one should not yield to temptation of making a general rule from these isolated success stories, and ignore other, more effective or more economical approaches achieving inherent compatibility.

Because this additional line conditioning equipment may require significant capital investment. the choice of corrective measures is made by economic trade-off.  However, if technical inputs to this trade-off are incorrect because erroneous conclusions result from a faulty site survey, the whole process is worthless or misleading.  For this reason, a good understanding of the merits and limitations of site surveys is essential for reconciling  expectations with reality before specifying expensive line conditioning equipment.  In their review of power quality site surveys, Martzloff and Gruzs [1] discussed how one should deal, not with fiction or fallacies, but with facts.

In an attempt to clarify the issues. this paper first presents a review of the origins and definition, of disturbances.  Next, the development of monitoring instruments during the last 25 years is described.      Finally, an appeal is made for improving measurement methods to provide more consistent reporting        power disturbances recorded in future surveys.

## CLASSIFICATION AND ORIGIN OF POWER LINE DISTURBANCES

The four power system parameters identified above – frequency, amplitude, waveform, and symmetry – can serve as frame of reference to classify the disturbances according to their impact on these four parameters.

Frequency disturbances are associated with power system faults.  Interconnection of the utility grid ensures frequency stability, except when a fault occurs that isolates the    local system from the grid. leaving local generation more sensitive to load variations.  Transient frequency disturbances, just before an outage. occur in a system containing large rotating machines: should the system trip out, the machines will maintain some voltage, with decaying amplitude and frequency, while they coast to a final stop

Amplitude variations can occur in several forms; their description is inextricably associated with their duration.  They range from extremely brief durations to steady-state conditions, making the description and definition difficult, even controversial at times.  Their causes and effects need close examination to understand the mechanisms and to define an appropriate solution.

Waveform variations occur when nonlinear loads draw a current which is not sinusoidal.  One could also describe an amplitude variation as momentary waveform variation, but the intended meaning of the term is a steady variation of the waveform, or lasting at least over several cycles.  This type of disturbance is also described as harmonic distortion because it is easy to analyze as the superposition of harmonics to the fundamental frequency of the power system.

Dissymmetry, also called unbalance, occurs when unequal single-phase loads are connected to a three-phase system and cause a loss of symmetry.  This type of disturbance primarily concerns rotating machines, and as such is not receiving broad attention.  It is important  however, for machine designers and users.  The percentage by which one phase voltage differs from the average of all three is the usual description of this type of disturbance.

The origin of disturbances can be described as external to the particular power system, or as. internal.  In a typical situation, the boundary of a power system is defined as the watthour meter, and reference  is  made to the utility side of the meter (external source), or to the user side of the meter (internal source).  A different approach is to describe the origin in technical  terms, such as  lightning, load switching. power system fault, and nonlinear loads.  Depending on local conditions, one can be more important than the others, but all need to be recognized.  The mechanism involved in generating the disturbance also determines whether the occurrence will be random or permanent. unpredictable or easy to define.

Lightning surges are the result of direct strikes  to the power system conductors as well as the result of indirect effects.  Indirect effects include induction of overvoltages in loops formed by conductors and ground potential rises resulting from lightning current in the soil.  A lightning strike to the power   system can activate a surge arrester,  producing a severe reduction or a complete loss of the power system voltage or one half-cycle.  A flashover of line insulators can cause a breaker to trip, with reclosing delayed by several cycles, causing a momentary power outage.  Thus, lightning can be the obvious cause of overvoltages near its point of impact, but also a less obvious cause of voltage loss at a considerable distance from its point of impact.  Clearly, the occurrence of this type of disturbance is unpredictable at the microscopic level.  At the macroscopic level, it is related to geography. seasons, and local system configuration.

Load switching is a major cause of disturbances.  Switching large loads on or off can produce long-duration voltage changes beyond the immediate transient response of the circuit.  Whether the switching is done by the utility or by the user is immaterial from the technical point of view, although the responsibility may be the subject of a contractual dispute.  The occurrence of these disturbances is somewhat predictable, but not necessarily under controlled conditions.  The introduction of power conversion equipment and voltage regulators operating by switching on and off at high frequency has created a new type of load switching disturbance.  These disturbances occur steadily, although their amplitude and harmonic content will vary for a given regulator as the load conditions vary.

Power system faults occur on both sides of the meter, resulting from equipment failure or external causes (vehicle collisions, storms, human errors). These disturbances can range from a momentary voltage reduction to a complete loss of power lasting for minutes, hours, or days.  Their accidental origin makes them unpredictable, although the configuration of a power system and its environment can make it more or less prone to this type of disturbance.

Nonlinear loads draw non-sinusoidal currents from the power system, even if the power system voltage is a perfect.   These currents produce non-sinusoidal voltage drops in the system source impedance, which distort the sine wave produced by the power plant generator.  A typical nonlinear load capacitor-input filter, such as used in most computers, drawing current only at the peaks of the voltage sine wave.

Characterizing these four types of disturbances and disturbance mechanisms involves detection (measurement) of their occurrence and description of the results of these measurements.  What might appear a simple process is in fact made difficult by deficiencies in de fining disturbances observed when making site survey measurements.

### DEFICIENCIES IN DEFINITIONS

One difficulty in coordinating efforts for improving power quality is that terms used to describe power disturbances are poorly defined.  An effort is being made by standards-writing organizations to resolve this problem, as described later in this paper, but consensus has yet to be reached.  The following two examples of this lack of consensus illustrate the point; resolving them is beyond the scope of this paper.

What is a surge?   The accepted meaning of surge. in the context of power systems, is a short-duration overvoltage, typically less than a few milliseconds. These surges are caused by lightning, power system switching, or faults.  Protection against them is obtained by protective devices called surge arresters (formerly called lightning arresters) for utility systems, and  surge suppressors, or spike suppressors for end-user systems.  This first meaning of the word ‘surge’ is not that established by manufacturers and users of disturbance monitors and line conditioners.  The unfortunate second meaning, a consequence of nonexistent standards on the subject, is a momentary overvoltage at the fundamental frequency, with a duration of typically a few cycles.  What the designers and users of surge arresters or suppressors call ‘surge’ is called ‘impulse’ or ‘spike’ by the monitoring instrument community.  Figure 1 shows graphic descriptions of the confusion created by the dual meaning of the word ‘surge.’

What is an outage?  Most users agree that it means a loss of line voltage.  The duration of this event, however, is quite different when ‘outage’ is cited by computer users (as short as one half-cycle), or by power engineers (seconds, perhaps minutes).  Furthermore, some users and manufacturers of line conditioners do not make a clear distinction between complete loss of line voltage (zero voltage condition), severe undervoltages (‘deep sags’), or the single-phasing of polyphase power systems.         Part of the problem  may be that the definition of ‘outage’ has regulatory implications for evaluating the performance of public utility companies.

As another example of definitions deficiencies, standards dictionaries do not define the term “sag”.  It is accepted as meaning a momentary voltage reduction at the ac power frequency.  However, there is no consensus on the details (threshold, duration, etc.) of what characterizes a sag.

With the present definition deficiencies, manufacturers and users of disturbance monitors are left without guidance and consequently define terms independently from each other, hence the confusion. In fact, the development and widespread use of disturbance monitors should motivate a more coordinated and rational approach toward resolving these deficiencies.  Progress in technology of monitoring instruments during the last two decades is remarkable and worthy of a brief review.

## DISTURBANCE MONITORS DEVELOPMENT HISTORY

Historically, the first (unintended) disturbance monitors were the actual load equipment. Only later, when confronted with unexplained failures or upsets, did the users start monitoring the quality of their power systems.   Electric utilities have been monitoring the parameters of their systems, but the precise characterization of microsecond-duration surges in the early 1960s required special oscilloscopes. For the next 15 years, oscilloscopes or simple peak detectors were the basic instruments for monitoring transient overvoltages. Starting in the 1970s, commercially-produced digitizers became available. Since then, technology has made continuing progress as experience has accumulated.

Early site surveys were limited to voltage measurements.  This limited interest reflected concerns for damage to sensitive electronic components connected across the line. Ignoring the importance of the source impedance led to some performance standards [2] that do not specify the current-handling requirements for surge protective devices.  With the introduction and widespread application of new clamping protective devices (silicon avalanche diodes or metal oxide varistors), the surge current diverted through these devices became a very important factor for proper device selection.. Therefore, the need emerged for characterizing current surges as well as voltage surges, but few surveys to date have addressed this need.  This need offers a challenge and an opportunity to designers of monitoring instruments.

This challenge has also produced attempts to measure “energy” with an instrument which is actually only a voltmeter.  By assigning parametric values to the source impedance of the surge and integrating the product (volts seconds) of the surge, some knowledge of the energy involved would be obtained.  Computing true energy, of course, requires the measurement of both voltage and current. However, the real question concerns the sharing of energy between the impedance of the source and the impedance of the load.  A discussion of the energy in the surge versus energy delivered to the protective device is beyond the scope of this paper.  The difference between the two must be recognized, however, to prevent further confusion as future monitoring instruments include an “energy” parameter in their readouts.

With. the present development of sophisticated multi-channel digitizing instruments,  future surveys should monitor both voltage and current.  Note, however, that the current of interest is that which the surge source would force through a surge protective device.  The amplitude as well as the waveform of the surges needs to be characterized for the correct application of surge protective devices.  Peak-reading monitors provide useful information on surge activity at a given site, but assessment of the surge severity level for the proper sizing of protective devices also requires waveform and source impedance information.

One difficulty facing users of monitoring instruments in this fast-paced technology is that manufacturers are steadily improving their instruments.  These improved features respond to specific wishes of the users or result from their own product research and development, a desirable situation.  On the negative side, however. data collected by different instruments become equipment-dependent.              Comparison of survey results by third parties is then difficult in the absence of details on the instrument characteristics and methods of measurement.

## TYPES OF MONITORS

The instruments used in past surveys reflect technology progress as well as logistics constraints, resulting in a diversity of approaches.  Until recently, all monitoring instruments were just special voltmeters.  Some of the monitors recorded a single parameter, such as the value of voltage peaks, or the occurrence of voltage peaks above a preset threshold.  Other monitors combined time with voltage measurements, to characterize the voltage waveforms.  The following list shows the evolution of simple surge monitors into complex disturbance monitors.

Threshold counters – The surge is applied to a calibrated voltage divider, triggering a counter each time it exceeds a preset threshold.  The early types had analog circuitry; more recent types have digital conversion of signals.

Digital peak recorders – The surge is converted to a digital value and recorded in a buffer memory for later playback.  In the early types of recorders, only the peak was recorded.  In later types, the duration of the surge was also recorded opening the way to the more  complex digital waveform recorders now available.

Oscilloscope with camera – The surge triggers a single sweep on the cathode !ay tube of the oscilloscope, and is recorded as it occurs by an automatic shutterless camera.

Screen storage oscilloscope – The surge is displayed and stored on the cathode ray tube. and a camera is used for permanent recording after the surge has occurred.  The writing speed capability of these oscilloscopes was a limitation in the late 1960s.

Digital storage oscilloscope – The surge is digitized and stored in a shift register for subsequent  playback  and display whenever it exceeds a preset threshold.  An important feature is the capability of displaying events occurring before the beginning of the surge.

Digital waveform recorder – With the advent of compact, portable instruments, a revolution has taken            place in the field of disturbance and recorders.  The earlier surge waveform recorders were large and difficult to transport to field sites [3]. [4].  New microprocessor-based instruments have introduced a. portable storage and computing power which has made waveform analysis and graphic display ;possible. In these instruments, voltage and current signals are digitized and stored, allowing reports of many different parameters of the disturbance.  The range of parameters which can be monitored is expanded. Long trends can be detected, harmonic analysis can be performed, and the types of possible measurements are limited only by the creativity of the instrument designers and the curiosity of the users.

Although some site surveys might aim at high accuracy, the real world experiences an infinite variety of disturbances, making it difficult to fit them into simple, orderly categories.   Any attempt to describe these disturbances in fine detail restricts general usefulness of the data and can lead to illusions on applicable accuracy.  Some simple (and inexpensive) instruments are useful indicators of frequent disturbances.  Other instruments, more complex (and more expensive), provide comprehensive data on disturbances.  A general observation from many surveys conducted by different researchers is that results vary widely from site to site.  Thus, there is a practical limit to the detail that a survey can yield, and unrealistic expectations of precise information should be avoided.  What is really needed is a more uniform and compatible recording and reporting of the data.

## COMPARISONS AMONG SITE SURVEY REPORTS

Relative  occurrence  of different  types of disturbances.  Two site surveys have been widely cited.  One was performed in the early 1970s the other in the late 1970s by Allen and Segall [5], the other in the late 1970s by Goldstein and Speranza [6]. Each of these surveys presented results by describing various kinds of disturbances (overvoltages, sags, etc.) and cited the percentages of each type of disturbance in the total  of all the observed disturbances.  The findings did not at first appear to agree, raising questions on the likelihood of a change in power systems between the first and second survey.  However, a detailed comparison of these two surveys [1], revealed that the disagreement was rooted in a difference of the thresholds built into the monitors, rather than a change in the behavior of power systems.

Differences in surge amplitudes.  Amplitudes of surges reported in several surveys vary over a wide range. Comparisons are difficult because the reports do not present the data in a uniform format. Attempting to get a quantitative comparison of the amplitudes reported seems a futile exercise, because of the following reasons:

1.	Looking at the “maximum values” cited in the reports, one finds that in some surveys this maximum is actually a value known only as being above the range of the instrument, while for others it is the measured value.

2.	Because the threshold of the recorder varies among surveys. and the frequency of occurrences increases dramatically with ' a' lower threshold, the labels of average, median, most ' frequent, typical, etc., are not meaningful for comparing amplitudes.

Differences in surge waveforms.   What a ‘typical’ surge might be has been the subject of many discussions.  Several surveys confirm the finding of ringing waves, as opposed to the traditional unidirectional impulses.   However, wide differences still exist among the reports.  The following examples illustrate this point.

Martzloff-Hahn [7] were among the first to report ring waves, recorded by 1960 vintage oscilloscopes.               Their findings were incorporated into the data that resulted in the selection of a 100 kHz ring wave for the UL Standard Ground Fault Circuit Interrupters [8] and the IEEE Guide on Surge Voltages [9].

Odenberg and Braskich [10] used different instruments recording only two points of the waveform: (1) the peak amplitude and time to peak, and (2) the time to 50% of the peak amplitude.  As such, this description is not a complete waveform.  Furthermore, they reported that 90% of their 250,000 recordings show the 50% point occurred between 900 and 1100 microseconds.  This finding is unique among all the surveys.

Wernstrom et al. [11] report ring waves of 500 kHz, bursts of fast transients lasting a few microseconds, and even some unidirectional isolated impulses.

Goedbloed [12] is more concerned with interference than damage; his report gives emphasis to amplitude, rate of rise, and ‘energy’ rather than to waveform.

With the advent of portable monitors capable of presenting the digitized data with graphic details as well as summaries, an explosion in the volume of data can expected.  Just the detail and weight of the information being collected might swamp the researchers, unless data reduction procedures are implemented.  However, whenever data reductions are performed by different persons, there is a high probability that criteria for reduction will be different, making comparisons difficult, even impossible.      Thus, this increased sophistication of available instrumentation makes coordination even more imperative.  The added availability of harmonic analysis by portable monitors will also lead to an expansion of data supporting standards on harmonic control [13].

Agreement and disagreement on rate of occurrence versus levels.  Several survey authors have attempted to fit a classic statistical distribution or a simple relationship between the rate of occurrence of surges and their amplitudes.  The motivation for such a simplified presentation might be rooted  in a belief that nature obeys simple mathematical laws.  The reality, however, is that so many different mechanisms contribute  to the generation of surges that a simple relationship is unlikely. Notwithstanding this rationale. a remarkable finding emerges from plotting  the results of all the surveys on the same graph.  Figure 2 shows the relative distributions of the findings, normalized for  voltage level and frequency of occurrence for each survey report.   The slope of the lines is what can be compared, not the absolute rate of occurrence.  It is remarkable that slopes are similar among the surveys. although  the absolute frequency of occurrence is site-dependent.

## WORKING TOWARD MORE CONSISTENT SURVEYS

The ambiguities plaguing the field of site surveys have become apparent to many interested researchers, resulting in the formation by IEEE of a new Working Group on Monitoring Electrical Quality. The scope of a Recommended Practice being prepared by this group reads:

This Recommended Practice concerns the application of instruments used for monitoring electrical disturbances on power systems. The scope includes the definition of disturbance terms, the calibration and connection of the instruments, and the interpretation and reporting of the results. It does not include specific design aspects of the instruments.

The disturbances of interest are those conducted on ac power lines for single or polyphase systems with direct operating voltage connections to the instruments not exceeding 1000 V RMS.       Depending on the design of the instruments, the duration of the recorded disturbances may range from nanoseconds to many seconds, or more.

While the prime interest is focused on monitoring low-voltage ac power systems (50, 60 or 400 Hz), suitable interfaces may allow monitoring  systems  of  higher  voltage;  dc  systems   may also be monitored with these instruments.    It is also recognized that available instruments may be capable of monitoring other parameters such as radiated EMI or environmental conditions; however. the scope of this document is limited to conducted electrical parameters (voltage, current, and derived parameters).

EXPECTATIONS VERSUS REALITY ON POWER QUALITY

Improved credibility of power quality data offers an opportunity to revisit existing standards or develop new standards dealing with power quality.  The areas would benefit from this review:

More realistic definitions of the limits of system voltages.  The limits currently defined are relatively small percentages (5 to 15%) of nominal values.  Many anecdotal stories have been told on momentary overvoltages exceeding the limits of the only standard addressing these limits, ANSI C84.1 [16].  Until well documented, these stories can only remain anecdotal.  However, ignoring them can lead to misapplication of surge protective devices by attempting to suppress surges at a level too close to the momentary overvoltages that do occur.

Improved consensus on the characteristics of surges.  The IEEE Guide on Surge Voltages [9], dating back to 1980, attempted to simplify the situation by describing the surge environment with only two waveforms and an upper practical limit.  Unfortunately. this Guide was misconstrued by some users as a mandatory standard.  A revision is underway, proposing two additional waveforms and presenting the information in a manner that should discourage the misguided use of the document as a performance standard.

Improved Consensus on harmonic control.  Harmonic causes and effects have been the subject of many studies and technical papers. but no performance standard exists to settle potential disputes between sources and receivers of harmonic distortion.   The prevailing document is a Guide. [13]; significant improvements are expected from a revision currently being conducted.

## CONCLUSIONS

Power quality measurements, typically performed by site surveys have evolved from the simple monitoring of surge voltages to the sophisticated analysis of many criteria of power quality.  There is still room for improvement in the procedures – an improvement that can be guided by voluntary standards.       Detailed observation of the issues lead to the following conclusions:

1.	 Considerable progress has been made in the recording capability of monitoring instruments as the result of progress in the  hardware and software used in digitizing systems.  Improvements  include    multi-channel synchronized recording of different parameters, fast data acquisition, automated data reduction, and improved resolution.

2.	Improvements in consistency must be made, commensurate with the steady progress and expanded capability of instruments.  This greater consistency is needed in the definitions of the disturbance parameters and the methods of application of the monitoring instruments.

3.	Site-to-site variations in the occurrence of disturbances prevent making precise predictions for a specific site from an overall data base.

4.	Differences among results indicated by a cursory comparison can be resolved by a closer examination of the conditions under which the surveys were conducted.  However, some differences are less likely to be explained if raw data have been processed and the initial parameter measurements are no longer available for review.

5.	A new IEEE Working Group on Monitoring Electrical Quality has been formed with a broad scope that encompasses this process of improving consistency in definitions and interpretation of power disturbances.  In addition, the IEEE Working Group on Surge Characterization is also attempting to obtain a broader data base for the revision of the Guide on Surge Voltages.

6.	Improved cooperation promoted by the process of voluntary standards development and the exchange of ideas made possible by forums such as the Energy Technology Conference, will avoid some of the difficulties on sharing the data pool recited in this paper.  This paper is presented in support of this effort and to promote greater participation among interested workers and users.

#### REFERENCES

[1]   Martzloff, F.D., and Gruzs, T.M., “Power Quality Site Surveys: Facts, Fiction, and Fallacies,” Conference Record, IEEE Industrial &Commercial Power Systems Conference, May 4-7, 1987.

[2]   Interface Standard for Shipboard Systems, DOD-SM13", Sec. 300, 1978.

[3]   Allen, G.W. “Design of Power-Line Monitoring Equipment,” IEEE Transactions on Power Apparatus and Systems, Vol.  PAS-90   No.6, Nov/Dec 1971.

[4]   Key, T.S, “Diagnosing Power Quality-Related Computer Problems,” IEEE Transactions on Industry Applications, Vol.  IA- 15, No. 4, July/August 1979.

[5]   Allen, G.W. and Segall, D., “Monitoring of Computer Installation for Power Line Disturbances,” IEEE PES Winter Meeting, Conference Paper C74199-6, January 1974.

[6]   Goldstein, M., and Speranza, P.D., “The Quality of U.S. Commercial AC Power,” Proceedings. INTELEC Conference, 82Ct(1818-4.1982.

[7]   Martzloff.  F.D., and Hahn, G.J., “Surge Voltages in Residential and Industrial Power Circuits,” IEEE Transactions on Power Apparatus & Systems, Vol.  PAS-89, No. 6, July/August 1970.

[8]   UL Standard for Safety 943, Ground Fault Circuit Interrupters, Underwriters Laboratories, 1976.

[9]   Guide on Surge Voltages in Low-Voltage AC Power Circuits, ANSI/ IEEE C62.41-1980.

[10]  Odenberg, R. and Braskich, B., “Measurements of Voltage and Current Surges on the AC Power Line in Computer and Industrial Environments,” IEEE Transactions on Power Apparatus and Systems, Vol.  PAS-104, No. 10, October 1985.

[11]  Wernstrom, H.. Broms, M., and Boberg, S., Transient Overvoltages on AC Power Supply Systems in Swedish Industry, Report FOA E 30002-E2, Foorsvarets Forskningsanstalt, Huvudavdelning 3. Sweden. 1984.

[12]  Goedbloed, J.J., “Transients in Low-Voltage Supply Networks,” IEEE Transactions on EMC, May 1987.

[13]  IEEE Guide for Harmonic Control and Reactive Compensation of Static Power Converters ANSI/IEEE Std 519-1981.

[14]  Bull, J. H. and Nethercot, M.A., “The Frequency of Occurrence and Magnitude of Short Duration Transients in Low-Voltage Supply Mains,” Radio Electronic Engineer, September 1964.

[15]  Cannova, S.F., “Short-time Voltage Transients in Shipboard Electrical Systems,” Conference Record, IEEE-IAS 1972 Annual Meeting, CH0685-8-IA.

[16]  American National Standard for Electric Power Systems and Equipment - Voltage Ratings (60 Hz), ANSI C84.1-1982

Monitoring Power Quality

François D. Martzloff

National Institute of Standards and Technology

Gaithersburg, Maryland

Thomas M. Gruzs

Liebert Corporation

Columbus, Ohio

Site surveys are generally initiated to evaluate the quality of the power available at a specific location with the aim of avoiding equipment disturbances in a planned installation or of explaining (and correcting) disturbances in an existing installation. In either case, survey results constitute one of the inputs in the decision-making process of providing supplementary line conditioning equipment, either before or after power disturbances have become a problem. Depending on the reliability requirements of the load equipment, its susceptibility, and the severity of the disturbances, various line conditioning methods have been proposed: surge suppressor (with or without filter), isolation transformer, voltage regulator, magnetic synthesizer, motor-generator set, or uninterruptible power supply (UPS).

Because this additional line conditioning equipment may require significant capital investment, the choice of corrective measures is generally made by economic tradeoff which is the prerogative and responsibility of the end user. However, if technical inputs to this trade-off are incorrect because erroneous conclusions were drawn as a result of a faulty site survey, the whole process is worthless – or worse yet, misleading.

For this reason, a good understanding of the merits and limitations of site surveys is essential for reconciling expectation with reality before expensive line conditioning equipment is called for; one should deal, not with fiction or fallacies, but with facts.

Power disturbances that affect sensitive electronic loads have a variety of sources. Lightning, utility switching, and utility outages are often-cited sources of power disturbances.  However, power disturbances are frequently caused by users themselves, through switching of loads, ground faults, or normal operation of equipment. As one example, computer systems are not only sensitive loads, but can also generate disturbances themselves. Their nonlinear load characteristics can cause interactions with the power system such as unusual voltage drops, overloaded neutral conductors, or distortion of the line voltage.

Utility systems are designed to provide reliable bulk power. However, it is not feasible for them to provide continuous power of the quality required for a completely undisturbed computer operation. Because normal use of electricity generates disturbances, and because unexpected power system failures will occur, every site will experience some power disturbances, but their nature, severity, and incidence rates will vary from site to site.

Confusion in Term Definitions

As will become painfully apparent in next month’s review of site surveys, the terms used by the workers reporting their measurements do not have common definitions. An effort is being made within the IEEE to resolve this problem, as described later in this paper, but consensus has yet to be reached. In this paper, terms describing disturbances are consistent with the IEEE Standard Dictionary of Electrical and Electronics Terms [1] and with established usage within the community of surge protective devices engineers.

The generally accepted meaning of surge voltage, in the context of power systems, is a short-duration overvoltage, typically less than 1 ms or less than one half-cycle of the power frequency. This meaning is not that which has been established by manufacturers and users of monitoring instruments and line conditioners. This unfortunate second meaning is a momentary overvoltage at the fundamental frequency with a duration of typically a few cycles.

Figure 1 – Graphic depictions of disturbances with multiple meanings

In this article, this second meaning of the word “surge” (a momentary overvoltage) will be signaled by the use of quotation marks. What power engineers call surge is referred to as “impulse” or “spike” by the monitoring instrument community. Figure 1 shows by graphic descriptions the confusion created by the dual meaning of the word surge. Acknowledging the desire of users for terse labels, we propose for consideration the word “swell” instead of “surge” for a momentary overvoltage.

The term “outage” is another example of confusion created by unsettled definitions. Most users agree that it means a complete loss of line voltage, but the duration of an outage can be quite different when defined by computer users (as short as one half-cycle) or power engineers (seconds, perhaps minutes). Part of the problem may be that the definition of “outage” has regulatory implications for evaluating the performance of public utility companies. Users and manufacturers of line conditioners do not make a clear distinction between complete loss of tine voltage (zero voltage condition), severe undervoltages (“deep sags”), or the single-phasing of polyphase power systems. For example, a momentary flicker of fluorescent lighting caused by a brief loss of voltage might be considered an outage; however, a brief sag to less than 80 percent of nominal voltage will produce the same visible effect. Some UPS manufacturers consider input voltage sags that cause transfer to the battery backup operation as outages.

The term “sag” has not yet been defined in the IEEE Dictionary, but it is now generally accepted as meaning a momentary voltage reduction at the ac power frequency. However, details (threshold, duration, etc.) of what characterizes a sag are not well defined.

Motivation For Site Surveys

With the increasing dependency on computer-based systems for industry, commerce, and consumers, disruptions from power disturbances are less and less acceptable. Operational problems such as hardware damage, system crashes, and processing errors are the most visible indications of power disturbances. Some computer system users may accept (albeit reluctantly) such problems because they see them as unavoidable. Others may be unaware that otherwise invisible power disturbances could be the cause of these problems. A single power disturbance can cost more in downtime and hardware damage than the investment in power protection that would have prevented the effect of the disturbance. Nearly all sites can benefit from a reduction of operational problems by improving the quality of power supplied to the computer systems [2].

Power line monitoring with sophisticated power disturbance recorders has often been advocated as a way of determining if any line conditioning is required. While monitoring appears to be a logical first step, it has limitations. For example, severe disturbances occur infrequently or on a seasonal basis. Therefore, monitoring periods of less than a year might not produce an accurate profile of power disturbance, and most users are unwilling to wait at least a year to characterize the problem. Also, power line monitoring only produces data on past performance. Changes within the site (or at neighboring sites) or by the utility can drastically alter the power disturbance profile in ways that line monitoring cannot predict.

Figure 2 – Origins of common mode disturbances

While exact prediction of the disturbances to be expected at a specific location is almost impossible – and attempting it would be a fallacy – general guidelines can be formulated. An attempt has been made by standards-writing groups to provide guidance [3] or specifications reflecting expected disturbances [4-6]. However, users will still seek specific data for their particular case, and site surveys will still be necessary. Another fallacy would be to attempt correction of power line disturbances revealed by monitoring and then to expect operational problems of equipment to disappear without having first determined the exact susceptibility of the equipment. Operational problems are the results of more than just power disturbances.

Types of Disturbances

Power line disturbances can be classified into two categories: common mode and normal mode disturbances. The two terms were first defined in the context of communication circuits; a recent IEEE Guide [7] has established an expanded definition which is used in this article, as outlined in the following paragraphs. The IEEE Dictionary [1] and the IEC Dictionary [8] define symmetrical and asymmetrical voltages akin to, but not interchangeable with, the definitions of normal mode and common mode, respectively.

Common mode disturbances are defined as unwanted potential differences between any or all current-carrying conductors and the grounding conductor or earth. In three-phase grounded-wye power supplies typical of large computer systems, common mode disturbances can also be defined as the potential difference between neutral and ground.

Two different types of common mode disturbances can affect a sensitive load. The first type is a disturbance on the input power conductors relative to the input power grounding conductor. Points 1 and 2 of Figure 2 show examples of the origins for these disturbances. This type of disturbance can be limited somewhat by a line conditioner, but it is also influenced by the location of the line conditioner and the wiring practices.

The second type is a ground potential difference between elements of the computer or remote peripherals connected to the computer. Point 3 of Figure 2 is an example of this type of disturbance, which is more difficult to limit because it is influenced by factors such as system configuration and the impedance of the grounding system. These two factors are generally beyond the direct control of the user except in the construction of a new facility.

Because of the broad frequency band involved, wiring resonances can make equalizing ground potentials difficult. Proper computer system grounding, including a signal reference grid, has been found to be effective against most common mode disturbances [9]. However, when remote elements are connected to the computer systems by data cables, large ground potential differences are possible. Proper surge protection of the power supply and proper grounding of data cables will help eliminate hardware damage but might not prevent data corruption. When dealing with the situation of example 3 in Figure 2, fiber optic links are very effective because they provide complete metallic separation of the various elements in the system – a separation that might not be sufficiently achieved by the discrete opto-isolation devices sometimes proposed for that function [10].

Normal mode disturbances are defined as unwanted potential differences between any two current-carrying circuit conductors. Figure 3 shows three examples of the origins of such disturbances. Usually a sine wave of nominal voltage is desired for a computer power supply; any deviation from this sine wave is a normal mode disturbance. Computer users and monitoring instruments designers characterize these disturbances by a variety of terms not always clearly defined such as sags, surges (“swells”), outages, impulses, ringing transients, waveform distortion, and high-frequency noise. Unfortunately, there is no consensus at the present time on the exact meaning of these terms and their underlying quantitative definitions such as amplitude, duration, and thresholds.

Figure 3 – Origins of normal mode disturbances

Types of Monitors

The instruments used in the various surveys reflect technological progress as well as logistics constraints resulting in a diversity of approaches. Nevertheless, all monitoring instruments used in past surveys were voltmeters (with one exception, combining voltage and current measurements) from which disturbance parameters were derived. Some of the monitors recorded a single parameter such as the actual voltage peak or the fact that the voltage exceeded a preset threshold. Other monitors combined time with voltage measurements describing voltage waveforms. The recording functions of instruments used in the surveys may be classified in broad categories:

Threshold counters — The surge is applied to a calibrated voltage divider, triggering a counter each time a preset threshold is exceeded. The early types were analog; more recent types are digital.

Digital peak recorders — The surge is converted to a digital value which is recorded in a buffer memory for later playback or printed out immediately after it occurs. In the early types of recorders, only the peak was recorded; in later types, the duration of the surge was also recorded, opening the way to the more complex digital waveform recorders now available.

Figure 4 – Effect upon voltage peak and waveforms with varistor placed upstream of monitor

Oscilloscope with camera — The surge triggers a single sweep on the oscilloscope’s CRT, which is recorded as it occurs by a shutterless camera with automatic film advance. The oscilloscopes available at that time (the early 1960s) did not allow differential measurements.

Screen storage oscilloscope — The surge is displayed and stored on the cathode ray tube. The writing-speed capability of these oscilloscopes was a limitation in the late 1960s.

Digital storage oscilloscope — The surge is digitized and stored in a shift register for subsequent playback and display whenever a preset threshold is exceeded. An important feature is the capability of displaying events prior to the beginning of the surge.

Digital waveform recorder — The surge is digitized and stored in a manner similar to the digital storage oscilloscope, but additional data processing functions are incorporated in the instrument, allowing reports of many different parameters of the disturbance relating voltage to time.

Although some surveys might aim at great accuracy, the real world experiences such a variety of disturbances that any attempt to describe them in fine detail only restricts general usefulness of the data. Seeking such fine and definitive detail is another fallacy. Some simple instruments are useful (and inexpensive) indicators of frequent disturbances; other, more sophisticated (and more expensive) instruments can provide quite comprehensive data on disturbances (but only on past events from which future disturbances can be extrapolated only by assuming that the causes will remain unchanged). Thus there is a practical limit to the amount of detail that a survey can yield, and unrealistic expectations of very precise information should be avoided.

# Previous And Future Surge Recordings

Before attempting yet another broad survey of power quality, would-be surveyors need to consider not only improvements in instrumentation but also changes that have occurred in modem power systems – in particular the proliferation of surge protective devices. These two differences between earlier surveys and the more recent surveys should be kept in mind when comparing results and when planning future surveys.

Prior to the proliferation of surge protective devices in low-voltage systems (those defined by IEEE and IEC as 1000 V or less), a limitation had already been recognized [4] for peak voltages: the flashover of clearances, typically between 2 and 8 kV for low-voltage wiring devices. For that reason the expected maximum value cited in the IEEE Guide on Surge Voltages [3] reflects this possible truncation of the distribution around 6 kV. Unfortunately, some readers of this Guide interpreted the upper practical limit of 6 kV as the basis for a withstand requirement, and they have included a 6-kV test requirement in their performance specifications. A new version of this Guide, currently under p reparation as a Recommended Practice, will attempt to avoid this misinterpretation.

The number of surge-protective devices such as varistors used in the United States since their introduction in 1972 on low-voltage ac power circuits may be estimated at 500 million. Therefore, a new limitation exists in the voltage surges that will be recorded. A surge-recording instrument installed at a random location might be close to a varistor connected near the point being monitored. Such a proximity of surge protective devices and recording instruments may impact present and future measurement campaigns. Four are outlined below.

1)	Locations where voltage surges were previously identified – assuming no change in the source of the surges – are now likely to experience lower voltage surges, while current surges will occur in the newly installed protective devices.

2)	Not only will the peaks of the observed voltages be changed, but also their waveforms will be affected by the presence of nearby vanistors as illustrated in Figures 4, 5, and 6.

A)  If a varistor is located between the source of the surge and the recording instrument (Figure 4), the instrument will record the clamping voltage of the varistor. This voltage will have lower peaks but longer time to half-peak than the original surge.

B)  If the instrument is located between the source of the surge and a varistor, or if a parallel branch circuit contains a vanstor (Figure 5), the instrument will now record the clamping voltage of the varistor, preceded by a spike corresponding to the inductive drop in the line feeding the surge current to the varistor.

C)  If a varistor is connected between the line and neutral conductors, and the surge is impinging between line and neutral at the service entrance (normal mode), a new situation is created, as shown in Figure 6. The line-to-neutral voltage is clamped as intended, but the inductive drop in the neutral conductor returning the surge current to the service entrance produces a surge voltage between the neutral and the grounding conductors at the point of connection of the varistor and any downstream point supplied by the same neutral. Because this surge has a short duration, it will be enhanced by the open-end transmission line effect between the neutral and grounding conductors [11].

- The surge voltage limitation function previously performed by flashover of clearances is now more likely to be assumed by the new surge protective devices that are constantly being added to the systems.

4)	These three situations will produce a significant reduction in the mean of voltage-surge recordings from the total population of different locations as more and more varistors are installed. However, the upper limit will remain the same for locations where no varistors have been installed. Focusing on the mean of voltage surges recorded in power systems can create a false sense of security and an incorrect description of the environment. Furthermore, the need for adequate surge current handling capability of a proposed suppresser with lower clamping voltage might be underestimated because some diversion is already being performed.

Figure 6 – Protective device installed between line and neutral conductors,

for surge applied in normal mode

## References

[1]  IEEE Standard Dictionary of Electrical and Electronics Terms, ANSI/IEEE Std. 100, 1988.

[2]  T.M. Gruzs, “Power Disturbances and Computer Systems: A Comparison of the Allen-Segall and the Goldstein-Speranza Power Line Monitoring Studies,” Proceedings, 1986 Electrical Overstress Exposition, Nelson Publishing Co., Nokomis, FL, Jan. 1986.

[3]  Guide on Surge Voltages in Low-voltage AC Power Circuits, ANSI/IEEE C62.41, 1980.

[4]  Insulation Coordination within Low-Voltage Systems, Including Clearances and Creepage Distances for Equipment, IEC Std 664, 1980.

[5]  Electromagnetic Emission and Susceptibility Requirements for the Control of Electromagnetic Interference, DOD-STD-461B.

[6]  Interface Standard for Shipboard Systems, DOD-STD-1399, Sec. 300, 1978.

[7]  IEEE Guide on Surge Testing for Equipment Connected to Low-Voltage AC Power Circuits, ANSI/IEEE C62.45, 1987.

[8]  IEC Multilingual Dictionary of Electricity, published by IEEE and distributed in cooperation with Wiley-Interscience.

[9] Guideline on Electrical Power for ADP Installations, FIPS Pub 94, National Bureau of Standards, 1983.

[10] F.D. Martzloff, “The Protection of Computer and Electronic Systems Against Power Supply and Data Line Disturbances,” General Electric Report 85CRD084, Schenectady, NY, , 1985.

[11] F.D. Martzloff and H.A. Gauper, “Surge and High-Frequency Propagation in Industrial Power Lines,” IEEE Transactions IA-22, no. 4., July/Aug. 1986.

_________________

Part II of this article, a detailed review of several site surveys, will appear in the March issue of Powertechnics. This article was based on “Power Quality Site Surveys: Facts, Fiction, and Fallacies,” by F.D. Martzloff and T.M. Gruzs, which first appeared in IEEE Transactions on Industry Applications, Vol. IA-24, No. 6, pp. 1005-1018, Nov./Dec. 1988. © 1988 IEEE

Systems and instruments in site surveys

François D. Martzloff

National Institute of Standards and Technology

Thomas M. Gruzs

Liebert Corporation

Every on-site survey of power quality utilizes a variety of methods and instruments, requiring careful interpretation of survey results.  A close examination of underlying assumptions in nine published surveys shows that some differences can be reconciled, but indicates the need for new or improved standards.

Power quality surveys have been conducted for two reasons: 1) to identify potential problems or causes of equipment disturbances at a specific site, and 2) to develop a broad data base with the hope that the general findings will be applicable in specific cases.  This article gives a review of nine papers reporting broad data base surveys, but the conclusions are also applicable for site-specific surveys.  The review shows problems that readers encounter when different authors use different instruments, different definitions, and as a result sometimes reach contradictory conclusions.  The nine surveys were conducted in the United States and Europe over the last 25 years.  Power systems have not changed much, but the load equipment characteristics, as well as the capabilities of disturbance monitoring instruments, have changed considerably.  Table 1 shows details of the locale, system voltage, instrument type, and connection mode as described in the papers.

Bull and Nethercot, in a 1964 article [11, report monitoring performed in the mid 1960s on 240-V systems in Great Britain with instruments of their design.  Their initial instrument used vacuum tubes, leading to the development of a solid-state circuit which may be considered the forerunner of modem monitors.  The instrument had several channels, each with a different threshold.

The monitoring locations were selected to include a variety of conditions, with data being collected for several weeks at each location over a total period of 2 years.  The results do not mention transients above 600 V; it seems that no channels were provided above that level because the authors were only concerned with the range of 50-600 V.

Martzloff and Hahn, in a 1970 paper [21, report the highlights of measurements made in the 1963 to 1967 period on residential, commercial, and industrial circuits, mostly single-phase 120 V. Waveform data were obtained with commercial, custom-modified oscilloscopes fitted with motor-driven cameras.  These oscilloscopes were installed at various locations where transient activity was suspected, not at randomly determined locations.  In addition, a peak counter circuit was developed, and 90 units with a 1200- or a 2000-V threshold were deployed at 300 locations where there was no prior suspicion of unusual transient activity.

The oscilloscope data gave one of the first indications that the traditional unidirectional impulse, long used for dielectric testing, might not be representative of surges occurring in low-voltage circuits.  The threshold data indicated locations where surges above 1200 V occur frequently (about 3 percent of the sample), while other locations appear far less exposed to surges.  The 100:1 reduction of an alarming failure rate of clock motors, achieved by increasing the surge withstand capability of the motors from 2000 to 6000 V, is documented in that paper.

Cannova, in a 1972 paper [3], reports the monitoring of surges on U.S. Navy shipboard 120- and 450-V power systems in the late 1960s.  Instrumentation used for the initial phase of the monitoring program consisted of oscilloscopes similar to those used by Martzloff.  Provision was also included for the option of measuring the transients alone (through filters) or superimposed on the ac line voltage; this option reflects the old dichotomy, still unsettled to this day, as to whether the transients should be measured as an absolute value or as a deviation from the instantaneous value of the ac sine wave (see the last column of Table 1).

The results are not reported separately for 120. and 450-V systems; therefore, it is not possible to express them in terms of per-unit or percentage of nominal system voltage.  Cannova's statistical treatment aims at fitting the recorded transients to a normal distribution and concludes that a log normal distribution is a better fit.  A brief statement is made on the durations of the recorded transients (without a statement on how those durations are defined), citing a majority of durations between 4 s and 6 s, with a few at 19 s.

From the data base, acknowledged to be a small total number of events, a protection level of 2500 V was defined.  The specification of a 2500-V 1.2/50-s voltage withstand by DOD STD 1399 was derived from this survey.

Two aspects of the conclusions are especially worth noting: 1) there  was no information on the source impedance of the surges' and yet the data eventually served to specify requirements for surge protective devices; and 2) a large difference in frequency of' occurrence was noted among ships of the same type and class, similar to the observations on land surveys.

Allen and Segall, in a 1974 paper [4] report the monitoring of several types of power disturbances at computer sites, performed with oscilloscopes, oscillographs, and digital instruments, in the 1969-1972 period.  Details of the instrumentation were described in a separate paper [5].  Disturbances are described as overvoltages and under-voltages, oscillatory decaying disturbances, voltage spike disturbances, and outages.  The terms sag and "surge" ("swell") had not yet made their appearance in the jargon.

The survey was conducted in two phases.  In a first phase, preliminary information was obtained on ranges of disturbances, leading to the development of a second generation of monitors deployed in the next phase.  The recorded disturbances are described by plots and histograms.  The highest surge recorded in the first phase is shown as 350 V. In the second phase, the monitors grouped all surges into three categories, the highest having a range of 100 percent (of line voltage) to infinity, so that no detailed information is provided to describe high peak values.  The survey does report in detail the occurrence of under-voltages and overvoltages, providing a basis for the comparisons with the Goldstein-Speranza results.

Goldstein and Speranza, in a 1982 paper [61, report the monitoring of several types of disturbances at a variety of locations in the Bell system, with digital multiparameter instruments, in the 1977 and 1979 period.  The conditions of the survey are documented, including instrument locations and definitions of the parameters as well as the methods of data processing.

The findings are briefly reported with emphasis on predictions for disturbances expected at specific sites.  The prediction is obtained by using a statistical model derived for all sites and making adjustments reflecting specific site conditions determined by a limited survey at that site.  The authors are emphatic on the point that the lack of correlation between sites prevents blanket application of the overall findings to any specific site, but that  useful predictions are possible by combining the overall data with limited knowledge on specific site data.

Werntrom, Broms, and Boberg, in a 1984 report published in Sweden and circulated in the United States as an English draft translation [71, report monitoring of industrial 220/380-V systems by digital multithreshold instruments, corroborated by waveform recording with digital storage oscilloscopes.  The parameters to be recorded and reported are defined in an introductory section; however, their description of "common mode" and "differential mode" in the English translation does not correspond exactly to symmetrical and asymmetrical voltages defined by the IEC.

The range of surges recorded extends from 200 to 2000 V.

In a summary tabulation, rise times are shown as ranging from 20 to 200 ns and duration from 0.2 to

2.5 s.  The results show a wide difference of surge activity among sites but a relatively constant slope of the rate of occurrence versus level.

Aspnes, Evans, and Merritt, in a 1985 paper [81, report a survey of the power quality in rural Alaska at isolated power generation facilities.  The monitoring instruments are identified as one of the contemporary commercial digitizing monitors.  A very comprehensive summary of the recordings is presented including frequency deviations (a unique situation in these isolated systems), sags and "surges" ("swells"), impulses (i.e., surges ), and outages.  Some ambiguity arose because of the possibility that built-in surge protection in the monitors might have attenuated the surges being recorded.

Odenberg and Braskich, in a 1985 paper [9], report the monitoring of computer and industrial environments with a digital instrument capable of the simultaneous recording of voltage surges and current surges.  This new capability for relating voltage and current shows a growing awareness of the need to monitor current surges - an improvement over previous surveys limited to the measurement of voltages.  However, the reported surge currents are those of a current toward undefined loads downstream from the instrument; they do not include any measurement of the current through a shunt-connected surge diverter, a measurement that would have provided new information on the source impedance of the surges.

The digital processing applied by the instrument yields two points of the surge: the peak value with the time to reach peak and the time elapsed until decay to 50 percent of the peak value.  From these two points, a "waveform" description is proposed without any other information on the actual waveform.  From a large number of recorded surges (more 250,000 events) a startling finding is cited: 90 percent of the recorded surges have their 50-percent point in a narrow window of 900-1100 s.  Attempts to reconcile this singular finding with the observations reported by other surveys have not been successful.

Goedbloed, in a 1987 paper [10], describes in detail a custom-built automated measurement system monitoring 220/380-V networks in Europe.  The automated measurement system reflects the progress made in digitizing techniques since the days of vacuum tubes.  By combining two commercial recorders with a custom interface, the developers obtained detailed recordings with a 10-ns sampling interval and 20-s window on the first recorder and a 1-s sampling interval and 2-ms window for the second recorder.

The system included a provision for automated data reduction, yielding raw data as well as statistical information on amplitude, rate of rise, energy measure, spectral density, and conversions from time domain to frequency domain.  With a relatively low threshold of 100 V above the line voltage, the distribution of occurrences is weighted toward low amplitudes; nevertheless, occurrences are reported above 3000 V.

# Relative Occurrence of Different Types of Disturbances

Two of the surveys reviewed in this paper have been widely cited, one performed in the early 1970s by Allen and Segall (A-S for short) [4], and the other performed in the late 1970s by Goldstein and Speranza (G-S) [6].  However, the findings do not at first appear to be in agreement; a detailed comparison of these two surveys provides a good illustration of the pitfalls of superficial interpretation of survey results.

A cursory comparison of the results might lead one to conclude that a significant change in power disturbances at computer sites occurred between 1972 (end of the A-S study) and 1979 (end of the G-S study).  A-S reported 88.3 percent of observed disturbances as spikes, impulses, and transients, 11.2 percent as sags, and 0.47 percent as outages.  G-S, on the other hand, reported 87 percent of the observed disturbances as sags, 7.4 percent as impulses, 0.7 percent as "  surges" ("swells"), and 4.7 percent as outages (which they call power failures).

Taking a more careful look at the monitoring thresholds used in each study helps to explain why the number of impulses appear to have decreased and the number of sags appear to  have increased.  Since G-S use a threshold of -4 percent for sags while A-S use - 10 percent, one can expect the G-S study to indicate a higher percentage of sags, because the sags between - 4 and - 10 percent are not included in the A-S study.  Oscillatory decaying disturbances are not specifically identified in the G-S study but are included under the category of impulses.  The threshold for impulses used by G-S (200 V for 120-V lines, or 118 percent) is higher than that used by A-S (+-l0 percent).  Because the rate of occurrence increases steeply for lower amplitude disturbances, one can expect a drastic reduction in the percentage of impulses reported by the G-S study as compared to the A-S study,

The increase in percentage of power outages reported by G-S may be explained by the shift in the number of disturbances observed due to other threshold changes.  Percentages can be a very misleading basis for comparison unless all conditions are equal.  For example, the incidence of power outages observed in both studies is very similar, even though the percentages are one order of magnitude apart; A-S report 0.6 occurrence per month while G-S report 0.4 occurrence per month.

When the disturbance rates at the same thresholds are compared for the A-S data and the G-S model (for 75 percent probability), the results are surprisingly similar.  The conclusions of these two studies are that deep sags contribute about 62 percent of the power system problems which are related to normal mode disturbances, severe impulses are responsible for 21 percent, outages for 14 percent and "surges" ("swells") for 2 percent.

## Differences in Surge Amplitudes

The amplitudes of the surges reported in the surveys vary over a    wide range, and comparisons are difficult because the data are not presented in a uniform format.  An attempt was made to get a quantitative comparison of the amplitudes reported in the surveys; however, the exercise was quickly found to be futile because of the following two main reasons.

- Looking at "maximum values," one finds that in some surveys the quoted maximum is actually a value in excess of the range of the instrumentation, while for others it is the measured value.  There are too few points and information is insufficient to attempt a statistical treatment of this truncated data base.  Furthermore, the quoted value in some surveys is the total voltage (instantaneous value of ac sine wave plus surge), while in others the sine voltage has been filtered out.  When surges are in the range of several thousand volts (the concern being damage), the difference between the two definitions is not significant; however,, when surges are in the range of a few hundred volts (the concern being malfunction), the difference is significant.

- Because the lower threshold of the recorders varies among surveys, and the frequency of occurrences increases dramatically with lower thresholds, the labels of average, median, most frequent, typical, etc., are not meaningful for comparing amplitudes.  The preceding discussion of A-S and G- S results has illustrated the profound effect of threshold selection on reported results when they are expressed in percentages.

A general explanation of differences in amplitudes found in the various surveys might be the observation by some of their authors of the lack of correlation between sites.  Furthermore, some surveys include sites where equipment failures were experienced or expected, while other surveys were made at sites not singled out for particular problems.  Thus the differences in overall results of various surveys might simply be the result of the different surge exposure at the points of monitoring.  This explanation implies that surveys will still be needed where specific information is desired.

## Differences in Waveform

From those surveys made with waveform recording capability, the "typical" forms suggested by each author have been collected in Figure 1.The finding of ringing waves, as opposed to the traditional unidirectional impulses, seems general in these low-voltage circuits. 4

Martzloff and Hahn were among the first to report ring waves.  Their reported measurements were incorporated into the data that resulted in the eventual selection of a 100-kHz Ring Wave with a 250- or 500-ns rise time for the UL Standard Ground Fault Circuit Interrupters [11] and the 0.5-s 100-kHz Ring Wave of the IEEE Guide on Surge Voltages [12].

While Cannova does not report detailed descriptions of the waveforms, the statements "4 to 6 s" and "up to, 19 s" could be interpreted either as a time to half-value or as the time between the initial rise and the first zero crossing of a ringing wave.  Interestingly, that data base led to the specification of a unidirectional longer impulse, the classic 1.2/50 s voltage impulse, for conservative rating of candidate surge protection devices to be installed in the shipboard environment [13].

Wernstrom, Broms, and Boberg show three examples of recordings.  The first is indeed a ring wave with a frequency of about 500 kHz and a rise time of 200 ns.  The second example is a burst of nanosecond-duration transients, similar in shape to the proposed IEC/TC65 Electrical Fast Transients [14].     The third example is (of all things) a unidirectional (almost) impulse.

The data reported by Odenberg and Braskich are different from the others in that only two points of the waveform are peak amplitude.  As such, waveform; furthermore, of their 250,000 recordings show between 900 and 1100 s in Power Quality Surveys unique among all the surveys.

The Goedbloed data presentation reflects concerns addressing interference rather than damage; hence, the emphasis was given to amplitude, rate of rise, and energy rather than waveform.  An oscillogram characterized as "typical" is presented in Figure 1, a ring wave with a frequency of about 800 kHz.

Thus, the ambiguities plaguing the field of site surveys have become apparent to many interested workers, resulting in the formation of a new Working Group Monitoring Electrical quality sponsored by a new IEEE Standard Coordinating Committee on Power Quality.  Stay tuned in this area; contributions to the development of a new standard by this working group are invited and welcome, and further information may be obtained from the authors.

Conclusions

A review of power quality site surveys conducted over the last twenty years reveals interesting facts, and close examination of the results can dispel some fictions and fallacies.

1)	Considerable progress has been made in the recording capabilities of monitoring instruments, mostly as the result of progress in the hardware and software used in digitizing systems.  Among the many improvements are multichannel synchronized recording of different parameters, fast data acquisition, automated data reduction, and improved resolution.

2)	 With the steady progress and expanded capability of instruments, it becomes increasingly important to achieve greater consistency in definitions of the disturbance parameters and the methods of application of the monitoring instruments.

3)	Site-to-site variations in exposures preclude making precise predictions for a specific site from an overall data base, but useful predictions can be made by adjusting the overall data base only slightly by limited data collection at the site of interest.

4)	 The steady increase in the number of surge protective devices being installed in low-voltage power circuits in the last several years can be expected to continue.  The result might be a lowering of the mean values of observed surges but not necessarily the extreme values of the distribution.

5)	Differences among results indicated by a cursory comparison can in many cases be resolved by a closer examination of the conditions under which the surveys were conducted.  However, some differences appear less likely to be explained if raw data have been processed and the initial parameter measurements are no longer available for consideration.  Providing greater detail in the published reports and sharing of experiences at technical meetings might help overcome this difficulty.

6)	A new IEEE Working Group on Monitoring Electrical Quality has been formed with a broad scope that encompasses this process of improving consistency in the definitions and interpretation of power disturbances.  In addition, the IEEE Working Group on Surge Characterization is also attempting to obtain a broader data base for the revision of the Guide on Surge Voltages.  These two groups are ready to provide counsel and forum to any would-be surveyor in planning and reporting the collection of new data on disturbances, thus avoiding later difficulties in incorporating the results in a shared data pool.

References

[1]	J. H. Bull and M. A. Nethercot, "The Frequency of Occurrence and Magnitude of Short Duration Transients in Low-Voltage Supply Mains," Radio Electronic Engineer, Sept. 1964.

[2] 	F. D. Martzloff and G. J. Hahn, "Surge Voltages in Residential and Industrial Power Circuits,"

IEEE Trans. Power App.  Syst., vol.  PAS-89, no. 6, July/Aug. 1970.

[3]	S. F. Cannova, "Short-Time Voltage Transients in Shipboard Electrical Systems," in IEEE IAS 1972 Annual Meeting Conf.  Rec.

[4]	G. W. Allen and D. Segall, "Monitoring of Computer Installation for Power Line Disturbances," presented at the IEEE PES Winter Meeting conference, New York, Jan. 1974, Paper C74199-6.

[5]	G. W. Allen, "Design of Power-Line Monitoring Equipment," IEEE Trans.  Power App.  Syst., vol.  PAS-90, no. 6 Nov/Dec. 1971.

[6]	M. Goldstein, and P.D. Speranza, "The Quality of U.S. Commercial AC Power," in Proc.  INTELEC Conf., 1982.

[7]	H. Wernstrom, M. Broms and S. Boberg, "Transient Overvoltages on AC Power Supply Systems in Swedish Industry," Foorsvarets Forskningsanstalt, Huvudavdelning 3, Sweden, Report FOA E 30002-F2, 1984.

[8]	J. D. Aspnes, B. W. Evans and R. P. Merritt, "Rural Alaska Electric Power Quality," IEEE Trans.  Power App Syst., vol.  PAS-104, no. 3, Mar. 1985.

[9]	R. Odenberg and B. Braskich, "Measurements of Voltage and Current Surges on the AC Power Line in Computer and Industrial Environments," IEEE Trans. Power App.  Syst., vol.  PAS-104, no. 10, Oct. 1985.

[10]	J. J. Goedbloed, "Transients in Low-Voltage Supply Networks," IEEE Trans. Electromagn.  Compat., vol. EMC-29, no. 2, May 1987.

[11]	UL Standard for Safety 943, Ground Fault Circuit Interrupters, Underwriters Laboratories, 1976.

[12]	Guide on Surge Voltages in Low-Voltage AC Power Circuits, ANSI/IEEE C62.41-1980.

[13]	Interface  Standard  for  Shipboard  Systems,   DOD-STD-1399, Sec. 300, 1978.

[14]	Electrical Fast Transients - Burst Requirements, IEC Standard 801-4.

No Joules for Surges:

Relevant and Realistic Assessment of Surge Stress Threats

Thomas Key and Arshad Mansoor		François Martzloff

Power Electronics Applications Center		National Institute of Standards and Technology

Knoxville, TN 37932 USA			Gaithersburg, MD 20899 USA

Abstract: The paper challenges attempts to characterize the surge environment in low-voltage end-users power systems by a single number - the "energy in the surge" - derived from a simple voltage measurement.  Our thesis is that such attempts are neither realistic nor relevant.  The paper shows that these erroneous attempts, based on the classical formula for computing the energy dissipated in a linear load of known resistance, cannot be applied to characterize the environment per se, but only to a well-defined combination of source and load.  In particular, there is no meaningful relationship between the "energy" in a surge event and the energy actually deposited in a varistor by this surge event.  A review of equipment failure or upset mechanisms related to the occurrence of a surge voltage reveals that none of these mechanisms are related to this so-called "energy in the surge." Several failure mechanisms other than energy-related are identified, pointing out the need to describe the surge events with a more comprehensive set of parameters in conducting future surveys.

# I.  INTRODUCTION

In an attempt to characterize the potential threat of surges to voltage-sensitive equipment, recordings of the surge voltages occurring in low-voltage power circuits have been conducted in the last quarter-century, driven by the increasing concern about the vulnerability of new electronic appliances to transient overvoltages.  However, practically all the recording conducted by organizations such as Bell Laboratories [I], Canadian Electrical Association [2], General Electric [3], IBM [4], National Power Laboratory [5] and other researchers, including Goedbloed [6], Hassler & Lagadec [7], Meissen [8], and Standler [9] have been limited to the measurements of transient voltages

Interest in these measurements has been re-kindled by several investigations aimed at assessing power quality in end-user facilities.  These recordings, initially limited to measurement of peak voltages, were perfected with the help of increasingly sophisticated voltmeters.

Early surveys were conducted with conventional oscilloscopes and later on, portable digital instruments with onboard computing became available.  While these instruments made possible the recording of a voltage transient as a function of time and graphical presentation of data, the recording of such a surge voltage profile does not lend itself to a simple description by a single number.  To circumvent this difficulty, many researchers called upon the basic concept of energy to characterize the level of surge threat in terms of voltage.

Referring now to classical electrical engineering, the instantaneous power dissipated in a resistor by a transient voltage is merely the square of the applied voltage, divided by the resistance.

Taking the integral over the duration of the transient yields the energy.  By analogy, the "energy" of a surge could then be computed from the voltage measured at some point of a power system.  According to this intuitive concept -- but fallacious as we will show -- the greater the measured voltage, the greater the "energy" and thus the greater the threat to potential victim equipment.

A review of the known failure or upset mechanisms of various types of devices and equipment identifies several surge parameters other than energy-related.  These include source impedance, peak amplitude, maximum rate of rise, tail duration, and repetition rate.  Therefore, future surveys of surge events conducted with present monitoring instruments or with even better instruments will need to include more comprehensive -- and hopefully standardized methods of presenting and interpreting the results.

## II. THESIS

Our thesis is that neither the threat nor the "energy level" of a surge can be characterized by simply measuring the voltage change during a surge event.  Any reference to the concept of "energy of a surge" should definitely not be introduced.  Such avoidance is based on two facts:

1.	A voltage measurement of the surge event cannot alone predict the energy levels affecting the devices exposed to that surge.  This is particularly true for nonlinear surge-protective devices where energy deposited in the device is relevant, but has little to do with the misleading concept of " energy in the surge" derived from an open-circuit voltage measurement.

2.	There are other than energy-related upset or failure modes of equipment.  These effects require consideration of other parameters when describing a surge event to yield relevant and realistic assessment of surge stress threats.

Our thesis will be supported by an analysis of the impact of surges on equipment, and illustrated by numerical examples of varistor applications showing how the description of a surge by its "energy" could then lead to vastly different conclusions.

## III.   INTERACTIONS BETWEEN SURGES AND VICTIM EQUIPMENT

At this point we need to identify the devices and equipment that may become the victims of a surge, and their failure mechanisms.  After-the-fact investigations and experimental data show a wide range of surge-related upset and failure mechanisms.

These mechanisms include insulation breakdown, flashover, fracture, thermal and instantaneous peak power overloads, dv/dt and di/dt limits being exceeded.  The following list gives some generic types of surge victims and the typical failure or upset mechanisms.

1.	Electrical insulation, where the failure mechanism (breakdown or sparkover) is principally a function of the surge voltage, with the complication of a volt-time characteristic such that failure under impulse occurs at a level that increases when the rise time or duration of the impulse decreases.  "Insulation" is to be taken in the broadest sense of solid or liquid material separating energized conductors in equipment, clearances on a printed circuit board, edges of semiconductor layers, etc.  A distinction must be made between the initial breakdown of insulation, related to voltage only, and the final appearance of the damaged insulation, related to the total energy dissipated in the breakdown path.  In another situation, the insulation of the first turns of a winding may be subjected to higher stress than the others as the result of the uneven voltage distribution resulting from a steep front rather than only the peak value of the surge.

2.	Surge-protective devices, for which the voltage across the device is essentially constant, and the energy deposited is a function of the surge current level and duration.  One failure mode of such a device will occur when the energy deposited in the bulk material raises the temperature above some critical level.  Failure modes associated with the current level, such as flashover on the sides of a varistor disc, failure at the boundary layers of the varistor grains, or fracture of large discs, have also been identified and are not related to energy.

3.	Semiconductor devices, such as thyristors responding to the rate of voltage change can be turned on by a surge [10], resulting in failure of the device or hazardous energizing of the load they control.  In a similar way, a triac may be turned on by a voltage surge without damage, but still fail by exceeding the peak power limit during a surge-induced turn-on with slow transition time.

4.	Power conversion equipment, with a front-end dc link where the filter-capacitor voltage can be boosted by a surge, resulting in premature or unnecessary tripping of the downstream inverter by on-board overvoltage or overcurrent protection schemes.

5.	 Data-processing equipment, where malfunction (data errors) -- not damage -- may be caused by fast rate of voltage changes (capacitive coupling) or fast rate of current changes (inductive coupling) that reflect the initial characteristic of the surge event.  This response is insensitive to the "tail" of the surge, where all the "energy" would be contained according to the misleading energy-related concept.

6.	Light bulbs, which of course have a limited life associated with filament evaporation and embrittlement - a long-term process where the short burst of additional heating caused by a few microseconds of overcurrent is negligible -- but also fail under surge conditions when a flashover occurs within the bulb, triggering a power-frequency arc that melts out the filament at its point of attachment -- another failure mechanism originating with insulation breakdown.

Among these types of victims, only the clamping-type varistor, exemplified by the metal-oxide varistors that became so prevalent after their introduction in the mid-seventies, is directly sensitive to an energy level associated with a surge event -- and at that, the energy deposited in the device', not the "energy in the surge." (To be absolutely correct, the ultimate failure mode of a triac or a light bulb may be indirectly influenced by the energy dissipated in the device during the surge, but the root cause, the trigger, of the failure is not the energy.) Considering the explosive proliferation of varistors, however, one might find some extenuating circumstances in emphasizing the significance of energy in describing the effect of surges on its principal target -- the ubiquitous metal-oxide varistor -- but this is a pitfall, a mental trap.

## IV.  BAITING THE TRAP

From the interactions described above, it is clear that using a single voltage measurement to determine surge threat is not sufficient.  The trap was baited by the simplicity and ease of using a single parameter obtained by analogy with the power dissipated in a fixed resistance, v2/IR by an instantaneous voltage, v. Clearly in that limited case, the total energy involved over the surge event would be the time integral of v2/R, expressed by a number having the same dimensions as watt-seconds, or joules in the SI system.  And thus some power quality monitors placed on the market in the early eighties were printing out surge event characterizations expressed in joules.  This "joule" number was obtained by computation of the v2 / R dt, where the voltage v was measured by the instrument, divided by a resistance (taken arbitrarily as 50 ), and integrated over the duration of the event.  Manufacturers of power quality monitor soon recognized the potentially misleading aspects of such reporting and discontinued the practice

Nevertheless, some researchers continued the practice and are to this day attempting to characterize the surge environment by the single parameter of "energy in the surge." As a half-way measure, some are now proposing a new parameter "specific energy" to be understood as the integral of voltage-squared divided by a reference resistance of 50  (why that particular value ?) and they would report results in watt-seconds.  Figure 1 shows an example of this type of reporting [11].

Figure 1 – Example of survey results with number of occurrences

as a function of “energy” in milliwatts-seconds

Acknowledging that indeed, the selection of an appropriate varistor should reflect the level of threat to which it will be exposed, there is a need to characterize the threat in terms of the energy that will be deposited in the varistor by a specific surge event.  However, there is no way that a voltmeter measurement only, even if it includes time, can provide that information.

V.   THESIS DEMONSTRATION BY VARISTOR APPLICATIONS

To demonstrate our thesis by the ad absurdum process, we will compute the "energy in the surge" as defined by the trap-baiting definition of "specific energy" for three surge events such that all have the same "specific energy" but different voltage levels, waveforms, and durations.  Then, making a further assumption for the unknown impedance of the surge source, we will compute the energy actually dissipated in the varistor for these different voltage levels, waveforms, and durations, and observe that the resulting deposited energy is not the same!

1.  Elementary example – basic calculation, fixed impedance

As a first easy-to-follow step, we take three rectangular pulses, all selected to have the same "specific energy" but different voltage levels and corresponding durations, and compute the energy deposited in a (nonlinear) varistor having a given maximum limiting voltage, assuming that the source of the surge is a voltage source with some arbitrary, fixed impedance.

It is noteworthy that some source impedance has to be presumed, because the varistor clamping action rests on the voltage divider effect of the source impedance and the dynamic varistor impedance prevailing for the resulting cur-rent.

Start with an assumed surge measurement of 1000 V with duration of 50 s.  The specific energy of such a surge event, according to the proposed definition, is:

(1000 V)2 x 50 s / 50  = 1 joule.

Now consider a surge with amplitude of 316 V (1000 / 10) and duration of 500 s (50 x 10).  Its specific energy, is:

(316 V)2 x 500 s / 50  = 1 joule.

To complete the bracketing range, consider a surge of 3160 V (1000 x 10), and a duration of 5 s (50 / 10).  Its specific energy is:

(3160 V)2 x 5 s / 50  = 1 joule.

We now apply each of the three voltage surges to a 130-V rated varistor (200 V at 1 mA dc), assuming an arbitrary source impedance of Zs = 1 . One can compute the resulting current or, for this simple example, make a fast-converging manual iteration without the help of a computer, as follows:

(a)	assume a current I, and look up the resulting voltage Vv on the varistor I-V characteristic;

(b)	 compute [Zs x I];

(c)	is [Zs x I]+ Vv = 1000V?

- If yes, I is correct, the energy deposited in the varistor is

I x Vv x t

If no, go back to (a) with a converging assumption for I.

Table I shows the results from this manual iteration for the three surges defined above.  It is quite apparent that the constant "specific energy" for the three surges does not result in the same energy deposition.  The dynamic impedance (Vv/I) of the varistor is also shown, to illustrate the well-known theorem that the power dissipated in a resistive load reaches a maximum for matched source-load impedance.  This theorem is yet another reason why a surge to be applied to a varistor cannot be characterized in the abstract: one needs to know the source impedance (real and imaginary components) as well, to assess the energy sharing between source and load.

2.  Calculation with changing the surge source impedance

As the next step toward reality, we repeat the manual computations for different values of the impedance of the voltage source, still for the same "measured specific energy" and for the case of the 1000 V rectangular pulse.  Somewhat arbitrarily, but no more arbitrary than the 50- value used in the definition of "specific energy", we select three values of the source impedance.

Bear in mind that the reported measurements of surge voltages have never provided any information on the system source impedance to be associated with the reported surge.  As a further oversimplification (an unjustified step in the real world), we will accept the assumption implied in the computation of the "specific energy" that this impedance has only real components, or is a characteristic impedance.  Three values are used in the following examples.

TABLE I

Energy deposited in a varistor by a surge, as a function of surge parameters

-	50  to go along with the proposed definition of "specific energy" (high-frequency measurements are often made in a 50- environment and may be the reason for the value selected in the proposed definition).

-	2 , the so-called effective impedance of a Combination Wave generator, which is "deemed to represent the environment" as stated in the ANSI/IEEE Recommended Practice C62.41-1991 [12];

-	 400 , a number sometimes cited as the characteristic impedance of an overhead line.

Again here, a simple manual iteration yields the result by postulating a varistor current, looking up the corresponding voltage on the I-V curve, such that this voltage is equal to the driving surge voltage, reduced by the voltage drop in the source for the postulated current.  Table 2 shows the results for the three examples of assumed source impedance and a 130-V rated varistor.

3.  Computer calculation with multiple combinations

We now compute the energy deposited in three varistors of three different maximum limiting voltages, for three combinations of voltage levels and durations that produce the same "specific energy," each with classical waveform (Ring Wave, Combination Wave, Long Wave), sized to produce 1 joule of energy dissipation in a 50- resistor, according to the classical formula cited earlier, and for three values of source impedance.  We can anticipate that the peaks will be quite different, foreboding very different effects on equipment.  In fact, the peaks turned out to be 3 kV, 1.2 kV, and 220 V respectively for the three waveforms.  Applying these three waveforms to a family of varistors typically used in 120-V or 240-V power systems, we computed the energy deposited in these varistors for three arbitrary source impedances (assumed to be ohmic), using the EMTP program [13] to input closed-form equations for the open-circuit surge voltage.  With the 220-V level of the Long Wave, predictably the current in a 130-V rated varistor is very low and the resulting energy deposition is negligible.  The results for the Ring Wave and Combination Wave are shown in Table 3. These simple illustrations show that the concept of "specific energy" cannot be used to select a candidate varistor energy-handling rating.

## VI.  HOW TO PROCEED IN FUTURE SURVEYS

In an effort to acknowledge the legitimate quest for the single number characterization, we should offer alternatives, not just stay with a negative vote     The solution might be to tailor the surge characterization to the intended application, that is, take into consideration the failure mode of the specific equipment, and present the data in a form most suited for that equipment.  Of course, this would mean not only avoiding a single number, but actually providing combinations of parameters, each combination best suited to a particular type of victim equipment, according to their failure modes.

Another consideration that must be observed in conducting and reporting the monitoring of surges is the proliferation of SPDs in end-user installations.  It is unlikely today to find an installation where some SPD is not present, either as a deliberate addition to the system, or as part of the connected equipment.  Aware of this situation, some researchers have attempted to disconnect all known SPDs from the system being monitored so that results would represent the "unprotected location" situation such as that initially described in IEEE 587-1980 [14], the forerunner of ANSI/IEEE C62.41-1991 [12].

However, even this precaution of disconnecting all known SPDs does not guarantee that some undetected SPD might not have been left connected somewhere and thus invalidate the record.  Thus, extreme caution must be applied to reporting and interpreting voltage monitoring campaigns conducted after 1980.

The recently-approved IEEE Recommended Practice Std 1159 on Monitoring Power Quality [15] offers guidance on conducting surveys, including not only surges, but other parameters.  The Working Group that developed this standard has now established task forces to develop further recommendations on processing and interpreting the recorded data, including more uniform formats.

Table 4 presents a matrix of surge parameters and types of equipment, showing for each type of victim which surge parameter is significant or insignificant.  The authors have sought to identify all types of potential victims (and invite additions to this list).  Inspection of Table 4 reveals that the [v2 x dt] integral, alone, is not directly involved in the failure of any of the listed equipment.

TABLE 2

Energy deposited in a varistor by a “1-joule surge” for three different values of source impedance

## TABLE 3

Energy deposited in varistors by Ring Wave and Combination Wave "1-joule surges" for different source amplitudes and varistor nominal voltages

TABLE 4

Significant surge parameters in the equipment failure modes

VII.  CONCLUSIONS

The attempt to characterize the surge environment by a single number -- the "energy in the surge" or "specific energy" -- is a misleading approach that should most definitely not be used in Power Quality research.  There are at least three reasons for this prohibition:

1.   The concept that energy can be defined in the abstract from a single measurement of voltage across the lines of an undefined power system is a faulty oversimplification.

2.   The potential victims of a surge event have responses that reflect their design and for many, their failure modes can be totally independent of any energy consideration.

3.  The prime interest of energy consideration is related to the energy-handling capability of metal-oxide varistors.  The energy deposited in such a device by a given surge event depends on amplitude, waveform, source impedance, and varistor characteristics, and not on the "effective energy."

Future surveys should be conducted keeping in mind the relevant parameters for characterization such as peak amplitude, maximum rate of rise, tail duration -- but not "energy."  Furthermore, a relevant and realistic assessment of surge stress threats must consider not only all the characteristics of a surge event, but also the source of the surge and the failure mechanisms of potential victim equipment.

## VIII.  ACKNOWLEDGMENTS

Support for the development of this thesis, motivated by the discussions and contributions of IEEE and IEC colleagues, was provided by Delmarva Power & Light and by Pacific Gas & Electric.  Support for the modeling was provided by the Electric Power Research Institute.

## IX.  REFERENCES

[1]	Goldstein, M. and Speranza, P., "The Quality of U.S. Commercial AC Power," IEEE - INTELEC Conference Proceedings, 1992.

[2]	Hughes, B. and Chan, J.S., 'Canadian National Power Quality Survey Results," Proceedings, PQA '95 Conference, EPRI, 1995.

[3]	Martzloff, F.D. and Hahn, G.J., "Surge Voltages in Residential and Industrial Power Circuits," IEEE Transactions PAS-89, No.6, July/August 1970.

[4]	Allen, G.W. and Segall, D., "Monitoring of Computer Installations for Power Line Disturbances," IEEE Winter Power Meeting Conference Paper WINP WR C74, 1974.

[5]	Dorr, D.S., "Point of Utilization Power Quality Study Results," IEEE Transactions L4-31, No.4, July/August 1995.

[6]	Goedbloed, J.J., "Transients in Low-Voltage Supply Networks," IEEE Transactions EMC-29, No.2, May 1987.

[7]	Hassler, R. and Lagadec, R., "Digital Measurement of Fast Transients on Power Supply Lines," Proceedings, Third Symposium on EMC, Rotterdam, 1979.

[8]	Meissen, W., "Overvoltages in Low-Voltage Networks" (In German), Elektrotechnishe Zeitschrift, Vol. 104, 1983.

[9]	Standler, R.B., "Transients on the Mains in a Residential Environment," IEEE Transactions EC-31, No.2, May 1989.

[10]	Goulet, K, "Susceptibility of Power Semiconductor-based Equipment to Power Line Disturbances," Conference Proceedings, Power Quality 1989.

[11]	Scheuerer, F., "Research on the Isolation Properties of Solid Insulation Upon Occurrence of HF Overvoltages, (In German) Doctoral Thesis, Darmstadt University, 1993.

[12]	ANSI/IEEE C62.41-1991, IEEE Recommended Practice on Surge Voltages in Low- Voltage AC Power Circuits, (Reaffirmed 1995).

[13]	EPRI Report EL-6421-L, Electromagnetic Transient Program (EMTP), Version 2.0, Volumes 1 and 2, July 1989.

[14]	IEEE 587-1980, IEEE Guide on Surge Voltages in Low- Voltage AC Power Circuits, 1980.

[15]	IEEE 11 59-1995, IEEE Recommended Practice for Monitoring Electrical Power Quality, 1995.

SURGE RECORDINGS THAT MAKE SENSE:

# Shifting focus from voltage to current measurements

François D. Martzloff

National Institute of Standards and Technology

Gaithersburg MD 20899 USA

Abstract - The paper proposes to establish a program for characterizing surge events according to the capability of a surge event to deliver a surge current through the power system in end-user facilities.  This characterization would replace the conventional and by now misleading monitoring of surge voltages.  The new approach will use a current transducer including a silicon-avalanche diode with the lowest possible voltage to "attract" surges away from other surge-protective devices connected within the facility.  The voltage signal from the current transducer will then be recorded using any power quality monitoring instrument available to the individual researchers, providing complete current waveform parameters.

1.  INTRODUCTION

1.1  Background

Characterizing the surge environment has been a subject of research for the last forty years, driven by the increasing concern about the vulnerability of new electronic appliances to transient overvoltages.  However, practically all the recording campaigns conducted by major organizations such as ERA (Bull and Nethercott, 1964) [1], General Electric (Martzloff & Hahn, 1970)[2], IBM (Allen & Segall, 1974)[3], Bell (Goldstein and Speranza, 1982) [4], Canadian Electrical Association (Hughes & Chan, 1995)[5], National Power Laboratory (Dorr, 1995)[61 and other researchers, including Hassler & Lagadec (1979)[71, Meissen (1983)[8], Wernstrom et al. (1984)[91, Goedbloed (1987)[10], Standler (1989)[11], and Forti & Millanta (1990)[12] have been limited to the measurement of transient voltages.

We now propose a change in the protocol for the monitoring of power quality in ac power systems.  This change has become necessary because end-user power systems are no longer what they were at the time the early surveys of transient overvoltages were conducted.  Varistor-based surge-protective devices (SPDs) have become so ubiquitous in low-voltage ac power systems that hardly any location ea be found where there is not some form of transient voltage limitation in effect.  Attempting now to characterize the environment so that appropriate SPDs could then be prescribed for specific locations based on voltage measurements would be quite misleading.  What such measurement would yield today is no longer the surge characteristics of the monitored system, as it was at the time of the early surveys, but the residual voltages of whatever SPDs are installed nearby.

1.2  Making meaningful measurements

The proposed change in monitoring practices is to insert a current transducer between the low-voltage power system being monitored and the existing monitoring instruments.  This transducer would consist of an SPD with the minimum tolerable voltage rating across the power line, to be connected at some point of an installation, and serve as a "magnet" for attracting the impinging surges.  To use a metaphor, this SPD in effect becomes the "winning bidder" by offering to the impinging surge the path with lowest clamping voltage among all the parallel-connected SPDs of the installation.

A current transformer with the "magnet SPD" in the primary and an appropriate burden on the secondary would be used to feed the resulting voltage signal into the existing power quality monitoring instruments now used by many organizations and individual researchers.  In this manner, the surge current attracted by the "magnet SPD" can be recorded to find the true character of surge events at that particular location, despite the presence in the local system of any and many unknown and uncontrolled SPDs.

II.   TRANSDUCER DESIGN

II.1  Breadboard design

Preliminary results on the feasibility of such a recording system have been obtained: a suitable silicon avalanche diode has been identified and proven to act as a "magnet," even in the presence of "competing" metal-oxide varistors, and yet able to withstand the temporary overvoltages that can occur in the system.  At this point, the transducer design principle is well defined, and concerns that the "magnet" effect could be effective only within a small power system have been addressed, as discussed later in the paper.

The current transducer would consist of a string of silicon avalanche diodes (SADs) in series with the primary of a current transformer with a burden connected across its secondary, an overcurrent protective fuse in series with the diodes, and an indicating light to signal a blown fuse.  In the final design that would be used to deploy a number of these transducers, all of these components will be included in a package derived from the so-called "plug-in SPD" which are offered by many manufacturers.  Using the external package of such a device will provide a low-cost envelope to build a few hundred transducers with no tooling costs and yet provide a package suitable for connection to wall receptacles in end-user systems.

The power system can include several branch circuits to supply the loads, some of which featuring SPDs incorporated into load equipment or installed by the end-user.  At some point of this system, selected for convenience by the instrument operator, the transducer will be installed.  A key point of the proposal is that pinning down the actual location of the monitor is no longer a concern because of the ,'magnet" effect of the low-clamping SAD string.

Figure 1 shows a schematic diagram of the transducer.  Selection of an appropriate string of SADs is an exercise in brinkmanship: the SAD string must have a clamping voltage sufficiently low to make it the winning bidder, and yet not so low that the temporary overvoltages occurring in the power system would destroy it.  In a preliminary experiment, a SAD string with a nominal voltage of 185 V at 1 mA de was found to survive exposure to 130% of nominal 120 V system voltage, ensuring sufficient distance from the brink of failure.

###### Figure 1 – Schematic of the transducer

It will be prudent to include a fuse in series with the SAD string for the case where a large surge would exceed the current-handling capacity of the SAD string and cause its failure.  A visible indication of a blown fuse can be added to the package, similar to the indication now routinely provided by the commercial plug-in SPDs offered for residential use.

A commercially available and low-cost current transformer* has been identified that can provide sufficient accuracy for the measurements over a sufficient frequency range.  Conventional current-viewing transformers used in the laboratory are much more expensive and would not be necessary for the purposes of the recordings.  Considering the wide range of surge events and the resulting statistical uncertainty in citing "representative values" of the surge events, obtaining results of current measurements within an order of magnitude is already a very large improvement over the present lack of knowledge.  In the example of recording capability discussed later in the paper, there is a 50:1 difference in the cost of a laboratory-type current-viewing transformer and the low-cost current transformer required for deployment of a large number of monitors.

* Please note that the author has no vested interest in promoting or endorsing any hardware, and that the final selection of the current transformer is still an open design tradeoff consideration. Commercial availability is cited here only in support of the concept of using readily available, low-cost component sfor the deployment of many transducers.

Matching the burden values to the voltage requirements of the monitor input circuits has not yet been done at the time of this writing, but might be reportable by the time of presentation of the paper.  Tradeoff between the cost of the current transformer and its frequency response is another area where improvements to the proposal can be made to obtain meaningful recordings at a cost that will not be a deterrent to acceptance of the proposal.

## II.2  Radius of attraction

By design, the string of diodes is intended to become the “magnet” that will attract the impinging surges. We recognize that this winning bid can be ensured only within a certain radius from the transducer. Increasing distances between the transducer and competing SPDs eventually produces a decoupling of the two devices and might allow a competing SPd connected upstream from the transducer to divert the surge first. This situation is the reverse of that sought when making studies of the coordination of cascaded SPDs, where the concern is to ensure that a heavy-duty SPD located upstream of a lower-duty SPD is sufficiently decoupled so that an impinging surge will be diverted by the upstream SPD. The parameters of cascade coordination have been addressed at length in the literature [13]. [14], [15] and will not be discussed here, but serve as a useful reminder to take a careful look at possible limitiation in the radius of meaningful measurements.

To ascertain that the transducer will remain the winning bidder, a simple test was performed by assembling a physical mock-up of an installation with a service panel feeding three branch circuits, with lengths of 4.5 m, 9 m, and 18 m respectively. The SAD string was connected at the end of one branch circuit while metal-oxide varistors (MOVs) with nominal 200 V at 1mA dc were connected at each end of the other branch circuits.

##### Figure 2 – Arrangement of competing SPDs

We can expect that the least favorable combination would be that of the SAD connected at the end of the longest branch circuit, with an SPD of relatively low clamping voltage installed at the end of the shortest branch circuit.  A Combination Wave [16] was applied to the service panel, and the currents in the three branch circuits were monitored, with the SAD string successively connected at the end of the 4.5 m, 9 m, and 18 m branch circuits.  In all three cases, the SAD attracted all the surge current, with no current detected in the MOV-terminated branch circuits.

More sophisticated analysis can be performed by applying the numerical modeling techniques developed in the referenced modeling studies [17], [18], extending the distances and combinations of competing SPDs from the simple example shown in Figure 2 to determine how extensive an installation can be and still have the transducer remain the winning bidder.  In this manner, the pitfall that threatens credibility of contemporary voltage recordings (uncertainty about other unknown SPDs connected in the system that can produce misleading results of low surge activity) will be eliminated.

## III.  BREADBOARD TEST

A simple breadboard was assembled with the 185 V SAD string connected to the output of an 8/20 s surge generator and a 100  resistance inserted in series to limit the current delivered by the low-impedance generator.  The resulting current (longer than 8/20 s because of the inserted resistance) was applied to the one-turn primaries of a laboratory-grade current-viewing transformer and of the low-cost current transformer, with a 2 k burden across its secondary.  Their secondary output voltage was recorded by a laboratory-grade digital signal analyzer.  Figure 3 shows the recorded voltage across the SAD string and the two current signals.

###### Figure 3 – Voltage across the SAD string and corresponding current signals

To make the comparison easier, the signal analyzer input sensitivity of the two current-displaying channels was adjusted so that the two current signals would coincide near their peaks.  The point to be made here is not the actual numerical values, but the quality of the frequency response of the low-cost transducer, illustrated by a time-domain representation of an impulse.

Inspection of the two current traces shows a loss of signal at the front as well as in the tail, symptomatic of a limited frequency response.  While such a loss would be absolutely intolerable in a laboratory environment, we must place it in its proper perspective.  As outlined in the introduction, we are now facing a new situation, brought about by the proliferation of SPDs, where surge voltage measurements no longer have the significance they once bad, so that we have no knowledge on the real surge threat existing in the system.  The current-delivery capability of the surge event, as recorded by the imperfect current transducer is an immense improvement over the present total lack of knowledge.

Given the wide range of possible surge events, the relatively small loss of information represented by the two areas separating the two current signal traces is small compared to the common area that represents a good estimate of the order of magnitude of the current-delivery capability of the recorded surge event.  In contrast to laboratory measurement researchers, operators and users of field surveys are already content to have the surge events characterized within one order of magnitude when the alternative is no meaningful information at all.  As discussed earlier, tradeoff between transducer cost and quality of the frequency response is still an open consideration, for which comments from interested parties are earnestly invited before implementation of the proposal is initiated.

## IV.  PROGRAM IMPLEMENTATION

The next step in making the change from surge voltage recording to surge current recording would be to recruit enough participants willing to acquire the transducer and use their existing commercial monitor(s) to record the occurrences of surge currents attracted by the transducer.  This transducer could be produced in cooperation with some manufacturer of a plug-in SPD, so that a readily adaptable outside package could contain the transducer components and provide a simple and safe way of connecting it to a receptacle.

Within the IEEE, a new Task Force of the Standards Coordinating Committee on Power Quality is developing protocols for reporting monitoring results; hopefully, the concepts presented in this paper will   be taken into consideration by that Task Force and by other organizations interested in making surveys for characterizing the electromagnetic environment.  The IEC is also considering the development of guidance  documents on measurement methods in the area of power quality, where this shift of focus should be taken into consideration.

The author is volunteering to collect and compile the statistics of the recordings that would be made with the new transducer.  Individual researchers and organizations are invited to contact the author with comments, suggestions of alternate approaches, and ideas for implementing this change in characterizing the surge environment that will make sense in the new environment of proliferating surge-protective devices.

### V.  CONCLUSIONS

1 .	Given the proliferation of SPDs, the need to replace the recording of surge voltage events by the recording of the capability of surge events to deliver a current into load equipment in particular SPDs has been identified.

2.	Tests made on a breadboard design using readily available components show that meaningful surge current recordings can be obtained, even with a very low-cost design.  Improvements in the frequency response could be obtained by a tradeoff in component costs and refinements of the design.

3.	Implementation of a program may be possible if sufficient interest is aroused by the proposed change in conducting field surveys of surge events.

4.	Standards-writing bodies concerned with characterizing the electromagnetic environment in low-voltage power systems could make an important contribution by giving recognition to the new situation and shifting focus from surge voltage measurements to surge current measurements.

## VI.   ACKNOWLEDGMENTS

Support for the development of this paper was provided by the Power Quality research groups of Delmarva Power & Light, and Pacific Gas & Electric.  Support for the prototype testing was provided in part by the Electric Power Research Institute.

VII.  REFERENCES

[1]  Bull & Nethercott "The Frequency of Occurrence and the Magnitude of Short Duration Transients in Low-voltage Supply Mains," The Radio and Electronic Engineer, Sept 1964, pp 185-190.

[2]  Martzloff & Hahn, "Surge Voltages in Residential and Industrial Power Circuits, " IEEE Transactions PAS -89, No.6, July/Aug 1970, pp 1049-1056.

[3]  Allen & Segall, "Monitoring of Computer Installations for Line Disturbances," Paper C74199-6, IEEE PES Winter Meeting, 1974.

[4]  Goldstein & Speranza, "The Quality of U.S. Commercial AC Power," Intelec Conference Proceedings, 1982, pp 28-33.

[5] Hughes & Chan, "Canadian National Power Quality Survey Results," Proceedings, PQA'95 Conference, EPRI, 1995.

[6]  Dorr, "Point of Utilization Power Quality Study Results," IEEE Transactions IA-31, July/August 1995.

[7]  Hassler & Lagadec, "Digital Measurement of Fast Transients on Power Supply Lines." Proceedings, Third Symposium on EMC, Rotterdam May 1979, pp 445-448.

[8]  Meissen, "Ueberspannungen in Niederspannungsnetzen," ("Overvoltages in Low-Voltage Networks"), Elektrotechnishe Zeitshrift, Vol 104, 1983.

[9] Wernstroem, Broms, & Boberg, "Transient Overvoltages on AC Power Supply Systems in Swedish Industry,"   Report FOA E 30002-E2, Sweden, 1984.

[10] Goedbloed, "Transients in Low-Voltage Supply Networks," IEEE, Transactions EMC-29, May 1987.

[11] Standler, "Transients on the Mains in a Residential Environment," IEEE Transactions EMC-31, May 1989.

[12] Forti & Millanta, "Power-Line Impedance and the Origin of Low-Frequency Oscillatory Transients," IEEE Transactions EMC-32, No.2, May 1990.

[13] Lai & Martzloff, "Coordinating Cascaded Surge Protection Devices: High-Low versus Low-High," Conference Record, IEEE-IAS 1991 Annual Meeting, pp 1812-1819.  Also in IEEE Transactions, IAS-29 No.4, July/August 1993, pp 680-687.

[14] Hostfet, Hervland, Nansen, & Huse, "Coordination of surge-protective devices in power supply systems: Needs for secondary protection," Proceedings, 20th International Conference on Lightning Protection, 1992.

[15] Rousseau & Perche, "Coordination of Surge Arresters in  the  Low-Voltage  Field,"  Proceedings,   17th  International Telecommunications Conference (INTELEC 95), 95CH35824, pp 119-125.

[16] IEEE/ANSI C62.41-1991, “Recommended Practice on Surge Voltages in Low-Voltage AC Power Circuits."

[17]  Martzloff, Mansoor, Phipps, & Grady, "Surging the Upside-Down House: Measurements and Modeling Results," Proceedings, PQA'95 Conference, EPRI, 1995.

[18]  EPRI, "Electromagnetic Transients Program (EMTP), Version 2; Vol.  I-, Main Program; Vol. 2: Auxiliary Routines" EPRI Report EL-6421-L, July 1989.

## SURGE RECORDINGS THAT MAKE SENSE

# Joule Deposition: Yes! - "Joule Content": Never!

Geoffrey Lindes		Arshad Mansoor	  François Martzloff		David Vannoy

Delmarva Power		Power Electronics	  National Institute of		Delmarva Power

& Light Company	Applications Center	  Standards & Technology		& Light Company

Abstract

This paper offers a rationale for avoiding attempts to characterize the surge environment in low-voltage end-user power systems by a single number -- the "energy in the surge" -- derived from a simple voltage measurement.  Numerical examples illustrate the fallacy of this concept.  Furthermore, based on the proliferation of surge-protective devices in low-voltage end-user installations, the paper draws attention to the need for changing focus from surge voltage measurements to surge current measurements.

### Introduction

Sensible application of surge-protective devices (SPDs) requires that the capability of a candidate SPD be sufficient to absorb the energy that an impinging surge could deposit in the device.  This eminently rational approach, however, was derailed when the erroneous concept was proposed that one could measure the "energy in the surge" and thus prescribe an easy match of the energy-handling capability of an SPD to the "energy" of its environment.

In a more recent approach by standard developers, an attempt was made to express this concept as a “specific energy” that would normalize it with respect to a postulated resistance of a device exposed to the impinging surge.  Our thesis is that such attempts are neither realistic nor relevant.  We will show that these erroneous attempts, based on the classical formula for computing the energy dissipated in a linear load of known resistance, cannot be applied to characterize the environment.  There is no meaningful relationship between the “energy” in a surge event as derived (erroneously) from the single voltage measurement and the energy actually deposited in a varistor by this surge event.

Furthermore, the results obtained when recording surge voltages conducted since the mid-eighties have now become questionable as a result of the proliferation of surge-protective devices.  It is very doubtful that a surge voltage monitor, installed in a typical end-user facility, will record anything but the residual voltage of unknown SPDs in the installation – which is no measure of the threat of an incoming surge.  Only a surge current measurement in a candidate SPD can assess the threat.

A review of equipment failure or upset mechanisms related to the occurrence of a surge voltage reveals that none of these mechanisms are related to this so-called "energy in the surge." Several failure mechanisms other than energy-related are identified, pointing out the need to describe the surge events with a more comprehensive set of parameters in conducting future surveys.

The Fallacy of Joules Content

In an attempt to characterize the potential threat of surges to voltage-sensitive equipment, recordings of the surge voltages occurring in low-voltage power circuits have been conducted in the last quarter-century, driven by the increasing concern about the vulnerability of new electronic appliances to transient overvoltages.  However, practically all the recording campaigns conducted by major organizations such as ERA (Bull and Nethercott, 1964)1, General Electric (Martzloff & Hahn, 1970)2, IBM (Allen & Segall, 1974)3, Bell (Goldstein and Speranza, 1982)4, Canadian Electrical Association (Hughes & Chan, 1995)5 , National Power Laboratory (Dorr, 1995)6 and other researchers, including Hassler & Lagadec (1979)7, Meissen (1983)8, Wernstrom et al. (1984)9, Goedbloed (1987)10, Standler (1989)11, and Forti & Millanta  (1990)12  have been limited to the measurement of transient voltages.

Interest in these measurements has been re-kindled by several investigations aimed at assessing power quality in end-user facilities.  These recordings, initially limited to measurement of peak voltages, were perfected with the help of increasingly sophisticated voltmeters.  Early surveys were conducted with conventional oscilloscopes; later on, portable digital instruments with on-board computing became available.  While these instruments made possible the recording of a voltage transient as a function of time and graphical presentation of data, the recording of such a surge voltage profile does not lend itself to a simple description by a single number.  To circumvent this difficulty, many researchers called upon the basic concept of energy to characterize the level of surge threat in terms of voltage.  Referring to classical electrical engineering, the instantaneous power dissipated in a resistor by a transient voltage is merely the square of the applied voltage, divided by the resistance.  Taking the integral over the duration of the transient yields the energy.  By analogy, the “energy” of a surge could then be computed from the voltage measured at some point of a power system.  According to this intuitive concept – but fallacious as we will show – the greater the measured voltage, the greater the “energy” and thus the greater the threat to potential victim equipment.

A review of the known failure or upset mechanisms of various types of devices and equipment identifies several surge parameters other than energy-related.  These include source impedance, peak amplitude, maximum rate of rise, tail duration, and repetition rate.  Thus, future surveys of surge events conducted with present or with even better monitoring instruments will need to include more comprehensive and hopefully standardized methods of presenting and interpreting the results.

Thesis

Our thesis is that neither the threat nor the “energy level” of a surge can be characterized by simply measuring the voltage change during a surge event.  Any reference to the concept of “energy of a surge” should definitely not be introduced.  Such avoidance is based on two facts:

1.	A voltage measurement of the surge event cannot alone predict the energy levels affecting the devices exposed to that surge.  This is particularly true for nonlinear surge-protective devices where energy deposited in the device is relevant, but has little to do with the misleading concept of “energy in the surge” derived from an open-circuit voltage measurement.

2.	There are other than energy-related upset or failure modes of equipment.  These effects require consideration of other parameters when describing a surge event to yield relevant and realistic assessment of surge stress threats.

This thesis will be supported by an analysis of the impact of surges on equipment, and illustrated by numerical examples of varistor applications showing how the description of a surge by its "energy" could then lead to vastly different conclusions.

Interactions Between Surges and Victim Equipment

At this point, we need to identify the devices and equipment that may become the victims of a surge, and their failure mechanisms.  After-the-fact investigations and experimental data show a wide range of surge-related upset and failure mechanisms.  These include insulation breakdown, flashover, fracture, thermal and instantaneous peak power overloads, dv/dt and di/dt limits being exceeded.  The following list gives some generic types of surge victims and the typical failure or upset mechanisms.  It is highly significant that in all this list, the term [v2 x dt] or its integral does not appear.  Table 1 provides a summary of this list of victims and relevant surge parameters associated with the failure modes.

1.  Electrical insulation, where the failure mechanism (breakdown or sparkover) is principally a function of the surge voltage, with the complication of a volt-time characteristic such that failure under impulse occurs at a level that increases when the rise time or duration of the impulse decreases.  “Insulation” is to be taken in the broadest sense of solid or liquid material separating energized conductors in equipment, clearances on a printed circuit board, edges of semiconductor layers, etc.  A distinction must be made between the initial breakdown of insulation, related to voltage only, and the final appearance of the damaged insulation, related to the total energy dissipated in the breakdown path.  In another situation, the insulation of the first turns of a winding may be subjected to higher stress than the others as the result of the uneven voltage distribution resulting from a steep front rather than only the peak value of the surge.

2.  Surge-protective devices, for which the voltage across the device is essentially constant, and the energy deposited is a function of the surge current level and duration.  One failure mode of such a device will occur when the energy deposited in the bulk material raises the temperature above some critical level.  Failure modes associated with the current level, such as flashover on the sides of a varistor disc, failure at the boundary layers of the varistor grains, or fracture of large discs, have also been identified and are not directly related to energy.

3.  Semiconductor devices, such as thyristors responding to the rate of voltage change can be turned on by a surge", resulting in failure of the device or hazardous energizing of the load they control.  In a similar way, a triac may be turned on by a voltage surge without damage, but still fail by exceeding the peak power limit during a surge-induced turn-on with slow transition time.

4.  Power conversion equipment, with a front-end de link where the filter-capacitor voltage can be boosted by a surge, resulting in premature or unnecessary tripping of the downstream inverter by its own on-board overvoltage or overcurrent protection schemes.

5.  Data-processing equipment, where malfunction (data errors) – not damage – may be caused by fast rate of voltage changes (capacitive coupling) or fast rate of current changes (inductive coupling) that reflect the initial characteristic of the surge event.  This response is insensitive to the "tail" of the surge, where all the "energy" would be contained according to the misleading energy-related concept.

6.  Light bulbs, which of course have a limited life associated with filament evaporation and embrittlement – a long-term process where the short burst of additional heating caused by a few microseconds of overcurrent is negligible – but also fail under surge conditions when a flashover occurs within the bulb, triggering a power-frequency arc that melts out the filament at its point of attachment – another failure mechanism originating with insulation breakdown.

Among these types of victims, only the clamping-type varistor is directly sensitive to an energy level associated with a surge event – and at that, the energy deposited in the device, not the "energy in the surge." Considering the explosive proliferation of varistors, however, one might find some extenuating circumstances in emphasizing the significance of energy in describing the effect of surges on its principal target – the ubiquitous metal-oxide varistor – but this is a pitfall, a mental trap.

Table 1

Significant parameters in equipment failure modes

Baiting The Trap

From the interactions described above, it is clear that using a single voltage measurement to determine surge threat is not sufficient.  The trap was baited by the simplicity and ease of using a single parameter obtained by analogy with the power dissipated in a fixed resistance,  by an instantaneous voltage, v. Clearly in that limited case, the total energy involved over the surge event would be the time integral of v2/R, expressed by a number having the same dimensions as watt-seconds, or joules in the SI system.  And thus some power quality monitors placed on the market in the early eighties were printing out surge event characterizations expressed in joules.  This "joule" number was obtained by computation of the v2/R.dt, where the voltage v was measured by the instrument, divided by a resistance (taken arbitrarily as 50 ), and integrated over the duration of the event.  Manufacturers of power quality monitors soon recognized the potentially misleading aspects of such reporting and discontinued the practice.

Nevertheless, some researchers continued the practice and are to this day attempting to characterize the surge environment by the single parameter of "energy in the surge." As a half-way measure, some are now proposing a new parameter "specific energy" to be understood as the integral of voltage-squared divided by a reference resistance of 50  (why that particular value ?) and they would report results in watt-seconds.  Figure 1 shows an example of this type of reporting 14.

Figure 1 – Example of report of survey results 10 with number of occurrences

as a function of “energy” in milliwatts-seconds

We completely agree that, indeed, the selection of an appropriate varistor should reflect the level of threat to which it will be exposed, so that there is a need to characterize the threat in terms of the energy that will be deposited in the varistor by a specific surge event.  However, there is no way that a voltmeter measurement only, even if it includes time, can provide that information.  This observation was presented at an earlier Power Quality Conference", and discussions in that forum, as well as in working groups developing standards on the surge environment, indicated the need to give a wider distribution to the message, hence this paper in this forum.

Thesis:  Demonstration by Varistor Applications

To demonstrate our thesis by the ad absurdum process, we will compute the "energy in the surge" as defined by the trap-baiting definition of "specific energy" for three surge events such that all have the same "specific energy" but different voltage levels, waveforms, and durations.  Then, making a further assumption for the unknown impedance of the surge source, we will compute the energy actually dissipated in the varistor for these different voltage levels, waveforms, and durations, and observe that the resulting deposited energy is not the same!

Elementary example: basic calculation with fixed impedance

As a first easy-to-follow step, we take three rectangular pulses, all selected to have the same "specific energy" but different voltage levels and corresponding durations, and compute the energy deposited in a nonlinear varistor having a given maximum limiting voltage, assuming that the source of the surge is a voltage source with some arbitrary, fixed impedance.  It is noteworthy that some source impedance has to be presumed, because the varistor clamping action rests on the voltage divider effect of the source impedance and the dynamic (variable) varistor impedance prevailing for the resulting current.

Start with an assumed surge measurement of 1000 V with duration of 50 s.  The "specific energy" of such a surge event, according to the proposed definition, is:

(1000 V)2 x 50 s / 50  = 1 joule.

Now consider a surge with a peak amplitude of 316 V (316 = 1000 x 10) and a duration of 500 s        (500 = 50 x 10).  Its "specific energy" is:

(316 V)2 x 500 s / 50  = 1 joule.

To complete the bracketing range, consider a surge of 3160 V (3160 = 1000 x 10), and a duration of 5 s (5 = 50/10).  Its "specific energy" is:

(3160 V)2 x 5 s / 50  = 1 joule.

We now apply each of the three voltage surges to a 130-V rated varistor (200 V at 1 mA dc), assuming an arbitrary source impedance of Zs = 1 .  One can compute the resulting current or, for this simple example, make a fast-converging manual iteration without the help of a computer, as follows:

(a)	assume a current I, and look up the resulting voltage Vv on the varistor I-V characteristic;

(b)	compute [Zs x I];

(c)	is [Zs x I] + Vv = 1000 V ?

(d)	If yes, I is correct, the energy deposited in the varistor is I x Vv x t

If no, go back to (a) with a converging assumption for I.

Table 2 shows the results from this manual iteration for the three surges defined above.  It is quite apparent that the constant "specific energy" for the three surges does not result in the same energy deposition.  The dynamic impedance (Vv /I) of the varistor is also shown, to illustrate the well-known theorem that the power dissipated in a resistive load reaches a maximum for matched source-load impedance.  This theorem is yet another reason why a surge to be applied to a varistor cannot be characterized in the abstract: one needs to know the source impedance (real and imaginary components) as well, to assess the energy sharing between source and load.

Table 2

Energy deposition in a varistor by a surge, as a function of surge parameters,

all surges having a 1-joule “specific energy” for a source impedance of 1 ohm

Computer calculation with multiple combinations

We now compute the energy deposited in three varistors of three different maximum limiting voltages, for two combinations of voltage levels and durations that produce the same "specific energy," each with classical waveform (Ring Wave or Combination Wave), sized to produce I joule of energy dissipation in a 50- resistor, according to the classical formula cited earlier, and for three values of source impedance.  We can anticipate that the peaks will be quite different, foreboding very different effects on equipment.  In fact, the peaks turned out to be 3 kV and 1.2 kV, respectively for the two waveforms.

Applying these two waveforms to a family of varistors typically used in 120-V or 240-V power systems, we computed the energy deposited in these varistors for three arbitrary source impedances (assumed to

be ohmic), using the EMTP program 16 to input closed-form equations for the open-circuit surge voltage.  The results are shown in Table 3. These simple illustrations show that even the concept of "specific energy” proposed as an improvement over the concept of “energy in the surge” cannot be used to select a candidate varistor energy-handling rating, and serves no useful purpose in characterizing the surge environment.

Table 3

Energy deposited in varistors by Ring Wave and Combination Wave ‘1-joule surges”

for different source amplitudes and varistor nominal voltages

Conducting Future Surveys: Make Recordings That Make Sense!

Recording Relevant Parameters

In an effort to acknowledge the legitimate quest for the single number characterization, we should offer alternatives, not just stay with a negative vote The solution might be to tailor the surge characterization to the intended application, that is, take into consideration the failure mode of the specific equipment, and present the data in a form most suited for that equipment.  Of course, this would mean not only avoiding a single number, but actually providing combinations of parameters, each combination best suited to a particular type of victim equipment, according to their failure modes.

The recently-approved IEEE Recommended Practice Std 1159 on Monitoring Power Quality 17  offers some guidance on conducting surveys, including not only surges, but other parameters.  The Working Group that developed this standard has now established task forces to develop further recommendations on processing and interpreting the recorded data, including more uniform formats.

Table 1, discussed earlier, presented a matrix of surge parameters and types of equipment, showing for each type of victim which surge parameter is significant or insignificant.  In compiling that table, the authors sought to identify all types of potential victims.  As it turned out, the term [v2 x dt] or its integral, alone, is not directly involved in the failure of any of the equipment listed in Table 1.  A more complete set of data, associated with specific equipment sensitivity, will be needed to characterize the surge environment and achieve compatibility between that environment and equipment to be installed.

##### The fallacy of present-day voltage measurements

Another consideration that must be observed in conducting and reporting the monitoring of surges is the proliferation of SPDs in end-user installations.  It is unlikely today to find an installation where some SPD is not present, either as a deliberate addition to the system, or as part of the connected equipment.  Aware of this situation, some researchers have attempted to disconnect all known SPDs from the system being monitored so that results would represent the "unprotected location" situation such as that initially described in IEEE 587-1980 18, the forerunner of ANSI/IEEE C62.41-1991 19.

However, even this precaution of disconnecting all known SPDs does not guarantee that some undetected SPD might not have been left connected somewhere and thus invalidate the record.  Thus, extreme caution must be applied to reporting and interpreting voltage monitoring campaigns conducted after 1980 20.

We now propose a change in the protocol for the monitoring of power quality in ac power systems.

This change has become necessary because end-user power systems are no longer what they were at the time the early surveys of transient overvoltages were conducted, a time at which measuring transient voltages did indeed make sense.  Varistor-based surge-protective devices (SPDs) have become so ubiquitous in low-voltage ac power systems that hardly any location can be found where there is not some form of transient voltage limitation in effect.  Attempting now to characterize the environment so that appropriate SPDs could then be prescribed for specific locations based on voltage measurements would be quite misleading.  What such a measurement would yield today is no longer the surge characteristics of the monitored system, as it was at the time of the early surveys, but the residual voltages of whatever SPDs are installed nearby.

Making meaningful measurements

The proposed change in monitoring practices is to insert a current transducer between the low-voltage power system being monitored and the existing monitoring instruments.  This transducer would consist of an SPD with the minimum tolerable voltage rating across the power line, to be connected at some point of an installation, and serve as a "magnet" for attracting the impinging surges.  To use a metaphor, this SPD in effect becomes the "winning bidder" by offering to the impinging surge the path with lowest clamping voltage among all the parallel-connected SPDs of the installation.

A current transformer with the "magnet SPD" in the primary and an appropriate burden on the secondary (Figure 2) would be used to feed the resulting voltage signal into the existing power quality monitoring instruments now used by many organizations and individual researchers.  Typically, the voltage channels have higher frequency response that current channels.  In this manner, the surge current attracted by the "magnet SPD" can be recorded to find the true character of surge events at that particular location, despite the presence in the local system of any and many unknown and uncontrolled SPDs.

Figure 2 – Schematic of the transducer

The current transducer would consist of a string of silicon avalanche diodes (SADs) in series with the primary of a current transformer with a burden connected across its secondary, an overcurrent protective fuse in series with the diodes, and an indicating light to signal a blown fuse.  Because the very principle requires that the SAD string have a clamping voltage lower than any other SPD in the installation, it would be the most vulnerable to a large swell.  To remove the transducer from the system in case of failure of the SAD string, the fuse is provided ahead of the transducer circuits.

In the final design that would be used to deploy a number of these transducers, all of these components would be included in a package derived from the so-called "plug-in SPD" which are offered by many manufacturers.  Using the external package of such a device will provide a low-cost envelope to build a few hundred transducers with no tooling costs and yet provide a package suitable for connection to wall receptacles in end-user systems.

It should be noted that only one channel of the monitor need to be allocated for recording the surge current.  While the determination of power and energy deposited in the SAD requires knowledge of three parameters: current, voltage, and time, for the calibrated SAD built in the transducer, the voltage can readily be computed from the device I-V characteristic when the current waveform is known.

Preliminary results on the feasibility of such a recording system have been obtained: a suitable silicon avalanche diode has been identified and proven to act as a "magnet," even in the presence of "competing" metal-oxide varistors, and yet able to withstand the temporary overvoltages that can occur in the system.  The current transformer can be any of readily available low-cost transformers; for the purposes of recording the surge events in the environment, the exacting accuracy of a laboratory-grade pulse current transformer would not be necessary.

The power system can include several branch circuits to supply the loads, some of which featuring SPDs incorporated into load equipment or installed by the end-user.  At some point of this system, selected for convenience by the instrument operator, the transducer will be installed.  A key point of the proposal is that pinning down the actual location of the monitor is no longer a concern because of the "  magnet" effect of the low-clamping SAD string.

By design, the string of diodes is intended to become the "magnet" that will attract the impinging surges.  We recognize that this winning bid can be ensured only within a certain radius from the transducer.  Increasing distances between the transducer and competing SPDs eventually produces a decoupling of the two devices and might allow a competing SPD connected upstream from the transducer to divert the surge first.  This situation is the reverse of that sought when making studies of the coordination of cascaded SPDs, where the concern is to ensure that a heavy-duty SPD located upstream of a lower-duty SPD is sufficiently decoupled so that an impinging surge will be diverted by the upstream SPD.  The parameters of cascade coordination have been addressed at length in the literature  21, 22, 23, 24 and will not be discussed here.  For typical circuit lengths in a low-voltage installation, our tests have demonstrated that the SAD string of Figure 2 offers a sufficiently low voltage path for impinging surges that it will indeed be the magnet.

More sophisticated analysis can be performed by applying the numerical modeling techniques developed in the referenced modeling studies 21-24,  extending the distances and combinations of competing SPDs to determine how extensive an installation can be and still have the transducer remain the winning bidder.  In this manner, the pitfall that threatens credibility of contemporary voltage recordings (uncertainty about other unknown SPDs connected in the system that can produce misleading results of low surge activity) will be eliminated.

##### Program Implementation

The next step in making the change from surge voltage recording to surge current recording would be to recruit enough participants willing to acquire the transducer and use their existing commercial monitor(s) to record the occurrences of surge currents attracted by the transducer.  The transducer could be produced in cooperation with a manufacturer of a plug-in SPD, so that a readily adaptable outside package could contain the transducer components and provide a simple and safe way of connecting it to a receptacle.

Within the IEEE, a new Task Force of the Standards Coordinating Committee on Power Quality SCC22 is developing protocols for reporting monitoring results; hopefully, the concepts presented in this paper will be taken into consideration by that Task Force and by other organizations interested in making surveys for characterizing the electromagnetic environment.  The IEC is also developing guidance documents on measurement methods in the area of power quality, where this shift of focus should be taken into consideration.

Conclusions

The attempt to characterize the surge environment by a single number – the "energy in the surge" or "   specific energy" – is a misleading approach that should most definitely not be used in Power Quality research.  There are at least four reasons for this prohibition:

1.	The concept that energy can be defined in the abstract from a single measurement of voltage across the lines of an undefined power system is a faulty oversimplification.

2.	The potential victims of a surge event have responses that reflect their design and for many, their failure modes can be totally independent of any energy consideration.

3.	The prime interest of energy consideration is related to the energy-handling capability of metaloxide varistors.  The energy deposited in such a device by a given surge event depends on amplitude, waveform, source impedance, and varistor characteristics, and not on the "effective energy."

4.	Last but not least, the proliferation of surge-protective devices (SPDs) in low-voltage, end-user facilities makes the recording of surge voltages a fallacy as the recorded voltages now represent the response of the installed (and generally unknown) SPDs in the installation, not the actual threat of impinging surges.  That threat can now only be assessed by installing an instrument that will attract impinging surges to itself and measure the current that can be delivered by the surge.

Future surveys should be conducted keeping in mind the relevant parameters for characterization such as peak amplitude, maximum rate of rise, tail duration –but not "energy." Relevant and realistic assessment of surge stress threats must consider not only all the characteristics of a surge event, but also the source of the surge and the failure mechanisms of potential victim equipment.  Standards-writing bodies concerned with characterizing the electromagnetic environment in low-voltage power systems could make an important contribution by giving recognition to the new situation and shifting focus from surge voltage measurements to surge current measurements.

Acknowledgments

Support for the development of this paper was provided by the authors' parent organizations and by the Power Quality research group of Pacific Gas & Electric.  Gerald FitzPatrick and Thomas Key provided comments on the initial two papers 15, 20  from which this new paper has been developed.

### References

1.	Bull and Nethercott "The Frequency of Occurrence and the Magnitude of Short Duration Transients in Low-Voltage Supply Mains," The Radio and Electronic Engineer, Sept 1964.

2.	Martzloff and Hahn, "Surge Voltages in Residential and Industrial Power Circuits, " IEEE Transactions PAS-89, No.6, July/Aug 1970.

3.	Allen and Segall, "Monitoring of Computer Installations for Line Disturbances," Paper C74199-6, IEEE PES Winter Meeting, 1974.

4.	Goldstein and Speranza, "The Quality of U.S. Commercial AC Power," Intelec Conference Proceedings, 1982.

5.	Hughes and Chan, "Canadian National Power Quality Survey Results," Proceedings, PQA'95 Conference, EPRI, 1995.

6.	Dorr, "Point of Utilization Power Quality Study Results," IEEE Transactions IA-3 1, No.4, July/August 1995.

7.	Hassler and Lagadec, "Digital Measurement of Fast Transients on Power Supply Lines." Proceedings, Third Symposium on EMC, Rotterdam May 1979.

8.	Meissen, "Oberspannungen in Niederspannungsnetzen," ("Overvoltages in Low-Voltage Networks"), Elektrotechnishe Zeitshrift, Vol 104, 1983.

9.	Wernstroem, Broms, and Boberg, "Transient Overvoltages on AC Power Supply Systems in Swedish Industry," Report FOA E 30002-E2, Sweden, 1984.

10.	Goedbloed, "Transients in Low-Voltage Supply Networks," IEEE Transactions EMC-29, No.2, May 1987.

11.	Standler, "Transients on the Mains in a Residential Environment," IEEE Transactions EMC-31, May 1989.

12.	Forti and Millanta, "Power-Line Impedance and the Origin of Low-Frequency Oscillatory Transients," IEEE Transactions EMC-32, No.2, May 1990.

13.	Goulet, "Susceptibility of Power Semiconductor-based Equipment to Power Line Disturbances," Conference Proceedings, Power Quality 1989.

14.	Scheuerer, "Research on the Isolation Properties qf Solid Insulation Upon Occurrence of HF Overvoltages, (In German) Doctoral Thesis, Darmstadt University, 1993.

15. 	Key, Mansoor, and Martzloff, "No Joules for Surges: Relevant and Realistic Assessment of Surge Stress Threats," Proceedings, IEEE International Con rence on Harmonics and Power Quality, Las Vegas, October 1996.

16.	EPRI Report EL-6421 -L, Electromagnetic Transient Program (EMTP), Version 2.0, Volumes I and 2, July 1989.

17.	 IEEE 1159-1995, IEEE Recommended Practice for Monitoring Electrical Power Quality.

18.	IEEE 587-1980, IEEE Guide on Surge Voltages in Low- Voltage AC Power Circuits.

19.	ANSI/IEEE C62.41-199 1, Recommended Practice on Surge Voltages in Low- Voltage A C Power Circuits.

20.	Martzloff, "Surge Recordings that Make Sense: Shifting Focus from Voltage to Current Measurements," Proceedings, EMC'96 ROMA Symposium, Rome, Italy, September 1996.

21.	Lai and Martzloff, "Coordinating Cascaded Surge Protection Devices: High-Low versus LowHigh," In Conference Record, IEEE-IAS 1991 Annual Meeting, pp 1812-1819.  Also in IEEE Transactions, IAS-29 No.4, July/August 1993, pp 680-687.

22.	Hostfet, Hervland, Nansen, and Huse, "Coordination of surge-protective devices 'in power supply systems: Needs for secondary protection," In Proceedings, 20th International Conference on Lightning Protection, 1992.

23.	Rousseau and Perche, "Coordination of Surge Arresters in the Low-Voltage Field," In Proceedings, 17th International Telecommunications Conference (INTELEC 95), 95CH35824.

24.	Martzloff, Mansoor, Phipps, and Grady, "Surging the Upside-Down House: Measurements and Modeling Results," In Proceedings, PQA'95 Conference, EPRI, 1995.

The Fallacy of Monitoring Surge Voltages:

SPDs and PCs Galore!

| ## Arshad Mansoor EPRI PEAC Corp Knoxville TN 37932 | ## François Martzloff National Institute of Standards and Technology Gaithersburg MD 20899 | ## Kermit Phipps EPRI PEAC Corp Knoxville TN 37932 |
| --- | --- | --- |

# Abstract

To support the recommendation of shifting transient monitoring from voltage surges to current surges, the paper presents experimental results as well as numerical modeling results demonstrating two mechanisms causing an apparent decrease of surge activity in low-voltage ac power circuits. The first mechanism is the proliferation of surge-protective devices, a situation which is by now well recognized. The second, which should also have been recognized, apparently escaped scrutiny so far: the proliferation of electronic appliances containing a switch-mode power supply that effectively places large surge-absorbing capacitors across the ac power systems.

1.  Introduction

This paper is unabashedly tutorial, and some of the themes presented here might be quite familiar to some of our readers. However, we have observed that these concepts, which could almost be characterized as obvious when given the benefit of hindsight, are still not widely recognized. Therefore, we will present them to this forum, and illustrate their validity by experimental measurements and numerical modeling.

The three major themes of this presentation are:

I.	There is a logical explanation for the apparent decrease in the level of voltage surges reported in recent power quality surveys: the proliferation of surge-mitigating devices.

2.	The present practice of recording voltage surges can lead to erroneous concepts on surge protection, which in turn can lead to equipment failures.

3.	There is an unfulfilled need to develop and deploy power quality monitors that can characterize the energy-delivery capability of a surge event.

The first theme will be introduced by a historical perspective showing how voltage surges became the focal point of monitoring surges, even before the term “power quality” was coined. Experimental measurements and numerical modeling will be described to illustrate the effect of the proliferation of surge-protective devices (SPDs) and of new electronic appliances that serve respectively as intended and unintended surge-mitigating devices. The next two themes will be only briefly discussed because, once the first is accepted, these two follow quite logically.

2.	Historical Perspective

The proliferation of SPDs in low-voltage ac power circuits has been recognized as one of the root causes of the apparent decrease of the surge levels recorded in recent power quality surveys. The change in the occurrence of surges began to be recognized [Dorr, 1995] and explanations were offered attributing the phenomenon to the emerging proliferation of SPDs in low-voltage ac power circuits [Martzloff, 1996]. It is noteworthy that for many people, the term “surge” is equivalent to “transient overvoltage” to the point that the phenomenon has generally been recorded by instruments acting as voltmeters, and the term was without much scrutiny accepted in general as meaning a voltage surge.

For instance, in the bi-lingual publications of the International Electrotechnical Commission (IEC), the French text which parallels the English text uses the term “surtension” (meaning overvoltage), because there is a mind set, reinforced by the lack of a neutral term in French that could be applied to either or both voltage surges and current surges. In the United States, the Underwriters Laboratories perpetuates this narrow perspective by calling SPDs “Transient Voltage Surge Suppressors” (italics ours) [UL Std 1449, 1996], although both recent IEC and IEEE definitions of SPDs introduce and emphasize the concept of current surges as well as voltage surges.

Now less recognized but significant, a similar cause for the apparent decrease of voltage surge levels is becoming important as more and more electronic appliances depend on a switch-mode power supply with a rectifier-capacitor DC link. Through the rectifier, the DC link capacitor, which is typically in the order of 200 pF to 500 pF, offers a low-impedance path to current surges impinging on the power port of these appliances. With many such appliances connected in an end-user installation, the effect is that of quite a large capacitor being connected across the ac mains. Small wonder then that even large surge currents (for instance, with the capability of delivering currents of 3 kA, 8/20 ms) [ANSI/IEEE C62.4l-1995] can no longer raise the voltage across the mains to the high values sometimes reported in earlier surveys of surge voltage occurrences.

Another historical mind-set has been to recognize the origin of surges only as a voltage event while in fact it can be either a true induced-voltage event, or the end-result of the injection of a surge current somewhere in the power system. Typical induced-voltage surges are associated with the electromagnetic coupling into the power circuits of the field created by a nearby (but not direct) lightning flash. Such voltage surges, which can develop substantial voltages in high-impedance circuit loops [Martzloff et al., 1995] can easily be mitigated with relatively small SPDs because their energy-delivery capability is relatively small [IEC document 64/1034/CD, 1998]. In contrast, current surges are produced either by the dispersion of the current associated with a lightning flash when a direct strike injects current at some point of the power system, in close vicinity or at a more remote point of the power distribution system [Mansoor et al., 1998]. Another source of current surges is switching surges involving the injection of residual energy into parts of the power system. The energy-delivery capability of these current surges can be substantial, and be a threat to the survival of improperly sized SPDs. Note in passing the use of the term “energy-delivery capability” and not “energy in the surge.” Some of our readers are by now familiar with that theme [Lindes et al., 1997] — perhaps even tired of seeing it repeated — but the sad truth is that usage of the term “surge energy” is still rampant.

The significance of making the distinction between recording current surges versus recording voltage surges is very important for equipment designers. A decision to provide only modest surge withstand capability for an SPD incorporated at the power port of the equipment might be made because the contemporary surveys reveal few and moderate (voltage) surges. When combined with the misconception that “the lower the clamping voltage, the better” [Martzloff et al., 1989], the result can be disastrous. We have in our laboratory ‘morgue’ two examples of such mass-produced devices incorporating an inappropriate SPD that led to early mortality of the product. Without identifying the culprit — perhaps a harsh word for a designer who was lulled into this position by referring to misleading reports on surge activity — but to illustrate the situation, we can name the two products: a compact fluorescent bulb, and a remotely-controlled ceiling fan. To recite a recurrent theme in our tutorial presentations (“Transients Are Here to Stay”), voltage surges might appear to have faded away, but current surges are still here, ready to destroy a small SPD incorporated in a design based on the misperception of fading voltage surges, fostered by recording only voltage surges.

3.	Experimental Measurements

To illustrate the effect of nonlinear SPDs as well as linear capacitors connected across the mains. the Power Electronics Applications Center (PEAC) “Upside-Down House” [Key et al., 1994] was used to inject surges into the service entrance of the Upside Down House with various combinations of SPDs and/or personal computer (PC) power supplies connected at the end of two branch circuits, one 9-rn long, the other 36-rn long. In Figure 1, currents in the branches and voltages at the nodes are identified respectively as Is, I9, I36, and V0, V9, V36 . The charging voltage setting of the Combination Wave surge generator was kept constant to provide a 2 kV, 1.2/50 ms open-circuit voltage (OCV). In a second series of experiments, the setting was increased to 4 kV. This second series, not reported here in detail because of limited space, confirmed the expected nonlinear response of varistors and the linear response for capacitors only.

Figure 1 - Upside-Down House branch circuits

3.1	Metal-oxide varistors only

Given the known and predictable behavior of multiple SPDs — often reported in the literature to the point that bibliographic citations would take several lines to list all of them — this part of the experiment was performed only to provide a baseline. Metal-oxide varistors (MOVs) rated 150 V, 20 mm diameter, were used for this experiment. To record all interesting currents and voltages, two shots are necessary when using the 4-channel digital signal analyzer; therefore each oscillogram in the figures contains the trace of V0 to serve as a common reference (Figure 2).

Figure 2-Typical recordings1 made during the first experiment— SPDs only.

In Figure 2, the current traces (left oscillogram) show the unequal sharing between the two MOVs, reflecting the difference in the inductance of the two branch circuits. Because the peaks of the two branch-circuit currents are not simultaneous (the current in the longer branch circuit takes longer to build up) their sum seems to exceed the peak of the injected current, IS.

The voltage traces (right oscillograrn) show how the voltage at the service entrance, V0, is mitigated from the 2 kV open-circuit voltage supplied by the generator that would propagate without attenuation in the absence of a surge-mitigating device [Martzloff et al., 1986]. This voltage V0 is the sum of the clamping performed by the varistor at the node V9, and the inductive voltage drop in the 9-rn long connection. Note that this inductive voltage is additive during the rise of the current I9, and subtractive during the fall, hence the apparent “overshoot” in the trace of V0, compared to the flat-top trace of the varistor at V9. The voltages at V9 and V36 are the typical clamping voltages of the MOVs corresponding to the current they carry.

In a subsequent experiment with a 4 kV open-circuit voltage setting of the generator (twice the value of Figure 2, but not reported here in detail because of limited space), the voltages across the varistors, predictably, were not substantially increased. However, the substantially increased current in the 9-rn long branch circuit (from 1000 A to 2800 A, resulting from the nonlinear response of the varistor) produced an increased inductive effect to the point that the voltage at the service entrance was raised to 1300 V from the 790 V recorded for the case of Figure 2. Table 1, at the end of this section, presents a summary of the peak values recorded in the various combinations of components, branch circuits, and amplitudes of the injected surge.

3.2	Capacitors only

In a second set of experiments, less easily predictable would be the behavior of the still all-linear circuit involving the capacitors of a PC power supply (440 mF each in this experiment) when receiving a surge originating from the complex RLC wave-shaping network of a Combination Wave surge generator (Figure 3).

Figure 3 - Typical recordings made during the second experiment — Capacitors only

In Figure 3, the voltage at the service entrance, V0, is mitigated from the 2 kV open-circuit voltage supplied by the generator. However, because of the interaction between the RLC components in the wave-shaping network of the Combination Wave generator on the one hand, and the capacitances of the PC power supplies and inductances of the branch circuits on the other hand, this voltage rings around an average voltage level of 1300 V, reaching a peak of 1700 V. To reflect this situation, the tabulation of the voltages in the figure shows two lines, peak and average. Thus, the mitigation effect is degraded by the ringing. Nevertheless, one can expect that as more PCs would be added, the ringing frequency would become lower and the voltage peaks lower.

  - Capacitor and MOV

In a third set of experiments, a capacitor was connected at the end of the 9-m branch circuit and an MOV was connected at the end of the 36-m branch circuit. Interest in this particular configuration was motivated by the desire to show how an MOV would mitigate the ringing that was observed in the preceding experiment at the end of the 36-m line (V36 in Figure 3).

Figure 4 - Typical recordings made during the third experiment — capacitor and MOV.

Experiments 2 and 3 (Figures 3 and 4) do show decreasing levels of voltage surges at various points of the Upside Down House, compared to the open-circuit conditions. However, the interactions between the capacitors of the generator RLC wave-shaping network on the one hand, and the PC capacitors on the other hand, make detailed interpretation of the waveforms tedious and beyond the scope of our illustrative examples. Numerical modeling with a current source, as reported in the following section, avoids this interaction and provides further evidence on the “PCs Galore” effect. For readers interested in the details, Table 1 documents the results concerning peak voltages noted from the oscillograms kept on file but not reproduced here. Readers interested primarily in the big picture may skip a close examination of this table.

Table 1 - Summary of node voltages for component combinations

4.  Numerical Modeling

Our previous experience with modeling cascaded SPDs [Lai et al., 1993] and the behavior of the Upside Down House with installed SPDs [Martzloff et al., 1995] can be readily applied to the prediction of the behavior of the three circuits subjected to the experimental measurements, with an imposed current source, free from the unavoidable interactions that occurred in the preceding experimental measurements. This approach yields the best of the two methods: a computation that has been well demonstrated as suitable for modeling nonlinear SPDs, and the freedom to impose any fixed waveform — what reality imposes on a residence is not the surge from an impedance-limited surge generator — combined with the possibility to model many branch circuits and many combinations of SPDs and/or capacitors.

4.1 Modeling combinations of loads and branch circuit lengths

In a series of modeling runs similar to the combinations of the experimental measurements, the model used the circuit of Figure 5. A current source feeds a fixed current surge via a common service drop to the panel bus of the service entrance, where three branch circuits made of 2-mm diameter conductors (#12 AWG) take off, with length of respectively 5 m, 10 m, and 20 m. The choice of these lengths was based on curiosity about the effect of the long distance connection (and thus an effect that might be delayed or degraded) to the immediate occurrence of an overvoltage at the end of shorter branch circuits. The currents in the circuit are identified in Figure 5 respectively as IS, I0, I5, I10, and I20 , with the node voltages at the service bus and branch circuit ends respectively as V0, V5, V10, and V20.

Figure 5 - Service drop and branch circuits for modeling combinations

As in our previous modeling applications, the EMTP program [EPRJ, 1989] was used. To avoid computational artifacts, a finite 10 kW resistance was always postulated at the ends of all branch circuits, whether these were left in “open” or “loaded” condition. The loads that were modeled included combinations of SPDs, capacitors, and 100 W resistors. The SPDs were all 20-mm diameter, 130-V rated MOVs. The capacitors included a capacitance of 440 mF and a series resistance (“ESR”) of 0.25 W to represent an electrolytic capacitor. Initial conditions for the models stipulated an initial charge on the capacitor to represent the normal condition of the DC link. The 100 W  resistor was selected as a typical value for a 150-W power-consuming appliance connected at the end of the branch circuit.

Just to illustrate the point of a readily predictable behavior of a purely linear circuit, Figure 6 shows the voltages and currents for the case of 100 W) loads confronted with a current source. Compared with the 100 W) load at the end of the branch circuits, the series impedance has a very small effect and the impinging surge current IS divides almost equally (3000 A /4  = 750 A) in the nearly identical four branches I0, I5, I10, and I20 (I0 being the current in the service entrance ‘branch’, with a length of 0). Thus, the voltage developed by this 750 A current across 100 W would simply be expected to be 75 000 V (seventy five thousand volts). We say “would be expected” because, of course, the insulation level of a real-world low-voltage insulation cannot withstand such a voltage. The result of this theoretical case is another illustration of the theme “More Begets Less,” according to which a high-amplitude, steep-front surge cannot propagate in branch circuits because a flashover will occur at the origin [Mansoor et al., 1998].

Figure 6 - Currents and voltages for the baseline case of 100 C) loads without SPDs

Figure 7 shows the example of two PCs, one at the end of the 5-m branch circuit, the other at the end of the 10-m branch circuit: the surge current is shared (unequally) between the two capacitors, with a corresponding decrease of the voltage level at each DC link, and also a reduction of the voltage at the open end (unprotected) of the 20-m branch circuit. This example shows the beginning of the “PCs Galore !“ effect. Several intermediate and further steps were modeled by adding combinations of surge-mitigating devices to build our case file and confirm the expected effects, but we will spare the reader from a tedious recitation.

The results shown in Figure 6 call for several comments:

•	The unequal division of the currents I5 and I10 reflects the effect of the larger impedance of the 10-m branch circuit, compared to the 5-m branch circuit.

•	Substantial mitigation is obtained at the nodes V5 and V10, as a result of the filter-like action of the line inductance and the capacitance of the PC power supply.

•	The voltage surge developed at the node V0 propagates, unabated, to the end of the open-circuited 20-m branch circuit, a reminder that the notion of voltage surges being attenuated as they propagate in building wiring [IEC Report 664, 1980] was incorrect.

Figure 7 - Currents and voltages for the case of two PCs without SPDs

The voltage results are especially worth noting, in the context of what a power quality monitor would report in such an installation, depending upon its point of connection.

•	From the (impossible) high voltages of the 100 W baseline (no SPDs), the voltage that would be recorded by a monitor installed at the service entrance is now reduced to “only” 1960 V.

•	A voltage-only monitor installed at the point of use of the power (typical selection of point of installation in many surveys), namely the two receptacles at 5 m and 10 m feeding the PCs, would report respectively 510 V and 290 V, creating the illusion (fallacy) that there is no significant surge activity at these points.

•	In reality a current surge I5 of nearly 2000 A is carried by the PC rectifier into the capacitor, via a line fuse. Such a high current — undetected by a voltage-only monitor — could very well be fatal for the rectifier or the input fuse, or for the capacitor of the PC power port. Such failures were found in post-mortems of equipment recently performed at PEAC. That scenario is also what occurred in the experimental test of Section 3 for a 4 kV open-circuit voltage and capacitor-MOV combination (shown in next-to-last row of Table I).

4.2  Modeling PCs Galore

As a grand finale for illustrating our major theme, the case of an increasing number of PCs was modeled, with each of the PCs connected at the end of a dedicated branch circuit, with all branch circuits having the same length of 20 m, still with the 10-m long service drop driving a 3 kA current surge into the installation.

Table 2 shows the resulting voltages at the service entrance and at the point of connection of the PCs, as well as the imposed impinging current and the resulting currents in the individual power ports of the PCs. Indeed, the effect is linear with increasing numbers of PCs, and the resulting decrease in the voltages expected to be reported by a power quality monitor installed at the point of use is quite apparent.

Table 2 - Effect of an increasing number of connected PCs

Inspection of the table shows that the effect is practically proportional to the number of PCs in use in the installation. While we have used the short acronym of PC in the title and preceding discussions, the proliferation that we observe is not limited to PCs, but includes many electronic appliances, such as home entertainment, heating and air conditioning with adjustable speed drive, that use a DC link with large energy-storage capacitor.

5.  Action Items

The customary closure of a paper is to list conclusions. However, in this case we suggest action items for industry, rather than academic conclusions:

•	The examples given here clearly show that the fallacy of little surge activity can be created by limiting power quality measurements to voltage surges. With undetected current surge activity, users of electronic appliances will be puzzled by unexplained failures in the face of reports of little voltage surge activity.

•	We offer the explanation that these unexplained failures are likely to be associated with the (heretofore not characterized) surge current delivery capability of the environment. Such failures could have been avoided, had designers been better informed.

•	With our leading theme now solidly established, questions arise about what to do about it. This matter requires the dedicated attention of both manufacturers and users of power quality monitoring instruments.

•	Unfortunately, more than three years after beginning the crusade to overcome the fallacy of limiting surge measurements to voltage surges [Martzloff, 1995], there is no commercially available power quality monitor capable of characterizing the energy-delivery capability of a surge event.

•	Worse yet, among the international delegates to an IEC working group chartered to develop a standard on measurement of power quality parameters (which is likely to dominate the design of future monitoring instruments), there are some claims being made that “a current surge is not a power quality parameter” and therefore it should not be included in the emerging standard prescribing measurements methods. This misconception needs to be corrected.

•	Therefore, the crusade must be pursued with perseverance, and it is the goal and hope of the authors that sufficient recognition of the fallacy will eventually create a market demand for appropriate instruments, which forward-looking manufacturers may have developed or may be in the process of developing in anticipation of such recognition.

7.	 Bibliography

ANSI/IEEE C62.41-1995, IEEE Recommended Practice on Surge Voltages in Low-Voltage AC Power Circuits.

Dorr, D., “Point of Utilization Power Quality Results,” IEEE Transactions IA-31, No.4, July/August 1995.

EPRI, “Electromagnetic Transient Program (EMTP),” Version 2.0; Volume 1: Main Program: Volume 2: Auxiliary Routines, EPRJ Report EL-6421-L, July 1989.

IEC Report 664-1980 (sic) Insulation coordination within low-voltage systems including clearances and creepage distances for equipment, 1980.

IEC 64/1034/CD, General basic information regarding surge overvoltages and surge protection in low-voltage a.c. power circuits, Committee Draft, 1998.

Key, T.S. and Martzloff, F.D., “Surging the Upside-Down House: Looking into Upsetting Reference Voltages,” Proceedings, PQA ‘94 Conference, 1994.

Lai, J.S. and Martzloff, F.D., “Coordinating Cascaded Surge Protection Devices: High-Low versus LowHigh,”IEEE Transactions, IAS-29 No.4, July/August 1993.

Lindes, G., Mansoor, A., Martzloff, F.D., and Vannoy, D., “Surge Recordings that Make Sense — Joule Deposition: Yes ! - ‘Joule Content’: Never !“ Proceedings, PQA ‘97 Conference, 1997.

Mansoor, A., Martzloff, F.D., and Nastasi, D, “Applying Reality Checks to Standards on the Surge Environment,” Proceedings, 23rd International Conference on Liglitning Protection, Florence, 1996.

Mansoor, A. and Martzloff, F.D., “Driving High Surge Currents into Long Cables: More Begets Less,” IEEE Transactions PWRD-12, July 1997.

Mansoor, A. and Martzloff, F.D., “The Effect of Neutral Earthing Practices on Lightning Current Dispersion,” IEEE Transactions PWRD-13, July 1998.

Martzloff, F.D. and Gauper, H.A., “Surge and High-Frequency Propagation in Industrial Power Lines,” IEEE Transactions IA-22, July/August 1986.

Martzloff, F.D. and Leedy. T.F., “Selecting Varistor Clamping Voltage: Lower Is Not Better!” Proceedings, 1989 Zurich International EMC Symposium, 1989.

Martzloff, F.D. and Lai, J.S., “Cascading Surge-Protective Devices: Coordination versus the IEC 664 Staircase,” Proceedings, PQA 91 Conference, 1991.

Martzloff, F.D., “Keeping up with the Reality of Today’s Surge Environment,” Conference Proceedings, Power Quality Solutions, Intertech Pub., Ventura CA, USA, September 1995.

Martzloff, F.D., Mansoor, A., Phipps, K., and Grady, W.M., “Surging the Upside-Down House:

Measurements and Modeling Results,” Proceedings, PQA ‘95 Conference, EPRI, 1995.

Martzloff, F.D., “Surge Recordings that Make Sense: Shifting Focus from Voltage to Current

Measurements,” Proceedings EMC’96 ROMA Symposium, Rome, September 1996.

UL Std. 1449, Transient Voltage Surge Suppressors, Second Edition, 1996.

SOME ENLIGHTENING CASE HISTORIES ON LIGHTNING DAMAGE

Thomas Key	Doni Nastasi	Kermit Phipps			     François Martzloff

EPRI PEAC, Inc.			National Institute of Standards and Technology

Abstract: Lightning-related damage stories abound, but it is not always possible to document precisely the mechanisms and scenarios involved when timely, first-hand knowledge is not obtainable.  From a collection of case histories accumulated by the authors, three cases are described.  Each of the three illustrates a different mechanism leading to structural damage or equipment failure, in ways that might not have been obvious from a casual investigation of the damage or sites, or from second-hand reports.

Keywords:    Lightning damage;  system interactions; equipment immunity.

1.  INTRODUCTION

In an area of Eastern Tennessee, U.S.A., where the three lightning incidents reported here occurred in 1998, the ground flashes over an area of 40 km radius average 22 000 per year.  The year 1998 was particularly active , a total of 27 993 ground flashes, or 5,5 flashes/km2 [1].  These incidents of damage came to the attention of the authors, providing a unique opportunity to document the mechanisms and failure modes of residential electronics.

The first incident involved a small house made primarily of wood where the power service entrance and the cable TV entrance were at opposite ends of the house - the classic error in installation practice - compounded with a violation of ground bonding rules.  The second incident involved a residence with an elaborate audio-video system with a central equipment rack distributing signals to speakers and monitors.  A third incident was the case of a direct lightning flash to the overhead service of a house, resulting in severe fire damage to the structure.

2.  THE CASE OF THE COZY CABIN

At this rural site, a wood-structure residence suffered two failures of video equipment during lightning storms, a few months apart.  The owners allowed the authors to visit the site and acquire the second failed TV receiver for a postmortem examination and tests.

The visit revealed a case of the incorrect but frequent practice of two uncoordinated providers -- the cable TV company and the power company -- installing their service entrance at opposite ends of the house (Figure 1).  The consequences of such practice are briefly described in the following.

2.1  The problem of shifting reference potentials

The general problem of shifting reference potentials during surge events has been described in previous work [2]; [3].  A brief description of this problem is given here to place the "Case of the Cozy Cabin" in perspective. In the scenario of Figure 1, a personal computer (PC) is connected to both the power system and the telephone system.  The surge current "Surge I" flows from the telephone system toward the common grounding point via the protective device "NID" at the point of entry, and the equipotential conductor.  This current produces a magnetic field which couples into the loop formed by the power branch circuit, the telephone premises wiring lines to the PC, and the equipotential conductors.  The voltage thus induced in the loop appears across the telephone and power ports, with upsetting or damaging consequences.

In a laboratory replica of this configuration [2], a peak voltage of 4,3 kV was recorded across the two ports for a typical surge injected at the telephone entrance.  A similar situation exists for a surge impinging on the video port of a TV receiver.  The tests reported in 2.3 below show that this level can cause damage.

2.2  Cozy cabin site configuration

I	n the Cozy Cabin installation, the power service entrance was located at one end of the house, while the cable TV service entrance was located at the opposite end.  Furthermore, a visit to the site revealed that the cable TV shield was grounded only by a questionable ground rod next to the house foundation (within the drip line, and thus in dry soil, see Figure 2).  This cable TV grounding electrode was not bonded to the grounding electrode of the power service entrance, a clear violation of the U.S National Electrical Code ('NEC", NFPA 70, 1999) [4].

Following the visit to the site by the authors, the local cable TV company was informed of this situation and took what they believed an appropriate action: the incoming cable was first routed under the house, in the crawl space, to allow bonding the shield to the power service grounding connection.  From there, the cable was returned to its original point of entry into the house, at the opposite end.  This modification did correct the NEC violation but left the arrangement in the topology shown in Figure 1.

However, the interaction was not pursued further with the cable company.  A recommendation was made to the owner, to install a surge reference equalizer [5] for each piece of video equipment.  After that was done, no damage occurred during the next lightning season.  Of course, it is still too early to declare victory over Zeus and Murphy, but encouraging when compared to a previous history of two incidents within a few months.

2.3  Post mortem and surge tests

One of the failed TV receivers from the Cozy Cabin was made available to the authors for examination.  No evidence of damage was found on the power side of the chassis and the related components, but a clear indication of surface flashover was observed along the insulation of the gap intended to isolate the cable input 'ground' termination (connected to the incoming cable shield) from the shielding can of the tuner (connected to one of the power cord conductors, see Figure 3).

After cleaning the carbonized path of the flashover, a 0,5 s - 100 kHz Ring Wave was applied in incremental steps between the two conductors of the power cord, bonded together, and the shield connector of the cable input: flashover occurred at 2 kV.  By removing the material to a greater depth and covering it with epoxy, the gap did withstand a greater level, and failed at 2,5 kV.  That flashover occurred at another part of the original insulation, thus providing valid information on the original withstand capability.

2.4  Conclusions from the Cozy Cabin

This case study illustrates the classic situation of separate service entrances, compounded with incorrect bonding.  The examination and test demonstrate that at least 2,5 kV were developed across the power port and the cable TV port of the receiver under a condition of distant or nearby lightning strike.

Another significant finding from this case history is the anecdotal confirmation of allegations that cable TV installation practices prevailing in many residential situations might be in violation of the U.S. National Electrical Code. This violation made even more hazardous the now well-recognized occurrence of undesirable separation of the service entrances.

3.  INPUT ISOLATION PRACTICES

Interest aroused by the Case of the Cozy Cabin led to a brief survey of what isolation schemes are applied by the manufacturers of video equipment.

Televisions and VCRs are of a similar category of equipment in that they both have the same input ports: ac power, and video (antenna or cable), for which the 'ground' reference can be raised to different potentials during a surge event.  The power port has no direct connection to the equipment grounding conductor because a two-prong ac plug is used.  However, at the service entrance, the neutral - one of the two conductors of the cord - is bonded to the ground bus of the service panel.  The video input is referenced to ground via a connection to a grounding rod outside the residence and (per the NEC [4]), a bonding conductor.

Manufacturers use various techniques to isolate these two ports from each other inside the equipment.  Surge tests were conducted on five televisions and three VCRs to determine the voltage level at which spark-over would occur between the power port and the video port.  Using a 0.5 s - 100 kHz Ring Wave, incremental steps of 500 V were applied between the power port and the shield of the video input port.

The units that had isolation built into the video port sparked-over at the series capacitor of the video port.  The breakdown voltage level was approximately 2,5 kV in these units.  Units in which the power supply outputs were electrically isolated from the inputs via transformers fared better.  One sample survived and performed normally after all surge tests.  Physical size of the transformer seemed to have some impact on the results.  Larger transformers seemed to tolerate surges better than smaller ones.

Based on this small number of VCR samples, a general observation is that VCRs use power supply transformers as isolation, similar to the newer TV sets, and do not have isolation between the cable or antenna input and the tuner chassis.  This type of isolation scheme withstood higher surge voltages than the isolating ring that can be found in older television sets and serving to isolate the chassis of the set from the ('grounded') shield of the signal cable.

4.  THE CASE OF THE RAMBLING RESIDENCE

An expansive residential estate, located in the same general area as the Cozy Cabin, was the scene of a lightning incident where a tree adjacent to the house was struck (and subsequently died).  Extensive damage was inflicted to the audio-video components that are connected to a central rack, and are located throughout the residence and its surroundings (large patio and swimming pool, with outdoor lighting and audio speakers).

The home owners graciously allowed the authors to visit the residence and observe the configuration of the system in an attempt to better understand the mechanisms leading to the damage.  They also made available to the authors the complement of damaged or presumed damaged equipment that had been replaced thanks to their insurance.  Thus, this case history, unlike most lightning incidents, offered an unusual

Three activities were undertaken to better understand the mechanism and verify some hypotheses:

1.	Bench examination of returned equipment and surge testing of undamaged equipment;

2.	Site visit of the residence;

3.	Laboratory coupling of electric field stress into a remote speaker-to-amplifier connection.

4.1  Bench Examination

Bench tests for each electrical appliance began by plugging it into a 120-V a.c. outlet.  Physical signs of normal operation were noted such as illuminated displays, response of controls, audio/video output.  The equipment cover was removed for an internal inspection.  In most of the equipment, physical damage such as a burned-out transistor was very apparent.  Table 1 lists the home entertainment equipment that were submitted, and their condition.

A significant finding was that all of the power supplies in the equipment were functional, indicating that the lightning surge either did not enter through the ac power port, or was not severe enough to cause damage to the power supplies.

Table 1 Equipment submitted for bench tests

The examination and, as appropriate, tests revealed the following conditions:

·	Except for its non-operational display, the stereo tuner/amplifier appeared undamaged.

·		The visible damage to the digital satellite receivers was nearly identical in all three units.  Apparently, the surge had entered through the telephone port and had damaged the small surface-mount electronics that make up the modem circuit.  However, because the satellite receivers could not be operated without their antenna and code-reading cards, the extent of the functional damage could not be determined

The two 12-channel amplifiers had sustained damage to their output transistors that drive the speakers.  The power supplies and fuses were not damaged.  Furthermore, it was found that some speaker outputs were still operational.  This situation suggested a possible mechanism that damaged only some of the output transistors, and therefore not attributable to a "power-line surge." In turn, that hypothesis was later verified by a laboratory test, as described in 4.3 below.

·	Speakers, tested by connecting them to an amplifier that was known to be functioning properly, were found to have their woofers damaged, but the tweeters still operational.

Other electrical appliances in the house including television- sets and VCRs not connected- to the centralized system were not included in the returned package and therefore presumed as not damaged.              This finding confirms the conclusion that the long leads  interconnecting the distributed- system components acted as energy collector&, feeding the induced voltages or currents into the communications ports of the equipment.

4.2  Site Visit

The purpose of the visit was to look for clues to explain the specific damage that was observed in some of the equipment.  The following observations were made:

·	Approximate distances between the lightning strike and affected equipment

·	Location and grounding at the service entrances of cable TV, power, and telephone

·	Other wiring and general installation practices

The overall physical layout of the house, damaged tree, and electronic equipment are shown in Figure 4. The tree that was struck is much taller than the house and is the tallest of the trees in the immediate area.  The bark was stripped from the tree trunk for most of its height.  The tree trunk is only approximately 15 m from the house and even closer to the patio, where some of the audio speakers were installed.  Outdoor speakers are also located in the pool area and connecting walkways.

In the audio amplifiers, as noted above, the power supplies of the units were not damaged, but their output transistors that drive the speakers and the speakers themselves were damaged.  Thus, it was speculated that the surge energy had been coupled into the speaker wires, which are probably very long and very near to the lightning strike, rather than as a 'power-line surge."

The visit to the installation verified this theory.  The home entertainment equipment, including amplifiers, is centrally installed in the basement of the house.  Speakers are located- throughout the house, the patio, and- the swimming pool area.  The wire length between the outdoor speakers and the central amplifier is about 30 m, and some of the wires run within 10 m of the tree trunk.

4.3  Laboratory Coupling of Electric Field

To validate the hypothesis of a failure mechanism involving the coupling of electric field energy into the speaker wire ran, a qualitative laboratory test war. staged, using the surviving channel of the amplifier to drive a speaker.  An audio signal from a tape deck was fed into the amplifier input to monitor its operation during the test.  A conventional Marx impulse generator at the NIST High-Voltage Laboratory was used to apply a 1,2/50 s high-voltage field between two parallel plates, each 2 m x 1 m.

A length of 5 m of speaker wire feeding the audio output from the system audio amplifier was sandwiched between the two plastic foam sheets separating the lower (grounded) plate, to which the amplifier chassis was bonded, from the upper (impulsed) plate.  The effective length of the wire was increased by connecting to each wire a- piece of foil of about 0.02 m, simulating the increased capacitance effect of about 50 m of wire.  Both the amplifier and tape deck were isolated from the power supply ground by an uninterruptible power supply.

The impulse was applied in increments.  At 70 kV, a flashover occurred between the two plate edges, but not involving the speaker wire. Immediate failure of the amplifier output circuit was noted, From this anecdote, we conclude that the rapid field change associated with the flashover did have the capability to couple enough surge energy into the capacitance divider of wire/ground plane and cause destructive failure of the output transistor effectively connected across that capacitance.  Such a scenario can be considered a reasonable emulation of the circumstances surrounding the "Lightning Incident at the Rambling Residence."

4.4  Conclusions from the Rambling Residence

The qualitative laboratory demonstration of coupling energy into the speaker wires provides one more piece of evidence that electronic appliances can   be   damaged-   by surges impacting their communications port, to the point that expecting protection by simple application of SPDs on the power port is not enough, and comprehensive protection is a necessity.  In this case, there was no evidence of any damaging surge introduced by the power supply connection of the residence.

5.  THE CASE OF THE STANDARD SUBURBAN

5.1  The aftermath

In this case, which occurred in a suburban, semi-rural hilly area, the post-strike investigation revealed that the overhead service drop to the house (involving a span of about 20 m across the street) had been severed by melting at the point of strike.  From there, the current traveled to the revenue meter (typically on the outside wall in U.S. practice), where a ground conductor is normally installed with a short run to the earthing electrode of the house.  Instead, according, to the practice when- constructed in the 1970s, a cold water pipe was allowed to be the main earthing electrode.  In this case, the conductor for the earthing electrode entered the garage and was routed upward near the ceiling with several bends before it was bonded to a copper water pipe.  Without any better path to earth, the lightning current had apparently followed the same route, severing the bare conductor while seeking the well-grounded water pipe (see Figure 5).

As shown in the photographs of Figure 5, the service entrances were overhead and without any direct path to earth.  This type of installation would not be approved by current US practice, which requires a direct connection to a driven ground rod in addition to any other supplemental electrodes such as the cold water pipe.  One of the main reasons that the practice was modified is the growing use of PVC or plastic water pipe.

On a later visit, the engineers who made the first visit were allowed to visit the repaired house.  Indeed, the new service grounding point includes not only the electric power but also the telephone and cable company.  The new water piping is PVC, and a driven ground rod has been installed as the primary grounding electrode.

This new arrangement (Figure 6) reflects a recently issued recommended practice [6] which, in addition to the NEC minimum requirements for safety, calls for intersystem bonding of all utilities serving a residence, and this by having all the utility connections next to each other.

5.2  Conclusion from the Standard Suburban

Architects and builders, guided by up-to-date codes, can provide appropriate grounding practices in new construction.    Surge-protective devices at the service entrance can provide a path from ungrounded conductors and equalize voltages between these conductors.  The practice is recommended as the first level of protection from surges in the exterior electrical environment.

6.  GENERAL CONCLUSIONS

·	The Case of the Cozy Cabin and related tests confirm the need to pay attention to the problems associated with the surge protection of multi-port equipment.  The solution of non-metallic communications media is not yet ready for the consumer market, but an effective mitigation approach is the surge reference

·	The Case of the Rambling Residence and related tests illustrates that the often-cited "power line surge" cause is not the only scenario responsible for appliance failures.  Other ports of equipment, communication ports in particular, can be damaged by surges induced into the cables used for incoming or outgoing signals, and therefore need appropriate protection.

·	The Case of the Standard Suburban shows that architects and builders have not fully understood the necessity of appropriate wiring and earthing practices.  The same lack of understanding by some utility providers was also evident in the Case of the Cozy Cabin.

·	The recommended practice of intersystem bonding at the service entrance described in this paper is compatible with the requirements of the U.S. National Electrical Code.  Codes applicable in other countries might require a different arrangement, but the principles are the same.

7.  ACKNOWLEDGMENTS

Resources for conducting these investigations were provided by the members of the Electric Power Research Institute.

Lightning flash density data and comments on the manuscript were contributed by Kenneth Cummins of Global Atmospherics, Inc.

The experiment on coupling energy into speaker wires, and a review of the manuscript were contributed by Gerald Fitzpatrick.

8.  REFERENCES

[1]	Personal communication, Global Atmospherics, Inc.

[21	Key, T. S., and Martzloff, F.D., “Surging the Upside-Down House: Looking into Upsetting Reference Voltages,” Proceedings, PQA94 Conference, Amsterdam, October 1995.

[3]	Martzloff, F.D., Mansoor, A., Phipps, K.O., and Grady, W.M., “Surging the Upside-Down House: Measurements and Modeling Results," Proceedings, PQA95 Conference, May 1995.

[4]	NFPA 70 - 1999, National Electrical Code, National Fire Protection Association, 1999.

[5]	IEEE Std 1100-1999 (Emerald Book) IEEE Recommended Practice for Powering and Grounding Electronic Equipment, IEEE, 1999.

[6]	EPRI PEAC, “Recommended Practice for Protecting Residential Structures and Appliances Against Surges,”  Report PEAC.0545.R, EPRI PEAC Corporation, Knoxville, TN, 1999.

## François Martzloff

END OF FILE “Text Site Surveys”

## April 2004