| # Last updated April 2004 | # Surge Protection Anthology Part 6 – Tutorials, Textbooks, and Reviews Text of “Standards Reviews” | # Surges Happen! |
| --- | --- | --- |

FOREWORD

This file contains the text part from eight papers on the subject of standards development:

- A guideline on surge voltages in AC power circuits rated up to 1000 V (1979)

- The development of a guideline on surge voltages in LV AC power circuits (1979)

- A consensus on powering and grounding sensitive electronic equipment (1986)

- A standard for the 90s: IEEE C62.41 surges ahead (1991)

- Standards: Transnational aspects (1991)

- Power Quality work at the International Electrotechnical Commission (1997)

- The Trilogy update of C62.41 (2000)

- New IEEE standards foster next-generation system compatibility (2002)

This file is formatted as MS Word, allowing you to do a search for keywords, but it does not support graphics as it was derived from an OCR scan of hard-copy archives.  However, should you wish to examine the complete original format, each page in this file has an identifying header and footer that contain a hyperlink to the pdf file for the document being displayed on that page, regardless of the font size that you select for optimum viewing.  These headers and footers and hyperlinks become accessible when you select the “Print Layout” in the “View” mode.

Best wishes and good browsing !

A GUIDELINE ON SURGE VOLTAGES

IN AC POWER CIRCUITS RATED UP TO 600 V

F.D. Martzloff

General Electric Company

Schenectady, New York 12345, U.S.A.

# Summary

Surge voltages occurring in ac power circuits can be the cause of misoperation or product failure for residential as well as industrial systems.  The problem has received increased attention in recent years because miniaturized solid state devices are more sensitive to voltage surges (spikes and transients) than were their predecessors.

Although surge voltage amplitudes and their frequency of occurrence on unprotected circuits are well known, their waveshapes and energy content are less well known.  On the basis of measurements, statistics, and theoretical considerations, a practical guideline for outlining the environment for use in predicting extreme waveshapes and energy content can nevertheless be established.  The Surge Protective Device Committee of the Institute of Electrical and Electronics Engineers has been developing such a guideline, the essential elements of which are presented in this paper.

Surge voltages [1] occurring in ac power circuits rated up to 600 V can be represented by various waveshapes in an attempt to duplicate actual surge voltages.  Two major types of surges reflecting differences in the environment are described to represent the situation realistically.

Systems located inside a building and separated from the overhead lines by some line impedance experience surge voltages of waveshapes and energy levels that differ from those of the outdoor environment.  Outside systems exposed to direct lightning strikes or lightning-induced surges--typically overhead lines--experience levels implied by IEEE standards for secondary arresters.  This guideline addresses particularly the hazards to these two types of systems [2].

Scope

The guideline presented here primarily addresses ac power circuits with rated voltages up to 600 V, although some of the conclusions offered could apply to higher voltages and also to some dc power systems.  Other standards have been established, such as IEEE 472, Guide for Surge Withstand Capability (SWC) Tests, intended for the special case of high-voltage substation environments, and IEEE 28, Standard for Surge Arresters far ac Power Circuits, covering primarily the utilities environment.  The guideline presented here intends to complement, not conflict with, existing standards, and to present a practical proposal for the selection of voltage and current tests to be applied in evaluating the surge withstand capability of equipment connected to these power circuits, primarily in residential and light industrial applications.

Some guidance is also presented on how to proceed from the environment description to the selection of “standard” test waves.

The surge voltages [1] considered in this guideline are those exceeding two per unit (or twice the peak operating voltage) and having durations ranging from a fraction of a microsecond to a millisecond. Overvoltages of less than two per unit are not covered here, nor are transients of longer duration resulting from power equipment operation and failure modes. Because these low-amplitude and long-duration surges are generally not amenable to suppression by conventional surge protective devices, they require different protection techniques.

1. The Origin of Surge Voltages

Surge voltages occurring in low-voltage ac power circuits originate from two major sources: load switching transients and direct or indirect lightning effects on the power system.  Load switching transients can be further divided into transients associated with (1) major power system switching disturbances, such as capacitor bank switching; (2) minor switching near the point of interest, such as an appliance turnoff in a household or the turnoff of other loads in an individual system; (3) resonating circuits associated with switching devices, such as thrusters; and (4) various system faults, such as short circuits and arcing faults.  Measurements and calculations of lightning effects have been made to yield data on what levels can be produced, even if the exact mechanism of any particular surge is unknown. The major mechanisms by which lightning produces surge voltages are the following:

(a)	A direct lightning strike to a primary circuit injects high currents into the primary circuit, producing voltages by either flowing through ground resistance or flowing through the surge impedance of the primary conductors.

- A lightning strike that misses the line but hits a nearby object sets up electromagnetic fields which can induce voltages on the conductors of the primary circuit.

- The rapid collapse of voltage that occurs when a primary arrester operates to limit the primary voltage couples effectively through the capacitance of the transformer and produces surge voltages in addition to those coupled into the secondary circuit by normal transformer action.

(d)	Lightning strikes the secondary circuits directly. Very high currents can be involved, exceeding the capability of conventional devices.

(e)	Lightning ground current flow resulting from nearby direct-to-ground discharges couples onto the common ground impedance paths of the grounding network.

Fast-acting protection devices, such as current-limiting fuses and circuit breakers capable of clearing or beginning to part contacts in less than 2 ms, leave trapped inductive energy in the circuit upstream; upon collapse of the field, very high voltages are generated.

Transient overvoltages [1] associated with the switching of power factor correction capacitors have lower frequencies than the high-frequency spikes with which this document is concerned. Their levels, at least in the case of  restrike-free switching operations, are generally less than twice normal voltage and are therefore not of substantial concern here, but should not be overlooked.

On the other hand, switching operations involving restrikes, such as those produced by air contactors or mercury switches can produce, through escalation, surge voltages of complex waveshapes and of amplitudes several times greater than the normal system voltage.  The severest case is generally found on the load side of the switch and involves only the device that is being switched.  While this situation should certainly not be ignored, in such a case the prime responsibility for protection rests with the local user of the device in question.  However, switching transients can also appear on the line side across devices connected to the line.  The presence and source of transients may be unknown to the users of those devices.  This potentially harmful situation occurs often enough to command attention.

2. Occurrence and Voltage Levels in Unprotected Circuits

  - Rate of Occurrence Versus Voltage Level

The rate of occurrence of surges varies over wide limits, depending on the particular system. Prediction of the rate for a particular system is always difficult and frequently impossible.  Rate is related to the level of the surges; low-level surges are more prevalent than high-level surges (3].  Data collected from many sources (Appendix I) have led to the plot shown in Figure 1.   This prediction shows with certainty only a relative frequency of occurrence, while the absolute number of occurrences can be described only for an “average location.”  The “high exposure” and “low exposure” limits of the band are shown as a guide, not as absolute limits [2], to reflect both the location exposure (lightning activity in the area and the nature of the system) and the exposure to switching surges created by other loads. Such data are useful in that they describe the maximum levels likely to be encountered and give some estimate of the rate of occurrence of such surges.  Of equal importance is the observation that surges in the range of 1 to 2 kV are fairly common in residential circuits.

Figure 1. Rate of Surge Occurrence vs Voltage Level

From the relative values of Figure 1, two typical levels can be cited for practical applications.  First, the expectation of a 3 kV transient occurrence on a 120 V circuit ranges from 0.01 to 1 per year at a given location -a number sufficiently high to justify the recommendation of a minimum 3 kV withstand capability.  Second, the wiring flashover limits indicate that a 6 kV withstand capability may be sufficient to ensure device survival indoors, but a 10 kV withstand capability may be required outdoors.

  - Timing of Occurrence

Surges occur at random times with respect to the power frequency, and the failure mode of equipment may be affected by the power frequency follow current.  Furthermore, the timing of the surge with respect to the power frequency may affect the level at which failure occurs [4]. Consequently, surge testing must be done with the line voltage applied to the test piece.

3.	Waveshape of Representative Surge Voltages

  - Waveshapes in Actual Occurrences

Indoor - Measurements in the field, measurements in the laboratory, and theoretical calculations indicate that most surge voltages in indoor low-voltage systems have oscillatory waveshapes, unlike the well-known and generally accepted unidirectional waves specified in high-voltage insulation standards.  A surge impinging on the system excites the natural resonant frequencies of the conductor system.  As a result, not only are the surges typically oscillatory, but surges may have different amplitudes and wave-shapes at different places in the system.  These oscillatory frequencies of surges range from 5 kHz to more than 500 kHz.  A 30 to 100 kHz frequency is a realistic measure of a “typical” surge for most residential and light industrial ac line networks.

Outdoor - Surges encountered in outdoor locations have also been recorded, some being oscillatory [5], others, being unidirectional.  Because the overriding concern here is the energy associated with these surges, a conservative but realistic description of the surges can be derived from the long-established specified duty of a secondary arrester, as detailed in Paragraph 3.2.  While this specification is arbitrary, it has the strength of experience and successful usage.

  - Selection of Representative Waveshapes

The definition of a waveshape to use as representative of the environment is important for the design of candidate protective devices, since unrealistic requirements, such as excessive duration of the voltage or very low source impedance, place a high energy requirement on the suppressor, with a resulting cost penalty to the end user.  The two requirements defined below reflect this trade-off.

Indoor - Based on measurements conducted by several independent organizations in 120 and 240 V systems (Appendix I), the waveshape shown in Figure 2 is reasonably representative of surge voltage in these power circuits. Under the proposed description of a “0.5 s x 100 kHz ring wave,” this waveshape rises in 0.5 s, then decays while oscillating at 100 kHz, each peak being about 60% of the preceding peak.

Figure 2. The proposed 0.5 s x 100 kHz Ring Wave (Open-circuit Voltage)

The fast rise can produce the effects associated with nonlinear voltage distribution in windings and the dv/dt effects on semiconductors.  Shorter rise times are found in many transients, but, as those transients propagate into the wiring or are reflected from discontinuities in the wiring, the rise time becomes longer.

The oscillating and decaying tail produces the effects of voltage polarity reversals in surge suppressors or other devices that may be sensitive to polarity changes.  Some semiconductors are particularly sensitive to damage when being forced into or out of a conducting state, or when the transient is applied during a particular portion of the 60 Hz supply cycle (Appendix II).  The response of a surge suppressor can also be affected by reversals in the polarity, as in the case of RC attenuation before a rectifier circuit in a dc power supply.

The pulse withstand capability of many semiconductors tends to improve if the surge duration is much shorter than one microsecond. For this reason, the first half-cycle of the test wave must have a sufficient duration.

Outdoor - In the outdoor and service entrance environment, as well as in locations close to the service entrance, substantial energy, or current, is still available. For these locations, the unidirectional impulses long established for secondary arresters are more appropriate than the oscillatory wave.

Accordingly, the recommended waveshape is 1.2 x 50 s for open-circuit voltage and 8 x 20 s for short-circuit current or current in a low-impedance device.  The numbers used to describe the impulse, 1.2 x 50 and 8 x 20, are as defined in IEEE Standard 28.  ANSI Standard C62.1; Figure 3 presents the waveshape and a graphic description of the numbers.

# Figure 3. Waveshapes for Outdoor Locations

4.  Energy and Source Impedance

  - General

The energy involved in the interaction of a power system with a surge source and a surge suppressor will divide between the source and the suppressor in accordance with the characteristics of the two impedances.  In a gap-type suppressor, the low impedance of the arc after sparkover forces most of the energy to be dissipated elsewhere: for instance, in a power-follow current-limiting resistor that has been added in series with the gap. In an energy-absorber suppressor, by its very nature, a substantial share of the surge energy - is dissipated in the suppressor, but its clamping action does not involve the power-follow energy resulting from the short-circuit action of a gap.  It is therefore essential to the effective use of suppression devices that a realistic assumption be made about the source impedance of the surge whose effects are to be duplicated.

The voltage wave shown in Figure 2 is intended to represent the waveshape a surge source would produce across an open circuit.  The waveshape will be different when the source is connected to a load having a lower impedance, and the degree to which it is lower is a function of the impedance of the source [6].

The degree to which source impedance is important depends largely on the type of surge suppressors that are used. The surge suppressors must be able to withstand the current passed through them by the surge source.  A test generator of too high an impedance may not subject the device under test to sufficient stresses, while a generator of too low an impedance may subject protective devices to unrealistically severe stresses.  A test voltage wave specified without reference to source impedance could imply zero source impedance - one capable of producing that voltage across any impedance, even a short circuit. That would imply an infinite surge current, clearly an unrealistic situation.

  - Proposed Approach

Because of the wide range of possible source impedances and the difficulty of selecting a specific value, three broad categories of building locations are proposed to represent the vast majority of locations [7, 8], from those near the service entrance to those remote from it.  The source impedance of the surge increases from the outside to locations well within the building. Open-circuit voltages, on the other hand, show little variation within a building because the wiring provides little attenuation f[9]. Table I outlines the three categories of building wiring.

Table 2 shows open-circuit voltages and short-circuit currents for each of the three categories.  The energy deposited in a 500 V suppressor has been computed and is shown for each of the categories.

TABLE 1 - Location Categories

TABLE 2 - Ranges of Voltage and Currents

The values shown in the table represent the maximum range, Corresponding to the “High Exposure” situation of Figure 1. For less exposed systems, or when the prospect of a failure is not highly objectionable, one could specify lower values of open-circuit voltages with corresponding reductions in the currents.

The broad range of surge voltages occurring in low-voltage ac power circuits can be simulated by a limited set of test waves, for the purpose of evaluating their effects on equipment.

Field measurements, laboratory experiments, and calculations indicate that two basic waves, at various open-circuit voltages and short-circuit current values, can represent the majority of surges occurring in residential, commercial, and light industrial power systems rated up to 600 V rms.

Exceptions will be found to the simplification of a broad guideline; however, these should not detract from the benefits that can be expected from a reasonably valid uniformity in defining the environment. Other test waves of different shapes may be appropriate for other purposes, and the present guideline should not be imposed where it is not applicable.

6.  Acknowledgments

The members of the IEEE Working Group contributed the data, shown in Appendix I, that shaped this guideline. Helpful comments, discussions, and reviews by all members of the Surge Protective Devices Committee are also acknowledged. The author is particularly indebted to the contributions of Catharine Fisher and Peter Richman for the presentation and discussion of the concepts and recommendations made in this guideline.

Appendix I - Data Base

[This format does not support the many graphics and tables of this Appendix – See the pdf file]

Appendix II - Effect of Transient Polarity Reversals on Semiconductors

Breakdown of semiconductors under various conditions of load and transient overvoltage applications has been investigated.  Evidence is presented in the two investigations cited that a reverse voltage applied during the conduction period of the power frequency produces lower breakdown voltages than the application of the same transient with no load or during blocking. Examples are given below, taken from these two investigations, showing statistically significant differences in the voltage levels.

[See the pdf file for tabulated data]

This effect is one of the reasons for selecting an oscillatory waveform to represent the environment: it will be more likely to induce semiconductor failures than a unidirectional wave. Also, it shows the significance of the timing of the transient application with respect to the power frequency cycle.

# Appendix III - Notes and References

1.	Surge Voltage

Definitions of terms used in this guideline are consistent with IEEE Standard l00-1977,Dictionwy of Electrical and Electronic Terms, 2nd ed.; however, some differences exist.  For instance, IEEE Std 100-1977 defines a surge as a “transient wave of current, potential or power in the electric circuit”--a definition broader than that used here. Transient overvoltage is defined as “the peak voltage during the transient condition resulting from the operation of a switching device”--a definition more restricted than that of the present guideline.

2.	Amplitudes of Strikes, Worst Case

The surge voltages described in this guideline include lightning effects on power systems, mostly strikes in the vicinity of a power line, or at a remote point of the power system.  The literature describes the frequency of occurrence vs amplitude of lightning strikes, from the low levels of a few kiloamperes, through the median values of about 20 kA, to the exceptional values in excess of 100 kA.  Clearly, a secondary arrester rated for 10 kA can protect adequately in case of a mild direct strike, or of a more severe strike divided among several paths to ground.  However, a very high and direct strike will exceed the capability of an ANSI-rated secondary arrester.

References:

Cianos, N. and E.T.Pierce, A Ground-Lightning Environment for Engineering Usage, Stanford Research Institute, Menlo Park, CA 94205, August 1972.

Bodle, D.W., A.J. Ghazi, M. Syed, and R.L. Woodside, Characterization of the Electrical Environment, Toronto and Buffalo, N.Y.: University of Toronto Press, 1976.

Martzloff, F.D. and G.J. Hahn, “Surge Voltage in Residential and Industrial Power Circuits,” IEEE PAS-89, 6, July/August 1970, 1049-1056.

3.	Level vs Rate of Occurrence

The relationship between the level and the rate of occurrence of surges is partly caused by the attenuation of the surges as they propagate away from the source of the surge and divide among paths beyond branching points. Equipment at a given point will be subjected to a relatively small number of high-level surges from nearby sources, but to a larger number of surges from more remote sources.

4.	Timing of Surges with Respect to Power Frequency

Lightning surges are completely random in their timing with respect to the power frequency. Switching surges are likely to occur near or after current zero, but variable load power factors will produce a quasi-random distribution. Some semiconductors, as shown in Appendix II, exhibit failure levels that depend on the timing of the surge with respect to the conduction of power frequency current. Gaps or other devices involving a power-follow current may withstand this power follow with success, depending upon the fraction of the halt-cycle remaining after the surge before current zero. Therefore, it is important to consider the timing of the surge with respect to the power frequency. In performing tests, either complete randomization of the timing or controlled timing should be specified, with a sufficient number of timing conditions to reveal the most critical timing.

5.	Oscillatory Surges During Lightning

The “classical lightning surge” has been established as 1.2 x 50 s for a voltage wave and 8 x 20 s for a current wave.  Evidence has been collected, however, to show that oscillations can also occur.  Lenz reports 50 lightning surges recorded in two locations, the highest at 5.6 kV, with frequencies ranging from 100 to 500 kHz.  Martzloff reports oscillatory lightning surges in a house during a multiple-stroke flash.

References:

Lenz, J.E., “Basic Impulse Insulation Levels of Mercury Lamp Ballast for Outdoor Applications,” Illuminating Eng., February 1964.

Martzloff, F.D. and G.J. Hahn, “Surge Voltage in Residential and Industrial Power Circuit,” IEEE PAS-89, 6, July/August 1970.

6.	Surge Impedance and Source Impedance

To prevent misunderstanding, a distinction between source impedance and surge impedance needs to be made.  Surge impedance, also called characteristic impedance, is a concept relating the parameters of a long line to the propagation of traveling waves. For the wiring practices of the ac power circuits discussed here, this characteristic impedance would be in the range of 150 to 300 , but because the durations of the waves being discussed (50 to 20 s) are much longer than the travel times in the wiring systems being considered, traveling wave analyses are not useful here.

Source impedance, defined as “the impedance presented by a source of energy to the input terminals of a device, or network” (IEEE Standard 100), is a more useful concept here.

7.	Power System Source Impedance

The measurements from which Figure 1 was derived were of voltage only. Little was known about the impedance of the circuits upon which the measurements were made. Since then, measurements have been reported on the impedance of power systems. Bull reports that the impedance of a power system, seen from the outlets, exhibits the characteristics of a 50  resistor with 50 H in parallel.  Attempts were made to combine the observed 6 kV open-circuit voltage with the assumption of a 50 /50 H impedance. This combination resulted in low energy deposition capability, which was contradicted by field experience of suppressor performance. The problem led to the proposed definition of oscillatory waves as well as high-energy unidirectional waves, in order to provide both the effects of an oscillatory wave and the high-energy deposition capability.

Reference:

Bull, J.H., “Impedance of the Supply Mains at Radio Frequencies,” Proceedings of 1st Symposium on EMC, 75CH1012-4 Mont., Montreux, May 1975.

8. Installation Categories

Subcommittee 28A of the International Electrotechnical Commission has prepared a report, referenced below, in which installation categories are defined. These installation categories divide the power systems according to the location in the building, in a manner similar to the location categories defined in this guideline.  However, there are some significant differences between the two concepts.  First, the IEC categories are defined for a “Controlled Voltage Situation,” a phrase that implies the presence of some surge suppression device or surge attenuation mechanism to reduce the voltage levels from one category to the next.  Second, the IEC report is more concerned with insulation coordination than with the application of surge protective devices; therefore it does not address the question of the coordination of the protectors, but rather the coordination of insulation levels - that is, voltages. Source impedances, in contrast to this guideline, have not been defined. Further discussion and work toward the application guidelines of both documents should eventually produce a consistent set of recommendations.

Reference:

Insulation Coordination Within Low-Voltage Systems Including Clearances and Creepage Distances for Equipment.  International Electrotechnical Commission, Report 5C28A (Central Office) 5, to be published in 1979.

9.	Open-Circuit Voltages and Wiring Flashover

Surges propagate with very little attenuation in a power system with no substantial connected loads. Measurements made in an actual residential system as well as in a laboratory simulation have shown that the most significant limitation is produced by wiring flashover, not be attenuation along the wires. Ironically, a carefully insulated installation is likely to experience higher surge voltages than an installation where wiring flashover occurs at low levels. Therefore, the open-circuit voltage specified at the origin of a power system must be assumed to propagate unattenuated far into the system, which is the reason for maintaining the 6 kV surge specification when going from the “B” location to the “C” location.

REFERENCES:

Martzloff, F.D. and K.E. Crouch “Coordination de la protection contre les surtensions dans les réseaux basse tension résidentiels,” Proceedings, 1978 IEEE Canadian Conference on Communications and Power, 78CH1373-O.

Martzloff, F.D. Surge Voltage Suppression in Residential Power Circuits, Report 76CRD092, Corporate Research and Development, General Electric Company, Schenectady, N.Y., 1976.

THE DEVELOPMENT OF A GUIDELINE ON

SURGE VOLTAGES IN LOW-VOLTAGE AC POWER CIRCUITS

F.D. Martzloff, Member, IEEE

General Electric Company

Schenectady, N.Y. 12345

Abstract - Surge voltages in ac power circuits become more significant with the increased application of miniaturized electronics in consumer and industrial products. A Working Group of IEEE is preparing a Guideline describing the nature of these surges in ac power circuits up to 600 V.  The paper describes the data base and approach used by the Working Group and the recommendations proposed to represent typical surges, in order to obtain feedback before the final writing of the Guideline. Two waveforms are proposed, one oscillatory, the other unidirectional, depending on the location within the power system. Recommendations for source impedance or short-circuit current are also included.

INTRODUCTION

Surge voltages occurring in ac power circuits can be the cause of misoperation or product failure for residential as well as industrial systems. The problem has received increased attention in recent years because miniaturized solid-state devices are more sensitive to voltage surges (spikes and transients) than were their predecessors.

Although surge voltage amplitudes and their frequency of occurrence on unprotected circuits are well known, their waveshapes and energy content are less well known. On the basis of measurements, statistics, and theoretical considerations, a practical guideline for outlining the environment for use in predicting extreme wave-shapes and energy content can nevertheless be established. A Working Group of the Surge Protective Devices Committee is currently developing such a guideline; this paper reports the status of the Guideline, presents the considerations which led to the approach chosen, and provides a possible vehicle for discussion before the final writing and publication of the Guideline.

SCOPE

The Guideline primarily addresses ac power circuits with rated voltages up to 600 V, although some of the conclusions offered could apply to higher voltages and also to some dc power systems.  Other standards have been established, such as IEEE 472, Guide for Surge Withstand Capability (SWC) Tests, intended for the special case of high-voltage substation environments, and IEEE 28, Standard for Surge Arresters for ac Power Circuits, covering primarily the utilities environment. The Guideline intends to complement, not conflict with, existing standards.

The surge voltages considered in the Guideline are those exceeding two per unit (or twice the peak operating voltage) and having durations ranging from a fraction of a microsecond to a millisecond. Overvoltages of less than two per unit are not covered, nor are transients of longer duration resulting from power equipment operation and failure modes.  Because these low-amplitude and long-duration surges are generally not amenable to suppression by conventional surge protective devices, they require different protection techniques.

Definitions of terms used in the Guideline are consistent with IEEE Standard 100-1977, Dictionary of Electrical and Electronic Terms, 2nd ed.; however, some differences exist.  For instance, IEEE Std 100-1977 defines a surge as a “transient wave of current, potential or power in the electric circuit — a definition broader than that used here. Transient overvoltage is defined as “the peak voltage during the transient condition resulting from the operation of a switching device—a definition more restricted than that of the Guideline.

While the major purpose of the Guideline is to describe the environment, a secondary purpose is to lead toward standard tests, through an application guide that will be prepared in the future. These standard tests will provide a realistic evaluation of the surge withstand capability of equipment connected to these power circuits. Of necessity, the complex real situation must be simplified to produce a manageable set of standards. One must recognize the unavoidably arbitrary character of any standard and be prepared to accept an imperfect approach which can simplify matters, rather than demand a perfect but unattainable match between the actual situation and the standard.

THE ORIGIN OF SURGE VOLTAGES

Surge voltages occurring in low-voltage ac power circuits originate from two major sources: load switching transients and direct or indirect lightning effects on the power system. Load switching transients can be further divided into transients associated with (1) major power system switching disturbances, such as capacitor bank switching; (2) minor switching near the point of interest, such as an appliance turnoff in a household or the turnoff of other loads in an individual system; (3) resonating circuits associated with switching devices, such as thyristors; and (4) various system faults, such as short circuits and arcing faults. Measurements and calculations of lightning effects have been made to yield data on what levels can be produced, even if the exact mechanism of any particular surge is unknown. The major mechanisms by which lightning produces surge voltages are the following:

(a)	A direct lightning strike to a primary circuit injects high currents into the primary circuit, producing voltages by either flowing through ground resistance or flowing through the surge impedance of the primary conductors.

(b)	A lightning strike that misses the line but hits a nearby object sets up electromagnetic fields which can induce voltages on the conductors of the primary circuit.

(c)	The rapid collapse of voltage that occurs when a primary arrester operates to limit the primary voltage couples effectively through the capacitance of the transformer and produces surge voltages in addition to those coupled into the secondary circuit by normal transformer action.

(d)	Lightning strikes the secondary circuits directly. Very high currents can be involved, exceeding the capability of conventional devices.

(e)	Lightning ground current flow resulting from nearby direct-to-ground discharges couples onto the common ground impedance paths of the grounding network.

Fast-acting protection devices, such as current-limiting fuses and circuit breakers capable of clearing or beginning to part contacts in less than 2 ms, leave trapped inductive energy in the circuit upstream; upon collapse of the field, very high voltages are generated.

Transient overvoltages associated with the switching of power factor correction capacitors [1] have lower frequencies than the high-frequency spikes with which this document is concerned. Their levels, at least in the case of restrike-free switching operations, are generally less than twice normal voltage and therefore are not of substantial concern here, but should not be overlooked.

On the other hand, switching operations involving restrikes, such as those produced by air contactors or mercury switches, can produce, through escalation, surge voltages of complex waveshapes and of amplitudes several times greater than the normal system voltage. The severest case is generally found on the load side of the switch and involves only the device that is being switched. While this situation should certainly not be ignored, in such a case the prime responsibility for protection rests with the local user of the device in question. However, switching transients can also appear on the line side across devices connected to the line. The presence and source of transients may be unknown to the users of those devices. This potentially harmful situation occurs often enough to command attention.

While the data have been recorded primarily on 120, 220/380, or 277/480 V systems, the general conclusions should be valid for 600 V systems. To the extent that surge voltages are produced by a discrete amount of energy being dumped into a power system, low-impedance, heavy industrial systems can be expected to experience lower peaks from surge voltages than 120 V residential systems, but comparable, or greater, amounts of energy potentially available for deposition in a surge suppressor.

### OCCURRENCE AND VOLTAGE LEVELS IN UNPROTECTED CIRCUITS

Rate of Occurrence Versus Voltage Level

The rate of occurrence of surges varies over wide limits, depending on the particular system. Prediction of the rate for a particular system is always difficult and frequently impossible.  Rate is related to the level of the surges; low-level surges are more prevalent than high-level surges.  The relationship between the level and the rate of occurrence of surges is partly caused by the attenuation of the surges as they propagate away from the source of the surge and divide among paths beyond branching points. Equipment at a given point will be subjected to a relatively small number of high-level surges from nearby sources, but to a larger number of surges from more remote sources.

Data collected from many sources have led to the plot shown in Fig. 1. This prediction shows with certainty only a relative frequency of occurrence, while the absolute number of occurrences can be described only for an average location. The ‘high exposure” and “low exposure” limits of the band are shown as a guide, not as absolute limits, to reflect both the location exposure (lightning activity in the area and the nature of the system) and the exposure to switching surges created by other loads.

The literature describes the frequency of occurrence vs amplitude of lightning strikes, from the low levels of a few kiloamperes, through the median values of about 20 kA, to the exceptional values in excess of 100 kA [2].  Clearly, a secondary arrester rated for 10 kA can protect adequately in case of a mild direct strike, or of a more severe strike divided among several paths to ground.  However, a very high and direct strike will exceed the capability of an ANSI-rated secondary arrester [3].

The voltage and current amplitudes presented in the Guideline attempt to provide for the vast majority of lightning strikes but should not be considered as “worst case,” since this concept cannot be determined realistically.  One should think in terms of the statistical distribution of strikes, accepting a reasonable upper limit for most cases.  Where the consequences of a failure are not catastrophic but merely represent an annoying economic loss, it is appropriate to make a trade-off of the cost of protection against the likelihood of a failure caused by a high but rare surge.  For instance, a manufacturer may be concerned with nation-wide failure rates, those at the upper limits of the distribution curve, while the user of a specific system may be concerned with a single failure occurring at a specific location under “worst-case conditions.”  Rates can be estimated f or average systems, however, and even if imprecise, they provide manufacturers and users with guidance.  Of equal importance is the observation that surges in the range of 1 to 2 kV are fairly common in residential circuits.

From the relative values of Fig. 1, two typical levels can be cited for practical applications.  First, the expectation of a 3 kV transient occurrence on a 120 V circuit ranges from 0.01 to 1 per year at a given location - a number sufficiently high to justify the recommendation of a minimum 3 kV withstand capability.  Second, the wiring flashover limits indicate that a 6 kV withstand capability may be sufficient to ensure device survival indoors, but a 10 kV withstand capability may be required outdoors.

Fig. 1. Rate of surge occurrence vs voltage level.

Timing of Occurrence

Surges occur at random times with respect to the power frequency, and the failure mode of equipment may be affected by the power frequency follow current or by the timing. Consequently, surge testing must be done with the ac voltage applied to the test piece.

Lightning surges are completely random in their timing with respect to the power frequency. Switching surges are likely to occur near or after current zero, but variable load power factors will produce a quasi-random distribution. Some semiconductors, as shown in Appendix II, exhibit failure levels that depend on the timing of the surge with respect to the conduction of power frequency current. Gaps or other devices involving a power-follow current may withstand this power follow with success, depending upon the fraction of the half-cycle remaining after the surge before current zero. Therefore, it is important to consider the timing of the surge with respect to the power frequency. In performing tests, either complete randomization of the timing or controlled timing should be specified, with a sufficient number of timing conditions to reveal the most critical timing.

WAVESHAPE OF REPRESENTATIVE SURGE VOLTAGES

Waveshapes in Actual Occurrences

Indoor - Measurements in the field, measurements in the laboratory, and theoretical calculations indicate that most surge voltages in indoor low-voltage systems have oscillatory waveshapes, unlike the well-known and generally accepted unidirectional waves specified in high-voltage insulation standards.  A surge impinging on the system excites the natural resonant frequencies of the conductor system.  As a result, not only are the surges typically oscillatory, but surges may have different amplitudes and waveshapes at different places in the system.  These oscillatory frequencies of surges range from 5 kHz to more than 500 kHz.  A 30 to 100 kHz frequency is a realistic measure of a “typical” surge for most residential and light industrial ac line networks.

Outdoor - Surges encountered in outdoor locations have also been recorded, some being oscillatory, others being unidirectional.  The “classical lightning surge” has been established as 1.2 x 50 s for a voltage wave and 8 x 20 s for a current wave.  Evidence has been collected, however, to show that oscillations can also occur.  Lenz [4] reports 50 lightning surges recorded in two locations, the highest at 5.6 kV, with frequencies ranging from 100 to 500 kHz.  Martzloff [5] reports oscillatory lightning surges in a house during a multiple-stroke flash.

Because the overriding concern here is the energy associated with these surges, a conservative but realistic description of the surges can be derived from the long-established specified duty of a secondary arrester, as detailed below.  While this specification is arbitrary, it has the strength of experience and successful usage.

###### Selection of Representative Waveshapes

The definition of a waveshape to be used as representative of the environment is important for the design of candidate protective devices, since unrealistic requirements, such as excessive duration of the voltage or very low source impedance, place a high energy requirement on the suppressor, with a resulting cost penalty to the end user.  The two requirements defined below reflect this trade-off.

Indoor - Based on measurements conducted by several independent organizations in 120 and 240 V systems (Appendix I), the waveshape shown in Fig. 2 is reasonably representative of surge voltages in these power circuits. Under the proposed description of a “0.5 s - 100 kHz ring wave,” this waveshape rises in 0.5 s, then decays while oscillating at 100 kHz, each peak being about 60% of the preceding peak.

Fig. 2. The proposed 0.5 s - 100 kHz ring wave (open-circuit voltage).

The fast rise can produce the effects associated with nonlinear voltage distribution in windings and the dv/dt effects on semiconductors.  Shorter rise times are found in many transients, but, as those transients propagate into the wiring or are reflected from discontinuities in the wiring, the rise time becomes longer.

The oscillating and decaying tail produces the effects of voltage polarity reversals in surge suppressors or other devices that may be sensitive to polarity changes.  Some semiconductors are particularly sensitive to damage when being forced into or out of a conducting state, or when the transient is applied during a particular portion of the 60 Hz supply cycle (Appendix II).  The response of a surge suppressor can also be affected by reversals in the polarity, as in the case of RC attenuation before a rectifier circuit in a dc power supply.  The pulse withstand capability of many semiconductors tends to improve if the surge duration is much shorter than one microsecond.  For this reason, the first half-cycle of the test wave must have a sufficient duration.

Outdoor - In the outdoor and service entrance environment, as well as in locations close to the service entrance, substantial energy, or current, is still available.  For these locations, the unidirectional impulses long established for secondary arresters are more appropriate than the oscillatory wave.

Accordingly, the recommended waveshape is 1.2 x 30 s for open-circuit voltages and 8 x 20 s for short-circuit current (impulse discharge current) or current in a low-impedance device.  The numbers used to describe the impulse, 1.2 x 50 and 8 x 20, are as defined in IEEE Standard 28 - ANSI Standard C62.l; Fig. 3 presents the wave-shape and a graphic description of the numbers.

Fig. 3. Waveshapes for outdoor locations.

ENERGY AND SOURCE IMPEDANCE

General

The energy involved in the interaction of a power system with a surge source and a surge suppressor will divide between the source and the suppressor in accordance with the characteristics of the two impedances.  In a gap-type suppressor, the low impedance of the arc after sparkover forces most of the energy to be dissipated elsewhere: for instance, in a resistor added in series with the gap for limiting the power-follow current.  In an energy-absorber -suppressor, by its very nature, a substantial share of the surge energy is dissipated in the suppressor, but its clamping action does not involve the power-follow energy resulting from the short-circuit action of a gap. It is therefore essential to the effective use of suppression devices that a realistic assumption be made about the source impedance of the surge whose effects are to be duplicated.

The voltage wave shown in Fig. 2 is intended to represent the waveshape a surge source would produce across an open circuit.  The waveshape will be different when the source is connected to a load having a lower impedance, and the degree to which it is lower is a function of the impedance of the source.

To prevent misunderstanding, a distinction between source impedance and surge impedance needs to be made.  Surge impedance, also called characteristic impedance, is a concept relating the parameters of a long line to the propagation of traveling waves.  For the wiring practices of the ac power circuits discussed here, this characteristic impedance would be in the range of 150 to 300 , but because the durations of the waves being discussed (50 to 20 s) are much longer than the travel times in the wiring systems being considered, traveling wave analyses are not useful here.

Source impedance, defined as the impedance presented by a source of energy to the input terminals of a device, or network” (IEEE Standard 100), is a more useful concept here.  In the conventional Thevenin’s description, the open-circuit voltage (at the terminals of the network or test generator) and the source impedance (of the surge source or test generator) are sufficient to calculate the short-circuit current, as well as any current for a specified suppressor impedance.

The measurements from which Fig. 1 was derived were of voltage only.  Little was known about the impedance of the circuits upon which the measurements were made.  Since then, measurements have been reported on the impedance of power systems. Bull [6] reports that the impedance of a power system, seen from the outlets, exhibits the characteristics of a 50  resistor with 50 H in parallel.  Attempts were made to combine the observed 6 kV open-circuit voltage with the assumption of a 50/50 H impedance [7]. This combination resulted in low energy deposition capability, which was contradicted by field experience of suppressor performance.  The problem led to the proposed definition of oscillatory waves as well as high-energy unidirectional waves, in order to provide both the effects of an oscillatory wave and the high-energy deposition capability.

The degree to which source impedance is important depends largely on the type of surge suppressors that are used.  The surge suppressors must be able to withstand the current passed through them by the surge source.  A test generator of too high an impedance may not subject the device under test to sufficient stresses, while a generator of too low an impedance may subject protective devices to unrealistically severe stresses.  A test voltage wave specified without reference to source impedance could imply zero source impedance -one capable of producing that voltage across any impedance, even a short circuit.  That would imply an infinite surge current, clearly an unrealistic situation.

Because of the wide range of possible source impedances and the difficulty of selecting a specific value, three broad categories of building locations are proposed to represent the vast majority of locations, from those near the service entrance to those remote from It.  The source impedance of the surge increases from the outside to locations well within the building.  Open-circuit voltages, on the other hand, show little variation within a building because the wiring provides little attenuation.  Figure 4 illustrates the application of the three categories to the wiring of a building.

Fig. 4. Location categories.

Subcommittee 28A of the International Electrotechnical Commission has prepared a Report [8], in which installation categories are defined.  These installation categories divide the power systems according to the location in the building, in a manner similar to the location categories defined in the Guideline.  However, there are some significant differences between the two concepts.  First, the IEC categories are defined for a “controlled voltage situation,” a phrase that implies the presence of some surge suppression device or surge attenuation mechanism to reduce the voltage levels from one category to the next.  Second, the IEC report is more concerned with insulation coordination than with the application of surge protective devices; therefore it does not address the question of the coordination of the protectors but, rather, the coordination of insulation levels — that is, voltages.

Surges propagate with very little attenuation in a power system with no substantial connected loads. Measurements made in an actual residential system as well as in a laboratory simulation have shown that the most significant limitation is produced by wiring flashover, not by attenuation along the wires. Ironically, a carefully insulated installation is likely to experience higher surge voltages than an installation where wiring flashover occurs at low levels.  Therefore, the open-circuit voltage specified at the origin of a power system must be assumed to propagate unattenuated far into the system, which is the reason for maintaining the 6 kV surge specification when going from one category to an adjacent category farther into the building.

Furthermore, source impedances are not defined in the lEC report.  The Guideline attempts to fill this need by specifying several levels of source impedance, or of short-circuit current, for the various categories.

# PROPOSED REPRESENTATION OF THE ENVIRONMENT

On the basis of the preceding discussions, the Guideline proposes to reduce the infinite variety of actual conditions to three categories, from the outside service drops to the long branch circuits and outlets.

For each category the most appropriate waveshape is indicated, an open-circuit voltage for high-impedance loads, or a short-circuit current for low-impedance loads.  The tabulation that follows shows open-circuit voltages and short-circuit currents for each of the three categories.  The energy deposited in a 500 V suppressor has been computed and is shown for each of the categories.

The values shown in the table represent the maximum range, corresponding to the “High Exposure” situation of Fig. 1.  For less exposed systems, or when the prospect of a failure is not highly objectionable, one could specify lower values of open-circuit voltages with corresponding reductions in the currents.  IEC Category I, not represented in the Guideline, would correspond to line cord-connected devices in this context.

# CONCLUSIONS

The broad range of surge voltages occurring in low-voltage ac power circuits can be simulated by a limited set of test waves, for the purpose of evaluating their effects on equipment.

Field measurements, laboratory experiments, and calculations indicate that two basic waves, at various open-circuit voltages and short-circuit current values, can represent the majority of surges occurring in residential, commercial, and light industrial power systems rated up to 600 V rms.

Exceptions will be found to the simplification of a broad guideline; however, these should not detract from the benefits that can be expected from a reasonably valid uniformity in defining the environment. Other test waves of different shapes may be appropriate for other purposes, and the present guideline should not be imposed where it is not applicable.

The Working Group is approaching the final phases of preparation of the Guideline document; comments are solicited from the engineering and user communities.  However, readers must recognize the unavoidably arbitrary character of any standard and be prepared to accept an imperfect approach, which can simplify matters and clarify the issues as well as provide uniform evaluations of performances, rather than demand a perfect but unattainable match between the actual situation and the standard.

### ACKNOWLEDGMENTS

The concepts presented in this paper have greatly benefited from the informed questions and discussions by members of the Working Group on Surge Voltage in AC Power Circuits Rated 600 V or Less, and from interested reviewers; particular appreciation for effective critiques from Catharine Fisher and Peter Richman is acknowledged.  The data base presented in Appendix I has been broadened by the contributions of the Bell Telephone Laboratories and Landis & Gyr, Inc.

# REFERENCES

1.	“Switching Surges Due to De-Energization of Capacitive Circuits,” AIEE Committee Report, AIEE Transactions, August 1 1957, pp. 562-564.

2.	Cianos, N. and E.T. Pierce, A Ground-Lightning Environment for Engineering Usage, Stanford Research Institute, Menlo Park, CA 94205, August 1972.

3.	Surge Arresters for Alternating-Current Power Circuits, IEEE Standard 28-1974; ANSI Standard C62.1-1975; lEC Standard 99-2.

4.	Lenz, J.E., “Basic Impulse Insulation Levels of Mercury Lamp Ballast for Outdoor Applications,” Illuminating Engrg., February 1964, pp. 133-140.

5.	Martzloff, F.D. and G.J. Hahn, “Surge Voltage in Residential and Industrial Power Circuits,” IEEE PAS-89, 6, July/August 1970, 1049-1056.

6.	Bull, J.H., “Impedance on the Supply Mains at Radio Frequencies,” Proceedings of 1st Symposium on EMC, 75CH1012-4, Montreux, May 1975.

7.	Martzloff, F.D. and F.A. Fisher, “Transient Control Level Philosophy and Implementation:	The Reasoning Behind the Philosophy,” Proceedings 2nd Symposium on EMC, 77CH1 224-5 EMC, Montreux, June 1977.

8.	Insulation Coordination Within Low-Voltage Systems Including Clearances and Creepage Distances for Equipment, International Electrotechnical Commission Report SC28A (Central Office) 5, to be published in 1979.

# APPENDIX – DATA BASE

[This format does not support the many oscillograms and tables of the Appendix.  See the pdf file]

A CONSENSUS ON POWERING AND GROUNDING

SENSITIVE ELECTRONIC EQUIPMENT

Thomas S. Key, Member IEEE

Sandia National Laboratories

Albuquerque, NM 87185

François D. Martzloff, Fellow IEEE

National Bureau of Standards

Gaithersburg, MD 20899

Abstract—As sensitive electronic processing systems proliferate in our facilities so do power-related problems.  Efforts to alleviate these problems have ranged from installing expensive power conditioning equipment to applying special grounding techniques not found in conventional safe grounding practice. Understanding of what is actually going on has been lacking. We find power systems, modified from basic practice to the extent of being unsafe, that continue to be plagued with powering- and grounding-related problems. Out of this chaos we are persuaded to study and understand the complexities of the problem and to begin developing good practices. This is the objective of the IEEE Working Group on Powering and Grounding Sensitive Electronic Equipment, Standards Project P1100. We will introduce Project P1100, preview its scope and technical content and, most importantly, invite participation in this seriously needed consensus standard activity.

INTRODUCTION

Powering and grounding sensitive electronic equipment is a growing concern for commercial and industrial power system designers. This concern frequently materializes after start-up when electronic system operating problems begin to occur.  Grasping for power conditioning equipment or magic grounding methods is a common response. In some cases this has led to unsafe practices and violations of the National Electrical Code without solving operating problems. Although good information is available, there is presently no consensus on recommended practice. This leaves responsible engineers to proceed from what they already know or can readily obtain in the literature. Unfortunately, there is conflicting information in the literature and, for most of us, the technical particulars are somewhat foreign to our power system design experience.

The concept of load and source compatibility is not new. The need to provide power with a steady voltage and frequency has been recognized since the inception of the electric utility industry. However, the definition of 'steady' has changed over the years, the greater susceptibility of increasingly sophisticated electronic equipment to the departure from ‘steady’ conditions. Some of the early concerns were flicker of light bulbs due to voltage variations and overheating of electomagnetic loads or interference of communication loads due to voltage waveform distortion. Recognition of these problems led to the development of voluntary standards which contributed significantly to reducing occurrences.

More recently, transient voltage disturbances associated with short circuits, lightning, and power system switching have emerged as a major concern to manufacturers and users of electronic equipment. Today's complaints about the quality of power are not easily resolved because they involve both a multitude of different causes and a variety of specific sensitivities in the affected equipment. Power system designers, utility companies, load as well as source equipment manufacturers, must cooperate with each other to find effective solutions. As in the past, voluntary consensus standards are needed.

The issue of grounding, in particular how to deal with noise and safety simultaneously, is complicated by philosophies advocated by people of different backgrounds. Power-oriented engineers often differ in their perception of common problems and solutions. One of the goals of the proposed standard is to promote better understanding of the real issues and to dispel some misconceptions on how to avoid or correct electronic system grounding problems.

Since the earliest days of electric power, users have counted on utilities to provide electricity that is as free as possible from outages, voltage surges, and harmonic waveshape distortions. Reducing such power line has always been a critical concern for utilities. Recently, however, new sources of disturbances have begun to proliferate, just as many pieces of equipment are becoming more sensitive to these same power disturbances. Some of these disturbances are generated by adjacent equipment, so that the supply should not be blamed for the occurrence. These developments have presented utilities and users with a new set of complex power quality issues that will require wide-reaching cooperative efforts to be resolved.

A common practice applicable to power incompatibilities is to install interface equipment between the raw utility power and sensitive loads. Difficulties in assessing this need are: (1) the quantification of just how much downtime is power-related, (2) the subjective nature of estimating the cost of sensitive operation attributable to power. The cost/ benefit aspects of the problem can be addressed from the technical point of view in a standard, but detailed economic analysis and specific decisions remain the prerogative of the user allocating the resources. Focusing on the technical issues, dispelling misconceptions, and recommending practices can assist the user in making an informed economic decision.

With that goal clearly defined, the new IEEE Working Group, Project P1100, was formed to develop a consensus standard that recommends practices for powering and grounding sensitive electronic loads in commercial and industrial power systems. The document is currently at the first draft stage.

## POWERING ELECTRONIC SYSTEMS

Powering an electronic system is fundamentally the same as powering any electrical system. Estimating the load, matching current and voltage requirements, or planning for future growth involves the same basic information. Similarly, designing an appropriate electrical distribution system, selecting and coordinating overcurrent protection, and assuring good voltage regulation makes use of the same engineering practices. Even the principles of availability and reliability can be applied to electronic loads in the same way as to any other load.

An excellent reference library available for designing commercial and industrial power systems of all types is the IEEE Color Book series. There are currently nine Color Books in the Series providing recommended practices. The objective is to assist in the design of safe, reliable, and economical electric power systems by providing the consensus of knowledge and experience of the contributing IEEE members. Project P1100 is intended to yield a new Color Book in the series, directed specifically at powering and grounding sensitive electronic equipment.

The Duration of a Disturbance Is Key to Its Impact,

Computers are just like motors or lights: when the power goes away, the device quits, and when power is restored, it restarts. Of course, it is frequently integrity of the process rather than the actual device that we must concern ourselves with. If we lose power to one high speed conveyor being fed by another high speed conveyor, we can expect a mess somewhere on the factory floor. Likewise, a central processor controlling a check printer with a stack of sequenced commands in volatile memory will most likely be upset by the loss of power continuity.

The duration of loss of power continuity is the key factor in predicting if a process disruption will occur. A large freezer may be able to ride through an outage of several hours before cooling loss. We are allowed seconds to restore light in a hospital operating room. Data processing upset may occur in tens of milliseconds, or in cycles of 60 Hz. ac power. An outage is therefore defined differently by different users and producers of electric power, sometimes' creating an obstacle to communication between these interested parties. Utility companies and their power supply contracts will normally only address outages measured in minutes. They do not consider perturbations lasting a few seconds or less as the utilities responsibility. When customer equipment is more critical or more sensitive than the norm, they consider it the customer’s problem. The special power quality and continuity requirements of a number of commercial and industrial loads are described in the IEEE Orange Book [1].

Data processing equipment susceptibility to short duration (cycle to cycle) breaks in power continuity not be overgeneralized. First, a computer can ride through a short outage. It happens every cycle of the ac power sine wave. Second computers should be no more sensitive to steady-state voltage variations than any other load. American National Standard C84.1 establishes steady-state voltage ranges that apply to all equipment. Furthermore, harmonic distortion in the utility voltage has not been shown to have any more impact on electronic loads than on motors or relays. We conclude that if electronic loads have susceptibilities to power-line disturbances, they also have tolerances that may reduce the cost and effort required to protect them.

A profile of data processing equipment susceptibility (and tolerance) to variations in the source voltage, Figure 1, has been published in an IEEE 'Recommended Practice’ [1], and a NBS "Guideline" [2]. Presented as a "Typical design objective of power-conscious computer hardware designers", it is not a computer industry standard. However, as a typical susceptibility profile, it does demonstrate the useful feature of increasing equipment tolerance with decreasing duration of voltage perturbation. As a practical matter, there are disturbances of short than long duration. So, by comparing actual disturbance data to this profile we begin to quantify our exposure to power-related problems.

Energy Analysis Is Useful In Diagnosing Power Problems

We can interpret Figure 1 from an energy flow viewpoint on the right, we have limitations related to the wrong energy level occurring in the steady state. This limitation equates to a steady state voltage regulation problem. For cycle to cycle time intervals, our concern shifts to insufficient energy that occurs during an undervoltage condition resulting from common overloads or short circuits. In microsecond time domains, too much energy, in the form of a lightning or switching event generated overvoltage, surfaces as a practical concern.

This analysis can facilitate defining power-related problems in a way that leads to effective selection of power equipment or other appropriate corrective action. The first step is powerline voltage monitoring to determine site power quality. Once a site-specific power quality profile has been established and energy-related problems identified, one can proceed to single out appropriate power enhancement measures. For example, if intermittent undervoltages or sags are recorded, then interface equipment such as a motor-generator might be effective in riding through these shortages of energy. Further discussion of this method of diagnosis and prescription is found in [3).

The application of Figure 1 seems quite straight-forward; however, solving a real-life power-related problem may not be. For one thing, the tolerance to overvoltage of several hundred volts, indicated in Figure 1, assumes an assault at the input to the computer power supply. The electronic equipment tolerance to overvoltages experienced in other locations may be significantly less. Noise coupled into the electronic system via many possible alternate paths, as compared to surges conducted along the power line, can disrupt data at a 5-volt logic level.

Related to the noise-coupling problem, is the attempt to apply Figure 1 in the presence of poor grounding or incorrect surge protecting of equipment. These mistakes may allow internally generated power-related problems that totally evade any power interface equipment installed, per Figure 1, to protect the site from the outside world. At the same time, such interface equipment will be adding cost and probably reducing overall power system reliability.

A systems engineering approach is required to properly address all aspects of the power- and noise-related, problems. In Project P1100, we are attempting to present the best explanation possible of the myriad of power enhancement products and at the same time maintain a systems perspective- This perspective must include other critical elements of the power system, i.e. grounding and surge protection details, and installation procedures. We have found that grounding, discussed next, is a key to noise-related problems.

## GROUNDING ELECTRONIC SYSTEMS

The subject of grounding is perhaps the most misunderstood, with the result that a large portion of the problems encountered in power supply applications originate from inappropriate grounding practices. An indication of the complexity of this subject is the fact that it occupies over five pages of the IEEE dictionary; no wonder misconceptions still abound. The existence of this problem in electronic systems can be explained by the different meanings attributed to the term 'ground' by the different specialists involved. Starting with the 60 Hz or power-frequency engineer, 'ground' is synonymous with 'earth'; its function is to provide a low-impedance path for return of power system fault currents to the generator. This low-impedance path serves a safety role by limiting voltage differences during system faults and by allowing sufficient fault currents to assure prompt tripping of the source circuit breakers.

In this context, ground connections are generally large copper conductors, offering low impedance to power-frequency current. Emphasis is given to the resistance of the connection to earth' – that is, the subjacent soil – by appropriate dimensions and’ number of driven rods in the earth, of buried counter-poise conductors, etc. The safety grounding system is passive and should not be called upon to carry rated current except during intermittent anomalies of power system operation such as short circuits. Occasionally, steady-state currents may be present due to device leakage or to the nearby influence of strong magnetic fields, for instance adjacent conductors of an arc furnace. Nevertheless, the steady-state current in grounding conductors should be relatively small when compared to phase conductor currents (NEC 250-21).

###### Both “Earthing” and “Referencing” Must Be Considered

Shifting now to the electronic engineer, designing his data processing equipment, “ground” is synonymous to 'chassis'. That is, the metal enclosure of the equipment, sometimes symbolically concentrated into a single shiny metal pad at the bottom of the cabinet to which all connections to ‘ground’ are routed—and not always by the most direct route. His data processing circuitry involves analog or pulse voltage signals of generally less than 15 volts, or it involves current loops of a few milliamperes.

These signals can be transferred in a balanced, ungrounded circuit or a single-ended circuit with a common reference. Balanced circuits are isolated from ground but their voltage with respect to ground (common mode) is still significant to the operation and potential susceptibility of the circuits. Single-ended circuits carry signals referred to a common potential, most often that of the equipment internal chassis, generally called ‘reference’. Thus, in either case it appears that the electronic engineer’s concern is that his referencing system carries signal currents that can become polluted by spurious ground currents either through common connection points with the earthed system or by common-mode noise coupling.

Now enters the systems engineer responsible for the installation of the data processing system within one room of a building at best, or distributed among several buildings at worst: to him, 'ground' takes a double meaning. The first is the concept of the power system engineer, the second is the concept of the electronic engineer and, alas, they are not the same. If only the first had been called 'earth', and the second called ‘reference', perhaps the designers would have coordinated their two distinctive requirements ahead of time and much on-site misery would have been avoided.

Instead, in the electronics engineer's case, the impedance of his 'reference' system includes a substantial inductive component because of the high frequency of the signal and noise currents. The large existing copper cables, suitable for earthing, are not suitable for referencing. A new ground reference grid providing a large number of different path links for the various noise frequencies will now have to be incorporated into the system.

So we see, for electronic loads, we have both safety and noise to concern ourselves with. Safe operation of an electrical or electronic system depends on the integrity and low impedance of its earthing. Undisturbed operation of the same systems depends on the geometry and intrinsic low impedance of its reference, regardless of the impedance between the reference and the earth [2].

The significance of reference and insignificance of earth connection can be illustrated by two examples:  to prove its reality, consider that sophisticated equipment aboard an electronic countermeasures airplane are doing quite well, thank you, without an earth connection; back an the ground we find an illusion held by the system operator, confronted with interference and a referencing problem, when he contemplates and sometimes implements 'better grounding' by breaking up the concrete floor of the computer room to install additional ground rods.

The solution to this operator's problem is not 'better grounding', but better referencing--such as in the case, of the airborne electronic system. On the ground level, the better referencing can be obtained by establishing a 'ground grid'. Here the major criterion is low impedance at high frequencies between any two points of the ground grid. Recall that the safety ground system should provide low impedance at low frequencies. In a computer room design, the 2'x2' grid of a usual raised floor structure lends itself quite naturally to providing such a good reference. There are or course a few electrical design features that must be properly incorporated. References [2] and [4] already provide guidance for implementing this solution, and Project P1100 will extend the guidance to the status of a consensus standard.

Attempts at Noise or Surge Control Should Not Create Adverse Side Effects.

The first side effect is associated with the problem of circulating currents in the ground and reference conductors. Without question, these currents can inject parasitic signals into the data lines. This injection is common-mode noise coupling caused by unavoidable shared connection points between the power and the electronic equipment chassis. The problem is real, the side effect is associated with how not to solve it.

There have been a number of apparently successful remedies such as sometimes obtained by opening up these ‘ground loops', by creating a 'single point ground', by establishing a ‘dedicated/isolated ground', and finally, in the ultimate language contradiction, by installing a 'floating ground'. All of these concepts, motivated by steady-state, low-level noise reduction theory, can and frequently do overlook the potential of power frequency faults.

Attempts to decouple equipment chassis from earth ground for the purpose of isolating and insulating often defeat the basic safety function of earth ground. They ignore safety and hardware damage issues associated with the relatively rare but potentially lethal situations occurring during power system faults and lightning surges. They also violate the National Electric Code as described in [5]; such practices should be eradicated!

Continuity of the green wire or metallic raceway grounding system is not incompatible with achieving effective noise, control. Simply apply the principles of the ground reference grid discussed above and in [2]. Give careful attention to surge protection for both data and power lines as presented below. Don't resort to tampering with safety aspects of the grounding system to control noise. Finally, as a consulting engineer, called upon to correct power- or noise-related problems, beware of both the desire for and the existence of dangerous grounding practices.

Another adverse side effect is associated with the configuration and use of grounding conductors. It is the occurrence and conversion of what is called ‘common mode’ and ‘differential mode’ in multi-conductor systems. Initially defined in the context of communications circuitry, these two modes have been applied to ac power systems that include phase, neutral, and grounding conductors. Here a grounding conductor exists or is implied by the presence of earthed bodies. As with ‘referencing,’ the situation is confused by the blurring of boundaries between signal processing technology and power delivery/system safety requirements.

Disturbances can occur in common mode but cures might be erroneously proposed that address only differential mode disturbances, or vice versa. Remedies to a differential mode surge can create a common-mode disturbance. For instance, a frequently applied and very effective method for common-mode noise elimination is the installation of an isolation transformer. However, we should not expect this transformer to reliably attenuate differential-mode noise [6]. Conversely, the installation of a single protective device between the phase and neutral conductors, at the end of a long branch circuit, will: (1) clamp the voltage between these two conductors, and (2) create a large voltage, akin to mode, between the neutral and grounding conductors.

The appropriate solution, discussed in detail in Reference [7] for the case of a single-phase three-wire system, consists of providing an additional surge-clamping device between the neutral and grounding conductors. Project Pl100 will address the polyphase as well as the single-phase situation.

With forethought, these side effects can be avoided. It is feasible to design a system where noise problems are successfully resolved without resorting to unsafe grounding practices. We have pointed out that a reference grid system may be economically incorporated in a computer room raised floor. Reference [4] describes how the reference grid approach, when used with computer power centers (isolation transformers) and surge suppression networks can successfully harmonize power and signal grounding requirements. In Reference [2] detailed guidelines are provided for computer room grounding. However, since these documents do not constitute a consensus standard, one major goal of Project P1100 will be to establish a consensus opinion by describing good practices as well as by citing erroneous practices that should be avoided.

###### SURGE PROTECTION

Power systems are exposed to external influences which can couple energy into the circuits, causing a momentary overvoltage or overcurrent, generally described by the term 'surge'. Internal switching of loads in these systems can also create these momentary events. Another phenomenon, the discharge of electrostatic charges that have built-up on the human body or objects, can also inject unwanted voltages or currents into electronic circuits. Finally, another threat is related to nuclear explosions effects, under the acronym of NEMP (Nuclear Electromagnetic Pulse). The proposed standard will address the first two of these surges, lightning- and switching-related surges.

Surges can have many effects on equipment, ranging from no detectable effect to complete destruction. In general, electromechanical devices withstand increasing voltage surges until breakdown occurs, while electronic devices can have their operation up-set before hard failure occurs. With increasing surge levels, progressively more intense upset occurs, until breakdown takes place. If sensitive electronic data processing equipment should be protect from even the upsetting levels, it is axiomatic that damaging surges need to be dealt with before they propagate beyond the service entry for the computer room [7] and [8].

Definitions of the level beyond which transient over-voltages become a threat depend on the type of victim equipment or process. Where electromechanical devices can generally tolerate short duration voltages of twice rating plus 1000 volts, few solid-state devices can tolerate more than twice their normal rating. Furthermore, data processing can be affected by fast changes with relatively small voltage amplitudes compared to the hardware-damaging overvoltages.

Lightning Surges Can Strike in More Ways Than One.

Lightning surges on power systems occur in two modes: direct attachment of the lightning path to the power systems conductors, and electromagnetic coupling of energy into the power system conductors by the radiation of a nearby lighting discharge.

Direct attachment injects the total lightning current into the system. The current amplitudes range from a few thousand amperes to more than 200,000 amperes. However, the rapid change of current through the impedance of the conductors produces a high voltage; most often this high voltage causes secondary flashover to ground, diverting some current even in the absence of an intentional diverter. As a result, equipments connected at the end of overhead conductors are rarely exposed to the full lightning discharge current.

Induction of surges by nearby lightning discharge is a less dramatic, but more frequent event. The resulting surge characteristics are influenced not only by the driving force—the electromagnetic field—but also by the response of the power system—its natural oscillations. This dual origin makes a general description of the occurrence impractical, but nevertheless a consensus exists on what representative threats can be expected in various physical environments[9].

### Switching Surges Can Be More Damaging Than Lightning

Whenever a circuit containing capacitance and inductance is being switched on or off, a transient disturbance occurs because the currents and voltages do not reach instantaneously their final value- This type of disturbance is inescapable and its severity depends on the relative power level of the load being switched compared to the power system in which the switching takes place Most of these disturbances involve the of the response of the power system, just as in the case of induced lightning surges, so that in practice the surges observed within a building are similar in their diversity, regardless of their origin—lightning or switching.

More complex circuit phenomena, such as current chopping and restrikes, can produce surge voltages reaching ten times the normal circuit voltage, involving energy levels determined by the power rating of the elements being switched. These complex surges can have very destructive effects, even on rugged equipment, and must generally be controlled at the source rather than simply mitigated at the load [9].

Effective Protection Techniques Have Been Developed.

Survival or undisturbed operation of the equipment can be achieved in three manners: eliminating the cause of surges (for instance, eliminate lightning, switching, etc.), producing equipment immune to any level of surges, no matter how high, or, the obvious choice, finding the best economic trade-off where moderate surge withstand capability is built into equipment, and the worst surges occurring in the environment are reduced, by application of suitable protective  devices, to a level which the equipment can tolerate.

Because the of the source of the surge is an energy transfer phenomenon, involving a current, any attempt at blocking or restricting this current by a high impedance series path will only produce higher surge voltages until breakdown occurs. Breakdown allows current in an uncontrolled manner, generally through an unwanted path. In contrast, a surge protective device, by diverting the current, offers a known, predictable and therefore harmless path.

This diversion of major surge currents is best accomplished in two stages. The first diversion should be performed at the entrance to the building, typically by a conventional surge arrester, such as a sparkover type device, rated for this duty [10]. Then, any residual overvoltage, resulting from the action of the service entrance arrester, can be dealt with by again diverting current with a secondary protective device.

For this secondary protection, we recommend a clamping type solid state device, installed at the power panel of the computer room, at the terminals of a connected load, etc. Figure 2 illustrates this coordination between two surge diverters and a series impedance.

A Need for Integrated Surge Protection Is Recognized.

An aspect of surge protection that might be overlooked is the need to provide an integrated approach to the protection of the power and data ports of an electronic system. A false sense of security might be created when surge protection is installed in the power supply and at the data entry and exit ports. However, unless the installation and ground connection of these protective devices have been correctly implemented, difficulties might still develop as a result of differences in ground potential rise during operation of the protective devices.

As an Figure 3 shows the case of a computer powered by the building supply on one side and interfacing with data lines from outside sensors on the other side. The power lines are protected at the service entrance and the data lines are protected at their entry point into the building. A surge impinging on the data lines and correctly diverted to ground at the entry point will unavoidably produce a rise in the potential at the 'ground' point where the data line protective device is connected, as compared to the 'ground' point where the power line protective device is connected. The same difference of potentials would arise if the surge impinged on the power supply port. Thus, the 'ground’, potentials on the power and data interface inputs at the computer cabinet will not be the same, leading to upsets or damage. This phenomenon is frequently to the dismay of the user who thought that adequate protection had been implemented with the two devices installed at the entry points.

In such an instance where the entry points are far apart, the solution consists in providing a secondary protective device for each port of entry into the computer cabinet (or entry to the computer room where the computer is installed on an equipotential plane or ground reference grid), and assuring the same point of ‘ground’ connection is used for these protective devices. While the qualitative aspect of this solution is gaining recognition, the quantitative parameters still need to be investigated. By the time Project P1100 nears completion, we expect that measurements, now in progress at the National Bureau of Standards, will contribute to the quantitative answer.

# STANDARDS PROJECT P1100

We have thus far reviewed the need and some of the key issues that motivate us to recommended practices for powering and grounding sensitive electronic loads. In so doing we recognize that there are clearly many more details to address and many opinions and facts to reconcile. The following section will layout how we are currently proceeding in this effort. It is intended that enough detail BE provided to encourage discussion and feedback to the Working Group.

## Approved Scope and Purpose of P1100

Project P1100 is titled "Recommended Practice for Powering and Grounding Sensitive Electronic Equipment (A Color Book)" The IEEE technical sponsor is the Power Systems Engineering Committee of the Industrial Applications Society. A scope has been approved as follows:

"This project recommends design, installation and maintenance practices for electrical power and grounding (including both safety and noise control) of sensitive electronic loads such as computers, industrial controllers, and other electronic data processing equipment used in commercial and industrial applications.”

## Status of Project P1100

The standards project authorization request (PAR) was submitted in June 1985 and approved by the IEEE Standards Board in September. A 'strawman' outline for eleven chapters was developed and chapter objectives translated into a set of directives to chapter authors. Internal and external review procedures have been established. Preparation of a first draft is underway.

Meanwhile interest continues to grow. A number of tutorials have been offered both inside and outside of IEEE. As an apparent offshoot of deregulation, the industry is beginning to look at marketing a higher quality electric service with power conditioning equipment incorporated at increased electric energy rates. Still, there is no consensus standard available as a reference for electrical engineers responsible for the power system design. Help is needed in developing, writing, and reviewing this standard.

Proposed Chapters and Directives

1.0	INTRODUCTION - covers the purpose and background in much the same way as in this paper.

2.0	SCOPE - as quoted in this paper.

- DEFINITIONS - this chapter provides definitions not otherwise available in IEEE Standards or as necessary to improve readability. The Chapter Chairperson is "Provost Marshal" with regard to use of undefined terms or acronyms in other chapters.

- NEED GENERAL NEED GUIDELINES – this chapter is intended to identify the relevant codes and standards as well as the existing electrical environment that sensitive electronic equipment is typically subjected to in the field. Topics include coordination with other guidelines, electrical safety, power quality, grounding, surge protection, life-safety, and telecommunications systems considerations. These guidelines are established as a basis for the treatment of performance requirements and recommended practices in subsequent chapters.

- FUNDAMENTALS - this chapter introduces the reader  to the fundamental technical information necessary to understand and to apply recommended practices for design of a compatible and essentially hazard-free interconnection. Fundamentals not unique to sensitive electronic and/or electrical equipment will be treated very lightly, or only by reference to other IEEE Standards and appropriate books on recommended engineering practice. Fundamentals to be covered include power system quality, electronic data processing equipment power quality requirements, load and supply compatibility, grounding bonding and shielding, protection, and wiring practices.

- RECOMMENDED DESIGN/INSTALLATION PRACTICES - is the main message of this publication and is expected to be most difficult to gain consensus. Vagueness at this point would be a disservice to the reader. We intend to. put down on paper our collective engineering experience and judgment to pinpoint recommended practices. The proposed subjects are general discussion on performance and safety, 60 Hz ac system, 400-480 Hz systems, and life-safety system interfaces and controls.

- NON-RECOMMENDED DESIGN/INSTALLATION PRACTICES --is the chapter in which we very deliberately attack "wives' tales" and raise "warning flags," but are careful not to introduce any. new concepts or materials. Commonly observed non-recommended practices will be emphasized. The chapter is outlined by specific design topic to facilitate quick retrieval from the reference.

- SPECIAL MEASUREMENTS AND INSTRUMENTATION -- presents information on special measurement requirements and on available equipment that are unique to investigating and diagnosing problems in power systems that serve sensitive electronic equipment. The proposed approach is to start with dc measurements of voltage, current, and power and to progress through the fundamental frequencies (60 and 415 Hz) to harmonic and higher frequencies, up to 300 kHz. RFI/EMI will be covered by reference only.

- SITE POWER ANALYSIS AND SITE SURVEYS - draws from the technical information base established in the previous chapters, and presents the practical aspects of problem diagnosis by an on-site engineer or technician. A section on interpreting and applying published power quality survey data is included; however, the chapter emphasis is he application of survey data from the user’s own site.

- SELECTION AND VERIFICATION OF EQUIPMENT AND MATERIALS - presents the myriad of available power enhancement equipment from a basic technology, performance, and functional point-of-view. A blend of manufacturer and user input is required. Manufacturers will be encouraged to provide generic rather than marketing details of equipment. How to verify equipment performance by testing is also covered.

- CASE HISTORIES - is intended to provide explicit examples of real-world performance and/or safety problems that have been encountered in the field. Examples are chosen that did not conform, in one or more ways, to specific recommended practices presented in this publication. Special care will be taken to ensure that the selected examples are representing key-points of Chapters 6 and 7, rather than interesting, but, obscure ones.

- APPENDIX (as required)

- ANNOTATED BIBLIOGRAPHY

- INDEX

Coordination With Other Codes and Standards

As with most standards activities, there is a whole array of existing and proposed standards that are to the technical scope. Careful coordination is critical to ensure proper treatment and avoid unnecessary overlap. Thus far we have identified or have been requested to coordinate with the activities listed in Table 1.

# CONCLUSIONS

A consensus standard is needed for powering and grounding sensitive electronic equipment. This standard should not only organize and present recommended practices but also identify and dispel misconceptions and discourage non-recommended practices. Ahead of us is a tough and time-consuming job of sorting out various points of view and coordinating various other related standards activities. It will be several years before the task can be properly completed. This introductory paper is intended to be the first of several preceding publication of the consensus standard. The Project P1100 Working Group will welcome comments on the concepts presented in this paper and contributions to the final document.

###### REFERENCES

[1]  IEEE Recommended Practice for Emergency and Standby Power Systems for Industrial and Commercial Applications, IEEE Orange Book, Std 446-1980

[2]  National Bureau of Standards, Guideline on Power for ADP Installations, Federal Information Processing Standards Publication, FIPS PUB 94, Sep 21, 1983.

[3]  T.S. Key, "Diagnosing Power Quality-Related Computer Problems," IEEE Transactions on Industrial Applications, Vol. IA-15, no.4 , pp 381-393, July/August 1979.

[4]  W.H. Lewis, "Recommended power and signal grounding for control and computer rooms," IEEE Transactions on Industrial Applications, Vol. IA-21, No 6, pp. 1503-1516, Nov/Dec 1985.

[5]  W.H. Lewis, "Application of the NEC to the of sensitive electronic equipment," IEEE Transactions on Industrial Applications, Vol. IA-22, No 3, pp. 400-415, May/Jun 1986.

[6]  F.D. Martzloff, "The propagation and attenuation of surge voltages and surge currents in low-voltage ac power circuits, IEEE Transactions Power Apparatus Systems, vol PAS-102, pp. 1163-1170, May 1983.

[7]  F.D. Martzloff and H.A. Gauper, Jr., "Surge and High-Frequency propagation in Industrial Power Lines," 	IEEE Transactions on Industrial Applications, Vol. IA-22, pp. 634-640, July/August 1986.

[8]  F.D. Martzloff, "Coordination of surge protectors in low-voltage ac power circuits," IEEE Transactions Power Apparatus Systems, vol PAS-99, pp. 129-133, Jan/Feb 1980.

[9]  IEEE Guide for Surge Voltages in Low-Voltage AC Power Circuits, ANSI/IEEE C62.41-1980.

[10]  IEEE Standard for Surge Arresters for AC Power Circuits, ANSI/IEEE C62.1-1981.

A STANDARD FOR THE 90S:

IEEE C62.41 SURGES AHEAD

François D. Martzloff

National Institute of Standards and Technology

With each year that passes, we are relying more and more on electronics in our lives, at home, at work, for travel, for defense... the list is endless. Reliability of these electronic systems is essential, and this in a context of increased sophistication which often brings about more susceptibility to disturbances. Thus, immunity to electromagnetic disturbances, including surges in the power line, is a must.

Designers and users perform surge testing to verify that, indeed, their equipment is immune to these surges. The question, however, is what level of immunity must be achieved, since there are engineering tradeoffs to be made, as well as economic considerations. Depending on the type of equipment (its mission) and the location where it will be used, a moderate or very high degree of immunity is appropriate. To select the appropriate level of surge stress and to perform surge testing in a manner that will yield valid results while ensuring safety, reliable guidance is needed.

Ten years after its first publication as IEEE Standard 587, the Guide on Surge Voltages in Low Voltage AC Power Circuits (now ANSI/IEEE C62.41-1980) has undergone a major transformation into a Recommended Practice format. From a guide proposing two basic waveforms to represent typical surges, the document now proposes consideration of two standard waveforms (the old friends of 1980) complemented by three additional waveforms, one a fast burst, the others longer, high-energy surges.

## A History of IEEE C62.41

Actually, the occurrence of surges that led to the launching of a small working group in 1966 to develop IEEE 587 have not changed much, although the electronic equipment affected by surges as well as the standard-writing group have undergone considerable changes. The initial effort to provide guidance for designers on surges in low voltage circuits was started by Dave Bodle [1], who persuaded a small group of concerned fellows to seek a home in the IEEE Surge-Protective Devices Committee (a body which, at the time, was mostly concerned with the high voltage world of electric utilities). This pioneer group set out to collect published data on surge occurrences and even circulated among its members a set of six peak-reading surge counters donated by one sponsor to add to its data base. These were the days before the explosive development of disturbance monitors cum graphics. And so, IEEE 587 was born in 1980, with great expectations that it would be a useful guide for designers and users of electrical and electronic equipment.

Alas, there were no other documents available to guide those users in selecting severity levels from the choice proposed by IEEE 587. In particular, the citation of 6 kV being a practical upper limit for the occurrence of surges in 120-V circuits was soon misconstrued as implying a requirement that all equipment should be designed to withstand 6 kV surges. Product specification sheets began to state ‘meets IEEE 587,’ forgetting the difference between a standard and a guide in IEEE parlance. In the meantime, the guide was renumbered ANSI/IEEE C62.41, as part of a family of surge-related documents [2] but the ‘587’ label has stuck and is even found in the model names of several commercial surge generators.

In a first attempt to help users make sensible and correct decision on surge testing, the IEEE working group developed a Guide on Surge Testing - ANSI/IEEE C62.45-1987. The Guide provided information on how to conduct reliable and safe surge tests (“Don't kid yourself, don't kill yourself!”), also pointing out how to interpret the concepts of locations categories proposed in the original document. However, the questions and misuse by some continued, so the working group resolved to update the guide.

Normally, IEEE procedures require a 5-year cycle of reaffirmation or revision but the challenge of reviewing new data and developing consensus on this subject stretched the work into ten years, culminating in a Recommended Practice that was approved early in 1991 and is now available from IEEE. From a group of 12 people in 1980, the working group grew to 29 by 1990, reflecting the growing interest about surge protection among users and manufacturers of electronic equipment. Reconciling the different points of view from the enlarged group has produced a new document that should receive even better acceptance than the original 1980 version and, hopefully, result in fewer misunderstandings.

## Toward a More Useful Standard

One of the first difficulties was to arrive at a satisfactory agreement of what the word ‘surge’ means; to some a surge is a temporary increase in the AC line voltage. That meaning is now replaced by the term “swell,” although a sizeable fraction of the engineering community will continue to use the word surge with that meaning.

Next came the issue of noise versus surges (spikes, etc.). How big must a voltage change be to become a surge? That issue was in fact not resolved; instead, a conceptual figure was included in the document to show the relationships among several parameters (see Figure 1) and thus leave the bottom end of the range open to appropriate interpretation depending on the circumstances. In addition, the single-value upper limit of voltages proposed in the 1980 version has been replaced by a table featuring three levels for each waveform, according to the location category or the system exposure. The menu of waveforms proposed in the 1991 version is new and, hopefully, improved, and includes the following types:

- The 0.5 s - 100 kHz Ring Wave, defined in the 1980 version, as standard waveform.

- The Combination Wave, 1.2/50 s - 8/20 s, also from 1980, as standard waveform.

- The EFT Burst (5/50 ns), adopted from IEC 801-4, as additional waveform.

- A new 10/1000 s Wave, for high-energy stress, as additional waveform.

- A new 5 kHz Ring Wave, for capacitor switching transient, as additional waveform.

The rationale for proposing standard and additional waveforms is rooted in the acceptance of the 1980 waveforms as being representative and useful, while recognizing that other waveforms may be encountered in specific cases and should be recognized. However, the wish for complete representation of all surges that may occur has to be tempered by economics and engineering judgment; hence, the split between standard (recommended) and additional (suggested). Figure 2 shows all five waveforms, and Table 1 presents a summary of the voltage and impedance values. The new waveforms are proposed in response to emerging concerns on surge occurring in specific environments. Thus, a brief discussion of these three new waveforms is in order.

## Additional Waveforms Address Emerging Concerns

The EFT Burst has been developed by Technical Committee 65 of the International Electrotechnical Commission (IEC) to provide a screening test for susceptibility to the fast transients that can be induced in power as well as data lines by the multiple re-ignitions occurring during the opening of a circuit by a contactor. While this type of contactor is mostly found in industrial environments (the world of TC65), other systems can have the same exposure (at least until the day when all power switching will be done by bounce-free, restrike-free solid-state relays). The catch, however, is that this test waveform was proposed to evaluate immunity of equipment by a test procedure that involves coupling the burst into the equipment under test by a capacitance divider: the coupling capacitor and the internal capacitance of the equipment under test. It does not mean that the 1-4 kV surges involved in this test necessarily occur in the power systems; what it means is that equipment that passes the high severity test will most likely be immune to what the real world does to connected equipment. One should not lose sight of this fundamental aspect of test standards; it is impossible to duplicate all possible occurrences in one test, but if a test can be developed so that equipment that passes the test has better field performance than equipment that fails the test, then the test is a valuable tool for reliable design.

The 10/1000 s Wave has been proposed to provide a means to stress equipment with high-energy surges, such as those that can occur during major power-system fault clearing. The data base for that waveform is somewhat limited, so a range of peak levels and source impedance is proposed, to be selected according to the particulars of the situation. As one check for reality, the energy deposition capability of this waveform is such that small varistors (l4-mm diameter or less) in common use - by the millions - could only withstand a few applications of that surge. Thus, we know that such a high-energy surge does not occur very often.

The 5 kHz Ring Wave has been proposed to represent the situation encountered near large power-factor correction capacitor banks. Switching transients in the range of 500 to 1000 Hz can occur, with high-energy capability. In this case, the data base is rich in computer simulations and anecdotal recordings but it is difficult to make an accurate prediction for the general case because the actual transients depend entirely on the local situation. It will be up to manufacturers and users to agree on a compromise between conservative overdesign wishes and economic viability of the design.

## Waveform Selection Supports International Harmonization Efforts

The waveforms presented in the new Recommended Practice document should also be a positive step toward harmonization with international standards. The Combination Wave is consistent with the conventional ‘impulse' typical of IEC surge testing; the EFT Burst represents the adoption of an existing IEC Standard. Conversely, the 100 kHz Ring Wave, long resisted by some of the IEC Committees, is beginning to gain a foothold in the IEC community. The 10/1000 s Wave could be an alternative to the 100/1300 s surge ‘under consideration' in some of the IEC TC 77 surge immunity drafts. (This 100/1300 s surge is a varistor killer and, therefore, should not be considered beyond its original scope of app1ication which is heavy industrial environments where faults are cleared by fuses (5). The 5 kHz Ring Wave has yet to gain international recognition.

To assist designers in making computer simulations, the Recommended Practice document provides equations for the waveforms, and tolerances are also specified. This detailed information might be better located in the Guide on Surge Testing but it was included in the Recommended Practice document until such time as a revised guide on surge testing will include it (that revision has just been initiated, and it will probably take another year before the revision is in print). [2004 note:  It took 5 years!]

Last but not least, the new Recommended Practice document has three appendices that offer tutorial discussions of the concepts used in the document, provide information on the data base, and list almost 100 bibliographic citations, with brief notes on the contents of the papers. Thus, readers of the Recommended Practice will have on hand a short course on how to be prepared to deal with surges in low voltage AC circuits.

Francois D. Martzloff is a member of C62.41 working group, and has been involved in surge protection issues for more than two decades. He has been at the National Institute of Standards and Technology since 1985.

The author acknowledges the five-year effort in consensus building by the members of the working group and other interested parties that made possible the revision of IEEE 587 into a Recommended Practice.

### REFERENCES

- Bodle, D.W. et al. Characterization of the Electrical Environment, University of Toronto Press, 1976.

- C62: Complete Edition: A bound-book collection of all the guides and standards on surge protection, published periodically by IEEE.

- Martzloff, F.D. & Leedy, T.P. Electrical Fast Transients: Applications and Limitations," IEEE Transactions IA-26, Jan/Feb 1990, pp 151-159

- Feninmore, C. and Martz1off, F.D. "Validating Surge Tests by Field Experience: High-Energy Tests and Varistor Performance." Conference Record, IEEE/IAS Annual Meeting, Seattle, 1990.

- Meissen, W. Uberspannungen in Niederspannungsnetzen, Elektrotechnische Zeitschrift, vol. 104, 1983.

STANDARDS: TRANSNATIONAL ASPECTS

F. Martzloff, NIST, USA and A. Mendes, EDF/DER, France

ABSTRACT - Mass-production  of  electrical  and electronic equipment for the world market requires a system of standards of world-wide applicability. The development of such standards is a complex task, involving various national, regional, transnational, or international organizations.  This paper presents a review of the standards-writing process, in particular in the area of Power Quality.

# The general need for standards

Mass production of electrical and electronic equipment for the world market requires standard of world-wide applicability.   Such standards are reference documents that  provide solutions to technical or commercial problems in relations between contracting parties concerning products, goods or services.  Thus, a standard is a foundation to any contract.  Compliance with a standard is not necessarily mandatory, but it is generally considered as 'règles de l'art'.  To make this implementation mandatory, a law, regulation, ordinance, etc. is needed.  Examples are French government decrees, European Directives, and ordinances in U.S. cities.  A new aspect of the European Directives is the position that electricity is a product, therefore subject to product standards.

This position gives an added importance to the development of rational, realistic, and cost-effective standards on Power Quality.  These three criteria for useful standards must be kept in mind at all stages of the process of standards development.  An unfortunate effect of selecting the term 'Power Quality' is its misinterpretation as a one-sided issue for which the utilities would be solely responsible.

# National, regional, transnational, and international standards

There are some clear and some less clear characteristics that can be identified to differentiate all the types of standards encountered in international transactions.  There is no universal 'standard' that regulates the development of these many standards.  A simplified classification might be as follows:

National standards include several types:

Voluntary consensus standards where a balance is established in the committee among the producers, users, and independent parties. Type: ANSI standards, Normes Françaises ...

Industry standards, developed within one industry, where a balance is established among competitors.

Type: NEMA Standards, PEG Standards, Specifications EDF, ERA Recommendations ...

Regulatory standards:

Developed and promulgated by government agencies within their jurisdiction. Type: MIL Standards ...

Developed by independent organizations, adopted by national or local governments Type: UL, NFPA, OIML Standards ...

Internal standards, perhaps more correctly called specifications, within one company, that can sometimes become de facto national standards.

Regional Standards are developed by a process similar to that of national standards but shared among regional groups of nations.  The need to comply within that region can force multinational manufacturers to adopt these regional standards, thereby making them de facto international standards.

Type: CENELEC ...

Transnational standards fall in two categories:

Standards developed by transnational organizations and adopted explicitly or by osmosis into local or national standards.  Compliance with these standards might not be required, but their existence is recognized and influences the process of developing other standards.

Type: IEEE Standards, Normes UNIPEDE ...

Internal standards developed by multinational firms, becoming de facto standards within the market of that firm.

International standards are characterized by the fact that they are developed by consensus among delegates from member countries, then approved by national committees.  These national committees in turn may be appointed by a voluntary process or by government action, depending on the country.  The resulting standards may be formulated as recommendations, but become de facto regulatory standards as purchasers require compliance through their contractual agreements, or as governments mandate compliance.

Type: IEC Standards, CCITT Standards ..

# Electromagnetic compatibility standards in the electrical industry

The performance of electrical equipment can often be described in fairly simple terms.  Therefore, the subject of ratings, dimensions, tolerances is readily addressed by product standards developed by the manufacturers or by the purchasers, working jointly or separately.  However, performance of equipment can be impacted by electromagnetic disturbances and, conversely, the operation of equipment can emit disturbances that impact other equipment.  Avoiding electromagnetic interference (EMI) became an important field of engineering, but all too often it has become a process of correcting problems, rather than anticipating and preventing them.  The successful approach, both from the point of view of sound engineering and from connotations of semantics, was to develop the concept of Electromagnetic Compatibility (EMC).

The International Electrotechnical Commission (IEC) has developed a hierarchy of standards to be observed by the various committees involved in the area of EMC standards:

Basic EMC Standards, providing general and fundamental concepts such as terminology, description of phenomena, test methods. etc.

Generic EMC Standards, providing specification for a limited number of requirements and tests applicable to all products operating in a particular environment.

Product EMC Standards, providing specific requirements and test procedures dedicated to particular products.

Product Family Standards, applicable to a group of similar products.

EMC standards are fundamental to the satisfactory operation of electrical equipment.  The issue of Power Quality may be considered as a subset of the broader domain of EMC, so that it is useful to approach the subject of Power Quality Standards along the same, well-developed path of electromagnetic compatibility.  That approach can be summarized in one directive that can be applied to many other aspects of human activities:

...  thou shalt operate satisfactorily in thine environment, but thou shalt not degrade it.

An interesting aspect in the European context is the interpretation that electrical energy is a product, therefore properly the object of standards, hence the increased interest in power quality issues.

### Power Quality Standards

In general, power quality issues have arisen from several aspects: increasing dependency on sophisticated electronic systems that may be affected by the quality of their power supply, competition among energy suppliers, and last but not least, the explosive development and deployment of disturbance recorders with graphics capability that print out records of disturbances for everyone to see.

From a handful of surveys of transient disturbances in the sixties and seventies, we now witness a multitude of large scale monitoring programs.  An unresolved issue at this point, is the translation (transformation) of objective measurements of electrical disturbances into a subjective statement of I good power quality' or 'poor power quality' - the statement that typical decision-makers desire, but that engineers have difficulty in defining.

Defining standards for the quality of the electrical energy produced and distributed by the utilities without considering the needs of the load equipment would be the first mistake in standards development.  The term Power Quality has now gained too wide an acceptance to be changed, but it fails to convey the concept of reciprocity between the parties.  A debate at a recent meeting of the IEEE Standards Coordinating Committee on Power Quality pointed out that a more accurate description of the Committee's scope would be Power Compatibility but the committee resolved, with regrets, to go along with the entrenched usage.

A second mistake would be an attempt to enforce one-sided standards based on narrow interests.  International as well as national standards bodies generally recognize this possible problem and make earnest attempts at providing a balance of interests among the writers, reviewers, and sponsors of product standards.  The consequence of this concern, however, is an agonizingly slow process in reaching sufficient consensus to ensure acceptance of the standards.     Even the top-down approach taken by the European Community has met that difficulty in the process, to wit the delay in application of the EMC Directive.

Satisfactory operation of electrical equipment requires an acceptable quality of the delivered electrical energy, but agreeing on criteria of what is acceptable is at the heart of the debate.   The other important requirement is that, in turn,  the equipment connected to the power system must  not degrade the quality of that power system.

A power system is a dynamic entity, at every instant, phenomena occur and produce disturbances that propagate throughout the system, impacting the connected equipment as well as the elements of the power delivery system.  There is a wide range of phenomena, characteristics, coupling and propagation modes, and consequences.  The IEC Technical Committee 77 on Electromagnetic Compatibility is in the process of describing and classifying the electromagnetic environment [1], [2].  These documents provide guidance on the nature of the disturbances and classify them in a limited number of types, making possible a rational approach to emission control, withstand capability, and mitigation when necessary [3].

As a universal phenomenon, electromagnetic disturbances can be defined, described, and classified on a world-wide scale.  However, when specific disturbances occurring on specific power systems are concerned, then the discussion must be carried among those sharing the same type of power system.  For instance, Europe uses 220 V, 50 Hz for residential and commercial end-users; North American systems use 120/240 V or 120/208 at 60 Hz; Japan uses 100 V at 60 Hz in some regions.  Thus, it should not be surprising nor discouraging to have different standards evolve for these different systems.  Nevertheless, the basic principles should be held in common and, therefore, a symposium such as this PQA 91 Confer-once offers an opportunity to work toward commonalty where possible, all under an EMC compatibility umbrella.

It is sometimes necessary to consider only national standards: the nature of the electrical stresses are dependent upon the nature of the networks, which are different among the countries and utilities.  For instance, in France or in the United States where the population density is relatively low, the major part of the distribution system is built as overhead lines: there will be many occurrences of voltage dips.  On the other hand, in a high-density country such as Holland where the distribution system uses underground cables, there will be few voltage dips. Another example of national differences is the different grounding practices for the neutral, requiring corresponding dedicated standards.  An intermediate approach between national standards and international standards is that of regional or transnational standards.  For instance, the countries of the European Community have sufficiently similar   practices,   with   a   common   market   for electrical equipment to motivate this approach.

### Regional (transnational) standards

As early as 1960, Europeans created CENELCOM (Comité Européen de Normalisation Electrotechnique) with the task of developing European standards.  This committee has now been replaced by CENELEC (Comité Européen de Normalisation Electrotechnique), the official standards organization of the European Community.  Leading the development of these standards, several organizations contribute to the necessary database: CIGRE (Conférence Internationale des Grands Réseaux Electriques), CIRED (Congrès International des Réseaux de Distribution), IEEE (Institute of Electrical and Electronics Engineers), UNIPEDE (Union Internationale des Producteurs et Distributeurs d’Énergie Électrique).

For instance, UNIPEDE has recently proposed a description of the voltage waveform [4].  This document describes the parameters characterizing the voltage waveform and the disturbances that may appear at the point of common coupling.  Now, CENELEC is tasked with turning the UNIPEDE document into a European Standard, which may then be used by European utilities in the contracts with their customers.  This standard will also provide equipment manufacturers with the necessary information for designing products with appropriate immunity levels.

# Nature of the equipment

The nature of the equipment involved has an influence on the concerns.  For instance, if waveform distortion results from its operation, questions arise on possible effects on revenue meters or on control systems.

Electrical and electronic equipment may be classified in two broad categories:

Small equipment, mass-produced, installed and used by anyone: appliances, electronic systems, with a load current of less than 16 A (Europe) or 12 A (USA, on 15 A branch circuits).

Large equipment, produced in smaller number, custom-installed and used by professionals, with load currents above 16 A.

For each of these two, the type of appropriate standard will be different:

In the first case, world-wide and comprehensive standards are necessary, specifying emission limits and immunity levels.  The IEC publications series 555 are an example of such standards.

In the second case, Recommendations or Installation Guides may be sufficient.  These documents may have an international basis, complemented as needed by local requirements.

# Conclusions

Free circulation of electrical and electronic equipment requires the observance of some rules.  The most important, of course, involve safety, which must not be placed in jeopardy by an insufficient level of immunity to the disturbances occurring in the environment.

Regulatory agencies have added a requirement concerning the electromagnetic environment, whereby the equipment shall not be the source of objectionable emissions, while being capable of operating amid a reasonable level of disturbances.  The proliferation of new technologies using higher frequencies, in particular in the 10-150 kHz band, requires the development and implementation of rules concerning the frequency spectrum and levels of emissions

In general; all these rules are promulgated through standards, acting as reference documents generated by broad consensus or agreement among the parties.

Specifications, regulations or directives can then refer to the relevant standards.  For instance, the European Directive will be more readily accepted as its effective application is made easier and in a timely manner.  Unfortunately, the process of standards development remains slow, and several more years will be required to reach a set of generally-accepted emission limits, while there are practically no standards concerning the immunity levels.  By making this forum available to many individuals involved in Power Quality issues, the process may be clarified and even accelerated.

### REFERENCES

[1] IEC 77(Secretariat)103 - Description of the electromagnetic environment.

[21 IEC 77(Secretariat)108 - Classification of the electromagnetic environment.

[3] IEEE C62.41-1991 - Recommended Practice on Surge Voltages in Low-Voltage AC Power Circuits.

[4] DISNORM 12 - Definitions of the Physical Characteristics of Electrical Energy Supplied by Low and Medium Voltage Public Systems.

POWER QUALITY WORK AT THE

INTERNATIONAL ELECTROTECHNICAL COMMISSION

François Martzloff

National Institute of Standards and Technology

## Abstract

The paper presents an update, including a brief historical background, on the work to be undertaken at the International Electrotechnical Commission (IEC) to address power quality issues.  To be useful, this work must take into consideration the three principal stakeholders, namely the producers of electric power, the manufacturers of equipment that use electric power, and the users of that equipment.  Other stakeholders include manufacturers of power quality monitors, manufacturers of line conditioners, and power quality consultants.  At this time there are some differences of perceptions on how the work can be accomplished to best serve the interests of all stakeholders.  Nevertheless, there is no disagreement on the first goal to be reached, which is to catalyze development of compatible, comparable, and consistent results in the measurement of power quality parameters.

###### Introduction

In a landmark 1996 decision, the Committee of Action of the IEC approved a recommendation to undertake work on power quality issues as part of the scope of Technical Committee TC77 on Electromagnetic Compatibility (EMC).  This decision, recommended by an Ad Hoc Group composed of power quality experts from ten countries, marks an expansion of the scope that will then reach beyond the purely technical issues generally addressed by the EMC community.  Power quality and EMC share many concerns, to the point that each has at some time been described as being a subset of the other.  In addition to this fundamental aspect, other issues permeate any discussion of power quality.  It would be more accurate to draw a multi-dimension diagram with many overlaps (see Figure 1).  The Ad Hoc Group considered three areas of contributions which an IEC Power Quality Group could make, complementing the work currently done by existing working groups or project teams of TC77:

-	Bringing order to the present chaos of uncoordinated methods of monitoring power quality

-	Proposing a classification of power quality levels describing what end-users can expect

-	Building bridges among producers and users of electric power, and equipment manufacturers

Concerns have surfaced that undertaking such work might ultimately result in the development and imposition of standards on the quality of "electricity as a product" and create an adversarial relationship, where for the moment the emphasis is on cooperation.  There is a need to reduce these concerns by defining more clearly the objectives and work program of this new IEC activity.

## Power Quality in Other Organizations

The term "Power Quality" first appeared in the U.S. literature in the late seventies        used at first by the computer-user community in a somewhat negative context, as it seemed to be associated with anecdotes or complaints of malfunctions attributed - correctly or incorrectly - to "poor power quality." At the beginning, there was a tendency to took for a culprit, the users blaming the electric power being supplied to them, and the electric power supplier blaming insufficient immunity of the equipment to unavoidable disturbances.

Even when a solution was indeed in sight, there remained among some stakeholders some reluctance to assume the cost of correction, and attempt to pass it on to the other stakeholder(s).  The "boundary" of the stakeholders was often defined as the revenue meter, as if electrons would change their behavior when going through the current coil of the meter.

Technically sound and economically viable solutions will depend on the cooperation of three principal stakeholders:

- 	Producers of electric power;

-	Manufacturers of equipment that uses electric power;

-	Users of equipment that uses electric power.

Perhaps not immediately obvious, but three other important stakeholders in correcting power quality problems are:

-	Manufacturers of power quality monitoring instruments;

-	Manufacturers of line conditioning equipment;

-	Consultants called upon to solve power quality problems.

Considerable progress has been made since the early days in bringing the parties together to seek mutually satisfactory solutions rather than hunt for culprits.  The PQA conferences held in the last several years are a good indication of this change of mood and mode.  We now hear the word "interface" more often than the word "boundary" suggesting that disputes are being replaced by constructive dialog.  The term and concept of "System Compatibility" have also become more visible 4, 5, 6, 7, with the goals of the utilities defined as making their customers satisfied and helping customers to be more competitive, rather than merely supplying them with electric power.

Many electric utilities have instituted power quality programs in their customer services, some as a defensive or reactive step, others as a proactive and marketing strategy.  Engineering societies have also focused on practical, application-oriented power quality issues, while initially the standards activities were slow in reacting to the growing interest in those issues.  Since then, several organizations have established power quality programs for developing standards or contributing to the development of standards, including the Canadian Electricity Association (CEA)', the European Committee for Electrotechnical Standardization (CENELEC)', the Electric Power Research Institute (EPRI)", the Institute of Electrical and Electronics Engineers (IEEE)", and the International Union of Producers and Distributors of Electrical Energy (UNIPEDE)     12  . All of these organizations have allocated substantial resources to address power quality issues.

One of these issues in particular is the incompatibility found when attempting to analyze and compare the results of power quality surveys based on different definitions or measurement methods ", ", ". This incompatibility is rooted on different definitions of disturbances, and hence different algorithms in the software of power quality monitoring instruments.  Eliminating these incompatibilities is one of the prime motivations for the proposed IEC work that will first focus on measurement methods.

###### Power Quality vs.  Voltage Quality

At the risk of oversimplification, one can identify two different approaches to addressing power quality issues on the two sides of the Atlantic Ocean.  In Europe, attention seems to have focused on the "voltage quality" while in North America, the concerns fell under a broader umbrella of "power quality." While the difference may seem to be a mere linguistic subtlety between the U.K. English which is the official English of the IEC and the U.S. English which is the unofficial English of the IEEE, the words also reflect a difference in perspective.  In French, the second official language of the IEC, one finds the label of "qualit6 de la tension" (tension = voltage), reflecting the emphasis on voltage.  Perhaps as a result of this difference of perceptions, the few existing bilingual IEC documents on the subject have not yet provided a satisfactory equivalent in the two languages

An anecdote can best illustrate this subtle perspective difference: in what the U.S. community would recognize as a power quality pamphlet influenced by the European Community, the untranslatable caption of a cartoon from Electricit6 de France, "Bien vivre avec sa tension" (Figure 2) proposes the double-entendre of learning to live with "tension" - understood as the blood pressure of the end-user, or "tension" - understood as the system voltage.  Hopefully, there will not be a triple-entendre where the word "tension" would refer to a sag, or to strained relations among the three principal stakeholders, resulting from concerns over the forthcoming IEC work on power quality issues.  The caption of Figure 2 is an attempt at providing in the power quality context a culturally-equivalent rendition of the French for an English-speaking audience.

Somewhat in contrast with the emphasis on voltage - but certainly not in conflict - the U.S. perspective has included more than just supply voltage in the power quality issues.  An often-cited statement in power quality articles is "... 83% of the alleged power quality problems are actually end-user wiring problems" and one article even shows a screwdriver as "the primary tool for solving power quality problems." This broad perspective is also illustrated by an IEEE standard, part of the IEEE Color Books series, on powering and grounding for sensitive loads " which is clearly related to power quality issues.

###### Satisfactory Operation vs.  Voltage Quality

During the proceedings of the IEC Ad-Hoc Group meeting held in April 1996, interesting discussions took place among the participants on their respective proposals for a definition of power quality - a necessary prerequisite to undertaking work on the subject.  A compromise consensus emerged so that the group would be able to present a recommendation for action where the terms would be defined.  One of the proposals had emphasized the voltage parameters, while another proposal had related power quality to satisfactory operation of the user's equipment.  The resulting definition, cited below, still reflects these two points of view:

Power Quality - Set of parameters defining the properties of the power supply as delivered to the user in normal operating conditions in terms of continuity of supply and characteristics of voltage (symmetry, frequency, magnitude, waveform).

Note 1: Power Quality expresses the users' satisfaction with the supply of electricity.  Power Quality is good if electricity supply is within statutory and any contractual limits, and there are no complaints from users, and vice-versa it is bad if the power supply is outside of limits and there are complaints from users.

Note 2: Power Quality depends not only on the supply but can be strongly affected by the users' selection of equipment and installation practices.

It will be one of the tasks (challenges?) of the group working on the forthcoming documents to allocate appropriate attention to the two points of view rather than to consider them as mutually exclusive.

## Forthcoming IEC Work on Power Quality

The approach now being considered by the IEC is to initially limit power quality work to measurement methods, and perhaps even to a narrower limit of characterization of voltage parameters.  Starting with measurement methods certainly is a necessity to get the work under way and ensure that all parties speak the same language when discussing power quality parameters.  However, stopping there, useful as it may be to catalyze compatible dialog between producer and consumer of electric energy (power) will not be sufficient to fulfill the expectations of equipment users.  From all the fuss about power quality being addressed at the IEC, they expect that more satisfactory operation of their equipment will be facilitated by the commitment of resources now envisaged by contributors to the IEC process, and that objective and reliable guidance will be found in the new documents.

As mentioned in the Introduction, an Ad-Hoc Group of representatives from several national or international organizations and committees developed a recommendation to begin work on power quality, starting first on measurement methods.  This priority is a recognition of the present uncoordinated efforts among dedicated, but isolated, organizations which have produced incompatible or contradictory results among power quality surveys conducted by different organizations.  The decision by the IEC Committee of Action to accept the recommendation developed by the Ad-Hoc Group has now cleared the way for New Work Item Proposals (NWIP), the method used by the IEC to launch the development of new documents, to be submitted to the IEC National Committees for approval.

As of the writing of this paper two NWIP proposals have been circulated.  One, originating from the French National Committee, has the title "Measurement Guide for Voltage Characteristics" while the other, submitted by the U.S. National Committee, has the title "Power Quality Measurements" again reflecting the difference in perspective.  The French proposal somewhat mirrors the UNIPEDE 12 approach while the U.S. proposal includes all the topics listed by the Ad-Hoc Group as well as a reference to the IEEE Standard 1159 ". The French proposal concentrates on low-frequency disturbance characterization, including power frequency, voltage magnitude, voltage fluctuations, voltage dips, harmonic voltages, and signalling voltages, but downplays transient overvoltages (surges).  It also makes several references to "Compliance with EN 50160"11 which might be seen as leading to mandatory clauses.  The U.S. proposal includes a comprehensive list of disturbances, suggests tutorial clauses on definitions and origins of disturbances, and even the possibility of providing some tutorial material on remedial or preventive actions.  Both proposals follow the Committee of Action decision that Technical Committee TC77 should be the principal responsible committee for this work, in coordination with Technical Committee TC8 (Standard voltages, current ratings and frequencies).

The officers of TC77 are on record as recommending that the two proposed projects be merged into a single project since it is clear that both proposals share the same goal of developing compatible, comparable, and consistent results in the measurement of power quality parameters.  The responses from the National Committees will not be compiled before late June 1997, but some responses will be known by the time of presentation of this paper.  Hopefully, the responses will be positive and the paper presentation will include an update on the project planning.

###### Conclusions

·	The first step has been taken at the IEC to start working on the development of documents addressing power quality issues.

·	The challenge will now be to proceed diligently to satisfy the needs of end-users and not have the work stalled by the difficulties of reaching consensus among many stakeholders.

·	The decision to start with measurement methods will enable development of a common language and build a working relationship among the participants which should promote continuing progress toward technically sound and cost effective solutions for the problems perceived - correctly or incorrectly - as power quality problems encountered by end-users in the equipment operation.

## Acknowledgments

Support for developing this paper, as well as support for participating in the related IEC work, was provided by the author's agency, by EPRI, by Delmarva Power, and by Pacific Gas & Electric.  Gerald FitzPatrick and Thomas Key provided helpful comments on the draft.

## References

I .  	Key, T. S., "Diagnosing Power-Quality Related Computer Problems," IEEE Transactions IA-15 No.4, July 1979.

2.	Goldstein, M. and Speranza, P.D., "The Quality of U.S. Commercial AC Power," Intelec Conference Proceedings, 1982, pp 28-33.

3.	Clemmensen, J.M. and Ferraro, R.J., "The Emerging Problem of Electric Power Quality," Public Utilities Fortnightly, November 28, 1985, Arlington VA.

4.	Gruzs, T., Key, T.S., Sitzlar, H.E., and Lai, J.S., "Compatibility at the Utility Interface: The UC Concept Applied to Surge-Protection Systems," Proceeding, PQA'91.

5.	Martzloff, F.D., "Performance Criteria for System Compatibility," Proceeding, IEEE APEC Conference, 1992, pp 287-292.

6.	Key, T.S., Sitzlar, H.E., and Moncrief, W., "Electrical System Compatibility Applied to End-use Equipment Characterization Projects," Proceedings, PQA'92.

7.	Key, T.S., Dorr, D.S., Hughes, M.B., and Stanislawski, J., "Matching Electronic Appliances to their Electrical Environments," Proceedings, PQA'95.

8.	CEA 220 D 711 - Power Quality Measurement Protocol - Guide to Performing Power Quality Surveys, Canadian Electricity Association, May 1996.

9.	EN 50160 "Voltage Characteristics of Electricity Supplied by Public Distribution Systems," November 1994.

10.	EPRI, Signature - A quarterly newsletter on power quality issues.

11.	IEEE Std 1100- 1992 "Recommended Practice for Powering and Grounding Electronic Equipment".

12.	UNIPEDE "Measurement Guide for Voltage Characteristics," May 1996.

13.	Martzloff, F.D. and Gruzs, T.M., "Power Quality Site Surveys: Facts, Fiction, and Fallacies," IEEE Transactions IAS Vol 24 No.6, November/December 1988, pp 1005-1018.

14.	Dorr, D.S., "Point of Utilization Power Quality Study Results," IEEE Transactions IA-3 1, No.4, July/August 1995.

15.	Martzloff, F.D., "Surge Recordings that Make Sense: Shifting focus from voltage to current measurements," Proceedings, ROMA'96 EMC Symposium, September 1996.

16.	IEEE Std 11 59-1995 "Recommended Practice for Monitoring Electric Power Quality”

## THE TRILOGY UPDATE OF IEEE Std C62.41

#### François Martzloff

National Institute of Standards and Technology

Abstract:  Progress report on the restructuring of two IEEE standards concerned with surges in low-voltage ac power circuits into a Trilogy of three documents. First a basic Guide describes the surge environment, then a Recommended Practice proposes a limited set of representative surge waveforms for test purposes, and finally a Recommended Practice shows how to perform safe, repeatable and reliable surge tests on equipment connected to these ac power circuits.

1.	INTRODUCTION

Since 1980 when the seminal IEEE Std 587 Guide on Surge Voltages in Low-Voltage AC Power Circuits was first approved, the document has gone through several revisions, while a companion, IEEE Std C62.45 Guide on Surge Testing for Equipment Connected to Low-Voltage AC Power Circuits was developed to provide guidance on test procedures. Experience in applying the documents, and the availability of new information on the subject led to a decision of performing a major update of the two documents, mostly the C62.41. The purpose of this paper is to present a progress report on the project and invite the International Conference on Lightning Protection (ICLP) community in sharing common interests about the occurrence of surges in low-voltage ac power circuits.

2.	HISTORY

In 1991, the 1980 version of the IEEE 587 Guide (which had been renamed IEEE/ANSI C62.4 1 soon after its original issue) was upgraded to a Recommended Practice, with the addition of new recordings to the data base, and the definition of “Additional Test Waves” to the seminal 100 kHz Ring Wave and Combination Wave (1.2/50 s – 8/20 s).

Since 1991, the Recommended Practice remained unchanged, but new information for the data base, and the perception of a need to describe the scenario of a direct flash to the building — not included in the scope of the 1980-1991 versions — have created a situation where a mere update of the document would be insufficient.

Consequently, the IEEE Surge Protective Devices Committee and the Standards Board of the IEEE have approved a new project, now known as “The Trilogy” whereby the two documents, C62.41 [1] and C62.45 [2], will be replaced by three separate, but related (and published simultaneously) IEEE standards. The present C62.41-1991 will be split in two, C62.41.1 and C62.41.2, while C62.45 will remain separate but better connected to the two C62.41 documents.

3.	THE TRILOGY

The identification of the three documents will be:

• C62.41.1-2000 – IEEE Guide on the Surge Environment in Low-Voltage AC Power Circuits

• C62.4 1.2-2000 – IEEE Recommended Practice on Characterization of Surges in Low-Voltage AC Power Circuits

• C62.45-2000 – IEEE Recommended Practice on Surge Testing for Equipment Connected to Low-Voltage AC

Power Circuits

To place these three documents of the Trilogy in perspective, note that the IEEE generically refers to three types of documents as “standards”:

Guides, in which information is presented with no attempt to steer the reader in a unique direction;

Recommended Practices, in which several possible choices are presented, and one is recommended as the first choice;

Standards, in which a single approach is specified, with no deviation allowed.

The last document of the Trilogy, C62.45 will not have major changes. It will be an update to make it consistent with the recommendations of C62.4 1.2, with the addition of some practical tips on how to perform more reliable surge measurements. In contrast, the first document of the 1990s vintage, C62.41, is undergoing major restructuring. The purpose and the contents of these three standards are summarized in the three following Sections 4, 5, and 6.

4.	GUIDE ON THE SURGE ENVIRONMENT

4.1   Data base

The initial approach to a description of the surge environment was limited to compiling the results of surge measurements made in the field, either by systematic monitoring, or on the occasion of staged tests, generally in connection with equipment failure investigations. As the development progressed, it was recognized that additional information on the surge environment can be gained by incorporating other data. In its new structure as a Guide four elements will be included into the data base:

1.	Recordings of surge events in the field;

2.	Numerical simulations and laboratory research;

3.	Inferences on the surge environment drawn from analysis of equipment field failures;

4.	Discussion of the data base.

The 1980 and 1991 versions of C62.41 proposed the concept of “Location Categories” as follows, in an effort to guide designers and users of equipment toward a realistic perception of the surge threat depending on the general location within a building, but not precise distances.

4.2 Location Categories

The concept of Location Categories was based on the fact that the inherent inductance of the building wiring would reduce the current stress imposed by an impinging surge as distance from the service entrance increases, while the voltage stress would not be affected.  The concept was illustrated in graphic form, showing buildings where increasing distance from the service entrance were marked by fine-line demarcations between the categories.  Of course, electrons flowing in the wiring were blissfully unaware of these demarcations, a fact that was troublesome to some readers of the document.  A possible misinterpretation of these fine-line demarcations might have implications on the rating specifications of surge-protective devices (SPDs) to be installed at a specific location.

To avoid this too-narrow interpretation the updated Guide will emphasize that “boundaries” separating the categories should rather be seen as “transitions” connecting the categories that overlap. The graphic illustration of the three Location Categories A, B, and C will show, rather than the fine lines of 1991, the amended concept and representation with transition overlaps, as seen in Figure 1.

Figure 1. The concept of Location Categories connected by transition overlaps

4.3	The tale of two scenarios

However, the concept of Location Categories was and remains implicitly applicable only for surges impinging upon the building from the outside or generated within. These were considered to be the vast majority of surge events, and the more rare event of a direct flash to the building was considered a special case, which was not addressed in the document. The updated version will now include that situation, as described in Section 5.

Given the increasing interest, and some of the undocumented perceptions on what is involved in the scenario of a direct flash to a building, the Trilogy is attempting to provide information presented in a manner that will be useful and realistic.  To emphasize the major difference between common surge events and a less frequent direct flash, the surge environment description of C62.41.1 is presented in two separate scenarios:

• Scenario I: All surges impinging from the outside or generated within the building, except for Scenario II

• Scenario II: Surges resulting exclusively from the dispersion of the lightning current in the earthing electrodes

The concept of presenting the two scenarios has been well accepted among the members of the IEEE Surge-Protective Devices Committee.  One of the pitfalls in applying this scenario might be an oversimplification made in a well-intentioned attempt to simplify the complexity of the dispersion of the lightning current among the available paths to multiple earthing electrodes.  Figure 2 shows an already very simplified building wiring with extraneous metal which still suggests multiple paths for the dispersion.

So far, few if any measurements have been reported in the literature to document the details of the dispersion of lightning current within a building [3]; [4]. However, several numerical simulation studies have been conducted [5]; [6]; [7], all involving a certain degree of simplification [8].  This evolving situation is closely monitored by the IEEE working group where the Trilogy is being developed, to provide the latest consensus at the time of balloting, but realizing that this consensus is an ever-evolving goal.

4.4	From database to representative waveforms

In turn, the environment description of the C62.4 1.1 Guide will serve as the basis for the definition of the waveforms given in the C62.41 .2 Recommended Practice, as described in the next section.  The waveforms that were proposed in the 1991 version will be maintained in the description of Scenario I, but the definition of appropriate parameters for Scenario II is still unresolved as of the writing of this paper.  Consensus might be reached among interested parties by the time of oral presentation of this paper at the ICLP Rhodes, where the most recent results of this process can be reported.

5.  RECOMMENDED PRACTICE ON CHARACTERIZATION OF SURGES

5.1	Purpose, proposals, and pitfalls

The explicit purpose of this Recommended Practice is to propose a limited set of test waveforms that can be used for subjecting equipment to representative surge stresses as encountered in the low-voltage ac power environment.

This set is a proposal, not a specification; it should be seen as a menu from which equipment manufacturers and users can select stress levels, as determined by the selected test waveform(s) and amplitude(s) best suited for their own application.

The common pitfall, however, has been in the past that the purpose was misinterpreted and the proposals were turned into equipment specifications that were expected to be appropriate for all applications.  Continuing efforts in the redaction of the successive versions of the document have been made, and appear to have reduced but still not yet completely eradicated such misinterpretations.

The menu aspect of this Recommended Practice will be emphasized by suggesting two types of test waveforms. First, a set of two “Standard Waveforms” recommended for general applications; then a set of “Additional Waveforms” recommended for special applications where they appear appropriate.

5.2	Standard Waveforms

The original 1980 version proposed two representative waveforms, and these have not changed since.  The first waveform, labeled  “0.5 s — 100 kHz Ring Wave” was constructed on the basis of the then novel recognition that the traditional test waveforms used in high-voltage laboratories might not be a good representation of the environment in low-voltage ac power circuits.  Even the limited field recordings available at that time were showing oscillatory, high-frequency waveforms rather than the textbook unidirectional impulses.

The second waveform, actually a combination of two stress types, was proposed for subjecting equipment to a voltage stress (1.2/50 s) when the equipment would present a high impedance, or a current stress (8/20 s) when the equipment would present a low impedance.  This choice was influenced by the wish of not denying the long experience gained with those wavefonns.  In contrast to the then prevalent test methods where the current and voltage impulses were two separate tests, this second waveform would be applied by a generator having the inherent capability of delivering a voltage or a current stress according to the impedance of the equipment under test.  This new type of generator and waveform became known as “Combination Wave.”

Figure 1 — The concept of Location Categories connected by transition overlaps

5.3  Additional Waveforms

During the process of updating the 1980 vintage of the C62.41 Guide into the 1991 version, several waveforms were considered by the working group.  The final proposal was to recommend considering a fast transient, adopted from the IEC 801-4 (now IEC 61000-4-4), called EFT for “Electrical Fast Transient,” a 10/1000 s Long Wave, and a 5 kHz Ring Wave. These waveforms were designated as “Additional Waveforms” to emphasize that a test program should not be overburdened by unnecessary tests when there was no compelling reason to include one or more of these additional waveforms in the test regimen.

In the updating process for the Trilogy, the EFT and the Long Wave have been kept as Additional Waveforms.  In the 1991 version, the 5 kHz waveform was intended to emulate capacitor switching surges.  In the laboratory, a conventional type of energy-storage surge generator could produce that waveform superimposed to the power-frequency voltage.  However, it has been abandoned as more data became available on the occurrence of capacitor switching surges, indicating that lower frequencies, below 1 kHz, were more typical.  Instead, the recommendation is offered that specific studies be performed for installations where large capacitor banks are being switched frequently.

6.  RECOMMENDED PRACTICE ON TESTING

One of the outcomes of the Recommended Practice on Surge Characterization is a set of tables indicating what types of surge test waveforms are recommended for specific combinations of conductors at the power port of equipment to be tested (phase, neutral, ground).  To illustrate the process, Table 1 presents a summary of these recommendations for surge testing the ac power ports of equipment (including surge protective devices, of course).

Now turning to the recommendations on actually performing the recommended tests, in the 1980s and the early 1990s, guidance on surge testing was offered in the format of an IEEE Guide.  In the Trilogy, with the experience accumulated in the use of the C62.45 Guide, augmented by some anecdotal examples of observed questionable surge testing procedures, the decision was made to elevate the C62.45 Guide to the more compelling visibility and status of a Recommended Practice.

This enhanced version also will address issues raised by the shift from analog to digital instruments and the resulting effects of aliasing, insufficient resolution, and transducer saturation.  Precautions for avoiding artifacts will also be included in the recommendations.

7.   SCHEDULE AND RELATIONS WITH OTHER STANDARDS

Efforts are being made to effect liaisons with the IEC Technical Committees TC37 and TC8 1, as well as with other parties involved in lightning studies.  The effort has been difficult because the liaisons were not optimized and the work was sometimes conducted by different groups without sharing relevant information.  It is one of the aims of this paper to lower these barriers by presenting the subject within the community of the ICLP participants.

The IEEE working group is hoping that the Trilogy will have matured through the summer of 2000, in particular the consensus on how to turn the agreed-upon Scenario II into one set of recommended test waveforms that represent the environment.   At the present time, IEC Publication 61643-1 [9] has been released, but it only specifies the types of tests, without reference to the location and environment in which the SPDs are to be installed.

Table 1

Summary of recommended types of surge tests

8.  SUMMARY

The update of the two original documents, IEEE Std C62.41 and IEEE Std C62.45, into a Trilogy will bring the following improvements to these two previous documents, notwithstanding the fact that they served well in the period of 1980 to 1999 (IEEE has filled over a thousand requests for C62.41 since its first publication):

The new structure will provide readers with a more direct route to fulfill their particular needs:

1.  A basic guide providing comprehensive data base and the rationale for the simplification leading to the recommended standard and additional test waveforms;

2.   A relatively terse description of the recommended test waveforms, uncluttered by the data base;

3.  A straightforward and well-connected Recommended Practice on surge testing methods.

The most significant changes in the Trilogy, compared to the earlier versions of C62.41-1991 and C62.45-1992, are the following:

- Separation of the database that was appended to C62.4 1 in the earlier versions, when enhancing acceptance and credibility of the proposals were deemed important elements.  A Guide provides a comprehensive database, a Recommended Practice provides the standard and additional test waveforms.

- Introduction of a Scenario II for the special case of a direct lightning flash to the building.  Such a scenario implies higher stress levels for those surge-protective devices installed at the service entrance, compared with the stress levels suggested for usual applications.

- Introduction of the concept of transition overlaps that act as interfaces between Location Categories, rather than the boundaries that previously separated these categories.

- Removal of the earlier attempt to provide across-the-board waveforms for the case of capacitor switching, but instead make recommendation to perform case-by-case studies.

9.  ACKNOWLEDGMENTS

The development of the IEEE C62 Trilogy update has been made possible only with the technical contributions and moral support of my colleagues, too numerous to list them all, from several standards-writing groups, but who nevertheless deserve recognition for their voluntary work.

Another beneficial factor that needs recognition is the growing trend toward harmonization among standards-writing organizations, in spite of their initial divergent positions.

10.  REFERENCES

[1]  IEEE Std C62.41- 1991 - Recommended Practice on Surge Voltages in Low-Voltage AC Power Circuits.

[2]  IEEE Std C62.45-1992 - Guide on Surge Testing for Equipment Connected to Low-Voltage AC Power Circuits.

[3]  Morris, M.E., Fisher, R.J., Schnetzer, G.H., Merewether, K.O., and Jorgenson, R.E., “Rocket-Triggered Lightning Studies for the Protection of Critical Assets,” IEEE Transactions IA-30, May/June 1993.

[4]  EPRI “Investigation of lightning entry into a secondary service using rocket triggered lightning”, EPRI Report TR110418, April 1998.

[5]  Birkl, J., Hasse, P., and Zahlmann, P., “Investigation of the interaction of lightning currents with low-voltage

installations and their related threat parameters”, Proceedings, 23rd International Conference on Lightning Protection, Firenze, 1996.

[6]  Mansoor, A. and Martzloff, F.D. ,“Driving high surge currents into long cables: More begets less”, IEEE

Transactions PWRD-12, No.3, July 1997.

[7]  IEC 62066: 2002: General basic information regarding surge overvoltages and surge protection in low-voltage a. c. power circuits.

[8]  Mansoor, A. and Martzloff, F.D., “On the Dispersion of Lightning Current after a Direct Flash to a Building,”

Submitted for ICLP 2000, September 2000.

[9]	IEC 61643-1:1998 Surge protective devices connected to low-voltage power distribution systems - Part 1: Performance requirements and testing methods.

New IEEE Standards Foster Next-Generation System Compatibility

#### By François Martzloff

In November 2002, the Institute of Electrical and Electronics Engineers (IEEE) approved a set of three standards that provide critical parameters on the surge environment in low-voltage ac power circuits, and suggest improved test methods for end-use equipment connected to these circuits. When this standards trilogy is published in early 2003, manufacturers and users of surge protective devices (SPDs) will have a definitive set of documents to help them make more cost-effective and technically sound design decisions regarding the compatibility of their equipment with the surge environment.

The seminal IEEE Standard 587—Guide on Surge Voltages in Low-Voltage AC Power Circuits—has gone through several revisions, including a name change to C62.41, since it was first published in 1980. A companion, IEEE Standard C62.45—Guide on Surge Testing for Equipment Connected to Low-Voltage AC Power Circuits—was also developed to provide guidance on test procedures.

IEEE 587/C62.41 and C62.45 served us well from 1980 to 1999. However, with the availability of new knowledge on surge protection, and after nearly 20 years of experience in applying the two standards, a major update was needed. The newly developed standards provide a more direct route to fulfilling the surge protection needs of users, and are designed to promote greater harmony with the related standards of international organizations.

The new trilogy consists of

- IEEE Standard C62.41.1TM 2002 – Guide on the Surge Environment in Low-Voltage AC Power Circuits, which contains a comprehensive database describing the surge environment;

- IEEE Standard C62.41.2TM 2002 – Recommended Practice on Characterization of Surges in Low-Voltage AC Power Circuits, which proposes a limited set of representative surge waveforms for test purposes; and

- IEEE Standard C62.45 TM 2002 – Recommended Practice on Surge Testing for Equipment Connected to Low-Voltage AC Power Circuits, which shows how to perform reasonable, repeatable, and reliable surge testing.

### New Focus

In developing the standards, IEEE focused on five key areas: transitions, temporary overvoltages, multiple-port equipment problems, scenarios, and harmonization. Because these factors can have significant impacts on hardware selection and specification, they were debated thoroughly by members of the working group and other interested parties before a consensus was reached. Fortunately, the IEEE standard format includes “normative” clauses, to emphasize important points, and “informative” annexes, to provide perspective on less definitive issues.

### Transitions

Earlier versions of C62.41 offered the concept of “Location Categories” to help designers and users of equipment define surge threats by the general location of the equipment within a building. Location categories are based on the fact that the inherent inductance of the building wiring reduces current stress from an impinging surge as the distance from the service entrance increases, while voltage stress is not affected. According to this concept, SPDs can be expected to have less stress exposure as their point of use moves away from the service entrance.

While the earlier standards did not specify precise distances, they featured graphic representations with fine lines, or “boundaries,” separating location categories. Because some users focused too narrowly on these boundaries, the updated guide now uses the concept of “Transitions” that connect rather than separate location categories, as the graphic shows. These transitions leave some flexibility for equipment manufacturers and users in selecting specific surge-withstand values.

#### Temporary Overvoltages

Although temporary overvoltages—which last seconds rather than the microseconds of surges—might be seen as outside the scope of the surge environment, their impact on SPDs can be devastating. For this reason, IEEE added a description of their occurrence and mechanism to the C62.41.1 guide.

#### Multiple-Port Equipment

Most of today’s electronic equipment contains multiple ports, with connections to both the ac power supply and one or more additional systems that must have a ground reference, such as phone systems, television cable systems, and computer networks. Multiple-port equipment is now the most common victim of surges. A surge on any of the connected systems will cause a shift in ground reference potential to appear across the equipment ports. Guide C62.41.1 alerts the engineering community to this phenomenon—the most frequent source of insurance claims—and supports the standardization of SPDs. Furthermore, IEEE has just launched two projects for developing new standards addressing performance and test methods of multiple-port SPDs.

#### Scenarios

In an effort to organize and present information in a way that will be as useful and realistic as possible, the standards trilogy introduces the concept of “Scenarios,” which distinguish between two types of surges. Scenario I describes surges coming from any source that impinge upon an installation or are generated within the installation by load switching. Scenario II covers surges that are associated with a rare but possible direct lightning flash to a building, and with surge current that exits the building via the service connection.

The concept of location categories applies only to surges in Scenario I—those impinging upon a building from the outside or being generated from within. These are considered to be the vast majority of surge events. Guide C62.41.1 provides a surge environment description that serves as the basis for defining the waveforms in Recommended Practice C62.41.2.

The more rare event of a direct flash to a building in Scenario II was considered to be a special case and not included in earlier documents. Given the increasing interest in the ramifications of such an event, the new standards address this situation. Definitions of appropriate parameters for this scenario did raise some discussion in gaining consensus, and therefore are proposed in an informative annex to allow case-by-case applications.

#### Harmonization

In keeping with the transnational aim of IEEE standards, the new standards were developed to harmonize with related documents from the International Electrotechnical Commission (IEC). The IEEE working groups established liaisons with IEC Technical Committees SC37A (Low-Voltage SPDs) and TC81 (Lightning Protection), as well as with other parties involved in lightning studies. These efforts will help to ensure greater credibility and worldwide acceptance of both IEEE and IEC standards.

##### Expanded Scope

In earlier versions of the standard, surge environment descriptions were limited to compilations of surge measurements in the field. The data were gathered either by systematic monitoring or through staged tests during equipment failure investigations. As development of Guide C62.41.1 progressed, it became clear that more information on the surge environment could be gained by incorporating other data. The standard now includes additional data from recordings of surge events in the field, numerical simulations and laboratory research, and inferences on the surge environment drawn from analysis of equipment failures.

The proposed waveforms and associated stress levels in Recommended Practice C62.41.2 required no major change during the updating process. The waveforms should not be construed as specifications—a misconception noted in the use of earlier versions of C62.41—but rather as a menu from which equipment manufacturers and users can select stress levels, as determined by the test waveform(s) and amplitude(s) best suited to their own applications. The menu offers a set of two standard waveforms for general applications and a set of two additional waveforms for special applications.

The first standard waveform, the “Ring Wave,” was constructed in 1980 on the basis of the then-novel recognition that traditional test waveforms used in high-voltage laboratories might not provide accurate representations of the environment in low-voltage ac power circuits. The second standard waveform, the “Combination Wave,” defines two stress types. It is used for subjecting equipment to voltage stress, when the equipment presents a high impedance, or to current stress, when the equipment presents a low impedance.

The additional waveforms are the “Electrical Fast Transient Burst,” first developed within IEC for electromagnetic compatibility purposes and adopted by IEEE in 1991, and the “Long Wave,” which reflects field observations of surge occurrences. The 1991 version of C62.41 also included a 5-kHz ring wave to emulate capacitor-switching surges. This wave was removed from the menu, as data on the wide range of capacitor-switching surges made it clear that only case-by-case applications would be reasonable.

Equipped with these waveforms, Recommended Practice C62.45 provides information on instrumentation, considerations on tolerances in the output of surge generators, and descriptions of test procedures, including coupling of surges into test circuits. This enhanced version addresses issues raised by the shift from analog to digital instruments as well as the possible effects of aliasing, insufficient resolution, and transducer saturation. It also includes precautions for avoiding artifacts.

With the implementation of the new IEEE standards trilogy, designers and users of next-generation devices will be well equipped to tackle the surge environment of the future in low-voltage ac power circuits. Among the benefits they will realize are more cost-effective use of resources and greater harmony with the related standards of international organizations.

## François Martzloff

END OF FILE “Text Standards Reviews”

## April 2004