| # Last updated June 2004 | # Surge Protection Anthology Part 6 – Tutorials, Textbooks, and Reviews Text of “System Protection Techniques” files | # Surges Happen! |
| --- | --- | --- |

FOREWORD

This file contains the text part from eight papers on the following subjects:

- Surge protection techniques in low-voltage AC power systems (1979)

- The coordination of transient protection for solid-state power conversion equipment (1982)

- Lightning protection of roof-mounted solar cells (1983)

- The protection of industrial electronics and equipment against power and data line        disturbances (1984)

- The protection of computer and electronic systems against power supply and data lines disturbances (1985)

- Lightning and surge protection of photovoltaic installations (1989)

- Protecting computer systems against power transients (1990)

- Update on a consumer-oriented guide for surge protection (1999)

This file is formatted as MS Word, allowing you to do a search for keywords, but it does not support graphics as it was derived from an OCR scan of hard-copy archives.  However, should you wish to examine the complete original format, each page in this file has an identifying header and footer that contain a hyperlink to the pdf file for the document being displayed on that page, regardless of the font size that you select for optimum viewing.  These headers and footers and hyperlinks become accessible when you select the “Print Layout” in the “View” mode.

Best wishes and good browsing !

Surge Protection Techniques

in Low-Voltage AC Power Systems

F. D. Martzloff

Corporate Research and Development

General Electric Company

Abstract

Designers involved in the ac power side of telecommunications equipment have been justifiably concerned with surge protection because field experience is rich in case histories of failures attributable to transient overvoltages. Insufficient knowledge of the exact nature of these overvoltages, however, has made their task difficult in the past.

After several years of data collection by a number of organizations, a more definitive understanding of the surge environment is emerging. The next few years' publications from the IEEE, the IEC, NEMA, and other interested groups will document that understanding. This paper presents an overview of the results of data collection and environment descriptions from the point of view of telecommunications power supply problems, as well as a review of applicable techniques and devices.

From the early days of the introduction of semiconductors, voltage surges have been blamed for device failures and system malfunctions. Silicon semiconductors are, indeed, sensitive to overvoltages, more so than their predecessors, such as the obsolete copper oxide or selenium rectifiers. From an early period of frustration and poor knowledge of the actual environment, progress has been made both in the area of defining the environment and of providing new surge protective devices and techniques to deal effectively with the problem.

Recent progress in the technology of transient voltage suppressors has opened new opportunities to improve the level of protection of semiconductors exposed to power system transients. In the past, direct exposure to outdoor system surges required surge arresters with high energy capability to survive the discharge currents associated with direct or indirect lightning effects, at the cost of voltage-clamping levels that were too high to protect sensitive semiconductors. The approach at that time was a coordinated combination of arresters and low-voltage suppressors, an approach that is still valid in many cases. It is now possible, however, to apply a single suppressor, with sufficient capability to withstand outdoor surges while clamping at a level low enough to protect power semiconductors such .as power supply rectifiers. Examples of coordinated protection as well as the application of high power surge suppression devices, with experimental verification of performance, will be given in the paper.

# THE ORIGIN OF SURGE VOLTAGES

Two major causes of surge voltages have long been recognized: system switching transients and transients triggered or excited by lightning discharges (in contrast to direct lightning discharges to the power systems, which are generally destructive and for which economical protection may be difficult to obtain). System switching transients tan involve a substantial part of the power system, as in the case of power-factor-correction capacitor switching operations, disturbances that follow the restoration of power after an outage, or load shedding. However, these disturbances do not generally involve substantial over voltages (more than two or three per unit), but they may be very difficult to suppress because the energies are high. Local load switching, especially if it involves restrikes in the switchgear devices, will produce higher voltages than the power system switching, but generally at lower energy levels. Considering the higher impedances of the local systems, the threat to sensitive electronics is quite real:  the few conspicuous case histories of failures blemish the record of a large number of successful applications.

# Lightning-Induced Surges

The phenomenon of lightning has been the subject of intensive study by many workers. The behavior of lightning is now fairly predictable in general terms, but the exact knowledge of specific incidents is not predictable. Protection against lightning effects includes two categories: 1. direct effects concerned with the energy, heating, flash, and ignition of the lightning current, and 2. indirect effects concerned with induced overvoltages in nearby electrical and electronic systems.

One of the major factors to consider in determining the probability of lightning damage, and thus the need for strong protection, is the number of lightning flashes to earth in a given area for a given time. Such statistics are not generally available; instead the number of "thunderstorm days" is quoted. However, the term "thunderstorm days" includes cloud-to-cloud discharges and does not include the duration and intensity of each storm. Thus it does not represent an accurate parameter. Progress is being made to improve statistics, but new statistics are not yet available; therefore, the "isokeraunic level" map (1), showing the number of storm days per year, is still the most widely used description of the occurrence distribution (2).

# Switching Surges

A transient is created whenever a sudden change occurs in a power circuit, especially during power switching - either closing or opening a circuit. It is important to recognize the difference between the intended switching - that is, the mechanical action of the switch - and the actual happening in the circuit. During the closing sequence of a switch the contacts may bounce, producing openings of the circuit with reclosing by restrikes and reopening by clearing at the high-frequency current zero. Likewise, during an opening sequence of a switch, restrikes can cause electrical closing(s) of the circuit.

Simple switching transients (3) include circuit closing transients produced when the two circuits on either side of the switch being opened oscillate at different frequencies. In circuits having inductance and capacitance (all physical circuits have at least some in the form of stray capacitance and inductance) with little damping, these simple switching transients are inherently limited to twice the peak amplitude of the steady-state sinusoidal voltage. Another limit to remember in analyzing transients associated with current interruption (circuit opening) is that the circuit inductance tends to maintain the current constant. At most, then, a surge protective device provided to divert the current will be exposed to that initial current.

Several mechanisms generating abnormal switching transients are encountered in practical power circuits. These mechanisms can produce overvoltages far in excess of the theoretical twice-normal limit mentioned above. Two such mechanisms occur frequently: current chopping and restrikes, the latter being especially troublesome when capacitor switching is involved.

These switching overvoltages, high as they may be, are somewhat predictable and can be estimated with reasonable accuracy from the circuit parameters, once the mechanism involved has been identified. There is still some uncertainty as to where and when they occur because the worst offenders result from some abnormal behavior of a circuit element. Lightning-induced overvoltages are even less predictable because there is a wide range of coupling possibilities. Moreover, one user, assuming that his system will not be the target of a direct hit, may take a casual view of protection while another, fearing his system will experience a “worst case,” may demand the utmost protection.

In response to these concerns, various committees and working groups have attempted to describe ranges of transient occurrences or maximum values occurring in power circuits. These transients include both surge voltages and surge currents, although the primary emphasis is generally given to surge voltages.

# EXISTING AND PROPOSED STANDARDS

# ON TRANSIENT OVER VOLTAGES

Several Standards or Guides have been issued or proposed - in Europe by VDE, IEC, CECC, Pro-Electron, and CCITT; in the USA by IEEE, NEMA, UL, REA, FCC, and the Military - specifying a surge withstand capability for specific equipment or devices and specific conditions of transients in power or communication systems. Some of these specifications represent early attempts to recognize and deal with the problem in spite of insufficient data. As a growing number of organizations address the problem and as exchanges of information take place, improvements are being made in the approach. A Working Group of the Surge Protective Device Committee of IEEE has completed a document describing the environment in low-voltage ac power circuits (4). The document is now being reviewed by the IEEE Standards Board for eventual publication as a standard. For some time now, a document prepared by a Relaying Committee of IEEE under the title “Surge Withstand Capability” has been available (5). The FCC has also published regulations concerning equipment interfacing the communications and power systems (6).The Low Voltage Insulation Coordination Subcommittee, SC/28A, of IEC has also completed a report, to be published in 1979, listing the maximum values of transient overvoltages to be expected in power systems, under controlled conditions and for specified system characteristics (7). These documents will be reviewed in the pages that follow. Greatest emphasis, however, will be placed on the IEEE document because it describes the transient environment; the others assume an environment for the purpose of specifying tests.

# The IEEE Surge Withstand Capability Test

One of the earliest published documents to address new problems facing electronic equipment exposed to power system transients was prepared by an IEEE committee dealing with the exposure of power system relaying equipment to the harsh environment of high-voltage substations. This document, which describes a transient generated by the arcing that takes place when air-break disconnect switches are opened or closed in the power system, presents significant innovations in surge protection. The voltage waveshape specified is an oscillatory waveshape, not the historical unidirectional waveshape; a source impedance, a characteristic undefined in many other documents, is defined; and the concept that all lines to the device under test must be subject to the test is spelled out.

Because this useful document was released at a time when little other guidance was available, users attempted to apply the document's recommendations to situations where the environment of a high-voltage substation did not exist. Thus, an important consideration in the writing and publishing of documents dealing with transients is a clear definition of the scope and limitations of application.

## Federal Communications Commission Requirements

The Federal Communications Commission (FCC) has issued regulations describing tests to be applied to equipment interfacing the power distribution system and the communication system. The intent of these tests is protection of the equipment itself as well as protection of the communications plant from surges originating on the ac power side of the equipment. This concern is especially motivated by the recent proliferation of terminal equipment being installed by telephone service subscribers.

The most exacting test specified by these regulations is the application on the ac side of equipment to be connected to the telephone system of a 1 x 10 s impulse superimposed to the 60 Hz line voltage. The crest of this voltage impulse is 2.5 kV, and the short-circuit capability of the impulse source must be no less than 1 kA. This requirement of a substantial short-circuit capability reflects the perceptions of contributors to the regulation-making process that such surge currents may occur in the real world, or it may express a wish to produce in the laboratory a detectable burn-in of the fault following sparkover during the application of the surge. Records on the background of this regulation available to the author are not specific on which of the two concerns was primary in the specification of such a high short-circuit capability.

# The IEC SC/28A Report on Clearances

The Insulation Coordination Committee of the International Electrotechnical Commission, following a comprehensive study of breakdown characteristics in air gaps, included in its report a table indicating the voltages that equipment must be capable of withstanding in various system voltages and installation categories (Table 1).

The table specifies that it is applicable to a “controlled voltage situation,” which phrase implies that some surge-limiting device will have been provided—presumably a typical surge arrester with characteristics matching the system voltage in each case. The waveshape specified for these voltages is the 1.2 x 50 s wave, a specification consistent with the insulation background of the equipment. No source impedance is indicated, but four “installation categories” are specified, each with decreasing voltage magnitude as the installation is farther removed from the outdoor environment. Thus, this document addresses primarily the concerns of insulation coordination, and the specification it implies for the environment is more the result of efforts toward coordinating levels than efforts to describe the environment and the occurrence of transients. The latter approach has been that of the IEEE Working Group on Surge Voltages in Low-Voltage ac Power Circuits, which we shall now review in some detail.

The IEEE Working Group Proposal

# Voltages and Rates of Occurrence

Data collected from a number of sources let to plotting a set of lines representing a rate of occurrence as a function of voltage for three types of exposures (Figure 1). These exposure levels are defined in general terms as follows:

- Low Exposure – Systems in geographical areas known for low lightning activity, with little load switching activity.

- High Exposure – Systems in geographical areas known for high lightning activity, with frequent and severe switching transients.

- Extreme Exposure – Rare but real systems supplied by long overhead lines and subject to reflections at line ends, where the characteristics of the installation produce high sparkover levels of the clearances.

Both the low-exposure and high-exposure lines are truncated at about 6 kV because that level is the typical wiring device sparkover. The extreme-exposure line, by definition, is not limited by this sparkover. Because it represents an extreme case, the extreme-exposure line needs to be recognized, but is should not be applied indiscriminately to all systems. Such application would penalize the vast majority of installations, where the exposure is lower.

# Waveshape of the Surges

Many independent observations (8, 9, 10) have established that the most frequent type of surge voltages in ac power systems is a decaying oscillation, with frequencies between 5 and 500 kHz. This finding is in contrast to earlier attempts to apply the unidirectional double exponential voltage wave, generally described as 1.2 x 50. Indeed, the unidirectional voltage wave has a long history of successful application in the field of dielectric withstand tests and is representative of the surges propagating in power transmission systems exposed to lightning. In order to combine the merits of both waveshape definitions and to specify them where they are applicable, the Working Group proposal specifies an oscillatory waveshape inside buildings and a unidirectional waveshape outside buildings, and both at the interface (Figure 2).

# Energy and Source Impedance

The energy involved in the interaction of a power system with a surge source and a surge protective device will divide between the source and the protective device in accordance with the characteristics of the two impedances.

Unfortunately, not enough data have been collected on what value should be assumed for the source impedance of the surge. Standards and recommendations, .such as MIL STD-1399 or the IEC SC/28A Report, either ignore the issue or indicate values applicable to limited cases, such as the SWC test for high-voltage substation equipment. The IEEE 587.1 document attempts to relate impedance to categories of locations but unavoidably remains vague on their definitions (Table II).

Having defined the environment for low-voltage ac power circuits, the Working Group is now preparing an Application Guide, where a step-by-step approach, perhaps in the form of a flow chart (Figure 3), will outline the method for assessing the need for surge protection and selecting the appropriate device or system. Parallel work in other IEEE working groups preparing test specification standards (11) for surge protective devices will be helpful in this selection process. Other groups in the U.S., as well as the international bodies of IEC and CCITT, are now working toward further refinements and the reconciliation of different approaches.

# SURGE PROTECTIVE DEVICES

Various devices have been developed for protecting electrical and electronic equipment against surge voltages. They are often called "transient suppressors" although, for accuracy, they should be called "transient limiters," "clamps," or "diverters" because they cannot really suppress transients; rather they limit surge voltages to acceptable levels or make them harmless by diverting the surge current to ground.

There are two categories of surge protective devices: those that block the surge voltages, preventing their propagation toward sensitive circuits, and those that divert surge currents, limiting residual voltages. Since some of  the surges originate from a current source, the blocking of a surge voltage may not always be possible; the diverting of the surge current is more likely to find general application. A combination of diverting and blocking can be a very effective approach: a first device diverts the surge current toward ground, a second device - impedance or resistance - offers a restricted path to the surge propagation but an acceptable path to the signal or power, and a third device clamps the residual transient overvoltage. Thus, we are primarily interested in the diverting devices. These diverting devices can be of two kinds: voltage-clamping devices and short-circuiting devices (crowbar). Both involve some nonlinearity, either frequency nonlinearity (as in filters) or, more usually, voltage nonlinearity. This voltage nonlinearity is the result of two different mechanisms - a continuous change in the device conductivity as current increases or an abrupt switching as voltage increases.

# Crowbar Devices

The principle of crowbar devices is quite simple. Upon occurrence of an overvoltage, the device changes from a high-impedance state to a low impedance state, offering a low-impedance path to divert the surge to ground. This switching can be inherent to the device, as in the case of spark gaps involving a switching action. Some applications have also been made of triggered devices, such as triggered vacuum gaps in high-voltage technology or thyristors in low-voltage circuits, where control circuits sense the rising voltage and turn on the power-rated devices to divert the surge.

The crowbar device, however, has two major limitations. One is the volt-time sensitivity of the breakdown process. As the voltage increases across a spark gap, significant conduction of current - and hence the voltage limitation of a surge - cannot take place until the transition to the arc mode of conduction by avalanche breakdown of the gas between the electrodes occurs. The load is left unprotected during the initial rise because of this delay time.

The most significant limitation to crowbar applications in power systems is the inability of the device to clear the circuit from the power-follow current supplied by the power system after the sparkover of the gap or turn-on of the device. Without some additional device to limit the power-follow current, a crowbar is generally not acceptable in a power system. On the other hand, a crowbar combined with a power frequency current-limiting varistor - the conventional surge arrester - has long been the most widely used protective device in power system.

# Voltage-Clamping Devices

Voltage-clamping devices have variable impedance, depending on the current flowing through the device or the voltage across its terminal. These components show a nonlinear characteristic - that is, Ohm's law can be applied, but the equation has a variable R. Impedance variation is monotonic and does not contain discontinuities, in contrast to the crowbar device, which shows a turn-on action.

When a voltage-clamping device is installed, the circuit remains unaffected by the device before and after the transient for any steady-state voltage below clamping level. Increased current drawn through the device as the voltage attempts to rise results in voltage-clamping action. Nonlinear impedance is the result if this current rise is faster than the voltage increase. The increased voltage drop (IR) in the source impedance due to higher current results in the apparent clamping of the voltage. It should be emphasized that the device depends on the source impedance to produce the clamping. A voltage divider action is at work, where one sees the ratio of the divider as not constant but changing (Figure 4).

The principle of voltage clamping can be achieved with any device exhibiting this nonlinear impedance. Two categories of devices, having the same effect but operating on very different physical processes, have found acceptance in the industry: the polycrystalline varistors and the single-junction avalanche diodes. Another technology, the selenium rectifier, has been practically eliminated from the field because of the improved characteristics of modern varistors.

Avalanche Diodes

Avalanche diodes, the Zener diodes, were initially applied as voltage clamps, a natural outgrowth of their application as voltage regulators. Improved construction, specifically aimed at surge absorption, has made these diodes very effective suppressors. Large-diameter junctions and low thermal impedance connections are used to deal with the inherent problem of dissipating the heat of the surge in a very thin single-layer junction.

The advantage of the avalanche diode, generally a PN silicon junction, is the possibility of achieving low clamping voltage and a nearly flat volt-ampere characteristic over its useful power range. Therefore, these diodes are widely used in low-voltage electronic circuits for the protection of 5 or 15 V logic circuits, for instance. For higher voltages, the heat generation problem associated with single junctions can be overcome by stacking a number of lower voltage junctions, admittedly at some extra cost.

In the same category, we find silicon diodes used in the forward direction rather than in the reverse avalanche. A stack of such diodes is required to produce the necessary clamping voltage (0.75 V per diode), but the result is a protective system with large current capability.

# Varistors

The term varistor is derived from its function as a variable resistor. The European usage is the term voltage-dependent resistor, but the term seems to imply that the voltage is the independent parameter in surge protection, a concept which is misleading. Two very different devices have been successfully developed as varistors: silicon carbide discs have been used for years in the surge arrester industry; more recently, metal oxide varistors (MOV) have come of age, with the result that these new varistors are sometimes referred to as "movistors" (12).

Metal oxide varistors depend on the conduction process occurring at the boundaries between the large grains of oxide (typically zinc oxide) grown in a carefully controlled sintering process. Detailed descriptions of the process can be found in many publications (13, 14, 15, 16, 17).

Metal oxide varistors were initially developed as electronic circuit protection devices. Later large metal oxide varistors were developed and applied to large station surge arrestors (18). No device, however, was available in a rating suitable for power distribution systems. The surge currents occurring in these systems are excessive for electronic-type varistors, a fact demonstrated by field failures resulting from improperly applied varistors. Such failures could have been anticipated had the data included in the proposed IEEE Guide reviewed above been available at the time. In this context, it is worthwhile to examine the implication of failure modes for the surge protective devices.

# Failure Modes

An electrical component is subject to failure either because its capability was exceeded by the applied stress or because some latent defect in the component went unnoticed in the quality control processes. While this situation is well recognized for ordinary components, a surge protective device, which is no exception to these limitations, tends to be expected to perform miracles, or at least to fail graciously in a "fail-safe" mode. The term "fail-safe," however, may mean different failure modes to different users and, therefore, should not be used. To some users, fail-safe means that the protected hardware must never be exposed to an over voltage, so that failure of the protective device must be in the fail-short mode, even if it puts the system out of operation. To other users, fail-safe means that the function must be maintained, even if the hardware is left temporarily unprotected, so that failure of the protective device must be in the open-circuit mode. It is more accurate and less misleading to describe failure modes as "fail-short" or "fail-open," as the case may be.

When the diverting path is a crowbar-type device, little energy is dissipated in the crowbar, as noted earlier. In a voltage-clamping device, more energy is deposited in the device, so that the energy-handling capability of a candidate protective device is an important parameter to consider in the designing of a protection scheme. With nonlinear devices, an error made in the assumed value of the current surge produces little error on the voltage developed across the protective device and thus applied to the protected circuit, but the error is directly reflected in the amount of energy which the protective device has to absorb. At worst, when surge currents in excess of the protective device capability are imposed by the environment, either because of an error made in the assumption, or because of human error in the use of the device, the circuit in need of protection can generally be protected at the price of failure in the short-circuit mode of the protective device. However, if substantial power-frequency currents can be supplied by the power system, the fail-short protective device generally terminates as fail-open when the power system fault in the failed device is not cleared by a series overcurrent protective device (fuse or breaker).

Protection Coordination

By protection coordination we mean a deliberate selection of two or more protective devices used with the goal of reliable protection at minimum cost. With the present situation of the unregulated and uncoordinated application of protective devices, this may seem an unattainable goal for complete systems. In specific cases, it is fully attainable, as the example that follows will show. One can hope that success will eventually spread the concepts and increase the drive to generalize the approach.

One of the first concepts to be adopted when a coordinated scheme is considered is that current, not voltage, is the independent variable involved. The physics of overvoltage generation involves either lightning or load switching. Both are current sources, and it is only the voltage drop associated with the surge current flow in the system impedance which appears as a transient overvoltage. Furthermore, there is a long history of testing insulation with voltage impulses which has reinforced the erroneous concept that voltage is the given parameter. Thus, overvoltage protection is really the art of offering low impedance to the flow of surge currents rather than attempting to block this flow through a high series impedance. In low-power systems, a series impedance is sometimes added in the circuit, but only after a low-impedance diverting path has first been established; for high-power systems, that option is generally not available.

# Coordination Between an Arrester and a Varistor

This example involves a load circuit for which the maximum transient overvoltage had to be limited to 1000 V (on a 120 V ac line) although lightning surges were expected on the incoming service. The only arresters available at the time which could withstand a 10 kA crest, 8 x 20 s impulse ha a protective (clamping) level of approximately 2200 V. some distance was available between the service entrance and the location of the protected circuit, so that impedance was in fact inserted in series between the arrester and the protected circuit where a varistor with lower clamping voltage would be installed. The testing objective was to determine at what current level the arrester would spark over for a given length of wire between the two protective devices, relieving the varistor from the excessive energy that it would absorb if the arrester did not spark over.

A circuit was set up in the laboratory (19), with 8 m of typical two-wire cable between the arrester and the varistor. The current, approximately 8 x 20 impulse, was raised until the arrester would spark over about half of the time in successive tests at the same level, thus establishing the transfer of conduction from the varistor to the arrester. Figure 5A shows the discharge current level required from the generator at which this transfer occurs. Figure 5B shows the voltage at the varistor when the arrester did not spark over. Figure 5C shows the voltage at the arrester when it sparked over, a voltage that would propagate inside all of the building if there were no suppressor added. However, when a varistor is added at 8 m, the voltage of Figure 5C is attenuated to that shown in figure 5D, at the terminals of the varistor.

# Comparison between a High-Energy Varistor and an Arrester/Low-Power Varistor

In the case of power circuits where no regulation or centralized engineering authority can mandate a coordinated approach, individual protection of each piece of equipment may remain the only safe approach to the manufacturer of equipment installed under this uncontrolled situation. The choice of protection is then a question of economics and calculated risks: provide equipment with low-cost, low-capability protection, or with high-capability protection at a higher cost.

The first choice, low-cost, low-capability protection, will be effective in the vast majority of indoors locations, such as Category A, or even B, described in the proposed IEEE guide (4); there is, however, a finite probability of failure if the equipment is installed close to the outdoor environment in a high-exposure location. An arrester installed at the service entrance would relieve the low-capability protection from absorbing excess energy. In that case, the situation explored in the experiment reported above would prevail: suitable coordination of the respective protective levels of the two devices and the impedance existing between them.

The second choice, provision of a high-capability protection in each piece of Equipment, would obviously provide adequate protection and might be justified where the cost of equipment failure in terms of money, dead-time, or embarrassment outweighs the initial outlay of component investment. It is doubtful, however, that even mass-production could lower the cost of the high-capability device.

In the case of power circuits where a centralized engineering authority is in a position to enforce coordinated protection and practices, the appropriate procedure is evident and much more economical: provide a single high-capability protective device at the service entrance to deal with incoming lightning-induced surges and power system switching surges; if necessary, complement the protection with coordinated low-capability protective devices at individual pieces of equipment, to deal with any internal switching transients that may occur. Indeed, coordination of the two protective devices is imperative to prevent the low-capability (and low clamping voltage) device from clamping the incoming surge and thus absorbing all the energy.

Such coordination is now possible, since varistors with surge ratings to 25 kA for single surges and appropriate derating for multiple surges (11) have become available. This rating is higher than the requirements of ANSI Standards for secondary arresters (20, 21) and thus would be suitable for Category C (10 kA) of the proposed IEEE Guide. These high-capability varistors will clamp the voltage at a level sufficiently low - typically 600 V in a 120 V system under a surge of 10 kA, or 1100 V in a 240 V system for the same 10 kA surge (by comparison, conventional arresters have a protective level of 2 to 3 kV). The availability of low clamping voltage devices for both the high-energy service entrance duty and the low-cost individual equipment protection makes an effective coordination easy to achieve.

# Conclusions

After many years of data collection and evaluation, a consensus is now emerging on the definition of the ac power system transient over voltage environment, including both voltage and current levels.

This definition will enable protection engineers in centralized organizations, such as those existing in the operating communications companies, to design coordinated schemes of protection, and will enable equipment designers and manufacturers to assess the risks involved in providing various levels of protection for their equipment on the basis of economic and functional criteria.

References

1. C.F. Wagner and G.D. McCann, "Lightning Phenomena," Electrical Transmission and Distribution Reference Book, Westinghouse Electric Corp., East Pittsburgh, PA, 1950, pp. 556-559.

2. N. Cianos and E.T. Pierce, A Ground-Lightning Environment for Engineering Usage, Stanford Research Institute, Technical Report, August 1972.

3.  A. Greenwood, "Electrical Transients in Power Systems," Wiley Interscience, New York, 1971.

4. "Guide on Surge Voltages in AC Power Circuits Rated Up to 600 V," Final Draft, May 1979. Document prepared by Working Group 3.4.4 of the Surge Protective Devices Committee of the Power Engineering Society, Institute of Electrical and Electronics Engineers.

5. Guide for Surge Withstand Capability (SWC) Tests, ANSI Standard C37.90a, 1974; IEEE Standard 472-1974.

6. Longitudinal Voltage Surge Test #3 - Section 68.302(e), Title 47, "Telecommunications," Code of Federal Regulations, U.S. Gov't. Printing Office, Washington, DC, 1977.

7. "Insulation Coordination Within Low-Voltage Systems Including Clearances and Creepage Distances for Equipment," International Electrotechnical Commission Report SC28A (Central Office) 5 (to be published in 1979).

8. J.E. Lenz, "Basic Impulse Insulation Levels of Mercury Lamp Ballast for Outdoor Applications," Illuminating Engrg., Feb. 1964, pp. 133-140.

9. F.D. Martzloff and G.J. Hahn, "Surge Voltage in Residential and Industrial Power Circuits," IEEE; PAS-89, 6, July/August 1970, pp. 1049-1056.

10. R. Hasler and R. Lagadec, "Digital Measurement of Fast Transients on Power Supply Lines," Proc. 3rd Symposium and Technical Exhibition on Electro-Magnetic Compatibility, Rotterdam, Holland, May 1979, pp. 445-448.

11. "Test Specifications for Varistor Surge-Protective Devices," P465.3. Draft prepared by Task Force 3.3.6.3 of the IEEE Surge Protective Devices for eventual publication as an IEEE Standard.

12. Harnden, J.D., Martzloff, F.D., Morris, W.G., and Golden, F.B., "The GE-MOV Varistor - The Super Alpha Varistor," Electronics 45, 21, 1972, p. 91.

13. Matsuoka, M., Masa Yama, To, and Lida, Y., "Nonlinear Electrical Properties of Zinc Oxide Ceramics," Proc. of First Conf. Solid State Devices, Tokyo, 1969, J. Japan Soc. Appl. Phys., 39, 1970, Suppl. p. 94.

14. Mahan, G.D., Levinson, L.M., and Phillip, H.R., Theory of Conduction in ZnO Varistors, 78CRD205, General Electric Company, Schenectady, NY, 1978.

15. Richman, P., "Diagnostic Surge Testing, Part I," Solid State Power Conversion, Sept./Oct. 1979.

16. Transient Voltage Suppression Manual, Second Edition, General Electric Company, Auburn, NY, 1978.

17. Gauthier, N., "Technologie et Applications des Varistances," Toute L'Electronique, January 1978

18. Sakshaug, E.C., Kresge, J.S., and Miske, S.A., "A New Concept in Station Arrester Design," IEEE PAS-96, No.2, March-April 1977, pp. 647-656.

19. F.D. Martzloff, "Coordination of Surge Protectors in Low-Voltage AC Power Circuits," Preprint No. F29 6354 for IEEE PES Summer Meeting, Vancouver, Canada, July 1979.

20. Surge Arresters for Alternating-Current Power Circuits, IEEE Standard 28-1974; ANSI Standard C62.1-1975; IEC Standard 99-2.

21. Guide for Application of Valve-Type Lightning Arresters for Alternating Current Systems, ANSI Standard C62.2. (Rev. 1979 to be published.)

The Coordination of Transient Protection

for Solid-State Power Conversion Equipment

F.D. Martzloff

Corporate Research and Development

General Electric Company

Schenectady, New York, USA

ABSTRACT

Transient overvoltages are no longer an unknown threat to the successful application of power conversion equipment, thanks to the availability of protective techniques and devices. This paper presents an overview of the origin of transient overvoltages and of recent IEEE and IEC documents identifying and categorizing transients. A brief review of available techniques and devices follows, with a description of the principles of coordinated protection, specific experimental examples, and results reconciling the unknown with the realities of equipment design.

INTRODUCTION

Since the introduction of semiconductors, transient over-voltages have been blamed for device failures and system malfunctions. Semiconductors are, indeed, sensitive to over-voltages. However, data have been collected for several years on the occurrence of overvoltages, to the point where the problem is now mostly a matter of economics and no longer one of lack of knowledge on what the environment of power systems can inflict to poorly protected semiconductor circuits. This statement may represent a slight oversimplification of the general problem because the environment is still defined in statistical terms, with unavoidable uncertainty as to what a specific power system can impress on a specific piece of power conversion equipment.

The IEEE has published a Guide (1) describing the nature of transient overvoltages (surges) in low-voltage ac power circuits. This Guide provides information on the rate of occurrence, on the waveshape, and on the energy associated with the surges, as a function of the location within the power system. In addition, the IEC has issued a report concerning insulation coordination (2), identifying four categories of installations, with a matrix of power system voltages and overvoltages specified for controlled situations. Other groups have also proposed test specifications, some of which are now enshrined in standards that may be applied where they are really not applicable, but have been applied because no other information was available at the time.

At this time, the environment seems to be defined with sufficient detail. However, there is still a lack of guidance on how to proceed for specific instances, and circuit designers may feel that they are left without adequate information to make informed decisions on the selection of component characteristics in the field of overvoltage withstand or protection. This situation has been recognized, and various groups concerned with the problem are attempting to close the gap by preparing application guides which will provide more specific guidance than a mere description of the environment, although that description in itself is already a considerable step forward.

One of the difficulties in designing a protection scheme in the industrial world of power conversion equipment is the absence of an overall system coordinator, in contrast to the world of electric utilities, for instance, which are generally under the single responsibility of a centralized engineering organization. The user of power conversion equipment is likely to purchase the material from a supplier independently of other users of the same power system, and coordination of overvoltage protection is generally not feasible under these conditions. Worse yet, an uncoordinated application of surge suppressors can lead to wasteful or ineffective resource allocation, since independent users would each attempt to provide protection in adjacent systems or independent designers would provide protective devices in adjacent subsystems.

To shed more light on this situation, this paper will briefly review some of the origins of transient overvoltages, with reference to recently published IEEE and IEC documents, which provide guidance on the environment. Techniques and protective devices will then be discussed, and examples of coordinated approaches presented.

THE ORIGIN OF TRANSIENT OVER VOLTAGES

Two major causes of transient overvoltages have long been recognized: system switching transients, and transients triggered or excited by lightning discharges (in contrast to direct lightning discharges to the power systems, which are generally quite destructive, and against which total protection may not be economical in the average application). System switching transients can involve a substantial part of the power system, as in the case of power factor correction capacitor switching operations, disturbances following restoration of power after an outage, and load shedding. However, these do not generally involve large overvoltages (more than two or three per unit), but may be very difficult to suppress since the energies are considerable. Local load switching, especially if it involves restrikes in switchgear devices, will produce higher voltages than the power system switching, but generally at lower energy levels. Considering, however, the higher impedances of the local systems, the threat to sensitive electronics is quite real, and only a few conspicuous case histories of failures can cast an adverse shadow over a large number of successful applications.

# VOLTAGE LEVELS

Two different approaches have been proposed to define voltage levels in ac power systems. At this time, the divergences have not yet been reconciled, as each proposal has its merits and justification. The IEEE approach involves reciting a rate of occurrence as a function of voltage levels, as well as of exposure in systems that do not necessarily use protective devices. The IEC approach indicates only a maximum level for each location category, but no higher values are expected because this approach implies the application of protective devices. These two proposals will be quoted in the following paragraphs.

The IEEE Guide (IEEE Std 587-1980)

Data collected from a number of sources led to plotting a set of lines representing a rate of occurrence as a function of voltage for three types of exposures in unprotected circuits (Figure 1). These exposure levels are defined in general terms as follows:

•	Low Exposure — Systems in geographical areas known for low lightning activity, with little load switching activity.

•	Medium Exposure — Systems in geographical areas known for high lightning activity, with frequent and severe switching transients.

•	High Exposure — Rare but real systems supplied by long overhead lines and subject to reflections at line ends, where the characteristics of the installation correspond to high sparkover levels of the clearances.

It is essential to recognize that a surge voltage observed in a power system can be either the driving voltage or the voltage limited by the sparkover of some clearance in the system. Hence, the term unprotected circuit must be understood to be a circuit in which no low-voltage protective device has been installed, but in which clearance sparkover will eventually limit the maximum voltage. The distribution of surge levels, therefore, is influenced by the surge-producing mechanisms as well as by the sparkover level of clearances in the system.

## Figure 1.  Rate of surge occurrence versus voltage level in unprotected circuits (IEEE 587)

The voltage and current amplitudes presented in the Guide attempt to provide for the vast majority of lightning strikes but should not be considered as “worst case,” since this concept cannot be determined realistically. One should think in terms of the statistical distribution of strikes, accepting a reasonable upper limit for most cases. Where the consequences of a failure are not catastrophic but merely represent an annoying economic loss, it is appropriate to make a tradeoff of the cost of protection against the likelihood of a failure caused by a high but rare surge.

The IEC Approach (IEC Report 664, 1980)

In a report dealing with clearance requirements for insulation coordination purposes, the IEC Subcommittee SC/28A recommends a set of impulse voltages to be considered as representative of the maximum occurrences at different points of a power system, and at levels dependent upon the system voltage (Table I). The report is not primarily concerned with a description of the environment, but more with insulation coordination of devices installed in these systems. This approach rests entirely on the establishment of controlled levels in a descending staircase, as the wiring systems progress within the building away from the service entrance.

The fundamental assumption made in establishing the levels of Table I is that a decreasing staircase of overvoltages will evolve from the outside to the deep inside of a building (system), either as the result of attenuation caused by the impedance network, or by the installation of overvoltage limiters at the interfaces.

If the descending staircase of voltages is provided by a surge protective device at each interface, it must be recognized that the successive devices will interact; the situation is not one of one-way propagation of the surges. Indeed, a protective device installed, say, at the III/II interface might be so close (electrically) to the device at interface IV/III that it could prevent the latter from operating; in other words, the III/II device might face the surge duty normally expected to be handled by the IV/III device. Thus, a vital aspect in the selection of interface devices is that of ensuring proper coordination.

Table I

Preferred Series Of Values Of Impulse Withstand Voltages

For Rated Voltages Based On A Controlled Voltage Situation

In both the IEEE standard and the IEC report, the assumption has been made that the surge is impinging the power system through the service entrance and is occurring between phase and earth. Experience has shown that a frequent cause of distress is the voltage differences existing between conductors reputed to be at ground potential; in fact, one of them is elevated above the other by the flow of surge current. This situation, not addressed in either document, needs to be recognized and dealt with on an individual, case-by-case basis, lest a false sense of security be created by restricting the protection to the power service entrance.

# WAVESHAPE OF THE TRANSIENT OVERVOLTAGES

Observations in different locations (3-6) have established that the most frequent type of transient overvoltage in ac power systems is a decaying oscillation, with frequencies between 5 and 500 kHz. This finding is in contrast to earlier attempts to apply the unidirectional double exponential voltage wave, generally described as 1.2/50, although the unidirectional voltage wave has a long history of successful application in the field of dielectric withstand tests and is representative of the surges propagating in transmission systems exposed to lightning. The IEEE Guide recommends two waveshapes, one for the indoor environment, and one for the outdoor and near-outdoor environment (Figure 2). Not only is a voltage impulse defined, but the discharge current, or short-circuit current of a test generator used to simulate these transients, is also defined in the IEEE document.

The oscillatory waveshape simulates those transients affecting devices that are sensitive to dv/dt and to voltage reversals during conduction (7). The unidirectional voltage and current waveshapes, based on long-established ANSI standards for secondary valve arresters, simulate the transients where energy content is the significant parameter.

### ENERGY AND SOURCE IMPEDANCE

The energy involved in the interaction of a power system with a surge source and a surge suppressor will divide between the source and the suppressor in accordance with the characteristics of the two impedances. In a gap-type suppressor, the low impedance of the arc after sparkover forces most of the energy to be dissipated elsewhere, e.g., in the power system series impedance or in a resistor added in series with the gap for limiting the power-follow current. In an energy-absorber suppressor, by its very nature, a substantial share of the surge energy is dissipated in the suppressor, but its clamping action does not involve the power-follow energy resulting from the short-circuit action of a gap. It is, therefore, essential to the effective use of suppression devices that a realistic assumption be made about the source impedance of the surge whose effects are to be duplicated.

Unfortunately, not enough data have been collected on what this assumption should be for the source impedance of the transient. Standards or recommendations either ignore the issue, such as MIL STD-1399 or the IEC Report 664 in its present published form [Footnote:  Continuing studies by the IEC SC28A Working Group are now addressing this issue, and additional publications are anticipated.]  they sometimes indicate values applicable to limited cases, such as the SWC test for electronic equipment operating in high-voltage substations (8). The IEEE Guide attempts to relate impedance with three categories of locations, A, B, and C. For most industrial environments, Categories A or B will apply; Category C is intended for outdoor situations (Table II).

# MATCHING THE ENVIRONMENT WITH THE EQUIPMENT

On the basis of the various documents mentioned in the preceding paragraphs, an equipment designer or user can take a systematic approach to matching the transient overvoltage capability of the equipment with the environment in which this equipment is to be installed. This design may involve tests to determine the withstand levels (9), some measurements and/or analysis to determine the degree of hostility of the environment, and a review of available protective devices. The latter will be discussed in the following paragraphs.

Figure 2. Transient overvoltages and discharge currents in IEEE Std. 587-1980

# Transient Suppressors

Two methods and types of devices are available to suppress transients: blocking the transient through some low-pass filter, or diverting it to ground through some nonlinear device. This nonlinearity may be either a frequency nonlinearity (high-pass filter) or a voltage nonlinearity  (clamping action or crowbar action). In this paper, a majority of the discussion will center on the latter type, since voltage clamping devices or crowbar devices are the most frequently used (10).

Voltage-clamping devices have a variable impedance, depending on the current flowing through the device or the voltage across its terminals.  These components show a nonlinear characteristic, i.e., Ohm’s law E=RI, can be applied but the equation has a variable R.  Impedance variation is monotonic and does not contain discontinuities, in contrast to the crowbar device which shows a turn-on action.  As far as volt-ampere characteristics of these components are concerned, they are time-dependent to a certain degree.  However, unlike sparkover of a gap or triggering of a thyristor, time delay is not involved here.

When a voltage-clamping device is installed, the circuit remains unaffected by the device before and after the transient for any steady-state voltage below clamping level. Increased current drawn through the device as the voltage attempts to rise results in voltage clamping action. Increased voltage drop (IZ) in the source impedance due to higher current results in the apparent clamping of the voltage. It should be emphasized that the device depends on the source impedance, Z, to produce the clamping. A voltage divider action is at work where one sees the ratio of the divider not constant, but changing (Figure 3). The ratio is low, however, if the source impedance is very low. The suppressor cannot work at all with a limit zero source impedance. In contrast, a crowbar-type device effectively short-circuits the transient to ground. Once established, however, this short circuit will continue until the current (the surge current as well as any power-follow current supplied by the power system) is brought to a low level.

Figure 3. Voltage clamping action of a suppressor

The crowbar device will often reduce the line voltage below its steady-state value, but a voltage clamping device will not.  Substantial currents can be carried by the crowbar suppressor without dissipating a considerable amount of energy within the suppressor, since the voltage (arc or forward-drop) during the discharge is held very low.  This characteristic constitutes the major advantage of these suppressors.  However, limitations in volt-time response, power-follow, and noise generation are the price paid for this advantage.  As voltage increases across a spark-gap, significant conduction cannot take place until transition to the arc mode has taken place by avalanche breakdown of the gas between the electrodes.  The load is left unprotected during the initial rise due to this delay time (typically in microseconds).  Considerable variation exists in the spark-over voltage achieved in successive operations, since the process is statistical in nature.  For some devices, this sparkover voltage can also be substantially higher after a long period of rest than after successive discharges.  From the physical nature of the process, it is difficult to produce consistent sparkover voltage for low voltage ratings.  This difficulty is increased by the effect of manufacturing tolerances on very small gap distances.  This difficulty can be alleviated by filling the tube with a gas having lower breakdown voltage than air.  However, if the enclosure seal is lost and the gas is replaced by air, this substitution creates a reliability problem because the sparkover of the gap is then substantially higher.

Another limitation occurs when a power current from the steady-state voltage source follows the surge discharge (follow-current or power-follow). In ac circuits, this power-follow current may or may not be cleared at a natural current zero. In dc power circuits, clearing is even more uncertain. Additional means must, therefore, be provided to open the power circuit if the crowbar device is not designed to provide self-clearing action within specified limits of surge energy, system voltage, and power-follow current.

A third limitation is associated with the sharpness of the sparkover, which produces fast current rises in the circuits and, thus, objectionable noise. A classic example of this kind of disturbance is found in oscillograms recording the sparkover of a gap where the trace exhibits an anomaly before the sparkover (Figure 4). This anomaly is due to the delay introduced in the oscilloscope circuits to provide an advanced trigger of the sweep. What the trace shows is the event delayed by a few nanoseconds, so that in real time, the gap sparkover occurs while the trace is still writing the pre-sparkover rise. Another, more objectionable effect of this fast current change can be found in some hybrid protective systems. Figure 5 shows the circuit of such a device, as found in the commerce.  The gap does a very nice job of discharging the impinging high-energy surges, but the magnetic field associated with the high di/dt induces a voltage in the loop adjacent to the secondary suppressor, adding what can be a substantial spike to the expected secondary clamping voltage.  Consequently, most electronic circuits are better protected with voltage clamping suppressors than with crowbars, but sometimes the energy deposited in a voltage clamping device by a high current surge can be excessive a combination of the two devices can provide effective protection at optimum cost.  However, this combined protection must be properly coordinated to obtain the full advantage of the scheme.  The following paragraphs will discuss some of the basic principles of coordination and provide some examples of applications.

Figure 4.  Interference to oscilloscope circuits caused by gap sparkover

Figure 5.  Hybrid protector with gap

# PROTECTION COORDINATION

One of the first concepts to be adopted when considering a coordinated scheme is that current, not voltage, is the independent variable involved. The physics of overvoltage generation involve either lightning or load switching. Both are current sources, and it is only the voltage drop associated with the surge current flow in the system impedance which appears as a transient overvoltage. Perhaps a long history of testing insulation with voltage impulses has reinforced the erroneous concept that voltage is the given parameter. Thus, overvoltage protection is really the art of offering low impedance to the flow of surge currents rather than attempting to block this flow through a high series impedance. In combined approaches, a series impedance is sometimes added in the circuit, but only after a low impedance diverting path has first been established.

When the diverting path is a crowbar-type device, little energy is dissipated in the crowbar, as noted earlier. In a voltage clamping device, more energy is deposited in the device, so that the energy handling capability of a candidate suppressor is an important parameter to consider when designing a protection scheme. With nonlinear devices, an error made in the assumed value of the current surge produces little error on the voltage developed across the suppressor and thus applied to the protected circuit (11). but the error is directly reflected in the amount of energy which the suppressor has to absorb. At worst, when surge currents in excess of the suppressor capability are imposed by the environment, because of an error made in the assumption or because nature tends to support Murphy’s law or because of human error in the use of the device, the circuit in need of protection can generally be protected at the price of failure in the short-circuit mode of the protective device. However, if substantial power-frequency currents can be supplied by the power system, the fail-short protective device generally terminates as fail-open when the power system fault in the failed device is not cleared by a series overcurrent protective device (fuse or breaker). Note that in this discussion, the term “fail-safe” has carefully been avoided since it can mean opposite failure modes to different users. To some, fail-safe means that the protected hardware must never be exposed to an overvoltage, so that failure of the protective device must be in the fail-short mode, even if it puts the system out of operation. To other users, fail-safe means that the function must be maintained, even if the hardware is left temporarily unprotected, so that failure of the protective device must be in the open-circuit mode.

EXAMPLES OF COORDINATED SURGE PROTECTION

# Retrofit of a Control Circuit Protection

In this case history, a field failure problem was caused by lack of awareness (on the part of the circuit designer) of the degree of hostility in the environment where the circuit was to be installed. A varistor had been provided to protect the control circuit components on the printed circuit board, but its capability was exceeded by the surge currents occurring in a Category B location (Table II). To the defense of the circuit designer, however, it must be stated that the data of Table II were not available to him at the time.

Table II

#### Recommended Values From IEEE Std 587

Since a number of devices were in service, complete redesign was not possible, and a retrofit — at an acceptable cost — had to be developed. Fortunately, the power consumption of this control circuit was limited so that it was possible to insert some series impedance in the line, ahead of the low-capacity varistor, while a higher capacity varistor was added at the line entrance to the circuit (Figure 6).  Laboratory proof-test of the retrofit demonstrated the capability of the combined scheme to withstand 6 kA crest current surges (Figure 7A) and a 200% margin from the proposed Category B requirement, as well as reproduction of the field failure pattern (Figure 7B). The latter is an important aspect of any field problem retrofit. By simulating in the laboratory the assumed surges occurring in the field (Table II), verification of the failure mechanism is the first step toward an effective cure. Figure 7C illustrates the effect of improper installation of the suppressor, with eight inches of leads instead of a direct connection across the input terminals of the circuit.

## Figure 6.  Retrofit protection of control circuit

# Coordination Between a Secondary Surge Arrester and a Varistor

In this example, the objective was to provide overvoltage protection with a maximum of 1000 V applied to the protected circuit, but to withstand current surges on the service entrance of magnitudes associated with lightning, as defined in ANSI C62.1 and C62.2 standards for secondary arresters. The only arresters available at the time which could withstand a 10 kA crest 8/20 s impulse had a protective (clamping) level of approximately 2200 V (12). Some distance was available between the service entrance and the location of the protected circuit, so that impedance was in fact inserted in series between the arrester and the protected circuit where a varistor with lower clamping voltage would be installed. The object was to determine the current level at which the arrester would spark over for a given length of wire between the two protective devices, relieving the varistor from the excessive energy that it would absorb if the arrester would not spark over.

A circuit was set up in the laboratory (13), with 8 m (24 ft) of #12 (2.05 mm) two-wire cable between the arrester and the varistor. The current, approximately 8/20 s impulse, was raised until the arrester would spark-over about half of the time in successive tests at the same level, thus establishing the transfer of conduction from the varistor to the arrester. Figure 8A shows the discharge current level required from the generator at which this transfer occurs. Figure 8B shows the voltage at the varistor when the arrester does not spark over. Figure 8C shows the voltage at the arrester when it sparks over; this voltage would propagate inside all of the building if there were no suppressor added. However, if a varistor is added at eight meters, the voltage of Figure 8C is attenuated to that shown in Figure 8D, at the terminals of the varistor.

## Figure 7.  Laboratory demonstration of retrofit effectiveness

## Figure 8.  Transfer of conduction in a coordinated scheme of protection

# Matching Suppressor Capability to the Environment

It is a recognized fact that varistors exhibit, as do many other components, an aging characteristic, so that a finite life can be predicted. Most manufacturers provide information on this aspect of application, and IEEE standards identify this parameter as one of the significant evaluation tests (14). Carroll has shown (15) how statistical information presented in IEEE Std 587 can be combined with Pulse Lifetime Ratings published by manufacturers (16) to arrive at a rational selection of device ratings, with a specific life goal, in a cost-effective manner.

However, these ratings are generally expressed as a number of pulses of constant value, e.g., the rated life of a given varistor may be 1 pulse of 6 kA at 8/20, 10 pulses at 2 kA, 1000 pulses at 500 A, and so forth. But since the surges encountered in real life have a range of values at a slope of probability versus magnitude described by Figure 1, one must consider the effect of this array of pulses with different values rather than the constant pulses implied by the manufacturer’s pulse lifetime rating.

The method described by Carroll in the referenced paper provides a computation that can be applied in general terms, but repeating it here would be too lengthy. Rather, we will take two examples of application and develop a table showing how the Pulse Lifetime Ratings can be combined with the data from IEEE Std 587 to make a reasonable estimation of the rated life consumption. The computations shown in the tables have been made with four digits for the sake of allowing a check of the arithmetic, but the base data are far from four significant digits in their accuracy, and the numbers are read from curves with rather coarse logarithmic scales. However, these examples do illustrate the method and the results that can be expected.

The first task is to convert the voltage surge density probability of Figure 1 into a histogram of surge currents. A family of surge voltage cells can be defined from the Figure 1 line, with the density read at the center of the cell. The number of occurrences for any cell is then the value of the ordinate of the line, minus the number of total occurrences of all cells to the right of the cell of interest. In the computations of Table III, this conversion is shown in the first three columns, indicating the voltage level at the cell center, the number per year, and the number of occurrences per year.

From the description of the Category B in IEEE Std 587, one can deduce an implied source impedance of 6 kV/3 kA for a surge or 8/20 s, or 2  as the most severe in Category B. The current that will flow in a varistor connected at this Category B location is then the surge voltage, minus the varistor clamping voltage, divided by the 2  source impedance of the surge. The varistor clamping voltage can be determined if the current is known, so an iteration would be required to obtain the clamping voltage. However, one can assume a clamping voltage, and later check the validity of the assumption against the resulting current obtained. The fourth column of Table III shows this assumed and subsequently checked value of the clamping voltage, hence the value of the available driving voltage in the next column, and the resulting surge current value, assumed to be an 8/20 s waveshape.

Table III

Life Consumption — 14 mm, 130 V RMS Varistor, Category B, Low Exposure

Turning then to the published Pulse Lifetime Ratings, one can read the rated number of pulses corresponding to the surge current for each cell. Table III is computed with the ratings for a 14 mm varistor (Figure 9a); Table IV is computed for a 32 mm varistor (Figure 9b). Note that this “rated life” is defined as the condition reached when the varistor nominal voltage has changed by 10%; this is not the end of life for the varistor, but only an indication of some permanent change beginning to take place. The varistor has still retained its voltage clamping capability at this point.

For each level of surge current, the number of pulses is read on the family of curves of Figures 9a or 9b, along the vertical axis, since these are 8/20 s impulses. The number of pulses with constant amplitude is shown in the next-to-last column of Table III. We can now define, for each level, the percentage of life consumed for one year of exposure at that level. For instance, at the 2500 V level of Table III, there will be 0.01 surges of 1010 A per year, with 10 allowed by the ratings. Therefore, in percent, the life consumption is (0.01/yr x 100)/10, or 0.10%. Likewise, taking the 900 V level, the consumption is (0.8/yr x 100)/2000 = 0.04%. The total of these life consumptions at all cell levels is then 0.43% of the rated life in one year, yielding an estimated 232 years for this 14 mm varistor to reach its rated life in the Low-Exposure Category B environment.

# Figure 9.  Pulse lifetime ratings

Similar computations for a 32 mm varistor in a Category B, Medium Exposure, are shown in Table IV. In the case of this “Medium Exposure,” we note the high frequency of occurrences below 3000 V. reflecting the “frequent and severe switching transients” cited in the IEEE definition of Medium Exposure. Thus, a still very conservative estimate would be that as many as half of the occurrences would be due to lightning, with the attendant 8/20 s high energy surges, while the other half would be switching transients, having a lower energy content than the 8/20 s surges accounted in this computation, being oscillatory as typified by the 0.5 s — 100 kHz wave. This translates to 13 surges of 760 A, 35 surges of 525 A, and 250 surges of 285 A, still a high number of lightning surges and therefore certainly conservative. Using this conservative estimate of half of the low-magnitude surges and all of the high-magnitude surges being 8/20 s lightning-related surges, the computation of Table IV yields 21 years to reach rated life for the 32 mm varistor. In this case, where the rated life is reached earlier, it should be pointed out that the results are strongly influenced by the assumption made for the source impedance. Using the IEEE 587 implied value of 2  leads to these conservative results. For example, the FCC test for communication equipment interfacing with power lines (17) implies a 2.5  source impedance. Current studies for complementary data to the IEC Report 664 make the assumption of a surge originating on the primary of a distribution transformer, with a 63  source impedance, yielding currents of less than 1 kA available at the service entrance interface. Thus, there is still room for more precise definitions of the source impedance, but we should recognize that any attempt to make broad generalizations will always encounter the contradiction of some special cases.

Table IV

Life Consumption — 32 mm, 150 V RMS Varistor, Category B, Medium Exposure

CONCLUSION

Effective protection of sensitive electronic equipment is possible through a systematic approach where the capability of the equipment is compared to the characteristics of the environment. The combined efforts of several organizations have produced a set of data which provide the circuit designer with reasonable information, albeit not fine specifications, on the assumptions to be made in assessing the hostility of the environment. With the publication of the IEEE Guide, and of application guides in the near future, we can expect better knowledge of the power system environment. As more field experience is gained in applying these documents to equipment design, the feedback loop can be closed to ultimately increase the reliability of new equipment at acceptable costs, while present problems may also be alleviated based on these new findings in the area of transient overvoltages.

ACKNOWLEDGMENTS

The data base for the Guide quoted in the paper as well as the writing of that Guide was provided by the members of the IEEE Working Group on Surge Characterization in Low-Voltage AC Power Circuits. Robert Mierendorf emphasized the significance of clearance sparkover; and Peter Richman’s critique of the concepts relating to source impedance proved very effective; and Eric Carroll’s cross examination of the IEEE Std 587 led to the concept of relating varistor pulse lifetime data to the distribution of expected surge currents.

REFERENCES

- “IEEE Guide for Surge Voltages in Low-Voltage AC Power Circuits,” IEEE Std 587-1980.

2.  “Insulation Coordination Within Low-Voltage Systems Including Clearances and Creepage Distances for Equipment,” International Electrotechnical Commission Report 664 (1980).

3.	J.E. Lenz, “Basic Impulse Insulation Levels of Mercury Lamp Ballast for Outdoor Applications,” Illuminating Engrg., pp. 133-140 (February 1964).

4.	F.D. Martzloff and G.J. Hahn, “Surge Voltage in Residential and Industrial Power Circuits,” IEEE PAS 89 (6), pp. 1049-1056 (July/August 1970).

5.	R. Hasler and R. Lagadec, “Digital Measurement of Fast Transients on Power Supply Lines,” Proc. 3rd Symposium and Technical Exhibition on Electromagnetic Compatibility, Rotterdam, Holland, pp. 445-448 (May 1979).

6.	F.D. Martzloff “Transient Overvoltages in Secondary Systems,” General Electric Company Report 81CRD 121, Schenectady, NY (1981).

7.	P. Chowdhuri, “Transient-Voltage Characteristics of Silicon Power Rectifiers,” IEEE IA-9 (5), p. 582 (September/October 1973).

8.  “Guide for Surge Withstand Capability,” (SWC) ANSI/IEEE C37.90a-1974.

9.	F.A. Fisher and F.D. Martzloff, “Transient Control Levels, A Proposal for Insulation Coordination in Low-Voltage Systems,” IEEE PAS-95 (1), pp. 120-129 (January/February 1976).

10.	Transient Voltage Suppression Manual, Chapter 2, General Electric Company, Auburn, NY, pp. 13-17 (1978).

11.	Transient Voltage Suppression Manual, Chapter 2, General Electric Company, Auburn, NY, p. 15 (1978).

12.	F.D. Martzloff, “Transient Overvoltage Protection: The Implications of New Techniques,” Proc. 4th Symposium and Technical Exhibition on Electromagnetic Compatibility, Zurich, Switzerland, pp. 505-510 (March 1981).

13.	F.D. Martzloff, “Coordination of Surge Protectors in Low-Voltage AC Power Circuits,” IEEE PAS-99 (1), pp. 129-133 (January/February 1980).

14.	“Test Specifications for Varistor Surge-Protective Devices,” IEEE STd C62. 33, 1982.

15.	E. Carroll, “Transient Attenuation with Metal Oxide Vanstors for AC Mains Powered Equipments,” presented at “Comel,” University of Twente, Holland (November 1980).

16.	Transient Voltage Suppression Manual, Chapter 4, General Electric Company, Auburn, NY, pp. 39-41 (1978).

17.	Longitudinal Voltage Surge Test #3, Code of Federal Regulation, Section 68.302(e), Title 37, Telecommunications, Washington, D.C., U.S. Government Printing Office. 197T

Lightning Protection of Roof-Mounted Solar Cells

F. D. Martzloff

General Electric Company

Schenectady, New York

# SUMMARY

Lightning interception by an unprotected building 30 feet high x 45 feet long on flat land, in the Cleveland area, can be estimated at one strike per 200 years on the average.  However, peculiar configuration can easily affect this estimate upward or downward.  Means are available to install air terminals so that interception will be done by these, without harm to the roof-mounted photovoltaic array.  Economic trade-off on the decision to invest in a lightning protection system during the life of the development project must also include intangible factors such as schedule delays and postmortem apologies for insufficient protection.

1.0  INTRODUCTION

This discussion is presented as an introductory guideline to alert system designers and provide a basic understanding of the phenomena governing the techniques of lightning protection.  No definitive numerical prediction is given at this time, pending availability of architectural details; an example of estimated interception rate is given for an assumed building in the Cleveland area.

A brief description is given of the lightning phenomena, as well as of the basic concepts which need to be understood for effective application of protective techniques.  Prevention of direct effects, that is, the effects associated with current flow in the system, to be avoided, is first discussed.  Indirect effects are also mentioned, and the document is completed by a bibliography for further reading by interested designers, and an Appendix discussing in more detail the history and rationale of the cone of protection concept.

2.0  LIGHTNING PHENOMENA

The phenomenon of lightning has been the subject of intensive study by many workers (see bibliography) and its behavior is fairly predictable in general terms, although the exact description of specific incidents is not predictable.  Protection against lightning effects includes two categories: direct effects concerned with the energy, heating, flash, ignition of the lightning current, and indirect effects concerned with induced overvoltages in nearly electrical and electronic systems.

Claims to the contrary notwithstanding, there is no conclusive evidence that lightning can be prevented.  Consequently, one has to design and implement a facility to recognize the possibility of a lightning strike, and take appropriate measures to make this strike harmless.  Lightning protection is then an approach where one can make the proper moves if the characteristics of the enemy are anticipated.

Two concepts must be understood to apply effective lightning protection devices: the "cone of protection" and the "striking distance." These will be discussed with some detail in the following pages.  Other fundamentals of electricity such as the impedance of a circuit to fast-changing currents impulses are assumed familiar to the reader.

We will first review current theories on the formation of lightning, then go on to the concept of the cone of protection and striking distance.  The following descriptions are based on the work and papers of Fisher, Cianos & Pierce, and Golde.

2.1  Generation of the lightning flash

The energy that produces lightning is provided by warm air rising upward into a developing cloud.  In detail, several theories vary, but all are based on the observed evidence that the cloud,, except for the top, is negative, with a small body of positive charge near the front base of the cloud.  Figure 2.1 shows a typical cloud distribution of charges; the solid lines represent the direction of the air movement in the cloud, with the cloud moving from right to left.  As the cloud passes over a point on the ground, an electrical charge is attracted under the cloud on the ground.  The average electric field at the surface of the ground will change from its fair-weather value of about 300 volts/meter to several thousand volts/meter.  The gradient will be concentrated around sharp protruding points on the ground, and can exceed the breakdown strength of air, typically 30 kV/cm.

However, the first significant event toward formation of a lightning flash occurs at the cloud.  A slow-moving column of ionized air forms at the cloud, called pilot streamer, moving by steps of 30 to 50 meters, and followed by a more intense discharge called step-leader, because of the discontinuous process of ionization and filling of the column with charged particles.

The step-leader does not move in straight line towards the ground, but seeks out the path with least electrical resistance, producing the familiar zig-zag pattern of the final stroke, with branches as several paths may be formed in the process of searching a weak path.  The interval between the successive steps is about 50 microseconds, allowing progressive build-up of charges on the ground as the charged column advances toward the ground.  Finally, a stage is reached with the step-leader being one step only away from the ground, when the last step is completed, either by continuation of the process, or by meeting a leader of positive charges originating from the ground.  We will discuss the implications of this in some detail in the section dealing with the striking distance concept.

With the path now completed, a positive charge then flows upward from the ground into the negative channel left in the wake of the step-leader, neutralizing the charge in this channel and moving at roughly one third of the speed of light.  This is what constitutes the lightning stroke, carrying the current at peaks of 1000 to 100,000 amperes, with a decrement to half-value in the order of 50 microseconds.  The first one of these which occurs in a flash is called the return stroke.

The first return stroke neutralizes the ionized column as well as a small pocket of changes in the cloud; a second or more return strokes, sometimes called re-strikes or subsequent strokes, can take place, using the same ionized channel, but moving much faster.  Thus, a series of strokes, such as shown in Figure 2.2, can occur in an interval in the order of a second.  Each of these strokes increases from a very low quiescent value to a very high amplitude in a very short time, resulting in rates of current change up to 1 x 1011  amperes/second.

When very tall objects are present, a step-leader can actually originate from this object, and travel upward to the cloud,, rather than the more general case of downward-moving leader.  Subsequent charges, however, will be similar, that is, move in the ionized channel left by the first discharge.

In addition to the short (tens of microseconds) discharges just described, a low amplitude current can exist between the individual strokes.  Although low in amplitude (a few hundred amperes), the long duration of this continuing current (tens to hundreds of milliseconds) is significant because of its total charge, resulting in most of the burning and metal-melting effects of a lightning flash.

The wave form and amplitude of lightning stroke and continuing currents vary over such a wide range that information has to be presented in statistical form; Cianos & Pierce have published a comprehensive set of statistics, from which the data of Figures 2-3 through 2-8 are derived, giving the reader a feel for the orders of magnitude involved.

2.2  Frequency of occurrence

One of the major factors to consider in determining the probability of lightning damage, and thus the need for strong protection, is the number of lightning flashes to earth in a given area for a given time.  This is not generally available, and instead the number of "thunderstorm days" is quoted.  However, this does also include the cloud-to-cloud discharges, and does not represent an accurate parameter, since it does not include the duration and intensity of each storm.  Progress is being made in improved statistics, but these are not yet available, and therefore the "isokeraunic level" maps, showing the number of storm-days per year, is still the most widely used description of the occurrence distribution.  An empirical equation has been derived, relating the density of flashes to ground and the number of storms per year, as follows:

density in flashes per km2  per year:	D

thunderstorm-days per year:   		T

D = 0.02 Tl,6

This corresponds to approximately 1 flash per year per km2  at an isokeraunic level of 10, and 10 flashes per year per km2  at a level of 40.

The significance of this situation is that, contrary to some popular beliefs, the density of lightning flashes, on the average, is independent of terrain.  However, detail of the ground objects (trees, buildings, hills) will produce a bias in the local distribution of this average.

2.3  Striking distance

This distribution at the local scale is determined by the final stages of the step-leader coming from the cloud, so to speak, without knowing what it will find on the ground.  Thus the actual point of termination can be somewhat controlled,, while the probability of a given area to receive a lightning stroke cannot.  This is where the concept of the striking distance, as explained by Golde, becomes very useful.

As the step-leader has approached the ground in the haphazard path described above, the point is reached where one more strike in the discontinuous process will close the path.  The distance between the top of the leader and the object about to be struck (or about to emit the meeting leader) is called striking distance.  The length of this distance is affected by the field established by the leader, which in turn is determined by the amount of charges existing in the ionized channel coming from the cloud.  With large charges in the channel, the field is more intense, so that breakdown can for longer distances, while a shorter distance is necessary to produce breakdown for the weaker fields established by smaller charges.  Figure 2-9 shows the relationship between the stroke current (which reflects the charge existing in the ionized channel) and the striking distance, as computed by Golde.

For instance, an average lightning current of 25 kA would correspond to a striking distance of 40 meters.  Thus, for an average stroke, details of the terrain do not affect the point of termination of the stroke beyond this distance, but only within this distance will there be a race, or a competition, as to which point will receive the flash, or invite it by sending a meeting streamer.  Conversely, very low amplitude flashes have an even shorter striking distance, meaning that they will ignore "attractive" points of termination, explaining some of the more puzzling exceptions to the generally assumed effect of tall-structures, rods, etc.  In other words, once a lightning step-leader has approached the ground within just short of the striking distance, no amount of devices beyond the striking distance will have any effect on the occurrence of the stroke, just the details of the area within the striking distance will determine the point of termination; the area is committed to receive the stroke, and it is now up to the humans controlling the shape of the objects on the ground to provide a least harmful point of termination, and make it most attractive to the approaching leader ("take me to your leader"...)

A number of photographs have been collected, and reported in the literature, showing a lightning flash approaching the ground in a somewhat wandering but generally downward direction, but with a sharp "turn" near the lower part of the path.  This, according to the striking distance just described, can be readily explained as being the point where the downcoming step-leader met the upcoming leader from the ground.  A photograph of a particularly clear occurrence of this will be found in the Appendix.

We are now ready to tackle the concept of the "cone of protection," having understood how the striking distance concept can explain some of the otherwise unexplained exceptions to the generally accepted and verified protection afforded by projecting objects, natural or artificial.

  - Cone of protection

From the days of Benjamin Franklin, the concept of a cone of protection has been used to provide effective protection of objects within the cone.  Briefly, this concept states that objects contained within a cone of 1:1 or 1:2 ratio of height to radius (Figure 2-10) will not receive the lightning stroke, but that the object at the apex of the cone will.  In the elementary concept, only one projecting object above a ground plane is being considered; in most practical situations involving buildings, multiple cones will be or should be considered.

Historically, a 1:2 cone was considered acceptable.  However., some exceptions to the "rule" of protection (as if Zeus should abide by "rules") have recently led to a more conservative use of a 1:1 cone of protection; the exceptions can be explained by the striking distance concept, as we shall now see.

Classical "cone of protection" rule for the building shown in Figure 2-11 would assure that the lightning mast shown provides dependable protection for the building against an approaching step-leader.  However, if we consider the striking distance shown by the circles, at each step of the leader advance, we can see that the leader will have ignored the lightning mast, and that at the fateful last decision point D, the shortest distance is to the corner of the building within the "cone of protection," rather than to ground, even less to the lightning mast.  The path drawn here also exhibits the tell-tale sharp inflexion of the last step mentioned above and often photographed.

By contrast, the step-leader drawn in Figure 2-12 for the case of a stroke with higher prospective intensity, and thus longer striking distance, will terminate at the lightning mast, starting from the same point "A" of its path.  This corresponds to the classical cone of protection situation; it implies that the step-leader can find within its striking distance a point of termination which is intentional,, rather than an object which happens to be close enough and shaped in a manner promoting the initiation of a streamer which will "win" the race to meet the step-leader.

3.0   DIRECT EFFECTS

3.1  Conduction of current to ground

We have now reached the state where lightning has struck and have seen that it may strike in some rather unexpected (and unprotected) locations, and are faced next with an evaluation of the effects of the stroke and continuing current flow.  In the case of a roof-top array of voltage-sensitive cells, the real story begins with the flow of current below the first metallic termination point.  Therefore, lightning protection in this context will mean making sure that the lightning does terminate where we want it to terminate, and that from there it is led to earth in an acceptable manner, along a safe, controlled path.

The most important consideration is then what happens to the potential drop along the current path to ground.  We have seen that the current increases very rapidly on the front of the wave.  Therefore the inductive drop L di/dt over the current path will be extremely large, in other words, during initial phase of the discharge, the "grounded" lightning rods and downcomers of a building network will be elevated to substantial potentials above earth ground, in the order of tens or hundreds of kilovolts.  Any circuitous path in the downcomer will increase this voltage drop, with the attendant risk that a flashover may occur to bridge and shorten this path, defeating the intent of carrying the current directly to earth, away from the array.

Another consideration is the difference of potential established during the initial phase, when the current increases at extremely fast rates, between the lightning system and the cell array.  The upper portions of the downcomers are elevated at very high potential because of the inductive drop, while the upper metallic parts of the array remain uninvolved in the current path, and therefore remain at "ground" potential.  We are writing "ground" in quotes as this is an arbitrary definition in the context of potential distribution during a lightning stroke.

With reference to Figure 3-1, the "ground" point can be represented as the common point "G" at which the electric power system of the house is tied to the downcomer conductors; any further impedance below point "G" and "true" earth is not relevant to the difference of potential V established across the wall of the building at point A. If the length (inductance) between points B and G is large, and the distance between A and B small, the voltage V will exceed the dielectric strength of the AB gap, and a "side flash" will occur between A and B, with possible disastrous effect.

3.2  Design of the air terminals

Protection of an experimental roof-top array is different from the protection to be provided, if any, for future mass-produced arrays.  In the case of the experimental system, the high cost of a lightning strike should prevail over aesthetic considerations, so that the objective will be to maximize protection.  Once the cost of the roof array is established as a commercial product, the trade off between economics and aesthetics will be quite different.  In this discussion., however, we are addressing the case of the experimental house.

There are two basic approaches to providing sufficient protection: lightning masts, at some distance from the house, with sufficient height to provide an effective cone of protection, and lightning conductors above the roof.  Neither can provide absolute protection against all possible strikes; however, the likelihood of a strike attaching to the roof-mounted array will be decreased by several orders of magnitude if a properly designed system is installed.

3.2.1  Lightning masts

The discussion of paragraph 2.4 above, and the possible exception to the protection expected for a strict interpretation of the cone of protection formula, give some guidance on the design of a mast system.  For the experimental model, two masts at minimum are recommended, with four being even more effective. (In the case of a project involving a group of closely spaced houses, it may be possible to provide a common mast at each lot boundary.  Figure 3-2 shows how such a mast system can be implemented.  One of the advantages would be complete independence of the power system and lightning system at all but one point.

3.2.2  Lightning conductors

A possibly more effective protection can be expected from a lattice of lightning conductors strung some distance above the roof.  The number of conductors, and the distance from the roof are in inverse proportions.  Therefore, there is a possible trade-off between a few conductors high above the roof, and many conductors close to the roof.  The boundaries of the trade-off correspond to the situation where the many conductors would be so close to the roof that side-flash becomes a problem, or where only a few, very distant conductors would allow a low-amplitude stroke, with attendant short striking distance, travel around the theoretical cone of protection, as discussed in paragraph 2.4.

In any case, the down conductors for the cable lattice have to be routed far enough away from the roof to prevent any side flash.  Figure 3.3 shows a possible arrangement for a cable lattice system.

4.0  INDIRECT EFFECTS

4.1  Indirect voltages

The major indirect effect of lightning strokes for this project is the voltage induced on the power system by the rapidly changing magnetic flux associated with the high di/dt of the lightning current.  A less important but still significant effect would be the voltage produced by electrostatic coupling between the roof array and the charges associated with atmospheric electricity.

Typical lightning strokes involve currents of 50 kA reaching crest in 1 microsecond.  Thus, the do//dt near the lightning conductors will be quite high and capable of inducing destructive voltages in any loop which would link a substantial flux from the lightning current.  Therefore, the power system, cell array and control circuits must be designed to minimize intrinsic coupling, or be suitably shielded.

4.2  Effect on incoming power system

There is a certain amount of information available from various sources on the magnitude of transient overvoltage entering a house wiring system by the route of the utility service.  While not exhaustive, the data collected so far have indicated that transients up to 6 kV can occur, infrequently, but still often enough to cause concern for sensitive electronics.  This problem of course is not unique to photo-voltaic systems, but is faced by every appliance manufacturer.

In the present case, recognition of the problem is all that is necessary since there is a wide variety of commercial devices available to suppress these surges.

5.0  FLASH INTERCEPTION RATE

The relationship between annual thunderstorm days and flash density has been defined by empirical formulae and plotted by Cianos & Pierce.  Table 5-1 shows the computed ground flash density, obtained by multiplying the flash density by a factor relating the ground flashes to the total flashes. This  factor  depends  on  the  latitude,  as  suggested  by  Cianos & Pierce.

Using the cone of protection concept in reverse, we can estimate that the effective area of  an object protruding over the ground surface, in attracting a strike, increases as its height increases.  For a height h, a circle of radius 2h can be considered as candidate for flash interception.  Thus, assuming a building of 45 feet (15 m) x 30 ft (10m), with a height of 30 ft (10 m), the effective area is indicated by the sketch of Figure 5-1.  The area corresponding to an  elongated double cone originating from a roof antenna on one side and the peak of the roof on the other side, at a 2:1 angle, is approximately

50 m x 50 m = 2500 m2 = 0. 0025 km2.

Applying the ground flash density of Table 5-1 for an isokeraunic level of 40 (see map of Figure 5-2), we obtain an estimated interception rate of  0.0025 x  2.1  =  0.005 flashes per year on the area covered by the house and its associated cones.

In other words, the house in this example can be expected to intercept a lightning strike once every two hundred years.  This prediction would be based on a house projecting above flat terrain, which we understand to be the case here.  One must bear in mind that in the absence of adjacent, overlapping cones of protection from other buildings, trees or structures, the house and its cones can be treated as completely independent from the surroundings.  On the other hand, hill tops and elevated details of the terrain can affect the local isokeraunic level upward, while depressed locations will affect it downward.

A simple trade-off based on economics would then consist in stating that for an estimated repair cost of say, $ 200 000, and a project life of two years, the break-even value of a lightning protection system is 20000 x 0.005 x 2 = $ 2000.  However, this trade-off undoubtedly would be modified to take into consideration the "utility" concept in a game plan.  This concept introduces subjective factors which tend to magnify the perceived cost of a failure, but decrease the perceived cost of a desired event.  Stated in other terms, a trade-off in this project must also take into consideration intangible factors such as delays in the study and the embarrassing situation of a major failure caused by a single lightning strike.

Therefore we submit that a well designed lightning protection system, at this time divorced from aesthetic considerations, would be a sound investment.  This situation may change when the cost of the arrays will be lower, giving greater weight to aesthetics.

6.0 BIBLIOGRAPHY

Cavendish, H. , Watson, W. , Franklin, B. , and Robertson, J. "Report of the Committee Appointed by the Royal Society to Consider a Method of Securing the Powder Magazines at Purfleet, Philosophical Transactions of the Royal Society (London, England), vol. 63, 1773, and vol. 68, 1777.

Walter, B., "Uber die Schutzwirkung von Fernblitzableitern und die Blitzchlaghaufigbeit in einigen Grosstadten, " Deutsche offentlichrechtliche Versicherung, no. 18, 1935.

Mc Cann, G. D., "The Measurement of Lightning Currents in Direct Strokes, " AIEE Transactions, vol. 63, 1944.

Golde, R. H. , "The Frequency of Occurrence and the Distribution of Lightning Flashes to Transmission Lines, " AIEE Transactions, vol. 647 1945.

Lewis, W. W. , The Protection of Transmission Lines Against Lightning, John Wiley, New York, 1950.

Westinghouse Electric Corp. , Electrical Transmission and Distribution Reference Book, Chapter 16, East Pittsburgh, Pa. , 1950.

Hagenguth, J. H. and Anderson, J. G. , "Lightning to the Empire State Building - Part III, "AIEE Transactions, vol. 71, Part III (Power Apparatus and Systems), August 1952.

British Standard Code of Practice CP 326:1965, "The Protection of Structures Against Lightning, " British Standards Institution, British Standards House, 2 Park Street, London, W. I.

Golde, R. H. , "The Lightning Conductor, " Journal of the Franklin Institute, vol. 283, No. 6, June 1967.

Berger, K., "Novel Observations of Lightning Discharges: Results of Research on Mount San Salvatore, " Journal of the Franklin Institute, vol. 283, No. 6, June 1967.

Blitzschutz, Eighth Edition, VDE-Verlag Gmbh., 1 Berlin 12, Bismarckstrasse 33.

Cianos, N. and Pierce, E. T. I "A Ground-Lightning Environment for Engineering Usage, " Stanford Research Institute Technical Report 1, August 1972.

Golde, R. H. , "Lightning Protection, " Edward Arnold Pub. , London, 1973.

Lightning Protection Code, 1975, NFPA-78, National Fire Protection Association, 60 Batterymarch St. , Boston, Mass. 02110.

The Protection of Industrial Electronics

and Power Conversion Equipment

Against Power Line and Data Line Disturbances

François D. Martzloff, Fellow IEEE

Corporate Research and Development

General Electric Company

Schenectady, New York

# Abstract

The irresistible trend toward distributed computing systems for the control of industrial power electronic equipment is adding new dimensions to the old problem of surge protection. Harmful surges may be produced by lightning, power switching, or by differences in ground potentials. The objective of the paper is to provide increased awareness and better understanding of the fundamentals of protection as well as the characteristics of protective devices.

1.  Introduction

The continuing development of power conversion equipment, further promoted by the success of microelectronics in controlling this equipment, raises the question of vulnerability to surge voltages or surge currents appearing at the power or control input terminals of the equipment. The very origin of these surges (lightning, switching, electrostatic discharges) makes it somewhat difficult to predict with accuracy their characteristics, so that surge protection has sometimes been presented as "art rather than science." There is, however, enough practical experience and data available to apply good engineering judgment in developing an understanding of the practical aspects of surge protection based on fundamental concepts and on protective device characteristics. The present paper is offered as a contribution toward better surge protection, neither as an art nor as a science, but as a no-nonsense, sound, and cost-effective engineering practice.

The paper presents first a discussion of the various and complex origins of lightning and switching surges electrostatic discharges are acknowledged but not addressed in a limited space discussion). The paper also shows how standards can help simplify the application of protection. A brief discussion is given on aspects of the propagation of these surges, followed by a presentation of some fundamental approaches to protection. Basic characteristics of protective devices are outlined. Three examples are given on how this knowledge and engineering judgment can be applied to answer specific questions and to avoid pitfalls.

2.  The Origins of Transient Overvoltages

Transient overvoltages in power systems originate from one cause, energy being injected into the power system, but from two sources: lightning discharges, or switching within the 'power system. In communication or data systems, there is another source of transients: the coupling of power system transients into the system. Furthermore, all systems involving several connections to the environment have the potential risk of transient overvoltages associated with ground potential rise during the flow of surge currents. As stated previously, static discharge problems are not treated in this paper.

Lightning discharges may not necessarily mean direct termination of a lightning stroke onto the system. A lightning stroke terminating near a power line, either by hitting a tall object or the bare earth, will create a very fast-changing magnetic field that can induce voltages - and inject energy - into the loop formed by the conductors of the system. Lightning can also inject overvoltages in a system by raising the ground potential on the surface of the .earth where the stroke terminates, while more distant "ground" points remain at a lower voltage, closer to the potential of "true earth." The literature provides information on the characteristics of lightning discharges [1-6].

Surges from power system switching create overvoltages as a result of trapped energy in loads being switched off, or of restrikes in the switchgear. These will be examined in greater detail in the following paragraphs.

2.1  Transients in Power Systems

A transient is created whenever a sudden change occurs in a power circuit, especially during power switching - either the closing or opening. It is important to recognize the difference between the intended switching (the mechanical action of the switch) and the actual happening in the circuit. During the closing sequence of a switch, the contacts may bounce, producing openings of the circuit with reclosing by restrikes and reopening by clearing at the high-frequency current zero. Pre-strikes can also occur just before the contacts close, with a succession of clearings at the high” frequency current zero, followed by restrikes. Similarly, during an .opening sequence of a switch, restrikes can cause electrical closing(s) of the circuit.

Simple switching transients [7] include circuit closing transients, transients initiated by the clearing of a short circuit, and transients produced when the two circuits on either side of the switch being opened oscillate at different. frequencies. In circuits having inductance and capacitance (all physical circuits have at least some, in the form of stray capacitance and inductance) with little damping, these simple switching transients are inherently limited to twice the peak amplitude of the steady-state sinusoidal voltage. Without a surge protective device, the current flowing just before switching is available to charge the circuit capacitances at whatever voltage is required to store the inductive energy of the current by converting it into capacitive energy.

Several mechanisms are encountered in practical power circuits that can produce transient overvoltages far in excess of the theoretical twice-normal limit mentioned above. Two such mechanisms occur frequently: current chopping and restrikes, the latter being especially troublesome when capacitor switching is involved.

A similar scenario can unfold when an ungrounded power system experiences an arcing ground fault. The switching action is then not the result of a deliberate parting of contacts but the intermittent connection produced by the arc.

These switching overvoltages, high as they may be, are somewhat predictable and can be estimated with reasonable accuracy from the circuit parameters, once the mechanism involved has been identified. There is still some uncertainty as to where and when they occur because the worst offenders result from some abnormal behavior of a circuit element. Lightning-induced transients are much less predictable because there is a wide range of coupling possibilities.

In response to these concerns, various committees and working groups have attempted to describe ranges of transient occurrences or maximum values occurring in power circuits. Three such attempts are described in the next section. Figures 1, 2, and 3 show typical examples of transients recorded in power systems.

3.  Standards on Transient Overvoltages in Power Lines

Several standards or guides have been issued or proposed in Europe and in the United States, specifying a surge withstand capability for specific equipment or devices and specific conditions of transients in power or communication systems. Some of these specifications represent early attempts to recognize and deal with the problem in spite of insufficient data. As a growing number of organizations address the problem and a$ exchanges of information take place, improvements are being made in the approach. Three of these are briefly discussed here.

3.1  The IEEE Surge Withstand Capability Test (SWC) [8]

One of the earliest published documents which addressed new problems facing electronic equipment exposed to power system transients was prepared by an IEEE committee dealing with the exposure of power system relaying equipment to the harsh environment of high-voltage substations.

Because this useful document was released at a time when little other guidance was available, users attempted to apply the recommendations of this document to situations where the environment of a high-voltage substation did not exist. The revised version of this standard, soon to be issued, recognizes the problem and attempts to be more specific (and restrictive) in its scope. Thus, an important consideration in the writing and publishing of documents dealing with transients is a clear definition of the scope and limitations of the application.

3.2  The IEC 664 Report [9]

The Insulation Coordination Committee of IEC included in its report a table indicating the voltages that equipment must be capable of withstanding in various system voltages and installation categories' (Table I). The table specifies its applicability to a controlled voltage situation, which implies' that some surge-limiting device has been provided - presumably a typical surge arrester with. characteristics matching the system voltage in each case. The waveshape specified for these voltages is the 1.2/50 s wave, a specification consistent with the insulation withstand concerns of the group that prepared the document. No source impedance is indicated, but four "installation categories" are specified, each with decreasing. voltage magnitude as the installation is further removed from the outdoor environment. Thus, this document primarily addresses the concerns of insulation coordination; the specification it implies for the environment is more the result of efforts toward coordinating levels than efforts to describe the environment and the occurrence of transients. The latter approach has been that of the IEEE Working Group on Surge Voltages in Low-Voltage AC Power Circuits, which will be reviewed in detail.

3.3 The IEEE Guide on Surge Voltages (ANSI/IEEE Std 62.41:1980) [10]

3.3.1  Voltages and Rate of Occurrence. Data collected from a number of sources led to plotting a set of lines representing a rate of occurrence as a function of voltage for three types of exposures (Figure 4). These exposure levels are defined in general terms as follows:

- Low Exposure - Systems in geographical areas known for low lightning activity, with little load switching activity.

- Medium Exposure - Systems in geographical areas known for high lightning activity, with frequent and severe switching transients.

- High Exposure - Rare, but real, systems supplied by long overhead lines and subject to reflections at line ends, where the characteristics of the installation produce high sparkover levels of the clearances.

The two lower lines of Figure 4 have been drawn at the same slope since the data base shows reasonable agreement among several sources on that slope. All lines may be truncated by sparkover of the clearances, at levels depending on the withstand voltage of these clearances. The high exposure line needs to be recognized, but it should not be indiscriminately applied to all systems. Such application would penalize the vast majority of installations where the exposure is lower.

The voltage and current amplitudes presented in the Guide attempt to provide for the vast majority of lightning strikes but none should be considered "worst case," as this concept cannot be determined realistically. It is necessary to think in terms of the statistical distribution of strikes, and to accept a reasonable upper limit for most cases. Where the consequences of a failure are not catastrophic but merely represent an annoying economic loss, it is appropriate to make a tradeoff of the cost of protection against the likelihood of a failure caused by a high but rare surge.

3.3.2  Waveshape of the Surges. Many independent observations [11, 13] have established that the most frequent type of transient overvoltage in ac power systems is a decaying oscillation, with frequencies between 5 and 500 kHz. This finding is in contrast to earlier attempts to apply the unidirectional double-exponential voltage wave that is generally described as 1.2/50. Indeed, the unidirectional voltage wave has a long history of successful application in the field of dielectric withstand tests and is representative of the surges propagating in power transmission systems exposed to lightning. In order to combine the merits of. both waveshape definitions and to specify them where they are applicable, the Guide specifies an oscillatory waveshape inside buildings, a unidirectional waveshape outside buildings, and both at the interface (Figure 5).

The oscillatory waveshape simulates those transients affecting devices that are sensitive to dv/dt and to voltage reversals during conduction [14), while the unidirectional voltage and current waveshapes, based on long-established ANSI standards for secondary valve arresters, simulate the transients where energy content is the significant parameter.

3.3.3  Energy and Source Impedance. The energy involved in the interaction of a power system with a surge source and a surge protective device will divide between the source and the protective device in accordance with the characteristics of the two impedances. In a gap type protective device, the low impedance of the arc after sparkover forces most of the energy to be dissipated elsewhere, e.g., in a resistor added in series with the gap for limiting the power-follow current, or on the impedance of the circuit upstream of the protective device. In an energy-absorber protective device, by its very nature, a substantial share of the surge energy is dissipated in the suppressor, but its clamping action does not involve the power-follow energy resulting from the short-circuit action of a gap. It is therefore essential to the effective use of surge protective devices that a realistic assumption be made about the source impedance of the surge whose effects are to be duplicated.

Unfortunately, not enough data have been collected on what this assumption should be for the source impedance of the transient. Standards and recommendations, such as MIL STD-1399 or the IEC 664 report, either ignore the issue or indicate values applicable to limited cases, such as the SWC test for high-voltage substation equipment. ANSI/IEEE Std C62.41-1980 attempts to relate impedance to categories of locations but unavoidably remains vague on their definitions (Table 2).

3.3.4  New Reports on Transient Occurrence. The importance of defining the environment has motivated a number of workers to install recording devices on their power systems, and thus created a market for commercial transient recorders in the last several years. Unfortunately, at least one such recorder contains a surge suppressor in its own power supply (Figure 6).

Consequently, if the line being monitored is that in which the analyzer has its power cord plugged, the transients that occurred on the line before the analyzer was installed disappear. This irony makes my facetious remark of 1969, “. . .the best surge suppressor is a surge monitor.” [12] the truth. Therefore, some of the recently published surveys on the occurrence of surges may show a lower number of surges than actually occur, and therefore data should be examined with caution until the ambiguity caused by this cord-connected suppressor is resolved.

--------------------------

* Note the difference between surge impedance of the line. also called characteristic impedance, and the impedance to the surge. Z1 of Figure 8. defined in terms of R. L. C at the frequency corresponding to the surge.

4.  Surge Propagation

4.1  The Limitations of Arbitrary Division into Categories

The standards cited in the preceding paragraphs describe surges which may be expected at specific points of a wiring system; the implication is that the surges will proceed downstream, at the same amplitude, until some interface somehow produces a decrease in amplitude down to the next lower level of voltage or to the next lower level of current specified by the next downstream category (Figure 7).

This staircase representation is useful to simplify the real world into a manageable set of assumptions. but it is a simplification that can mask the reality. Surges will propagate in the system starting at the point of entry: voltage surges will be attenuated to the extent that the series impedance between the point of interest and the source (Z1, Figure 8) and the shunt impedance (Z2). form a voltage. divider. If the series impedance is low and the shunt impedance is high (light loading of the system), the voltage divider does not produce high attenuation of the voltage surge's. Conversely, current surges, if they are the result of a current source such as a lightning strike, will produce high voltages unless a low-impedance diverting path is offered to the flow of current. If the current surge in a system is the result of a combined current source and multi path to ground (Figure 9), there is then a division of the current among the paths that is governed by the inverse ratio of the impedances. If a user has control over only one of the paths, he can decrease the amplitude of the current surge in his path only by forcing ,a greater share of the total current to flow through the other paths: thus, surge blocking is likely to be an exercise in passing the problem from one point of the system to another. The solution lies in surge diversion, offering to the surge a path where the current flow can occur harmlessly.

4.2  The Limitations of Transmission Line Analysis

In qualitative discussions of surge propagation. the classical behavior of a transmission line is often called upon to provide explanations of the situation. In particular, the theoretical reflections occurring at the end of a line are cited: doubling the impulse if the line is open-ended, returning an inverse impulse if the line is shorted. However, these discussions sometimes lose sight of the fact that the concept can be applied only if the line length is sufficient to contain all of the surge front. If the surge has a rise time longer than the propagation time along the line, the point is moot and, by the time the surge reaches its peak, the voltage at the receiving end of the line does not differ from the voltage applied at the sending end. Figure 10 illustrates this situation showing the voltage at the sending end (SD) and the voltage at the receiving end (RC) of a conduit-enclosed three-wire line (B: black or phase conductor, W: white or neutral conductor, G: green or grounding conductor). There is a minor difference during the rise, where the initial front is doubled at the receiving end, but the crests are the same. Thus, for many installations in buildings, the line lengths are short compared to the length required to contain, say, a 1 s front traveling at a typical speed of 200 m/s.

A more detailed report describing some of the aspects of the propagation of surges and their implications is given in Reference 15.

4.3  Common Mode or Normal Mode?

Another aspect of the propagation of surges concerns the dichotomy normal mode/common mode. In other words, the issue is whether significant surges occur line-to-line (black-to-white, or phase-to. neutral), the situation described by "normal mode," or whether they occur between any - or both - of the lines and ground (black-to-green, white-to-green, or [black-and-white]-to-green) , the situation described by "common mode."

The answer to that dichotomy is that, in most cases, both modes must be considered, since one often converts into the other, depending upon the coupling, the wiring practices, and the attempts made at suppressing the mode perceived as the greatest threat. Here again, the pervasive and pervert reality is too often that a solution aimed at suppressing one effect only displaces the problem. Examples 1 and 2, in the Appendix, show how controversies on the method of suppressing a surge assumed to occur between two wires can lead to partial or misleading solutions when the realities of the situation are not recognized.

5.  Fundamental Protection Techniques

The protection of a power conversion system or an electronic black box against the threats of the surge environment can be accomplished in different ways. There .is no single truth or magic cure ensuring immunity and success, but, rather; there are a number of valid approaches that can be combined as necessary to achieve the goal. The competent protection engineer can contribute his knowledge and perception to the choice of approaches against a threat which is imprecise and unpredictable, keeping in mind the balance between the technical goal of maximum protection and the economic goal of realistic protection at an acceptable cost. However, just as in the case of accident insurance, the cost of the premium appears high before the accident, not after.

A discussion of fundamental protection techniques that is limited in space and scope has the risk of becoming an inventory of a bag of tricks; yet, there are a few fundamental principles and fundamental techniques that can be useful in obtaining transient immunity, especially at the design stages of a computer system or circuit. All too often, the need for protection becomes apparent at a late stage, when it is much more difficult to apply the fundamental techniques which are most effective and economical when implemented at the outset.

5.1  Basic Techniques

Protection techniques can be classified into several categories according to the purpose and the system level at which the engineer is working. For the system as a whole, protection is primarily a preventive effort. One must consider the physical exposure to transients - in particular, the indirect effects of lightning resulting from building design, location, physical spread, and coupling to other disturbance sources - as well as such inherent susceptibility characteristics as frequency response and nominal voltage. A system depending on low-voltage signals, high-impedance circuits, and installed over a wide area would present much more serious problems than the same system confined to a single building or a single cubicle.

For the system components or electronic black boxes, the environment is often beyond the control of the designer or user, and protection becomes a curative effort - learning to live and survive in an environment which is imposed. Quite often this effort is motivated by field failures, and retrofit is needed. The techniques involved here tend to be the application of protective devices to circuits or a search for inherent immunity rather than the elimination of surges at their origin.

Another distinction can be made in classifying protective techniques. While surges are unavoidable, one can attempt to block them, divert them, or strive to withstand them; the latter, however, is generally difficult to achieve alone.

5.2  Shielding, Bonding, and Grounding

Shielding, bonding, and grounding are three interrelated methods for protecting a circuit from external transients. Shielding consists of enclosing the circuit wiring in a conductive enclosure, which theoretically cancels out any electromagnetic field inside the enclosure; actually, it is more an attenuation than a cancellation. Bonding is the practice of providing low-impedance connections between adjacent metal parts, such as the panels of a shield, cabinets in an electronic rack, or rebars in a concrete structure. Grounding is the practice of providing a low impedance to earth, through various methods of driving conductors into the soil. Each of these techniques has its limitations, and each can sometimes be overemphasized. Many texts and papers discuss the subject at length, so that a detailed discussion is not necessary here, with one exception. which follows.

5.3  Ground One End or Both Ends of the Shield?

Shielding conductors by wrapping them in a grounded sheath or shielding an electronic circuit by enclosing it in a grounded conductive box is a defensive measure that occurs very naturally to the system designer or the laboratory experimenter anticipating a hostile electromagnetic environment. Difficulties arise, however, when the concept of "grounded" is examined in detail. Difficulties also arise when the goals of shielding for noise immunity conflict with the goals of shielding for lightning surge immunity.

A shield can be the size of a matchbox or an airplane fuselage; it can cover a few inches of wire, or miles of buried or overhead cables. Grounding these diverse shields is not an easy thing to do because the impedance to earth of the grounding connection must be acknowledged. The situation is made even more controversial because of the conflict between the often-proclaimed design rule "ground cable shields at one end only" - a rule justified by noise immunity performance. in particular common mode noise reduction - and the harsh reality of current flow and Ohm's law when lightning strikes.

The difficulty may be caused by a perception on the part of the noise prevention designers that the shield serves as an electrostatic shield in which longitudinal currents associated with common mode noise coupling should not flow. This concept is exemplified in the terminology of shielded cable users, when they describe the shield construction of some cable design as having a foil plus drain wire. as if there were electrostatic charges that needed to be removed (drained). Indeed, electrostatic charges can be drained by connecting only one end of the shield. Furthermore, if the two ends of the shield of a cable spanning some distance are connected to the local ground at each end, there is a definite possibility that some power frequency current may flow in the shield. For low-level signals, this current would produce noise (hum) in the signals. For that reason, many system designers will insist on the one-end-only grounding rule, and they are correct from that point of view. Sometimes the shield is used as a return path for the circuit, in which case shield currents can cause voltage drops added to the signal. But the fact is that, when surge currents flow near the circuits, they will unavoidably inject magnetic flux variations into the circuits, hence induced voltages. Worse yet, in the case of a lightning stroke injecting current into the earth in the area spanned by the one-end-only grounded shield, the potential of one end of the cable defined as "ground" is not the same as the "ground" at the other end of the cable. Very high voltages can be developed (Figure 11) between the floating end of the shield and the local ground. No practical insulation can withstand these levels, and breakdown will occur, allowing surge currents to flow in spite of the designers' intent to prevent them; the path of these currents will be determined by the components most likely to fail when the voltage rises - the low-level logic circuits, of course. In contrast, by deliberately allowing part of these surge currents to flow in the shields, one obtains a cancellation of the voltages that otherwise would be induced in the circuits, and the currents will follow a well-defined path that can be designed to provide harmless effects.

This conflict is actually very simple to resolve if recognized in time: provide an outer shield, grounded at both ends (and at any possible intermediate points); inside this shield the electronic designer is then free to enforce his single-point grounding rules. The only drawback to this approach is the hardware cost of double shields. In many installations, however, there is a metallic conduit through which the cables are pulled; with simple but close attention to maintaining the continuity of this conduit path, through all the joints and junction boxes, a very effective outer shield is obtained at negligible additional cost. In the case of underground conduit runs, the most frequent practice is  to use plastic conduit, which unfortunately breaks the continuity. System designers would be well advised to require metal conduits where the circuits are sensitive or, at a minimum, to pull a shielded cable in the plastic conduit where the shield is used to maintain continuity between the above-ground metal conduits. That additional cost, then, is the insurance premium, which is well worth accepting. Example 3 in the Appendix shows the consequence of the misapplied "ground one end only" rule.

6.  Transient Suppressors

Various devices have been developed for protecting electrical and electronic equipment against transients. They are often called "transient suppressors" although, for accuracy, they should be called "transient limiters," "clamps," or "diverters" because they cannot really suppress transients; rather, they limit transients to acceptable levels or make them harmless by diverting them to ground.

There are two categories of transient suppressors: those that block transients, preventing their propagation toward sensitive circuits, and those that divert transients, limiting residual voltages. Since many of the transients originate from a current source, .the blocking of a transient may not always be possible; thus, diverting the transient is more likely to find general application. A combination of diverting and blocking can be a very effective approach. This approach generally takes the form of a multistage circuit, where a first device diverts the transient toward ground, a second device - an impedance or resistance - offers a restricted path to the transient propagation but an acceptable path to the signal or power, and a third device clamps the residual transient (Figure 12). Thus, we are primarily interested in the diverting devices. These diverting devices can be of two kinds: voltage-clamping devices ,or short-circuiting devices (crowbar). Both involve some nonlinearity, either frequency nonlinearity (as in filters) or, more usually, voltage nonlinearity. This voltage nonlinearity is the result of two different mechanisms - a continuous change in the device conductivity as the current increases, or an abrupt switching as the voltage increases.

Because the technical and trade literature contains many articles on these devices, a discussion of the details will be limited. Some comparisons will be made, however, to point out the significant differences in performance.

6.1  Crowbar Devices

The principle of crowbar devices is quite simple: upon occurrence of an overvoltage, the device changes from a high-impedance state to a low-impedance state, offering a low-impedance path to divert the surge to ground. This switching can be inherent to the device, as in the case of spark gaps involving the breakdown of a gas. Some applications have also been .made of triggered devices, such as triggered vacuum gaps in high-voltage technology or thyristors in low-voltage circuits where a control circuit senses the rising voltage and turns on the power-rated device to divert the surge.

The major advantage of the crowbar device is that its low impedance allows (he flow of substantial surge currents without the development of high energy within the device itself; the energy has to be spent elsewhere in the circuit. This "reflection" of the impinging surge can also be a disadvantage in some circuits when the transient disturbance associated with the gap firing is being considered. Where there is no problem of power-follow (discussed below), such as in some communication circuits, the spark gap has the advantage of very simple construction with potentially low cost.

The crowbar device, however, has three major limitations. The first limitation concerns the volt-time sensitivity of the breakdown process. As the voltage increases across a spark gap, a significant conduction of current - and hence the voltage limitation of a surge - cannot take place until the transition occurs to the arc mode pf conduction, by avalanche breakdown of the gas between the electrodes. The load is left unprotected during the initial rise because of this delay time (typically in microseconds). Considerable variation exists in the sparkover voltage achieved in successive operations, since the process is statistical in nature. In addition, this sparkover voltage can be substantially higher after a long period of rest than after successive discharges. From the physical nature of the process, it is difficult to produce consistent sparkover voltage for low voltage ratings,

The second limitation is associated with the sharpness of the spark-over, which produces fast current rises in the circuits and, thus, objectionable noise. A classic example is found in oscillograms recording the sparkover of a gap where the trace exhibits an anomaly before the sparkover (Figure 13). This anomaly is due to the delay introduced in the oscilloscope circuits to provide an advanced trigger of the sweep. What the trace shows is the event delayed by a few nanoseconds, so that in real time, (he gap sparkover occurs and noise enters the oscilloscope by stray coupling while the electron beam is still writing the pre-sparkover rise.

A third limitation occurs when a power current from the steady-state voltage source follows' the surge discharge (follow-current, or power-follow). In ac circuits, this power-follow current mayor may not be cleared at a natural current zero: In dc circuits, clearing is even more uncertain. Additional means, therefore, must be provided to open the power circuit if the crowbar device is not designed to provide self-clearing action within specified limits of surge energy, system voltage, and power-follow current. This combination of a gap with a nonlinear varistor that limits the power-follow current has been very successful in the utility industry as a surge arrester or surge diverter.

  - Voltage-Clamping Devices

Voltage-clamping devices will exhibit a variable impedance, depending on the current flowing through the device or the voltage across its terminals. These components show a nonlinear characteristic - that is Ohm's law can be applied, but the equation has a variable R. Impedance variation is monotonic and does not contain discontinuities, in contrast to the crowbar device, which shows a turn-on action. As far as volt-ampere characteristics are concerned, these components are time-dependent to a certain degree. However, unlike the sparkover of a gap or the triggering of a thyristor, time delay is not involved.

When a voltage-clamping device is installed, the circuit remains essentially unaffected by the device before and after the transient for any steady-state voltage below clamping level. Increased current drawn through the device as the surge voltage attempts to rise results in voltage-clamping action. Nonlinear impedance is the result if this current rise is greater than the voltage increase. The increased voltage drop (IR) in the source impedance due to higher current results in the apparent clamping of the voltage. It should be emphasized that the device depends on the source impedance to produce clamping. A voltage divider action is at work where the ratio of the divider as not constant, but changing. If the source impedance is very low, the ratio is low, and eventually the suppressor could not work at all with a zero source impedance (Figure 14). In contrast, a crowbar-type device effectively short circuits the transient to ground; once established, however, this short circuit will continue until the current (the surge current as well as any power-follow current supplied by the power system) is brought to a low level.

The principle of voltage clamping can be achieved with any device exhibiting this nonlinear impedance. Two categories of devices, having the same effect but operating on very different physical processes, have found acceptance in the industry: polycrystalline varistors and single-junction avalanche diodes. Another technology, selenium rectifiers, has been practically eliminated from the field because of the improved characteristics of modern varistors.

6.3  Avalanche Diodes

Avalanche diodes, or Zener diodes, were initially applied as voltage clamps, a natural outgrowth of their application as voltage regulators. Improved construction, specifically aimed at surge absorption, has made these diodes very effective suppressors. Large diameter junctions and low thermal impedance connections are used to deal with the inherent problem of dissipating the heat deposited by the surge: in the small volume of a very thin single-layer junction.

The advantage of the avalanche diode, generally a P-N silicon junction, is the possibility of achieving low clamping voltage and a nearly flat volt-ampere characteristic over its useful power range. Therefore, these diodes are widely used in low-voltage electronic circuits for the protection of 5 or 15 V logic circuits, for instance. For higher voltages, the heat generation problem associated with single junctions can be overcome by stacking a number of lower voltage junctions.

6.4  Varistors

The term varistor is derived from its function as a variable resistor. It is also called a voltage-dependent resistor, but that description tends to imply that the voltage is the independent parameter in surge protection. Two very different devices have been successfully developed as varistors: silicon carbide disks have been used for years in the surge arrester industry, and more recently, metal oxide varistor technology has come of age.

Metal oxide varistors depend on the conduction process occurring at the boundaries between the large grains of oxide (typically zinc oxide) grown in a carefully controlled sintering process. The physics of the nonlinear conduction mechanism have been described in the literature [16-20].

Because the prime function of a varistor is to provide the nonlinear effect, other parameters are generally the result of tradeoffs in design and inherent characteristics. The electrical behavior of a varistor can be understood by examination of the equivalent circuit of Figure 15. The major element is the varistor proper, Rv, whose V -I characteristic is assumed to be the perfect power law I = kV". In parallel with this varistor, there is a capacitor, C, and a leakage resistance, Rp. In series with this three-component group, there is the bulk resistance of the zinc oxide grains, Rs, and the inductance of the leads, L.

Under de conditions, at low-current densities because obviously no varistor could stand the high energy deposited by de currents of high density, only the varistor element and the parallel leakage resistance are significant. Under pulse conditions at high-current densities, all but the leakage resistance are significant: the varistor provides low impedance to the flow of current, but eventually the series resistance will produce an upturn in the V -I characteristic; the lead inductance can give rise to spurious overshoot problems if it is not dealt with properly; the capacitance can offer either a welcome additional path with fast transients or an objectionable loading at high frequency, depending on the application.

6.4.1  V-I Characteristic. When the V -I characteristic is plotted on a log-log graph, the curve of Figure 16 is obtained. Three regions result from the dominance of Rp, Rv, and Rs as the current in the device goes from nanoamperes to kiloamperes.

The V -I characteristic is then the basic application design tool for selecting a device in order to perform a protective function. For a successful application, however, other factors, discussed in detail in the information available from manufacturers, must also be taken into consideration. Some of these factors are:

- Selection of the appropriate nominal voltage for the line volt age of the application

- Selection of the energy-handling capability (including consideration of the source impedance of the transient, the wave-shape, and the number of occurrences [21])

- Heat dissipation

- Proper installation in the circuit (lead length) [22]

6.5  Packaged Suppressors

The need for protection and the opportunity to provide packaged protective devices to concerned computer users has prompted the marketing of many packaged suppressors, ranging from the very simple and inexpensive to the complicated (not necessarily much better) and expensive. The field has also seen a number of devices claiming energy savings in conjunction with transient suppression; there is no foundation for such a claim, and the issue hopefully has been settled in a study published by EPRI [23).

Line conditioners using a ferro-resonant transformer are offered primarily as line-voltage regulators, but also provide high attenuation of transient overvoltages, a performance that isolating transformers do not provide. Example No.2, in the Appendix, gives examples of the poor performance of isolating transformers and of the effective performance of line conditioners .in dealing with normal mode transients.

6.6  Failure Modes

Failure of an electrical component can occur because its capability was exceeded by the applied stress or because some latent defect in the component went unnoticed in the quality control processes. While this situation is well recognized for ordinary components, a surge protective device, which is no exception to these limitations, tends to be expected to perform miracles, or at least to fail graciously in a fail-safe mode. The term "fail-safe," however, may mean different failure modes to different users and, therefore, should not be used. To some users, fail-safe means that the protected hardware must never be exposed to an overvoltage, so that failure of the protective device must be in the fail-short mode, even if it puts the system out of operation. To others, fail-safe means that the junction must be maintained, even if the hardware is left temporarily unprotected, so that failure of the protective device must be in the open-circuit mode. It is more accurate and less misleading to describe failure modes as fail-short or fail-open, as the case may be.

When the diverting path is a crowbar-type device, little energy is dissipated in the crowbar, as noted earlier. In a voltage-clamping device, because more energy is deposited in the device, the energy-handling capability of a candidate protective device is an important parameter to consider in the design of a protection scheme. With nonlinear devices, an error made in the assumed value of the current surge produces little error on the voltage developed across the protective device and thus applied to the protected circuit, but the error is directly reflected in the amount of energy which the protective device has to absorb. At worst, when surge currents in excess of the protective device capability are imposed by the environment, e.g., an error made in the assumption, a human error in the use of the device, or because nature tends to support Murphy's law, the circuit in need of protection can generally be protected at the price of failure in the short-circuit mode of the protective device. However, if substantial power-frequency currents can be supplied by the power system, the fail-short protective device generally terminates as fail-open when the power system fault in the failed device is not quickly cleared by a series overcurrent protective device (fuse or breaker).

With the failure mode of a suppressor being of the fail-short type, the system protection with fuses can take two forms (Figure 17). For the user concerned with maintaining the protection of expensive equipment, even if failure of the protector means the loss of the function, Alternative A must be selected. Conversely, if the function is paramount, Alternative B must be selected.

7.  Conclusions

Power system disturbances can inject damaging overvoltages in power lines as well as data lines. Lightning surges can be equally damaging, by direct termination of a stroke, or by induction or even differences in ground potential caused by the flow of the current. Beware of differential ground potential rise!

Fundamental precautions, best applied in the design and construction stages, can provide effective protection at a small cost compared to the alternative of failures and later retrofits. The cost of insurance premiums always seems high before the accident.

Shielding, bonding, and grounding are the classical preventive methods at the system and component leve1. Conflicts between traditional grounding practices for noise reduction can be reconciled with the requirements of surge protection. Grounding the shields at one end only invites trouble.

A combined approach of fundamental precautions and protective devices can provide effective protection over the range of natural and man-made disturbances. However, these devices must be applied as part of a concerted effort. Coordination of protective devices is the key to functional and cost-effective protection.

Acknowledgments

Motivation for presenting this paper was provided by the reported case histories and the penetrating questions raised by students at the University of Wisconsin annual conferences on surge protection, as well as by discussions with members of the IEEE Surge Protective Devices Committee. Catharine Fisher and Elizabeth Zivanov of CRD contributed valuable reviews and comments toward development of the final text.

References

1. J.H. Hagenguth and J.G. Anderson, "Lightning to the Empire State Building," Part III, AlEE Transactions 7I PAS, August 1952.

2. N. Cianos and E.T. Pierce, A Ground Lightning Environment for Engineering Usage. Stanford Research Institute Technical Report, August 1972.

3. R.H. Golde, "The Frequency of Occurrence and the Distribution of Lightning Flashes to Transmission Lines," AlEE Transactions 64, 1945.

4. World Distribution of Thunderstorm Days, WMO-OMM #21 TP6. Geneva World Meteorological Organization, 1953.

5. R.H. Golde, "The Lightning Conductor," Lightning II, R.H. Golde, ed. New York: Academic Press, 1977.

6. H. Cavendish, W. Watson, B. Franklin, and J. Robertson, "Report of the Committee Appointed by the Royal Society to Consider a Method of Securing the Powder Magazines at Purfleet," Philosophical Transactions of the Royal Society 63, London, 1773, and 68, 1777.

7. A. Greenwood, Electrical Transients in Power Systems. New York: Wiley Interscience, 1971.

8. Guide for Surge Withstand Capability (SWC) Tests, ANSI Std C37.90a, 1974; IEEE Std 472-1974.

9. Insulation Coordination Within Low-Voltage Systems Including Clearances and Creepage Distances for Equipment, International Electro	technical Commission Report 664, 1980.

10. IEEE Guide for Surge Voltages in Low-Voltage AC Power Circuits, ANSI/IEEE Std C62.41-1980.

11. J.E. Lenz, "Basic Impulse Insulation Levels of Mercury Lamp Ballast for Outdoor Applications," Illuminating Engrg., pp. 133-140, February 1964.

12. F.D. Martzloff and G.J. Hahn, "Surge Voltage in Residential and Industrial Power Circuits," IEEE PAS 89, vol. 6, pp. 1049-1056, July/August 1970.

13. R. Hasler and R. Lagadec, "Digital Measurement of Fast Transients on Power Supply Lines," in Proc. Third Symposium and Technical Exhibition on Electro-Magnetic Compatibility. Rotterdam, Holland, May 1979, pp. 445-448.

14. P. Chowdhuri, "Transient Voltage Characteristics of Silicon Power Rectifiers," IEEE Transactions on Industry Applications IA-9, September/October 1973.

15. F.D. Martzloff, The Propagation and Attenuation of Surge Voltages and Surge Currents in Low-voltage AC Circuits, IEEE Transactions on Power Apparatus and Systems PAS-102, May 1983, pp. 1163-1170.

16. Transient Voltage Suppression Manual, Third Edition, General Electric Company, Auburn, New York, 1982.

17. J.D. Harnden, F.D. Martzloff, W.G. Morris, and F.B. Golden, "The GE-MOV Varistor - The Super Alpha Varistor," Electronics. vol. 45 (21), 1972, p. 91.

18. G.D. Mahan, L.M. Levinson, and H.R. Philipp, Theory of Conduction in ZnO Varistors. 78CRD205, General Electric Company, 	Schenectady, New York, 1978.

19. M. Matsuoka, T. Masa Yama, and Y. Lida, "Nonlinear Electrical Properties of Zinc Oxide Ceramics," in Proc. of First Conf. Solid State Devices, Tokyo, 1969, J. Japan Soc. Appl. Phys., vol. 39, 1970.

20. M. Matsuoka, "Non-Ohmic Properties of Zinc Oxide Ceramics," Jap. J. Appl. Phys.. vol. 10, 1971.

21. F.D. Martzloff, "Matching Surge Protective Devices to Their Environment," Proc. of IEEE-I AS Annual Meeting. October 1983, pp. 387-392. Also available as Report 83CRD169, General Electric Company, Schenectady, New York.

22. F.A. Fisher, "Overshoot - A Lead Effect in Varistor Characteristics," Report 78CRD201, General Electric Company, Schenectady, New York.

23. Alexander Kusko, Inc., Evaluation of Transient Voltage Suppressors for Saving Electric Energy, Electric Power Research Institute Report EM-1722, Palo Alto, California, 1981.

24. National Electrical Code 1981, National Fire Protection Association, Boston, Massachusetts.

25. K.E. Crouch, Lightning Technology Inc., Pittsfield, Massachusetts, private communication.

APPENDIX - EXAMPLES

To illustrate the preceding discussion, some practical examples are given in this appendix as the basis for sound design approaches.

Example No.1 - Does an isolating transformer help?

The author has witnessed and engaged in many discussions on the merits of isolating transformers, sparked by the misconception that "spikes are attenuated by transformers" or "spikes do not pass through transformers." Figures 18 and 19 are offered to support the position that these quotations are misconceptions. When properly applied, isolating transformers are useful to break ground loops and reduce common mode effect, but .they do not by themselves attenuate spikes that occur line-to-line in the normal mode.

Figure 18 shows the propagation - or worse, the enhancement - of a voltage impulse in a 1:1 isolating transformer. The 6 kV, 0.5 s-100 kHz impinging wave of ANSI/IEEE Std C62.41-1980 is applied to the primary of the transformer, H1H3 to H2H4. The output voltage, measured at X1X3 to X2X4, appears as a 7 kV crest on the secondary side of this "isolating" transformer. on the secondary side of a transformer.

Figure 18 was recorded with no load on the transformer secondary, which represents the extreme case of the low-power electronic control in the standby mode. Figure 19 shows the primary and secondary voltages of the transformer with a 10 W (1500 ) and a 100 W (150 ) load on the secondary side, at the same generator setting as Figure 18. With the 10 W load that might be typical of an electronic control in standby mode, the combined series reactance of the transformer and shunt resistance of the load produce the output shown in Figure 19A, still slightly higher than the input.

With the l00W load shown in Figure 19B, the attenuation is now apparent, but is only 2:1. Capacitive loads would, of course, produce a greater attenuation than resistive loads for the inductive series impedance of the transformer, at the frequency spectrum of this fast 2 s-wide spike. For surges of longer duration, the attenuation would be even smaller.

These examples show that, unless a well-defined load is connected to the transformer, expecting attenuation from the transformer may prove to be hazardous to the health of low-power electronics connected on the secondary side of a transformer.

In contrast, decoupling is possible with a ferro-resonant line conditioner which is primarily intended for line voltage regulation, but which also provides a high degree of surge suppression. Figure 20 shows the 6 kV incoming wave being attenuated to 60 V (100:1) on the secondary side, of the unloaded line conditioner, and to 40 V (150:1) with a load of only 10%; at full load, an attenuation to less than 10 V was observed. The nature of the ferro-resonant line conditioner is such that the decoupling improved with loading, while the simple transformer of Figure 18 can only act as linear dividers with load changes. Conversely, the decoupling between primary and secondary sides of the line conditioner is further seen on the oscillogram recorded on the input side of the line conditioner. This oscillogram is, in fact, a photograph of two successive measurements, one with no load on the line conditioner and one with a 100 W load. The input waves are exactly superimposed.

This decoupling reflects the nonlinear behavior of the ferro-resonant line conditioner, which is significant in this case, compared to the linear behavior of transformers: For surge sources of lower impedance than the generator used in these tests, or for frequencies lower than that contained in the 0.5 s - 100 kHz spike, the transformer attenuation would become lower, in direct proportion to the corresponding impedance change, while the ferro-resonant line conditioner would keep the decoupling unchanged.

For worst-case demonstration, the two oscillograms of the output were recorded with the spike timed to occur at the peak of the 60 Hz line voltage demonstration The peak-to-peak amplitude of the line voltage is indicated by the gray band recorded on the oscillograms by photographically superimposing repetitive traces of the line voltage. For timings other than .the peak, the small voltage oscillation on the output voltage would be completely contained within the normal peak-to-peak band of the 60 Hz line voltage.

There is at present a trend to an upward spiral in specifying dB's of attenuation in line conditioners. In the author's opinion, the point of citing a 120 dB attenuation is moot because typical installation practice will degrade that level of decoupling.

Example No.2 - Connections options for suppressors and effects on residual voltages.

The author has witnessed lively controversies among various application information sources on the most effective transient suppression configuration to be applied. Taking, as a simplified example, the task of specifying the protection of a single. phase equipment connected at the end of a line with no opportunity to divert the transient closer to the source (for instance; at the service entrance), the options would be to connect one, two, or three varistors between the three wires (black, white, and green) at the end of the line. However, additional information needs to be known: Will the impinging surge be in the normal mode (black-to-white) or in the common mode ([black-and-white]-to-green)? Where in the equipment is the most sensitive component:. line-to-line (most likely) or line (black OR white)-to-green? Clearly, the situation is confusing, and there will not be a single, simple answer applicable indiscriminately to all cases. The National Electrical Code [24] specifically allows the connection of surge arresters, (Article 280-22) if the interconnection occurs only by operation of the surge arrester during the surge. Since the standby current of varistors is very low, this requirement can be met; furthermore, there will not be any interference with the operation of Ground Fault Circuit Interrupters if there is only a small number of protectors.

The set of measurements recorded in Figure 21 shows an example of these many options with increasing protection, albeit at increasing cost, from a single varistor to three varistors. The selection would depend on the vulnerability level and location of the equipment to be protected. The impinging surge is assumed to be black-to-[white-and-green], since white and green are tied together at the service entrance. The line is a 75 m line and the surge is that available from the generator set for a 2000 A, 8/20 s short-circuit impulse. Rather than attempt to modify the setting of the generator for each case in order to maintain constant current crest for the various configurations (an impossible task if wave form is also to be maintained), the generator was left unchanged, to discharge a constant total energy in the system - not a bad hypothesis for the real world. The current crests are all in the range of 300 to 380 A, which is not a significant change for comparing varistor clamping voltages.

If only one varistor is allocated to protect the equipment, the black-to-white varistor connection (first row) affords maximum protection for the electronics which are also likely to be connected black-to-white. However, the voltages between either black or white and green are large; this is the stress that will be applied to the clearances of the equipment. This is a good example of conversion of a normal mode transient into a common mode.

The configuration with varistor black-to-green (second row) does not afford very good protection for components connected black-to-white; therefore, it should be used only if there is a special need to clamp black-to-green at a low voltage with only one varistor available.

An improved protection is obtained with a varistor connected black-to-white, complemented by a second varistor connected white-to-green (third row). The ultimate protection is, of course, one varistor in every position (fourth row), but this should be required only for exceptionally sensitive loads.

Example No.3 - Ground potential rise on data lines.

A distributed computer system had been installed with a central processing unit and remote terminals located in separate buildings. In a span of 5 weeks during the first summer, after commissioning the system, three lightning storms occurred in the area; no direct strikes were reported on the buildings, but extensive damage was done to the circuit boards on terminals and CPU inputs.

After the first occurrence, power line surges were suspected and some precautions were applied, when access to the hardware was possible, by pulling out the ac power plugs from the CPU or terminal at the onset of a lightning storm. This did not help. Next, isolating transformers were considered but, again, did not help. At this point, the author was called in for consultation, and the following proposed diagnostic was established: the surges were not coming from the ac lines, but rather were due to differences in the ground potential existing between the separate buildings during flow of lightning currents. The data cables had been run in PVC conduit, buried between the buildings and, true to one tenet of steady-state noise prevention, only one end of the shield, of the wire pairs had been grounded, with the, other left floating. Figure 22 shows how this arrangement can produce high voltage between a floating end of the shield and the local ground, a practice which is bound to produce a flashover and flow of surge currents along unwanted paths, in the circuit components. Thus, the problem was not power line surges, but differential ground potential. Worse, by pulling out the ac line plugs but leaving the incoming data cables connected, the operators had unwittingly removed the local grounding connection from the hardware frame, leaving only the data cables coming in, with a possibility of raising the complete hardware several thousand volts above local grounds in the room - a dangerous condition.

A solution to the problem could take several approaches. Radical solutions, such as a microwave link or a fiber optics cable, would indeed have eliminated the differential ground potential problems, but were considered too expensive or too long to install.

Incidentally, part of the original puzzlement at the failures was the notion that opto-isolators provided in the data link route should have avoided problems. Close scrutiny of the circuits, however, disclosed that the opto-isolators had been provided for some other purpose; in fact, the ground potential loop was closed by the power supply to the opto-isolator feeding the amplifiers from a local source rather than the remote source, negating the isolation function.

Another solution, really the most simple and effective, would have been the replacement of the plastic underground conduit by a continuous steel conduit linking the steel conduits used inside the buildings. This would have provided equalization of the ground potentials along the data cable, while allowing the desired use of shields with one end only at ground. However, that solution was not acceptable to the plant facility organization.

In this particular location, a spare conduit had been buried next to the data line conduit. This offered the possibility of pulling a heavy ground cable in this conduit, close to the data cables, which could then tie the two corners of the buildings at the point of entry of the data cables, as a first step toward reducing differential ground potentials. At first, this concept was somewhat difficult to sell to plant facilities: because there is a ground grid tying to two buildings for 60 Hz faults, further ties between the two buildings did not seem necessary. However, our thesis was that this grid would have too high an impedance to serve the purpose, and furthermore that the data cable run, located away from the ground grid, would form a flux-collecting loop with the ground grid. After lengthy discussions, the thesis was accepted and the cable was installed.

Simultaneously, the concept of tying the two ends of the cable shields to ground was proposed, with the provision of a barrier that would avoid the circulation of power-frequency currents [25]: inserting an array of diodes (Figure 23) at one end of the shields reconciled the needs of noise prevention under normal operation and the requirement of grounding at both ends during lightning events. The forward drop of the two diodes in series (1.5 V) was enough to block any 60 Hz circulating current that would inject noise in the data cables. During a lightning strike, however, the diodes would allow flow of current to compensate and cancel the ground potential differences.

These two cures were implemented during the first summer, and no further problems occurred for the rest of the lightning season. While these two solutions might have been sufficient, the concern over another possible failure of the system was sufficient to motivate the design of further protection, the insertion of a voltage clamp in each data pair. This solution required some design and acceptance testing from the system manufacturer, so that it was not implemented until the next lightning season. Thus, the system survived the remainder of the first lightning season with only the first two remedies.

Experience has shown that conclusions on the effectiveness of lightning protection schemes should wait perhaps as much as 10 years before being proclaimed, because of the large variations in lightning activity. However, after three summers of trouble-free operation compared to three major failures in 5 weeks, the cure would seem effective. Hopefully, these words will not have to be eaten by the author in a few years.

In retrospect, then, the following recommendations can be drawn from this horror tale, for retrofits or new installations:

1. Data cables linking separate buildings or spanning beyond a single room within one building should have a shield tied to local ground at both ends of the cable. If the first shield provided with the cables must be left with one end floating by diktat of the system vendor, then these cables should be installed within a continuous metal shield. This continuous shield can be either a double shield of the flexible cable, or simply a metal conduit, with both ends grounded.

2. Substantial relief can be obtained in retrofits by grounding both ends of existing shields through a low-voltage clamp, such as a diode array, that will block noise-inducing power frequency currents, but will allow the flow of ground-potential equalizing currents during surges.

3. The ultimate protection may be the insertion of surge-protective devices in each line. However, this solution requires careful design so that degradation of the signals does not occur, and residual spikes are not allowed to pass through.

The Protection of Computer and Electronic Systems

Against Power Supply and Data Lines Disturbances

François D. Martzloff

General Electric Company

Schenectady NY

1.  INTRODUCTION

The irresistible trend toward greater numbers of distributed computing systems may be a source  of difficulties which the earlier, centralized systems had overcome: surge voltages and surge currents injected or induced into power supply lines and communication (data) lines.  These surges may be produced by lightning, by power system switching, or by differences in the actual potential of points expected to be at ground potential but which are, in fact, driven apart by a surge current. Uninformed users of terminal equipment or personal computers might also connect their equipment in a manner inviting difficulties.  Another source of transients, not covered in this report, is static discharge.

A different source of disturbances for computers is, of course, undervoltage transients, sometimes called "sags."  These are largely due to power system switching  or faults, some being the consequence  of lightning.   Unfortunately, it is more difficult to fill a void in the power delivery than to divert and block an excess energy, so that the techniques needed to protect computer systems against these sags require approaches and equipment different from those discussed in this report, whose scope is limited to overvoltage or overcurrent surges.  A number of approaches for mitigation of externally caused sags have been successfully implemented by computer manufacturers and users.   These approaches range from power supplies with sufficient storage capacity or motor generator sets with sufficient mechanical inertia to ride through short sags, to uninterruptible power supplies with storage   batteries and solid-state inverters being instantaneously switched to take over a failing utility power supply.  These are now classical remedies and, when properly applied, eliminate the problems of sags, while the problems associated with surges still seem to be with us.  This report  presents a summary of present knowledge on the occurrence of surges and on mitigating measures, with recent case histories illustrating the pitfalls of inappropriate applications.

2,  THE ORIGINS OF TRANSIENT OVERVOLTAGES

Transient  overvoltages in power systems originate from one cause – energy being injected into the power system – but from two sources: lightning discharges or switching within the power system.  In communication or data systems there is another source of transients: the coupling of power system transients into the system.  Furthermore, all systems involving several connections to external equipment face the risk of transient overvoltages associated with ground potential rise during the flow of surge currents.  As stated previously, static discharge problems are not treated in this report.

Lightning discharges may not necessarily mean direct termination of a lightning stroke onto the system.  A lightning stroke terminating on some object near a power or data line will create a very fast-changing magnetic field that can induce voltages - and inject energy - into the loops formed by the conductors of the system.  Lightning can also inject overvoltages in a system by raising the ground potential on the surface of the earth where the stroke terminates, while more distant "ground" points remain at a lower voltage, closer to the potential of "true earth." The literature provides information on the characteristics of lightning discharges.  (1-6)

Surges from power system switching create overvoltages as a result of trapped energy in loads being switched off, or of restrikes in the switchgear.  These transients will be examined in greater detail in the following paragraphs.

  - Transients in power systems

A transient is created whenever a sudden change occurs in a power circuit, especially during power switching - either the closing or opening.  It is important to recognize the difference between the intended switching (the mechanical action of the switch) and the actual happening in the circuit.  During the closing sequence of a switch, the contacts may bounce, producing openings of the circuit with reclosing by restrikes and reopening by clearing at the high-frequency current zero.  Prestrikes can also occur just before the contacts close, with a succession of clearings at the high frequency current zero, followed by restrikes.  Similarly, during an opening sequence of a switch, restrikes can cause electrical closing(s) of the circuit.

Simple switching transients  (7)  include circuit closing transients, transients initiated by the clearing of a short circuit, and transients produced when the two circuits on either side of the switch, being opened, oscillate at different frequencies.  On the load side of the switch, for circuits having inductance and capacitance (all physical circuits have at least some, in the form of stray capacitance and inductance) with little damping, these simple switching transients are inherently limited to twice the peak amplitude of the steady-state sinusoidal voltage.  On the load side of the switch and without a surge protective device, the current flowing just before switching is available to charge the circuit  capacitances at whatever voltage is required to store the inductive energy of the current by converting it into capacitive energy; voltages can reach high levels, such as ten times the normal level.

Several mechanisms are encountered in practical power circuits that can produce large transient overvoltages.   Two such mechanisms occur frequently: current chopping and restrikes, the latter being especially troublesome when capacitor switching is involved.

A similar scenario can unfold when an ungrounded power system experiences an arcing ground fault.  The switching action is then not the result of a deliberate parting of contacts but the intermittent connection produced by the arc.

These switching overvoltages, high as they may be, are somewhat predictable and can be estimated with reasonable accuracy from the circuit parameters, once the mechanism involved has been identified.(8) There is still some uncertainty as to when and where they occur because the worst offenders result from some abnormal, and thus rare,* behavior of a circuit element.  Lightning-induced   transients are much less  predictable because  there is a wide range of possibilities for

* This rarity can take two different aspects:  1. In the vast majority of circuits, these abnormal transients can sometimes occur, but rarely ("when"). 2. Among all circuits, a few rare ones are frequently and consistently afflicted with such abnormal behavior ("where").

In response to these concerns, various committees and working groups have attempted to describe ranges of transient occurrences or maximum values occurring in power circuits.  Three such attempts are described in the next section.  Figures 1, 2, and 3 show typical examples of transients recorded in power systems.

2.2  Transients in data lines

Data lines are different from power lines in the occurrence of surges: power systems can generate their own transients, as seen above, in addition to receiving injected surges.  Data lines are only subjected to what the environment will inject.  However, the operating voltages and the overvoltage tolerance of signal-processing components in these data systems are generally much lower than those of power system components.  Thus, damage (not to discount problems of misoperation) is more likely to occur to data lines than to power system components from the same exposure to injected transients.

The systematic effort at characterizing surges in power circuits, exemplified by the IEEE standard described in the next section, has not been extensively reported by users of data lines, with the exception of the telephone industry. (9- 13)  In the telephone environment, much emphasis is placed on lightning effects on long overhead or buried cables and lines, as well as on induced noise from adjacent power systems.  The same IEEE group that produced the Guide on surge voltages is now addressing the lack of knowledge on data lines, such as inter-building computer links and process control lines in chemical plants, which will be more relevant to computer users than are telephone environment data. (14)  Figures 4 and 5 show transients recorded on typical data lines exposed to lightning effects.

3.  STANDARDS ON TRANSIENT OVERVOLTAGES IN POWER LINES

Several standards or guides have been issued or proposed in Europe and in the United States specifying a surge withstand capability for specific equipment or devices and specific conditions of transients in power or communication systems.  Some of these specifications represent early attempts to recognize and deal with the problem in spite of insufficient data.  As a growing number of organizations address the problem and as exchanges of information take place, improvements are being made in the approach.  Three of these are briefly discussed here.

  - The IEEE Surge Withstand Capability Test (SWC) (15)

One of the earliest published documents which addressed new problems facing electronic equipment exposed to power system transients was prepared by an IEEE committee dealing with the exposure of power system relaying equipment to the harsh environment of high-voltage substations.

Because this useful document was released at a time when little other guidance was available, users attempted to apply the recommendations of this document to situations where the environment of a high-voltage substation did not exist.    The revised version of this standard, soon to  be issued, recognizes the problem and attempts to be more specific (and restrictive) in its scope.  Thus, an important consideration in the writing and publishing of documents dealing with transients is a clear definition of the scope and limitations of the application.

3.2  The IEC 664 Report  (16)

The Insulation Coordination Committee of the International Electrotechnical Commission (IEC) included in its report a table indicating the voltages that coordinated equipment must be capable of withstanding in various system voltages and installation categories (Table 1).  The table specifies its applicability to a controlled voltage situation, which implies that some surge-limiting device has been provided - presumably a typical surge arrester with characteristics matching the system voltage in each case.   The waveshape specified for these voltages is the 1.2/50 as wave, a specification consistent with the insulation withstand concerns of the group that prepared the document.  No source impedance is indicated, but four "installation categories" are specified, each with decreasing voltage magnitude as the installation is farther away from the outdoor environment.  Thus, this document primarily addresses the concerns of insulation coordination; the specification it implies for the environment is more the result of efforts toward coordinating the voltage levels than efforts to describe the environment and the occurrence of transients.  The latter approach has been that of the IEEE Working Group on Surge Characterization in Low-Voltage Circuits, which will be reviewed in detail.

3.3  The IEEE Guide on Surge Voltages (ANSI/IEEE Std C62.41-1980) (17)

Voltages and rate of occurrence

Data collected from a number of sources led to plotting a set of lines representing a rate of occurrence as a function of voltage for three types of exposures (Figure 6).  These exposure levels are defined in general terms as follows:

- Low Exposure - Systems in geographical areas known for low lightning activity, with little load-switching activity.

- Medium Exposure - Systems in geographical areas known for high lightning activity, or with frequent and severe switching transients.

- High Exposure - Rare, but real, systems supplied by long overhead lines and subject to reflections at line ends, where the characteristics of the installation result in high sparkover levels of the clearances.

The two lower lines of Figure 6 have been drawn at the same slope because the data base shows reasonable agreement among several sources on that slope.  All lines may be truncated by sparkover of the clearances, at levels depending on the withstand voltage of these clearances. The high exposure line needs to be recognized, but it should not be indiscriminately applied to all systems.  Such application would penalize the vast majority of installations where the exposure is lower.

The voltage and current amplitudes presented in the Guide attempt to provide for the vast

majority of lightning strikes, but none should be considered "worst case," because  this concept cannot be determined realistically.  It is necessary to think in terms of the statistical distribution of strikes and to accept a reasonable upper limit for most cases.  Where the consequences of a failure are not catastrophic but merely represent an annoying economic loss, it is appropriate to make a tradeoff of the cost of protection against the likelihood of a failure caused by a high but rare event.

Waveshape of the surges

Many independent observations (17- 21 ) have established that the most frequent type of transient overvoltage in ac power systems is a decaying oscillation, with frequencies between 5 and 500 kHz.     This finding is in contrast to earlier attempts to specify    the unidirectional double-exponential voltage wave that is generally described as 1.2/50.  Indeed, the unidirectional voltage wave has a long history of successful application in the field of dielectric withstand tests and is representative of the surges propagating in power transmission systems exposed to lightning. In order to combine the merits of  both waveshape definitions and to specify them where they are applicable, the Guide proposes two representative waveshapes: an oscillatory waveshape inside buildings, a unidirectional waveshape outside buildings, and both at the interface (Figure 7).

The oscillatory waveshape simulates those transients affecting devices that are sensitive to dv/dt and to voltage reversals during conduction, (22) while the unidirectional voltage and current waveshapes, based on long-established ANSI standards for secondary valve arresters, represent an equivalent of the transients where energy content is the significant parameter.  Recent concerns on the occurrence of longer duration surges, or lower frequencies, such as the 5 kHz lower limit cited, will probably be reflected in the updating of this standard over the next several years.

From a pragmatic point of view, the realization that oscillating waves are unavoidably produced by practical test systems will also be a driving force toward specification of oscillatory waveforms rather than unidirectional impulses in future standards.

Increased recognition of the upset aspect of transient overvoltages is also likely to result in the inclusion of a "fast transient" with rise time and duration in the nanosecond range.

Energy and source impedance

The energy involved in the interaction of a power system with a surge source and a surge protective device will divide between the source and the protective device in accordance with the characteristics of the two impedances.  With a gap-type protective device, the low impedance of the arc after sparkover forces most of the energy to be dissipated elsewhere: for instance, in a resistor added in series with the gap for limiting the power-follow current, or in the impedance of the circuit upstream of the protective device.  With an energy-absorber gapless protective device, a substantial share of the surge energy is dissipated in the suppressor, but its clamping action does not involve the power-follow energy resulting from the short-circuit action of a gap.  It is therefore essential to the effective use of surge protective devices that a realistic assumption be made about the source impedance of the surge whose effects are to be duplicated.

Unfortunately, not enough data have been collected on what this assumption should be for the source impedance of the transient.  Standards and recommendations, such as DOD STD-1399 or the IEC 664 report, either ignore the issue or indicate values applicable to limited cases, such as the SWC test for high-voltage substation equipment.  ANSI/IEEE C62.41 attempts to relate impedance to categories of locations but unavoidably remains vague on their definitions (Table 2).

Having defined the environment for low-voltage ac power circuits, the Working Group is now preparing an Application Guide, where a step-by-step approach will outline the method for assessing the need for transient protection and selecting the appropriate device or system.  Parallel work in other IEEE working groups preparing test specification standards  (24- 27)  for surge protective devices will be helpful in this selection process.  Other groups in the USA, as well as the international bodies of the IEC and the Comité Consultatif International Télégraphique et Téléphonique (CCITT), are now working toward further refinements and the reconciliation of different approaches.

3.4  Previous and future surge recordings

The supporting data cited in Appendix A of ANSI/IEEE C62.41 are based on voltage surge recordings made in the 1962-1975 period.  In that period, digital instrumentation for surge monitoring was not as readily available as it is now, and, most significantly, the proliferation of surge protective devices, such as metal oxide varistors, had not reached the present level.

Measurements, limited to voltage, were  conducted with oscilloscope/camera systems or with peak-recording instruments.  Voltages were generally recorded between the line(s) and the neutral of a single-phase or polyphase power system.  No measurements had been reported as neutral-to-ground;  some may have been between line and ground.  Of course, that distinction is moot for measurements made at the service entrance where neutral and ground are bonded.

Prior to the proliferation of varistors, a limitation had been recognized for peak voltages: the flashover of clearances, occurring typically between 2 and 8 kV for low-voltage wiring devices.  For that reason, the curves of Figure 1 in the Guide include the indication of a possible truncation of the distribution around 6 kV.  Recent studies, still in progress, have indicated that benign flashover of clearances, without power follow and therefore not readily detectable, may be more prevalent than was previously believed.

An estimate of the number of low-voltage surge protective devices such as varistors used in the United States since 1972 on ac power circuits is in the order of 500 million.  An undefined but substantial portion of that number is installed in permanently connected equipment.  Therefore, it is now very likely that a new limitation exists in the recording of voltage surges.  A surge recording instrument installed indiscriminately at a random location may have a varistor connected across the line near the point being recorded.(28)  This situation will have several implications for the recordings obtained in present and future measurements, as contrasted to those of previous measurement campaigns.

1.	Locations where voltage surges were previously identified - assuming no change in the source of surges - are now likely to experience lower voltage surges, while current surges will occur in the newly installed protective devices.

2.	Not only will the peaks of the observed voltages be changed, but also their waveforms will be affected by the presence of nearby varistors as follows:

a.	If a varistor is located between the source of the surge and the recording instrument, the instrument will record the clamping voltage of the varistor.  This voltage will have lower peaks but longer time to half-peak than the original surge.

b.	If the instrument is located between the source of the surge and a varistor, or if a varistor is installed in a parallel branch circuit, the instrument will record the clamping voltage of the varistor, preceded by a spike corresponding to the inductive drop in the line supplying surge current into the varistor.

c.	 If a varistor is connected between line and neutral with a surge impinging

between line and neutral at the service entrance, a new situation is created: the line-to-neutral voltage is indeed clamped as intended, but the inductive drop in the neutral conductor between the point of connection of the varistor and the service entrance creates a spike voltage between the neutral and the grounding connector at the point of connection of the varistor and downstream points supplied by the same neutral.   Because this spike will have a short duration, it will be enhanced by the open-end transmission line effect between the neutral and grounding conductors.(29)

3.	The surge voltage limitation function performed by flashover of clearances is more likely to be assumed by new surge protective devices that are constantly being added to the systems.

4.	The considerations discussed in paragraphs 1, 2, and 3 above will produce a significant reduction in the mean of recorded voltage surges in a population of different locations.  This reduction will continue as more and more varistors are installed.  The upper limit, however, will remain the same for locations where no varistor has yet been installed.  A sense of false security and an incorrect description of the environment might be created by attention given only to the average of voltage surges presently recorded in power systems.  Furthermore, the need for adequate surge current handling capability of a new candidate surge suppressor might be underestimated if partial surge diversion is already being performed by a nearby varistor.  This risk will be exacerbated if an attempt is made to clamp at lower voltages by the installation of a new protective device with a clamping voltage lower than that of the device already installed.(8)

4.  SURGE PROPAGATION

4.1  The limitations of arbitrary division into categories

The standards cited in the preceding paragraphs describe surges which may be expected at specific points of a wiring system; the implication is that the surges will proceed downstream, at the same amplitude and waveform, until some interface somehow produces a staircase-like decrease in amplitude.  IEC 664 proposes a voltage staircase with its overvoltage categories (Table 1), while ANSI/IEEE C62.41 proposes a current staircase with its location categories (Figure 8).

This staircase representation is useful to simplify the real world into a manageable set o assumptions, but it is a simplification that ca mask the reality.  Surges will propagate in the system starting at the point of entry; voltage surge will be attenuated to the extent that the series impedance between the point of interest and the source (ZI, Figure 9) on one hand and the shun impedance (Z2) on the other hand, form a voltage divider.  If the series impedance is low and the shunt impedance is high (light loading of the system), the voltage divider does not produce high attenuation of the voltage surges.  In addition to an attenuation of the amplitude,  a waveform change takes place which is most apparent for fast front and short duration pulses. (29)  Conversely, current surges, if they are the result of a current source such as a lightning strike, will produce high voltages unless a low-impedance diverting path is offered to the flow of current.  If the current surge in a system is the result of a combined current source and multipath to ground (Figure 10), there is then a division of the current among the path that is governed by the inverse ratio of the impedances.  If a user has control over only on of the paths, he can decrease the amplitude of the current surge in his path only by forcing a greater share of the total current to flow through the other paths; thus, surge blocking is likely to be an exercise in passing the problem from one point of the system to another.  The solution lies in surge diversion, offering to the surge a path where the current flow can occur harmlessly.

4.2   The limitations of transmission line analysis

In qualitative discussions of surge propagation, the classical behavior of a transmission line is often called upon to provide explanations of the situation.  In particular, the reflections occurring at the end of a line are cited in accordance with the theory that the impulse is doubled if the line is open-ended, and that an inverse impulse is returned if the line is shorted.    However, these discussions sometimes lose sight of  the fact that the concept is applicable only if the  line length is sufficient to contain all of the surge front.  If the surge has a rise time longer than the propagation time along the line, the point is moot and, by the time the surge reaches its peak, the voltage at the receiving end of the line does not differ  from the voltage applied at the sending end.

Independently from the location of a device or equipment In the above figure, It should remain safe (no fires, no personnel hazard) over the full range of available surges at any point within the Installation.  It may also be desirable, under particular circumstances and for specific devices, to proscribe damage as a result of testing at higher levels than might be suggested by its typical location.

The effects of reflections and attenuations along a line are further illustrated in Figures 12, 13, and 14, excerpted from Reference 29.   A three-wire, conduit-enclosed line, 225 m long was subjected to short pulses applied through an impedance-matching network to provide minimum interaction between the surge generator and the line.  Access points at 75 and 150 m, in addition to the far end at 225 m, were provided within reach of the measuring oscilloscope probes by folding the line in a zig-zag configuration.

Figure 12 shows the propagation of a 200 ns-wide pulse when a matching impedance is connected at the receiving end.  The attenuation of this pulse is quite apparent, with an average ratio of 0.7 between the voltages at points 75 m apart in the line.  The travel time can also be seen as 1.1 s from sending to receiving and, corresponding to 225 m/1.1 /s = 204 m/s, or two-thirds the speed of light in vacuum.

Figure 13 shows the same pulse propagating in the same line, but with a doubling of the voltage at the receiving end, which was left open.  In spite of this doubling affect, there has been enough attenuation of the short spike over the 225 m that the pulse at the receiving end is lower than the pulse at the sending end.  However, for shorter lines, the attenuation would not have taken its toll before doubling at the end: doubling the pulse which appears at the intermediate 75 m of the 225 m line implies that, at the end of an open-ended 75 m, one could have a pulse 20% greater than at the sending end.    Note also that, while the amplitudes are attenuated, the rise time tends to be increased; therefore, the time integral of the pulse   (and therefore its potential for damaging energy-sensitive components) is not attenuated as quickly as is the amplitude along the line length.

Figure 14 shows a 2 s-wide pulse propagating along the same line, with matched termination.  The attenuation is lower than for the 200 ns pulse, with an average ratio of 0.9 between the voltages of points 75 m apart in the line.  This lower attenuation at longer pulse duration (lower frequencies) results from the decreased effect of the shunt capacitance of the line.

These propagation characteristics will be discussed again in conjunction with the performance of protective devices, in Section 6 of this report.  Thus, for many installations contained in a building, the line lengths are short compared to the length required to contain, say, a 1 s front traveling at the speed of 200 m/s.  A more detailed report describing some of the aspects of the propagation of surges and their implications is given in References 29 and 30.

4.2  Common Mode or Normal Mode?

Another aspect of the propagation of surges concerns the dichotomy normal mode/common mode.  In power lines, the issue is whether significant surges occur line-to-line (black-to-white, or phase-to-neutral), the situation described by "normal mode," or whether they occur between any - or all - of the lines and ground (black-to-green, white-to-green, or [black-and-white]-to-green), the situation described by "common mode." These terms were first defined in the context of signal lines, where the concern for balanced circuits reflects the fact that apparently innocuous common mode noise can be converted into objectionable normal mode when circuit impedances along the two signal-carrying wires are not symmetrical with respect to the ground (common) conductor (Figure 15).

Conversely, Figure 16 shows how an attempt to protect against a normal mode surge can produce a harmful common mode-like surge: at the end of a branch circuit, the user installs a surge-protective device connected line-to-neutral, in order to protect his load equipment against a normal mode surge impinging the origin of the branch circuit, where the user in this assumed scenario has no access to provide a surge protective device.  Common knowledge that the neutral and grounding conductors are bonded at this origin might lead the user to believe that no harmful voltage can occur at his end between neutral and grounding conductors.  Yet, the very installation of the protective device between line and neutral, results in a significant L di/dt voltage developed along both line and neutral conductors when the surge current flows into the protective device; half of the total voltage appears at the user's end between the neutral and the grounding conductors.  Because there is generally no admittance between the neutral and grounding conductors at the user's end, the situation is then that of an open-ended line, which produces a doubling of the impinging neutral-to-ground voltage.  An example of this situation is discussed in Section 6.5.

Thus, the answer to the normal/common mode dichotomy is that, in most cases, both modes must be considered, because one can convert into the other, depending upon the coupling, the wiring practices, and the attempts made at suppressing the mode perceived as the greatest threat.  Here again, the pervasive and pervert reality is too often that a solution aimed at suppressing one effect only displaces the problem.     Case History No. 5, later in this report, shows quantitative measurement results of the effects of various methods of connecting a surge protective device at the end of a line.

5.   FUNDAMENTAL PROTECTION TECHNIQUES

The protection of a power system, a computer system, or an electronic black box against the threats of the surge environment can be accomplished in different ways.  There is no single truth or magic cure ensuring immunity and success, but, rather, there are a number of effective approaches that can be combined as necessary to achieve the goal.  The competent protection engineer can contribute his knowledge and perception to the choice of approaches against a threat that is imprecise and unpredictable, keeping in mind the balance between the technical goal of maximum protection and the economic goal of realistic protection at an acceptable cost.   However, just as in the case of accident insurance,  the cost of the premium appears high before the accident, not after.

A discussion of fundamental protection techniques that is limited in space and scope has the risk of becoming an inventory of a bag of tricks; yet, there are a few fundamental principles and fundamental techniques that can be useful in obtaining transient immunity, especially at the design stages of a computer system or circuit.  All too often, the need for protection becomes apparent at a late stage, when it is much more difficult to apply those fundamental techniques which are most effective and economical when implemented at the outset.

5.1  Basic techniques

Protection techniques can be classified into several categories according to the purpose and the system level at which the engineer is working.  For the system as a whole, protection is primarily a preventive effort.  One must consider the physical exposure to transients - in particular, the indirect effects of lightning and power system faults resulting from building design, location, physical spread, and coupling to other disturbance sources - as well as such inherent susceptibility characteristics as frequency response and nominal voltage.   A data processing system using low-voltage signals, high-impedance circuits, and installed over a wide area such as a chemical plant spread over several kilometers, would present much more serious problems than the same system confined to a single building.  As discussed in Case History No. 1, the installation of remote terminals in separate buildings is a prime candidate for trouble unless some basic precautions are observed.

For the system components or electronic black boxes, the environment is often beyond the control of the designer or user, and protection becomes a curative effort - learning to live and survive in an environment which is imposed.  Quite often this effort is motivated by field failures, and retrofit is needed.  The techniques involved here tend to be the application of protective devices to circuits or a search for inherent immunity rather than the elimination or diversion of surges at their origin.

Another distinction can be made in classifying protective techniques.  While surges are unavoidable, one can attempt to block them, divert them, or strive to withstand them; the latter, however, is generally difficult to achieve alone.

5.2   Shielding, Bonding, and Grounding

Shielding, bonding, and grounding are three interrelated methods  for protecting a circuit from external transients.  Shielding is the practice of enclosing the circuit components in a conductive enclosure, which theoretically cancels out any electromagnetic field inside the enclosure-, actually, it is more an attenuation than a cancellation because the enclosure is rarely complete and perfect.  Bonding is the practice of providing low-impedance connections between adjacent metal parts, such as the panels of a shield, cabinets in an electronic rack, or rebars in a concrete structure.  Grounding is the practice of providing a low impedance to earth or a well-defined reference ultimately connected to earth,* through various methods of driving conductors into the soil.  Each of these techniques has its limitations, and each can sometimes be overemphasized.

### Shielding

Shielding conductors by wrapping them in a grounded sheath or shielding an electronic circuit by enclosing it in a grounded conductive box is a defensive measure that occurs very naturally to the system designer or the laboratory experimenter anticipating a hostile electromagnetic environment.  Difficulties arise, however, when the concept of "grounded" is examined in detail. Difficulties also arise when the goals of shielding for noise immunity conflict with the goals of shielding for surge immunity.

A shield can be the size of a matchbox or an airplane fuselage; it can cover a few centimeters of wire or kilometers of buried or overhead cables.  Effective grounding of these diverse shields is not always an easy thing to do because the impedance to earth of the grounding connection must be acknowledged.  The situation is made even more controversial because of the conflict between the often-proclaimed design rule "ground cable shields at one end only" - a rule justified by noise immunity performance, in particular common mode noise reduction - and the harsh reality of current flow and Ohm's law when lightning strikes or when power systems faults occur.

The difficulty may be caused by a perception on the part of the noise prevention designers that the shield serves as an electrostatic shield in which longitudinal currents associated with common mode noise coupling should not flow.  This concept is exemplified in the terminology of shielded cable users, when they describe the shield construction of some cable design as having a foil plus "drain wire," as if there were electrostatic charges that needed to be removed (drained).  Indeed, electrostatic charges can be drained by connecting only one end of the shield.  Further-more, if the two ends of the shield of a cable spanning some distance are connected to the local ground at each end, there is a definite possibility that some power frequency current may flow in the shield.   For low-level signals, this current could produce noise (hum) in the signals.  For that reason, many system designers will insist on the one-end-only grounding rule, and they are correct from that point of view.  Sometimes the shield is used as a return path for the signal circuit, in which case shield currents will cause voltage drops added to the signal.  But the fact is that, when surge currents flow near the circuits, they will unavoidably inject magnetic flux variations into the circuits; hence induced voltages.  Worse yet, in the case of a lightning stroke or of a power system fault injecting current into the earth in the area spanned by the one-end-only grounded shield, the potential of one end of the cable defined as "ground" is not the same as the " ground" at the other end of the cable.   Very high voltages can   be developed   (Figure 17) between the floating end of the shield and the local ground.   No practical insulation can with -stand these levels, and breakdown will occur, allowing surge currents to flow in spite of the designers' intent to prevent them.  The path of these currents will be determined by the components most likely to fail when the voltage rises - the low-level logic circuits, of course.  In contrast, by deliberately allowing a small part of these surge currents to flow in the shields, one obtains a cancellation of the voltages that  connection of the reference to earth is a general safety requirement involving low frequency fault currents for which adequate low-impedance connection is a matter of conductor resistance.   At the high frequencies involved with transient disturbances, the inductance of the connection becomes significant.

This conflict is actually very simple to resolve if recognized in time: provide an outer shield, grounded at both  ends (and at any possible intermediate points); inside this shield the electronic designer is then free to enforce his single-point grounding rules.   The only drawback to this approach is the hardware cost of double shields.  In many installations, however, there is a metallic conduit through which the cables are pulled; with simple but close attention to maintaining the continuity of this conduit path, through all the joints and junction boxes, a very effective outer shield is obtained at negligible additional cost.  In the case of underground conduit runs, the most frequent practice is to use plastic conduit, which unfortunately breaks the continuity.    System designers would be well advised to require metal conduits where the circuits are sensitive or, at a minimum, to pull a shielded cable in the plastic conduit where the shield is used to maintain continuity between the above-ground metal conduits.    That additional cost, then, is the insurance premium, which is well worth accepting.     Case History No. 1, given later in this report, illustrates the penalty inflicted by nature when the one-and-only one-ground rule was misapplied by the designer.

### Bonding

We have already mentioned one aspect of bonding in describing the continuity of the outer shield.  Another instance of bonding occurs where the shield of an incoming cable is connected to an equipment cabinet in order to allow shield current flow.  The shield current flows in the connecting pigtail and creates electromagnetic radiation at the point of cable entry.

Adjacent cabinets in a lineup must be bonded together for safety as well as transient and noise immunity.  In principle, a flat strap has a lower inductance than a round wire of the same area.  This concept may be somewhat overused; actually several strategically located smaller wires provide a much more effective bond than one massive strap, either round or flat.  The difficulty lies in implementing this alternate view, and overcoming the comforting sight of a large grounding strap at the bottom of the cabinet lineup.  Such a strap does no harm and is a good safety practice, but it may not do as much good as expected from the point of view of surge protection, compared to multiple point bonds.

A significant subset of the general subject of bonding is the termination of cable shields by connectors at the junction to an equipment cabinet.    The search for low-cost construction often  results in  the shield being connected through one pin of the multiple-pin connector.  Add to this construction the misguided concept that all grounding connections in a cabinet should be made to a single point, and the result will be the worst possible practice, as shown in Figure 18A: the shield current is injected inside the cabinet along a tortuous path, creating interference in all circuits.  Figure 18B shows a tolerable practice, where the connection is still made through the connector, for convenience, but a very short lead makes the connection to the cabinet frame inside the cabinet.  Figure 18C shows an improvement, with the connection made outside the cabinet.  A variation of this arrangement is encountered in RS232 connectors with a metal shell where the two securing screws provide a double (and symmetrical) bond to the equipment chassis.  The ultimate and best bond, of course, is obtained by using a connector with a continuous bond provided by a cable connector with metallic shell and ring screwed to the chassis connector all around the cable (Figure 18D).

### Grounding

Grounding, or earthing, has different meanings as well as different roles.  The primary definition is the connection of the circuit, shield, or reference to earth.     But what is earth?    System designers, construction crews, inspectors, and technical conference authors are concerned with establishing, measuring, and maintaining a low ground resistance, often determined by dc measurements on rods driven into the ground.  Driving many rods into the ground at great expense does not ensure a low impedance under the transient conditions of a high rate of current change associated with lightning discharges.

When one deals with a reasonably compact system, be it cabinet-size, room-size, or building-size, it is more effective to view the grounding as a well-bonded connection to the outer shield (if any), building frame, or cabinet enclosure, acting as a zero-reference.    The resistance (impedance) from that reference to earth is not very significant as long as other wires at ground potential are not brought to the system.  Since there is little chance of dealing with an absolutely isolated system (short of a flying aircraft, which does quite well, thank you, without an earth connection), the question is:   What should be done with incoming wires? These wires can be isolated from the local ground during normal operation, but one must recognize that, during transient  conditions of lightning surges or power system faults, high voltages will appear across these isolated wires and local ground - voltages which, in some cases, are far beyond the withstand capability of insulation.  That insulation, then, must be protected by suitable devices which, in fact, do connect the wires to the local ground, but only for the duration of the transient.  This type of momentary grounding is one function of transient suppressors.

An effective approach to limiting the adverse effects of ground potential differences is the enforcement of a "ground window"* arrangement of all conductors entering a system, as shown in Figure 19.  The system can be a single cabinet, room-size equipment, or a complete floor in a building - the principle remains the same.  This ground window must be specified from the beginning, as retrofits are generally difficult to make.

5.3  Isolation of subsystems

In the case of systems involving separate buildings, remote sensors, or the interconnection of a power system with a communication system, other requirements may dictate the isolation of the subsystems, creating the illusion that protection against overvoltages has also been accomplished.  And yet we have seen that during transient conditions high voltages can occur between the subsystems.

Where moderately high voltages only can occur, effective isolation can be accomplished by the insertion of an isolating transformer or an opto-isolator; if metallic isolation is not required, a filter can also be used if it does not degrade data pulse shapes or system frequency response.

Where the voltages will reach levels exceeding the withstand capability of economically or technically feasible insulation, two possible solutions exist.  The first, already mentioned, and applicable to power as well as data systems, is to bond the grounds or references of the two systems during the transient by means of a surge protective device, which returns to a high level of insulation after the transient has subsided.   The second, applicable only to low-power data transmission, is to use other methods, such as insertion of audio couplers or a fiber optics link.  Complete decoupling of electrical transients and noise resulting from ground potential differences can be achieved in this manner; however, these techniques will not guard against noise collected by the circuits themselves and faithfully transmitted by the link to the other end.

6.  TRANSIENT SUPPRESSORS

Various devices have been developed for protecting electrical and electronic equipment against transients.  They are often called "transient suppressors" although, for accuracy, they should be called "transient limiters.......  clamps," or "diverters" because they cannot really suppress transients; rather, they limit transients to acceptable levels or make them harmless by diverting them to ground around the sensitive equipment.

There are two categories of transient suppressors: those that block transients, preventing their propagation toward sensitive circuits, and those that divert transients, limiting voltages to an acceptable residual level.   Because many of the transients originate from a current source, the blocking of a transient may not always be possible; thus, diverting the transient is more likely to find general application.   A combination of diverting and blocking can be  a very effective approach.  This approach generally takes the form of a multistage circuit, where a first device diverts the transient toward ground, a second device - an impedance or resistance - offers a restricted path to the transient propagation but an acceptable path to the signal or power, and a third device clamps the residual transient  (Figure 20).  Thus, we are primarily interested  in  the diverting devices.  These diverting devices  can be of two kinds: voltage-clamping devices  or short-circuiting devices (crowbar).  Both involve  some nonlinearity, either frequency nonlinearity (as in filters) or, more usually, voltage nonlinearity.  Depending on the type of device, this voltage nonlinearity is the result of two different mechanisms - a continuous increase in the device conductivity as the current increases, or an abrupt switching as the voltage increases.

Because the technical and trade literature contains many articles on these devices, a discussion of the details will be limited and review of the references is suggested.  Some comparisons will be made,   however,   to point out the significant differences in performance; clarification of some issues resulting from unwarranted concern will also be given.  We will first examine the basic principles of single-component suppressors, then the application of these devices to protect circuits, as single- or multiple-component packaged devices.

  - Crowbar devices

The principle of crowbar devices is simple: upon occurrence of an overvoltage, the device changes from its normal high-impedance state to a low-impedance state, offering a low-impedance path to divert the surge to ground.  This switching can be inherent to the device, as in the case of spark gaps involving the breakdown of a gas or the recently introduced two-terminal multi-junction semiconductors.  Some applications have also been made of externally triggered devices, such as triggered vacuum gaps in high-voltage technology or thyristors in low-voltage circuits, where a control circuit senses the rising voltage and turns on the surge-rated device to divert the surge.

The major advantage of the crowbar device is that its low impedance allows the flow of substantial surge currents without dissipation of high energy within the device itself-, the energy has to be spent elsewhere in the circuit.  This so-called "reflection" of the impinging surge can also be a disadvantage in some circuits when the transient disturbance associated with the gap firing is being considered.  Where there is no problem of power-follow (discussed below), such as in communication circuits, the spark gap has the advantage of very simple construction with potentially low cost.

The crowbar device, however, has three major limitations.  The first limitation concerns the volt-time sensitivity of the breakdown process.  As the voltage increases across a spark gap, a significant conduction of current - and hence the voltage limitation of a surge - cannot take place until the transition occurs to the arc mode of conduction by avalanche breakdown of the gas between the electrodes.  The load is left unprotected during the initial rise because of this delay time (typically in microseconds).  Considerable variation exists in the sparkover voltage achieved in successive operations, because the process is statistical in nature.  In addition, this sparkover voltage can be substantially higher after a long period of rest than after successive discharges.   From the physical nature of the process, it is difficult to produce consistent sparkover voltage for low-voltage ratings.  This difficulty is increased by the effect of manufacturing tolerances on very small gap distances, but it can be alleviated by filling the tube with a gas having a lower breakdown voltage than air.  However, if the enclosure seal is lost and the gas is replaced by air, this substitution creates a reliability problem due to the substantially higher sparkover of the air gap.

In communication circuits using a pair of conductors, protection is often provided by connecting a gas tube between each conductor and ground.  Upon occurrence of a common mode surge, which would leave the input circuits unaffected, an nature of the process, it is difficult to produce consistent sparkover voltage for low-voltage ratings.   This difficulty is increased by the effect of manufacturing tolerances on very small gap distances, but it can be alleviated by filling the tube with a gas having a lower breakdown voltage than air.  However, if the enclosure seal is lost and the gas is replaced by air, this substitution creates a reliability problem due to the substantially higher sparkover of the air gap.

In communication circuits using a pair of conductors, protection is often provided by connecting a gas tube between each conductor and ground.  Upon occurrence of a common mode surge, which would leave the input circuits unaffected, an undesirable condition results from the volt-time variation between the two devices: unavoidable manufacturing tolerances between the two devices, plus the statistical variation for each tube breakdown cause one tube to fire before the other.  During the time separating the two firings, a substantial normal surge is applied to the input circuitry, with possible destructive effects (Figure 21).  This problem can be avoided by using three-electrode tubes where firing of the first gap causes firing of the second gap with no delay (Figure 22).

The second limitation is associated with the sharpness of the sparkover, which produces fast current rises in the circuits and, thus, objectionable noise.  A classic illustration of this problem is found in oscillograms recording the sparkover of a gap where the trace exhibits an anomaly before the sparkover (Figure 23).  This anomaly is due to the delay introduced into the oscilloscope circuits to provide an advanced trigger of the sweep.

What the trace actually shows is the event delayed by a few nanoseconds, so that in real time, the gap sparkover occurs and noise enters the oscilloscope by stray coupling, while the electron beam is still writing the pre-sparkover rise.  Another, more objectionable, effect of this fast current change can be found in some hybrid protective systems.  The circuit of one such commercial device is shown in Figure 24.  The gap does a very nice job of discharging the impinging high-energy surges, but the magnetic field associated with the high di/dt induces a voltage in the loop adjacent to the second suppressor, adding what can be a substantial spike to the expected clamping voltage provided by the second device.  An illustration of this effect is discussed in Case History No. 1.

A third limitation occurs when a power current from the steady-state voltage source follows the surge discharge (follow-current or power-follow).  In ac circuits, this power-follow current may or may not be cleared at a natural current zero.  In dc circuits, clearing is even more uncertain.  Additional means, therefore, must be provided to open the power circuit if the crowbar device is not designed to provide self-clearing action within specified limits of surge energy, system voltage, and power-follow current.  This combination of a gap with a current-limiting, nonlinear varistor has been very successful in the utility industry as a surge arrester, often referred to as a "valve-type arrester."

  - Voltage-clamping devices

Voltage-clamping devices exhibit a variable impedance, depending on the current flowing through the device or the voltage across its terminals.  These components show a nonlinear characteristic – that is, Ohm's law can be applied, but the equation has a variable R. Impedance variation is monotonic and does not contain discontinuities, in contrast to the crowbar device, which shows a discontinuity by turn-on action.  As far as volt-ampere characteristics are concerned, these components are time-dependent  to a certain degree.  However, unlike the sparkover of a gap or the triggering of a thyristor, time delay is not involved.

When a voltage-clamping device is installed in a circuit, the circuit remains essentially unaffected by the device before and after the transient for any voltage below clamping level.  Increased current drawn through the device as a surge voltage attempts to rise results in voltage-clamping action.   Nonlinear impedance means that this current increases more than the voltage.  The increased voltage drop (IR) in the source impedance due to higher current results in the apparent clamping of the voltage.  It should be emphasized that the device depends on the source impedance to produce clamping.  A voltage divider action is at work where the ratio of the divider is not constant, but changing.  If the source impedance were very low, the ratio would be low, and eventually the suppressor could not work at all with a zero source impedance (Figure 25).  In contrast, a crowbar type of device effectively short circuits the transient to ground; once established, however, this short circuit will continue until the current (the surge current as well as any power-follow current supplied by the power system) is brought to a low level.

The principle of voltage clamping can be achieved with any device exhibiting this nonlinear impedance.  Two categories of devices, having the same effect but operating on very different physical processes, have found acceptance in the industry: polycrystalline  varistors and single-junction avalanche diodes.  Another technology, selenium rectifiers, has been  practically eliminated from the field because of the improved characteristics of modern varistors.

  - Avalanche diodes

Avalanche diodes, or Zener diodes, were initially applied as voltage clamps, a natural out-growth of their application as voltage regulators.  Improved construction, specifically aimed at surge absorption, has made these diodes very effective suppressors.   Large-diameter junctions and low thermal impedance connections are used to deal with the inherent problem of dissipating the heat deposited by the surge in the small volume of a very thin single-layer junction.

The advantage of the avalanche diode, generally a P-N silicon junction, is the possibility of achieving low clamping voltage and a nearly flat volt-ampere characteristic over its useful power range.  Therefore, these diodes are widely used in low-voltage electronic circuits for the protection of 5 V or 15 V logic circuits, for instance.  For higher voltages, the heat generation problem associated with single junctions can be overcome by stacking a number of lower voltage junctions, admittedly at some extra cost.

Silicon avalanche diodes are available with characteristics  tailored  to transient suppression.  These should not be confused with regulator-type Zener diodes although many engineers tend to use the generic term "Zener diode." May Zeus help them if they misapply a regulator-type Zener, expecting to achieve good protection!

Since the junction is very thin, the capacitance of an avalanche diode is appreciable.  This can be a concern.  The effect of capacitance can he minimized by  using series combinations with low-capacitance diodes (Figure 26).

  - Varistors

The term varistor is derived from the function of the device as variable resistor.  This device has also been called a voltage-dependent resistor, but that description tends to imply that voltage is the independent parameter in surge protection, while in fact surge current is the given parameter.  Two very different devices have been successfully developed as varistors: silicon carbide blocks have been used for years in the surge arrester industry, and more recently, metal oxide varistors have become widely used.

Metal oxide varistors depend on the conduction process occurring at the boundaries between grain of oxide (typically zinc oxide) grown in a carefully controlled sintering process.   The physics of the nonlinear conduction mechanism have been described in the literature. (31-35)

Because the prime function of a varistor is to provide the nonlinear effect, other parameters are generally the result of tradeoffs in design and inherent characteristics.  The electrical behavior of a varistor can be understood by examination of the equivalent circuit of Figure 27.    The major element is the varistor proper, Rave,  whose V-I characteristic is assumed to be the perfect power law, I = kV".  In parallel with this varistor, there is a capacitor, C, and a leakage resistance, Rap.  In series with this three-component group, there is the bulk resistance of the zinc oxide grains, Rest, and the inductance of the leads, L.

Under dc conditions (at low-current densities because obviously no varistor could stand the high energy deposited by dc currents of high density), only the varistor element and the parallel leakage resistance are significant.   Under pulse conditions at high-current densities, all but the leakage resistance are significant: the varistor provides low impedance to the flow of current, but eventually the series resistance will produce an upturn in the V-I characteristic; the lead inductance can give rise to spurious overshoot problems if not dealt with property; and the capacitance can offer either a welcome additional path for fast transients or an objectionable loading at high frequency, depending on the application.

When the V-I characteristic is plotted on a log-log graph, the curve of Figure 28 is obtained.  Three regions result from the dominance of Rap, then Rave, and finally R, as the current in the device increases from Nan amperes to kilo amperes.

The V-I characteristic is then the basic application design tool for selecting a  device in order to perform a protective function.  For a successful application, however, other factors, discussed in  7.6.

  - Packaged suppressors

The need for protection and the opportunity to provide packaged protective devices to concerned computer users has prompted the marketing of many packaged suppressors, ranging from the very simple and inexpensive to the complicated (not necessarily much better) and expensive.  The field has also seen a number of devices claiming energy savings in conjunction with transient suppression; there is no foundation for such a claim, and the issue, hopefully, has now been settled in a study published by EPRI. (36)

Component surge protective devices such as gaps, varistors, or avalanche diodes are used by manufacturers for  incorporation into the circuitry of their products.   In contrast, packaged suppressors are applied by  prudent users as preventive and complementary protection, or by aggrieved users as retrofit protection.  These packaged suppressors may contain only a single protective device or a combination of devices; they are available for power-line protection, for data-line protection, and also in combined power/data lines protection.

The combined power/data lines protection packages offer not only convenience for protecting both lines of peripheral or remote equipment but also, and very important, permit the implementation of a common reference (ground) between the power and the data line.  This common reference can be located right at the point of installation, and thus realize the ground window approach discussed in the preceding section.

A new type of suppressor has also appeared on the market, the so-called "tracking protectors." This type of device provides a voltage-limiting action over a narrow band of deviation from the power-frequency sine wave, rather than the fixed, absolute voltage limit of clamping or crowbar devices.  Typical circuits involve the switching on of a shunt capacitor when the instantaneous voltage deviation exceeds a preset limit.

Packaging of the suppressors accomplishes two desirable goals: convenience of insertion by the user and coordination of the design for multiple-component protective schemes.  Unfortunately, this packaging sometimes intentionally obscures the principles of protection being offered, making an evaluation of performance claims difficult.  The competitive nature of these products is an unavoidable reality, which does not justify obscuring performance characteristics, even if some users are only interested in simple assurances that the devices packaged will provide them with adequate protection.

One reason for the frequent lack of information on the performance of the packages being offered is a lack of standards that would provide manufacturers and users with realistic and uniform application requirements.   Component protective devices have the benefit of  presently available test specification standards,  (24-27)   but standards-writing groups have not yet completed their projects on packaged suppressors.  In particular, the IEEE has an ongoing project that will take several years of work before publication; the Underwriters' Laboratories (UL) are approaching release of a document (36)  that will provide not only safety guidance but also a more uniform basis of comparison of the packages being offered in the trade.

As an example of power line packaged suppressors, the recently introduced General Electric VSS device offers plug-in protection with both line-to-neutral and neutral-to-ground protective devices (Figure 29).  Further protection against low-level, high-frequency disturbances is obtained with the VNS device, which has an L-C filter added to the package (Figure 30).

The presence of neutral-to-ground protection in these two packages is a definite improvement over the simpler packages, which provide only line-to-neutral or neutral-to-line protective devices.  Each of these two simpler devices may leave parts of the "protected" load unprotected during the occurrence of certain types of surges, as mentioned in the common mode/normal mode discussion of the preceding section.  Figure 31 illustrates the complete protection provided by the dual devices, and Figure 32 shows the incomplete protection of the simple devices, where a normal mode surge is converted into a voltage transient between the neutral and the grounding conductor.

  - Line conditioners as surge suppressors

The need to provide "clean power" to sensitive electronic equipment has promoted the development of a wide variety of devices generally described as "line conditioners." Depending upon the design and principle involved, these devices can perform several of the following functions: line isolation, voltage regulation (medium- and long-term), noise suppression, surge suppression, common  mode suppression, and back-up power supply.   Close inspection of the specifications is required to distinguish the details of the performance of these devices.  Their principle of operation can be used to categorize the types:

- Ferro resonant transformers (primarily regulation)

- Isolation transformers with filters (primarily common-mode decoupling)

- Motor-generator sets (primarily decoupling and short-time ride-through)

- Magnetic synthesizers (primarily regulation)

- Electronic synthesizers (primarily regulation)

- Electronic rectifiers/battery/inverters (primarily uninterruptible power supplies)

When properly understood and applied, these devices can provide not only their desired primary functions, but surge suppression as well - a welcome side effect.  A notable exception, resulting from misunderstanding of the application, is discussed in Case History No. 4.

  - Failure modes

Failure of an electrical component can occur because its capability was exceeded by the applied stress or because some latent defect in the component went unnoticed in the quality control processes.  While this situation is well recognized for ordinary components, a surge protective device, which is no exception to these limitations, tends to be expected to perform miracles, or  at least to fail graciously in a fail-safe mode.   The term "fail-safe," however, may mean different failure modes to different users and, therefore, should not be used.   To some users, fail-safe means that the protected  hardware must never be exposed to an overvoltage, so that failure of the protective device must be in the fail-short mode, even if it puts the system temporarily out of operation.   To others, fail-safe means that the function must be maintained, even if the hardware is left temporarily unprotected, so that failure of the protective device must be in the open-circuit mode.  It is more accurate and less misleading to describe failure modes as fail-short or fail-open, as the case may be.

When the diverting path is a crowbar-type device, little energy is dissipated in the crowbar, as noted earlier.   In a voltage-clamping device, because more energy is deposited in the device, the current-handling capability of a candidate protective device is an important parameter to consider in the design of a protection scheme.  With nonlinear devices, an error made in the assumed value of the current surge produces little error on the voltage developed across the protective device and thus does not affect the protective function (Figure 33).   However, the error is directly reflected in the  amount of energy which the protective device has to absorb.  At worst, when surge currents in excess of the  protective device capability are imposed by the environment (for example, an error made in the assumption, a human error in the use of the device, or nature's tendency to support Murphy's law), the circuit in need of protection can generally be protected at the price of failure of the protective device in the short-circuit mode.  However, if substantial power-frequency currents can be supplied by the power system, the fail-short protective device generally terminates as fail-open when the power system fault in the failed device is not quickly cleared by a series overcurrent protective device (fuse or breaker).

With the failure mode of a suppressor being of the fail-short type, the system protection with fuses can take two forms (Figure 34).   For the user concerned with maintaining the protection of expensive equipment, even if failure of the protector means the loss of the function, Alternative A must be selected.    Conversely, if the function is paramount, Alternative B must be selected.

7.  EXAMPLES AND CASE HISTORIES

To illustrate the preceding considerations, some practical examples are given in this section as the basis for sound design approaches, or as horror tales where the names of the "guilty" have been withheld: it is always easy, with hindsight, to see what should have been done, but less easy at the outset for engineers unfamiliar with surge protection and more concerned with other system considerations.

These case histories show how unintentional but clear violations of the principles described in this report resulted in the problems that follow:

Case 1:		Ground potential differences on data lines caused by discontinuous shield

Case 2:		Ground potential differences on power lines caused by ignorance of the ground window approach

Case 3:		Insufficient and poor utilization o protection

Case 4:		Misunderstanding of common versus normal mode

Case 5:		Controversies on connection options

Case 6:		Measurement problems

Case 7:		Unwanted surge suppression by a instrument

Case 8:		Undersized protective device

The detailed explanations of the problems and cures in these case histories are offered as a help to avoid these types of pitfalls.

Case History No. 1 - 	Computer graphics system:  Ground potential difference on data lines

A CAD/CAM graphics system had bee installed by a computer graphics vendor linking central processing unit to remote terminals locate in separate buildings.  In a span of 5 weeks during the first summer after the system was commissioned, three lightning storms occurred in the area; no direct strikes were reported on the buildings, but extensive damage was done to the circuit boards on terminals and central processing unit (CPU) inputs.

After the first occurrence, power line surges were suspected and some precautions were applied, when access to the hardware was possible, by pulling out the ac power plugs from the CPU or terminals at the onset of a lightning storm.  This did not help.  Next, isolating transformers were installed but, again, did not help.  At this point, the author was called in for consultation, and the following proposed diagnosis was established: the surges were not coming from the ac lines but, rather, were due to differences in the ground potential existing between the separate buildings during flow of lightning currents.  The data cables had been run in plastic conduit buried between the buildings and, true to the controversial tenet of steady-state noise prevention, only one end of the shield of the wire pairs had been grounded, with the other left floating.  Figure 35 shows how this arrangement can produce high voltages between a floating end of the shield and the local ground, an arrangement that is bound to produce a flashover and flow of surge currents along unwanted paths in the circuit components.  Thus, the problem was not power line surges but differential ground potential.  Worse, by pulling out the ac line plugs but leaving the incoming data cables connected, the operators had unwittingly removed the local grounding connection of the hardware frame, leaving only the data cables coming in, with a possibility of raising the complete hardware several thousand volts above local grounds in the room a dangerous condition.

A solution to the problem could take several approaches.   Radical solutions, such as a microwave link or a fiber optics bundle, would indeed have eliminated the differential ground potential problems, but were considered too expensive or too long to install.

Incidentally, part of the original bewilderment at the failures was the notion that opto-isolators provided in the data link route should have served to avoid problems.  Close scrutiny of the circuits, however, disclosed that the opto-isolators had been provided for some other purpose; in fact, the ground potential loop was closed by the power supply to the opto-isolator feeding the amplifiers from a local source rather than the remote source, negating the isolation function.

Another solution, really the most simple and effective in principle, would have been the replacement of the plastic underground conduit by a continuous steel conduit linking the steel conduits used inside the buildings. This additional metal would have provided equalization of the ground potentials along the data cable, while allowing, within the conduit, the desired use of shields with one end only at ground.  However, that solution was not acceptable to the plant facility organization.   (One does not dig up the front lawn two times within a few months at an industrial park!)

In this particular location, a spare conduit, buried next to the data line conduit, offered the possibility of pulling a heavy ground cable in the spare conduit,. close to the data cables.  This cable the computer vendor, so that it was not implemented until the next lightning season, the spring of 1981.  Thus, the system survived all of the remainder of the 1980 lightning season with only the first two remedies.

Voltage clamps were designed for insertion at each end of the data cable, at the point where the cables were terminated prior to connection to the CPU or to the terminal (Figure 37).  The objective was to clamp any transient developed in the pair, with respect to ground, at less than 25 V, without introducing excessive degradation of the pulses' fronts in the signals transmitted by the cables.   Vendors of hybrid protection packages were consulted and samples were obtained for evaluation.  All these samples consisted of a gas tube protective device connected between the line and ground and followed by some resistance, and a silicon avalanche suppressor between line and ground (Figure 38).  The criteria were the optimization of the RC parameters of the suppressor R being the series resistance, and C the capacitance of the silicon diode - for maximum suppression with limited and acceptable decrease in the steepness of the data pulses.

During evaluation testing of the various candidate suppressors submitted by prospective vendors, it became apparent that the physical layout of the components had an effect on the clamping voltage obtained: when the gas tube gap sparked over, the high di/dt in the gap produced a high rate of flux change in adjacent loops, in particular the loop involving the second-stage avalanche diode and the load (Figure 39).  While the clamping voltage of the avalanche diode was, in fact, 15 V, as much as 45 V spikes were recorded across the output of the packaged hybrid suppressors, raising doubts about the effectiveness of the protection.  These spikes were extremely short (nanoseconds), but the vendor of the integrated circuits that had failed in the initial problems would not agree to consider more than the specified maximum 25 V overvoltage, even for these very short spikes.

Since the proposed connection between the interface box in the terminal or CPU rooms and the terminal equipment involved a flexible connection by shielded pairs, a simple solution was possible.  The inherent capacitance of the pairs to their shield, combined with an additional resistance at the output of the hybrid suppressor could reduce this induced spike below 25 V (Figure 40).  Thus, an acceptable package was designed, providing for the clamping of any surge to a level below the tolerance level of the integrated circuits of the line drivers or line receivers, but still not producing an objectionable degradation of pulse fronts.  The complete protection scheme was installed before the 1981 lightning season, and no further problems have been reported.

Experience has shown that conclusions on the effectiveness of lightning protection schemes should wait perhaps as much as 10 years before being proclaimed, because of the large variations in lightning activity.  However, after several years of trouble-free operation compared to three major failures in 5 weeks, the cure would seem effective.

In retrospect, then, the following recommendations can be drawn from this horror tale,' for retrofits or new installations:

1.	Data cables linking separate buildings or spanning beyond a single room within one building should have a shield tied to local ground at both ends of the cable.  If the first shield provided with the cables must be left with one end floating by diktat of the system vendor, then these cables should be installed within a continuous metal shield.  This continuous shield can be either a double shield of the flexible cable or simply a metal conduit with both ends grounded and proper attention to maintenance of its continuity.

*Which, in the last several years, was found repeated at several other facilities involving different systems but the same basic problem.  Thus, this case history has achieved the status of "classic" or "textbook" importance.

2.	Substantial relief can be obtained in retrofits by grounding both ends of existing shields through a low-voltage clamp, such as a diode array, that will block noise-inducing power frequency currents but will allow the flow o ground-potential equalizing currents during surges.

3.	The ultimate protection may be the insertion of surge-protective devices in each line.  However, this solution requires careful design so that degradation of the signals does not occur and residual spikes are not allowed to pass through.

4.	While damage prevention can be accomplished by these approaches, data errors may still be produced.  If data integrity is an absolute requirement, metallic connections should be avoided for data links spanning remote terminals.

Case History No. 2 - 	Computer-aided industrial control: Ground potential differential on the

power lines (absence of ground window)

In this situation, a novel  adaptive  control  using sophisticated microprocessor-based sensors and phase-control of power thyristors, limited to a single room in a building, had suffered system crashes and memory component damage on repeated occasions.   Suspicions developed that there was some correlation between the crashes or damage and the operation of another developmental power system in an adjacent laboratory.  The software engineers working on the control system were attempting to continue their work by staggering the schedule with their neighbors; they were also considering installation of an independent power feeder to their system.

From another point of view, focused by the author, this case presented an opportunity to learn, while still in the laboratory, what the real world can inflict on unprotected computerized power systems.  Rather than blame the power supply, a more fruitful approach for the long run would be to develop immunity to interference and damage.  In defense of the system designers, it should be pointed   out that their system had enough challenges to be tackled in the main objectives that it might have seemed reasonable to overlook the interference problems in the initial stages.   Sooner or later, however, the ignored problems will crop up, and, sooner is better than later when fundamental design concepts are involved.

A review of the total system revealed the existence of ground loops.   On one side, the power supply for the computer  and some signal processing circuits were obtained from the room outlets of the laboratory 120 V system, including the grounding conductor (green safety wire).  On the other side, the power supply for the high-power circuit was obtained from a feeder coming directly from the building power center, including again a grounding conductor run alongside this power line, properly installed by electricians, and bonded to the frame of the machine being con-trolled.   One of the signals used for controlling the process was derived from a voltage pickup referred to the frame of the machine, while the chassis of the computer and its zero reference were bonded to the grounding conductor of the 120 V room supply.  Thus, a double ground loop was formed: one between the grounding conductor of the 120 V room supply and the power-feed grounding conductor, and the other between the overall zero reference of the signal processing and the voltage pickup with its separate ground reference (Figure 41).

With hindsight, it was not difficult to conclude that during transient conditions involving the high-power feed to this system and the neighboring system, substantial current could flow between the two grounding wires linked by the computer reference wiring.  An immediate cure was to open this path for surge ground currents by inserting an isolating transformer in the 120 V supply to the computer, and bonding   the secondary side of this transformer to the single ground point derived from the high-power feed (a   National Electrical Code requirement).  This correct application of an isolating transformer, to open a ground loop, is in contrast to the misconception that isolating transformers can eliminate line-to-line spikes, as discussed in Case History No. 4.

Opening the second ground loop involving the voltage pickup could not be as readily implemented because it required a differential voltage pickup circuitry.  Plans for further refinements of the system included this change, but even with only the first ground loop opened, the major crashes and damage stopped; only occasional interference occurred, probably not associated with the second group loop but, rather, with a more subtle software problem associated with sensing the power flow in the system.  Clearly, the first ground loop was one of the major sources of the problem, a problem that would have been avoided if the system had been arranged with a single ground window.

Case History No. 3 - 	Outdoor recorder retrofit: Insufficient surge protection against

line-to-ground surges

In this case history, a field failure problem was caused by a lack of awareness (on the part of the circuit designer) of the degree of hostility in the environment where the circuit was to be installed.  A varistor had been provided to protect control circuit components on the printed circuit board, but its capability was exceeded by the surge currents occurring in the particular location.      In defense of the circuit designer, however, it must be stated that he was unaware of the data published in IEEE Std 587 (now ANSI/IEEE C62.41).

Since a number of devices were in service, complete redesign was not possible, and a retrofit – at an acceptable cost – had to be developed.    Fortunately, the power consumption of this control  circuit was limited, so that it was possible to insert some series impedance in the line, ahead of the low-capacity varistor, while a higher capacity varistor was added at the line entrance to the circuit (Figure 42).   Laboratory proof-testing of the retrofit demonstrated  the capability of the combined scheme to withstand 6 kA crest current surges (Figure 43), which is a 200% margin from the suggested IEEE/ANSI C62.41 Category B level.  Furthermore, it  demonstrated reproduction of the field failure   pattern (Figure 43).  The latter is an important  aspect of any field problem retrofit.  By simulating  in the laboratory the assumed surges occurring in the field, verification of the failure mechanism is the first step toward an effective cure.  Figure 43 illustrates the effect of improper installation of the suppressor in a first retrofit attempt with 8 inches of leads instead of a direct connection across the input terminals of the circuit.    The author has observed far too many applications  of varistors with excessive lead lengths, to the point that the protection is substantially reduced for fast rising surges, the present case being typical.

## Case History No. 4 - 	Does an Isolating transformer help?

The author has witnessed and engaged in many discussions on the merits of isolating transformers, sparked by the misconception that "spikes are attenuated by transformers" or "spikes do not pass through transformers."   Figures 44 through 46 are offered to support the position that these quotations are misconceptions.   When properly applied, isolating transformers are useful to break ground loops, but they do not by themselves attenuate spikes that occur line-to-line, the so-called "normal mode."

Figure 44 shows the propagation - or worse, the enhancement - of a voltage impulse in a 1:1 isolating transformer.  The 6 kV, 0.5 s-100 kHz impinging wave of ANSI/IEEE C62.41 is applied to the primary of the transformer, H1H3 to H2H4.  The output voltage, measured at X1X3 to X2X4, appears as a 7 kV crest on the secondary side of this "isolating" transformer.

Figure 45 shows the similar behavior of a transformer offered as a line isolator.  This transformer is intended to provide low effective capacitance and ground loop isolation between primary and secondary windings, but here again, the author has observed that users of this device expect attenuation of spikes.  The response of this isolator, due to its internal construction, is different from that of the simple two-winding transformer of Figure 44, but we also note that a crest of 8 kV occurs on the secondary side during the second half-cycle.  Hardly an improvement.

Figures 44 and 45 were recorded with no load on the transformer secondary, which represents the extreme case of a low-power electronic control in standby mode.  Figure 46 shows the primary and secondary voltages of the transformer with a 10 W (1500 ) and a 100 W (150 ) load on the secondary side, at the same surge generator setting as Figure 44.  With the 10 W load that might be typical of an electronic control in standby mode, the combined series reactance of the transformer and shunt resistance of the load produce the output shown in Figure 46, still slightly higher than the input.

With the 100 W load shown in Figure 46, the attenuation is now apparent, but is only 2:1.  Capacitive loads would, of course, produce a greater attenuation than resistive loads for the inductive series impedance of the transformer, at the frequency spectrum of this fast, 2 s, wide spike.  For surges of longer duration, the attenuation would be even smaller.

These examples show that, unless a well-defined load is connected to the transformer, expecting attenuation from the transformer may prove to be hazardous to the health of low-power electronics connected on the secondary side of a transformer.

By contrast, decoupling is possible with a ferro-resonant line conditioner which is primarily intended for line voltage regulation but which also provides a high degree of surge suppression.  Figure 47 shows the 6 kV incoming wave being attenuated to 60 V (100:1) on the secondary side of the unloaded line conditioner, and to 40 V (150:1) with a load of only 10%; at full load, an attenuation to less than 10 V was observed.  The nature of the ferro-resonant line conditioner is such that the decoupling improves with loading, while the simple transformers of Figures 44, 45, and 46 can only act as linear dividers with load changes.  Conversely, the decoupling between primary and secondary sides of the line conditioner is further seen on the oscillogram recorded on the input side of the line conditioner.  This oscillogram is, in fact, a photograph of two successive measurements, one with no load on the line conditioner and one with a 100 W load.  The input waves are exactly superimposed.

This decoupling reflects the nonlinear behavior of the ferro-resonant line conditioner, which is significant in this case, compared to the linear behavior of transformers:    For surge sources of lower impedance than the generator used in these tests, or for frequencies lower than the frequency contained in the 0.5 s - 100 kHz spike, the transformer attenuation would become lower, in direct proportion to the corresponding impedance change, while the ferro-resonant line conditioner would keep the decoupling unchanged.  See also Case History No. 7 for an application of a ferro-resonant line conditioner to decouple a surge protective device from the power supply, the inverse situation of what is described here.

For worst-case demonstration, the two oscillograms of the output were recorded with the spike timed to occur at the peak of the 60 Hz line voltage demonstration.  The peak-to-peak amplitude of the line voltage is indicated by the gray band recorded on the oscillograms by photographically superimposing repetitive traces of the line voltage.  For timings other than at peak, the small voltage oscillation on the output voltage would be completely contained within the normal peak-to-peak band of the 60 Hz line voltage.

## Case History No. 5 - 	Connections options for suppressors and effects on residual voltages

The author has witnessed lively controversies over the most effective transient suppression configuration to be applied.  Taking, as an example, the task of specifying the protection of an appliance or equipment connected at the end of a line with no opportunity to divert the transient closer to the source (for instance, at the service entrance), the options would be to connect one, two, or three varistors between the three wires (black, white, and green) at the end of the line.  However, additional information needs to be known: Will the impinging surge be in the normal mode (black-to-white) or in the common mode ([black-and-white-to-green)? Where in the equipment is the most sensitive component: line-to-line (most likely) or line (black or white)-to-green?  Clearly, the situation is confusing, and there will not be a single, simple answer applicable indiscriminately to all cases.  The National Electrical Code  (39)  specifically allows the connection of surge arresters between neutral and grounding conductors (Article 280-22) if the interconnection occurs only by operation of the surge arrester during the surge.  Since the standby current of varistors is very low, this requirement can be met; furthermore, there will not be any interference with the operation of Ground Fault Circuit Interrupters if there are only a small number of protectors.

The set of measurements recorded in Figure 48 shows an example of these many options with increasing protection, albeit at increasing cost, from a single varistor to three varistors.  The selection would depend on the vulnerability level and location of the equipment to be protected.  The impinging surge is assumed to be black-to-[white-and-green], since white and green are tied together at the service entrance. The line is a 75 m line and the surge is that available from the generator set for a 2000 A 8/20 s short-circuit impulse.  Rather than attempt to modify the setting of the generator for each case in order to maintain a constant current crest for the various configurations (an impossible task if waveform is also to be maintained), the generator was left unchanged, to discharge a constant total energy into the system - not a bad hypothesis for the real world.  The current crests are all in the range of 300 to 380 A, which is not a significant variation for comparing varistor clamping voltages.

Only one varistor is allocated to protect the equipment, the black-to-white varistor connection (first row) affords maximum protection for the electronics, which are also likely to be connected black-to-white.  However, the voltages between either black or white and green are large; that voltage is the stress that will be applied to the clearances of the equipment.  This situation is a good example of the conversion of a normal mode transient into a common mode, as discussed in Section 6.5.

The configuration with varistor black-to-green (second row) does not afford very good protection for components connected black-to-white; therefore, it should be used only if there is a special need to clamp black-to-green at a low voltage with only one varistor available or allowed.

An improved protection is obtained with a varistor connected black-to-white, complemented by a second varistor connected white-to-green (third row).  The ultimate protection is, of course, one varistor in every position (fourth row), but this should be required only for exceptionally sensitive loads.

## Case History No. 6 - 	Measurement problems

Considerable controversy has been raised on an "overshoot" associated with the performance of varistors under fast pulses.  Actually, this overshoot is primarily a measurement problem associated  with lead effects.  To illustrate the effect of  lead length on the  overshoot, two measurement arrangements were used.  As shown in Figures 49(a) and 49(b), respectively, 0.5 cm2 and 22 cm2  of area were enclosed by the leads o the varistor and of the voltage probe.

The corresponding voltage measurements are shown in the oscillograms of Figures 49(c) and 49(d).  With a slow current front of 8 As, there is little difference in the voltages occurring with a small or large loop area, even with a peak current of 2.7 kA.  With the steep front of 0.5 s, the peak voltage recorded with the large loop is nearly twice the voltage of the small loop.     Note in Figure 49(d), that at the current peak L di/dt = 0 and the two voltage readings are equal; before the peak L di/dt is positive and after, it is negative.

Other measurement errors can be introduced by the connection of the voltage probes, as illustrated by the following experiment.  When making voltage measurements across a clamping device for evaluating its performance, one must recognize possible difficulties requiring special precautions.  Two precautions must be taken:

1.	Use two probes in a differential mode to make a measurement directly at device terminals.  Commercial oscilloscope preamplifiers offer a wide choice of differential mode operation, either through a mode (add Channel A + invert Channel B) with two-channel preamplifiers, or through a differential amplifier built specifically for high common mode rejection, sometimes at the expense of bandwidth.  Thus, careful attention must be given to this aspect of measurements.

- Avoid contaminating the true device voltage by the additional voltage caused by magnetic coupling.  The voltage measured by the two probes is the sum of the actual clamping voltage existing across the device and a spurious voltage caused by magnetic coupling.  This spurious voltage is induced into the loop formed by the clamping device length and the two probes by the changing magnetic field of the current flowing in the device.

- To illustrate the second point, the measurement circuit shown in Figure 50 was set up in the output circuit of a generator producing a 8/20 s impulse.  The "device" was a hollow conductor, with a hole at the center through which a twisted pair was fed, one wire of the pair branching out to each end of the conductor, separated by 10 cm.  At the same 10 cm separation, but outside of the hollow conductor, two thin wires were attached and brought -to the midpoint of the hollow conductor, in close contact with the conductor; from the midpoint outward, they were twisted in the same manner as the inside  pair. A third set of wires was soldered at the end points of the hollow conductor, and arranged to form a rectangle, the hollow conductor being one side of that rectangle.  Several widths could be set up for the rectangle, and each time the measured voltage was recorded.  Figure 52 shows the measured voltage versus radial distance of the opposite side of the rectangle, plotted from the oscillograms of Figure 51.

This experiment shows that not only must one connect the probes as close as possible to the terminals of a clamping device but still strive to minimize the area established by the probes close to the device.  In the case of a low-voltage suppressor, it would be better to solder short leads to the device terminals, bring them together while tightly hugging the device, then twist them in a pair and connect the oscilloscope probes some distance away from the device.

This experiment also shows the importance of wire layout in making the connections of a protective device in an actual circuit.  As discussed in Case History No. 1, creating a loop near the protective device is an invitation to induce additional voltages in the output of the protective device, thus losing some of its effectiveness.

Hence, when one is making measurements as well as when one is designing a circuit for a protection scheme, it is essential to be alert to the effects of lead length (or more accurately of loop area) for connecting the varistors.  This warning is especially important when the currents are in excess of a few amperes with rise times of less than 1 s.

## Case History No. 7 - 	The best surge suppressor is a surge monitor!

Increasing recognition of the existence of transients on power lines has encouraged extensive use of commercial disturbance analyzers as a first step in identifying a potential transient problem.  Surveys have also been made on the quality of the available ac power, based on recordings obtained from such analyzers.  However, the results of such measurements may be ambiguous as a result of the design of at least one of these instruments, as made by Dranetz Technologies, Inc., until recently.

The problem arises from a characteristic of the Dranetz equipment, which exists for both Models 606 and 626, and which was not recognized at the time some measurements were made but is now pointed out in more recent Dranetz instruction manuals.

In order to protect the electronics of the Disturbance Analyzer from damage by overvoltages in the power supply to these internal electronics, a surge suppressor has been provided in the input to the power supply - not the monitoring input of course.  However, if the ac power system being monitored is the same as the power system in which the instrument power supply cord is plugged - a likely possibility in the general case and precisely the situation of some reported measurements - then the observations of surge occurrences on that power system are those of a system whose transients have been suppressed!

To support this claim, Figure 53 shows an oscillogram recorded at the output of a surge generator which provides both 120 V ac power and the IEEE/ANSI C62.41 Ring Wave, Category B. The oscillogram shows the surge without the Dranetz analyzer plugged into the test system out-put, and, superimposed, the effect of plugging the power cord only of the Dranetz analyzer into the test system output.   Without the analyzer, the open-circuit voltage is  3 kV; with the analyzer plugged in, the output voltage is reduced to 1.1 kV.

The ANSI/IEEE C62.41 Category B characteristics are 6 kV open-circuit voltage, 500 A shortcircuit current, therefore a source impedance of 6000 : 500 = 12 .  From the circuit values of  Figure 54, the unknown effective impedance o the analyzer, Z, can be computed to be only 7 .  That low impedance, when connected in parallel with the voltage measurement leads, will load the source of the transient and yield lower voltage recordings than the actual occurrence would have been without the analyzer connected.  This situation makes the facetious remark in the 1970 paper come true ("the best surge suppressor is a surge monitor!").

While it is too late to correct data already recorded, there is a very simple solution to the problem.  Ferro-resonant line conditioners not on] provide surge isolation at their output but also decoupling of the input from the output. (30)  Figure 55 shows the open-circuit output of the surge generator at 6 kV (upper trace) and the output with the line conditioner feeding the analyze plugged in (lower trace).  There is no detectable effect on the impinging surge.  Thus, by merely inserting the line conditioner in the power cord o the analyzer, the issue disappears, and measurements can be obtained without the ambiguity which can cause a sense of false security in the relatively low levels of impulse cited in some o the published reports.

Case History No. 8 - 	Varistor versus environment: Winning the rematch

During the initial startup of a solid-state motor drive in a chemical processing plant, difficulties arose with the varistor and its protective fuse at the input of the thyristor circuits.   Frequent blowing of the fuse was observed, with occasional failure of the varistor.  The plant substation, fed at 23 kV from the local utility, included a large capacitor bank with one-third of the bank switched on and off to provide power factor and system voltage regulation.  These frequent switching operations were suspected of generating high-energy transients that might be the cause of the failure of the fuses and varistors, because literally thousands of similar drive systems have been installed in other locations without this difficulty.

On-site measurements performed after repeated blowing of fuses and occasional failure of varistors connected at the input to the thyristor drive indicated that indeed the devices were not matched to their environment.  From this point on, specifying larger sizes, sizes appropriate to the environment, solved the problem.  Immediate relief was secured by the installation of a larger varistor at the same point of the circuit; long-term protection was obtained by the addition of a gapless metal-oxide varistor arrester on the primary side of the step-down transformer feeding the drive.  The situation has been changed from failures occurring every few days to no further problems in the 3 years since the larger varistor was installed.  A complete description of this case history is given in Reference 8; a summary is given in this report.

This case history illustrates how surge protective devices that are successfully applied for the majority of cases can occasionally suffer failure when exposed to exceptionally severe surge environments.  It also shows how little attenuation occurs, at the frequencies produced by switching surges, between the distribution level (23 kV) and the utilization level (460 V), even though a long line and two step-down transformers exist between the source of the transient and the point of measurement.

A typical total event recorded on one of the phases during a capacitor bank closing is shown in Figure 56 A.  A low-frequency oscillation with a period of 3 ms (330 Hz) and initial peak-to-peak amplitude of 450 V decayed in about 10 ms.  The high-frequency oscillations are resolved in the recording of Figure 56B (recorded during a similar switching sequence).  This high frequency has an initial peak-to-peak amplitude of 2000 V, decaying in about 5 ms. The period is 180 s (5.5 kHz), A similar, third event is shown in Figure 56C.  For scaling the amplitudes, the steady-state voltage is shown in Figure 56D.

Figure 57 shows recordings of transient currents in all of the three varistors.  Figure 57A shows a train of current pulses in the range of 10 to 40 A.   In the burst of Figure 57B, the recorded current pulses range from 5 A to 200 A.

Conclusive evidence, therefore, was obtained that substantial current pulses were absorbed by the varistors during capacitor switching.  The magnitude and duration of these pulses were excessive for the capability of a 20 mm disc used originally; many similar drives installed elsewhere do not experience the failures encountered at that particular location.  Another significant finding from these measurements is the fact that the switching transients, generated at the 23 kV level, propagate down to the point of utilization at the 460 level.

An obvious remedy would be to use a varistor with greater current-handling capability.  The 32 mm size offers such a possibility.  The improvement in the number of pulses is 50 times more pulses until pulse rating is reached.  The improvement in the number of pulses until  varistor failure occurs, however, is not necessarily 50 times more pulses.  Because of the imprecision in the margin between end of pulse rating an ultimate failure, that margin is not necessarily the same for the two sizes, 20 mm and 32 mm, but it is reasonable to expect the same order of magnitude improvement  in the ultimate failure as in the pulse rating.  This expectation of a 50-time improvement would change the time between failures from the few days observed with the 20 mm size to perhaps 1 year with the 32 m size, providing immediate relief and time to make further changes for the long term.  Therefore, the change to a 32 mm size, connected at the same point of the circuit, was immediately implemented for that particular environment.

In addition to the proposed upgrading of protection at the 460 V level, three other remedies could be considered:  installation of surge arresters at the 2300 V level, installation of surge arresters at the 23 kV level, or a change in the circuits involved in the capacitor switching, designed to reduce the severity of the transients at their origin.  In a second phase of the retrofit described here, 2300 V arresters were installed at the transformer primary.

8.  CONCLUSIONS

Power system disturbances can inject damaging overvoltages into power lines as well as data lines.  Lightning surges can be equally damaging, by direct termination of a stroke, by induction, or especially, by differences in ground potential caused by the flow of the current into earth. Beware of differential ground potential rise!

Fundamental precautions, best applied in the design and construction stages, can provide effective protection at a small cost compared to the alternative of failures and retrofits.    The cost of insurance premiums always seems high before the accident.

Shielding, bonding, and grounding are the classical preventive methods at the system and component level.  Conflicts between tradition grounding practices for noise reduction can b reconciled with the requirements of surge protection.  Grounding the shields at only one en invites trouble.

A combined approach of fundamental precautions and protective devices can provide effective protection over the range of natural and man made disturbances.  However, these devices must be applied as part of a concerted effort.  The coordination of protective devices is the key t functional and cost-effective protection.

9.  ACKNOWLEDGMENTS

Motivation for preparing this report was pro vided by the reported case histories and the penetrating questions raised by students at the University of Wisconsin annual conferences of surge protection of computers and electronic systems, as well as by discussions with members of the IEEE Surge Protective Devices Committee Maurice Tetreault of Digital Equipment Corporation graciously made available the recordings of transients on data cable.  Virginia Barnum, Catharine Fisher, and Elizabeth Zivanov of Corporate Research and Development contributed valuable review and comments toward development of the final text.

## REFERENCES

1.	J.H. Hagenguth and J.G. Anderson, "Lightning to the Empire State Building," Part III, AIEE Transactions 71 PAS, August 1952.

2.	N. Cianos and E.T. Pierce, A Ground Lighting Environment for Engineering Usage, Stanford Research Institute Technical Report, August 1972.

3.	R.H. Golde, "The Frequency of Occurrence and the Distribution of Lightning Flashes to Transmission Lines," AIEE Transactions 64, 1945.

4.	 World Distribution of Thunderstorm Days, WMO-OMM #21 TP6, World Meteorological Organization, Geneva, 1953.

5.	R.H. Goide, "The Lightning Conductor," Lightning II, R.H. Golde, ed., Academic Press, New York, 1977.

6.	H. Cavendish, W. Watson, B. Franklin, and  J. Robertson, "Report of the Committee Appointed by the Royal Society to Consider a Method of Securing the Powder Magazines at Purfleet," Philosophical Transactions of the Royal Society 63, London, 1773, and 68, 1777.

7.	A. Greenwood, Electrical Transients in Power Systems, Wiley Interscience, New York, 1971.

8.	F.D. Martzloff, Varistor Versus Environment: Winning the Rematch, 85CRD037, General Electric Company, Schenectady, New York, 1985.

9.	D.W. Bodle, et al., Characterization of the Electrical Environment, University of Toronto Press, Toronto, Canada, 1976.

10.	E. Bennison, D. Ferland, and A.J. Ghazi, "Lightning Surges in Open-Wire, Coaxial, and Paired Cables," Proc. of the IEEE International Conference on Communications, June 1972.

11.	C.F. Boyce, "Protection of Telecommunications Systems," in Lightning 2, R.H. Golde, ed., Academic Press, New York, 1977.

12.	R.L. Carroll and P.S. Miller, "Loop Transients at the Customer Station," Bell System Technical Journal 59 (9), pp. 1609-1643, November 1980.

13. 	R.L. Carroll, "Loop Transient Measurements in Cleveland, South Carolina," Bell System Technical Journal 59 (9), pp. 1630-1645, November 1980.

14.	M. Tetreault and F.D. Martzloff, "Characterization of Disturbing Transient Waveforms on Computer Data Communication Lines," Proc. of the 6th Symposium on Electromagnetic Compatibility, Zurich, pp. 423-428, 1985.

15.	Guide for Surge Withstand Capability (5WC) Tests, ANSI Std C37.90a, 1974; IEEE Std 472-1974.

16.	Insulation Coordination Within Low-Voltage Systems Including Clearances and Creepage Distances for Equipment, International Electrotechnical Commission Report 664, 1980.

17.	IEEE Guide for Surge Voltages in Low-Voltage AC Power Circuits, ANSI/IEEE Std C62.411980.

18.	J.E. Lenz, "Basic Impulse Insulation Levels of Mercury Lamp Ballast for Outdoor Applications," Illumin.  Eng., pp. 133-140, February 1964.

19.	F.D. Martzloff and G.J. Hahn, "Surge Voltage in Residential and Industrial Power Circuits," IEEE Transactions on Power Apparatus and Systems PAS 89 (6), pp. 1049-1056, July/August 1970.

20.	R. Hasler and R. Lagadec, "Digital Measurement of Fast Transients on Power Supply Lines," Proc. 3rd Symposium and Technical Exhibition on Electro-Magnetic Compatibility, Rotterdam, Holland, pp. 445-448, May 1979.

21.	H. Wernsto6m, M. Broms, and S. Boberg, Transient Overvoltages on AC Power Supply Systems in Swedish Industry, National Defence Research Institute, Linkoping, Sweden, 1984.

22.	P. Chowdhuri, "Transient Voltage Characteristics of Silicon Power Rectifiers," IEEE Transactions on Industry Applications IA-9, September/October 1973.

23.	P. Richman, "Changes to Classic Surge Test Waves Required by Back Filters Used for Testing Powered Equipment, Proc. of the 6th Symposium on Electromagnetic Compatibility, Zurich, pp. 413-418, 1985.

24.	IEEE Standard Test Specifications for Gas Tube Surge-Protective Devices, ANSI/IEEE C62.311981.

25.	IEEE Standard Test Specifications for LowVoltage Air Gap Surge-Protective Devices (Excluding Valve and Expulsion Type Devices), ANSI/IEEE C62.32-1981.

26.	IEEE Standard Test Specifications for Varistor Surge-Protective Devices, ANSI/IEEE C62.331982.

27.	IEEE Standard Test Specifications for Avalanche Junction Semiconductor Surge-Protective Devices, IEEE C62.34-1984.

28.	Martzloff, F.D., Discussion of paper "Rural Alaska Electric Power Quality," IEEE Transactions on Power Apparatus  and  Systems  PAS-104,

No. 3, pp. 618-619, March 1985.

29.	F.D. Martzloff and H.A. Gauper, Surge and High Frequency Propagation in Industrial Power Lines, 85CRD087, General Electric Company, Schenectady, New York, 1985.

30.	F.D. Martzloff, "The Propagation and Attenuation of Surge Voltages and Surge Currents in Low-Voltage AC Circuits," IEEE Transactions on Power Apparatus and Systems, PAS-102, pp. 1163-1170, May 1983.

31.	Transient Voltage Suppression Manual, Fourth Edition, General Electric Company, Syracuse, New York, 1983.

32.	J.D. Harnden, F.D. Martzloff, W.G. Morris, and F.B. Golden, "The GE-MOV Varistor The Super Alpha Varistor," Electronics 45 (21), p. 91, 1972.

33.	G.D. Mahan, L.M. Levinson, and H.R. Philipp, Theory of Conduction in ZnO Varistors, 78CRD205, General Electric Company, Schenectady, New York, 1978.

34.	M. Matsuoka, T. Masa Yama, and Y. Lida, "Nonlinear Electrical Properties of Zinc Oxide Ceramics," Proc. of First Conf.  Solid State Devices, Tokyo, 1969, J. Japan Soc.  Appl. Phys. 39, 1970, Suppl., 94.

35.	M. Matsuoka, "Non-Ohmic Properties of Zinc Oxide Ceramics," Jpn.  J. AppL Phys. 10, p.736, 1971.

36.	Alexander Kusko, Inc., "Evaluation of Transient Voltage Suppressors for Saving Electric Energy," Electric Power Research Institute Report EM-1722, Palo Alto, California, 1981.

37.	Standard for Voltage Surge Suppressors, UL 1449, Underwriters' Laboratories, 1985.

38.	K.E. Crouch, Lightning Technology, Inc., Pittsfield, Massachusetts, private communication.

39.	National Electrical Code, National Fire Protection Association, Boston, Massachusetts.

Lightning and Surge Protection of Photovoltaic Installations

# Two Case Histories: Vulcano and Kythnos

François D. Martzloff

National Institute of Standards and Technology

## Abstract

Two installations of photovoltaic (PV) systems were damaged during lightning storms.  The two sites were visited and the damaged equipment that was still available on the site was examined for analysis of the suspected lightning-related damage.  The evidence, however, is insufficient to conclude that all the observed damage was caused by the direct effect of lightning.  A possible scenario may be that lightning-induced overvoltages caused insulation breakdown at the edges of the photovoltaic modules, with subsequent damage done by the dc current generated by the array.  Other surge protection considerations are also addressed, and suggestions are presented for further investigations.

1. Introduction

Photovoltaic systems are inherently exposed to direct and indirect lightning effects.  For high-capacity systems, the deployment of solar cell arrays requires a large area with commensurate exposure to direct lightning strikes at the local annual rate of ground strikes per unit area.  The presence of a ground grid related to the PV system in an otherwise isolated area may act as a collector of lightning ground-current from nearby strikes.  For PV systems tied to a local power grid, the exposure also includes surges coming from the power grid and the possible differences in the ground potential of the ac power system and that of the dc array system.

In the present development state of photo-voltaic systems, occurrences of lightning strikes have been rare, thus field experience is still limited.  Nevertheless, justifiable concerns exist, both from the economic point of view of damage versus cost of protection and from the less tangible impact on the perceptions of reliability for a technology still in the early stages of commercial utilization.

The Sandia National Laboratories, sponsored by the U.S. Department of Energy, are developing a Recommended Practice document for the electrical design of photovoltaic systems.  As part of that project, the National Institute of Standards and Technology is contributing the lightning, surge protection, and grounding recommendations for these systems, based on known characteristics T of surge protective devices and on field experience.  By this means, a review of the circumstances and effects of lightning in the few known or suspected cases of lightning damage to worldwide photovoltaic installations will contribute to more effective design and application of future systems.

In this report, two case histories are examined.  These include the photovoltaic installations at Vulcano Island (Italy) and at Kythnos Island (Greece).  Following the description of these two case studies, a discussion is presented, leading to firm conclusions when the evidence is sufficient, and allowing conjectures when the evidence is less conclusive.  Both should serve as an indication of the need for further investigations, laboratory work, or theoretical study.

2.  Surge Protection at the Vulcano Island Installation

2.1  Background

Vulcano is one of the islands in the Aeolian Group in the Tyrrhenian Sea, north of Sicily.  The photovoltaic system in this island was designed by ENEL, the Italian national electric utility, as a research and demonstration facility and was commissioned in 1984 (Photograph 2-1)  ENEL has been operating this facility since the commissioning.  The visit, arranged by Dr. A. Previ of ENEL, took place in November 1988.

One case of damage attributed to lightning has been reported, with damage to only one panel (Photograph 2-2).  No other damage occurred in the system, not even to the protective varistors provided at each junction box in the array field.  This history makes that site an interesting case study, considering the scarcity of documented lightning occurrences on photovoltaic systems.

2.2  System Configuration

The Vulcano photovoltaic system (see Figure 2-1) includes the following major components: the array (1); a storage battery (2); one self commutated, stand-alone inverter (3); one line-commutated inverter (4); a rectifier for charging the battery (5); and a static switch (6).

Photograph 2-3 shows the block diagram of the system provided on the control cubicle. interface with the 20 kV ac grid of the island is obtained by the three-winding 150/150/20 000 V transformer which is an integral part of the output circuit of the line-commutated inverter.  A group of 40 local domestic users was originally supplied at 380 V by an existing substation connected to the 20 kV grid.  The 380 V bus of the substation was modified to allow power flow from the output of the stand-alone inverter, through the static switch, to the local users.

With this configuration, the system can operate in two modes: grid-connected, and stand-alone.  In the grid-connected mode, the tie to the grid is obtained through the 150/150/20 000 V transformer, absorbing all of the plant output.  In that mode, the storage battery is not in the circuit, and the local loads are supplied by the ac grid.  In the stand-alone mode, the local loads are supplied at 380 V directly from the self-commutated inverter. in that mode, the storage battery is connected to the dc bus and it can either absorb power from the array or deliver power to the inverter.  The local loads can also be supplied, if necessary, from the island ac grid through a back-up transformer.

Individual strings from the array can be switched by dc contactors located in the control room, to be connected to the dc bus or disconnected from the dc bus according to the charge state of the battery.  For maintenance purposes, a dc disconnect is located in terminal boxes next to the respective strings of the array (Photograph 2-4).  Mechanical interlock is provided between the contactor and the cover of the terminal box, which prevents accidental opening of the disconnect under load.

2.3  Grounding Practices

A major design decision in a photovoltaic system is whether to ground or not to ground the dc side.  In contrast to ac power systems, which are grounded in most cases (by generally accepted practice or by mandate, depending on the country), no general agreement has been reached on grounding practices for photovoltaic systems.  Two reasons are generally cited for an ungrounded system:

(1)	the possibility to continue operating with one ground fault on the system, and

(2)	some limitation of single L-G fault currents and hence reduction of damage in case of a fault,  because two ground faults are then required to produce a significant dc fault current.

In the Vulcano system, the dc system is not grounded.  A ground fault detection system is provided (Figure 2-2), with alarm indication on the control panel (Photograph 2-3) but no automatic trip nor remote indication of the fault condition (the system is unattended).  Experience with this system is described as satisfactory after an initial period of reported difficulties associated with insulation deficiencies in the panels. (These were eventually corrected by field or factory rework on the panels.)

While the dc system is not grounded, a ground grid has been installed at the site, for safety, surge protection, and grounding of the ac side.  In addition to a grid of ground cables running along the dc cables in the array (but outside of the plastic conduits containing the dc cables, see Photograph 2-5), ground rods (16 rods, each 2 m long) were driven into the earth.  Considerable care was given to the implementation of this ground grid.  For instance, the integrity and effectiveness of the grounding system for protection against step voltage and touch voltage, in case of a ground fault on the 20 kV system, were the subject of well-documented tests.  Providing low impedance earthing was made easier by the volcanic nature of the soil, which resulted in the unusually low value of 1.8  for the earth resistance.  The lower leg of each panel frame is bonded to the ground grid (Photographs 2-6 and 2-7).

Concerns frequently associated with grounding practices are corrosion of connections and leakage of the insulation from energized parts to ground At this site, the ground grid was implemented with direct-burial copper cables with welded connections (Photographs 2-5 and 2-7), an effective assurance against corrosion problems.  Some corrosion. problems occurred in the original metal boxes containing the module by-pass diodes (Photograph 2-8).  The problems were corrected by improving the insulation to ground with a better sealing of the metallic frames.

The significance of a history of corrosion/ insulation tracking is that these insulation problems may be a clue to a scenario other than that of simple direct lightning damage.  One may speculate on a scenario involving a double ground fault that could have resulted in panel damage; this scenario will be presented in the discussion of the observations of Section 2.5.

2.4  Surge Protection

Overvoltage protection for the Vulcano system is provided at three interfaces, as sketched in Figure 2-2:

(1)	At the terminal box of each pair of strings (Photograph 2-9), between each of the two dc lines and ground, by one 32-mm diameter varistor (4 total) rated 560 V dc (GE Cat.  No. V420HE400).  No further protective devices are provided at the entrance of the dc cables to the power conditioner house (the capacitor bank at the input of the inverters can serve as overvoltage limiter for any impinging surge because the front time is relatively long as a result of the cable impedance).  The blocking diode for each string, located in the field terminal box, is protected by one 32-mm diameter varistor (2 total), rated 560 V dc (GE Cat.  No. V420HE400).  This varistor has a clamping voltage of 1200 V for a 300 A peak surge current.  The repetitive peak voltage rating of the diode (IR Cat.  No. SD 70N12P) is 1200 V.

(2)	At the 380 V ac interface of the output of the inverters, by three varistors connected lineto-ground (Photographs 2-10 and 2-11).  These are also 32-mm diameter varistors, with a 420 V ac rms rating (GE Cat.  No. V420HE400).  A fuse rated 8 A, 500 V, 100 kA interrupting capacity is provided in series with each varistor (Photograph 2-12).  About 50 cm of leads are used to connect the varistors to the 380 V terminals at the base of each inverter cabinet. (In this case, this length is not significant because of the front time limitation discussed above.)

(3)	At the 20 kV interface with the island system, by 'conventional" surge arresters installed at the potheads of the underground connection, and connected line to ground (Photograph 2-13).  The 20 kV overhead line stops about 200 m from the control room, with the final connection to the plant made by underground cable (Photograph 2-14).

2.5  Discussion

2.5.1  Lightning damage report

The damage caused to the PV panel by the presumed lightning strike is shown in Photograph 2-2. (The photograph was supplied by Previ as part of the background history; the damaged module was not available for examination.) This damage occurred during the commissioning period of the plant in the autumn of 1984; it was found early in the morning by the ENEL staff after a thunderstorm occurred during the night.  The glass and part of the cells were described as 'melted near the metallic frame of the module." No failure of the blocking diode nor of the varistor of that string was found as a result of that incident.

2.5.2  Lightning damage scenarios

The damage to the module is located at the lower part of the array, as shown in Photograph 2-2.  Postulating a scenario of a direct strike to the array, the point of attachment of the lightning would be the point of origin of the rising streamer that meets the descending stepped leader (Figure 2-3).

This position at the lower part of the array is rather unexpected for the point of initiation of the streamer.  A more likely point for streamer initiation - and resulting termination of the strike - would be the upper edge of the array, which is 2 m above grade level (Photograph 2-15).  Thus, there is some doubt on drawing a conclusion that the damage was the result of a direct strike terminating at the array.

In view of the reported insulation problems that occurred during the initial period of operation, one might ask whether the damage to that panel might be the result of a leakage of dc current to the frame, rather than the simple direct effect of a lightning strike.  This dc leakage might be the consequence of a lightning induced overvoltage stress that created a double fault in one single event, or that created the second fault after the first had previously occurred but remained uncorrected.  The scenario could unfold as follows:

Assume that two independent ground faults, (A) and (B) have occurred on the system (Figure 24).  When the first, say (A), occurs, the fault detection system indicates that event but no immediate action is taken because of the unattended status of the system, and there is no ground fault current resulting from that first fault (except the insignificant current passing through  the detection circuit).  A ground fault current can exist only after the second fault occurs, establishing the path through (A) and (B).

Assume now that one of the two faults, say (B), involves a very low resistance.  Then, even for substantial fault currents, little heat is generated at fault (B).  Assume further that (A) has a low enough resistance to produce a "sufficient" current in the fault path, where "sufficient" is defined as a level which, combined with the low but finite resistance of fault (A), will create heat dissipation in (A), in contrast with the negligible heat dissipation in (B).

In this manner, we have the elements that could create the observed effects, that is, an obvious fault with burning at (A), and a less obvious fault at (B), with a low resistance that may be eliminated during emergency maintenance work following the occurrence of the incident.  The likelihood of such a double fault is admittedly low, but cannot be ruled out in view of the design of the ground fault detection system which indicates faults locally only.  This scenario, still associated with lightning, would not be in contradiction with the observed low position of the damage since it does not require termination of the strike at that low point of the panel.  Furthermore, the low point on the sloped array is also a place where moisture is more likely to accumulate and thus create a good candidate for a contributing cause in the scenario of two-stage insulation breakdown.

A variation on the theme of the double fault might even be that the fault was entirely caused by long-term insulation breakdown, without the "coup de grace" administered by the lightning incident.  However, the observation of a damaged module soon after a lightning storm would point to the lightning-induced overvoltage scenario.

One significant aspect of the failure mode is the reported shattering of the glass cover of that module.  The question is whether it could have been produced by the less violent action of a dc fault (glass breakage has been reported in the United States during dc ground faults), or could be explained only by the mechanical shock associated with a lightning strike.  The reported melting of the glass is also a clue that could be investigated further.

If data were available on the failure modes of this type of module, some of the conjectures proposed in this discussion might be replaced by more positive conclusions.  The incentive for reaching such positive conclusions is not merely one of intellectual curiosity. if overvoltages induced by indirect lightning are sufficient to cause insulation breakdown, then the provision of lightning air terminals is irrelevant - and thus becomes an unjustifiable cost - while improving the insulation levels in the modules would yield better results for the added expense.

2.5.3  Insulation coordination

Coordination of the protective devices with the withstand capability of the equipment to be protected is sometimes overlooked in system designs.  At the Vulcano site, this coordination was presumed to have been incorporated in all the system design and was not audited during a visit aimed primarily at a review of the lightning incident.

However, given the concerns on the protection afforded by the varistors, the coordination for one example of protection can be evaluated by a simple comparison: From their catalog description, the blocking diodes of the array strings have a repetitive peak voltage rating of 1200 V (albeit not a perfect assessment of their transient withstand capability).  Therefore, the maximum clamping voltage for the protective varistor should not exceed 1200 V. For a varistor rated 560 V dc, this maximum allowable clamping voltage of 1200 V corresponds to a 300 A surge crest current.  In other words, protection can be expected as long as surge currents do not exceed 300 A in that string.

At first glance, this 300 A allowable level of surge current may appear low.  However, when postulating a lightning-induced surge current level in the wiring, one should not be influenced by the thousands of amperes of the direct stroke, but rather consider the voltage required to drive the postulated current waveform along the inductance of the wiring: a high rate of current change means a high driving voltage.  However, in this case, high driving voltage would not be possible because sparkover of the insulation would occur.  Thus, the 300 A crest of an 8/20 s postulated waveform appears an appropriate order of magnitude.  In this example, therefore, insulation coordination was in fact achieved for voltage levels that might be induced in the wiring.

2.6  Suggestions on the Design

In his role of sponsor of the visit, Previ asked for comments on the surge protection provided at this site.  Accepting for the moment the hypothesis that lightning was the cause for damage to the panel, the successful operation of the installation and survival of the electronics through one lightning occurrence are already a testimonial of the adequacy of the protection system.

Taking a devil's advocate view in search of greater protection, a more conservative approach could have been to provide additional surge protection for the incoming dc cables at the interface with the inverter inputs, but experience so far has indicated survival without these additional protective devices.  This observation, however, does not necessarily guarantee that another lightning strike scenario, with a different point of termination or higher amplitude, could not induce some damaging overvoltage along the cables between the array protections and the inverter input.

A concern expressed by Previ was the failure mode of the varistors installed at the base of the electronic cabinets at the ac interface.  These varistors can be expected, in case of failure, to be promptly isolated from the power source by operation of their series-connected fuses (that have ample interrupting capacity).  Therefore, the generation of hot gases during the short-circuit following failure of the varistor would be brief.  Again, as an exercise in very conservative design, a further step could be applied to limit the consequences of a varistor failure by providing a partial metal shielding around the varistors to deflect any evolving gas away from the rest of the circuit.  The 8 A rating of the fuses seems adequate to avoid premature aging of the fuses caused by repetitive surges [3], should such repetitive surges occur at that site.

Previ also asked about the possibility of monitoring the condition of the varistor aging for the purpose of anticipating an impending failure.  This question has been raised by many users, sensitized to the issue by competitive claims from advocates of silicon avalanche diodes.  At this time, no easy method has been proposed for field measurements (especially in dc circuits where a clamp-on transformer is not suitable [4]).

Increasing concerns on the issue are likely to catalyze the development of such measurements.  For the moment, the only technically simple but operationally difficult method would be to remove each varistor from the circuit and compare its present nominal voltage to its original nominal voltage.  In existing installations, that information is not likely to be available.  An intermediate solution for this installation would be to implement monitoring the varistors, albeit at a late stage of the project, and watch for trends, even though the initial value is not available.  As a last resort, a surface temperature measurement on the varistor might give a warning of impending failure.

This discussion of varistor failure scenarios should not be interpreted as an inference that the varistors are in fact in jeopardy.  It is only an exercise in asking and answering conservative "what-if' questions.

2.7  Specific Conclusions from the Vulcano Case

The experience accumulated at the Vulcano site indicates no major problem of surge occurrences, with only one reported case of damage to one panel among several hundred.  This one case of damage is not conclusively attributable to lightning.

Furthermore, even if the damage were caused by lightning, then a partially satisfactory conclusion would be that sufficient protection could be provided for the electronic components in the power conditioning system, at least for that particular case.  Power conditioning equipment is the most expensive part of the system and cannot be considered "expendable" in contrast with a few modules being lost with the rest of the system remaining operational.  The ambiguity in attributing the damage to direct or indirect lightning might be resolved by further study of the failure modes of a panel (a module within its frame). one failure mode to be investigated would be under simulated lightning strikes; the other failure mode would be under dc stress with surface contamination.  Further discussion of this issue, from the technical as well as economic and intangible aspects, is offered in the general discussion of Section 5.

3.  Surge Protection at the Kythnos Island Installation

3.1 Background

Kythnos is one of the islands in the Cyclades Group, in the southern part of the Aegean Sea.  The photovoltaic system on this island was designed and implemented in 1983 by Siemens.  It is operated by the Greek Public Power Corporation.  The visit, which was arranged by Dr. J. Chadjivassiliadis of Public Power Corporation, took place in November 1988.

Several panel failures have occurred in 1986, 1987, and 1988, which have been attributed to lightning.  Lightning rods and surge arresters are provided at this site, making it an interesting subject of study, both for an explanation of the presumed direct strikes occurring in spite of the lightning rods, and for a study of the protection afforded by the surge protective devices installed in the circuits, as well as their failure modes.

3.2  System Configuration

The installation was designed and implemented by Siemens, as one of the experimental facilities coordinated by the European Economic Community (Photograph 3-1).  The plant has a nominal output capacity of 100 kW.  Figure 3-1 shows a schematic of the system components.  The modules are grouped in arrays formed by a series string of 20 modules, each producing a dc bus voltage of 160 V. Each of these 43 arrays is terminated in a junction box in the field, where two or three strings are connected in parallel to bring the dc power to the power conversion cabin (Photograph 3-2).

In the power conversion circuitry, the variable 160 V dc is raised and regulated to 250 V by a dc/dc converter to match the battery voltage for optimum charging conditions and operation of the solar cells.  The dc/dc conversion is per-formed by four units, each rated 25 kW.  Depending on the instantaneous power transfer, one to four converters are in service.

Conversion to ac power is performed by three inverters, each rated 50 kW.  The output voltage of 380 V is stepped up to 15 kV for connection to the island power grid.  Although the arrays and conversion equipment are located adjacent to the Diesel generating plant of the island, operation of the photovoltaic system can be automatic, and does not require daily supervisory.  Extensive monitoring and control of operating parameters is provided by a "Logistronic" control system and other controls incorporated in the design.

3.3  Grounding Practices

This site is located in the center part of the island next to the Diesel power plant, but with its ground grid isolated from that of the Diesel plant.  This grid consists of several loops encircling each of the four groups of arrays.  Part of the each loop follows the routing of the dc cables between the array junction boxes and the power conditioning cabin (Figure 3-2).

The perimeter of the field is defined by stone walls, in keeping with the prevailing island practice for marking boundaries between pastures and cultivated fields.  Consequently, there is no metal fence around the photovoltaic field, and thus no perimeter grounding cable.  The conductors are made of 10-mm diameter galvanized steel, buried directly at the bottom of a trench, with the dc cables above the ground conductors.  There are no driven ground rods added to this grid.  The choice of galvanized steel probably reflects the German practice, where concerns over corrosion effects by buried copper seem to deprecate the use of copper.

All the metal structures of the system, including the array supporting beams, junction boxes, lightning rods, and housings for the power conditioners and battery, are bonded to the ground grid.  Connections are made using bolted connectors above ground (Photographs 3-3, 3-4, and 3-5), as well as under ground, with protection against corrosion being provided in accordance with the normal practices of the various manufacturers and contractors (these were not discussed during the visit).

The dc system is not grounded, but includes a ground fault detection circuit with fault indication available only in the control cubicle of the system.  The separation of the photovoltaic ground grid from the Diesel plant ground grid raises the question of a possible difference of ground potential between these two systems during a lightning strike.  If instrumentation or telemetering equipment spans across the two systems, the difference in ground potentials might become a problem.  However, no such problem was identified at that site.

3.4  Surge Protection

This installation presents an interesting case history because it includes both lightning rods (air terminals) in the array and surge arresters in the circuits.  Damage to several panels, presumably as a result of lightning over a period involving three separate occurrences, raises questions on the effectiveness of the protection against direct strikes.  Damage to the surge arresters also occurred in one of the field junction boxes, but no damage occurred on the power conversion units. Some damage occurred in the control circuits  of the battery charger during the initial period, when they did not have surge arresters at their ac power input.  After arresters were added to this ac input, no further damage events occurred but some upsets did still occur in the control system.

3.4.1  Air terminals

Air terminals (lightning rods) have been installed between rows of the array as shown on Photograph 3-6.  The height of these air terminals is 10.5 m above grade level; the upper edge of the panels is 2 m above grade level, thus leaving a net elevation of the air terminals 8.5  m above the upper edges of the panels.  Considering a 45o cone of protection, one of the classical criteria, the panel upper edges would then be "protected" within a radius of 8.5 m from each air terminal.  Those panels located beyond that radius would be left unprotected.  Reviewing the location of panels involved in the damage (Figure 3-2) shows the following horizontal distance from the nearest air terminal:

-   Module E2/B4/1	-	Location	10m
-   Module E2/B6/5	-	Location II	10m
-   Module   E3/B4/13	-	Location III	10m
-   Module   E3/B4/19	-	Location IV	12m
-   Module   E3/B5/18	-	Location V	8m
-   Module   E4/B3/20	-	Location VI	10m

Thus, five of the six damaged modules were beyond the 45o cone, and the sixth was on the fringe of the cone.  Some panels in the array, not impacted by lightning, are further away from an air terminal, the greatest distance in the field being 15 meters.  Another interesting statistic is the distribution of the panels with respect to being within a protected area of 8.5 meters radius (approximately 75%) or outside the protected area (25%).

Another protection criterion has been developed, that of the "rolling ball' [5], as discussed in section 3.5. According to that criterion, the protection radius would extend to 12 m so that all panels would have been expected to be in the protected zone.

According to yet another definition of the cone of protection, sometimes cited by less conservative designers, a 2:1 instead of a 1:1 ratio of radius to height may be considered. in such a case, one would expect all of the panels to be "protected" as the distance from the mast would increase to 17 m.

It is not known whether such a 2:1 cone, or the 1:1 (45) cone, or the rolling ball with a 30-m radius was used in the initial layout of the air terminals.  The design has been described as "installed according to VDE standards" (VDE is the acronym for Verein Deutscher Electrotechniker).

3.4.2  Overvoltage protection

Overvoltage protection at the Kythnos installation is provided at four interfaces, numbered (1) through (4) in Figure 3-3:

(1)	At the Junction boxes In field - There are several slightly different types of junction boxes in the field.  Some include termination for two or for three strings, while some also contain additional circuitry for the data collection system.  Photograph 3-7 shows a typical three-circuit box (undamaged).  One surge arrester is connected between each of the floating dc lines (+) and (-) and a ground bus inside the box.  In turn, this bus is bonded to the footing by a copper cable (in parallel with the inherent bonding between the metallic junction box and the I beam of the footing).

These arresters appear similar to those for which the voltage response had been documented in a paper presented at the 1981 EMC Zurich Symposium [8].  From the voltage response characteristic reported in that paper, it appears that the surge arrester consisted of a silicon-carbide varistor with a series gap.  The presence of a series gap is significant in discussing the upset events cited for the control circuits at this site.

The string blocking diodes are mounted in the junction box and are protected by a metal-oxide varistor connected in parallel with each -diode (Photograph 3-8).  Photograph 3-9 shows another junction box with the additional data collection circuitry installed in the box cover.  This particular box is the one where the lightning-suspected damage occurred, as shown in the close-up views of Photographs 3-10 and 3-11.

(2)	 At the power conversion units - The dc lines from the array are brought to the cabinets of the dc-dc converters where each of the four converter inputs is protected by two surge arresters (2a) (Photograph 3-12) connected between the (+) and (-) lines, and ground.  This arrester is of the same type as that described for the array junction boxes.

Similarly, the ac outputs of the inverters are protected against surges from the ac grid by four arresters (2b); one is connected between each line (a,b,c) and ground, and one between neutral and ground (N) (Photograph 3-13).  While the grounding connection of the 220/380 V system was not reviewed, presumably it follows the European practice of bonding to earth only at the secondary transformer, in this case the step-up transformer of the grid interface.  This practice, different from that used in the United States, motivates and justifies the provision of the arrester between neutral and ground.

(3)	At the Logistronic circuit power supply -The 'Logistronic' circuit controlling the battery charger is powered from the 220 V ac line in the battery cabin.  Thus, its power supply is exposed to surges that may occur on that supply.  Initially, there was no protection on this ac supply; perhaps as a consequence, damage occurred three times in the early years of the system (Appendix B).  Subsequently, two arresters were installed on the ac supply line ahead of the Logistronic input terminals (Photograph 3-14).  After these ac arresters were installed, only upsets were recorded (four occurrences).  This behavior is consistent with the voltage-limiting effect of the arresters but at the price of a steep voltage collapse when the gaps fires.  This electromagnetic disturbance is a likely source of interference in nearby digital circuits.

(4)	 At the ac grid interface - Protection against surges coming from the island ac power grid is provided by the three distribution-type arresters mounted on a cross-arm above the transformer (Photograph 3-15).  No information was available on these arresters; they are likely to be of the conventional design using a silicon carbide varistor with a series gap. This type of arrester is perfectly adequate for protecting transformers against surges, but might not be sufficient for the electronic components on the 220/380 V side.  For that reason, the secondary arresters described above are a good idea.  However, gapless secondary arresters are now available that can offer a more comprehensive protection, including some degree of upset protection.

3.4.3  Examination of the damaged modules

      - Summary

At the date of the visit, the three modules damaged in 1986 had been replaced in the array.  These modules were still kept in storage at the site, so that it was possible to examine them closely.  The two modules damaged in 1987 and the one module damaged in 1988, however, were still in position in the array, as no spares were available.  Detailed photographs and observations for each panel are given in the following paragraphs, in chronological order.

At this site, the arrays are only one module high, so that the long edge of the  module reaches from the highest to the lowest edge of the array.  In all six failed modules,  there is damage evident at one or both upper corners, along one or both long edges, and at the bottom of the module.  The panel is completely separated from the frame in some cases, while in other cases, only partial separation occurred.  One of the modules has severe bums marks on the top corner of the frame, while on the other modules the damage ranges from none to some readily visible burn marks.

3.4.3.2  Detailed examinations

MODULE -  307 0423 This module was in storage and had been at location E2 B4 I ("I" on Figure 3-2), 10 m from the nearest air terminal.  There are burn marks along both long edges, but not the complete length (Photograph 3-16).  On the right side, the burns are mostly at the lower part of the edge, away from the most damaged corner (Photograph 3-17).  On the left side, the burns are mostly in the upper part, with intriguing spots over some of the cells (Photograph 3-18).  The top right comer shows some marks on the frame, with the most extensive damage at that corner (Photograph 3-19).

MODULE - 303 0267 This module was in storage and had been at location E3 B5 18 ("V" on Figure 3-2), 8 m from the nearest air terminal.  There are burn marks along both vertical edges, but not over the complete length (Photograph 3-20).  On the right side, the burns are mostly at the upper part of the module, with damage at both corners (Photographs 3-21 and 3-22).  The top right corner (Photograph 3-21) shows heavy burn marks on the frame, while the top left corner (Photograph 3-23) shows light marks on the frame.  It should be noted that this module, which has the heaviest burn marks on its frame among the six modules, is the only module that was located within the "cone of protection" of an air terminal.  This remark will be discussed further in the next section.

MODULE - 304 0294 This module was in storage and had been at location E3 B5 19 ("IV" on Figure 3-2), 12 m from the nearest air terminal.  There are burn marks along all of the right side, and part of the left side (Photograph 3-24).  Both top corners show damage (Photographs 3-25 and 3-26).  The top right corner (Photograph 3-25 shows light burn marks on the frame, while the top left corner (Photograph 3-26) hardly shows any burn marks on the frame.  There is extensive separation of the panel from the frame along the right side (Photograph 3-27)

MODULE - 306 04l7 This module is still in the array at location E2 B6 5 ("II" on Figure 3-2), 10 m from the nearest air terminal, and was found damaged on February 5, 1987.  The bypass diode in the string allows the array to remain operational.  The right edge shows burns (Photograph 3-28).  Both right side corners show extensive destruction of panel material (Photographs 3-29 and 3-30), but the upper corner has no burn marks on the frame (Photograph 3-29).

MODULE - 304 0300 This module is still in the array at location E3 B4 13 ("III" on Figure 3-2), 10 m from the nearest air terminal, and was found damaged on February 5, 1987.  The bypass diode in the string allows the array to remain operational.  There is damage on three of the comers and some of the edges (Photographs 3-31, 3-32, and 3-33), but the heaviest damage is on the lower left corner (Photograph 3-34).  The two upper corners shows surface degradation on the frame, but these do not appear to be burn marks (Photographs 3-32 and 3-33).

MODULE - 310 0592 This module is still in the array at location E4 B3 20 ("VI" on Figure 3-2), 10 m from the nearest air terminal, and was found damaged on February 25, 1988.  The bypass diode in the string allows the array to remain operational.  The damage is concentrated on the left edge of the module (Photographs 3-35 and 3-37).  The panel is separated from the frame (Photograph 3-38).  The apparent discoloration of the frame at the top left corner does not seem attributable to burns (Photograph 3-36).

3.5  Discussion

3.5.1  Effectiveness of air terminals

Lightning protection of solar arrays by air terminals is still a subject of debate (effectiveness, shadow effects, cost, appearance).  The observations made at the Kythnos site do not bring conclusive evidence for or against the effective-ness of correctly designed air terminals, although they tend to weaken the case for providing air terminals.

The Kythnos experience involves points of (presumed) lightning termination that are at the edges of the zone of protection of several criteria, where this protection becomes more uncertain. ironically, the most severe burn mark is found on the frame of the module that was closest to an air terminal, and within the zone of protection as detailed in paragraph 3.4.1. Thus, a brief review of the uncertainties of the zone-of-protection concepts will provide the necessary perspective on the issue.

Indiscriminate application of the 45o cone of protection criterion to tall structures has led to contradictions.  An example is occurrence of lightning strikes terminating on the side of tall buildings, within the cone of "protection".  The original concept of a cone of protection is now generally replaced by the rolling ball criterion, based on the striking distance theory.  According to this striking distance theory [6], the striking distance at the tip of the descending stepped leader increases with the amount of charge in the leader.  Thus, the leaders having the highest potential current level have the longest striking distance (Figure 3-4).  Conversely, leaders having the lowest potential current level have the shortest striking distance.  The point of termination of a lightning strike can be anywhere within the striking distance from the last point of advance of the descending stepped leader.  This fact can be represented by imagining a sphere with a radius equal to the striking distance, which is determined by the charge in the lower part of the leader.  Any point at ground potential penetrating that sphere is a candidate for emitting a upward streamer that will complete the path for the return stroke.  Thus, points at ground potential outside of the sphere are still 'protected’ while the points inside the sphere are not.

Considering now the configuration of a vertical mast on the ground plane (Figure 3-5), rolling a ball on the ground until it touches the tip of the mast defines the limiting condition when the descending leader will terminate at the tip of the mast, thus leaving  other points below the sphere uninvolved.   Figure 3-6 shows graphically the configuration for the 10.5 m masts used in Kythnos, with the upper edge of the panels at 2 m above the ground plane.

Figure 3-6 shows the zone of protection as defined by the traditional 45o cone of protection, as well as that defined by a rolling ball of 30.m radius, as specified in the Lightning Protection Code [5].  Simple geometry shows a distance of 8.5 m from the mast for the 45o cone, while the graphical solution for the rolling ball shows a distance of 12 m from the mast.  It should be emphasized that the selection of a 30 m radius for the ball is somewhat arbitrary, in view of the data shown in Figure 3-4.  From Figure 3-6, it is apparent that a pessimistic assumption would be a smaller radius for the rolling ball: such a smaller ball would roll closer to the mast and thus would reduce the "  protected" distance from the mast.

This observation needs to be combined with the statistical distribution of lightning current amplitudes as stated by Cianos & Pierce [2] to appreciate that the 30 m radius is only a pragmatic choice, not an absolute criterion.  Therefore, observing points of presumed lightning termination at distances of 8.5 m to 12 m from the base of an air terminal is not startling, especially for low-current strokes.  This observation shows how precarious the assurance of protection can be when only sparsely distributed air terminals are provided.  In other words, increasing the degree of confidence that sufficient protection zones are established might require such a density of masts (or overhead wires) that the cost, appearance, and shadow effects would loom large in the overall trade-off.

3.5.2  Lightning current path

The resulting return stroke would then draw charges from the earth via the grounded structure, that is, the return current would come out of the grounding cable at the base of the column, and proceed by the shortest route toward the upper edge of the panel.  This shortest path does not include the lower half of the panel edges, as it would require the lower panel brace plus the panel edge to become involved.  While this path may still be somewhat involved, the major part of the current should only involve the upper half of the panel, a situation which is not reflected in the more or less even (or. random) distribution of the damage observed on both upper and lower halves of the long edges of the modules.

    - Direct versus consequential effects

In the absence of definitive knowledge on the direct effect of a lightning current involving a module, only conjectures can be made on the failure mode of the panel.  As discussed in the preceding paragraph, the presence of damage at the lower half of the panels is somewhat contradictory to the hypothesis of all the damage being done by the lightning current.  This contradiction adds weight to the argument (also presented in the case of the Vulcano incident), that the observed damage may be the result of a dc fault current occurring after an initial insulation breakdown caused by an indirect lightning overvoltage induced in the de circuit.  The insulation breakdown would occur at the point of lowest withstand, not necessarily in the upper half of the panel, and the ensuing dc fault would proceed along the edge as the blow-torch effect associated with the high temperatures of the dc arc, lingering at the fault, would cause burning along the edges, similar to what was observed.

On the other hand, the extent of the damage in the E2 B5 box (Photographs 3-10 and 3-11) appears to be greater than what could be expected from the dc current alone.  Damage caused by the occurrence of a lightning surge current is a more likely scenario in this case.

3.5.4  Mechanical effects

The top glass cover plates of the damaged modules generally had several cracks, but do not have the frosty appearance associated with the tempered glass used in the Vulcano module.  This difference may provide some clue about the sequence of the scenario, if it could be correlated with the mechanical characteristics of the glass.  Damage to the glass during dc faults has been reported in the United States.  However, no further detailed information is available in either case to pursue this line of thought.  This subject could be part of a test program aimed at finding failure modes of PV modules related to dc faults and lightning (both direct and indirect).

    - Integrity of the grounding system

The grounding system has been implemented with galvanized steel conductors, in keeping with the standard German practice where concerns over cathodic corrosion have steered designers away from copper. in the salty environment of an island, questions may be raised on the long-term integrity of buried galvanized steel conductors.  Even in the dry environment of the array footings, some signs of corrosion are apparent (Photograph 3-40).

3.6  Specific Conclusions from the Kythnos Case

The observed damage to the panels cannot be conclusively attributed to a direct lightning strike.  The six reported incidents might involve a combination of effects, with one case involving a direct strike, and the others being an indi-rect effect. in other words, the evidence that might point to invalidating a particular scenario might not apply to the scenarios of other incidents.  The surge-protective devices provided at the site performed well since no damage was inflicted to the electronics.  Failure of one surge arrester in the performance of its protective duty can be viewed as the ultimate sacrifice of the device fulfilling its mission - but it raises the question of monitoring for failure of protective devices.

4.  General Discussion

4.1  To protect or not to protect ?

The debate on whether to provide protection by air terminals or suffer the consequences of a direct strike is not settled by these case histories.  In spite of the presence of air terminals at Kythnos, damage occurred.  This damage my be a direct effect, or may be an indirect effect, or a combination of both.  At Vulcano, with no air terminals, only one case of lightning-related damage has occurred, and this single case may be an indirect effect rather than a direct effect.  Indirect effects are not eliminated by air terminals.  A better argument could be made if a firm conclusion were reached on whether the damage was a direct or indirect effect.

If the damage is attributed to direct effects, then the conclusion is that the air terminals, at the spacing and height used at Kythnos, were ineffective.  However, precisely because air terminals were distributed perhaps too sparsely, the Kythnos case history does not invalidate protection if it were ensured by appropriate air terminals with adequate height and density.

If the damage is attributed to an indirect effect, then one would argue that the air terminals cannot serve any useful purpose - the counter-argument being that the direct damage would have been even worse than what actually occurred.

4.2   Grounding practices

Differences in grounding practices leave many questions unanswered.  On the materials aspects, there is the different approach of using copper or of using galvanized steel.  On the circuitry aspects, there is the issue of grounding the dc circuit or leaving it floating (but with a ground fault detection scheme).  This latter choice, however, raises questions on the implementation of a ground fault indication which is available only to local operators.  That design may raise concerns in the context of long-term operation where immediate action on a ground fault may not be perceived as important.  This postponing of action may then lead to the occurrence of a second fault caused by lightning or by further pollution of insulation, with damage to components at that time.

4.3  Suggestions for further investigations

The ambiguity on the interpretation of the reported damage gives added weight to the desirability of consolidating all available data on panel failure modes, and eventually performing lightning simulation tests, as well as insulation failure (tracking) tests.  Evidence from the lightning damage incident that occurred at the photovoltaic installation of the Sacramento Municipal Utility District (SMUD PV1) in California [7] should be compared to the damage observed at Vulcano and Kythnos.

The conjectural scenario of a nearby lightning strike inducing sparkover at points of weak insulation, followed by damage caused by the dc current, could be more credible if knowledge were available on two parameters: (1)  dielectric withstand of the insulation between the modules and their frame, under various conditions of contamination, and (2) levels of the overvoltages that could be induced in the circuits.  The first parameter would require tests on the actual configurations, and might be impractical in view of the large number of possible configurations.  The second parameter might be evaluated by theoretical analysis, such as that reported Stolte [9].

The ambiguity in the postmortem may be resolved by further study of the failure modes of a panel (module within its frame) under simulated lightning and under dc stress with surface contamination.  The value of such tests would be to determine the need of further protection or design improvements in the panels to avoid damage, or to better understand the mechanism of the failure in order to settle the dilemma on the exact scenario leading to the observed damage.  Ultimately, the knowledge would also provide the basis for an informed decision on the cost-effectiveness of air terminals.

5.  General Conclusions

The two case histories presented in this report demonstrate that it is possible to provide protection for the power conversion electronics in the face of inescapable lightning strikes to the array field. in several instances, damage was limited to the modules; the surge protective devices performed their function with no damage to themselves.  In one instance, damage was inflicted to the surge protective devices, but even while failing, they protected the expensive downstream circuitry.  Depending on the point of view, achieving protection at the cost of a failed protective device may be considered successful, while an alternate view might be to expect protection with no sacrifice of the protective device.

The observations made at these two sites, the evidence collected before the visits, and the preceding discussions lead to a set of conclusions, some still in the form of conjectures, some in the form of firm conclusions.  Furthermore, implementation of the recommendations presented here may validate the conjectures and elevate them to the status of firm conclusions. A most important point to bear in mind, however, is that the unpredictability of lightning occurrences make it a risky business to draw sweeping conclusions based on only a few years of observation [6].

Protection against lightning damage to the array modules is a more difficult and less clear-cut issue than operation and survival of protective devices incorporated in the circuit:

- First, there is still some ambiguity in attributing all of the observed damage either to a direct effect of lightning, or to an indirect effect.

- Second, there is no sufficient evidence and long-term data on the effects and costs of a presumed direct strike to rule out air terminals, although their cost-effectiveness appears questionable.

5.1  Conjectural conclusions

A likely scenario to explain the observed effect is a combination of lightning-induced overvoltages with low insulation withstand.  This low withstand may be an inherent limitation of the photovoltaic module layout, or may be the result of pollution or moisture.

The evidence at Vulcano tends to point away from a simple direct lightning strike because the reported damage was limited to the lower part of the array.  However, no direct inspection of the failed module was possible in this case.

The overvoltages associated with the one incident at Vulcano were successfully suppressed as no damage was inflicted to either the surge suppressor themselves, the first line of defense, or to the power conversion electronics, the potential victim equipment.  However, since the amplitude of the lightning stroke in that incident is not known, the conclusion should not be that protection has been achieved for level of severity.

The effectiveness of lightning rods appears questionable in view of the several incidents at Kythnos.  However, a higher density of rods, or greater height, might have reduced the damage.  Nevertheless, the scenario of possible damage by indirect effects leaves in doubt the justification for the expense and disadvantages of providing lightning rods.

5.2  Firm conclusions

The one obvious conclusion, not unexpected, is that lightning does represent a threat to photo-voltaic arrays, either by direct damage or by indirect damage.

Good evidence has been provided that surge-protective devices with appropriate ratings (coordinated protection with the equipment to be protected, adequate surge current handling capability, and not excessively low clamping voltage for the systems voltage conditions) can protect the electronic equipment.

The one case of failure of a surge protective device that occurred shows that with suitable failure mode (i.e., short-circuit), protection of the electronics can be obtained for the first incident.  However, if the protective devices are associated with fuses, as in the case of Vulcano, failure of the protective device would result in blowing the fuse and, unless an indication of that situation were provided, the equipment would then be left unprotected for the next occurrence.

5.3  Recommendations

The ambiguity in attributing the damage to a direct lightning strike may be reduced if the suggestions proposed in this report for simulated lightning tests and study of failure modes were implemented:

- Establish a common, world-wide data base summarizing all observations of documented or suspected lightning damage to panels.

- Establish a common, world-wide data base summarizing all observations of damage to surge protective devices

- Establish a common, world-wide data base summarizing all observations of documented dc insulation faults on panels.

- Perform laboratory simulation of lightning attachment to panel frames and to module surfaces.

- In view of the prevalent practice, with apparent success, among European designers of not grounding the dc system, the quasi-axiomatic practice by U.S. designers of multiple-point grounding should be re-examined, and a dialogue initiated between the two parties.

- Operating procedures associated with the occurrence of the first fault in an isolated dc system should be reviewed and clearly defined.

An intriguing although not crucial question is that of the nature (and thus cost) of the materials used for the ground grid.  The Italian practice calls for copper, while the German practice applied in Kythnos calls for galvanized steel.  The question of copper versus galvanized steel in this context should be re-examined by specialists of cathodic protection schemes.

6.  Acknowledgements

The two site visits described in this report were made possible by the cooperation and hospitality of A. Previ and V. Messina of ENEL, and of J.  Chadjivassiliadis and A. Grielas of Public Power.  T.S. Key provided insights in reviewing the draft of this report.  Funding for this project was provided by the Sandia National Laboratories for the U.S. Department of Energy.

7.  References

[1]  Previ , A., 'The Vulcano Project, "Int. J. Solar Energy, 1985, Vol 3, pp 124-141.

[2] Cianos, N. and Pierce, E.T. "A ground-lightning environment for engineering usage." Stanford Research Institute, Menlo Park, Ca, 1972.

[3] Martzloff, F.D., "Matching Surge Protective Devices to their Environment," IEEE Transactions, Vol IA-21, No.1, January/ February 1985.

[4]  Shirakawa, S., F. Endo, H. Kitajima, S. Kobayashi, and K. Kurita, “Maintenance of Surge Arrester by a Portable Arrester Leakage Current Detector,” IEEE Transactions, Vol PD-3, No. 3, July 1988.

[5]  NFPA 78 'Lightning Protection Code, "National Fire Protection Association, Boston, MA, 1986.

[6]  Golde, R.H., "Lightning Protection, "Chemical Publishing Company, New York, NY, 1975.

[7] Collier, D.E., and Key, T.S., "Electrical Fault Protection for a Large Photovoltaic Plant Inverter," Proceedings, 20th IEEE Photovoltaic Specialist Conference, September 1988.

[8]  Martzloff, F.D., “Transient Overvoltage Protection: The Implications of New Techniques,”  Proceedings, 4th Symposium on EMC, Zurich, 1981.

[9] Stolte, W.J., "Photovoltaic System Grounding and Fault Protection Guidelines,” Contractor Report SAND83-7025, National Technical Information Service, 1985.

Protecting Computer Systems against Power Transients

François Martzloff

National Institute of Standards and Technology

Because small systems have moved from computer rooms into offices, factories, and homes, users and systems designers must deal with the subtle dangers the machines encounter

For the third time in less than three weeks, the sky darkened and thunder rumbled in the distance. With that ominous warning, the appointed "thunder scout" decided it was time to pull the plugs of the central unit and remote terminals of his CAD/CAM computer system. Better to shut down the operation than risk damage to the system, as had occurred in the two previous storms.

But pulling the plugs did not help. When the storm was over and the system was restarted, permanent damage had been done to it—to the chagrin of both the operator and the service contractor.

In this common example, the damage was caused not by power-line surges but by differences in ground potential at various terminals of the system. The oversimplified assumption that power-line surge problems could be eliminated had led the uninformed operator to attempt a simple prevention step. Not only did it not work, but it created a safety hazard: unplugging the line cords removed the safety ground, leaving the equipment still connected to the data lines where the surges were occurring.

Understanding the general causes of, and remedies for, power transients can help users of small computer systems, especially stand-alones, protect their systems with do-it-yourself methods. More complex systems may need the attention of a specialist. Systems designers should also be aware of the way users hook up their systems, the potential damage that could be caused by power transients, and side effects of incorrectly applied measures.

Growing concern among computer users that power-line surges may damage equipment or cause loss of data has created a market for surge suppressors. But clear performance standards in the industry are lacking, and several standards-writing groups are striving to develop adequate ones. To make a difficult choice among these devices, the consumer should learn some basic rules about selecting and installing a suitable surge suppressor. Even the best surge suppressor, if incorrectly applied, might not work and could cause adverse side effects.

# Transient origins

While the term "transient" is often understood as a transient overvoltage, it is also more broadly interpreted as the occurrence of any disturbance, either on the power line or the computer system's data line.

The most obvious source of an electrical disturbance is a lightning strike, but the lightning bolt need not hit power lines to cause damage. Because the electromagnetic field radiated by the lightning current couples into the conductors of power lines or data lines, it induces transient voltages along these conductors. Also, as the lightning current spreads into the ground, it produces differences in potential at points that are normally at "ground" potential. Conductors spanning some distance between their ends in the area where the lightning current is spreading will be exposed to these differences of potential, or to a transient overvoltage.

Though the direct effects of lightning can be dramatic, their relatively low rate of occurrence can lull one into complacency, and most of their widespread indirect effects can be overcome through sound protection practices. On the other hand, electrostatic discharges, which could be considered miniature lightning discharges, require only the fingertips of mortals rather than an Olympian fistful of lightning bolts to have very serious effects

A less obvious but more frequent source of transients is switching sequences in the power system. Switching can be a normal, recurrent operation such as turning a local load on and off, or it could entail occasionally clearing an overload or short circuit.

These switching transients cover a wide range of frequencies and amplitudes. Some have a brief duration (nanoseconds) and involve little energy (millijoules). While they present little risk of damage, their high-frequency spectrum makes them likely sources of interference. Others have a longer duration (microseconds or even milliseconds) and involve greater energy (up to hundreds of joules) with lower frequencies. They have the opposite trait of low risk of interference because of the relatively low frequencies, but because of the longer duration and increased energy, they have a higher damage risk.

Another source of disturbance to computer systems is the occurrence of an undervoltage that could be caused by a nearby startup of heavy loads or by distant faults, such as lightning-induced line flashover, falling trees, or utility lines downed by runaway vehicles. While transient overvoltages can be easily suppressed—a more correct description would be "mitigated"—by a simple added device that diverts the excess energy, the reduced energy associated with an undervoltage cannot be supplemented by a simple device. Different methods are needed for a solution of that problem.

Over the years, the need to learn more about the characteristics of these transients has led to various projects aimed at monitoring power-line disturbances. One result of these projects—which are performed by isolated researchers, sometimes with equipment designed by the researchers rather than commercial equipment—is that their reports are based on different assumptions and definitions of disturbances. Comparing results can thus become difficult and confusing [see table, overleaf].

Leaving the problems of monitoring transients and designing protective devices to the specialists, an informed user can take several steps toward buttressing the reliability and integrity of the system. The first step is to distinguish between mere temporary upset and permanent damage, each of which has a different impact on the user, depending on the relative importance of the operation. For a commercial setup, disrupting the operation can be more expensive than repairing the damage so that protecting data integrity ranks high. For an engineer working at his home computer, however, damage protection may be more important than some data loss. In this case, limiting the protection expense to avoiding damage and accepting interruptions may be preferred.

# Vulnerable stand-alones

Small computer "systems" can be categorized as stand-alone systems or distributed systems. A stand-alone system is typically a one-operator setup consisting of a desktop computer coupled with a printer, or any microcomputer not linked to a net-work. Distributed systems range from a simple stand-alone augmented by a telephone or other network link to multiple-station systems or process control systems with remote sensors and actuators.

Found in offices, laboratories, and homes, stand-alone systems can be disrupted or damaged by two possible causes. First, transients with low amplitudes (less than 1000 volts) are buffered by the computer's power supply but might still couple into circuits and cause glitches. Transients of high amplitudes (over 1000 V) may at worst damage the power input components and are likely to cause glitches at best. Second, power interruptions (sags or outages) can cause a momentary shutdown.

Transient damage protection for these systems is simple to achieve and is probably built in to some degree. However, until the day arrives when equipment has its transient capability stated on the nameplate (which may be sooner than expected because the Europeans are increasingly concerned with electromagnetic compatibility issues), the user has no way to know the extent of that protection. The European approach, motivated by a 1989 Directive on Electromagnetic Compatibility promulgated by the European Community Council, requires that equipment must operate satisfactorily in a specified environment without introducing intolerable disturbances into that environment. Thus, this ability is likely to be stated explicitly, in addition to the usual volt-age, frequency, and current ratings now required.

So far, the approach has been one of purchasing additional peace of mind by inserting a separate surge suppressor (also called spike protector and transient voltage suppressor) on the power cord. Prices for these devices range over an order of magnitude, and claims of performance may include the fastest response (an irrelevant issue) and the lowest clamping voltage (a reliability risk because the transient protector may fail under abnormal power fluctuations).

Though its basic technology does not change rapidly, details of the rating and packaging of a surge suppressor are driven by market competition. Ideally, its rating should reflect three basic requirements: the nominal line voltage, the surge current capability, and the clamping voltage during the surge. All of these should be stated by the maker of the device with due consideration to the user's needs for protection and long-term reliability.

At this time, there is only one performance standard in the United States for transient voltage surge suppressors, UL 1449, which was developed by the Underwriters Laboratories. This standard specifies primarily the safety aspects of the product, but does contain some performance specifications. The UL label on a surge suppressor means that a test has been applied to the device, reflecting industry consensus standards on the severity of the environment. In the UL test, a specified surge current is applied to the device and the maximum resulting voltage is measured; this is then indicated on the product.

Product literature for some devices, however, makes claims of response time in nanoseconds—even picoseconds—a feature that is not important in a power system. Nanosecond pulses do not propagate very far in power systems, and measuring a picosecond response time in support of the claim would be a technical challenge. Like-wise, emphasis on achieving the lowest clamping voltage only demonstrates imbalance in the design goals: the object of a surge suppressor is to lessen the surge level from the thousands of volts that can occur occasionally; it is not to shave off the last tens of volts from the protection level in a "lower is better" bid for ranking in the purchaser's choice. An excessively low clamping voltage introduces the risk of premature aging, even failure, of the device when the power line goes through repeated momentary overvoltages, or "swells."

The second type of disturbance, a sag or outage, cannot be corrected by a surge suppressor. The computer operation is interrupted when the sag or outage exceeds the capability of the internal dc supply to power the logic and memory circuits. Most computers have a built-in capability to maintain operation for a short time when this power is lost, but that supply is drained out if the interruption is long enough. if the computer is using a disk drive when the sag occurs, a shut-down is likely; in an office using several identical machines, some ride through a disturbance while others, especially those reading from a disk, shut down and have to be restarted. Protection against such sags and outages requires an uninterruptible power supply (UPS), which is now readily available. In fact, the volume of UPS production as well as competition has brought prices down so low that purchasing one becomes a viable solution and, for users de-pendent on the continuity of their operation, a must.

Unexpected problems

A power outage or sag on distributed systems has the same effect as for stand-alone systems. A more subtle problem, however, has crept in for some sophisticated systems that include automatic restart, or rebooting, after a power interruption. Anecdotes have circulated of damage caused by repeated sags during the automatic rebooting sequence, typically occurring because of multiple lightning strokes or during fault clearing with automatic reclosing by the utility system.

In the case of surges, as soon as a simple stand-alone system is augmented by peripherals, additional remote terminals, networking, and sensors that require a data link, the threat that the system will be affected increases. Even what may appear as a stand-alone system, such as a simple desktop pair of a PC linked with a printer, might be at risk if the two units are plugged into different power receptacles fed by separate branch circuits from the breakers.

In addition to the risk of interference or damage from surges on the power line, the data-line input and output ports are also vulnerable. Several mechanisms can inject interfering or damaging transients into the data lines of distributed systems. First, a problem could result because data lines act as antennas that can collect energy from electromagnetic fields and feed it, as noise or surges, to the data port's input or output, the driver or the receiver of the computer, or its peripherals.

The problem's severity increases with the length of the data link Within the same room, the risk of damage is minimal. But as the communication link reaches farther out, the risk increases that a surge would not only interfere with a system but could damage it. Though there may be an unknown (to the user) built-in protection or inherent capability of the data port components to with-stand these surges, little is known about the occurrence of surges on data lines, compared to that on ac power lines, which makes the task of designing protection difficult.

For users of computer systems in the same room or the same corner of a building, the built-in capability probably suffices. For systems with longer reach, the ultimate protection is an optical-fiber link with no metallic jacket, which provides immunity against noise collection as well as possible surge damage. For these complex systems, however, the do-it-yourself approach should be replaced by one that has been designed by a specialist.

Another mechanism that could cause trouble is the difference in the potential of objects at nominal "ground" potential occur-ring during surge events. Most data links operate with the signal reference conductor (shield or one wire of a group) connected to the chassis of the equipment. This chassis is in turn connected to the grounding conductor of the power cord supplying the equipment, a requirement of the National Electrical Code. Thus, if lightning or power system faults inject a high current in the sites ground conductors, the potential of the "grounded" points at the two ends of the data link differs. This potential difference causes a current to flow into the data link, possibly exceeding the capability of the input or output components.

The user can stay with conductors for the data link or convert (or initially design) it to an optical-fiber link, an approach that is becoming increasingly popular as hardware costs fall with economics of scale. However, if the conversion electronics at the ends of the fiber link are disturbed by electrical noise, that noise will be faithfully transmitted, not blocked.

If a conductive data link is to remain, the remedy is to insert protective devices that are complementary for the power line and data line. These devices typically operate by limiting the overvoltage or attenuating the higher frequencies by filtering, which works effectively on the power line but not on the data link. Here, filtering is not possible because it would affect the signals; limiting the overvoltages will eliminate that damage risk, but might still let through a spurious signal. Thus, data integrity may be more difficult to achieve unless the software includes inherent immunity or fault tolerance.

# Side effects

Avoiding damage with protective devices may then seem to re-quire only the insertion of a power-line surge suppressor at the wall receptacle and a data-line surge suppressor at the input to the computer. This apparent simplicity, however, is deceptive because the very operation of this device, if incorrectly installed, can have a side effect that would put the data link components at risk, a mechanism that is only beginning to be fully recognized.

Still another mechanism can be demonstrated by a scenario that can occur in any building with power and telephone service. The incoming telephone line is provided with surge suppressors (car-bon blocks or gas tubes) that divert surges to the nearest grounded conductor, generally a nearby water pipe. The manufacturer of the computer or modem used for the computer-telephone-line linkup may have provided a protective device within the equipment. Alternately, the surge-conscious user may have inserted a protective device in the power cord. But should a surge occur on either the data line or the power line, the corresponding protective device will dutifully divert that surge to the nearest ground. Since the "nearest ground" may not be the same for the connection of the two suppressors, the surge current in the ground connection raises the potential of one side with respect to the other, placing the data input at risk.

The solution is a miniature setup of the "ground window" concept developed by telephone companies in protecting their central station switches: all cables entering a room or a complete floor in a building are routed through a single "window" where grounding conductors, shields, and ground connections of protective devices are bonded together. In this manner, there cannot be any potential difference between the various ground reference points within the room or floor.

Some surge suppressor manufacturers have adapted that concept to a portable version of the ground window, a device consisting of a suppressor for the power line and one for the data line, but packaged in a single box most likely sharing the same ground connection. This local ground window is now found in computer or hobby stores and is easily recognizable because it features both a power connection (male plug for connection to a wall receptacle and female receptacles for powering the loads) and a pair of data link connectors (input and output). Depending on what is needed, these connectors can be a standard telephone jack, a multipin RS232, or a cable television coaxial connector. The device is then inserted near the computer, with the power cord and data link routed through its connectors.

Another protection scheme is always available: disconnect the system when not in use! In fact, some of the consumer guidance folders inserted by the utilities with their monthly bills mention that approach. That option may not be practical for commercial operations, where some link could be left connected, creating the risk of ungrounded equipment. Thus, if applied, every link to the outside world must be disconnected.

To probe further

A good source of information on the basics of lightning is the book Understanding Lightning by Martin A. Uman, available from Academic Press, New York, 1971. Solutions to noise problems are given a general treatment in the second edition of Noise Reduction Techniques in Electronic Systems by Henry W. Ott, available from John Wiley & Sons, New York, 1989. Fundamentals of surge protection techniques are treated in Protection of Electronic Circuits from Overvoltages by Ronald B. Standler, also available from John Wiley & Sons, 1989. Another useful reference is Uninterruptible Power Supplies by David C. Griffith, published by Marcel Dekker, New York, 1989.

Guidance on the nature and severity of transients (not specifications for protective devices) is given in the IEEE Guide for Surge Voltages in Low Voltage AC Power Circuits, American National Standards Institute, C62.41-1980, available from the IEEE Service Center, 445 Hoes Lane, Box 1331, Piscataway, N.J.; 800-678-IEEE.

A paper by François Martzloff and Thomas Gruzs titled "Power Quality Site Surveys: Facts, Fiction and Fallacies" in the November 1988 IEEE Industry Applications Society Transactions presents a review of recording, analyzing, and reporting transient disturbances on power lines. Another paper, "Coupling, Propagation, and Side Effects of Surges in an Industrial Wiring System," by Martzloff in the same Transactions is in press. The journal is available from the IEEE Service Center.

Update on a Consumer-Oriented Guide

for Surge Protection

| Thomas Key, Doni Nastasi, Kermit Phipps EPRI-PEAC 10521 Research Dr. Knoxville, TN 37932 | François Martzloff National Institute of Standards and Technology* Gaithersburg MD 20899-8113 f.martzloff@ieee.org | Jim May Illinois Power Company 500 South 27th Street Decatur, IL 62525 |
| --- | --- | --- |

# Abstract

Caught among contradictory stories on the need for surge protection as well as unsupported anecdotes of surge-related failures found in some editorial advertising, the typical consumer is in a quandary on how to best allocate personal resources to protect the expensive electronic equipment found in a modern household.  To help provide some answers to this quandary, a team of experts had previously developed a basic engineering Recommended Practice on surge protection of residential electronics.  The value of the theoretical concepts presented in the Recommended Practice is illustrated by two case histories where such concepts were not applied.  In addition, “post mortem” examinations have been performed on appliances turned in as having failed as a result of a lightning surge.  Those appliances that were in fact not damaged by lightning, although part of a claim settlement, were tested for surge immunity.

1.  Introduction

1.1  The need for a Guide on Surge Protection

As home appliances and electronics have become more sophisticated they have also become more susceptible to damage from energy anomalies.  These anomalies are most often caused by switching surges and lightning strikes.  They are also causing more frequent homeowner insurance claims.  While there is a considerable amount of knowledge about the various components of the issue (lightning, surge damage and protection, and grounding practices),  there is no single definitive source for combined information.  Therefore, a partnership was formed between State Farm, Illinois Power, the Electric Power Research Institute, and the National Institute of Standards and Technology to develop a document that would fill the need for a consumer-oriented, reader-friendly guide on surge protection.  The initial goal of this partnership was to develop a recommended practice for protecting homes against surges and lightning.  From this, the partners expect to convey best surge mitigation practices, to decrease appliance damage and the number of loss claims to insurance companies, and to reduce consumer worry about surge-related damage to their electronic appliances.

Like many electric utilities, Illinois Power, with over 500,000 customers, understood the need to provide an authoritative and well-documented reference document applicable to protecting property and equipment.  With such a reference, electric power producers can more easily answer the many customer inquiries about surge protection as well as to better communicate with customers via specific power quality and equipment protection programs.  Promoting such customer-oriented service programs is expected to be a win-win situation.  In the case of Illinois Power, sponsoring this project was also an opportunity to help one of their large customers, State Farm Insurance in Bloomington, IL.

1.2  From engineering writing to general-public writing

As a first phase of this project, a group of experts had developed a Recommended Practice document [EPRI Project 01 39-8002, 1997] on the origins and mitigation of surges in the residential environment.  This 90-page document was written from the engineering point of view to document the consensus reached among these experts and serve as the basis for the next step, a consumer-oriented publication available to the general public.  The need for a consumer-oriented guide stems from the practical fact that, for most situations, a generic surge protection system costs less than an engineering analysis to determine exact requirements.  Consequently the partners recognized the value of developing a version of the guide written so the general public could understand and apply the basic concepts.  The idea is that individual homeowners, who are concerned about their appliances, will better understand what to look for and how to correct deficiencies so that they might take sound and cost-effective actions.

To accomplish this objective, NIST, in concert with the co-authors of the present paper, is undertaking the writing of a shorter, reader-friendly guide on surge protection.  One of the important theoretical points made in the engineering report was the need to provide coordinated grounding practices among the utilities (electric power, telephone, cable and satellite TV) serving a residence.  To further document the importance of this coordination and the dire consequences of not following them, two case studies were performed on lightning-related incidents.  Bench tests were performed on damaged equipment obtained by agents of State Farm, with the purpose to determine typical failure modes and assess surge vulnerabilities and immunity.

Three critical elements for the guide are recognized in this task:

1. 	To be clearly written in layman's language — a challenge to the editors

2.	To originate from an objective source — hence the participation of NIST as the “publisher.”

3.	To provide simple instructions on how to reduce surge vulnerabilities in the home — another editorial challenge for engineers accustomed to write engineering instructions.

2.  Lightning-Damage Case Studies

In general much more technical information had been collected in the Recommended Practice development effort than a typical, or even highly motivated, homeowner could use.  Even so, some voids in understanding appliance failures still existed, namely exactly why some appliances fail and other do not.  Both field experience and lab evaluations of appliances show that susceptibility to surges varies by appliance type, make, and model. According to insurance claim records, the most commonly damaged appliances include telephones and modems, computerized equipment, televisions, VCRs, and satellite receiver systems, which are all generally “multi-port” appliances.

The theory for failures presented in the recommended engineering practice document was the likelihood that voltage potential differences between ports was the Achilles’ heal of many residential appliances and systems.  To back up this theory, a sampling of multiple-port appliances   was obtained from appliances surrendered as part of insurance claims in the state of Tennessee.  Postmortems and laboratory experiments were conducted to better understand the failure modes of these appliances.

Two known lightning incidents occurred recently in the Knoxville area, providing a unique opportunity to document the mechanisms and failure modes of residential electronics.  The first incident involved a small house made primarily of wood where the power service entrance and the cable TV entrance were at opposite ends of the house – the classic error in installation practice.  The second incident involved an expansive residence with an elaborate audio-video system with a centralized equipment rack distributing signals to speakers and video monitors.

2.1  The case of the Cozy Cabin

At this rural site in Eastern Tennessee, a wood-structure residence suffered two successive failures of video equipment during lightning storms, a few months apart.  The owners allowed PEAC personnel to visit the site and acquire the second failed TV receiver for a post-mortem.

2.1.1  Site configuration

The power service entrance is located at one end of the house, while the cable TV service entrance is located at the opposite end.  A visit to the site revealed that the cable TV shield was grounded only by a questionable ground rod next to the house foundation (within the drip line, and thus in dry soil, see Figure 1).  Furthermore, this grounding connection was not bonded to the grounding connection of the power service entrance, a clear violation of the National Electrical Code, according to the current edition as well as several, if not all, earlier editions [NFPA 70, 1999].

[See pdf file]

## Figure 1 – Cable TV service entrance and ‘ground bonding’

The local cable TV company was informed of this situation and took what they believed an appropriate action: the incoming cable was first routed under the house, in the crawl space, to allow bonding the shield to the power service grounding connection.  From there, the cable was returned to its original point of entry into the house, at the opposite end.  It would seem that under such a configuration, a lightning current surge traveling along the cable shield (instead of a proper bonding conductor), might create sufficient voltage drop along the path under the house to create problems.  However, the interaction was not pursued further with the cable company.  A recommendation was made to the owner of the house to install a surge reference equalizer near each of the video equipment in the house.

2.1.2  Post mortem and surge tests

One of the failed TV receivers was made available to PEAC for examination.  No evidence of damage was found on the power side of the chassis, but a clear indication of surface flashover was observed between the cable input ‘ground’ termination (connected to the incoming cable shield) and the shielding can of the tuner (Figure 2).  After cleaning as best as possible the carbonized path of the flashover, a surge voltage was applied between the power cord of the receiver and the ‘ground’ of the cable input: flashover occurred for a 2 kV Ring Wave.  By removing the material to a greater depth and covering it with epoxy, the gap did withstand a greater level, and failed at 2.5 kV.  That flashover occurred at another part of the original insulation, thus providing valid information on the original withstand capability.

[See pdf file]

## Figure 2 – Cable TV input termination and UHF tuner at rear of receiver

2.1.3 Conclusions from the Cozy Cabin

This case study illustrates the classic situation of separate service entrances, compounded with incorrect bonding.  The examination and test demonstrate that at least 2.5 kV can be developed across the power port and the cable TV port of the receiver under a condition of distant or nearby lightning strike.  This finding is consistent with the results of other tests reported under Section 4.

Another significant finding from this case history is the anecdotal confirmation of allegations that cable TV installation practices prevailing in many residential situations might be in violation of the National Electrical Code (NEC).  This violation makes even more hazardous the now well-recognized occurrence of undesirable separation between utilities entrances.

2.2  The Case of the Rambling Residence

A residential estate insured by State Farm was the scene of a lightning incident where a tree adjacent to the house was struck (and subsequently died).  Extensive damage was inflicted to the audio-video components distributed from a central rack throughout the residence and its surroundings (large patio and swimming pool with outdoor lighting and audio speakers).

Through the cooperation of the State Farm agents, the home owners graciously allowed PEAC engineers to visit the residence and observe the configuration of the system in an attempt to better understand the mechanisms leading to the damage.  State Farm also made available to PEAC the complement of damaged or presumed damaged equipment that had been promptly replaced as part of the claim settlement.  Thus this case history, unlike most lightning incidents, offered an unusual opportunity for documenting the process and consequences.  It was made very clear to the owners that the visit was prompted by the curiosity of electrical engineers and not by State Farm agents.

Three activities were undertaken for that purpose:

- Bench examination of returned equipment and surge testing of undamaged equipment

- Site visit of the residence

- Laboratory coupling of electric field stress into a remote speaker-to-amplifier connection

    - Bench Examination

The complete central rack of audio-video entertainment equipment, as well as the remote speakers had been replaced as part of the claim settlement.  Local State Farm agents were able to retrieve the damaged entertainment equipment from the house and send it to PEAC for examination.  Bench tests for each electrical appliance began by plugging it into a 120-V ac outlet.  Physical signs of normal operation were noted such as illuminated displays, response of controls, or audio/video output.  The equipment cover was removed for an internal inspection.  In most of the equipment, physical damage such as a burned-out transistor was very apparent.  Table 1 lists the home entertainment equipment that was submitted, and their condition.

A significant finding was that all of the power supplies in the equipment were functional, indicating that the lightning surge either did not enter through the ac power port, or was not severe enough to cause damage to the power supplies.

Table 1 Equipment submitted for bench tests

| Qty. | Equipment | Condition |
| --- | --- | --- |
| 1 | Stereo tuner/amplifier | Illuminated display was not working |
| 3 | DSS receiver | Damage to telephone circuit |
| 2 | Twelve-channel integration amplifier | Damage to power transistors |
| 12 | Indoor speaker | Woofer damaged |
| 4 | Indoor/outdoor speaker | Woofer damage on all but two units |
| 1 | Independent color TV receiver | No damage |

The examination and, as appropriate, tests revealed the following conditions:

- Except for its non-operational display, the stereo tuner/amplifier appeared undamaged.

- The visible damage to the DSS receivers was nearly identical in all three units.  Apparently, the surge had entered through the telephone port and had damaged the small surface-mount electronics that make up the modem circuit.  However, because the satellite receivers could not be operated without their antenna and code-reading cards, the extent of the functional damage could not be determined

- The two 12-channel amplifiers had sustained damage to their output transistors that drive the speakers.  The power supplies and fuses were not damaged.  Furthermore, it was found that some speaker outputs were still operational.  This situation suggested a possible mechanism that damaged only some of the output transistors, and therefore not attributable to a “power-line surge.”  In turn, that hypothesis was later verified by a laboratory test, as described in 2.2.3 below.

- Speakers, tested by connecting them to an amplifier that was known to be functioning properly, were found to have their woofers damaged, but the tweeters still operational.

Other electrical appliances in the house including television sets and VCRs not connected to the centralized system were not included in the returned package and therefore presumed as not damaged.  This finding helps to confirm the conclusion that the long leads interconnecting the distributed system components acted as energy collectors, feeding the induced voltages or currents into the communications ports of the equipment.

    - Site Visit

The purpose of the visit was to look for clues to explain the specific damage that was observed in some of the equipment.  The following observations were made:

- Approximate distances between the lightning strike and affected equipment

- Location and grounding at the service entrances of cable TV, power, and telephone

- Other wiring and general installation practices

The overall physical layout of the house, damaged tree, and electronic equipment are shown in Figure 3.  The mature tree that was struck is much taller than the house and is the tallest of the trees in the immediate area.  The bark was stripped from the tree trunk for most of its height.  As shown in the figure, the trunk is only approximately 15 meters from the house and even closer to the patio, where some of the audio speakers were installed.  Outdoor speakers are also located in the pool area and connecting walkways.

From this informal examination, it appears that no electrical codes were violated.  Furthermore, the cable TV and telephone entered the residence together with the electrical service at the same location (garage), as is the practice recommended in the engineering report.

One of the observations during the laboratory inspection of the audio amplifiers was that the power supplies of the units were not damaged, but their output transistors that drive the speakers and the speakers themselves were damaged.  Before arrangements could be made for the site visit, it was speculated that the surge energy had been coupled into the speaker wires, which are probably very long and very near to the lightning strike, rather than as a “power-line surge.”  The visit to the installation verified this theory.  The home entertainment equipment, including amplifiers, is centrally installed in the basement of the house.  Speakers are located throughout the house, the patio, and the swimming pool area.  The wire length between the outdoor speakers and the central amplifier is about 30 meters, and some of the wires run within 10 meters of the tree trunk.

[See pdf file]

Figure 3 – Schematic configuration of the Rambling Residence

    - Laboratory Coupling of Electric Field

To validate the hypothesis of a failure mechanism involving the coupling of electric field energy into the speaker wire run, a qualitative laboratory test was staged, using the surviving channel of the amplifier to drive a speaker.  An audio signal from a tape deck was fed into the amplifier input to monitor its operation during the test.

A conventional Marx impulse generator at the NIST High-Voltage Laboratory was used to apply a 1.2/50 s high-voltage field between two parallel plates, each 2 m x 1 m.  A length of 5 m of speaker wire feeding the audio output from the system audio amplifier was sandwiched between the two plastic foam sheets separating the lower (grounded) plate, to which the amplifier chassis was bonded, from the upper (impulsed) plate.  A UPS was used to power the tape deck supplying the audio input signal to the power amplifier, which was also powered by the floating UPS.

With increasing amplitude of the impulse, a total potential of up to 30 kV was developed between the speaker wire and the chassis of the amplifier, but no distress was observed at that level.  Note that the actual field strength during the incident is unknown but suspected to be quite high, so that this test does not pretend to duplicate the incident, but only to illustrate a possible mechanism.

The effective length of the wire was then increased by connecting to each wire a piece of foil of about 0.02 m2, simulating the increased capacitance effect of about 50 m of wire.  Again, the impulse was applied in increasing steps.  At 70 kV, a flashover occurred between the two plate edges, but not involving the speaker wire.  Immediate failure of the amplifier output circuit was noted.  From this anecdote, we conclude that the rapid field change (not recorded during the test but certainly faster than the standard 1.2/50 s impulse) did have the capability to couple enough surge energy into the capacitance divider of wire/ground plane and cause destructive failure of the output transistor effectively connected across that capacitance.  Such a scenario can be considered a reasonable emulation of the circumstances surrounding the “Lightning Incident at the Rambling Residence.”

Thus, this qualitative laboratory demonstration provides one more piece of evidence that electronic appliances can be damaged by surges impacting their communications port, to the point that expecting protection by simple application of SPDs on the power port is not enough, and comprehensive protection is a necessity.

    - Conclusions from the Rambling Residence

Generally, electronic equipment can be protected from surges by proper installation and with the use of surge suppressors.  In the rare case of a nearly direct strike, however, there is little that can be done in widespread residential settings to prevent damage, unless a thorough mitigation study and extensive protection implementation would be performed.  While that type of protection is theoretically possible and has been implemented — at considerable cost — for facilities involving national security, airports, communications centers, etc., it is generally not considered as economically justifiable for residential installations.  A central home entertainment system with remote speakers, such as the one installed at this house, is an easy victim for coupling of surge voltages or surge currents in the long runs of cable.

Since the visit to the residence was motivated, as stated, by the curiosity of PEAC engineers rather than by a customer complaint, there was no need to offer a prescription for protection.  Instead, the visiting engineers offered the general statement that for a direct strike such as the one that had occurred, providing a high level of protection confidence by a comprehensive retrofit would probably cost more than the equipment that was damaged.  In contrast, the dead tree was the one irreplaceable loss that was most painful for the owners.  Techniques for protecting trees exist (an extensive array of grounding cables along the limbs, [NFPA 780, 1997] and are sometimes applied to trees recognized as having great historical or esthetic value, but the cost is generally a deterrent for typical residential surroundings.

3.  Post-Mortems on Returned Equipment

An assortment of residential equipment returned to State Farm as settlement of lightning-related claims was made available to PEAC.  These included submersible well pumps, audio and video equipment, and telephones.  The goal was to determine the failure mechanisms of the samples, whether it be failed power supply components, input/output ports, or other types of equipment failures.

Individual pieces of equipment were examined for mechanical condition, signs of electrical insulation breakdown, and if it seemed appropriate, powered to test their possible functionality.  Most were in fact damaged, as tabulated below, but a few appeared still operational.  This apparent functionality may well be a case of “walking wounded” so that the intention of the examination was not to contest the claim of damage, but to gain insight into the failure levels and mechanisms.

3.1  Equipment condition

    - Well pumps

Fifteen submersible well pumps in the size range of ½ hp to 1 hp were examined.  These pumps spend their lives underwater while connected to the power system conductors, and are therefore susceptible to lightning damage.

The units were visually inspected and resistance was measured between pairs of motor terminals and between case and terminals.  No conclusive evidence was observed on most of the samples, however one sample had very interesting evidence of lightning damage.  It had burn marks present at the point where the voltage is applied to the stator winding.  It also had a bulge in the stator that appeared to have been caused by excessive current through the winding.

    - Television Sets

Seven television sets were received for inspection.  Of these units, the failures most commonly observed were in the power supply.  Four of seven units had open fuses, suggesting that components inside had drawn excessive current and had failed, causing a short circuit.  Two of the units had shorted rectifier diodes, further confirming this theory.  One television had an open fuse, but was fully functional after a fuse replacement.  One of the more interesting cases was a television that had its tuner severely damaged, but the power supply was not damaged.

Television sets, being two-port devices, require some type of isolation between antenna port and ac power port.  Different protection schemes were observed in the television sets depending on their age.  Older sets utilized an antenna isolation scheme, with television chassis connected to the one of the line cord conductors.  Newer designs had direct antenna connections (no isolation), but had isolation built into their power supplies.

3.1.3    VCRs

Five VCRs were inspected.  Two had damaged power supply components.  One had apparent damage to the tuner.  VCRs have the same two ports as televisions and therefore require the same type of isolation.  All of the VCR samples studied at PEAC had the isolation scheme built into the power supplies rather than in the antenna port.

3.1.4    Stereo Equipment

Nine individual stereo components were examined.  One had damaged power supply components.  Three of the amplifiers had damaged output transistors.  Two of these were from the “Rambling Residence.”  Others were functional.

3.1.5    Telephones

Five telephones were examined, from which three had damaged ICs.  These may have been damaged by lightning.  Most electronic phones are equipped with plug-in adapters.  These adapters may sustain damage, but seem to protect the telephone equipment from damage on the ac power port.

3.2  Conclusions for Post Mortems

There were almost as many types of equipment failure modes as there were samples to examine.  The samples that had apparent lightning damage presented the signs one could expect from insulation failure, most often with subsequent damage done by the power-frequency fault current following the insulation breakdown.

4.  Surge Immunity Tests

The returned equipment that was found still operational was then used for destructive surge testing by subjecting them to Ring Waves or Combination Waves on their power port or on their communication port.  Two types of surge tests were conducted:

- Application of the surge to the power port only.  This test is primarily a surge current withstand capability for the rectifier that connects the DC link capacitor to the ac mains.  During a surge, this capacitor acts as a “surge absorber” and can draw a substantial charging current [Mansoor et al., 1999].  Ultimately, the voltage in the DC link might reach an excessive level for the downstream components, but from the few limited tests performed here, it appears that either the rectifier fails, followed by opening of the fuse, or that the fuse itself opens without downstream failure.  In either case, however, the appliance is a candidate for a trip to the repair shop, or a total loss damage claim, as indicated in the post-mortems.

- Application of the surge between power port and communication port.  This is the scenario illustrated by the Cozy Cabin case history in this paper.  The tests served to document further the process and the levels at which failure can occur.

4.1  Power port tests

Combination wave surges were applied to the equipment between the two power port conductors. Beginning with a peak voltage of 1 kV, the test sample was surged and then checked for functionality.  If the equipment sustained no apparent damage, then the surge voltage was increased and re-applied in 1 kV steps until either the equipment failed or until a maximum of 6 kV was delivered.

Three well pumps from the original group were functional and therefore were available for surge tests.  The coil resistance was measured and recorded before applying any surges.  The well pumps demonstrated a strong immunity to these surges.  All three samples survived all tests to and including 6. V and with no notable changes in performance or in coil resistance.  This remarkable withstand capability might be attributed to the presence of a built-in SPD.

Two working televisions were available for surge tests.  Each unit was energized, and using an antenna, was tuned to a local station having a strong signal.  The two units failed at 3 kV.  Upon examination of the circuits, both had suffered open fuses and failed power supply components. Rectifier diodes were found shorted inside one of the units.  Recall that in the post-mortem examinations, inside four of the sets, there were open fuses and two samples had shorted rectifier diodes.

Three VCRs were functional and were subjected to surge tests.  The first sample failed at 3 kV.

An open fuse and failed rectifier diodes were found inside.  The second sample failed at 4 kV, but without opening fuses and with no visible damage.  A probable result was a damaged voltage regulator.  The third sample withstood surges up to 5 kV, where a open fuse resulted.  The fuse was replaced and the unit functioned normally.  Surges were repeated, opening the fuse again at 4 kV.  The difference in survivability among the VCRs seemed to be transformer size.  Modern power supply transformers are miniaturized, operating at higher frequencies than the 60 Hz power frequency.  The VCR samples that had physically larger transformers survived the higher surge voltages.  The sample that blew the fuses and withstood the surge tests had the largest transformer of the three VCRs tested.

Five individual stereo components, specifically two cassette decks, two amplifiers, and one CD player were tested.  This type of stereo equipment is designed for use as interconnected systems of media-playing devices, amplifier, and speakers.  The goal of the surge tests was to assess the immunity of individual components' power supply circuits.  Therefore, each piece was tested without connection to other components.  After each surge, the tested sample was briefly connected to necessary components to verify that it was working properly.  A very consistent outcome was observed.  All of the samples survived the surge tests up to and including 6 kV.

Only one telephone sample was available for surge tests.  It was of the cordless variety, with an external power supply adapter.  This unit survived all of the surge tests with no apparent damage.

4.2  Two-port tests

Televisions and VCRs are of a similar category of equipment in that they both have the same input ports: ac power and antenna, for which the ‘ground’ reference can be raised to different potentials during a surge event.  The power port has no direct connection to the equipment grounding conductor because a two-prong ac plug is used.  However, at the service entrance, the neutral — one of the two conductors of the cord — is bonded to the ground bus of the service panel.  The antenna input is referenced to ground via a connection to a grounding rod outside the residence and (per NEC), a bonding conductor.  Manufacturers use various techniques to isolate these two ports from each other inside the equipment.  The purpose of these tests was to determine the surge voltage at which this isolation breaks down.

Most of the equipment was less than 6 years old and therefore represents the current state of technology.  By observation of a few samples, there seem to be two isolation schemes.  Older technology seemed to use a potted ring (an amorphous, plastic insulating material) paralleled with a resistor to isolate the shielded conductor of the antenna from the chassis of the tuner.  Newer sets have isolation in their switch-mode power supplies and directly connect the shielded antenna conductor to the tuner chassis.  All VCRs that have been observed use the latter technique.

Surge tests were conducted on five televisions and three VCRs to determine the voltage level at which spark-over would occur between these power and antenna ports.  The two power port conductors (line and neutral) were tied together because the two conductors act together to create the power port, and because there is no rationale to support the separate application of surges to each of the conductors of that port individually.  Using a 0.5 :s — 100 kHz ring wave, a 500 V peak surge was applied between power port and shield of the antenna port.  Subsequent tests were performed at incremental steps of 500 V until spark-over occurred or until a maximum of 6 kV was reached.  This voltage level was recorded and an oscillogram was taken.  A decision was then necessary.  If a surge voltage of 500 V less than the recorded value would also produce sparkover, it is possible that a carbon trace exists in the device, and tests were discontinued.  If there was no sparkover at the reduced voltage, the unit was subjected to a 1.2/50-8/20 s Combination Wave, starting at 500 V and increasing in increments of 500 V until breakdown or a maximum of 6 kV was reached.

The units that had isolation built into the antenna port sparked-over at the series capacitor of  the antenna port.  The breakdown voltage level averaged approximately 2.5 kV in these units. Units whose power supply outputs were electrically isolated from the inputs via transformers generally fared better.  One sample survived and performed normally after all surge tests.  Physical size of the transformer seemed to have some impact on the results.  Larger transformers seemed to tolerate surges better than smaller ones.

4.3  Conclusions to two-port surge immunity tests

Some type of isolation scheme is used in televisions and VCRs to electrically isolate the antenna input from the power supply input.  A general observation based on the small number of test samples is that older televisions (before VCRs were popularly used) seem to have their isolation built into the antenna ports using an insulating plastic material.  Newer technology seems to have moved the isolation from the antenna port to the power supply port by utilizing the high-frequency chopper output transformer.  During these surge tests, it was observed that the power supply isolation method was more immune to damage than the antenna port isolation method.

Based on this small number of VCR samples, a general observation is that VCRs use power supply transformers as isolation, similar to the newer TV sets, and have no isolation between antenna input to tuner chassis.  Generally, this type of isolation scheme withstood higher surge voltages than the antenna port isolating ring that can be found in older television sets, therefore VCRs seem to have the same (or slightly greater) levels of immunity as any television set.

5.  From the Engineering Report to the Consumer-Oriented Publication

The engineering report completed as the first phase of the project [EPRI Project 01-39-8002, 1997] and described in the PQA’97 summary paper [Key et al., 1997] was written for engineers, not for the general public.  The ultimate goal of the project, however, has been from the beginning to produce a self-standing but brief publication aimed at the general public, in particular electrical contractors, builders, insurance agents, and interested homeowners.  In the 1980's a Federal Information Processing Standards Publication [FIPS Pub 94, 1983] was developed by the then National Bureau of Standards (NBS) for the “computer room” environment.  At that time, when the residential electronics had not yet started their exponential growth, FIPS 94 became — and remains — a widely read reference.  It was first envisioned that a similar publication, albeit less voluminous, might be issued by the National Institute of Standards and Technology (NIST), the successor of NBS.  The project end-goal subsequently evolved to plan for a shorter publication, limited to the perceived limits of a typical reader’s attention span, but still under the sponsorship of the generic perspective of NIST.

The target date for general availability of this publication is now late 1999, giving interested parties an opportunity to implement feasible retrofit recommendations in time for the Y2K lightning season.  Hopefully, the recommendations will also influence future installations.

6.  General Conclusions

The combination of the theoretical considerations, presented in the cited engineering report, with further documentation presented in this paper, clearly demonstrates that the two-port interaction plays a large role in appliance failures during surge events.  That concept will be emphasized in the final proposed NIST Special Publication, which remains the ultimate goal of the project.

Nevertheless, readers of the present paper might be interested in a list of technical and practical conclusions, leading to recommendations they might wish to make to their colleagues or clients pending availability of the NIST publication:

- The expanding use of multi-port appliances is increasing surge vulnerability in residential environments.  More attention to their design and installation wiring is needed.  The concept of “compatibility levels” can help.

- The power port might not even be one of the ports involved in the damage.

- The typical homeowner is likely to assume the worst after a lightning event and mis-diagnose lightning damage.  “If it works it is probably not damaged” may be a reasonable point to publicize.  (Notwithstanding a justifiable concern about keeping a “walking wounded” in case of serious damage to other equipment in the residence.)

- In fact, when lightning strikes, the configuration of the residence appliances and wiring may be more important than the level of the threat.  This is particularly true for non-power born surges.

- House wiring systems will play an increasing role in determining vulnerability of appliances as installed in specific locations, as more wires are run and more appliance ports are referenced to each other.

7.  Acknowledgments

Roger Witt provided encouragement to the authors and comments on this paper, as well as making arrangements for the return of equipment and site visits.

The owners of the two residences, whose identity and exact location are not given here to preserve their privacy, provided a rare opportunity for documenting these two enlightening case histories, for which the authors are indeed grateful.

8.  Bibliography

Bibliographic citations in the text are listed below by alphabetical order of the lead author.

FIPS 94, Guideline on Electrical Power for ADP Installations, Federal Information Processing Standards Publication 94, Sept. 21, 1983.

EPRI Report 01-39-8002, “Recommended Practice for Protecting Residential Structures and Appliances Against Surges,” Final Report, 1997.

IEEE Std 1100-1992, IEEE Recommended Practice for Powering and Grounding of Sensitive Electronic Equipment, Emerald Book, 1992.

Key, T.S., Martzloff, F.D., Witt, R., May, J., and Black, S., “Developing a Consumer-Oriented Guide on Surge Protection,” Proceedings, EPRI PQA’97 Conference, Columbus, OH, March 1997.

Key, T.S. and Martzloff, F.D., “Surging the Upside-Down House: Looking into Upsetting Reference Voltages,” Proceedings of the 3rd International Conference on Power Quality, Amsterdam, Holland, October 1994.

Mansoor, A., Martzloff, F.D., and Phipps, K.O., “The Fallacy of Monitoring Surge Voltages: SPDs and PCs Galore !” Proceedings, EPRI PQA ‘99 Conference, Charlotte, NC, May 1999.

NFPA 70,  National Electrical Code, National Fire Protection Association, 1999.

NFPA 780, Standard for the Installation of Lightning Protection Systems, National Fire Protection Association, 1997.

## François Martzloff

END OF FILE “Text System Protection Techniques”

## June 2004

Citations in the text appearing as [Author, Date] are listed in alphabetical order in Section 6, Bibliography.